## Cover
2012-13
2013-14
Distribution Network Service Provider
Annual reporting template
This template is to be used by a DNSP to fulfil its annual reporting obligations to the AER.
Colour coding of input sheets:
Dark blue - Headings
Yellow - Input cells
Grey - No inputs required
Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so.
All dollar amounts are to be unrounded, and in nominal terms.
DNSP - trading name: |  | Endeavour Energy
DNSP - Australian business number: |  | 59 253 130 878
Reporting year: |  | 2012-13
Business address | Address |  | 51 Huntingwood Drive
| Suburb |  | HUNTINGWOOD
|  | State | NSW | Postcode | 2148
Postal address | Address |  | PO Box 811
| Suburb |  | SEVEN HILLS
|  | State | NSW | Postcode | 1730
Contact name/s | Jon Hocking
Contact phone/s | 02 9853 4386 or 0407 348 156
Contact email address/s | jon.hocking@endeavourenergy.com.au

## Contents
Electricity DNSP Annual Reporting Template
Table of contents
Cover sheet | 3. Quality of service and customer service
1. Service Target Performance Incentive Scheme | 4. General Information
1a. STPIS - Reliability | 5. Outages
1b. STPIS - Customer service | 5a. Network data - outages
1c. STPIS - Daily performance | 5b. Network data - feeder reliability
1d. STPIS - MED threshold | 5c. Network data - outages
1e. STPIS - Exclusions | 5d. Network data - planned outages
1f. STPIS - GSL | 6. Weighted average cost of debt
2. Demand | 7. Asset installation

## 1a. STPIS Reliability
Endeavour Energy
STPIS Data Reporting
2012-13
Reliability
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: SAIDI
Unplanned SAIDI | CBD | Urban | Rural short | Rural long | Whole network
Total | N/A | 85.27 | 268.01 | 730.68 | 116.03
Total - after removing excluded events | N/A | 75.5 | 247.99 | 730.68 | 104.55
Table 2: SAIFI
Unplanned SAIFI | CBD | Urban | Rural short | Rural long | Whole network
Total | N/A | 0.99 | 2.551 | 13.505 | 1.255
Total - after removing excluded events | N/A | 0.955 | 2.49 | 13.505 | 1.216
Table 3: Average distribution customer numbers
| CBD | Urban | Rural short | Rural long | Whole network
Customer numbers start of period | N/A | 735650 | 147717 | 291 | 883658
Customer numbers end of period | N/A | 755912 | 151785 | 291 | 907988
Average distribution customer numbers | 0 | 745781 | 149751 | 291 | 895823
Contents

## 1b. STPIS Customer Service
Endeavour Energy
STPIS Data Reporting
2012-13
Customer service
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Telephone answering
Telephone answering | Total - after removing excluded events | Total
Total number of calls | 193516 | 374574
Number of calls answered within 30 seconds | 162877
Percentage of calls answered within 30 seconds | 0.84167
Table 2: New connections
Note: this is for newly energised properties only
New connections
Number of new connections
Number of new connections not provided on or before the agreed date
Percentage of new connections not provided on or before the agreed date
Table 3: Streetlight repair
Streetlight repair
Total number of streetlights
Total number of streetlight faults
Total number of streetlight faults reported by person who is the occupier of an immediately neighbouring residence or is the proprietor of an immediately neigbouring business
Faulty streetlights not repaired within 5 days of fault report or agreed date
Percentage of faulty streetlights not repaired within 5 days of fault report or agreed date
Table 4: Response to written enquiries
Note: this does not include Saturdays, Sundays and Public holidays
Response to written enquiries
Number of written enquiries
Number of written enquiries not responded to in 5 days
Percentage of written enquiries not responded to in 5 days
Contents

## 1c. STPIS Daily Performance
Endeavour Energy
STPIS Data Reporting |  |  |  | 2012-07-01
2012-13 |  |  |  | 2013-07-01
Daily Performance
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Daily performance data (Unplanned SAIDI, Unplanned SAIFI)
Note: the excluded events to be removed from the data refer only to events listed in clause 3.3(a) of the STPIS, with respect to reliability data, and in clause 5.4(a) of the STPIS with respect to customer service parameters.
Customer service
Date | Network SAIDI all events total | Network SAIDI all events after removing excluded events | CBD SAIDI all events total | CBD SAIDI all events after removing excluded events | Urban SAIDI all events total | Urban SAIDI all events after removing excluded events | Long rural SAIDI all events total | Long rural all events after removing excluded events | Short rural SAIDI all events total | Short rural SAIDI all events after removing excluded events | Network SAIFI all events total | Network SAIFI all events after removing excluded events | CBD SAIFI all events total | CBD SAIFI all events after removing excluded events | Urban SAIFI all events total | Urban SAIFI all events after removing excluded events | Long rural SAIFI all events total | Long rural SAIFI all events after removing excluded events | Short rural SAIFI all events total | Short Rural SAIFI all events after removing excluded events | Total number of calls | Number of calls answered within 30 seconds | MED
2012-07-01 | 0.1526 | 0.1526 |  |  | 0.077167 | 0.077167 |  |  | 0.5286 | 0.5286 | 0.001434 | 0.001434 |  |  | 0.00135 | 0.00135 |  |  | 0.00188 | 0.00188 | 275 | 254 | Yes
2012-07-02 | 0.25674 | 0.25674 |  |  | 0.29158 | 0.29158 |  |  | 0.083714 | 0.083714 | 0.003793 | 0.003793 |  |  | 0.00439 | 0.00439 |  |  | 0.000809 | 0.000809 | 751 | 572 | Yes
2012-07-03 | 0.098482 | 0.098482 |  |  | 0.089013 | 0.089013 |  |  | 0.14583 | 0.14583 | 0.001032 | 0.001032 |  |  | 0.00107 | 0.00107 |  |  | 0.000835 | 0.000835 | 630 | 541 | Yes
2012-07-04 | 0.072653 | 0.072653 |  |  | 0.07265 | 0.07265 |  |  | 0.072808 | 0.072808 | 0.000614 | 0.000614 |  |  | 0.000572 | 0.000572 |  |  | 0.000829 | 0.000829 | 624 | 509 | Yes
2012-07-05 | 0.26379 | 0.26379 |  |  | 0.27304 | 0.27304 |  |  | 0.21824 | 0.21824 | 0.002514 | 0.002514 |  |  | 0.00238 | 0.00238 |  |  | 0.0032 | 0.0032 | 593 | 475 | Yes
2012-07-06 | 0.044192 | 0.044192 |  |  | 0.041138 | 0.041138 |  |  | 0.059489 | 0.059489 | 0.000447 | 0.000447 |  |  | 0.000425 | 0.000425 |  |  | 0.000555 | 0.000555 | 526 | 442 | Yes
2012-07-07 | 0.12401 | 0.12401 |  |  | 0.14712 | 0.14712 | 0.73883 | 0.73883 | 0.0077185 | 0.0077185 | 0.00115 | 0.00115 |  |  | 0.00107 | 0.00107 | 0.739 | 0.739 | 8.69e-05 | 8.69e-05 | 267 | 253 | Yes
2012-07-08 | 0.34893 | 0.34893 |  |  | 0.40575 | 0.40575 |  |  | 0.066647 | 0.066647 | 0.004408 | 0.004408 |  |  | 0.00517 | 0.00517 |  |  | 0.000615 | 0.000615 | 296 | 227 | Yes
2012-07-09 | 0.050508 | 0.050508 |  |  | 0.057337 | 0.057337 |  |  | 0.0166 | 0.0166 | 0.000366 | 0.000366 |  |  | 0.000388 | 0.000388 |  |  | 0.000261 | 0.000261 | 466 | 370 | Yes
2012-07-10 | 0.33103 | 0.33103 |  |  | 0.29267 | 0.29267 |  |  | 0.52267 | 0.52267 | 0.004486 | 0.004486 |  |  | 0.00436 | 0.00436 |  |  | 0.00513 | 0.00513 | 610 | 491 | Yes
2012-07-11 | 0.51381 | 0.51381 |  |  | 0.58773 | 0.58773 |  |  | 0.1467 | 0.1467 | 0.007655 | 0.007655 |  |  | 0.00748 | 0.00748 |  |  | 0.00853 | 0.00853 | 622 | 455 | Yes
2012-07-12 | 0.041494 | 0.041494 |  |  | 0.034257 | 0.034257 |  |  | 0.07762 | 0.07762 | 0.000602 | 0.000602 |  |  | 0.000483 | 0.000483 |  |  | 0.0012 | 0.0012 | 518 | 402 | Yes
2012-07-13 | 0.15282 | 0.15282 |  |  | 0.0093448 | 0.0093448 | 1.0653 | 1.0653 | 0.86558 | 0.86558 | 0.001215 | 0.001215 |  |  | 9.26e-05 | 9.26e-05 | 0.0172 | 0.0172 | 0.00678 | 0.00678 | 435 | 356 | Yes
2012-07-14 | 0.028928 | 0.028928 |  |  | 0.026525 | 0.026525 |  |  | 0.040952 | 0.040952 | 0.000179 | 0.000179 |  |  | 0.000144 | 0.000144 |  |  | 0.000354 | 0.000354 | 201 | 200 | Yes
2012-07-15 | 0.17101 | 0.17101 |  |  | 0.19811 | 0.19811 |  |  | 0.036401 | 0.036401 | 0.001774 | 0.001774 |  |  | 0.00206 | 0.00206 |  |  | 0.000374 | 0.000374 | 164 | 158 | Yes
2012-07-16 | 0.37292 | 0.37292 |  |  | 0.41998 | 0.41998 |  |  | 0.13931 | 0.13931 | 0.002581 | 0.002581 |  |  | 0.00273 | 0.00273 |  |  | 0.00183 | 0.00183 | 529 | 397 | Yes
2012-07-17 | 0.009927 | 0.009927 |  |  | 0.0029105 | 0.0029105 |  |  | 0.044888 | 0.044888 | 7.04e-05 | 7.04e-05 |  |  | 3.35e-05 | 3.35e-05 |  |  | 0.000254 | 0.000254 | 520 | 428 | Yes
2012-07-18 | 0.042484 | 0.042484 |  |  | 0.046868 | 0.046868 |  |  | 0.020736 | 0.020736 | 0.001708 | 0.001708 |  |  | 0.000291 | 0.000291 |  |  | 0.00877 | 0.00877 | 442 | 325 | Yes
2012-07-19 | 0.23311 | 0.23311 |  |  | 0.23586 | 0.23586 |  |  | 0.21987 | 0.21987 | 0.004156 | 0.004156 |  |  | 0.0025 | 0.0025 |  |  | 0.0124 | 0.0124 | 548 | 454 | Yes
2012-07-20 | 0.032498 | 0.032498 |  |  | 0.032775 | 0.032775 |  |  | 0.031182 | 0.031182 | 0.000225 | 0.000225 |  |  | 0.000247 | 0.000247 |  |  | 0.000114 | 0.000114 | 479 | 434 | Yes
2012-07-21 | 0.007503 | 0.007503 |  |  | 0.0030179 | 0.0030179 |  |  | 0.029852 | 0.029852 | 0.000122 | 0.000122 |  |  | 3.35e-05 | 3.35e-05 |  |  | 0.000561 | 0.000561 | 223 | 219 | Yes
2012-07-22 | 0.13728 | 0.13728 |  |  | 0.0081264 | 0.0081264 |  |  | 0.78075 | 0.78075 | 0.00234 | 0.00234 |  |  | 0.00119 | 0.00119 |  |  | 0.00807 | 0.00807 | 195 | 187 | Yes
2012-07-23 | 0.019725 | 0.019725 |  |  | 0.0088564 | 0.0088564 |  |  | 0.073891 | 0.073891 | 0.000256 | 0.000256 |  |  | 4.29e-05 | 4.29e-05 |  |  | 0.00132 | 0.00132 | 638 | 413 | Yes
2012-07-24 | 0.029372 | 0.029372 |  |  | 0.033528 | 0.033528 |  |  | 0.0087343 | 0.0087343 | 0.000324 | 0.000324 |  |  | 0.000349 | 0.000349 |  |  | 0.0002 | 0.0002 | 537 | 463 | Yes
2012-07-25 | 0.060787 | 0.060787 |  |  | 0.06947 | 0.06947 |  |  | 0.017662 | 0.017662 | 0.000364 | 0.000364 |  |  | 0.000409 | 0.000409 |  |  | 0.00014 | 0.00014 | 565 | 416 | Yes
2012-07-26 | 0.21448 | 0.21448 |  |  | 0.19905 | 0.19905 | 7.2577 | 7.2577 | 0.27765 | 0.27765 | 0.002212 | 0.002212 |  |  | 0.00239 | 0.00239 | 0.0206 | 0.0206 | 0.00127 | 0.00127 | 581 | 382 | Yes
2012-07-27 | 0.010006 | 0.010006 |  |  | 0.011178 | 0.011178 |  |  | 0.0041901 | 0.0041901 | 0.000101 | 0.000101 |  |  | 0.000115 | 0.000115 |  |  | 2.67e-05 | 2.67e-05 | 432 | 352 | Yes
2012-07-28 | 0.52129 | 0.52129 |  |  | 0.012891 | 0.012891 |  |  | 3.0542 | 3.0542 | 0.000947 | 0.000947 |  |  | 0.000152 | 0.000152 |  |  | 0.00491 | 0.00491 | 234 | 219 | Yes
2012-07-29 | 0.19544 | 0.19544 |  |  | 0.21679 | 0.21679 |  |  | 0.089488 | 0.089488 | 0.001802 | 0.001802 |  |  | 0.002 | 0.002 |  |  | 0.000802 | 0.000802 | 174 | 162 | Yes
2012-07-30 | 0.30503 | 0.30503 |  |  | 0.33455 | 0.33455 |  |  | 0.15865 | 0.15865 | 0.004772 | 0.004772 |  |  | 0.00539 | 0.00539 |  |  | 0.00168 | 0.00168 | 707 | 530 | Yes
2012-07-31 | 0.32341 | 0.32341 |  |  | 0.38834 | 0.38834 |  |  | 0.00066827 | 0.00066827 | 0.004754 | 0.004754 |  |  | 0.00571 | 0.00571 |  |  | 6.68e-06 | 6.68e-06 | 744 | 567 | Yes
2012-08-01 | 0.069139 | 0.069139 |  |  | 0.049435 | 0.049435 |  |  | 0.1674 | 0.1674 | 0.001797 | 0.001797 |  |  | 0.0018 | 0.0018 |  |  | 0.00178 | 0.00178 | 584 | 370 | Yes
2012-08-02 | 0.32521 | 0.32521 |  |  | 0.39031 | 0.39031 |  |  | 0.0016239 | 0.0016239 | 0.00142 | 0.00142 |  |  | 0.0017 | 0.0017 |  |  | 6.68e-06 | 6.68e-06 | 606 | 422 | Yes
2012-08-03 | 0.12525 | 0.12525 |  |  | 0.14755 | 0.14755 |  |  | 0.014435 | 0.014435 | 0.003728 | 0.003728 |  |  | 0.00318 | 0.00318 |  |  | 0.00646 | 0.00646 | 501 | 378 | Yes
2012-08-04 | 0.042509 | 0.042509 |  |  | 0.034756 | 0.034756 |  |  | 0.081202 | 0.081202 | 0.001358 | 0.001358 |  |  | 0.00148 | 0.00148 |  |  | 0.000762 | 0.000762 | 317 | 307 | Yes
2012-08-05 | 0.079394 | 0.079394 |  |  | 0.003513 | 0.003513 |  |  | 0.45744 | 0.45744 | 0.001692 | 0.001692 |  |  | 4.56e-05 | 4.56e-05 |  |  | 0.0099 | 0.0099 | 172 | 167 | Yes
2012-08-06 | 0.30353 | 0.30353 |  |  | 0.36189 | 0.36189 |  |  | 0.013506 | 0.013506 | 0.003331 | 0.003331 |  |  | 0.00398 | 0.00398 |  |  | 0.00012 | 0.00012 | 580 | 385 | Yes
2012-08-07 | 0.027541 | 0.027541 |  |  | 0.013204 | 0.013204 |  |  | 0.098998 | 0.098998 | 0.000368 | 0.000368 |  |  | 0.000239 | 0.000239 |  |  | 0.00101 | 0.00101 | 469 | 369 | Yes
2012-08-08 | 0.29267 | 0.29267 |  |  | 0.30924 | 0.30924 |  |  | 0.21075 | 0.21075 | 0.002388 | 0.002388 |  |  | 0.00247 | 0.00247 |  |  | 0.00196 | 0.00196 | 483 | 356 | Yes
2012-08-09 | 0.34088 | 0.34088 |  |  | 0.02368 | 0.02368 |  |  | 1.9213 | 1.9213 | 0.003356 | 0.003356 |  |  | 0.000259 | 0.000259 |  |  | 0.0188 | 0.0188 | 797 | 418 | Yes
2012-08-10 | 2.4208 | 2.4208 |  |  | 1.852 | 1.852 |  |  | 5.2584 | 5.2584 | 0.018987 | 0.018987 |  |  | 0.0141 | 0.0141 |  |  | 0.0432 | 0.0432 | 1355 | 772 | Yes
2012-08-11 | 0.50424 | 0.50424 |  |  | 0.47184 | 0.47184 |  |  | 0.66658 | 0.66658 | 0.005037 | 0.005037 |  |  | 0.00411 | 0.00411 |  |  | 0.00968 | 0.00968 | 421 | 397 | Yes
2012-08-12 | 0.17066 | 0.17066 |  |  | 0.20485 | 0.20485 |  |  | 0.00071505 | 0.00071505 | 0.002529 | 0.002529 |  |  | 0.00304 | 0.00304 |  |  | 1.34e-05 | 1.34e-05 | 386 | 258 | Yes
2012-08-13 | 0.17884 | 0.17884 |  |  | 0.17408 | 0.17408 |  |  | 0.20287 | 0.20287 | 0.001358 | 0.001358 |  |  | 0.00149 | 0.00149 |  |  | 0.000702 | 0.000702 | 681 | 384 | Yes
2012-08-14 | 0.11647 | 0.11647 |  |  | 0.12911 | 0.12911 |  |  | 0.053756 | 0.053756 | 0.001968 | 0.001968 |  |  | 0.00232 | 0.00232 |  |  | 0.000214 | 0.000214 | 512 | 425 | Yes
2012-08-15 | 0.11615 | 0.11615 |  |  | 0.1339 | 0.1339 |  |  | 0.02798 | 0.02798 | 0.001165 | 0.001165 |  |  | 0.00133 | 0.00133 |  |  | 0.000368 | 0.000368 | 522 | 399 | Yes
2012-08-16 | 0.055872 | 0.055872 |  |  | 0.0013137 | 0.0013137 |  |  | 0.32769 | 0.32769 | 0.001744 | 0.001744 |  |  | 5.37e-06 | 5.37e-06 |  |  | 0.0104 | 0.0104 | 462 | 328 | Yes
2012-08-17 | 2.5837 | 2.5837 |  |  | 2.4531 | 2.4531 |  |  | 3.2393 | 3.2393 | 0.019923 | 0.019923 |  |  | 0.0203 | 0.0203 |  |  | 0.018 | 0.018 | 1456 | 915 | Yes
2012-08-18 | 0.16425 | 0.16425 |  |  | 0.025461 | 0.025461 |  |  | 0.85575 | 0.85575 | 0.001535 | 0.001535 |  |  | 0.000396 | 0.000396 |  |  | 0.00721 | 0.00721 | 470 | 402 | Yes
2012-08-19 | 0.016213 | 0.016213 |  |  | 0.011555 | 0.011555 |  |  | 0.039441 | 0.039441 | 0.000132 | 0.000132 |  |  | 0.000123 | 0.000123 |  |  | 0.000174 | 0.000174 | 123 | 117 | Yes
2012-08-20 | 0.50069 | 0.50069 |  |  | 0.58366 | 0.58366 |  |  | 0.088472 | 0.088472 | 0.003649 | 0.003649 |  |  | 0.00412 | 0.00412 |  |  | 0.00128 | 0.00128 | 668 | 513 | Yes
2012-08-21 | 0.13139 | 0.13139 |  |  | 0.021784 | 0.021784 |  |  | 0.67747 | 0.67747 | 0.000919 | 0.000919 |  |  | 0.000193 | 0.000193 |  |  | 0.00454 | 0.00454 | 541 | 479 | Yes
2012-08-22 | 0.017883 | 0.017883 |  |  | 0.019417 | 0.019417 |  |  | 0.010278 | 0.010278 | 0.000144 | 0.000144 |  |  | 0.000157 | 0.000157 |  |  | 8.02e-05 | 8.02e-05 | 507 | 373 | Yes
2012-08-23 | 4.1051 | 4.1051 |  |  | 2.8449 | 2.8449 |  |  | 10.3889 | 10.3889 | 0.022588 | 0.022588 |  |  | 0.015 | 0.015 |  |  | 0.0603 | 0.0603 | 1659 | 1073 | Yes
2012-08-24 | 0.33978 | 0.33978 |  |  | 0.35589 | 0.35589 |  |  | 0.26024 | 0.26024 | 0.002696 | 0.002696 |  |  | 0.00246 | 0.00246 |  |  | 0.00386 | 0.00386 | 793 | 619 | Yes
2012-08-25 | 0.035788 | 0.035788 |  |  | 0.032743 | 0.032743 |  |  | 0.051022 | 0.051022 | 0.000188 | 0.000188 |  |  | 0.000193 | 0.000193 |  |  | 0.00016 | 0.00016 | 274 | 259 | Yes
2012-08-26 | 0.060243 | 0.060243 |  |  | 0.0042967 | 0.0042967 | 99.6735 | 99.6735 | 0.14515 | 0.14515 | 0.000582 | 0.000582 |  |  | 6.31e-05 | 6.31e-05 | 1.01 | 1.01 | 0.0012 | 0.0012 | 179 | 175 | Yes
2012-08-27 | 0.029667 | 0.029667 |  |  | 0.035391 | 0.035391 |  |  | 0.0012229 | 0.0012229 | 0.001217 | 0.001217 |  |  | 0.00146 | 0.00146 |  |  | 1.34e-05 | 1.34e-05 | 465 | 341 | Yes
2012-08-28 | 0.046983 | 0.046983 |  |  | 0.055604 | 0.055604 |  |  | 0.0041366 | 0.0041366 | 0.000267 | 0.000267 |  |  | 0.000309 | 0.000309 |  |  | 6.01e-05 | 6.01e-05 | 505 | 382 | Yes
2012-08-29 | 0.05075 | 0.05075 |  |  | 0.018102 | 0.018102 | 14.2612 | 14.2612 | 0.18571 | 0.18571 | 0.002751 | 0.002751 |  |  | 9.66e-05 | 9.66e-05 | 1.09 | 1.09 | 0.0139 | 0.0139 | 544 | 305 | Yes
2012-08-30 | 0.087381 | 0.087381 |  |  | 0.030784 | 0.030784 |  |  | 0.36941 | 0.36941 | 0.001136 | 0.001136 |  |  | 0.000185 | 0.000185 |  |  | 0.00587 | 0.00587 | 536 | 392 | Yes
2012-08-31 | 0.41496 | 0.41496 |  |  | 0.31417 | 0.31417 |  |  | 0.91775 | 0.91775 | 0.003913 | 0.003913 |  |  | 0.00267 | 0.00267 |  |  | 0.0101 | 0.0101 | 484 | 417 | Yes
2012-09-01 | 0.38663 | 0.38663 |  |  | 0.010316 | 0.010316 |  |  | 2.2615 | 2.2615 | 0.001742 | 0.001742 |  |  | 0.000166 | 0.000166 |  |  | 0.00959 | 0.00959 | 264 | 249 | Yes
2012-09-02 | 0.005274 | 0.005274 |  |  | 0.0011097 | 0.0011097 |  |  | 0.026022 | 0.026022 | 0.000149 | 0.000149 |  |  | 0.000123 | 0.000123 |  |  | 0.000274 | 0.000274 | 134 | 127 | Yes
2012-09-03 | 0.018655 | 0.018655 |  |  | 0.010821 | 0.010821 |  |  | 0.057705 | 0.057705 | 0.000189 | 0.000189 |  |  | 9.66e-05 | 9.66e-05 |  |  | 0.000648 | 0.000648 | 523 | 424 | Yes
2012-09-04 | 0.16904 | 0.16904 |  |  | 0.20295 | 0.20295 |  |  | 0.00046779 | 0.00046779 | 0.001041 | 0.001041 |  |  | 0.00125 | 0.00125 |  |  | 6.68e-06 | 6.68e-06 | 526 | 416 | Yes
2012-09-05 | 0.474 | 0.474 |  |  | 0.20448 | 0.20448 |  |  | 1.8172 | 1.8172 | 0.021282 | 0.021282 |  |  | 0.00965 | 0.00965 |  |  | 0.0793 | 0.0793 | 709 | 530 | Yes
2012-09-06 | 0.6131 | 0.6131 |  |  | 0.48802 | 0.48802 |  |  | 1.2372 | 1.2372 | 0.009501 | 0.009501 |  |  | 0.00806 | 0.00806 |  |  | 0.0167 | 0.0167 | 581 | 363 | Yes
2012-09-07 | 1.2808 | 1.2808 |  |  | 0.26897 | 0.26897 |  |  | 6.3226 | 6.3226 | 0.008566 | 0.008566 |  |  | 0.00489 | 0.00489 |  |  | 0.0269 | 0.0269 | 796 | 646 | Yes
2012-09-08 | 0.16019 | 0.16019 |  |  | 0.1551 | 0.1551 |  |  | 0.18586 | 0.18586 | 0.002001 | 0.002001 |  |  | 0.0023 | 0.0023 |  |  | 0.000501 | 0.000501 | 407 | 330 | Yes
2012-09-09 | 0.036895 | 0.036895 |  |  | 0.028253 | 0.028253 |  |  | 0.080005 | 0.080005 | 0.000832 | 0.000832 |  |  | 0.000899 | 0.000899 |  |  | 0.000501 | 0.000501 | 170 | 166 | Yes
2012-09-10 | 0.15432 | 0.15432 |  |  | 0.0098547 | 0.0098547 |  |  | 0.87409 | 0.87409 | 0.001616 | 0.001616 |  |  | 3.89e-05 | 3.89e-05 |  |  | 0.00948 | 0.00948 | 575 | 405 | Yes
2012-09-11 | 0.18272 | 0.18272 |  |  | 0.20481 | 0.20481 |  |  | 0.073062 | 0.073062 | 0.00199 | 0.00199 |  |  | 0.00237 | 0.00237 |  |  | 8.02e-05 | 8.02e-05 | 577 | 484 | Yes
2012-09-12 | 0.011175 | 0.011175 |  |  | 0.0050495 | 0.0050495 |  |  | 0.0417 | 0.0417 | 0.000121 | 0.000121 |  |  | 7.25e-05 | 7.25e-05 |  |  | 0.000361 | 0.000361 | 473 | 396 | Yes
2012-09-13 | 0.11518 | 0.11518 |  |  | 0.13259 | 0.13259 |  |  | 0.028655 | 0.028655 | 0.001031 | 0.001031 |  |  | 0.00121 | 0.00121 |  |  | 0.00016 | 0.00016 | 768 | 576 | Yes
2012-09-14 | 0.028907 | 0.028907 |  |  | 0.031722 | 0.031722 |  |  | 0.014943 | 0.014943 | 0.000414 | 0.000414 |  |  | 0.000266 | 0.000266 |  |  | 0.00116 | 0.00116 | 434 | 383 | Yes
2012-09-15 | 0.01403 | 0.01403 |  |  | 0.011737 | 0.011737 |  |  | 0.025474 | 0.025474 | 0.000271 | 0.000271 |  |  | 0.00028 | 0.00028 |  |  | 0.000227 | 0.000227 | 226 | 213 | Yes
2012-09-16 | 1.6994 | 1.6994 |  |  | 2.0376 | 2.0376 |  |  | 0.018645 | 0.018645 | 0.009019 | 0.009019 |  |  | 0.0108 | 0.0108 |  |  | 0.00012 | 0.00012 | 474 | 216 | Yes
2012-09-17 | 0.50245 | 0.50245 |  |  | 0.29495 | 0.29495 |  |  | 1.5368 | 1.5368 | 0.007088 | 0.007088 |  |  | 0.00222 | 0.00222 |  |  | 0.0313 | 0.0313 | 630 | 503 | Yes
2012-09-18 | 0.093142 | 0.093142 |  |  | 0.088543 | 0.088543 |  |  | 0.11623 | 0.11623 | 0.003503 | 0.003503 |  |  | 0.00407 | 0.00407 |  |  | 0.000695 | 0.000695 | 579 | 480 | Yes
2012-09-19 | 0.096193 | 0.096193 |  |  | 0.024176 | 0.024176 |  |  | 0.45503 | 0.45503 | 0.000546 | 0.000546 |  |  | 0.000274 | 0.000274 |  |  | 0.0019 | 0.0019 | 534 | 431 | Yes
2012-09-20 | 0.012408 | 0.012408 |  |  | 0.014269 | 0.014269 |  |  | 0.0031609 | 0.0031609 | 0.002181 | 0.002181 |  |  | 0.00262 | 0.00262 |  |  | 2e-05 | 2e-05 | 454 | 342 | Yes
2012-09-21 | 0.13857 | 0.13857 |  |  | 0.16471 | 0.16471 |  |  | 0.0086608 | 0.0086608 | 0.009367 | 0.009367 |  |  | 0.0112 | 0.0112 |  |  | 6.68e-05 | 6.68e-05 | 454 | 315 | Yes
2012-09-22 | 0.088733 | 0.088733 |  |  | 0.096803 | 0.096803 |  |  | 0.048717 | 0.048717 | 0.001136 | 0.001136 |  |  | 0.00123 | 0.00123 |  |  | 0.000648 | 0.000648 | 292 | 280 | Yes
2012-09-23 | 0.091287 | 0.091287 |  |  | 0.10199 | 0.10199 |  |  | 0.038165 | 0.038165 | 0.002816 | 0.002816 |  |  | 0.00267 | 0.00267 |  |  | 0.00354 | 0.00354 | 251 | 233 | Yes
2012-09-24 | 0.055748 | 0.055748 |  |  | 0.066963 | 0.066963 |  |  | 0 | 0 | 0.001198 | 0.001198 |  |  | 0.00144 | 0.00144 |  |  | 0 | 0 | 488 | 369 | Yes
2012-09-25 | 0.071219 | 0.071219 |  |  | 0.083707 | 0.083707 |  |  | 0.009162 | 0.009162 | 0.00257 | 0.00257 |  |  | 0.00303 | 0.00303 |  |  | 0.000267 | 0.000267 | 618 | 471 | Yes
2012-09-26 | 0.076858 | 0.076858 |  |  | 0.091662 | 0.091662 |  |  | 0.0032812 | 0.0032812 | 0.000213 | 0.000213 |  |  | 0.000247 | 0.000247 |  |  | 4.68e-05 | 4.68e-05 | 517 | 369 | Yes
2012-09-27 | 0.021555 | 0.021555 |  |  | 0.018272 | 0.018272 |  |  | 0.037944 | 0.037944 | 0.000351 | 0.000351 |  |  | 0.000342 | 0.000342 |  |  | 0.000394 | 0.000394 | 449 | 359 | Yes
2012-09-28 | 0.23259 | 0.23259 |  |  | 0.06374 | 0.06374 |  |  | 1.0739 | 1.0739 | 0.004632 | 0.004632 |  |  | 0.00135 | 0.00135 |  |  | 0.021 | 0.021 | 599 | 464 | Yes
2012-09-29 | 0.054406 | 0.054406 |  |  | 0.027993 | 0.027993 |  |  | 0.18605 | 0.18605 | 0.000442 | 0.000442 |  |  | 0.000192 | 0.000192 |  |  | 0.00169 | 0.00169 | 280 | 264 | Yes
2012-09-30 | 0.028268 | 0.028268 |  |  | 0.022356 | 0.022356 |  |  | 0.057765 | 0.057765 | 0.000145 | 0.000145 |  |  | 9.66e-05 | 9.66e-05 |  |  | 0.000388 | 0.000388 | 125 | 119 | Yes
2012-10-01 | 0.007913 | 0.007913 |  |  | 0.0013003 | 0.0013003 |  |  | 0.040858 | 0.040858 | 0.000101 | 0.000101 |  |  | 2.95e-05 | 2.95e-05 |  |  | 0.000454 | 0.000454 | 164 | 162 | Yes
2012-10-02 | 0.017663 | 0.017663 |  |  | 0.018766 | 0.018766 |  |  | 0.012203 | 0.012203 | 0.000103 | 0.000103 |  |  | 0.000111 | 0.000111 |  |  | 6.01e-05 | 6.01e-05 | 467 | 313 | Yes
2012-10-03 | 0.19631 | 0.19631 |  |  | 0.17893 | 0.17893 |  |  | 0.28325 | 0.28325 | 0.002811 | 0.002811 |  |  | 0.00176 | 0.00176 |  |  | 0.00805 | 0.00805 | 666 | 461 | Yes
2012-10-04 | 0.086033 | 0.086033 |  |  | 0.10141 | 0.10141 |  |  | 0.0096431 | 0.0096431 | 0.000436 | 0.000436 |  |  | 0.000502 | 0.000502 |  |  | 0.000107 | 0.000107 | 500 | 394 | Yes
2012-10-05 | 0.17329 | 0.17329 |  |  | 0.20168 | 0.20168 |  |  | 0.032217 | 0.032217 | 0.002677 | 0.002677 |  |  | 0.00317 | 0.00317 |  |  | 0.000207 | 0.000207 | 528 | 404 | Yes
2012-10-06 | 0.27984 | 0.27984 |  |  | 0.31824 | 0.31824 |  |  | 0.089101 | 0.089101 | 0.003857 | 0.003857 |  |  | 0.00441 | 0.00441 |  |  | 0.00112 | 0.00112 | 317 | 302 | Yes
2012-10-07 | 0.011023 | 0.011023 |  |  | 0.0044657 | 0.0044657 |  |  | 0.043698 | 0.043698 | 7.37e-05 | 7.37e-05 |  |  | 2.82e-05 | 2.82e-05 |  |  | 0.000301 | 0.000301 | 138 | 138 | Yes
2012-10-08 | 0.047288 | 0.047288 |  |  | 0.032583 | 0.032583 |  |  | 0.12061 | 0.12061 | 0.000545 | 0.000545 |  |  | 0.000184 | 0.000184 |  |  | 0.00235 | 0.00235 | 521 | 392 | Yes
2012-10-09 | 0.031034 | 0.031034 |  |  | 0.015233 | 0.015233 |  |  | 0.10978 | 0.10978 | 0.000233 | 0.000233 |  |  | 0.000126 | 0.000126 |  |  | 0.000769 | 0.000769 | 623 | 414 | Yes
2012-10-10 | 0.019579 | 0.019579 |  |  | 0.023327 | 0.023327 |  |  | 0.00094894 | 0.00094894 | 0.000183 | 0.000183 |  |  | 0.000217 | 0.000217 |  |  | 1.34e-05 | 1.34e-05 | 557 | 385 | Yes
2012-10-11 | 0.44396 | 0.44396 |  |  | 0.087057 | 0.087057 |  |  | 2.2222 | 2.2222 | 0.01236 | 0.01236 |  |  | 0.00966 | 0.00966 |  |  | 0.0258 | 0.0258 | 670 | 436 | Yes
2012-10-12 | 3.9155 | 3.9155 |  |  | 1.5796 | 1.5796 |  |  | 15.5561 | 15.5561 | 0.034941 | 0.034941 |  |  | 0.0203 | 0.0203 |  |  | 0.108 | 0.108 | 1151 | 830 | Yes
2012-10-13 | 0.026286 | 0.026286 |  |  | 0.029647 | 0.029647 |  |  | 0.0095964 | 0.0095964 | 0.000174 | 0.000174 |  |  | 0.00017 | 0.00017 |  |  | 0.000194 | 0.000194 | 322 | 286 | Yes
2012-10-14 | 0.29134 | 0.29134 |  |  | 0.15332 | 0.15332 |  |  | 0.97922 | 0.97922 | 0.004185 | 0.004185 |  |  | 0.00284 | 0.00284 |  |  | 0.0109 | 0.0109 | 180 | 167 | Yes
2012-10-15 | 0.12783 | 0.12783 |  |  | 0.047624 | 0.047624 |  |  | 0.52751 | 0.52751 | 0.001522 | 0.001522 |  |  | 0.00071 | 0.00071 |  |  | 0.00557 | 0.00557 | 591 | 487 | Yes
2012-10-16 | 0.11294 | 0.11294 |  |  | 0.10142 | 0.10142 |  |  | 0.17052 | 0.17052 | 0.002767 | 0.002767 |  |  | 0.000997 | 0.000997 |  |  | 0.0116 | 0.0116 | 510 | 453 | Yes
2012-10-17 | 0.30654 | 0.30654 |  |  | 0.3396 | 0.3396 |  |  | 0.1425 | 0.1425 | 0.003161 | 0.003161 |  |  | 0.00375 | 0.00375 |  |  | 0.000234 | 0.000234 | 604 | 505 | Yes
2012-10-18 | 0.021696 | 0.021696 |  |  | 0.01163 | 0.01163 |  |  | 0.071866 | 0.071866 | 0.000791 | 0.000791 |  |  | 0.000165 | 0.000165 |  |  | 0.00391 | 0.00391 | 494 | 406 | Yes
2012-10-19 | 0.28411 | 0.28411 |  |  | 0.23269 | 0.23269 | 32.8247 | 32.8247 | 0.47692 | 0.47692 | 0.004422 | 0.004422 |  |  | 0.00224 | 0.00224 | 0.993 | 0.993 | 0.0134 | 0.0134 | 539 | 470 | Yes
2012-10-20 | 0.06163 | 0.06163 |  |  | 0.017354 | 0.017354 |  |  | 0.28225 | 0.28225 | 0.0006 | 0.0006 |  |  | 0.000242 | 0.000242 |  |  | 0.00239 | 0.00239 | 302 | 293 | Yes
2012-10-21 | 0.27671 | 0.27671 |  |  | 0.031287 | 0.031287 | 81.5292 | 81.5292 | 1.3409 | 1.3409 | 0.002365 | 0.002365 |  |  | 0.000133 | 0.000133 | 0.962 | 0.962 | 0.0116 | 0.0116 | 161 | 158 | Yes
2012-10-22 | 0.36939 | 0.36939 |  |  | 0.39761 | 0.39761 |  |  | 0.22958 | 0.22958 | 0.006126 | 0.006126 |  |  | 0.00687 | 0.00687 |  |  | 0.00244 | 0.00244 | 729 | 600 | Yes
2012-10-23 | 0.10583 | 0.10583 |  |  | 0.1155 | 0.1155 |  |  | 0.057892 | 0.057892 | 0.001781 | 0.001781 |  |  | 0.00209 | 0.00209 |  |  | 0.000234 | 0.000234 | 503 | 434 | Yes
2012-10-24 | 0.078405 | 0.078405 |  |  | 0.093243 | 0.093243 |  |  | 0.0046645 | 0.0046645 | 0.000449 | 0.000449 |  |  | 0.000537 | 0.000537 |  |  | 1.34e-05 | 1.34e-05 | 514 | 423 | Yes
2012-10-25 | 0.040925 | 0.040925 |  |  | 0.0018223 | 0.0018223 |  |  | 0.23574 | 0.23574 | 0.00048 | 0.00048 |  |  | 9.39e-06 | 9.39e-06 |  |  | 0.00283 | 0.00283 | 499 | 422 | Yes
2012-10-26 | 0.078462 | 0.078462 |  |  | 0.080897 | 0.080897 |  |  | 0.066486 | 0.066486 | 0.000285 | 0.000285 |  |  | 0.00017 | 0.00017 |  |  | 0.000855 | 0.000855 | 466 | 415 | Yes
2012-10-27 | 0.011882 | 0.011882 |  |  | 0.0064034 | 0.0064034 |  |  | 0.039187 | 0.039187 | 0.000121 | 0.000121 |  |  | 4.96e-05 | 4.96e-05 |  |  | 0.000474 | 0.000474 | 199 | 170 | Yes
2012-10-28 | 0.047136 | 0.047136 |  |  | 0.030737 | 0.030737 |  |  | 0.1289 | 0.1289 | 0.000394 | 0.000394 |  |  | 0.000319 | 0.000319 |  |  | 0.000769 | 0.000769 | 115 | 109 | Yes
2012-10-29 | 0.077353 | 0.077353 |  |  | 0.02141 | 0.02141 |  |  | 0.35611 | 0.35611 | 0.001147 | 0.001147 |  |  | 0.000235 | 0.000235 |  |  | 0.00569 | 0.00569 | 542 | 453 | Yes
2012-10-30 | 0.083633 | 0.083633 |  |  | 0.029988 | 0.029988 |  |  | 0.35096 | 0.35096 | 0.000685 | 0.000685 |  |  | 0.000271 | 0.000271 |  |  | 0.00275 | 0.00275 | 517 | 481 | Yes
2012-10-31 | 0.60877 | 0.60877 |  |  | 0.7308 | 0.7308 |  |  | 0.0022253 | 0.0022253 | 0.003232 | 0.003232 |  |  | 0.00388 | 0.00388 |  |  | 6.68e-06 | 6.68e-06 | 563 | 504 | Yes
2012-11-01 | 0.48546 | 0.48546 |  |  | 0.0033439 | 0.0033439 |  |  | 2.8874 | 2.8874 | 0.005163 | 0.005163 |  |  | 0.000129 | 0.000129 |  |  | 0.0302 | 0.0302 | 595 | 515 | Yes
2012-11-02 | 0.073808 | 0.073808 |  |  | 0.083642 | 0.083642 |  |  | 0.02498 | 0.02498 | 0.000333 | 0.000333 |  |  | 0.000374 | 0.000374 |  |  | 0.000127 | 0.000127 | 464 | 408 | Yes
2012-11-03 | 0.29835 | 0.29835 |  |  | 0.17722 | 0.17722 |  |  | 0.90217 | 0.90217 | 0.00307 | 0.00307 |  |  | 0.00179 | 0.00179 |  |  | 0.00946 | 0.00946 | 357 | 325 | Yes
2012-11-04 | 0.098412 | 0.098412 |  |  | 0.011972 | 0.011972 |  |  | 0.52908 | 0.52908 | 0.001227 | 0.001227 |  |  | 5.77e-05 | 5.77e-05 |  |  | 0.00705 | 0.00705 | 140 | 134 | Yes
2012-11-05 | 0.33151 | 0.33151 |  |  | 0.37302 | 0.37302 |  |  | 0.12543 | 0.12543 | 0.003978 | 0.003978 |  |  | 0.00449 | 0.00449 |  |  | 0.00145 | 0.00145 | 668 | 569 | Yes
2012-11-06 | 0.006552 | 0.006552 |  |  | 0.0052682 | 0.0052682 |  |  | 0.012958 | 0.012958 | 4.36e-05 | 4.36e-05 |  |  | 3.76e-05 | 3.76e-05 |  |  | 7.35e-05 | 7.35e-05 | 457 | 398 | Yes
2012-11-07 | 0.083122 | 0.083122 |  |  | 0.032369 | 0.032369 |  |  | 0.33604 | 0.33604 | 0.000534 | 0.000534 |  |  | 0.000217 | 0.000217 |  |  | 0.00211 | 0.00211 | 541 | 465 | Yes
2012-11-08 | 2.6097 | 2.6097 |  |  | 2.438 | 2.438 |  |  | 3.47 | 3.47 | 0.018657 | 0.018657 |  |  | 0.0178 | 0.0178 |  |  | 0.0228 | 0.0228 | 1183 | 884 | Yes
2012-11-09 | 0.18391 | 0.18391 |  |  | 0.049895 | 0.049895 |  |  | 0.8517 | 0.8517 | 0.003027 | 0.003027 |  |  | 0.00144 | 0.00144 |  |  | 0.0109 | 0.0109 | 667 | 478 | Yes
2012-11-10 | 0.012296 | 0.012296 |  |  | 0.011397 | 0.011397 |  |  | 0.0168 | 0.0168 | 0.000146 | 0.000146 |  |  | 0.000146 | 0.000146 |  |  | 0.000147 | 0.000147 | 271 | 241 | Yes
2012-11-11 | 0.021162 | 0.021162 |  |  | 0.0090885 | 0.0090885 |  |  | 0.081329 | 0.081329 | 0.000486 | 0.000486 |  |  | 0.000148 | 0.000148 |  |  | 0.00217 | 0.00217 | 103 | 101 | Yes
2012-11-12 | 0.12096 | 0.12096 |  |  | 0.04857 | 0.04857 |  |  | 0.4817 | 0.4817 | 0.001248 | 0.001248 |  |  | 0.000109 | 0.000109 |  |  | 0.00692 | 0.00692 | 576 | 515 | Yes
2012-11-13 | 0.32558 | 0.32558 |  |  | 0.38934 | 0.38934 | 4.1237 | 4.1237 | 0.00068832 | 0.00068832 | 0.008896 | 0.008896 |  |  | 0.0107 | 0.0107 | 0.0344 | 0.0344 | 6.68e-06 | 6.68e-06 | 659 | 554 | Yes
2012-11-14 | 0.15694 | 0.15694 |  |  | 0.16767 | 0.16767 |  |  | 0.10378 | 0.10378 | 0.001857 | 0.001857 |  |  | 0.00202 | 0.00202 |  |  | 0.00106 | 0.00106 | 618 | 501 | Yes
2012-11-15 | 0.01077 | 0.01077 |  |  | 0.0051756 | 0.0051756 |  |  | 0.038653 | 0.038653 | 6.14e-05 | 6.14e-05 |  |  | 4.43e-05 | 4.43e-05 |  |  | 0.000147 | 0.000147 | 527 | 435 | Yes
2012-11-16 | 0.32918 | 0.32918 |  |  | 0.25666 | 0.25666 |  |  | 0.69095 | 0.69095 | 0.003247 | 0.003247 |  |  | 0.0019 | 0.0019 |  |  | 0.00994 | 0.00994 | 574 | 454 | Yes
2012-11-17 | 0.11133 | 0.11133 |  |  | 0.099351 | 0.099351 |  |  | 0.17119 | 0.17119 | 0.00179 | 0.00179 |  |  | 0.00193 | 0.00193 |  |  | 0.00109 | 0.00109 | 311 | 273 | Yes
2012-11-18 | 0.58247 | 0.58247 |  |  | 0.4225 | 0.4225 |  |  | 1.3803 | 1.3803 | 0.019792 | 0.019792 |  |  | 0.0106 | 0.0106 |  |  | 0.0655 | 0.0655 | 377 | 260 | Yes
2012-11-19 | 0.13634 | 0.13634 |  |  | 0.15587 | 0.15587 |  |  | 0.039354 | 0.039354 | 0.001862 | 0.001862 |  |  | 0.00197 | 0.00197 |  |  | 0.00132 | 0.00132 | 517 | 442 | Yes
2012-11-20 | 0.12607 | 0.12607 |  |  | 0.038246 | 0.038246 |  |  | 0.56371 | 0.56371 | 0.00194 | 0.00194 |  |  | 0.000244 | 0.000244 |  |  | 0.0104 | 0.0104 | 567 | 497 | Yes
2012-11-21 | 0.13603 | 0.13603 |  |  | 0.15945 | 0.15945 |  |  | 0.019667 | 0.019667 | 0.002769 | 0.002769 |  |  | 0.003 | 0.003 |  |  | 0.00162 | 0.00162 | 471 | 367 | Yes
2012-11-22 | 0.009431 | 0.009431 |  |  | 0.0075198 | 0.0075198 |  |  | 0.018966 | 0.018966 | 0.000214 | 0.000214 |  |  | 8.72e-05 | 8.72e-05 |  |  | 0.000849 | 0.000849 | 441 | 381 | Yes
2012-11-23 | 0.002984 | 0.002984 |  |  | 3.0863e-05 | 3.0863e-05 |  |  | 0.017696 | 0.017696 | 2.9e-05 | 2.9e-05 |  |  | 1.34e-06 | 1.34e-06 |  |  | 0.000167 | 0.000167 | 463 | 396 | Yes
2012-11-24 | 0.15675 | 0.15675 |  |  | 0.1811 | 0.1811 |  |  | 0.035786 | 0.035786 | 0.001739 | 0.001739 |  |  | 0.00203 | 0.00203 |  |  | 0.000301 | 0.000301 | 279 | 236 | Yes
2012-11-25 | 0.44293 | 0.44293 |  |  | 0.45956 | 0.45956 |  |  | 0.36095 | 0.36095 | 0.00511 | 0.00511 |  |  | 0.00553 | 0.00553 |  |  | 0.00301 | 0.00301 | 253 | 180 | Yes
2012-11-26 | 0.75077 | 0.75077 |  |  | 0.45207 | 0.45207 |  |  | 2.2398 | 2.2398 | 0.008815 | 0.008815 |  |  | 0.00478 | 0.00478 |  |  | 0.0289 | 0.0289 | 813 | 683 | Yes
2012-11-27 | 1.7193 | 1.7193 |  |  | 0.091693 | 0.091693 |  |  | 9.8283 | 9.8283 | 0.007889 | 0.007889 |  |  | 0.000827 | 0.000827 |  |  | 0.0431 | 0.0431 | 1190 | 593 | Yes
2012-11-28 | 0.26986 | 0.26986 |  |  | 0.011923 | 0.011923 |  |  | 1.5549 | 1.5549 | 0.00107 | 0.00107 |  |  | 0.000215 | 0.000215 |  |  | 0.00533 | 0.00533 | 651 | 534 | Yes
2012-11-29 | 0.033089 | 0.033089 |  |  | 0.013303 | 0.013303 |  |  | 0.13169 | 0.13169 | 0.000641 | 0.000641 |  |  | 0.000126 | 0.000126 |  |  | 0.00321 | 0.00321 | 503 | 437 | Yes
2012-11-30 | 2.0874 | 2.0874 |  |  | 0.71981 | 0.71981 | 0.10309 | 0.10309 | 8.9021 | 8.9021 | 0.014211 | 0.014211 |  |  | 0.0105 | 0.0105 | 0.00344 | 0.00344 | 0.0329 | 0.0329 | 1111 | 673 | Yes
2012-12-01 | 0.31298 | 0.31298 |  |  | 0.16862 | 0.16862 |  |  | 1.0325 | 1.0325 | 0.003857 | 0.003857 |  |  | 0.0022 | 0.0022 |  |  | 0.0121 | 0.0121 | 672 | 462 | Yes
2012-12-02 | 0.049665 | 0.049665 |  |  | 0.022207 | 0.022207 |  |  | 0.18651 | 0.18651 | 0.000394 | 0.000394 |  |  | 0.000219 | 0.000219 |  |  | 0.00127 | 0.00127 | 149 | 148 | Yes
2012-12-03 | 0.43096 | 0.43096 |  |  | 0.47947 | 0.47947 |  |  | 0.19022 | 0.19022 | 0.003369 | 0.003369 |  |  | 0.00393 | 0.00393 |  |  | 0.000595 | 0.000595 | 600 | 478 | Yes
2012-12-04 | 0.24436 | 0.24436 |  |  | 0.033502 | 0.033502 |  |  | 1.295 | 1.295 | 0.003407 | 0.003407 |  |  | 0.00205 | 0.00205 |  |  | 0.0102 | 0.0102 | 600 | 508 | Yes
2012-12-05 | 0.47841 | 0.47841 |  |  | 0.26907 | 0.26907 |  |  | 1.5219 | 1.5219 | 0.007103 | 0.007103 |  |  | 0.00505 | 0.00505 |  |  | 0.0173 | 0.0173 | 811 | 702 | Yes
2012-12-06 | 0.023028 | 0.023028 |  |  | 0.0013258 | 0.0013258 |  |  | 0.13115 | 0.13115 | 0.001088 | 0.001088 |  |  | 0.000553 | 0.000553 |  |  | 0.00376 | 0.00376 | 512 | 436 | Yes
2012-12-07 | 0.12725 | 0.12725 |  |  | 0.15117 | 0.15117 |  |  | 0.0084002 | 0.0084002 | 0.000343 | 0.000343 |  |  | 0.000407 | 0.000407 |  |  | 2.67e-05 | 2.67e-05 | 437 | 388 | Yes
2012-12-08 | 0.12079 | 0.12079 |  |  | 0.10636 | 0.10636 |  |  | 0.1929 | 0.1929 | 0.002119 | 0.002119 |  |  | 0.002 | 0.002 |  |  | 0.00273 | 0.00273 | 263 | 255 | Yes
2012-12-09 | 0.10596 | 0.10596 |  |  | 0.10026 | 0.10026 |  |  | 0.13456 | 0.13456 | 0.001267 | 0.001267 |  |  | 0.000939 | 0.000939 |  |  | 0.0029 | 0.0029 | 234 | 203 | Yes
2012-12-10 | 0.098235 | 0.098235 |  |  | 0.044808 | 0.044808 |  |  | 0.3645 | 0.3645 | 0.001546 | 0.001546 |  |  | 0.00135 | 0.00135 |  |  | 0.00252 | 0.00252 | 492 | 413 | Yes
2012-12-11 | 0.18333 | 0.18333 |  |  | 0.0075695 | 0.0075695 |  |  | 1.059 | 1.059 | 0.001763 | 0.001763 |  |  | 0.000298 | 0.000298 |  |  | 0.00906 | 0.00906 | 537 | 461 | Yes
2012-12-12 | 0.043606 | 0.043606 |  |  | 0.048321 | 0.048321 |  |  | 0.020209 | 0.020209 | 0.000437 | 0.000437 |  |  | 0.000423 | 0.000423 |  |  | 0.000508 | 0.000508 | 548 | 453 | Yes
2012-12-13 | 0.20868 | 0.20868 |  |  | 0.045256 | 0.045256 |  |  | 1.023 | 1.023 | 0.001488 | 0.001488 |  |  | 0.000274 | 0.000274 |  |  | 0.00754 | 0.00754 | 541 | 428 | Yes
2012-12-14 | 0.043643 | 0.043643 |  |  | 0.047814 | 0.047814 | 0.34021 | 0.34021 | 0.022294 | 0.022294 | 0.001574 | 0.001574 |  |  | 0.00184 | 0.00184 | 0.00344 | 0.00344 | 0.000247 | 0.000247 | 489 | 417 | Yes
2012-12-15 | 0.57522 | 0.57522 |  |  | 0.32324 | 0.32324 |  |  | 1.8313 | 1.8313 | 0.003134 | 0.003134 |  |  | 0.00129 | 0.00129 |  |  | 0.0123 | 0.0123 | 275 | 250 | Yes
2012-12-16 | 0.039502 | 0.039502 |  |  | 0.045068 | 0.045068 |  |  | 0.011862 | 0.011862 | 0.000175 | 0.000175 |  |  | 0.000204 | 0.000204 |  |  | 3.34e-05 | 3.34e-05 | 188 | 182 | Yes
2012-12-17 | 0.34278 | 0.34278 |  |  | 0.14949 | 0.14949 | 2.0069 | 2.0069 | 1.3021 | 1.3021 | 0.010601 | 0.010601 |  |  | 0.00746 | 0.00746 | 1 | 1 | 0.0243 | 0.0243 | 553 | 467 | Yes
2012-12-18 | 0.070657 | 0.034144 |  |  | 0.067139 | 0.02328 |  |  | 0.088312 | 0.088312 | 0.002653 | 0.002493 |  |  | 0.00316 | 0.00297 |  |  | 0.00012 | 0.00012 | 527 | 434 | Yes
2012-12-19 | 0.56298 | 0.56298 |  |  | 0.65575 | 0.65575 |  |  | 0.10209 | 0.10209 | 0.006966 | 0.006966 |  |  | 0.00791 | 0.00791 |  |  | 0.00226 | 0.00226 | 1111 | 661 | Yes
2012-12-20 | 0.18781 | 0.18781 |  |  | 0.1782 | 0.1782 |  |  | 0.23607 | 0.23607 | 0.002204 | 0.002204 |  |  | 0.0022 | 0.0022 |  |  | 0.00223 | 0.00223 | 655 | 584 | Yes
2012-12-21 | 0.11091 | 0.11091 |  |  | 0.11694 | 0.11694 |  |  | 0.081108 | 0.081108 | 0.00374 | 0.00374 |  |  | 0.00382 | 0.00382 |  |  | 0.00337 | 0.00337 | 445 | 373 | Yes
2012-12-22 | 0.088387 | 0.088387 |  |  | 0.03332 | 0.03332 |  |  | 0.3628 | 0.3628 | 0.000286 | 0.000286 |  |  | 0.000184 | 0.000184 |  |  | 0.000795 | 0.000795 | 213 | 206 | Yes
2012-12-23 | 0.27087 | 0.27087 |  |  | 0.054995 | 0.054995 |  |  | 1.3465 | 1.3465 | 0.002814 | 0.002814 |  |  | 0.000593 | 0.000593 |  |  | 0.0139 | 0.0139 | 285 | 263 | Yes
2012-12-24 | 1.3886 | 1.3886 |  |  | 0.57809 | 0.57809 |  |  | 5.4276 | 5.4276 | 0.012869 | 0.012869 |  |  | 0.00768 | 0.00768 |  |  | 0.0387 | 0.0387 | 932 | 639 | Yes
2012-12-25 | 0.64976 | 0.64976 |  |  | 0.20688 | 0.20688 |  |  | 2.8566 | 2.8566 | 0.005316 | 0.005316 |  |  | 0.00154 | 0.00154 |  |  | 0.0242 | 0.0242 | 395 | 331 | Yes
2012-12-26 | 0.067237 | 0.067237 |  |  | 0.07298 | 0.07298 |  |  | 0.038766 | 0.038766 | 0.000988 | 0.000988 |  |  | 0.00102 | 0.00102 |  |  | 0.000815 | 0.000815 | 210 | 207 | Yes
2012-12-27 | 0.041538 | 0.041538 |  |  | 0.0045087 | 0.0045087 |  |  | 0.22603 | 0.22603 | 0.000514 | 0.000514 |  |  | 1.34e-05 | 1.34e-05 |  |  | 0.00301 | 0.00301 | 272 | 262 | Yes
2012-12-28 | 0.13744 | 0.13744 |  |  | 0.11116 | 0.11116 |  |  | 0.26858 | 0.26858 | 0.003294 | 0.003294 |  |  | 0.00348 | 0.00348 |  |  | 0.00239 | 0.00239 | 391 | 360 | Yes
2012-12-29 | 0.064002 | 0.064002 |  |  | 0.074124 | 0.074124 | 1.1409 | 1.1409 | 0.011501 | 0.011501 | 0.000696 | 0.000696 |  |  | 0.000813 | 0.000813 | 0.0103 | 0.0103 | 9.36e-05 | 9.36e-05 | 149 | 143 | Yes
2012-12-30 | 0.006785 | 0.006785 |  |  | 0.0048334 | 0.0048334 |  |  | 0.01652 | 0.01652 | 4.69e-05 | 4.69e-05 |  |  | 4.43e-05 | 4.43e-05 |  |  | 6.01e-05 | 6.01e-05 | 80 | 80 | Yes
2012-12-31 | 0.26418 | 0.26418 |  |  | 0.31482 | 0.31482 |  |  | 0.012497 | 0.012497 | 0.002717 | 0.002717 |  |  | 0.00297 | 0.00297 |  |  | 0.00144 | 0.00144 | 368 | 337 | Yes
2013-01-01 | 0.10554 | 0.10554 |  |  | 0.01483 | 0.01483 |  |  | 0.5575 | 0.5575 | 0.001564 | 0.001564 |  |  | 0.00013 | 0.00013 |  |  | 0.00871 | 0.00871 | 178 | 176 | Yes
2013-01-02 | 0.3631 | 0.3631 |  |  | 0.32142 | 0.32142 |  |  | 0.57141 | 0.57141 | 0.004441 | 0.004441 |  |  | 0.00459 | 0.00459 |  |  | 0.00369 | 0.00369 | 362 | 320 | Yes
2013-01-03 | 0.2491 | 0.2491 |  |  | 0.10718 | 0.10718 |  |  | 0.95639 | 0.95639 | 0.004554 | 0.004554 |  |  | 0.00202 | 0.00202 |  |  | 0.0172 | 0.0172 | 463 | 392 | Yes
2013-01-04 | 0.46897 | 0.46897 |  |  | 0.4129 | 0.4129 | 0.54639 | 0.54639 | 0.74808 | 0.74808 | 0.004031 | 0.004031 |  |  | 0.00402 | 0.00402 | 0.00344 | 0.00344 | 0.0041 | 0.0041 | 531 | 464 | Yes
2013-01-05 | 0.1019 | 0.1019 |  |  | 0.0061176 | 0.0061176 |  |  | 0.5791 | 0.5791 | 0.000705 | 0.000705 |  |  | 7.51e-05 | 7.51e-05 |  |  | 0.00384 | 0.00384 | 238 | 203 | Yes
2013-01-06 | 0.19532 | 0.19532 |  |  | 0.074933 | 0.074933 |  |  | 0.79526 | 0.79526 | 0.001809 | 0.001809 |  |  | 0.000706 | 0.000706 |  |  | 0.0073 | 0.0073 | 161 | 153 | Yes
2013-01-07 | 0.081112 | 0.081112 |  |  | 0.096766 | 0.096766 |  |  | 0.0033079 | 0.0033079 | 0.001758 | 0.001758 |  |  | 0.00211 | 0.00211 |  |  | 3.34e-05 | 3.34e-05 | 494 | 438 | Yes
2013-01-08 | 0.97685 | 0.97685 |  |  | 1.0459 | 1.0459 |  |  | 0.63497 | 0.63497 | 0.010778 | 0.010778 |  |  | 0.0114 | 0.0114 |  |  | 0.00759 | 0.00759 | 1069 | 859 | Yes
2013-01-09 | 0.27922 | 0.27922 |  |  | 0.26748 | 0.26748 |  |  | 0.33823 | 0.33823 | 0.002816 | 0.002816 |  |  | 0.00283 | 0.00283 |  |  | 0.00273 | 0.00273 | 530 | 463 | Yes
2013-01-10 | 0.070174 | 0.070174 |  |  | 0.0715 | 0.0715 |  |  | 0.063706 | 0.063706 | 0.00441 | 0.00441 |  |  | 0.00396 | 0.00396 |  |  | 0.00664 | 0.00664 | 422 | 372 | Yes
2013-01-11 | 0.098824 | 0.098824 |  |  | 0.10903 | 0.10903 |  |  | 0.048189 | 0.048189 | 0.002228 | 0.002228 |  |  | 0.00254 | 0.00254 |  |  | 0.000668 | 0.000668 | 464 | 370 | Yes
2013-01-12 | 0.23026 | 0.23026 |  |  | 0.15059 | 0.15059 |  |  | 0.62749 | 0.62749 | 0.006807 | 0.006807 |  |  | 0.0069 | 0.0069 |  |  | 0.00636 | 0.00636 | 277 | 262 | Yes
2013-01-13 | 0.85213 | 0.85213 |  |  | 0.69806 | 0.69806 |  |  | 1.621 | 1.621 | 0.014802 | 0.014802 |  |  | 0.0135 | 0.0135 |  |  | 0.0214 | 0.0214 | 641 | 392 | Yes
2013-01-14 | 0.50767 | 0.50767 |  |  | 0.53807 | 0.53807 |  |  | 0.35728 | 0.35728 | 0.003291 | 0.003291 |  |  | 0.00359 | 0.00359 |  |  | 0.00182 | 0.00182 | 757 | 617 | Yes
2013-01-15 | 0.31075 | 0.31075 |  |  | 0.3193 | 0.3193 |  |  | 0.26877 | 0.26877 | 0.002441 | 0.002441 |  |  | 0.00261 | 0.00261 |  |  | 0.00158 | 0.00158 | 521 | 464 | Yes
2013-01-16 | 0.78195 | 0.78195 |  |  | 0.7122 | 0.7122 |  |  | 1.1308 | 1.1308 | 0.058389 | 0.058389 |  |  | 0.0563 | 0.0563 |  |  | 0.0688 | 0.0688 | 890 | 473 | Yes
2013-01-17 | 0.26175 | 0.26175 |  |  | 0.18753 | 0.18753 |  |  | 0.63184 | 0.63184 | 0.003264 | 0.003264 |  |  | 0.00244 | 0.00244 |  |  | 0.00739 | 0.00739 | 471 | 409 | Yes
2013-01-18 | 2.6413 | 2.6413 |  |  | 1.2678 | 1.2678 | 294.89 | 294.89 | 8.9132 | 8.9132 | 0.023686 | 0.023686 |  |  | 0.0134 | 0.0134 | 3.03 | 3.03 | 0.0692 | 0.0692 | 2040 | 961 | Yes
2013-01-19 | 0.22151 | 0.22151 |  |  | 0.086407 | 0.086407 |  |  | 0.89474 | 0.89474 | 0.001774 | 0.001774 |  |  | 0.00107 | 0.00107 |  |  | 0.00528 | 0.00528 | 387 | 346 | Yes
2013-01-20 | 0.42058 | 0.42058 |  |  | 0.40047 | 0.40047 |  |  | 0.52155 | 0.52155 | 0.003503 | 0.003503 |  |  | 0.00243 | 0.00243 |  |  | 0.00885 | 0.00885 | 149 | 142 | Yes
2013-01-21 | 0.27967 | 0.27967 |  |  | 0.25061 | 0.25061 |  |  | 0.42493 | 0.42493 | 0.003506 | 0.003506 |  |  | 0.00338 | 0.00338 |  |  | 0.00413 | 0.00413 | 599 | 520 | Yes
2013-01-22 | 1.3978 | 1.3978 |  |  | 1.3385 | 1.3385 |  |  | 1.6958 | 1.6958 | 0.022164 | 0.022164 |  |  | 0.021 | 0.021 |  |  | 0.0279 | 0.0279 | 837 | 669 | Yes
2013-01-23 | 0.2594 | 0.2594 |  |  | 0.25006 | 0.25006 |  |  | 0.30643 | 0.30643 | 0.0107 | 0.0107 |  |  | 0.00719 | 0.00719 |  |  | 0.0282 | 0.0282 | 666 | 526 | Yes
2013-01-24 | 0.041746 | 0.041746 |  |  | 0.034228 | 0.034228 |  |  | 0.079264 | 0.079264 | 0.000207 | 0.000207 |  |  | 0.000153 | 0.000153 |  |  | 0.000474 | 0.000474 | 512 | 416 | Yes
2013-01-25 | 0.17607 | 0.17607 |  |  | 0.074587 | 0.074587 | 7.0206 | 7.0206 | 0.66816 | 0.66816 | 0.003389 | 0.003389 |  |  | 0.00172 | 0.00172 | 0.0447 | 0.0447 | 0.0116 | 0.0116 | 722 | 640 | Yes
2013-01-26 | 0.016279 | 0.016279 |  |  | 0.0061149 | 0.0061149 |  |  | 0.066927 | 0.066927 | 0.000168 | 0.000168 |  |  | 7.11e-05 | 7.11e-05 |  |  | 0.000648 | 0.000648 | 194 | 188 | Yes
2013-01-27 | 0.63909 | 0.63909 |  |  | 0.38935 | 0.38935 |  |  | 1.8841 | 1.8841 | 0.005803 | 0.005803 |  |  | 0.00373 | 0.00373 |  |  | 0.0162 | 0.0162 | 403 | 376 | Yes
2013-01-28 | 1.3015 | 1.3015 |  |  | 0.99523 | 0.99523 |  |  | 2.8295 | 2.8295 | 0.016972 | 0.016972 |  |  | 0.011 | 0.011 |  |  | 0.0469 | 0.0469 | 869 | 652 | Yes
2013-01-29 | 0.95839 | 0.95839 |  |  | 1.0283 | 1.0283 |  |  | 0.6121 | 0.6121 | 0.008747 | 0.008747 |  |  | 0.00921 | 0.00921 |  |  | 0.00648 | 0.00648 | 1035 | 1000 | Yes
2013-01-30 | 0.20494 | 0.20494 |  |  | 0.02732 | 0.02732 |  |  | 1.0899 | 1.0899 | 0.000811 | 0.000811 |  |  | 0.000197 | 0.000197 |  |  | 0.00387 | 0.00387 | 712 | 702 | Yes
2013-01-31 | 0.6619 | 0.6619 |  |  | 0.34042 | 0.34042 |  |  | 2.2642 | 2.2642 | 0.009849 | 0.009849 |  |  | 0.00618 | 0.00618 |  |  | 0.0281 | 0.0281 | 893 | 807 | Yes
2013-02-01 | 0.6242 | 0.6242 |  |  | 0.45943 | 0.45943 | 53.1237 | 53.1237 | 1.3427 | 1.3427 | 0.011343 | 0.011343 |  |  | 0.00871 | 0.00871 | 1.03 | 1.03 | 0.0225 | 0.0225 | 903 | 829 | Yes
2013-02-02 | 0.17921 | 0.17921 |  |  | 0.059132 | 0.059132 |  |  | 0.77758 | 0.77758 | 0.002394 | 0.002394 |  |  | 0.00109 | 0.00109 |  |  | 0.00887 | 0.00887 | 395 | 341 | Yes
2013-02-03 | 0.020327 | 0.020327 |  |  | 0.019028 | 0.019028 |  |  | 0.026838 | 0.026838 | 0.000169 | 0.000169 |  |  | 0.00018 | 0.00018 |  |  | 0.000114 | 0.000114 | 150 | 147 | Yes
2013-02-04 | 0.32975 | 0.32975 |  |  | 0.38891 | 0.38891 |  |  | 0.035786 | 0.035786 | 0.004238 | 0.004238 |  |  | 0.00507 | 0.00507 |  |  | 8.69e-05 | 8.69e-05 | 736 | 678 | Yes
2013-02-05 | 0.020711 | 0.020711 |  |  | 0.01291 | 0.01291 | 20.3883 | 20.3883 | 0.019955 | 0.019955 | 0.000153 | 0.000153 |  |  | 7.51e-05 | 7.51e-05 | 0.172 | 0.172 | 0.000207 | 0.000207 | 620 | 603 | Yes
2013-02-06 | 0.35114 | 0.35114 |  |  | 0.34136 | 0.34136 |  |  | 0.40055 | 0.40055 | 0.018562 | 0.018562 |  |  | 0.0168 | 0.0168 |  |  | 0.0274 | 0.0274 | 959 | 669 | Yes
2013-02-07 | 0.078717 | 0.078717 |  |  | 0.051474 | 0.051474 | 0.38832 | 0.38832 | 0.21379 | 0.21379 | 0.000718 | 0.000718 |  |  | 0.000384 | 0.000384 | 0.00344 | 0.00344 | 0.00238 | 0.00238 | 615 | 591 | Yes
2013-02-08 | 0.08384 | 0.08384 |  |  | 0.093139 | 0.093139 |  |  | 0.03769 | 0.03769 | 0.004233 | 0.004233 |  |  | 0.00462 | 0.00462 |  |  | 0.00231 | 0.00231 | 621 | 597 | Yes
2013-02-09 | 0.24857 | 0.24857 |  |  | 0.063517 | 0.063517 |  |  | 1.1706 | 1.1706 | 0.001762 | 0.001762 |  |  | 0.000929 | 0.000929 |  |  | 0.00591 | 0.00591 | 257 | 250 | Yes
2013-02-10 | 1.4136 | 1.4136 |  |  | 0.39369 | 0.39369 | 16.5773 | 16.5773 | 6.4632 | 6.4632 | 0.013809 | 0.013809 |  |  | 0.00427 | 0.00427 | 1.8 | 1.8 | 0.0578 | 0.0578 | 466 | 306 | Yes
2013-02-11 | 0.034727 | 0.034727 |  |  | 0.017044 | 0.017044 | 1.9416 | 1.9416 | 0.11908 | 0.11908 | 0.000321 | 0.000321 |  |  | 6.17e-05 | 6.17e-05 | 0.00344 | 0.00344 | 0.0016 | 0.0016 | 695 | 648 | Yes
2013-02-12 | 0.006444 | 0.006444 |  |  | 0.0016693 | 0.0016693 |  |  | 0.030233 | 0.030233 | 0.00021 | 0.00021 |  |  | 0.000215 | 0.000215 |  |  | 0.000187 | 0.000187 | 643 | 629 | Yes
2013-02-13 | 0.017684 | 0.017684 |  |  | 0.0092804 | 0.0092804 |  |  | 0.05957 | 0.05957 | 9.72e-05 | 9.72e-05 |  |  | 5.1e-05 | 5.1e-05 |  |  | 0.000327 | 0.000327 | 761 | 748 | Yes
2013-02-14 | 0.095072 | 0.095072 |  |  | 0.11128 | 0.11128 |  |  | 0.014542 | 0.014542 | 0.001516 | 0.001516 |  |  | 0.00181 | 0.00181 |  |  | 6.01e-05 | 6.01e-05 | 683 | 671 | Yes
2013-02-15 | 0.059949 | 0.059949 |  |  | 0.022794 | 0.022794 |  |  | 0.2451 | 0.2451 | 0.000337 | 0.000337 |  |  | 9.39e-05 | 9.39e-05 |  |  | 0.00155 | 0.00155 | 714 | 653 | Yes
2013-02-16 | 0.048414 | 0.048414 |  |  | 0.029297 | 0.029297 |  |  | 0.14371 | 0.14371 | 0.000946 | 0.000946 |  |  | 0.00103 | 0.00103 |  |  | 0.000508 | 0.000508 | 243 | 210 | Yes
2013-02-17 | 0.17927 | 0.17927 |  |  | 8.8563e-05 | 8.8563e-05 |  |  | 1.072 | 1.072 | 0.002619 | 0.002619 |  |  | 1.34e-06 | 1.34e-06 |  |  | 0.0157 | 0.0157 | 133 | 122 | Yes
2013-02-18 | 0.097729 | 0.097729 |  |  | 0.0073172 | 0.0073172 | 35.1306 | 35.1306 | 0.47987 | 0.47987 | 0.002573 | 0.002573 |  |  | 8.99e-05 | 8.99e-05 | 1 | 1 | 0.013 | 0.013 | 798 | 660 | Yes
2013-02-19 | 0.18598 | 0.18598 |  |  | 0.1372 | 0.1372 |  |  | 0.42926 | 0.42926 | 0.002212 | 0.002212 |  |  | 0.0021 | 0.0021 |  |  | 0.00276 | 0.00276 | 813 | 746 | Yes
2013-02-20 | 0.2777 | 0.2777 |  |  | 0.24804 | 0.24804 |  |  | 0.42594 | 0.42594 | 0.004892 | 0.004892 |  |  | 0.00419 | 0.00419 |  |  | 0.00841 | 0.00841 | 843 | 810 | Yes
2013-02-21 | 0.043571 | 0.043571 |  |  | 0.028585 | 0.028585 | 4.5979 | 4.5979 | 0.10935 | 0.10935 | 0.000902 | 0.000902 |  |  | 0.000945 | 0.000945 | 0.0481 | 0.0481 | 0.000595 | 0.000595 | 752 | 721 | Yes
2013-02-22 | 0.2109 | 0.2109 |  |  | 0.14813 | 0.14813 |  |  | 0.5239 | 0.5239 | 0.00277 | 0.00277 |  |  | 0.00201 | 0.00201 |  |  | 0.00655 | 0.00655 | 672 | 646 | Yes
2013-02-23 | 4.7798 | 4.7798 |  |  | 2.1658 | 2.1658 |  |  | 17.8074 | 17.8074 | 0.02475 | 0.02475 |  |  | 0.0156 | 0.0156 |  |  | 0.0705 | 0.0705 | 1316 | 676 | Yes
2013-02-24 | 11.4018 | 11.4018 |  |  | 9.6908 | 9.6908 |  |  | 19.9451 | 19.9451 | 0.038799 | 0.038799 |  |  | 0.0345 | 0.0345 |  |  | 0.0601 | 0.0601 | 2087 | 795 | Yes
2013-02-25 | 1.4333 | 1.4333 |  |  | 0.93199 | 0.93199 |  |  | 3.9324 | 3.9324 | 0.011624 | 0.011624 |  |  | 0.00882 | 0.00882 |  |  | 0.0256 | 0.0256 | 1551 | 1291 | Yes
2013-02-26 | 0.17121 | 0.17121 |  |  | 0.050835 | 0.050835 |  |  | 0.77104 | 0.77104 | 0.001749 | 0.001749 |  |  | 0.000385 | 0.000385 |  |  | 0.00855 | 0.00855 | 857 | 735 | Yes
2013-02-27 | 0.063473 | 0.063473 |  |  | 0.063617 | 0.063617 |  |  | 0.062878 | 0.062878 | 0.003221 | 0.003221 |  |  | 0.00376 | 0.00376 |  |  | 0.000521 | 0.000521 | 889 | 766 | Yes
2013-02-28 | 0.28786 | 0.28786 |  |  | 0.2475 | 0.2475 |  |  | 0.48939 | 0.48939 | 0.002295 | 0.002295 |  |  | 0.00139 | 0.00139 |  |  | 0.00681 | 0.00681 | 776 | 650 | Yes
2013-03-01 | 3.6516 | 3.6516 |  |  | 3.6652 | 3.6652 |  |  | 3.5908 | 3.5908 | 0.022779 | 0.022779 |  |  | 0.0232 | 0.0232 |  |  | 0.0206 | 0.0206 | 1416 | 1068 | Yes
2013-03-02 | 0.32977 | 0.32977 |  |  | 0.21875 | 0.21875 |  |  | 0.88329 | 0.88329 | 0.002244 | 0.002244 |  |  | 0.00225 | 0.00225 |  |  | 0.0022 | 0.0022 | 360 | 308 | Yes
2013-03-03 | 0.010748 | 0.010748 |  |  | 0.0097702 | 0.0097702 |  |  | 0.015638 | 0.015638 | 7.26e-05 | 7.26e-05 |  |  | 6.04e-05 | 6.04e-05 |  |  | 0.000134 | 0.000134 | 182 | 172 | Yes
2013-03-04 | 0.38478 | 0.38478 |  |  | 0.45133 | 0.45133 |  |  | 0.054076 | 0.054076 | 0.004429 | 0.004429 |  |  | 0.00489 | 0.00489 |  |  | 0.00216 | 0.00216 | 862 | 786 | Yes
2013-03-05 | 0.15899 | 0.15899 |  |  | 0.06348 | 0.06348 |  |  | 0.63496 | 0.63496 | 0.001514 | 0.001514 |  |  | 0.000466 | 0.000466 |  |  | 0.00674 | 0.00674 | 799 | 683 | Yes
2013-03-06 | 0.025522 | 0.025522 |  |  | 0.017314 | 0.017314 |  |  | 0.066446 | 0.066446 | 0.001277 | 0.001277 |  |  | 0.00147 | 0.00147 |  |  | 0.000327 | 0.000327 | 703 | 656 | Yes
2013-03-07 | 0.051886 | 0.051886 |  |  | 0.040492 | 0.040492 |  |  | 0.10873 | 0.10873 | 0.000209 | 0.000209 |  |  | 0.000161 | 0.000161 |  |  | 0.000448 | 0.000448 | 700 | 661 | Yes
2013-03-08 | 0.032783 | 0.032783 |  |  | 0.025398 | 0.025398 | 0.85911 | 0.85911 | 0.067956 | 0.067956 | 0.000279 | 0.000279 |  |  | 0.000174 | 0.000174 | 0.0172 | 0.0172 | 0.000769 | 0.000769 | 614 | 564 | Yes
2013-03-09 | 0.041594 | 0.041594 |  |  | 0.04745 | 0.04745 |  |  | 0.01251 | 0.01251 | 0.000685 | 0.000685 |  |  | 0.000802 | 0.000802 |  |  | 0.0001 | 0.0001 | 219 | 211 | Yes
2013-03-10 | 1.1656 | 1.1656 |  |  | 1.3996 | 1.3996 |  |  | 0.0023055 | 0.0023055 | 0.015031 | 0.015031 |  |  | 0.018 | 0.018 |  |  | 3.34e-05 | 3.34e-05 | 337 | 290 | Yes
2013-03-11 | 0.050181 | 0.050181 |  |  | 0.02026 | 0.02026 |  |  | 0.19929 | 0.19929 | 0.000714 | 0.000714 |  |  | 0.000126 | 0.000126 |  |  | 0.00364 | 0.00364 | 657 | 555 | Yes
2013-03-12 | 0.59581 | 0.59581 |  |  | 0.60908 | 0.60908 |  |  | 0.53089 | 0.53089 | 0.005668 | 0.005668 |  |  | 0.00548 | 0.00548 |  |  | 0.0066 | 0.0066 | 732 | 678 | Yes
2013-03-13 | 0.1235 | 0.1235 |  |  | 0.037842 | 0.037842 |  |  | 0.55031 | 0.55031 | 0.000684 | 0.000684 |  |  | 0.000331 | 0.000331 |  |  | 0.00244 | 0.00244 | 686 | 621 | Yes
2013-03-14 | 0.081322 | 0.081322 |  |  | 0.042454 | 0.042454 |  |  | 0.27505 | 0.27505 | 0.000553 | 0.000553 |  |  | 0.000271 | 0.000271 |  |  | 0.00196 | 0.00196 | 612 | 574 | Yes
2013-03-15 | 0.24274 | 0.24274 |  |  | 0.28822 | 0.28822 |  |  | 0.016713 | 0.016713 | 0.002378 | 0.002378 |  |  | 0.00283 | 0.00283 |  |  | 0.000127 | 0.000127 | 651 | 606 | Yes
2013-03-16 | 0.15535 | 0.15535 |  |  | 0.11685 | 0.11685 |  |  | 0.34739 | 0.34739 | 0.002503 | 0.002503 |  |  | 0.0025 | 0.0025 |  |  | 0.00254 | 0.00254 | 384 | 277 | Yes
2013-03-17 | 0.10009 | 0.10009 |  |  | 0.1179 | 0.1179 |  |  | 0.011594 | 0.011594 | 0.002465 | 0.002465 |  |  | 0.00291 | 0.00291 |  |  | 0.000247 | 0.000247 | 208 | 178 | Yes
2013-03-18 | 0.15784 | 0.15784 |  |  | 0.18847 | 0.18847 |  |  | 0.0056001 | 0.0056001 | 0.00152 | 0.00152 |  |  | 0.00181 | 0.00181 |  |  | 8.02e-05 | 8.02e-05 | 760 | 687 | Yes
2013-03-19 | 0.1122 | 0.1122 |  |  | 0.13413 | 0.13413 |  |  | 0.0031943 | 0.0031943 | 0.000862 | 0.000862 |  |  | 0.00101 | 0.00101 |  |  | 0.000127 | 0.000127 | 897 | 645 | Yes
2013-03-20 | 0.029586 | 0.029586 |  |  | 0.029458 | 0.029458 |  |  | 0.030279 | 0.030279 | 0.00034 | 0.00034 |  |  | 0.000341 | 0.000341 |  |  | 0.000334 | 0.000334 | 776 | 615 | Yes
2013-03-21 | 0.019209 | 0.019209 |  |  | 0.0092562 | 0.0092562 |  |  | 0.068812 | 0.068812 | 0.000154 | 0.000154 |  |  | 0.00016 | 0.00016 |  |  | 0.000127 | 0.000127 | 792 | 643 | Yes
2013-03-22 | 0.46013 | 0.46013 |  |  | 0.39447 | 0.39447 |  |  | 0.78806 | 0.78806 | 0.004231 | 0.004231 |  |  | 0.00388 | 0.00388 |  |  | 0.006 | 0.006 | 851 | 737 | Yes
2013-03-23 | 0.17578 | 0.17578 |  |  | 0.020007 | 0.020007 |  |  | 0.95192 | 0.95192 | 0.002373 | 0.002373 |  |  | 0.00119 | 0.00119 |  |  | 0.00826 | 0.00826 | 246 | 157 | Yes
2013-03-24 | 0.010771 | 0.010771 |  |  | 0.0078889 | 0.0078889 |  |  | 0.025147 | 0.025147 | 0.000249 | 0.000249 |  |  | 7.25e-05 | 7.25e-05 |  |  | 0.00113 | 0.00113 | 141 | 128 | Yes
2013-03-25 | 0.01676 | 0.01676 |  |  | 0.019457 | 0.019457 | 0.61512 | 0.61512 | 0.0021652 | 0.0021652 | 0.000108 | 0.000108 |  |  | 0.000123 | 0.000123 | 0.00344 | 0.00344 | 2.67e-05 | 2.67e-05 | 732 | 620 | Yes
2013-03-26 | 0.13878 | 0.13878 |  |  | 0.15823 | 0.15823 |  |  | 0.042175 | 0.042175 | 0.002034 | 0.002034 |  |  | 0.00237 | 0.00237 |  |  | 0.000388 | 0.000388 | 831 | 653 | Yes
2013-03-27 | 0.16998 | 0.16998 |  |  | 0.20361 | 0.20361 |  |  | 0.0028802 | 0.0028802 | 0.006537 | 0.006537 |  |  | 0.00785 | 0.00785 |  |  | 6.68e-06 | 6.68e-06 | 860 | 675 | Yes
2013-03-28 | 0.20411 | 0.20411 |  |  | 0.22297 | 0.22297 |  |  | 0.1106 | 0.1106 | 0.002049 | 0.002049 |  |  | 0.0022 | 0.0022 |  |  | 0.00131 | 0.00131 | 622 | 550 | Yes
2013-03-29 | 0.31005 | 0.31005 |  |  | 0.37002 | 0.37002 |  |  | 0.011962 | 0.011962 | 0.002797 | 0.002797 |  |  | 0.00334 | 0.00334 |  |  | 8.02e-05 | 8.02e-05 | 164 | 140 | Yes
2013-03-30 | 0.007558 | 0.007558 |  |  | 0.0063041 | 0.0063041 |  |  | 0.01382 | 0.01382 | 8.49e-05 | 8.49e-05 |  |  | 8.32e-05 | 8.32e-05 |  |  | 9.36e-05 | 9.36e-05 | 119 | 109 | Yes
2013-03-31 | 0.10923 | 0.10923 |  |  | 0.034444 | 0.034444 |  |  | 0.48188 | 0.48188 | 0.001261 | 0.001261 |  |  | 0.000625 | 0.000625 |  |  | 0.00443 | 0.00443 | 126 | 113 | Yes
2013-04-01 | 0.019986 | 0.019986 |  |  | 0.010942 | 0.010942 |  |  | 0.06507 | 0.06507 | 0.000227 | 0.000227 |  |  | 0.00015 | 0.00015 |  |  | 0.000608 | 0.000608 | 132 | 132 | Yes
2013-04-02 | 0.010458 | 0.010458 |  |  | 0.012112 | 0.012112 |  |  | 0.0022454 | 0.0022454 | 6.48e-05 | 6.48e-05 |  |  | 6.98e-05 | 6.98e-05 |  |  | 4.01e-05 | 4.01e-05 | 658 | 573 | Yes
2013-04-03 | 0.089315 | 0.089315 |  |  | 0.10581 | 0.10581 |  |  | 0.0073376 | 0.0073376 | 0.001481 | 0.001481 |  |  | 0.00178 | 0.00178 |  |  | 2e-05 | 2e-05 | 683 | 580 | Yes
2013-04-04 | 0.144 | 0.144 |  |  | 0.10774 | 0.10774 |  |  | 0.3249 | 0.3249 | 0.001689 | 0.001689 |  |  | 0.00149 | 0.00149 |  |  | 0.00271 | 0.00271 | 709 | 642 | Yes
2013-04-05 | 0.053311 | 0.053311 |  |  | 0.059678 | 0.059678 |  |  | 0.021705 | 0.021705 | 0.001081 | 0.001081 |  |  | 0.00123 | 0.00123 |  |  | 0.000334 | 0.000334 | 599 | 552 | Yes
2013-04-06 | 0.007061 | 0.007061 |  |  | 0.0083424 | 0.0083424 |  |  | 0.000695 | 0.000695 | 0.000121 | 0.000121 |  |  | 0.000144 | 0.000144 |  |  | 6.68e-06 | 6.68e-06 | 185 | 174 | Yes
2013-04-07 | 0.029995 | 0.029995 |  |  | 0.034936 | 0.034936 |  |  | 0.0054464 | 0.0054464 | 0.00149 | 0.00149 |  |  | 0.00178 | 0.00178 |  |  | 7.35e-05 | 7.35e-05 | 141 | 135 | Yes
2013-04-08 | 0.12562 | 0.12562 |  |  | 0.042814 | 0.042814 |  |  | 0.53827 | 0.53827 | 0.002198 | 0.002198 |  |  | 0.000204 | 0.000204 |  |  | 0.0121 | 0.0121 | 776 | 686 | Yes
2013-04-09 | 0.11456 | 0.11456 |  |  | 0.10898 | 0.10898 |  |  | 0.14259 | 0.14259 | 0.002591 | 0.002591 |  |  | 0.00235 | 0.00235 |  |  | 0.0038 | 0.0038 | 679 | 643 | Yes
2013-04-10 | 0.42124 | 0.42124 |  |  | 0.50299 | 0.50299 |  |  | 0.014896 | 0.014896 | 0.004589 | 0.004589 |  |  | 0.00549 | 0.00549 |  |  | 9.36e-05 | 9.36e-05 | 806 | 699 | Yes
2013-04-11 | 0.18697 | 0.18697 |  |  | 0.024482 | 0.024482 |  |  | 0.99656 | 0.99656 | 0.001581 | 0.001581 |  |  | 0.000188 | 0.000188 |  |  | 0.00852 | 0.00852 | 688 | 642 | Yes
2013-04-12 | 0.068895 | 0.068895 |  |  | 0.081535 | 0.081535 |  |  | 0.0060813 | 0.0060813 | 0.001461 | 0.001461 |  |  | 0.00174 | 0.00174 |  |  | 7.35e-05 | 7.35e-05 | 570 | 528 | Yes
2013-04-13 | 0.72619 | 0.72619 |  |  | 0.10367 | 0.10367 |  |  | 3.8278 | 3.8278 | 0.008708 | 0.008708 |  |  | 0.00127 | 0.00127 |  |  | 0.0458 | 0.0458 | 503 | 239 | Yes
2013-04-14 | 0.023851 | 0.023851 |  |  | 0.0021416 | 0.0021416 |  |  | 0.13201 | 0.13201 | 0.000244 | 0.000244 |  |  | 5.1e-05 | 5.1e-05 |  |  | 0.0012 | 0.0012 | 128 | 125 | Yes
2013-04-15 | 1.2312 | 1.2312 |  |  | 1.0943 | 1.0943 |  |  | 1.9156 | 1.9156 | 0.009428 | 0.009428 |  |  | 0.00931 | 0.00931 |  |  | 0.01 | 0.01 | 864 | 746 | Yes
2013-04-16 | 0.43531 | 0.43531 |  |  | 0.39716 | 0.39716 |  |  | 0.62614 | 0.62614 | 0.005954 | 0.005954 |  |  | 0.00645 | 0.00645 |  |  | 0.00352 | 0.00352 | 792 | 674 | Yes
2013-04-17 | 0.02787 | 0.02787 |  |  | 0.028618 | 0.028618 |  |  | 0.024198 | 0.024198 | 0.000258 | 0.000258 |  |  | 0.000258 | 0.000258 |  |  | 0.000261 | 0.000261 | 784 | 697 | Yes
2013-04-18 | 0.057726 | 0.057726 |  |  | 0.069004 | 0.069004 |  |  | 0.0016707 | 0.0016707 | 0.000576 | 0.000576 |  |  | 0.00069 | 0.00069 |  |  | 1.34e-05 | 1.34e-05 | 742 | 634 | Yes
2013-04-19 | 0.18284 | 0.18284 |  |  | 0.031372 | 0.031372 |  |  | 0.93755 | 0.93755 | 0.001714 | 0.001714 |  |  | 0.000172 | 0.000172 |  |  | 0.0094 | 0.0094 | 798 | 656 | Yes
2013-04-20 | 0.22672 | 0.22672 |  |  | 0.16368 | 0.16368 |  |  | 0.5411 | 0.5411 | 0.00189 | 0.00189 |  |  | 0.00111 | 0.00111 |  |  | 0.00577 | 0.00577 | 277 | 225 | Yes
2013-04-21 | 0.002729 | 0.002729 |  |  | 0.0032782 | 0.0032782 |  |  | 0 | 0 | 7.48e-05 | 7.48e-05 |  |  | 8.99e-05 | 8.99e-05 |  |  | 0 | 0 | 101 | 94 | Yes
2013-04-22 | 0.1536 | 0.1536 |  |  | 0.11366 | 0.11366 |  |  | 0.35276 | 0.35276 | 0.001586 | 0.001586 |  |  | 0.0014 | 0.0014 |  |  | 0.00251 | 0.00251 | 717 | 634 | Yes
2013-04-23 | 0.019988 | 0.019988 |  |  | 0.00037036 | 0.00037036 |  |  | 0.11772 | 0.11772 | 5.47e-05 | 5.47e-05 |  |  | 2.68e-06 | 2.68e-06 |  |  | 0.000314 | 0.000314 | 602 | 550 | Yes
2013-04-24 | 0.18508 | 0.18508 |  |  | 0.19118 | 0.19118 |  |  | 0.15505 | 0.15505 | 0.00189 | 0.00189 |  |  | 0.002 | 0.002 |  |  | 0.00134 | 0.00134 | 602 | 565 | Yes
2013-04-25 | 0.038901 | 0.038901 |  |  | 0.04486 | 0.04486 |  |  | 0.0093023 | 0.0093023 | 0.00033 | 0.00033 |  |  | 0.000374 | 0.000374 |  |  | 0.000107 | 0.000107 | 132 | 121 | Yes
2013-04-26 | 0.63655 | 0.63655 |  |  | 0.62328 | 0.62328 |  |  | 0.70385 | 0.70385 | 0.007942 | 0.007942 |  |  | 0.00669 | 0.00669 |  |  | 0.0142 | 0.0142 | 811 | 721 | Yes
2013-04-27 | 0.18585 | 0.18585 |  |  | 0.2023 | 0.2023 |  |  | 0.10434 | 0.10434 | 0.001802 | 0.001802 |  |  | 0.00195 | 0.00195 |  |  | 0.00105 | 0.00105 | 241 | 202 | Yes
2013-04-28 | 0.16158 | 0.16158 |  |  | 0.18311 | 0.18311 |  |  | 0.054665 | 0.054665 | 0.001759 | 0.001759 |  |  | 0.00202 | 0.00202 |  |  | 0.000461 | 0.000461 | 213 | 192 | Yes
2013-04-29 | 0.1109 | 0.1109 |  |  | 0.12769 | 0.12769 | 0.0068729 | 0.0068729 | 0.027459 | 0.027459 | 0.002459 | 0.002459 |  |  | 0.00275 | 0.00275 | 0.00344 | 0.00344 | 0.00103 | 0.00103 | 785 | 742 | Yes
2013-04-30 | 0.003084 | 0.003084 |  |  | 0.0022329 | 0.0022329 |  |  | 0.0073309 | 0.0073309 | 3.8e-05 | 3.8e-05 |  |  | 3.22e-05 | 3.22e-05 |  |  | 6.68e-05 | 6.68e-05 | 673 | 630 | Yes
2013-05-01 | 0.013051 | 0.013051 |  |  | 0.014283 | 0.014283 |  |  | 0.0069433 | 0.0069433 | 0.000172 | 0.000172 |  |  | 0.000201 | 0.000201 |  |  | 2.67e-05 | 2.67e-05 | 588 | 557 | Yes
2013-05-02 | 0.025464 | 0.025464 |  |  | 0.026892 | 0.026892 |  |  | 0.018397 | 0.018397 | 0.001492 | 0.001492 |  |  | 7.51e-05 | 7.51e-05 |  |  | 0.00855 | 0.00855 | 602 | 548 | Yes
2013-05-03 | 0.002617 | 0.002617 |  |  | 0.003144 | 0.003144 |  |  | 0 | 0 | 0.000242 | 0.000242 |  |  | 0.000291 | 0.000291 |  |  | 0 | 0 | 724 | 522 | Yes
2013-05-04 | 0.082834 | 0.082834 |  |  | 0.043623 | 0.043623 |  |  | 0.27827 | 0.27827 | 0.001156 | 0.001156 |  |  | 0.000649 | 0.000649 |  |  | 0.00368 | 0.00368 | 252 | 234 | Yes
2013-05-05 | 0.002679 | 0.002679 |  |  | 0 | 0 |  |  | 0.016025 | 0.016025 | 2.68e-05 | 2.68e-05 |  |  | 0 | 0 |  |  | 0.00016 | 0.00016 | 119 | 118 | Yes
2013-05-06 | 0.062563 | 0.062563 |  |  | 0.07391 | 0.07391 |  |  | 0.0061748 | 0.0061748 | 0.000757 | 0.000757 |  |  | 0.000903 | 0.000903 |  |  | 3.34e-05 | 3.34e-05 | 744 | 655 | Yes
2013-05-07 | 0.30412 | 0.30412 |  |  | 0.06448 | 0.06448 |  |  | 1.4982 | 1.4982 | 0.003874 | 0.003874 |  |  | 0.000941 | 0.000941 |  |  | 0.0185 | 0.0185 | 737 | 396 | Yes
2013-05-08 | 0.4386 | 0.4386 |  |  | 0.52205 | 0.52205 | 0.70447 | 0.70447 | 0.022454 | 0.022454 | 0.002798 | 0.002798 |  |  | 0.00334 | 0.00334 | 0.00344 | 0.00344 | 0.00012 | 0.00012 | 734 | 629 | Yes
2013-05-09 | 0.024073 | 0.024073 |  |  | 0.026662 | 0.026662 |  |  | 0.011227 | 0.011227 | 0.000162 | 0.000162 |  |  | 0.000182 | 0.000182 |  |  | 6.01e-05 | 6.01e-05 | 642 | 605 | Yes
2013-05-10 | 0.13892 | 0.13892 |  |  | 0.15129 | 0.15129 |  |  | 0.077559 | 0.077559 | 0.00236 | 0.00236 |  |  | 0.00263 | 0.00263 |  |  | 0.00102 | 0.00102 | 736 | 600 | Yes
2013-05-11 | 0.23311 | 0.23311 |  |  | 0.0013459 | 0.0013459 | 0.63574 | 0.63574 | 1.3865 | 1.3865 | 0.001286 | 0.001286 |  |  | 1.74e-05 | 1.74e-05 | 0.00344 | 0.00344 | 0.0076 | 0.0076 | 210 | 207 | Yes
2013-05-12 | 0.096869 | 0.096869 |  |  | 0.0013607 | 0.0013607 |  |  | 0.5727 | 0.5727 | 0.001505 | 0.001505 |  |  | 4.16e-05 | 4.16e-05 |  |  | 0.00879 | 0.00879 | 131 | 114 | Yes
2013-05-13 | 0.049429 | 0.049429 |  |  | 0.047627 | 0.047627 |  |  | 0.0585 | 0.0585 | 0.000345 | 0.000345 |  |  | 0.000331 | 0.000331 |  |  | 0.000414 | 0.000414 | 741 | 622 | Yes
2013-05-14 | 0.12675 | 0.12675 |  |  | 0.0038364 | 0.0038364 |  |  | 0.7391 | 0.7391 | 0.001784 | 0.001784 |  |  | 5.1e-05 | 5.1e-05 |  |  | 0.0104 | 0.0104 | 844 | 739 | Yes
2013-05-15 | 0.07714 | 0.07714 |  |  | 0.064221 | 0.064221 |  |  | 0.14163 | 0.14163 | 0.001803 | 0.001803 |  |  | 0.00198 | 0.00198 |  |  | 0.000922 | 0.000922 | 874 | 702 | Yes
2013-05-16 | 0.19046 | 0.19046 |  |  | 0.16936 | 0.16936 |  |  | 0.29593 | 0.29593 | 0.00291 | 0.00291 |  |  | 0.00299 | 0.00299 |  |  | 0.00251 | 0.00251 | 775 | 687 | Yes
2013-05-17 | 0.1463 | 0.1463 |  |  | 0.1654 | 0.1654 |  |  | 0.051443 | 0.051443 | 0.000981 | 0.000981 |  |  | 0.00118 | 0.00118 |  |  | 1.34e-05 | 1.34e-05 | 752 | 645 | Yes
2013-05-18 | 0.24827 | 0.24827 |  |  | 0.27253 | 0.27253 | 1.0103 | 1.0103 | 0.12601 | 0.12601 | 0.001965 | 0.001965 |  |  | 0.0021 | 0.0021 | 0.0103 | 0.0103 | 0.00128 | 0.00128 | 269 | 234 | Yes
2013-05-19 | 0.11353 | 0.11353 |  |  | 0.13494 | 0.13494 |  |  | 0.007097 | 0.007097 | 0.001432 | 0.001432 |  |  | 0.00171 | 0.00171 |  |  | 4.01e-05 | 4.01e-05 | 208 | 191 | Yes
2013-05-20 | 0.54994 | 0.54994 |  |  | 0.65278 | 0.65278 |  |  | 0.038827 | 0.038827 | 0.0031 | 0.0031 |  |  | 0.0037 | 0.0037 |  |  | 0.00012 | 0.00012 | 961 | 704 | Yes
2013-05-21 | 0.037097 | 0.037097 |  |  | 0.030242 | 0.030242 |  |  | 0.071311 | 0.071311 | 0.001745 | 0.001745 |  |  | 0.000305 | 0.000305 |  |  | 0.00892 | 0.00892 | 880 | 658 | Yes
2013-05-22 | 0.5213 | 0.5213 |  |  | 0.61206 | 0.61206 |  |  | 0.070349 | 0.070349 | 0.005166 | 0.005166 |  |  | 0.00545 | 0.00545 |  |  | 0.00377 | 0.00377 | 871 | 708 | Yes
2013-05-23 | 0.16459 | 0.16459 |  |  | 0.11469 | 0.11469 | 45.3505 | 45.3505 | 0.32522 | 0.32522 | 0.001562 | 0.001562 |  |  | 0.000972 | 0.000972 | 0.416 | 0.416 | 0.0037 | 0.0037 | 756 | 674 | Yes
2013-05-24 | 0.041861 | 0.041861 |  |  | 0.045997 | 0.045997 |  |  | 0.021345 | 0.021345 | 0.003697 | 0.003697 |  |  | 0.00441 | 0.00441 |  |  | 0.000147 | 0.000147 | 764 | 644 | Yes
2013-05-25 | 0.051568 | 0.051568 |  |  | 0.0098628 | 0.0098628 |  |  | 0.25937 | 0.25937 | 0.0004 | 0.0004 |  |  | 4.03e-05 | 4.03e-05 |  |  | 0.00219 | 0.00219 | 257 | 238 | Yes
2013-05-26 | 0.028895 | 0.028895 |  |  | 0.027596 | 0.027596 | 1.8247 | 1.8247 | 0.031877 | 0.031877 | 0.00025 | 0.00025 |  |  | 0.000114 | 0.000114 | 0.0103 | 0.0103 | 0.000909 | 0.000909 | 180 | 164 | Yes
2013-05-27 | 0.085095 | 0.085095 |  |  | 0.092735 | 0.092735 |  |  | 0.047213 | 0.047213 | 0.000986 | 0.000986 |  |  | 0.000997 | 0.000997 |  |  | 0.000936 | 0.000936 | 737 | 637 | Yes
2013-05-28 | 0.311 | 0.311 |  |  | 0.046736 | 0.046736 |  |  | 1.6277 | 1.6277 | 0.003697 | 0.003697 |  |  | 0.000258 | 0.000258 |  |  | 0.0208 | 0.0208 | 846 | 740 | Yes
2013-05-29 | 0.033052 | 0.033052 |  |  | 0.039702 | 0.039702 |  |  | 0 | 0 | 8.71e-05 | 8.71e-05 |  |  | 0.000105 | 0.000105 |  |  | 0 | 0 | 813 | 635 | Yes
2013-05-30 | 0.017219 | 0.017219 |  |  | 0.0050911 | 0.0050911 |  |  | 0.077653 | 0.077653 | 0.000187 | 0.000187 |  |  | 9.26e-05 | 9.26e-05 |  |  | 0.000655 | 0.000655 | 714 | 611 | Yes
2013-05-31 | 0.031588 | 0.031588 |  |  | 0.03049 | 0.03049 |  |  | 0.037116 | 0.037116 | 0.000139 | 0.000139 |  |  | 0.000138 | 0.000138 |  |  | 0.00014 | 0.00014 | 632 | 580 | Yes
2013-06-01 | 0.032227 | 0.032227 |  |  | 0.038643 | 0.038643 |  |  | 0.00033413 | 0.00033413 | 0.00014 | 0.00014 |  |  | 0.000166 | 0.000166 |  |  | 6.68e-06 | 6.68e-06 | 185 | 160 | Yes
2013-06-02 | 0.40528 | 0.40528 |  |  | 0.23206 | 0.23206 |  |  | 1.2687 | 1.2687 | 0.0141 | 0.0141 |  |  | 0.0137 | 0.0137 |  |  | 0.0161 | 0.0161 | 461 | 230 | Yes
2013-06-03 | 0.001229 | 0.001229 |  |  | 0.00083062 | 0.00083062 |  |  | 0.0032144 | 0.0032144 | 5.59e-06 | 5.59e-06 |  |  | 4.03e-06 | 4.03e-06 |  |  | 1.34e-05 | 1.34e-05 | 778 | 730 | Yes
2013-06-04 | 0.008973 | 0.008973 |  |  | 0.0097017 | 0.0097017 |  |  | 0.0053595 | 0.0053595 | 0.000365 | 0.000365 |  |  | 5.77e-05 | 5.77e-05 |  |  | 0.0019 | 0.0019 | 753 | 603 | Yes
2013-06-05 | 0.022072 | 0.022072 |  |  | 0.026513 | 0.026513 |  |  | 0 | 0 | 8.49e-05 | 8.49e-05 |  |  | 0.000102 | 0.000102 |  |  | 0 | 0 | 841 | 692 | Yes
2013-06-06 | 0.091404 | 0.091404 |  |  | 0.10901 | 0.10901 |  |  | 0.003876 | 0.003876 | 0.001349 | 0.001349 |  |  | 0.00147 | 0.00147 |  |  | 0.000762 | 0.000762 | 691 | 611 | Yes
2013-06-07 | 0.003164 | 0.003164 |  |  | 0.0018008 | 0.0018008 |  |  | 0.0099572 | 0.0099572 | 3.8e-05 | 3.8e-05 |  |  | 3.49e-05 | 3.49e-05 |  |  | 5.35e-05 | 5.35e-05 | 656 | 609 | Yes
2013-06-08 | 0.30293 | 0.30293 |  |  | 0.023977 | 0.023977 |  |  | 1.6928 | 1.6928 | 0.003044 | 0.003044 |  |  | 0.00112 | 0.00112 |  |  | 0.0126 | 0.0126 | 252 | 223 | Yes
2013-06-09 | 0.024234 | 0.024234 |  |  | 0.014978 | 0.014978 |  |  | 0.070376 | 0.070376 | 0.000151 | 0.000151 |  |  | 3.89e-05 | 3.89e-05 |  |  | 0.000708 | 0.000708 | 117 | 112 | Yes
2013-06-10 | 0.27599 | 0.27599 |  |  | 0.24982 | 0.24982 |  |  | 0.40684 | 0.40684 | 0.002898 | 0.002898 |  |  | 0.00334 | 0.00334 |  |  | 0.000695 | 0.000695 | 299 | 214 | Yes
2013-06-11 | 0.20013 | 0.20013 |  |  | 0.24004 | 0.24004 |  |  | 0.0017576 | 0.0017576 | 0.001185 | 0.001185 |  |  | 0.00142 | 0.00142 |  |  | 2e-05 | 2e-05 | 842 | 674 | Yes
2013-06-12 | 0.06343 | 0.06343 |  |  | 0.074164 | 0.074164 |  |  | 0.010098 | 0.010098 | 0.000656 | 0.000656 |  |  | 0.000776 | 0.000776 |  |  | 6.01e-05 | 6.01e-05 | 844 | 682 | Yes
2013-06-13 | 0.007939 | 0.007939 |  |  | 0.008482 | 0.008482 |  |  | 0.0052526 | 0.0052526 | 5.36e-05 | 5.36e-05 |  |  | 5.5e-05 | 5.5e-05 |  |  | 4.68e-05 | 4.68e-05 | 806 | 724 | Yes
2013-06-14 | 0.18338 | 0.18338 |  |  | 0.20824 | 0.20824 |  |  | 0.059964 | 0.059964 | 0.001749 | 0.001749 |  |  | 0.00191 | 0.00191 |  |  | 0.000942 | 0.000942 | 734 | 583 | Yes
2013-06-15 | 0.030429 | 0.030429 |  |  | 0.014053 | 0.014053 |  |  | 0.11204 | 0.11204 | 0.000248 | 0.000248 |  |  | 0.000103 | 0.000103 |  |  | 0.000969 | 0.000969 | 199 | 165 | Yes
2013-06-16 | 0.019695 | 0.019695 |  |  | 0.017839 | 0.017839 |  |  | 0.028976 | 0.028976 | 0.002163 | 0.002163 |  |  | 0.00256 | 0.00256 |  |  | 0.000187 | 0.000187 | 140 | 130 | Yes
2013-06-17 | 0.069422 | 0.069422 |  |  | 0.030428 | 0.030428 |  |  | 0.26375 | 0.26375 | 0.004887 | 0.004887 |  |  | 0.00203 | 0.00203 |  |  | 0.0191 | 0.0191 | 832 | 724 | Yes
2013-06-18 | 0.014803 | 0.014803 |  |  | 0.0037089 | 0.0037089 |  |  | 0.070082 | 0.070082 | 0.00202 | 0.00202 |  |  | 4.56e-05 | 4.56e-05 |  |  | 0.0119 | 0.0119 | 691 | 607 | Yes
2013-06-19 | 0.026374 | 0.026374 |  |  | 0.014577 | 0.014577 |  |  | 0.085178 | 0.085178 | 0.009729 | 0.009729 |  |  | 0.00311 | 0.00311 |  |  | 0.0427 | 0.0427 | 764 | 649 | Yes
2013-06-20 | 0.051839 | 0.051839 |  |  | 0.058728 | 0.058728 |  |  | 0.017629 | 0.017629 | 0.000304 | 0.000304 |  |  | 0.000303 | 0.000303 |  |  | 0.000307 | 0.000307 | 746 | 637 | Yes
2013-06-21 | 0.21468 | 0.21468 |  |  | 0.064103 | 0.064103 |  |  | 0.96498 | 0.96498 | 0.001536 | 0.001536 |  |  | 0.000279 | 0.000279 |  |  | 0.0078 | 0.0078 | 717 | 651 | Yes
2013-06-22 | 0.074911 | 0.074911 |  |  | 0.089785 | 0.089785 |  |  | 0.00098236 | 0.00098236 | 0.000294 | 0.000294 |  |  | 0.000352 | 0.000352 |  |  | 6.68e-06 | 6.68e-06 | 227 | 198 | Yes
2013-06-23 | 0.65508 | 0.65508 |  |  | 0.75679 | 0.75679 |  |  | 0.1498 | 0.1498 | 0.003941 | 0.003941 |  |  | 0.00452 | 0.00452 |  |  | 0.00108 | 0.00108 | 254 | 225 | Yes
2013-06-24 | 1.2089 | 1.2089 |  |  | 0.48884 | 0.48884 |  |  | 4.7971 | 4.7971 | 0.012772 | 0.012772 |  |  | 0.00766 | 0.00766 |  |  | 0.0383 | 0.0383 | 931 | 651 | Yes
2013-06-25 | 0.95784 | 0.95784 |  |  | 0.3397 | 0.3397 |  |  | 4.0381 | 4.0381 | 0.006074 | 0.006074 |  |  | 0.00255 | 0.00255 |  |  | 0.0236 | 0.0236 | 1127 | 853 | Yes
2013-06-26 | 0.082259 | 0.082259 |  |  | 0.02794 | 0.02794 |  |  | 0.35293 | 0.35293 | 0.000313 | 0.000313 |  |  | 0.000176 | 0.000176 |  |  | 0.000996 | 0.000996 | 913 | 716 | Yes
2013-06-27 | 0.082054 | 0.082054 |  |  | 0.093158 | 0.093158 |  |  | 0.026911 | 0.026911 | 0.000608 | 0.000608 |  |  | 0.000631 | 0.000631 |  |  | 0.000495 | 0.000495 | 822 | 626 | Yes
2013-06-28 | 0.15033 | 0.15033 |  |  | 0.17638 | 0.17638 |  |  | 0.02091 | 0.02091 | 0.002039 | 0.002039 |  |  | 0.00242 | 0.00242 |  |  | 0.000167 | 0.000167 | 743 | 584 | Yes
2013-06-29 | 0.2145 | 0.2145 |  |  | 0.040165 | 0.040165 |  |  | 1.0831 | 1.0831 | 0.001279 | 0.001279 |  |  | 0.000172 | 0.000172 |  |  | 0.0068 | 0.0068 | 248 | 235 | Yes
2013-06-30 | 0.06525 | 0.06525 |  |  | 0.026262 | 0.026262 |  |  | 0.25954 | 0.25954 | 0.006982 | 0.006982 |  |  | 0.00244 | 0.00244 |  |  | 0.0296 | 0.0296 | 234 | 213 | Yes
Contents

## 1d. STPIS MED Threshold
Endeavour Energy
STPIS Data Reporting
2012-13 |  |  |  | 2007-07-01
MED Threshold |  |  |  | 2008-07-01
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: MED threshold
MED threshold (timed) year ending 30 June
Alpha - average of Ln(Saidi)
Beta-standard deviation of Ln(SAIDI)
X Beta from the mean
Table 2: MED calculation
Date | Unplanned SAIDI - total (after removing exluded events allowed under clause 3.3(a) of the STPIS) | Total unplanned customer minutes off supply (after removing exluded events allowed under clause 3.3(a) of the STPIS) | Ln (SAIDI)
2007-07-01 | 0.21171 | 178329 | -1.5525
2007-07-02 | 0.082471 | 69469 | -2.4953
2007-07-03 | 0.20769 | 174953 | -1.5717
2007-07-04 | 2.9732 | 2504598 | 1.0896
2007-07-05 | 1.6482 | 1388491 | 0.49968
2007-07-06 | 0.13621 | 114754 | -1.9935
2007-07-07 | 0.10962 | 92357 | -2.2107
2007-07-08 | 0.34149 | 287714 | -1.0744
2007-07-09 | 0.13161 | 110890 | -2.0279
2007-07-10 | 0.035125 | 29595 | -3.3489
2007-07-11 | 0.045055 | 37963 | -3.0999
2007-07-12 | 0.13742 | 115797 | -1.9847
2007-07-13 | 0.034305 | 28907 | -3.3725
2007-07-14 | 0.052006 | 43825 | -2.9564
2007-07-15 | 0.027491 | 23167 | -3.5939
2007-07-16 | 0.22191 | 187016 | -1.5055
2007-07-17 | 0.073626 | 62050 | -2.6088
2007-07-18 | 0.07946 | 66969 | -2.5325
2007-07-19 | 0.096527 | 81356 | -2.3379
2007-07-20 | 0.012114 | 10210 | -4.4134
2007-07-21 | 0.069955 | 58964 | -2.6599
2007-07-22 | 0.1737 | 146418 | -1.7504
2007-07-23 | 0.037615 | 31707 | -3.2804
2007-07-24 | 0.021693 | 18287 | -3.8307
2007-07-25 | 0.14981 | 126288 | -1.8984
2007-07-26 | 0.084475 | 71215 | -2.4713
2007-07-27 | 0.030061 | 25343 | -3.5045
2007-07-28 | 0.034244 | 28871 | -3.3742
2007-07-29 | 0.29439 | 248201 | -1.2229
2007-07-30 | 0.042536 | 35864 | -3.1574
2007-07-31 | 0.00556 | 4688 | -5.1922
2007-08-01 | 0.017775 | 14988 | -4.03
2007-08-02 | 0.033359 | 28129 | -3.4004
2007-08-03 | 0.038537 | 32497 | -3.2561
2007-08-04 | 0.086769 | 73171 | -2.4445
2007-08-05 | 0.0064816 | 5466 | -5.0388
2007-08-06 | 0.12443 | 104934 | -2.084
2007-08-07 | 0.10358 | 87353 | -2.2675
2007-08-08 | 0.11842 | 99873 | -2.1335
2007-08-09 | 0.08598 | 72518 | -2.4536
2007-08-10 | 0.48766 | 411319 | -0.71814
2007-08-11 | 0.13948 | 117648 | -1.9698
2007-08-12 | 0.20636 | 174069 | -1.5781
2007-08-13 | 0.01925 | 16238 | -3.9503
2007-08-14 | 0.028721 | 24228 | -3.5501
2007-08-15 | 0.035968 | 30343 | -3.3251
2007-08-16 | 0.053522 | 45153 | -2.9277
2007-08-17 | 0.11345 | 95712 | -2.1764
2007-08-18 | 0.018074 | 15249 | -4.0133
2007-08-19 | 0.80164 | 676359 | -0.22109
2007-08-20 | 1.1871 | 1001640 | 0.17155
2007-08-21 | 0.018913 | 15958 | -3.9679
2007-08-22 | 0.24754 | 208873 | -1.3962
2007-08-23 | 0.54271 | 457955 | -0.61118
2007-08-24 | 0.0074278 | 6268 | -4.9025
2007-08-25 | 0.0026378 | 2226 | -5.9378
2007-08-26 | 0.023145 | 19532 | -3.766
2007-08-27 | 0.2984 | 251834 | -1.2093
2007-08-28 | 0.23192 | 195733 | -1.4614
2007-08-29 | 0.0069147 | 5836 | -4.9741
2007-08-30 | 0.015991 | 13497 | -4.1357
2007-08-31 | 0.0075741 | 6393 | -4.883
2007-09-01 | 0.01215 | 10256 | -4.4104
2007-09-02 | 0.16558 | 139772 | -1.7983
2007-09-03 | 0.012109 | 10222 | -4.4138
2007-09-04 | 0.064302 | 54282 | -2.7442
2007-09-05 | 0.21566 | 182061 | -1.534
2007-09-06 | 0.01505 | 12706 | -4.1963
2007-09-07 | 0.12229 | 103241 | -2.1014
2007-09-08 | 0.13355 | 112754 | -2.0133
2007-09-09 | 0.092193 | 77840 | -2.3839
2007-09-10 | 0.10783 | 91045 | -2.2272
2007-09-11 | 0.02428 | 20501 | -3.7181
2007-09-12 | 0.026293 | 22202 | -3.6384
2007-09-13 | 0.11729 | 99045 | -2.1431
2007-09-14 | 0.82231 | 694407 | -0.19564
2007-09-15 | 0.10335 | 87281 | -2.2696
2007-09-16 | 0.39963 | 337495 | -0.91721
2007-09-17 | 0.55118 | 465494 | -0.5957
2007-09-18 | 0.0039559 | 3341 | -5.5326
2007-09-19 | 0.058152 | 49115 | -2.8447
2007-09-20 | 0.021772 | 18389 | -3.8271
2007-09-21 | 0.42122 | 355790 | -0.86459
2007-09-22 | 0.027119 | 22907 | -3.6075
2007-09-23 | 0.0032236 | 2723 | -5.7373
2007-09-24 | 0.027549 | 23272 | -3.5918
2007-09-25 | 0.60976 | 515110 | -0.49469
2007-09-26 | 0.023396 | 19765 | -3.7552
2007-09-27 | 0.12595 | 106408 | -2.0719
2007-09-28 | 0.66377 | 560789 | -0.40982
2007-09-29 | 0.059189 | 50008 | -2.827
2007-09-30 | 0.44659 | 377334 | -0.80611
2007-10-01 | 0.2702 | 228307 | -1.3086
2007-10-02 | 0.14975 | 126533 | -1.8988
2007-10-03 | 0.81125 | 685509 | -0.20918
2007-10-04 | 0.044413 | 37530 | -3.1142
2007-10-05 | 0.011972 | 10117 | -4.4252
2007-10-06 | 0.76093 | 643053 | -0.27321
2007-10-07 | 0.091507 | 77334 | -2.3913
2007-10-08 | 0.0053861 | 4552 | -5.2239
2007-10-09 | 0.010668 | 9016 | -4.5405
2007-10-10 | 0.60638 | 512509 | -0.50026
2007-10-11 | 0.0085373 | 7216 | -4.7633
2007-10-12 | 0.1191 | 100671 | -2.1278
2007-10-13 | 0.030327 | 25635 | -3.4957
2007-10-14 | 0.024325 | 20562 | -3.7163
2007-10-15 | 0.36559 | 309051 | -1.0062
2007-10-16 | 1.5449 | 1305978 | 0.43493
2007-10-17 | 0.021773 | 18407 | -3.8271
2007-10-18 | 0.24348 | 205849 | -1.4127
2007-10-19 | 0.26688 | 225637 | -1.321
2007-10-20 | 0.0013424 | 1135 | -6.6133
2007-10-21 | 0.1432 | 121080 | -1.9435
2007-10-22 | 0.22811 | 192878 | -1.4779
2007-10-23 | 0.18645 | 157654 | -1.6796
2007-10-24 | 0.25638 | 216798 | -1.3611
2007-10-25 | 0.41222 | 348584 | -0.8862
2007-10-26 | 1.7101 | 1446174 | 0.53656
2007-10-27 | 0.062419 | 52787 | -2.7739
2007-10-28 | 0.1328 | 112315 | -2.0189
2007-10-29 | 0.22465 | 190000 | -1.4932
2007-10-30 | 0.16296 | 137829 | -1.8142
2007-10-31 | 0.012881 | 10895 | -4.352
2007-11-01 | 0.0055531 | 4697 | -5.1934
2007-11-02 | 0.40109 | 339263 | -0.91358
2007-11-03 | 0.63797 | 539653 | -0.44946
2007-11-04 | 0.36273 | 306839 | -1.0141
2007-11-05 | 0.035112 | 29703 | -3.3492
2007-11-06 | 0.023082 | 19527 | -3.7687
2007-11-07 | 0.10615 | 89800 | -2.2429
2007-11-08 | 0.076798 | 64973 | -2.5666
2007-11-09 | 0.2054 | 173782 | -1.5828
2007-11-10 | 0.051458 | 43538 | -2.967
2007-11-11 | 0.16456 | 139235 | -1.8045
2007-11-12 | 0.0097525 | 8252 | -4.6302
2007-11-13 | 0.012683 | 10732 | -4.3675
2007-11-14 | 0.31139 | 263499 | -1.1667
2007-11-15 | 0.084203 | 71255 | -2.4745
2007-11-16 | 0.049608 | 41981 | -3.0036
2007-11-17 | 0.20322 | 171986 | -1.5934
2007-11-18 | 0.053445 | 45231 | -2.9291
2007-11-19 | 0.28322 | 239703 | -1.2615
2007-11-20 | 0.048798 | 41301 | -3.0201
2007-11-21 | 3.4276 | 2901159 | 1.2319
2007-11-22 | 0.5189 | 439216 | -0.65604
2007-11-23 | 0.10374 | 87809 | -2.2659
2007-11-24 | 0.041885 | 35455 | -3.1728
2007-11-25 | 0.50927 | 431108 | -0.67477
2007-11-26 | 0.078069 | 66089 | -2.5502
2007-11-27 | 0.25649 | 217141 | -1.3606
2007-11-28 | 0.5454 | 461737 | -0.60623
2007-11-29 | 0.068313 | 57836 | -2.6837
2007-11-30 | 2.0351 | 1723066 | 0.71056
2007-12-01 | 0.086906 | 73582 | -2.4429
2007-12-02 | 0.38178 | 323259 | -0.96291
2007-12-03 | 2.9903 | 2531986 | 1.0954
2007-12-04 | 1.7831 | 1509888 | 0.57836
2007-12-05 | 0.3448 | 291976 | -1.0648
2007-12-06 | 1.2718 | 1077038 | 0.24047
2007-12-07 | 2.318 | 1963017 | 0.84071
2007-12-08 | 0.11607 | 98301 | -2.1535
2007-12-09 | 6.4468 | 5459849 | 1.8636
2007-12-10 | 0.20798 | 176147 | -1.5703
2007-12-11 | 0.0037841 | 3205 | -5.577
2007-12-12 | 0.034482 | 29206 | -3.3673
2007-12-13 | 0.021038 | 17820 | -3.8614
2007-12-14 | 0.71651 | 606922 | -0.33337
2007-12-15 | 0.53295 | 451456 | -0.62932
2007-12-16 | 0.1706 | 144519 | -1.7684
2007-12-17 | 0.25178 | 213290 | -1.3792
2007-12-18 | 0.19895 | 168548 | -1.6147
2007-12-19 | 0.093694 | 79378 | -2.3677
2007-12-20 | 0.013615 | 11535 | -4.2966
2007-12-21 | 0.36683 | 310803 | -1.0028
2007-12-22 | 0.66842 | 566347 | -0.40283
2007-12-23 | 0.11599 | 98277 | -2.1543
2007-12-24 | 2.0117 | 1704595 | 0.69898
2007-12-25 | 0.18609 | 157686 | -1.6815
2007-12-26 | 0.10328 | 87518 | -2.2703
2007-12-27 | 0.88177 | 747235 | -0.12583
2007-12-28 | 0.18295 | 155044 | -1.6985
2007-12-29 | 0.20714 | 175550 | -1.5744
2007-12-30 | 0.057513 | 48743 | -2.8557
2007-12-31 | 0.089833 | 76137 | -2.4098
2008-01-01 | 0.041368 | 35062 | -3.1853
2008-01-02 | 0.0078091 | 6619 | -4.8525
2008-01-03 | 0.50769 | 430331 | -0.67789
2008-01-04 | 0.041609 | 35270 | -3.1794
2008-01-05 | 0.17212 | 145903 | -1.7596
2008-01-06 | 0.77161 | 654104 | -0.25928
2008-01-07 | 0.023546 | 19961 | -3.7488
2008-01-08 | 0.14281 | 121073 | -1.9462
2008-01-09 | 3.0474 | 2583570 | 1.1143
2008-01-10 | 0.018665 | 15825 | -3.9811
2008-01-11 | 0.22521 | 190945 | -1.4907
2008-01-12 | 0.70118 | 594519 | -0.35499
2008-01-13 | 7.4734 | 6336768 | 2.0113
2008-01-14 | 0.2196 | 186206 | -1.516
2008-01-15 | 0.3773 | 319937 | -0.97472
2008-01-16 | 7.4495 | 6317205 | 2.0082
2008-01-17 | 0.21979 | 186392 | -1.5151
2008-01-18 | 0.097217 | 82446 | -2.3308
2008-01-19 | 0.38193 | 323908 | -0.96252
2008-01-20 | 0.59176 | 501884 | -0.52465
2008-01-21 | 0.0048341 | 4100 | -5.3321
2008-01-22 | 0.21143 | 179331 | -1.5538
2008-01-23 | 0.023769 | 20161 | -3.7394
2008-01-24 | 0.12916 | 109554 | -2.0467
2008-01-25 | 0.25345 | 214989 | -1.3726
2008-01-26 | 0.05882 | 49896 | -2.8333
2008-01-27 | 0.11785 | 99977 | -2.1383
2008-01-28 | 0.11397 | 96683 | -2.1718
2008-01-29 | 0.12658 | 107391 | -2.0668
2008-01-30 | 4.1151 | 3491210 | 1.4147
2008-01-31 | 9.9346 | 8428794 | 2.296
2008-02-01 | 0.6571 | 557523 | -0.41992
2008-02-02 | 0.39254 | 333063 | -0.93512
2008-02-03 | 0.17095 | 145057 | -1.7664
2008-02-04 | 0.29703 | 252043 | -1.2139
2008-02-05 | 0.62828 | 533140 | -0.46477
2008-02-06 | 1.3331 | 1131278 | 0.28751
2008-02-07 | 0.75059 | 636971 | -0.2869
2008-02-08 | 0.4375 | 371289 | -0.82667
2008-02-09 | 0.30849 | 261811 | -1.1761
2008-02-10 | 0.094669 | 80347 | -2.3574
2008-02-11 | 0.29182 | 247678 | -1.2316
2008-02-12 | 0.0172 | 14599 | -4.0628
2008-02-13 | 0.4142 | 351575 | -0.8814
2008-02-14 | 0.016749 | 14217 | -4.0894
2008-02-15 | 0.23252 | 197375 | -1.4588
2008-02-16 | 0.04353 | 36952 | -3.1343
2008-02-17 | 0.012779 | 10848 | -4.36
2008-02-18 | 0.85265 | 723854 | -0.1594
2008-02-19 | 0.090892 | 77165 | -2.3981
2008-02-20 | 0.32616 | 276910 | -1.1204
2008-02-21 | 0.23387 | 198559 | -1.453
2008-02-22 | 0.21247 | 180397 | -1.549
2008-02-23 | 0.62399 | 529821 | -0.47162
2008-02-24 | 0.21857 | 185595 | -1.5206
2008-02-25 | 0.14454 | 122737 | -1.9342
2008-02-26 | 1.6302 | 1384339 | 0.48872
2008-02-27 | 1.2145 | 1031380 | 0.19436
2008-02-28 | 0.42513 | 361033 | -0.85536
2008-02-29 | 0.20135 | 171002 | -1.6027
2008-03-01 | 0.25275 | 214654 | -1.3754
2008-03-02 | 0.026828 | 22785 | -3.6183
2008-03-03 | 0.3753 | 318762 | -0.98002
2008-03-04 | 0.1459 | 123920 | -1.9249
2008-03-05 | 0.039834 | 33835 | -3.223
2008-03-06 | 0.16604 | 141037 | -1.7955
2008-03-07 | 0.42252 | 358913 | -0.86152
2008-03-08 | 0.062492 | 53086 | -2.7727
2008-03-09 | 0.082193 | 69824 | -2.4987
2008-03-10 | 0.19283 | 163817 | -1.6459
2008-03-11 | 0.52239 | 443812 | -0.64933
2008-03-12 | 0.041644 | 35381 | -3.1786
2008-03-13 | 0.0068971 | 5860 | -4.9767
2008-03-14 | 0.01341 | 11394 | -4.3117
2008-03-15 | 0.0032047 | 2723 | -5.7431
2008-03-16 | 0.15965 | 135655 | -1.8348
2008-03-17 | 0.13924 | 118319 | -1.9715
2008-03-18 | 0.35532 | 301945 | -1.0347
2008-03-19 | 0.12515 | 106356 | -2.0782
2008-03-20 | 0.22686 | 192791 | -1.4834
2008-03-21 | 0.042537 | 36150 | -3.1574
2008-03-22 | 0.27612 | 234668 | -1.2869
2008-03-23 | 0.092206 | 78367 | -2.3837
2008-03-24 | 0.93128 | 791531 | -0.0712
2008-03-25 | 0.059903 | 50916 | -2.815
2008-03-26 | 0.080971 | 68825 | -2.5137
2008-03-27 | 0.02776 | 23597 | -3.5842
2008-03-28 | 0.081498 | 69278 | -2.5072
2008-03-29 | 0.028474 | 24205 | -3.5588
2008-03-30 | 0.53713 | 456623 | -0.62151
2008-03-31 | 0.042856 | 36434 | -3.1499
2008-04-01 | 0.16866 | 143386 | -1.7799
2008-04-02 | 0.5808 | 493796 | -0.54335
2008-04-03 | 0.26002 | 221077 | -1.347
2008-04-04 | 0.13112 | 111485 | -2.0316
2008-04-05 | 0.015354 | 13055 | -4.1764
2008-04-06 | 0.051622 | 43895 | -2.9638
2008-04-07 | 0.091525 | 77828 | -2.3911
2008-04-08 | 0.40776 | 346748 | -0.89708
2008-04-09 | 0.26062 | 221628 | -1.3447
2008-04-10 | 0.53447 | 454528 | -0.62648
2008-04-11 | 0.020757 | 17653 | -3.8749
2008-04-12 | 0.20654 | 175658 | -1.5773
2008-04-13 | 0.74951 | 637465 | -0.28834
2008-04-14 | 0.094429 | 80316 | -2.3599
2008-04-15 | 0.14051 | 119510 | -1.9625
2008-04-16 | 0.2054 | 174717 | -1.5828
2008-04-17 | 0.0089863 | 7644 | -4.7121
2008-04-18 | 0.40505 | 344562 | -0.90374
2008-04-19 | 0.40153 | 341574 | -0.91248
2008-04-20 | 0.16846 | 143314 | -1.781
2008-04-21 | 0.23828 | 202714 | -1.4343
2008-04-22 | 0.0053034 | 4512 | -5.2394
2008-04-23 | 0.0076963 | 6548 | -4.867
2008-04-24 | 0.41266 | 351103 | -0.88513
2008-04-25 | 0.27328 | 232522 | -1.2973
2008-04-26 | 0.49711 | 422984 | -0.69894
2008-04-27 | 1.0241 | 871410 | 0.023801
2008-04-28 | 0.10965 | 93308 | -2.2104
2008-04-29 | 0.006811 | 5796 | -4.9892
2008-04-30 | 0.011989 | 10203 | -4.4237
2008-05-01 | 0.22245 | 189313 | -1.503
2008-05-02 | 0.02092 | 17804 | -3.8671
2008-05-03 | 0.29173 | 248286 | -1.2319
2008-05-04 | 0.011278 | 9599 | -4.4849
2008-05-05 | 0.013999 | 11915 | -4.2688
2008-05-06 | 0.34832 | 296482 | -1.0546
2008-05-07 | 0.0026339 | 2242 | -5.9393
2008-05-08 | 0.0072284 | 6153 | -4.9297
2008-05-09 | 0.016592 | 14124 | -4.0988
2008-05-10 | 0.092756 | 78962 | -2.3778
2008-05-11 | 0.00085045 | 724 | -7.0697
2008-05-12 | 0.026968 | 22959 | -3.6131
2008-05-13 | 0.51789 | 440920 | -0.65799
2008-05-14 | 0.042336 | 36045 | -3.1621
2008-05-15 | 0.10768 | 91682 | -2.2286
2008-05-16 | 0.02894 | 24641 | -3.5425
2008-05-17 | 0.0633 | 53899 | -2.7599
2008-05-18 | 0.025329 | 21568 | -3.6758
2008-05-19 | 0.10139 | 86337 | -2.2888
2008-05-20 | 0.32812 | 279415 | -1.1144
2008-05-21 | 0.10438 | 88892 | -2.2597
2008-05-22 | 0.033754 | 28746 | -3.3887
2008-05-23 | 0.011385 | 9696 | -4.4755
2008-05-24 | 0.029021 | 24717 | -3.5397
2008-05-25 | 0.26421 | 225032 | -1.331
2008-05-26 | 0.076469 | 65132 | -2.5709
2008-05-27 | 0.0050929 | 4338 | -5.2799
2008-05-28 | 0.51299 | 436964 | -0.6675
2008-05-29 | 0.072793 | 62007 | -2.6201
2008-05-30 | 0.0048048 | 4093 | -5.3381
2008-05-31 | 0.029526 | 25153 | -3.5225
2008-06-01 | 0.13456 | 114633 | -2.0058
2008-06-02 | 0.10739 | 91489 | -2.2313
2008-06-03 | 0.42677 | 363595 | -0.85151
2008-06-04 | 0.090345 | 76974 | -2.4041
2008-06-05 | 0.63277 | 539140 | -0.45764
2008-06-06 | 0.1376 | 117241 | -1.9834
2008-06-07 | 0.0050124 | 4271 | -5.2958
2008-06-08 | 0.0055239 | 4707 | -5.1987
2008-06-09 | 0.3673 | 312993 | -1.0016
2008-06-10 | 0.045122 | 38452 | -3.0984
2008-06-11 | 0.016806 | 14322 | -4.086
2008-06-12 | 0.14712 | 125381 | -1.9165
2008-06-13 | 0.028724 | 24480 | -3.55
2008-06-14 | 0.056576 | 48219 | -2.8722
2008-06-15 | 0.0059133 | 5040 | -5.1305
2008-06-16 | 0.005391 | 4595 | -5.223
2008-06-17 | 0.34168 | 291236 | -1.0739
2008-06-18 | 0.082179 | 70049 | -2.4989
2008-06-19 | 0.011555 | 9850 | -4.4606
2008-06-20 | 0.022009 | 18762 | -3.8163
2008-06-21 | 0.0066347 | 5656 | -5.0154
2008-06-22 | 0.027767 | 23672 | -3.5839
2008-06-23 | 0.010029 | 8550 | -4.6023
2008-06-24 | 0.011393 | 9713 | -4.4748
2008-06-25 | 0.012374 | 10550 | -4.3922
2008-06-26 | 2.8117 | 2397374 | 1.0338
2008-06-27 | 0.060525 | 51607 | -2.8047
2008-06-28 | 0.011554 | 9852 | -4.4607
2008-06-29 | 0.12661 | 107962 | -2.0666
2008-06-30 | 0.52115 | 444405 | -0.65172
2008-07-01 | 1.7743 | 1514034 | 0.57339
2008-07-02 | 1.5005 | 1280452 | 0.40581
2008-07-03 | 0.037197 | 31742 | -3.2915
2008-07-04 | 0.014645 | 12498 | -4.2236
2008-07-05 | 0.0070332 | 6002 | -4.9571
2008-07-06 | 0.075926 | 64795 | -2.578
2008-07-07 | 0.0067002 | 5718 | -5.0056
2008-07-08 | 0.10956 | 93503 | -2.2113
2008-07-09 | 0.020557 | 17544 | -3.8846
2008-07-10 | 0.60208 | 513850 | -0.50736
2008-07-11 | 1.0533 | 898954 | 0.051921
2008-07-12 | 0.01131 | 9653 | -4.4821
2008-07-13 | 0.026299 | 22446 | -3.6382
2008-07-14 | 0.19431 | 165850 | -1.6383
2008-07-15 | 0.025672 | 21912 | -3.6623
2008-07-16 | 0.0077934 | 6652 | -4.8545
2008-07-17 | 0.048421 | 41330 | -3.0278
2008-07-18 | 0.51328 | 438124 | -0.66693
2008-07-19 | 0.021994 | 18774 | -3.817
2008-07-20 | 0.093851 | 80111 | -2.366
2008-07-21 | 0.15001 | 128051 | -1.897
2008-07-22 | 0.02708 | 23116 | -3.609
2008-07-23 | 0.024412 | 20839 | -3.7127
2008-07-24 | 0.15261 | 130278 | -1.8799
2008-07-25 | 0.0062448 | 5331 | -5.076
2008-07-26 | 0.027175 | 23199 | -3.6055
2008-07-27 | 0.048468 | 41377 | -3.0269
2008-07-28 | 0.21436 | 183000 | -1.5401
2008-07-29 | 0.0087077 | 7434 | -4.7435
2008-07-30 | 0.12186 | 104035 | -2.1049
2008-07-31 | 0.15451 | 131918 | -1.8675
2008-08-01 | 14.2499 | 12166109 | 2.6567
2008-08-02 | 4.0617 | 3467826 | 1.4016
2008-08-03 | 0.14642 | 125011 | -1.9213
2008-08-04 | 0.11667 | 99612 | -2.1484
2008-08-05 | 0.17324 | 147918 | -1.7531
2008-08-06 | 0.30473 | 260193 | -1.1883
2008-08-07 | 0.38206 | 326228 | -0.96217
2008-08-08 | 0.30175 | 257651 | -1.1982
2008-08-09 | 0.13847 | 118241 | -1.9771
2008-08-10 | 0.043715 | 37328 | -3.1301
2008-08-11 | 0.30986 | 264596 | -1.1716
2008-08-12 | 0.2632 | 224752 | -1.3348
2008-08-13 | 0.011736 | 10022 | -4.4451
2008-08-14 | 0.040328 | 34438 | -3.2107
2008-08-15 | 0.013259 | 11323 | -4.3231
2008-08-16 | 0.055692 | 47560 | -2.8879
2008-08-17 | 0.0012482 | 1066 | -6.686
2008-08-18 | 0.013609 | 11622 | -4.297
2008-08-19 | 0.12884 | 110029 | -2.0492
2008-08-20 | 0.001507 | 1287 | -6.4977
2008-08-21 | 0.097379 | 83167 | -2.3291
2008-08-22 | 0.032234 | 27530 | -3.4347
2008-08-23 | 0.094918 | 81068 | -2.3547
2008-08-24 | 0.028967 | 24741 | -3.5416
2008-08-25 | 0.16859 | 143998 | -1.7803
2008-08-26 | 0.0062719 | 5357 | -5.0717
2008-08-27 | 0.013453 | 11491 | -4.3085
2008-08-28 | 0.27841 | 237805 | -1.2787
2008-08-29 | 0.032615 | 27859 | -3.423
2008-08-30 | 0.01587 | 13556 | -4.1433
2008-08-31 | 0.11473 | 98004 | -2.1652
2008-09-01 | 0.017339 | 14811 | -4.0548
2008-09-02 | 0.0081384 | 6952 | -4.8112
2008-09-03 | 0.026947 | 23019 | -3.6139
2008-09-04 | 0.10087 | 86169 | -2.2939
2008-09-05 | 0.32952 | 281501 | -1.1101
2008-09-06 | 0.040695 | 34765 | -3.2017
2008-09-07 | 0.020555 | 17560 | -3.8847
2008-09-08 | 0.17342 | 148154 | -1.752
2008-09-09 | 0.067641 | 57787 | -2.6935
2008-09-10 | 1.3973 | 1193805 | 0.33457
2008-09-11 | 0.035715 | 30513 | -3.3322
2008-09-12 | 0.022119 | 18898 | -3.8113
2008-09-13 | 0.17725 | 151440 | -1.7302
2008-09-14 | 0.82873 | 708066 | -0.18786
2008-09-15 | 0.37316 | 318833 | -0.98574
2008-09-16 | 0.16042 | 137069 | -1.8299
2008-09-17 | 0.13731 | 117323 | -1.9855
2008-09-18 | 0.012899 | 11022 | -4.3506
2008-09-19 | 0.31801 | 271733 | -1.1457
2008-09-20 | 0.17381 | 148520 | -1.7498
2008-09-21 | 0.0015834 | 1353 | -6.4482
2008-09-22 | 0.15152 | 129478 | -1.887
2008-09-23 | 0.27335 | 233581 | -1.297
2008-09-24 | 0.028868 | 24669 | -3.545
2008-09-25 | 0.059371 | 50736 | -2.8239
2008-09-26 | 0.0020572 | 1758 | -6.1864
2008-09-27 | 0.0089927 | 7685 | -4.7113
2008-09-28 | 0.20456 | 174815 | -1.5869
2008-09-29 | 0.010226 | 8739 | -4.5828
2008-09-30 | 0.33304 | 284625 | -1.0995
2008-10-01 | 0.077595 | 66316 | -2.5562
2008-10-02 | 0.31242 | 267014 | -1.1634
2008-10-03 | 0.1926 | 164609 | -1.6471
2008-10-04 | 0.019768 | 16895 | -3.9237
2008-10-05 | 0.20077 | 171597 | -1.6056
2008-10-06 | 1.7983 | 1537021 | 0.58684
2008-10-07 | 0.10062 | 86005 | -2.2964
2008-10-08 | 0.0080235 | 6858 | -4.8254
2008-10-09 | 0.026776 | 22887 | -3.6202
2008-10-10 | 0.11556 | 98777 | -2.158
2008-10-11 | 0.12889 | 110177 | -2.0488
2008-10-12 | 0.013796 | 11793 | -4.2834
2008-10-13 | 0.12642 | 108063 | -2.0682
2008-10-14 | 0.32651 | 279110 | -1.1193
2008-10-15 | 0.0085034 | 7269 | -4.7673
2008-10-16 | 0.31408 | 268493 | -1.1581
2008-10-17 | 0.21101 | 180385 | -1.5559
2008-10-18 | 0.01473 | 12592 | -4.2179
2008-10-19 | 0.11391 | 97382 | -2.1723
2008-10-20 | 0.17128 | 146432 | -1.7644
2008-10-21 | 0.0012656 | 1082 | -6.6722
2008-10-22 | 0.90098 | 770280 | -0.10427
2008-10-23 | 0.0080613 | 6892 | -4.8207
2008-10-24 | 0.082137 | 70224 | -2.4994
2008-10-25 | 0.013244 | 11323 | -4.3242
2008-10-26 | 0.035564 | 30407 | -3.3364
2008-10-27 | 0.080458 | 68792 | -2.52
2008-10-28 | 0.010699 | 9148 | -4.5376
2008-10-29 | 0.47555 | 406610 | -0.74329
2008-10-30 | 0.046757 | 39980 | -3.0628
2008-10-31 | 0.76858 | 657188 | -0.26321
2008-11-01 | 0.40012 | 342134 | -0.91599
2008-11-02 | 0.0051889 | 4437 | -5.2612
2008-11-03 | 0.47287 | 404353 | -0.74894
2008-11-04 | 0.024954 | 21339 | -3.6907
2008-11-05 | 0.012387 | 10593 | -4.3911
2008-11-06 | 0.0056224 | 4808 | -5.181
2008-11-07 | 0.060124 | 51416 | -2.8113
2008-11-08 | 0.0074932 | 6408 | -4.8938
2008-11-09 | 0.014018 | 11988 | -4.2674
2008-11-10 | 0.33101 | 283083 | -1.1056
2008-11-11 | 0.033673 | 28798 | -3.3911
2008-11-12 | 0.031256 | 26731 | -3.4656
2008-11-13 | 0.046517 | 39784 | -3.0679
2008-11-14 | 2.3147 | 1979679 | 0.83928
2008-11-15 | 0.1062 | 90832 | -2.2424
2008-11-16 | 0.41447 | 354495 | -0.88075
2008-11-17 | 0.031549 | 26984 | -3.4562
2008-11-18 | 0.010969 | 9382 | -4.5127
2008-11-19 | 1.1034 | 943816 | 0.098436
2008-11-20 | 0.27613 | 236186 | -1.2869
2008-11-21 | 0.048034 | 41087 | -3.0358
2008-11-22 | 1.117 | 955475 | 0.11066
2008-11-23 | 1.6804 | 1437401 | 0.51903
2008-11-24 | 0.019061 | 16305 | -3.9601
2008-11-25 | 0.026168 | 22385 | -3.6432
2008-11-26 | 0.019093 | 16333 | -3.9584
2008-11-27 | 0.10353 | 88563 | -2.2679
2008-11-28 | 0.32304 | 276346 | -1.13
2008-11-29 | 0.89956 | 769554 | -0.10585
2008-11-30 | 0.013299 | 11377 | -4.3201
2008-12-01 | 0.19749 | 168950 | -1.6221
2008-12-02 | 0.17222 | 147336 | -1.759
2008-12-03 | 0.22437 | 191957 | -1.4945
2008-12-04 | 0.24092 | 206115 | -1.4233
2008-12-05 | 0.097995 | 83841 | -2.3228
2008-12-06 | 0.1442 | 123376 | -1.9365
2008-12-07 | 0.88939 | 760958 | -0.11722
2008-12-08 | 0.16277 | 139267 | -1.8154
2008-12-09 | 0.12608 | 107880 | -2.0708
2008-12-10 | 0.12186 | 104267 | -2.1049
2008-12-11 | 0.005279 | 4517 | -5.244
2008-12-12 | 0.34086 | 291666 | -1.0763
2008-12-13 | 3.6589 | 3130806 | 1.2972
2008-12-14 | 0.79699 | 681978 | -0.22691
2008-12-15 | 0.037464 | 32058 | -3.2844
2008-12-16 | 0.040942 | 35035 | -3.1956
2008-12-17 | 0.16308 | 139553 | -1.8135
2008-12-18 | 0.27945 | 239143 | -1.2749
2008-12-19 | 0.29011 | 248263 | -1.2375
2008-12-20 | 0.21671 | 185459 | -1.5292
2008-12-21 | 0.037536 | 32123 | -3.2825
2008-12-22 | 0.26568 | 227375 | -1.3254
2008-12-23 | 0.0049204 | 4211 | -5.3144
2008-12-24 | 0.22187 | 189881 | -1.5057
2008-12-25 | 0.15305 | 130992 | -1.877
2008-12-26 | 0.029215 | 25004 | -3.5331
2008-12-27 | 1.0962 | 938175 | 0.091808
2008-12-28 | 0.19673 | 168381 | -1.6259
2008-12-29 | 0.49239 | 421436 | -0.70849
2008-12-30 | 0.2044 | 174946 | -1.5877
2008-12-31 | 0.10473 | 89638 | -2.2564
2009-01-01 | 0.021157 | 18109 | -3.8558
2009-01-02 | 0.009338 | 7993 | -4.6737
2009-01-03 | 0.077045 | 65949 | -2.5634
2009-01-04 | 0.14192 | 121482 | -1.9525
2009-01-05 | 0.13939 | 119319 | -1.9705
2009-01-06 | 0.73574 | 629805 | -0.30688
2009-01-07 | 0.6446 | 551796 | -0.43913
2009-01-08 | 0.32073 | 274564 | -1.1371
2009-01-09 | 0.016294 | 13949 | -4.1169
2009-01-10 | 0.009783 | 8375 | -4.6271
2009-01-11 | 0.73973 | 633280 | -0.30146
2009-01-12 | 0.11499 | 98443 | -2.1629
2009-01-13 | 0.30292 | 259340 | -1.1943
2009-01-14 | 0.55374 | 474074 | -0.59106
2009-01-15 | 0.8831 | 756067 | -0.12431
2009-01-16 | 0.15868 | 135855 | -1.8409
2009-01-17 | 0.034628 | 29648 | -3.3631
2009-01-18 | 0.018671 | 15986 | -3.9808
2009-01-19 | 0.0097687 | 8364 | -4.6286
2009-01-20 | 0.3714 | 318001 | -0.99047
2009-01-21 | 0.93738 | 802621 | -0.064661
2009-01-22 | 0.042227 | 36157 | -3.1647
2009-01-23 | 0.43895 | 375857 | -0.82337
2009-01-24 | 1.5738 | 1347576 | 0.45347
2009-01-25 | 0.29489 | 252511 | -1.2212
2009-01-26 | 0.38043 | 325762 | -0.96646
2009-01-27 | 0.5124 | 438782 | -0.66864
2009-01-28 | 0.20557 | 176038 | -1.582
2009-01-29 | 0.17912 | 153391 | -1.7197
2009-01-30 | 0.094182 | 80654 | -2.3625
2009-01-31 | 0.075466 | 64627 | -2.5841
2009-02-01 | 0.23242 | 199043 | -1.4592
2009-02-02 | 0.35688 | 305632 | -1.0304
2009-02-03 | 0.012534 | 10734 | -4.3793
2009-02-04 | 0.13127 | 112424 | -2.0305
2009-02-05 | 0.46376 | 397186 | -0.76839
2009-02-06 | 1.341 | 1148521 | 0.29342
2009-02-07 | 0.52001 | 445378 | -0.6539
2009-02-08 | 0.72867 | 624102 | -0.31653
2009-02-09 | 0.46315 | 396691 | -0.7697
2009-02-10 | 0.20475 | 175373 | -1.586
2009-02-11 | 0.29271 | 250713 | -1.2286
2009-02-12 | 0.04541 | 38896 | -3.092
2009-02-13 | 0.10318 | 88380 | -2.2713
2009-02-14 | 0.12214 | 104620 | -2.1026
2009-02-15 | 0.12569 | 107664 | -2.0739
2009-02-16 | 0.043391 | 37169 | -3.1375
2009-02-17 | 0.17762 | 152154 | -1.7281
2009-02-18 | 0.094885 | 81282 | -2.3551
2009-02-19 | 0.64125 | 549327 | -0.44433
2009-02-20 | 0.21037 | 180213 | -1.5589
2009-02-21 | 0.21276 | 182264 | -1.5476
2009-02-22 | 0.30403 | 260456 | -1.1906
2009-02-23 | 2.5498 | 2184435 | 0.93602
2009-02-24 | 0.22111 | 189427 | -1.5091
2009-02-25 | 0.21837 | 187084 | -1.5216
2009-02-26 | 0.021283 | 18234 | -3.8499
2009-02-27 | 0.017639 | 15112 | -4.0377
2009-02-28 | 0.43835 | 375571 | -0.82473
2009-03-01 | 0.074339 | 63693 | -2.5991
2009-03-02 | 0.16204 | 138833 | -1.8199
2009-03-03 | 0.078541 | 67295 | -2.5441
2009-03-04 | 0.17735 | 151963 | -1.7296
2009-03-05 | 0.030231 | 25903 | -3.4989
2009-03-06 | 0.24086 | 206382 | -1.4235
2009-03-07 | 0.18758 | 160729 | -1.6736
2009-03-08 | 0.2821 | 241727 | -1.2655
2009-03-09 | 0.072145 | 61821 | -2.6291
2009-03-10 | 0.25743 | 220599 | -1.357
2009-03-11 | 0.13227 | 113346 | -2.0229
2009-03-12 | 0.20494 | 175621 | -1.585
2009-03-13 | 0.029257 | 25072 | -3.5316
2009-03-14 | 1.1753 | 1007195 | 0.16152
2009-03-15 | 0.073946 | 63371 | -2.6044
2009-03-16 | 0.077745 | 66628 | -2.5543
2009-03-17 | 0.027064 | 23194 | -3.6096
2009-03-18 | 0.14442 | 123774 | -1.935
2009-03-19 | 0.43486 | 372695 | -0.83273
2009-03-20 | 0.65361 | 560184 | -0.42524
2009-03-21 | 0.0455 | 38997 | -3.09
2009-03-22 | 1.2119 | 1038745 | 0.19223
2009-03-23 | 0.46439 | 398027 | -0.76704
2009-03-24 | 0.091952 | 78814 | -2.3865
2009-03-25 | 2.8806 | 2469058 | 1.058
2009-03-26 | 0.25682 | 220134 | -1.3594
2009-03-27 | 0.14668 | 125727 | -1.9195
2009-03-28 | 0.014041 | 12036 | -4.2657
2009-03-29 | 0.42312 | 362696 | -0.86009
2009-03-30 | 0.014471 | 12405 | -4.2356
2009-03-31 | 0.26126 | 223954 | -1.3423
2009-04-01 | 0.70465 | 604048 | -0.35005
2009-04-02 | 0.23498 | 201436 | -1.4483
2009-04-03 | 0.22689 | 194503 | -1.4833
2009-04-04 | 0.013674 | 11722 | -4.2923
2009-04-05 | 0.044475 | 38128 | -3.1128
2009-04-06 | 0.13188 | 113060 | -2.0259
2009-04-07 | 0.18473 | 158369 | -1.6889
2009-04-08 | 0.30996 | 265742 | -1.1713
2009-04-09 | 0.0071336 | 6116 | -4.9429
2009-04-10 | 0.0085378 | 7320 | -4.7632
2009-04-11 | 0.16579 | 142143 | -1.797
2009-04-12 | 0.057784 | 49543 | -2.851
2009-04-13 | 0.27943 | 239588 | -1.275
2009-04-14 | 0.40709 | 349047 | -0.89872
2009-04-15 | 0.20725 | 177700 | -1.5738
2009-04-16 | 0.062287 | 53408 | -2.776
2009-04-17 | 0.0039069 | 3350 | -5.545
2009-04-18 | 0.34282 | 293955 | -1.0706
2009-04-19 | 0.5017 | 430202 | -0.68975
2009-04-20 | 0.23436 | 200967 | -1.4509
2009-04-21 | 0.37729 | 323532 | -0.97474
2009-04-22 | 0.1609 | 137978 | -1.827
2009-04-23 | 0.32872 | 281893 | -1.1125
2009-04-24 | 0.053044 | 45488 | -2.9366
2009-04-25 | 0.34247 | 293693 | -1.0716
2009-04-26 | 2.6984 | 2314150 | 0.99267
2009-04-27 | 0.16123 | 138270 | -1.8249
2009-04-28 | 0.67529 | 579138 | -0.39262
2009-04-29 | 0.010219 | 8764 | -4.5835
2009-04-30 | 0.028072 | 24076 | -3.573
2009-05-01 | 0.080399 | 68955 | -2.5208
2009-05-02 | 0.085824 | 73609 | -2.4555
2009-05-03 | 0.079662 | 68325 | -2.53
2009-05-04 | 0.049574 | 42520 | -3.0043
2009-05-05 | 0.099752 | 85559 | -2.3051
2009-05-06 | 0.016067 | 13781 | -4.131
2009-05-07 | 0.07626 | 65412 | -2.5736
2009-05-08 | 0.010131 | 8690 | -4.5921
2009-05-09 | 0.019441 | 16676 | -3.9404
2009-05-10 | 0.23971 | 205617 | -1.4283
2009-05-11 | 0.020639 | 17704 | -3.8806
2009-05-12 | 0.64074 | 549638 | -0.44513
2009-05-13 | 0.010942 | 9386 | -4.5152
2009-05-14 | 0.018348 | 15740 | -3.9982
2009-05-15 | 0.59063 | 506675 | -0.52657
2009-05-16 | 1.5272 | 1310135 | 0.42343
2009-05-17 | 0.015578 | 13364 | -4.1619
2009-05-18 | 0.14427 | 123770 | -1.9361
2009-05-19 | 0.31576 | 270892 | -1.1528
2009-05-20 | 0.051435 | 44128 | -2.9674
2009-05-21 | 0.32825 | 281623 | -1.114
2009-05-22 | 0.97718 | 838376 | -0.023089
2009-05-23 | 0.11832 | 101515 | -2.1344
2009-05-24 | 0.090818 | 77921 | -2.3989
2009-05-25 | 0.039748 | 34104 | -3.2252
2009-05-26 | 0.23689 | 203254 | -1.4402
2009-05-27 | 0.13707 | 117608 | -1.9873
2009-05-28 | 0.015574 | 13363 | -4.1622
2009-05-29 | 0.075179 | 64508 | -2.5879
2009-05-30 | 0.12438 | 106731 | -2.0844
2009-05-31 | 0.0092998 | 7980 | -4.6778
2009-06-01 | 0.19208 | 164821 | -1.6499
2009-06-02 | 0.16217 | 139161 | -1.8191
2009-06-03 | 0.58159 | 499079 | -0.54199
2009-06-04 | 0.17342 | 148817 | -1.7521
2009-06-05 | 0.027066 | 23227 | -3.6095
2009-06-06 | 0.019649 | 16862 | -3.9297
2009-06-07 | 0.45018 | 386341 | -0.7981
2009-06-08 | 0.0017245 | 1480 | -6.3628
2009-06-09 | 0.040457 | 34721 | -3.2075
2009-06-10 | 0.11872 | 101893 | -2.1309
2009-06-11 | 0.0081177 | 6967 | -4.8137
2009-06-12 | 0.027896 | 23942 | -3.5793
2009-06-13 | 0.14323 | 122930 | -1.9433
2009-06-14 | 0.054545 | 46815 | -2.9087
2009-06-15 | 0.19504 | 167402 | -1.6346
2009-06-16 | 0.1921 | 164879 | -1.6498
2009-06-17 | 0.027413 | 23529 | -3.5968
2009-06-18 | 0.025019 | 21475 | -3.6881
2009-06-19 | 0.25943 | 222687 | -1.3493
2009-06-20 | 0.06102 | 52378 | -2.7966
2009-06-21 | 0.2744 | 235539 | -1.2932
2009-06-22 | 0.092726 | 79596 | -2.3781
2009-06-23 | 0.018454 | 15841 | -3.9925
2009-06-24 | 0.15224 | 130689 | -1.8823
2009-06-25 | 0.045614 | 39157 | -3.0875
2009-06-26 | 0.062067 | 53282 | -2.7795
2009-06-27 | 0.002388 | 2050 | -6.0373
2009-06-28 | 0.012305 | 10564 | -4.3977
2009-06-29 | 0.060705 | 52115 | -2.8017
2009-06-30 | 0.10473 | 89910 | -2.2564
2009-07-01 | 0.28278 | 243114 | -1.2631
2009-07-02 | 0.20048 | 172364 | -1.607
2009-07-03 | 0.2101 | 180635 | -1.5602
2009-07-04 | 0.18491 | 158984 | -1.6879
2009-07-05 | 0.071009 | 61053 | -2.6449
2009-07-06 | 0.038571 | 33164 | -3.2552
2009-07-07 | 0.72059 | 619587 | -0.32768
2009-07-08 | 0.82127 | 706169 | -0.1969
2009-07-09 | 0.14938 | 128450 | -1.9012
2009-07-10 | 0.10871 | 93480 | -2.2191
2009-07-11 | 0.08764 | 75362 | -2.4345
2009-07-12 | 0.041542 | 35723 | -3.1811
2009-07-13 | 0.032502 | 27950 | -3.4264
2009-07-14 | 0.016567 | 14247 | -4.1003
2009-07-15 | 0.025573 | 21992 | -3.6662
2009-07-16 | 0.21297 | 183153 | -1.5466
2009-07-17 | 0.15649 | 134584 | -1.8548
2009-07-18 | 1.2714 | 1093460 | 0.24013
2009-07-19 | 0.091982 | 79110 | -2.3862
2009-07-20 | 0.40302 | 346630 | -0.90876
2009-07-21 | 0.009299 | 7998 | -4.6779
2009-07-22 | 0.1705 | 146647 | -1.769
2009-07-23 | 0.029848 | 25673 | -3.5116
2009-07-24 | 0.086887 | 74736 | -2.4431
2009-07-25 | 0.032179 | 27679 | -3.4365
2009-07-26 | 0.13358 | 114903 | -2.0131
2009-07-27 | 0.0151 | 12989 | -4.1931
2009-07-28 | 0.14016 | 120573 | -1.9649
2009-07-29 | 0.29941 | 257564 | -1.2059
2009-07-30 | 0.0237 | 20388 | -3.7423
2009-07-31 | 0.53459 | 459896 | -0.62626
2009-08-01 | 0.019967 | 17178 | -3.9137
2009-08-02 | 0.017539 | 15089 | -4.0433
2009-08-03 | 0.046845 | 40303 | -3.0609
2009-08-04 | 0.048643 | 41850 | -3.0233
2009-08-05 | 0.0078954 | 6793 | -4.8415
2009-08-06 | 0.19585 | 168511 | -1.6304
2009-08-07 | 0.61085 | 525588 | -0.4929
2009-08-08 | 0.04125 | 35493 | -3.1881
2009-08-09 | 0.038842 | 33422 | -3.2482
2009-08-10 | 0.12765 | 109842 | -2.0584
2009-08-11 | 0.035885 | 30879 | -3.3274
2009-08-12 | 0.18828 | 162015 | -1.6698
2009-08-13 | 0.010503 | 9038 | -4.5561
2009-08-14 | 0.0090512 | 7789 | -4.7049
2009-08-15 | 0.050712 | 43641 | -2.9816
2009-08-16 | 0.045546 | 39196 | -3.089
2009-08-17 | 0.34679 | 298452 | -1.059
2009-08-18 | 0.0099788 | 8588 | -4.6073
2009-08-19 | 0.064823 | 55789 | -2.7361
2009-08-20 | 0.40849 | 351572 | -0.89528
2009-08-21 | 0.1054 | 90719 | -2.25
2009-08-22 | 0.0051052 | 4394 | -5.2775
2009-08-23 | 0.037317 | 32119 | -3.2883
2009-08-24 | 0.32521 | 279918 | -1.1233
2009-08-25 | 1.7704 | 1523905 | 0.57122
2009-08-26 | 0.37782 | 325214 | -0.97335
2009-08-27 | 0.00033806 | 291 | -7.9923
2009-08-28 | 0.15458 | 133065 | -1.867
2009-08-29 | 0.21592 | 185873 | -1.5328
2009-08-30 | 0.23338 | 200903 | -1.4551
2009-08-31 | 0.0048289 | 4157 | -5.3331
2009-09-01 | 0.091641 | 78892 | -2.3899
2009-09-02 | 0.077529 | 66745 | -2.5571
2009-09-03 | 0.39179 | 337303 | -0.93702
2009-09-04 | 0.094998 | 81788 | -2.3539
2009-09-05 | 0.052991 | 45623 | -2.9376
2009-09-06 | 0.010978 | 9452 | -4.5118
2009-09-07 | 0.20821 | 179267 | -1.5692
2009-09-08 | 0.0070533 | 6073 | -4.9543
2009-09-09 | 0.046175 | 39758 | -3.0753
2009-09-10 | 0.055468 | 47761 | -2.8919
2009-09-11 | 0.006946 | 5981 | -4.9696
2009-09-12 | 0.0035885 | 3090 | -5.63
2009-09-13 | 0.0027801 | 2394 | -5.8853
2009-09-14 | 0.0027998 | 2411 | -5.8782
2009-09-15 | 0.014797 | 12742 | -4.2134
2009-09-16 | 0.1732 | 149154 | -1.7533
2009-09-17 | 0.15918 | 137081 | -1.8377
2009-09-18 | 0.10099 | 86974 | -2.2927
2009-09-19 | 0.3536 | 304530 | -1.0396
2009-09-20 | 0.20988 | 180755 | -1.5612
2009-09-21 | 0.19345 | 166612 | -1.6427
2009-09-22 | 0.53246 | 458597 | -0.63025
2009-09-23 | 1.5738 | 1355513 | 0.45349
2009-09-24 | 0.004305 | 3708 | -5.448
2009-09-25 | 0.073255 | 63097 | -2.6138
2009-09-26 | 0.36553 | 314852 | -1.0064
2009-09-27 | 1.5475 | 1332976 | 0.43664
2009-09-28 | 0.0055271 | 4761 | -5.1981
2009-09-29 | 0.094875 | 81726 | -2.3552
2009-09-30 | 0.07423 | 63944 | -2.6006
2009-10-01 | 0.13982 | 120444 | -1.9674
2009-10-02 | 2.1599 | 1860725 | 0.77008
2009-10-03 | 1.6191 | 1394842 | 0.48188
2009-10-04 | 0.3089 | 266122 | -1.1747
2009-10-05 | 2.3698 | 2041606 | 0.86279
2009-10-06 | 0.5297 | 456360 | -0.63544
2009-10-07 | 0.11846 | 102063 | -2.1332
2009-10-08 | 0.27328 | 235450 | -1.2973
2009-10-09 | 0.1114 | 95985 | -2.1946
2009-10-10 | 0.12942 | 111510 | -2.0447
2009-10-11 | 0.00083214 | 717 | -7.0915
2009-10-12 | 0.10026 | 86389 | -2.3
2009-10-13 | 0.45637 | 393243 | -0.78445
2009-10-14 | 0.31736 | 273467 | -1.1477
2009-10-15 | 0.0015991 | 1378 | -6.4383
2009-10-16 | 0.018897 | 16284 | -3.9688
2009-10-17 | 0.034758 | 29953 | -3.3593
2009-10-18 | 0.026211 | 22588 | -3.6416
2009-10-19 | 0.36692 | 316204 | -1.0026
2009-10-20 | 0.047901 | 41281 | -3.0386
2009-10-21 | 0.30557 | 263349 | -1.1856
2009-10-22 | 0.032779 | 28250 | -3.418
2009-10-23 | 0.11254 | 96990 | -2.1845
2009-10-24 | 0.0087251 | 7520 | -4.7416
2009-10-25 | 0.46475 | 400566 | -0.76626
2009-10-26 | 0.26928 | 232094 | -1.312
2009-10-27 | 0 | 0
2009-10-28 | 0.0066117 | 5699 | -5.0189
2009-10-29 | 0.0070628 | 6088 | -4.9529
2009-10-30 | 0.13626 | 117455 | -1.9932
2009-10-31 | 0.010488 | 9041 | -4.5575
2009-11-01 | 0.24296 | 209443 | -1.4148
2009-11-02 | 0.052778 | 45497 | -2.9417
2009-11-03 | 0.16037 | 138252 | -1.8303
2009-11-04 | 0.072269 | 62302 | -2.6274
2009-11-05 | 0.36746 | 316790 | -1.0011
2009-11-06 | 0.5268 | 454166 | -0.64094
2009-11-07 | 0.0089347 | 7703 | -4.7178
2009-11-08 | 0.025174 | 21704 | -3.6819
2009-11-09 | 0.32288 | 278382 | -1.1305
2009-11-10 | 0.040404 | 34836 | -3.2088
2009-11-11 | 0.036038 | 31073 | -3.3232
2009-11-12 | 0.80428 | 693480 | -0.21781
2009-11-13 | 0.025001 | 21557 | -3.6889
2009-11-14 | 0.016316 | 14069 | -4.1156
2009-11-15 | 0.30419 | 262302 | -1.1901
2009-11-16 | 0.45833 | 395221 | -0.78017
2009-11-17 | 0.22748 | 196160 | -1.4807
2009-11-18 | 0.040579 | 34993 | -3.2045
2009-11-19 | 0.11001 | 94868 | -2.2072
2009-11-20 | 0.83041 | 716140 | -0.18583
2009-11-21 | 0.038442 | 33153 | -3.2586
2009-11-22 | 0.98866 | 852648 | -0.011404
2009-11-23 | 0.34541 | 297899 | -1.063
2009-11-24 | 0.15631 | 134813 | -1.8559
2009-11-25 | 0.042339 | 36517 | -3.162
2009-11-26 | 0.34595 | 298383 | -1.0615
2009-11-27 | 0.21329 | 183967 | -1.5451
2009-11-28 | 0.35817 | 308940 | -1.0267
2009-11-29 | 0.012239 | 10557 | -4.4031
2009-11-30 | 0.093425 | 80586 | -2.3706
2009-12-01 | 0.24926 | 215015 | -1.3892
2009-12-02 | 0.44523 | 384064 | -0.80916
2009-12-03 | 0.02898 | 24999 | -3.5412
2009-12-04 | 0.033629 | 29010 | -3.3924
2009-12-05 | 0.016041 | 13838 | -4.1326
2009-12-06 | 0.041049 | 35413 | -3.193
2009-12-07 | 0.54358 | 468949 | -0.60958
2009-12-08 | 0.51682 | 445876 | -0.66006
2009-12-09 | 0.027335 | 23583 | -3.5996
2009-12-10 | 0.15283 | 131857 | -1.8784
2009-12-11 | 0.076512 | 66013 | -2.5703
2009-12-12 | 0.078944 | 68113 | -2.539
2009-12-13 | 0.023891 | 20614 | -3.7342
2009-12-14 | 0.26195 | 226019 | -1.3396
2009-12-15 | 0.12457 | 107484 | -2.0829
2009-12-16 | 0.16228 | 140024 | -1.8185
2009-12-17 | 0.90733 | 782936 | -0.097245
2009-12-18 | 0.46649 | 402541 | -0.76252
2009-12-19 | 0.0060028 | 5180 | -5.1155
2009-12-20 | 0.21689 | 187168 | -1.5284
2009-12-21 | 0.026981 | 23284 | -3.6126
2009-12-22 | 0.1828 | 157758 | -1.6993
2009-12-23 | 0.4754 | 410272 | -0.74361
2009-12-24 | 0.026241 | 22647 | -3.6404
2009-12-25 | 0.16404 | 141578 | -1.8076
2009-12-26 | 0.12484 | 107742 | -2.0808
2009-12-27 | 0.23124 | 199578 | -1.4643
2009-12-28 | 0.42539 | 367156 | -0.85475
2009-12-29 | 0.12589 | 108657 | -2.0724
2009-12-30 | 0.0063501 | 5481 | -5.0593
2009-12-31 | 0.0078572 | 6782 | -4.8463
2010-01-01 | 0.17814 | 153763 | -1.7252
2010-01-02 | 0.12691 | 109547 | -2.0643
2010-01-03 | 0.069538 | 60026 | -2.6659
2010-01-04 | 0.054301 | 46875 | -2.9132
2010-01-05 | 0.51209 | 442065 | -0.66925
2010-01-06 | 0.23922 | 206509 | -1.4304
2010-01-07 | 0.006196 | 5349 | -5.0838
2010-01-08 | 0.13755 | 118750 | -1.9838
2010-01-09 | 0.23923 | 206538 | -1.4303
2010-01-10 | 0.21099 | 182161 | -1.5559
2010-01-11 | 0.61992 | 535216 | -0.47817
2010-01-12 | 0.87968 | 759505 | -0.1282
2010-01-13 | 0.68817 | 594171 | -0.37372
2010-01-14 | 0.14697 | 126900 | -1.9175
2010-01-15 | 0.025767 | 22248 | -3.6587
2010-01-16 | 0.4858 | 419468 | -0.72196
2010-01-17 | 0.30932 | 267090 | -1.1734
2010-01-18 | 0.14311 | 123575 | -1.9441
2010-01-19 | 0.01935 | 16709 | -3.9451
2010-01-20 | 0.097977 | 84607 | -2.323
2010-01-21 | 0.29245 | 252547 | -1.2295
2010-01-22 | 0.26113 | 225506 | -1.3427
2010-01-23 | 0.69441 | 599692 | -0.36469
2010-01-24 | 0.028343 | 24477 | -3.5634
2010-01-25 | 0.040971 | 35384 | -3.1949
2010-01-26 | 0.19233 | 166106 | -1.6485
2010-01-27 | 0.74774 | 645798 | -0.2907
2010-01-28 | 1.7187 | 1484413 | 0.54156
2010-01-29 | 0.064963 | 56109 | -2.7339
2010-01-30 | 0.26802 | 231499 | -1.3167
2010-01-31 | 0.15596 | 134707 | -1.8582
2010-02-01 | 0.097962 | 84616 | -2.3232
2010-02-02 | 0.30875 | 266693 | -1.1752
2010-02-03 | 0.30433 | 262879 | -1.1896
2010-02-04 | 0.33716 | 291246 | -1.0872
2010-02-05 | 0.80931 | 699110 | -0.21158
2010-02-06 | 0.87062 | 752095 | -0.13854
2010-02-07 | 0.26307 | 227261 | -1.3353
2010-02-08 | 0.029383 | 25384 | -3.5273
2010-02-09 | 0.12988 | 112205 | -2.0411
2010-02-10 | 0.16427 | 141922 | -1.8062
2010-02-11 | 0.21683 | 187332 | -1.5286
2010-02-12 | 0.38296 | 330862 | -0.95984
2010-02-13 | 0.19096 | 164991 | -1.6557
2010-02-14 | 0.39931 | 345007 | -0.91802
2010-02-15 | 0.28055 | 242403 | -1.271
2010-02-16 | 0.032274 | 27886 | -3.4335
2010-02-17 | 0.062049 | 53614 | -2.7798
2010-02-18 | 0.22587 | 195172 | -1.4878
2010-02-19 | 0.32682 | 282402 | -1.1184
2010-02-20 | 0.29029 | 250842 | -1.2369
2010-02-21 | 0.051958 | 44899 | -2.9573
2010-02-22 | 0.15844 | 136919 | -1.8424
2010-02-23 | 0.16982 | 146757 | -1.773
2010-02-24 | 0.086749 | 74968 | -2.4447
2010-02-25 | 0.11799 | 101965 | -2.1372
2010-02-26 | 0.10511 | 90840 | -2.2527
2010-02-27 | 0.17811 | 153929 | -1.7254
2010-02-28 | 1.3371 | 1155593 | 0.29048
2010-03-01 | 0.32471 | 280643 | -1.1248
2010-03-02 | 0.028068 | 24259 | -3.5731
2010-03-03 | 0.013791 | 11920 | -4.2837
2010-03-04 | 0.05049 | 43641 | -2.986
2010-03-05 | 0.013904 | 12018 | -4.2756
2010-03-06 | 0.11233 | 97096 | -2.1863
2010-03-07 | 0.19355 | 167304 | -1.6422
2010-03-08 | 0.032034 | 27691 | -3.441
2010-03-09 | 0.070402 | 60858 | -2.6535
2010-03-10 | 0.12851 | 111093 | -2.0517
2010-03-11 | 0.021571 | 18648 | -3.8364
2010-03-12 | 0.0016796 | 1452 | -6.3892
2010-03-13 | 0.20188 | 174529 | -1.6001
2010-03-14 | 0.82783 | 715691 | -0.18894
2010-03-15 | 0.017059 | 14748 | -4.0711
2010-03-16 | 0.16494 | 142605 | -1.8022
2010-03-17 | 0.022245 | 19233 | -3.8056
2010-03-18 | 0.045242 | 39117 | -3.0957
2010-03-19 | 0.61763 | 534018 | -0.48187
2010-03-20 | 0.10501 | 90796 | -2.2537
2010-03-21 | 0.015267 | 13201 | -4.1821
2010-03-22 | 0.033741 | 29175 | -3.3891
2010-03-23 | 0.24367 | 210706 | -1.4119
2010-03-24 | 0.071218 | 61584 | -2.642
2010-03-25 | 0.070544 | 61002 | -2.6515
2010-03-26 | 0.11199 | 96848 | -2.1893
2010-03-27 | 0.1436 | 124183 | -1.9407
2010-03-28 | 0.44187 | 382127 | -0.81674
2010-03-29 | 0.025725 | 22247 | -3.6603
2010-03-30 | 0.87314 | 755124 | -0.13566
2010-03-31 | 0.15556 | 134539 | -1.8607
2010-04-01 | 0.096692 | 83626 | -2.3362
2010-04-02 | 0.0036213 | 3132 | -5.6209
2010-04-03 | 0.00034686 | 300 | -7.9666
2010-04-04 | 0.37843 | 327315 | -0.97172
2010-04-05 | 0.023419 | 20256 | -3.7542
2010-04-06 | 0.0055297 | 4783 | -5.1976
2010-04-07 | 0.43473 | 376032 | -0.83304
2010-04-08 | 0.14784 | 127881 | -1.9116
2010-04-09 | 0.20925 | 181003 | -1.5642
2010-04-10 | 0.066753 | 57744 | -2.7068
2010-04-11 | 0.19695 | 170374 | -1.6248
2010-04-12 | 0.17642 | 152618 | -1.7349
2010-04-13 | 0.40837 | 353278 | -0.89559
2010-04-14 | 0.012784 | 11060 | -4.3595
2010-04-15 | 0.007919 | 6851 | -4.8385
2010-04-16 | 0.28538 | 246902 | -1.2539
2010-04-17 | 0.042877 | 37096 | -3.1494
2010-04-18 | 0.017178 | 14862 | -4.0641
2010-04-19 | 0.01534 | 13272 | -4.1773
2010-04-20 | 0.021684 | 18762 | -3.8312
2010-04-21 | 0.19324 | 167205 | -1.6438
2010-04-22 | 0.20148 | 174335 | -1.6021
2010-04-23 | 0.064265 | 55608 | -2.7447
2010-04-24 | 0.085945 | 74369 | -2.454
2010-04-25 | 0.03721 | 32199 | -3.2912
2010-04-26 | 0.3244 | 280721 | -1.1258
2010-04-27 | 0.020671 | 17888 | -3.879
2010-04-28 | 0.060873 | 52678 | -2.799
2010-04-29 | 0.13834 | 119716 | -1.9781
2010-04-30 | 0.11761 | 101779 | -2.1404
2010-05-01 | 0.004786 | 4142 | -5.3421
2010-05-02 | 0.44875 | 388375 | -0.80129
2010-05-03 | 0.062452 | 54051 | -2.7734
2010-05-04 | 0.034291 | 29679 | -3.3729
2010-05-05 | 0.27275 | 236070 | -1.2992
2010-05-06 | 0.15476 | 133950 | -1.8659
2010-05-07 | 0.06613 | 57239 | -2.7161
2010-05-08 | 0.19407 | 167985 | -1.6395
2010-05-09 | 0.12275 | 106250 | -2.0976
2010-05-10 | 0.068662 | 59434 | -2.6786
2010-05-11 | 0.63663 | 551082 | -0.45157
2010-05-12 | 0.10118 | 87588 | -2.2908
2010-05-13 | 0.00095649 | 828 | -6.9522
2010-05-14 | 0.004906 | 4247 | -5.3173
2010-05-15 | 0.015055 | 13033 | -4.1961
2010-05-16 | 0.009778 | 8465 | -4.6276
2010-05-17 | 0.0028762 | 2490 | -5.8513
2010-05-18 | 0.29182 | 252642 | -1.2316
2010-05-19 | 0.054616 | 47285 | -2.9074
2010-05-20 | 0.008286 | 7174 | -4.7932
2010-05-21 | 0.015674 | 13571 | -4.1557
2010-05-22 | 0.0055322 | 4790 | -5.1972
2010-05-23 | 0.033159 | 28711 | -3.4064
2010-05-24 | 0.26516 | 229591 | -1.3274
2010-05-25 | 0.21522 | 186355 | -1.5361
2010-05-26 | 0.44694 | 387007 | -0.80534
2010-05-27 | 0.052816 | 45735 | -2.9409
2010-05-28 | 0.016985 | 14708 | -4.0754
2010-05-29 | 0.28982 | 250973 | -1.2385
2010-05-30 | 0.38574 | 334048 | -0.95258
2010-05-31 | 0.30395 | 263222 | -1.1909
2010-06-01 | 0.061705 | 53438 | -2.7854
2010-06-02 | 0.024106 | 20877 | -3.7253
2010-06-03 | 0.082773 | 71686 | -2.4917
2010-06-04 | 0.56579 | 490020 | -0.56953
2010-06-05 | 0.014177 | 12279 | -4.2561
2010-06-06 | 0.084409 | 73108 | -2.4721
2010-06-07 | 0.18042 | 156270 | -1.7125
2010-06-08 | 0.19481 | 168738 | -1.6357
2010-06-09 | 0.37087 | 321234 | -0.99191
2010-06-10 | 0.087147 | 75486 | -2.4402
2010-06-11 | 0.069843 | 60499 | -2.6615
2010-06-12 | 0.063218 | 54761 | -2.7612
2010-06-13 | 0.00311 | 2694 | -5.7731
2010-06-14 | 0.0089222 | 7729 | -4.7192
2010-06-15 | 2.4232 | 2099208 | 0.8851
2010-06-16 | 0.080683 | 69896 | -2.5172
2010-06-17 | 0.010048 | 8705 | -4.6004
2010-06-18 | 0.04284 | 37114 | -3.1503
2010-06-19 | 0.15987 | 138501 | -1.8334
2010-06-20 | 0.0347 | 30063 | -3.361
2010-06-21 | 0.29817 | 258331 | -1.2101
2010-06-22 | 0.085609 | 74173 | -2.458
2010-06-23 | 0.062526 | 54175 | -2.7722
2010-06-24 | 0.11657 | 100999 | -2.1493
2010-06-25 | 0.31343 | 271579 | -1.1602
2010-06-26 | 0.0488 | 42285 | -3.02
2010-06-27 | 0.075947 | 65809 | -2.5777
2010-06-28 | 0.055769 | 48325 | -2.8865
2010-06-29 | 0.02245 | 19454 | -3.7965
2010-06-30 | 0.0082519 | 7151 | -4.7973
2010-07-01 | 0.44644 | 386951 | -0.80644
2010-07-02 | 0.10872 | 94232 | -2.219
2010-07-03 | 0.47049 | 407821 | -0.75397
2010-07-04 | 0.013289 | 11519 | -4.3208
2010-07-05 | 0.013341 | 11565 | -4.3169
2010-07-06 | 0.11884 | 103022 | -2.13
2010-07-07 | 0.0025897 | 2245 | -5.9562
2010-07-08 | 0.51465 | 446166 | -0.66427
2010-07-09 | 0.043634 | 37829 | -3.1319
2010-07-10 | 0.14185 | 122983 | -1.953
2010-07-11 | 0.0067796 | 5878 | -4.9938
2010-07-12 | 0.18366 | 159241 | -1.6947
2010-07-13 | 0.098751 | 85624 | -2.3152
2010-07-14 | 0.74921 | 649636 | -0.28874
2010-07-15 | 0.017314 | 15013 | -4.0563
2010-07-16 | 0.097969 | 84954 | -2.3231
2010-07-17 | 0.52312 | 453638 | -0.64794
2010-07-18 | 0.094644 | 82076 | -2.3576
2010-07-19 | 0.07703 | 66803 | -2.5636
2010-07-20 | 0.02905 | 25194 | -3.5387
2010-07-21 | 0.16012 | 138871 | -1.8318
2010-07-22 | 0.021877 | 18974 | -3.8223
2010-07-23 | 0.021982 | 19066 | -3.8175
2010-07-24 | 0.2877 | 249546 | -1.2458
2010-07-25 | 0.2054 | 178163 | -1.5828
2010-07-26 | 0.020016 | 17362 | -3.9112
2010-07-27 | 0.030714 | 26643 | -3.483
2010-07-28 | 0.1151 | 99850 | -2.1619
2010-07-29 | 0.077768 | 67464 | -2.554
2010-07-30 | 0.37363 | 324134 | -0.9845
2010-07-31 | 0.02004 | 17386 | -3.91
2010-08-01 | 0.39598 | 343547 | -0.92639
2010-08-02 | 0.74808 | 649040 | -0.29025
2010-08-03 | 1.0307 | 894270 | 0.03023
2010-08-04 | 0.069689 | 60467 | -2.6637
2010-08-05 | 0.087704 | 76100 | -2.4338
2010-08-06 | 0.027149 | 23558 | -3.6064
2010-08-07 | 0.0062679 | 5439 | -5.0723
2010-08-08 | 0.40875 | 354704 | -0.89465
2010-08-09 | 0.16045 | 139238 | -1.8298
2010-08-10 | 0.047282 | 41033 | -3.0516
2010-08-11 | 0.10654 | 92462 | -2.2392
2010-08-12 | 0.42837 | 371779 | -0.84776
2010-08-13 | 0.037314 | 32385 | -3.2884
2010-08-14 | 0.022754 | 19749 | -3.783
2010-08-15 | 0.23155 | 200975 | -1.463
2010-08-16 | 0.23322 | 202432 | -1.4558
2010-08-17 | 0.064623 | 56094 | -2.7392
2010-08-18 | 0.32728 | 284092 | -1.117
2010-08-19 | 0.18608 | 161535 | -1.6816
2010-08-20 | 0.039622 | 34396 | -3.2284
2010-08-21 | 0.064148 | 55689 | -2.7466
2010-08-22 | 0.003201 | 2779 | -5.7443
2010-08-23 | 0.094814 | 82316 | -2.3558
2010-08-24 | 1.2028 | 1044281 | 0.18465
2010-08-25 | 0.29482 | 255975 | -1.2214
2010-08-26 | 0.015263 | 13252 | -4.1824
2010-08-27 | 0.07061 | 61310 | -2.6506
2010-08-28 | 0.0216 | 18756 | -3.835
2010-08-29 | 0.068623 | 59589 | -2.6791
2010-08-30 | 0.024892 | 21616 | -3.6932
2010-08-31 | 0.13518 | 117392 | -2.0011
2010-09-01 | 0.19556 | 169828 | -1.6319
2010-09-02 | 0.11407 | 99064 | -2.171
2010-09-03 | 0.13575 | 117894 | -1.997
2010-09-04 | 0.53775 | 467046 | -0.62036
2010-09-05 | 63.7367 | 55357925 | 4.1548
2010-09-06 | 0.0028069 | 2438 | -5.8757
2010-09-07 | 0.12129 | 105351 | -2.1096
2010-09-08 | 0.18372 | 159585 | -1.6943
2010-09-09 | 0.13468 | 116993 | -2.0048
2010-09-10 | 0.73221 | 636052 | -0.31169
2010-09-11 | 0.0074041 | 6432 | -4.9057
2010-09-12 | 0.0030355 | 2637 | -5.7974
2010-09-13 | 0.028165 | 24469 | -3.5697
2010-09-14 | 0.049731 | 43206 | -3.0011
2010-09-15 | 0.2139 | 185841 | -1.5422
2010-09-16 | 0.34645 | 301009 | -1.06
2010-09-17 | 0.21767 | 189123 | -1.5248
2010-09-18 | 0.0069985 | 6081 | -4.9621
2010-09-19 | 0.018609 | 16170 | -3.9841
2010-09-20 | 0.0072835 | 6329 | -4.9221
2010-09-21 | 0.19015 | 165233 | -1.66
2010-09-22 | 0.012452 | 10821 | -4.3859
2010-09-23 | 0.015514 | 13482 | -4.166
2010-09-24 | 0.11656 | 101301 | -2.1493
2010-09-25 | 0.015203 | 13213 | -4.1862
2010-09-26 | 0.01715 | 14905 | -4.0658
2010-09-27 | 0.070627 | 61385 | -2.6503
2010-09-28 | 0.025943 | 22549 | -3.6518
2010-09-29 | 0.13278 | 115414 | -2.019
2010-09-30 | 0.096797 | 84138 | -2.3351
2010-10-01 | 0.012903 | 11216 | -4.3503
2010-10-02 | 0.055206 | 47989 | -2.8967
2010-10-03 | 0.20083 | 174582 | -1.6053
2010-10-04 | 0.18822 | 163629 | -1.6701
2010-10-05 | 0.010658 | 9266 | -4.5414
2010-10-06 | 0.10888 | 94658 | -2.2175
2010-10-07 | 0.15425 | 134107 | -1.8692
2010-10-08 | 0.5313 | 461933 | -0.63243
2010-10-09 | 0.11287 | 98133 | -2.1816
2010-10-10 | 0.060841 | 52901 | -2.7995
2010-10-11 | 0.002422 | 2106 | -6.0232
2010-10-12 | 0.25815 | 224470 | -1.3542
2010-10-13 | 0.19435 | 169002 | -1.6381
2010-10-14 | 0.20936 | 182062 | -1.5637
2010-10-15 | 2.8416 | 2471120 | 1.0444
2010-10-16 | 1.5171 | 1319402 | 0.41683
2010-10-17 | 0.53081 | 461641 | -0.63334
2010-10-18 | 0.13882 | 120735 | -1.9746
2010-10-19 | 0.022509 | 19577 | -3.7938
2010-10-20 | 0.1553 | 135073 | -1.8624
2010-10-21 | 0.0098173 | 8539 | -4.6236
2010-10-22 | 0.041096 | 35746 | -3.1919
2010-10-23 | 0.3109 | 270437 | -1.1683
2010-10-24 | 0.019211 | 16711 | -3.9523
2010-10-25 | 0.083966 | 73042 | -2.4773
2010-10-26 | 0.10582 | 92052 | -2.2461
2010-10-27 | 0.33231 | 289094 | -1.1017
2010-10-28 | 0.03501 | 30458 | -3.3521
2010-10-29 | 0.030202 | 26276 | -3.4999
2010-10-30 | 0.11463 | 99737 | -2.166
2010-10-31 | 0.06093 | 53013 | -2.798
2010-11-01 | 0.39335 | 342248 | -0.93307
2010-11-02 | 0.096218 | 83721 | -2.3411
2010-11-03 | 0.038076 | 33132 | -3.2682
2010-11-04 | 0.0061298 | 5334 | -5.0946
2010-11-05 | 0.17578 | 152968 | -1.7385
2010-11-06 | 0.050638 | 44067 | -2.983
2010-11-07 | 0.069104 | 60138 | -2.6721
2010-11-08 | 1.2211 | 1062714 | 0.19976
2010-11-09 | 0.20692 | 180084 | -1.5754
2010-11-10 | 0.32749 | 285027 | -1.1163
2010-11-11 | 0.13846 | 120515 | -1.9771
2010-11-12 | 0.095427 | 83059 | -2.3494
2010-11-13 | 0.10246 | 89182 | -2.2783
2010-11-14 | 0.0022356 | 1946 | -6.1032
2010-11-15 | 0.15352 | 133635 | -1.8739
2010-11-16 | 0.032809 | 28560 | -3.4171
2010-11-17 | 0.012518 | 10897 | -4.3806
2010-11-18 | 0.08759 | 76252 | -2.4351
2010-11-19 | 0.027367 | 23825 | -3.5984
2010-11-20 | 0.0013485 | 1174 | -6.6088
2010-11-21 | 0.072433 | 63063 | -2.6251
2010-11-22 | 0.033318 | 29009 | -3.4017
2010-11-23 | 0.021531 | 18747 | -3.8383
2010-11-24 | 0.52833 | 460029 | -0.63803
2010-11-25 | 0.10412 | 90663 | -2.2622
2010-11-26 | 0.42317 | 368483 | -0.85999
2010-11-27 | 0.094269 | 82090 | -2.3616
2010-11-28 | 0.028087 | 24459 | -3.5724
2010-11-29 | 0.10909 | 95005 | -2.2155
2010-11-30 | 0.045456 | 39587 | -3.091
2010-12-01 | 0.20612 | 179516 | -1.5793
2010-12-02 | 0.2373 | 206673 | -1.4384
2010-12-03 | 0.28872 | 251462 | -1.2423
2010-12-04 | 0.034849 | 30353 | -3.3567
2010-12-05 | 0.09822 | 85552 | -2.3205
2010-12-06 | 0.03804 | 33135 | -3.2691
2010-12-07 | 0.21807 | 189956 | -1.5229
2010-12-08 | 0.28056 | 244400 | -1.271
2010-12-09 | 0.0985 | 85806 | -2.3177
2010-12-10 | 0.036869 | 32119 | -3.3004
2010-12-11 | 0.11758 | 102434 | -2.1406
2010-12-12 | 0.47748 | 415985 | -0.73924
2010-12-13 | 0.021646 | 18859 | -3.8329
2010-12-14 | 0.013496 | 11759 | -4.3053
2010-12-15 | 0.09353 | 81492 | -2.3695
2010-12-16 | 4.9235 | 4289987 | 1.594
2010-12-17 | 0.089528 | 78010 | -2.4132
2010-12-18 | 1.1545 | 1006023 | 0.14369
2010-12-19 | 0.30741 | 267881 | -1.1796
2010-12-20 | 0.64334 | 560623 | -0.44109
2010-12-21 | 0.038165 | 33259 | -3.2658
2010-12-22 | 0.28612 | 249353 | -1.2513
2010-12-23 | 0.12077 | 105255 | -2.1138
2010-12-24 | 0.11242 | 97982 | -2.1855
2010-12-25 | 0.16428 | 143185 | -1.8062
2010-12-26 | 0.79486 | 692794 | -0.22959
2010-12-27 | 0.28568 | 249008 | -1.2529
2010-12-28 | 0.041117 | 35840 | -3.1913
2010-12-29 | 0.073954 | 64464 | -2.6043
2010-12-30 | 0.052689 | 45929 | -2.9434
2010-12-31 | 0.5783 | 504126 | -0.54765
2011-01-01 | 0.4253 | 370762 | -0.85495
2011-01-02 | 1.9087 | 1663935 | 0.6464
2011-01-03 | 0.46438 | 404851 | -0.76706
2011-01-04 | 0.035414 | 30875 | -3.3407
2011-01-05 | 0.26124 | 227768 | -1.3423
2011-01-06 | 0.010562 | 9209 | -4.5505
2011-01-07 | 0.14153 | 123405 | -1.9552
2011-01-08 | 0.30123 | 262653 | -1.1999
2011-01-09 | 0.17805 | 155257 | -1.7257
2011-01-10 | 0.3191 | 278260 | -1.1422
2011-01-11 | 0.15019 | 130968 | -1.8959
2011-01-12 | 0.51832 | 452005 | -0.65716
2011-01-13 | 0.10581 | 92278 | -2.2461
2011-01-14 | 0.10763 | 93865 | -2.2291
2011-01-15 | 0.045183 | 39406 | -3.097
2011-01-16 | 0.049346 | 43038 | -3.0089
2011-01-17 | 0.12228 | 106656 | -2.1014
2011-01-18 | 0.097052 | 84651 | -2.3325
2011-01-19 | 0.20135 | 175623 | -1.6027
2011-01-20 | 0.036267 | 31635 | -3.3168
2011-01-21 | 0.06119 | 53376 | -2.7938
2011-01-22 | 0.014063 | 12268 | -4.2642
2011-01-23 | 0.19771 | 172475 | -1.6209
2011-01-24 | 0.39513 | 344708 | -0.92853
2011-01-25 | 0.24057 | 209880 | -1.4247
2011-01-26 | 0.27637 | 241117 | -1.286
2011-01-27 | 0.20989 | 183119 | -1.5612
2011-01-28 | 0.055603 | 48513 | -2.8895
2011-01-29 | 0.17592 | 153497 | -1.7377
2011-01-30 | 0.4778 | 416905 | -0.73856
2011-01-31 | 0.43675 | 381101 | -0.82839
2011-02-01 | 1.3441 | 1172862 | 0.29572
2011-02-02 | 0.59102 | 515741 | -0.52591
2011-02-03 | 0.115 | 100357 | -2.1628
2011-02-04 | 0.28813 | 251443 | -1.2444
2011-02-05 | 0.77872 | 679597 | -0.25011
2011-02-06 | 0.62181 | 542675 | -0.47513
2011-02-07 | 0.4215 | 367874 | -0.86393
2011-02-08 | 0.034805 | 30378 | -3.358
2011-02-09 | 0.73471 | 641274 | -0.30827
2011-02-10 | 0.24395 | 212928 | -1.4108
2011-02-11 | 0.10067 | 87876 | -2.2959
2011-02-12 | 0.22541 | 196759 | -1.4898
2011-02-13 | 0.19931 | 173982 | -1.6129
2011-02-14 | 0.11498 | 100375 | -2.163
2011-02-15 | 0.038912 | 33970 | -3.2464
2011-02-16 | 0.027169 | 23719 | -3.6057
2011-02-17 | 0.18257 | 159387 | -1.7006
2011-02-18 | 0.054305 | 47412 | -2.9131
2011-02-19 | 0.079376 | 69303 | -2.5336
2011-02-20 | 0.20891 | 182406 | -1.5658
2011-02-21 | 0.19105 | 166819 | -1.6552
2011-02-22 | 0.0018736 | 1636 | -6.2799
2011-02-23 | 0.055509 | 48471 | -2.8912
2011-02-24 | 0.16955 | 148052 | -1.7746
2011-02-25 | 0.10699 | 93429 | -2.235
2011-02-26 | 0.052086 | 45486 | -2.9549
2011-02-27 | 0.021455 | 18737 | -3.8418
2011-02-28 | 0.34602 | 302190 | -1.0613
2011-03-01 | 0.23665 | 206682 | -1.4412
2011-03-02 | 0.018317 | 15998 | -3.9999
2011-03-03 | 0.20561 | 179583 | -1.5818
2011-03-04 | 0.064969 | 56747 | -2.7338
2011-03-05 | 0.53654 | 468657 | -0.62261
2011-03-06 | 0.4773 | 416924 | -0.73961
2011-03-07 | 0.07854 | 68607 | -2.5441
2011-03-08 | 0.26642 | 232732 | -1.3227
2011-03-09 | 0.0032098 | 2804 | -5.7416
2011-03-10 | 0.41769 | 364900 | -0.87301
2011-03-11 | 0.61892 | 540711 | -0.47978
2011-03-12 | 0.057133 | 49915 | -2.8624
2011-03-13 | 0.41579 | 363269 | -0.87759
2011-03-14 | 0.11573 | 101115 | -2.1565
2011-03-15 | 0.0064252 | 5614 | -5.0475
2011-03-16 | 0.35048 | 306237 | -1.0485
2011-03-17 | 0.54518 | 476376 | -0.60665
2011-03-18 | 0.14735 | 128758 | -1.915
2011-03-19 | 0.33101 | 289256 | -1.1056
2011-03-20 | 0.31406 | 274455 | -1.1582
2011-03-21 | 0.67562 | 590436 | -0.39212
2011-03-22 | 0.038799 | 33908 | -3.2494
2011-03-23 | 0.13929 | 121733 | -1.9712
2011-03-24 | 0.071583 | 62563 | -2.6369
2011-03-25 | 0.032736 | 28612 | -3.4193
2011-03-26 | 0.16058 | 140351 | -1.829
2011-03-27 | 0.25962 | 226929 | -1.3485
2011-03-28 | 0.11753 | 102729 | -2.1411
2011-03-29 | 0.042645 | 37277 | -3.1549
2011-03-30 | 0.37253 | 325654 | -0.98743
2011-03-31 | 0.34075 | 297879 | -1.0766
2011-04-01 | 0.14861 | 129915 | -1.9064
2011-04-02 | 0.094792 | 82871 | -2.3561
2011-04-03 | 0.024804 | 21685 | -3.6968
2011-04-04 | 0.12726 | 111264 | -2.0615
2011-04-05 | 0.081117 | 70922 | -2.5119
2011-04-06 | 0.17135 | 149822 | -1.764
2011-04-07 | 0.096065 | 83997 | -2.3427
2011-04-08 | 0.017701 | 15478 | -4.0341
2011-04-09 | 0.38798 | 339265 | -0.94679
2011-04-10 | 0.11251 | 98384 | -2.1847
2011-04-11 | 0.029614 | 25897 | -3.5195
2011-04-12 | 0.057114 | 49947 | -2.8627
2011-04-13 | 0.21479 | 187839 | -1.5381
2011-04-14 | 0.0047852 | 4185 | -5.3422
2011-04-15 | 0.012614 | 11032 | -4.373
2011-04-16 | 0.14531 | 127089 | -1.9289
2011-04-17 | 0.027988 | 24480 | -3.576
2011-04-18 | 0.020226 | 17691 | -3.9008
2011-04-19 | 0.004717 | 4126 | -5.3566
2011-04-20 | 0.037926 | 33175 | -3.2721
2011-04-21 | 0.15926 | 139317 | -1.8372
2011-04-22 | 0.051608 | 45146 | -2.9641
2011-04-23 | 0.16576 | 145012 | -1.7972
2011-04-24 | 0.033626 | 29417 | -3.3925
2011-04-25 | 0.29169 | 255190 | -1.2321
2011-04-26 | 0.10589 | 92642 | -2.2454
2011-04-27 | 0.060994 | 53365 | -2.797
2011-04-28 | 0.06885 | 60240 | -2.6758
2011-04-29 | 0.15202 | 133015 | -1.8837
2011-04-30 | 0.2023 | 177016 | -1.598
2011-05-01 | 0.038313 | 33525 | -3.262
2011-05-02 | 0.00079081 | 692 | -7.1425
2011-05-03 | 0.41641 | 364392 | -0.87609
2011-05-04 | 0.026231 | 22955 | -3.6408
2011-05-05 | 0.011893 | 10408 | -4.4318
2011-05-06 | 0.0032942 | 2883 | -5.7156
2011-05-07 | 0.019802 | 17331 | -3.9219
2011-05-08 | 0.0070839 | 6200 | -4.9499
2011-05-09 | 0.26659 | 233329 | -1.3221
2011-05-10 | 0.34728 | 303962 | -1.0576
2011-05-11 | 0.56098 | 491024 | -0.57808
2011-05-12 | 0.093926 | 82216 | -2.3653
2011-05-13 | 0.20706 | 181253 | -1.5747
2011-05-14 | 0.046447 | 40659 | -3.0694
2011-05-15 | 0.074527 | 65242 | -2.5966
2011-05-16 | 0.23967 | 209820 | -1.4285
2011-05-17 | 0.036969 | 32365 | -3.2977
2011-05-18 | 1.7133e-05 | 15 | -10.9745
2011-05-19 | 0.01039 | 9097 | -4.5669
2011-05-20 | 0.06035 | 52839 | -2.8076
2011-05-21 | 0.032624 | 28565 | -3.4227
2011-05-22 | 0.61793 | 541063 | -0.48138
2011-05-23 | 0.25106 | 219832 | -1.3821
2011-05-24 | 0.024146 | 21144 | -3.7236
2011-05-25 | 0.20442 | 179006 | -1.5876
2011-05-26 | 0.31786 | 278354 | -1.1461
2011-05-27 | 0.012791 | 11202 | -4.359
2011-05-28 | 0.0025098 | 2198 | -5.9876
2011-05-29 | 0.2134 | 186893 | -1.5446
2011-05-30 | 0.45356 | 397235 | -0.79063
2011-05-31 | 0.38681 | 338786 | -0.94982
2011-06-01 | 0.028775 | 25203 | -3.5483
2011-06-02 | 0.0041694 | 3652 | -5.48
2011-06-03 | 0.053862 | 47179 | -2.9213
2011-06-04 | 0.01755 | 15373 | -4.0427
2011-06-05 | 0.08939 | 78304 | -2.4147
2011-06-06 | 0.33141 | 290321 | -1.1044
2011-06-07 | 0.094084 | 82421 | -2.3636
2011-06-08 | 0.58814 | 515249 | -0.53079
2011-06-09 | 0.27821 | 243736 | -1.2794
2011-06-10 | 0.016123 | 14126 | -4.1275
2011-06-11 | 0.014243 | 12479 | -4.2515
2011-06-12 | 0.23701 | 207665 | -1.4396
2011-06-13 | 0.027552 | 24141 | -3.5917
2011-06-14 | 0.15535 | 136125 | -1.8621
2011-06-15 | 0.46666 | 408917 | -0.76215
2011-06-16 | 0.013595 | 11913 | -4.2981
2011-06-17 | 0.22713 | 199038 | -1.4822
2011-06-18 | 0.03119 | 27333 | -3.4677
2011-06-19 | 0.10305 | 90306 | -2.2726
2011-06-20 | 0.1818 | 159328 | -1.7049
2011-06-21 | 0.79355 | 695481 | -0.23124
2011-06-22 | 0.35608 | 312085 | -1.0326
2011-06-23 | 0.01521 | 13331 | -4.1858
2011-06-24 | 0.27217 | 238561 | -1.3013
2011-06-25 | 0.13588 | 119099 | -1.996
2011-06-26 | 0.17944 | 157285 | -1.7179
2011-06-27 | 0.35787 | 313704 | -1.0276
2011-06-28 | 0.19122 | 167629 | -1.6543
2011-06-29 | 0.11629 | 101948 | -2.1516
2011-06-30 | 0.16199 | 142013 | -1.8202
2011-07-01 | 0.01526 | 13388 | -4.1825
2011-07-02 | 0.16233 | 142419 | -1.8181
2011-07-03 | 0.035639 | 31268 | -3.3343
2011-07-04 | 0.012284 | 10778 | -4.3994
2011-07-05 | 73.2326 | 64252883 | 4.2936
2011-07-06 | 0.089058 | 78139 | -2.4185
2011-07-07 | 0.050915 | 44673 | -2.9776
2011-07-08 | 0.072188 | 63339 | -2.6285
2011-07-09 | 0.38105 | 334344 | -0.96482
2011-07-10 | 0.62103 | 544908 | -0.47638
2011-07-11 | 0.17516 | 153691 | -1.7421
2011-07-12 | 0.35413 | 310728 | -1.0381
2011-07-13 | 0.11152 | 97851 | -2.1936
2011-07-14 | 0.046888 | 41143 | -3.06
2011-07-15 | 0.18147 | 159241 | -1.7066
2011-07-16 | 0.10116 | 88765 | -2.2911
2011-07-17 | 0.15379 | 134951 | -1.8722
2011-07-18 | 0.10141 | 88991 | -2.2886
2011-07-19 | 0.24767 | 217335 | -1.3957
2011-07-20 | 0.59734 | 524185 | -0.51527
2011-07-21 | 0.26906 | 236108 | -1.3128
2011-07-22 | 0.36357 | 319049 | -1.0118
2011-07-23 | 0.041123 | 36088 | -3.1912
2011-07-24 | 0.40051 | 351477 | -0.91502
2011-07-25 | 0.22626 | 198563 | -1.4861
2011-07-26 | 0.069532 | 61021 | -2.666
2011-07-27 | 0.07074 | 62082 | -2.6487
2011-07-28 | 0.019104 | 16766 | -3.9579
2011-07-29 | 0.030941 | 27155 | -3.4757
2011-07-30 | 0.085965 | 75446 | -2.4538
2011-07-31 | 0.011169 | 9802 | -4.4947
2011-08-01 | 0.15596 | 136875 | -1.8582
2011-08-02 | 0.19054 | 167227 | -1.6579
2011-08-03 | 0.093444 | 82014 | -2.3704
2011-08-04 | 0.24677 | 216589 | -1.3993
2011-08-05 | 0.056288 | 49404 | -2.8773
2011-08-06 | 0.081634 | 71651 | -2.5055
2011-08-07 | 0.048262 | 42360 | -3.0311
2011-08-08 | 0.36946 | 324289 | -0.9957
2011-08-09 | 0.023451 | 20584 | -3.7528
2011-08-10 | 0.1914 | 168003 | -1.6534
2011-08-11 | 0.097236 | 85350 | -2.3306
2011-08-12 | 0.24887 | 218453 | -1.3908
2011-08-13 | 0.28027 | 246015 | -1.272
2011-08-14 | 0.14272 | 125277 | -1.9469
2011-08-15 | 0.01691 | 14844 | -4.0798
2011-08-16 | 0.093226 | 81835 | -2.3727
2011-08-17 | 0.22793 | 200078 | -1.4787
2011-08-18 | 1.2323 | 1081753 | 0.20889
2011-08-19 | 0.92943 | 815895 | -0.073178
2011-08-20 | 0.02254 | 19787 | -3.7925
2011-08-21 | 0.10239 | 89881 | -2.279
2011-08-22 | 0.004233 | 3716 | -5.4649
2011-08-23 | 0.01803 | 15828 | -4.0157
2011-08-24 | 0.27349 | 240093 | -1.2965
2011-08-25 | 0.61295 | 538107 | -0.48948
2011-08-26 | 0.24441 | 214571 | -1.4089
2011-08-27 | 0.037123 | 32591 | -3.2935
2011-08-28 | 0.3917 | 343886 | -0.93726
2011-08-29 | 0.12538 | 110076 | -2.0764
2011-08-30 | 0.16194 | 142173 | -1.8205
2011-08-31 | 0.050313 | 44173 | -2.9895
2011-09-01 | 0.011278 | 9902 | -4.4849
2011-09-02 | 0.021051 | 18482 | -3.8608
2011-09-03 | 0.033315 | 29250 | -3.4018
2011-09-04 | 0.0024897 | 2186 | -5.9956
2011-09-05 | 0.016114 | 14148 | -4.1281
2011-09-06 | 0.65227 | 572707 | -0.4273
2011-09-07 | 0.025358 | 22265 | -3.6747
2011-09-08 | 0.046384 | 40727 | -3.0708
2011-09-09 | 0.087544 | 76868 | -2.4356
2011-09-10 | 0.076214 | 66921 | -2.5742
2011-09-11 | 0.093456 | 82061 | -2.3703
2011-09-12 | 0.013682 | 12014 | -4.2917
2011-09-13 | 0.080388 | 70588 | -2.5209
2011-09-14 | 0.04762 | 41815 | -3.0445
2011-09-15 | 0.10574 | 92855 | -2.2467
2011-09-16 | 0.12124 | 106463 | -2.11
2011-09-17 | 0.011991 | 10530 | -4.4236
2011-09-18 | 0.0027683 | 2431 | -5.8895
2011-09-19 | 0.06346 | 55728 | -2.7573
2011-09-20 | 0.63317 | 556028 | -0.45702
2011-09-21 | 0.17492 | 153614 | -1.7434
2011-09-22 | 0.059065 | 51870 | -2.8291
2011-09-23 | 0.083742 | 73542 | -2.48
2011-09-24 | 0.42959 | 377273 | -0.84491
2011-09-25 | 0.34918 | 306657 | -1.0522
2011-09-26 | 0.00528 | 4637 | -5.2438
2011-09-27 | 0.07278 | 63918 | -2.6203
2011-09-28 | 0.041229 | 36209 | -3.1886
2011-09-29 | 1.8864 | 1656742 | 0.63467
2011-09-30 | 0.48902 | 429490 | -0.71535
2011-10-01 | 0.079667 | 69970 | -2.5299
2011-10-02 | 0.27353 | 240240 | -1.2963
2011-10-03 | 0.20501 | 180063 | -1.5847
2011-10-04 | 0.013977 | 12276 | -4.2704
2011-10-05 | 1.6353 | 1436332 | 0.49184
2011-10-06 | 0.090301 | 79314 | -2.4046
2011-10-07 | 2.5291 | 2221423 | 0.92787
2011-10-08 | 0.98172 | 862294 | -0.018449
2011-10-09 | 0.20474 | 179832 | -1.586
2011-10-10 | 0.072624 | 63791 | -2.6225
2011-10-11 | 0.081054 | 71196 | -2.5126
2011-10-12 | 0.12589 | 110583 | -2.0723
2011-10-13 | 0.1699 | 149241 | -1.7725
2011-10-14 | 0.27682 | 243165 | -1.2844
2011-10-15 | 0.053535 | 47026 | -2.9274
2011-10-16 | 0.01575 | 13835 | -4.1509
2011-10-17 | 0.0066106 | 5807 | -5.0191
2011-10-18 | 0.069122 | 60720 | -2.6719
2011-10-19 | 0.00010245 | 90 | -9.1861
2011-10-20 | 0.26325 | 231261 | -1.3346
2011-10-21 | 0.067637 | 59418 | -2.6936
2011-10-22 | 0.29162 | 256187 | -1.2323
2011-10-23 | 0.040701 | 35756 | -3.2015
2011-10-24 | 0.051533 | 45272 | -2.9655
2011-10-25 | 0.0023175 | 2036 | -6.0673
2011-10-26 | 0.17489 | 153651 | -1.7436
2011-10-27 | 0.21797 | 191499 | -1.5234
2011-10-28 | 0.052625 | 46234 | -2.9446
2011-10-29 | 0.033671 | 29582 | -3.3911
2011-10-30 | 0.16102 | 141468 | -1.8262
2011-10-31 | 0.1856 | 163064 | -1.6842
2011-11-01 | 0.030277 | 26601 | -3.4974
2011-11-02 | 0.06591 | 57909 | -2.7195
2011-11-03 | 0.11098 | 97513 | -2.1984
2011-11-04 | 0.034884 | 30650 | -3.3557
2011-11-05 | 0.32775 | 287975 | -1.1155
2011-11-06 | 0.071212 | 62570 | -2.6421
2011-11-07 | 0.51381 | 451461 | -0.6659
2011-11-08 | 2.2038 | 1936423 | 0.79019
2011-11-09 | 0.084619 | 74353 | -2.4696
2011-11-10 | 0.97391 | 855761 | -0.026437
2011-11-11 | 0.035869 | 31518 | -3.3279
2011-11-12 | 0.19187 | 168595 | -1.651
2011-11-13 | 0.037491 | 32944 | -3.2837
2011-11-14 | 0.34504 | 303198 | -1.0641
2011-11-15 | 0.030954 | 27200 | -3.4753
2011-11-16 | 0.23163 | 203540 | -1.4626
2011-11-17 | 0.024392 | 21435 | -3.7135
2011-11-18 | 0.1217 | 106944 | -2.1062
2011-11-19 | 0.012949 | 11379 | -4.3468
2011-11-20 | 0.75515 | 663621 | -0.28083
2011-11-21 | 0.035365 | 31079 | -3.342
2011-11-22 | 0.26653 | 234230 | -1.3223
2011-11-23 | 0.62988 | 553554 | -0.46222
2011-11-24 | 0.028694 | 25217 | -3.5511
2011-11-25 | 0.021427 | 18831 | -3.8431
2011-11-26 | 0.23717 | 208440 | -1.439
2011-11-27 | 0.077717 | 68302 | -2.5547
2011-11-28 | 0.10869 | 95525 | -2.2192
2011-11-29 | 0.099595 | 87532 | -2.3066
2011-11-30 | 0.41768 | 367097 | -0.87303
2011-12-01 | 0.015092 | 13264 | -4.1936
2011-12-02 | 0.013378 | 11758 | -4.3141
2011-12-03 | 0.28677 | 252050 | -1.2491
2011-12-04 | 0.044355 | 38985 | -3.1155
2011-12-05 | 0.21819 | 191773 | -1.5224
2011-12-06 | 0.098914 | 86941 | -2.3135
2011-12-07 | 0.16639 | 146250 | -1.7934
2011-12-08 | 0.037463 | 32929 | -3.2844
2011-12-09 | 0.02356 | 20709 | -3.7482
2011-12-10 | 0.028474 | 25028 | -3.5588
2011-12-11 | 0.25619 | 225190 | -1.3618
2011-12-12 | 0.3492 | 306951 | -1.0521
2011-12-13 | 0.0090601 | 7964 | -4.7039
2011-12-14 | 0.015506 | 13630 | -4.1665
2011-12-15 | 0.42837 | 376557 | -0.84776
2011-12-16 | 0.031154 | 27386 | -3.4688
2011-12-17 | 0.011968 | 10521 | -4.4255
2011-12-18 | 0.19267 | 169375 | -1.6468
2011-12-19 | 0.34167 | 300356 | -1.0739
2011-12-20 | 0.01798 | 15806 | -4.0185
2011-12-21 | 0.17957 | 157857 | -1.7172
2011-12-22 | 0.049179 | 43234 | -3.0123
2011-12-23 | 0.14956 | 131485 | -1.9
2011-12-24 | 0.21054 | 185089 | -1.5581
2011-12-25 | 0.0058523 | 5145 | -5.1409
2011-12-26 | 0.35507 | 312161 | -1.0354
2011-12-27 | 0.0023522 | 2068 | -6.0524
2011-12-28 | 0.046261 | 40672 | -3.0734
2011-12-29 | 0.017023 | 14966 | -4.0732
2011-12-30 | 0.30877 | 271472 | -1.1751
2011-12-31 | 0.31696 | 278670 | -1.149
2012-01-01 | 0.012401 | 10903 | -4.39
2012-01-02 | 0.050746 | 44617 | -2.9809
2012-01-03 | 0.025519 | 22437 | -3.6683
2012-01-04 | 0.68144 | 599152 | -0.38355
2012-01-05 | 0.7722 | 678964 | -0.25851
2012-01-06 | 0.042615 | 37470 | -3.1555
2012-01-07 | 0.023073 | 20288 | -3.7691
2012-01-08 | 0.60953 | 535954 | -0.49506
2012-01-09 | 0.18803 | 165336 | -1.6711
2012-01-10 | 0.027911 | 24542 | -3.5787
2012-01-11 | 1.4051 | 1235569 | 0.34014
2012-01-12 | 0.24646 | 216723 | -1.4005
2012-01-13 | 0.13261 | 116608 | -2.0204
2012-01-14 | 0.23384 | 205623 | -1.4531
2012-01-15 | 0.12505 | 109963 | -2.079
2012-01-16 | 0.25558 | 224752 | -1.3642
2012-01-17 | 0.034657 | 30477 | -3.3622
2012-01-18 | 0.62456 | 549236 | -0.4707
2012-01-19 | 0.0093359 | 8210 | -4.6739
2012-01-20 | 0.32677 | 287361 | -1.1185
2012-01-21 | 0.2033 | 178787 | -1.5931
2012-01-22 | 0.00075958 | 668 | -7.1827
2012-01-23 | 0.027117 | 23848 | -3.6076
2012-01-24 | 0.16105 | 141637 | -1.826
2012-01-25 | 0.5545 | 487661 | -0.58969
2012-01-26 | 0.19539 | 171843 | -1.6327
2012-01-27 | 0.21674 | 190618 | -1.5291
2012-01-28 | 0.36366 | 319836 | -1.0115
2012-01-29 | 0.0042206 | 3712 | -5.4678
2012-01-30 | 0.54201 | 476702 | -0.61248
2012-01-31 | 0.042439 | 37326 | -3.1597
2012-02-01 | 0.029607 | 26040 | -3.5198
2012-02-02 | 0.016429 | 14450 | -4.1087
2012-02-03 | 0.4989 | 438807 | -0.69535
2012-02-04 | 0.90961 | 800062 | -0.094737
2012-02-05 | 0.025274 | 22230 | -3.678
2012-02-06 | 0.067408 | 59291 | -2.697
2012-02-07 | 0.088694 | 78015 | -2.4226
2012-02-08 | 0.01001 | 8805 | -4.6042
2012-02-09 | 0.76907 | 676488 | -0.26257
2012-02-10 | 1.5344 | 1349658 | 0.42811
2012-02-11 | 1.5129 | 1330816 | 0.41404
2012-02-12 | 1.7105 | 1504645 | 0.53679
2012-02-13 | 0.93666 | 823938 | -0.065435
2012-02-14 | 0.029734 | 26156 | -3.5155
2012-02-15 | 0.1421 | 124998 | -1.9513
2012-02-16 | 0.090751 | 79832 | -2.3996
2012-02-17 | 0.32378 | 284828 | -1.1277
2012-02-18 | 0.24211 | 212986 | -1.4184
2012-02-19 | 1.7881 | 1572982 | 0.58113
2012-02-20 | 0.1416 | 124569 | -1.9548
2012-02-21 | 0.062657 | 55122 | -2.7701
2012-02-22 | 0.0050287 | 4424 | -5.2926
2012-02-23 | 0.20093 | 176772 | -1.6048
2012-02-24 | 0.81379 | 715950 | -0.20605
2012-02-25 | 0.12437 | 109418 | -2.0845
2012-02-26 | 0.026282 | 23123 | -3.6389
2012-02-27 | 0.10899 | 95890 | -2.2165
2012-02-28 | 0.38982 | 342970 | -0.94206
2012-02-29 | 0.55801 | 490949 | -0.58338
2012-03-01 | 1.0939 | 962409 | 0.089712
2012-03-02 | 0.32998 | 290331 | -1.1087
2012-03-03 | 0.28636 | 251958 | -1.2505
2012-03-04 | 0.49634 | 436711 | -0.70049
2012-03-05 | 0.86832 | 764008 | -0.1412
2012-03-06 | 0.016975 | 14936 | -4.076
2012-03-07 | 0.58906 | 518306 | -0.52923
2012-03-08 | 1.2423 | 1093139 | 0.217
2012-03-09 | 0.28519 | 250940 | -1.2546
2012-03-10 | 0.021302 | 18744 | -3.849
2012-03-11 | 0.13561 | 119327 | -1.998
2012-03-12 | 0.19138 | 168402 | -1.6535
2012-03-13 | 0.094403 | 83070 | -2.3602
2012-03-14 | 0.038362 | 33757 | -3.2607
2012-03-15 | 0.042022 | 36978 | -3.1696
2012-03-16 | 0.45322 | 398823 | -0.79138
2012-03-17 | 0.10931 | 96189 | -2.2136
2012-03-18 | 0.010064 | 8856 | -4.5988
2012-03-19 | 0.49013 | 431320 | -0.71309
2012-03-20 | 0.013055 | 11489 | -4.3386
2012-03-21 | 0.053904 | 47437 | -2.9206
2012-03-22 | 0.04461 | 39259 | -3.1098
2012-03-23 | 0.58259 | 512711 | -0.54027
2012-03-24 | 0.19553 | 172076 | -1.6321
2012-03-25 | 0.17336 | 152567 | -1.7524
2012-03-26 | 0.062484 | 54991 | -2.7728
2012-03-27 | 0.17441 | 153498 | -1.7463
2012-03-28 | 2.0204 | 1778174 | 0.7033
2012-03-29 | 0.16893 | 148678 | -1.7783
2012-03-30 | 0.069381 | 61064 | -2.6681
2012-03-31 | 0.05395 | 47483 | -2.9197
2012-04-01 | 0.11561 | 101756 | -2.1575
2012-04-02 | 0.099222 | 87331 | -2.3104
2012-04-03 | 0.14678 | 129195 | -1.9188
2012-04-04 | 0.069844 | 61475 | -2.6615
2012-04-05 | 0.0063896 | 5624 | -5.0531
2012-04-06 | 0.09973 | 87782 | -2.3053
2012-04-07 | 0.023699 | 20860 | -3.7423
2012-04-08 | 0.45516 | 400641 | -0.7871
2012-04-09 | 0.11539 | 101573 | -2.1594
2012-04-10 | 0.2251 | 198140 | -1.4912
2012-04-11 | 0.49738 | 437819 | -0.6984
2012-04-12 | 0.082881 | 72957 | -2.4903
2012-04-13 | 0.19592 | 172466 | -1.63
2012-04-14 | 0.0075226 | 6622 | -4.8898
2012-04-15 | 0.022703 | 19985 | -3.7853
2012-04-16 | 0.023123 | 20355 | -3.7669
2012-04-17 | 0.16799 | 147884 | -1.7838
2012-04-18 | 0.86487 | 761364 | -0.14517
2012-04-19 | 0.11435 | 100664 | -2.1685
2012-04-20 | 0.23047 | 202891 | -1.4676
2012-04-21 | 0.0084569 | 7445 | -4.7728
2012-04-22 | 0.12798 | 112667 | -2.0559
2012-04-23 | 0.047528 | 41842 | -3.0464
2012-04-24 | 0.29536 | 260028 | -1.2196
2012-04-25 | 0.45828 | 403462 | -0.78028
2012-04-26 | 0.00026806 | 236 | -8.2243
2012-04-27 | 0.0082643 | 7276 | -4.7958
2012-04-28 | 0.2633 | 231818 | -1.3344
2012-04-29 | 0.0084538 | 7443 | -4.7731
2012-04-30 | 0.029802 | 26239 | -3.5132
2012-05-01 | 0.00055653 | 490 | -7.4938
2012-05-02 | 0.56293 | 495637 | -0.5746
2012-05-03 | 0.069832 | 61485 | -2.6617
2012-05-04 | 0.058635 | 51627 | -2.8364
2012-05-05 | 0.0059308 | 5222 | -5.1276
2012-05-06 | 0.00089267 | 786 | -7.0213
2012-05-07 | 0.012098 | 10652 | -4.4148
2012-05-08 | 0.075766 | 66714 | -2.5801
2012-05-09 | 0.40334 | 355152 | -0.90798
2012-05-10 | 0.13916 | 122533 | -1.9722
2012-05-11 | 0.038274 | 33702 | -3.263
2012-05-12 | 0.33025 | 290803 | -1.1079
2012-05-13 | 0.14061 | 123817 | -1.9618
2012-05-14 | 0.084338 | 74267 | -2.4729
2012-05-15 | 0.23077 | 203214 | -1.4663
2012-05-16 | 0.016575 | 14596 | -4.0999
2012-05-17 | 0.33336 | 293565 | -1.0985
2012-05-18 | 0.039953 | 35184 | -3.22
2012-05-19 | 0.055384 | 48773 | -2.8935
2012-05-20 | 0.0083814 | 7381 | -4.7817
2012-05-21 | 0.036758 | 32371 | -3.3034
2012-05-22 | 0.01566 | 13791 | -4.1567
2012-05-23 | 0.02512 | 22123 | -3.6841
2012-05-24 | 0.14239 | 125397 | -1.9492
2012-05-25 | 4.2578 | 3749825 | 1.4488
2012-05-26 | 2.9913 | 2634416 | 1.0957
2012-05-27 | 0.16156 | 142286 | -1.8229
2012-05-28 | 0.1238 | 109035 | -2.0891
2012-05-29 | 0.09079 | 79962 | -2.3992
2012-05-30 | 0.0041453 | 3651 | -5.4858
2012-05-31 | 0.052232 | 46004 | -2.9521
2012-06-01 | 0.032922 | 28997 | -3.4136
2012-06-02 | 0.39159 | 344904 | -0.93754
2012-06-03 | 0.031294 | 27563 | -3.4643
2012-06-04 | 0.34029 | 299728 | -1.078
2012-06-05 | 4.2848 | 3774114 | 1.4551
2012-06-06 | 1.2141 | 1069401 | 0.194
2012-06-07 | 0.015715 | 13842 | -4.1532
2012-06-08 | 0.094466 | 83209 | -2.3595
2012-06-09 | 0.10987 | 96776 | -2.2085
2012-06-10 | 0.21271 | 187370 | -1.5478
2012-06-11 | 0.063446 | 55888 | -2.7576
2012-06-12 | 0.30559 | 269189 | -1.1855
2012-06-13 | 0.035272 | 31071 | -3.3447
2012-06-14 | 0.028394 | 25012 | -3.5616
2012-06-15 | 0.32867 | 289529 | -1.1127
2012-06-16 | 0.02549 | 22455 | -3.6695
2012-06-17 | 0.44326 | 390477 | -0.81361
2012-06-18 | 0.23384 | 206001 | -1.4531
2012-06-19 | 0.02663 | 23460 | -3.6257
2012-06-20 | 0.28419 | 250362 | -1.2581
2012-06-21 | 0.15942 | 140441 | -1.8362
2012-06-22 | 0.18902 | 166523 | -1.6659
2012-06-23 | 0.064634 | 56942 | -2.739
2012-06-24 | 0.17985 | 158447 | -1.7156
2012-06-25 | 0.01092 | 9621 | -4.5171
2012-06-26 | 0.062679 | 55222 | -2.7697
2012-06-27 | 0.23849 | 210118 | -1.4334
2012-06-28 | 0.0091914 | 8098 | -4.6895
2012-06-29 | 0.035699 | 31453 | -3.3326
2012-06-30 | 0.13558 | 119453 | -1.9982
Contents

## 1e. STPIS Exclusions
Endeavour Energy
STPIS Data Reporting
2012-13
Exclusions
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Table 1: Exclusions
Date of event (DD/MM/YYYY) | Outage ID | Feeder ID / name | Feeder classification | Cause of event | Number of customers interrupted | Duration of interruption (mins) | Total unplanned customer minutes off supply | Event category (Use Exclusion categories listed in section 3.3 (a) of the AER's STPIS) | Unplanned SAIDI impact | Unplanned SAIFI impact | Further information (Please provide separate explanation to confirm the outage was not due to inadequate transmission connection planning)
2012-12-18 | 1578631-1 | NE1212 | CBD;Urban;Rural short; Rural long | Transmission failure | 152 | 336 | 32694 | 6 | 0.037 | 0.0017134 | OH Earth Wire dropped down in TG 132kV Bus Section A @ Sydney West Transmission Sub -
Weather
Equipment failure
Operational error
Vegetation
Animals
Third party impacts
Transmission failure
Load shedding
Inter-distributor connection failure
Other
Contents

## 1f. STPIS GSL
Endeavour Energy
STPIS Data Reporting - AER Definitions
2012-13
Guaranteed Service Level
This information is collected to inform the application of the STPIS to the DNSP in future regulatory periods. The information is also collected to monitor network performance, and may be used in performance reports.
Did the AER's GSL Scheme apply at any time during the regulatory year? | No
If the AER's GSL scheme applied at any time during the regulatory year, table 1 must be completed. Do not complete table 1 if the AER's GSL scheme did not apply during the regulatory year.
Table 1: Guaranteed service levels - AER GSL scheme
Reliability of supply
Frequency of interruptions CBD feeders – 9 interruptions
Low reliability payments - 9 interruptions - ($)
Frequency of interruptions Urban feeders – 9 interruptions
Low reliability payments - 9 interruptions - ($)
Frequency of interruptions Rural (short and long) feeders – 15 interruptions
Low reliability payments - 15 interruptions - ($)
Duration of interruptions CBD feeders – 12 hours
Low reliability payments - 12 hours - ($)
Duration of interruptions urban feeders – 12 hours
Low reliability payments - 12 hours - ($)
Duration of interruptions Rural (short and long) feeders – 18 hours
Low reliability payments - 18 hours - ($)
Total duration of interruptions Level 1 – 20 hours
Low reliability payments - 20 hours - ($)
Total duration of interruptions Level 2 – 30 hours
Low reliability payments - 30 hours - ($)
Total duration of interruptions Level 3 – 60 hours
Low reliability payments - 60 hours - ($)
Street lights
Streetlight repair 5 days - GSL payments - number
Street lights - GSL payments - ($)
New connections
Connections made
Connection not made on or before the day agreed - number
Connection not made on or before the day agreed - ($)
Connections - GSL payments - 1-6 day delay - number
Connections - GSL payments - 1-6 day delay - ($)
Connections - GSL payments - 7+ day delay - number
Connections - GSL payments - 7+ day delay - ($)
Planned interruptions
Notice of planned interruptions - 4 days not given - number
Notice of planned interruptions - 4 days not given - ($)
Total GSL payments payable under the AER's GSL scheme ($) | 0
Contents

## 2. Demand
Endeavour Energy
Demand
2012-13
The information is required to assess forecasts against outturn demand, and will inform the AER’s review of demand forecasts in future regulatory proposals. The information may be used in performance reports.
Note: a) Forecasts should be the demand forecasts for the relevant regulatory year that were made at the time of the regulatory proposal
b) t+1 forecasts should be the latest updates to the demand forecasts for the regulatory year t+1.
c) The PoE level only applies to the forecasts
Table 1: Maximum coincident demand at the network level
Network coincident maximum demand | Forecast | Actual - raw | Actual - weather normalised | Variation % | t+1 forecast
90% PoE level
Network coincident maximum demand (MW)
Network coincident maximum demand (MVA)
50% PoE level
Network coincident maximum demand (MW) | 4663 | 3708 | 3340 | -20.48% | 3660
Network coincident maximum demand (MVA)
10% PoE level
Network coincident maximum demand (MW) | 4855 | 3708 | 3657 | -23.63% | 4001
Network coincident maximum demand (MVA)
Table 2: Summer and winter non-coincident maximum demand by zone substation
Summer and winter maximum demand - ZS | [12 empty] | t+1 forecast |  |  |  | Nameplate rating (MVA)
POE level = 50% | Forecast |  |  |  | Actual - raw |  |  |  | Actual - weather normalised
Location | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF
albion_park Summer | 25.8987 | 28.1802 | 11.1078 | 0.91904 | 22.48 | 24.9832 | -10.9 | 0.8998 | 18.6176 | 20.6907 | 9.0272 | 0.8998 | 20.5761 | 22.8673 | 9.9768 | 0.8998 | 37.5
albion_park Winter | 24.1282 | 25.2973 | 7.6016 | 0.95378 | 18.07 | 18.8653 | -5.42 | 0.95784 | 16.5506 | 17.399 | 5.3666 | 0.95124 | 16.5506 | 17.399 | 5.3666 | 0.95124 | 37.5
ambarvale Summer | 32.6186 | 33.4828 | 7.5579 | 0.97419 | 32.094 | 32.479 | 4.986 | 0.98815 | 23.8071 | 24.0927 | 3.6986 | 0.98815 | 26.4845 | 26.8682 | 4.5246 | 0.98572 | 70
ambarvale Winter | 24.3974 | 24.471 | 1.8964 | 0.99699 | 18.63 | 18.6395 | 0.594 | 0.99949 | 17.8685 | 17.8776 | 0.56975 | 0.99949 | 17.8685 | 17.9052 | 1.1443 | 0.99796 | 70
anzac_village Summer | 51.3172 | 53.1883 | 13.9836 | 0.96482 | 28.03 | 29.1383 | 7.96 | 0.96196 | 24.7326 | 25.7106 | 7.0235 | 0.96196 | 27.9678 | 29.3566 | 8.9225 | 0.95269 | 75
anzac_village Winter | 44.9951 | 46.6619 | 12.3599 | 0.96428 | 20.64 | 20.6784 | -1.26 | 0.99814 | 19.8271 | 19.864 | 1.2104 | 0.99814 | 24.0349 | 24.2189 | 2.9794 | 0.9924 | 75
appin Summer | 6.5758 | 7.6246 | 3.8592 | 0.86245 | 4.824 | 5.2064 | 1.9584 | 0.92656 | 3.6775 | 3.969 | 1.4929 | 0.92656 | 3.7519 | 4.0406 | 1.4998 | 0.92856 | 15
appin Winter | 5.0219 | 5.389 | 1.9551 | 0.93187 | 4.896 | 5.0759 | 1.3392 | 0.96457 | 4.896 | 5.0759 | 1.3392 | 0.96457 | 4.896 | 5.1055 | 1.4476 | 0.95896 | 15
arndell_park Summer | 50.7985 | 52.3701 | 12.7334 | 0.96999 | 43.995 | 44.2879 | 5.085 | 0.99339 | 41.5455 | 41.8221 | 4.8019 | 0.99339 | 43.2242 | 43.9515 | 7.9627 | 0.98345 | 90
arndell_park Winter | 50.9326 | 52.0504 | 10.7287 | 0.97853 | 34.152 | 34.3375 | 3.564 | 0.9946 | 33.0381 | 33.2175 | 3.4478 | 0.9946 | 32.3786 | 32.5039 | 2.8513 | 0.99615 | 90
baulkham_hills_11kv Summer | 53.8382 | 58.3098 | 22.3937 | 0.92331 | 32.1 | 33.6514 | 10.1 | 0.9539 | 26.9777 | 29.1966 | 11.1646 | 0.924 | 33.1375 | 35.8631 | 13.7138 | 0.924 | 90
baulkham_hills_11kv Winter | 33.4176 | 34.8657 | 9.944 | 0.95847 | 23.94 | 24.6326 | 5.8 | 0.97188 | 22.9671 | 24.8562 | 9.5048 | 0.924 | 23.6768 | 25.6242 | 9.7985 | 0.924 | 90
bella_vista Summer | 50.1451 | 51.7819 | 12.9165 | 0.96839 | 53.76 | 55.6552 | 14.4 | 0.96595 | 50.0726 | 51.8378 | 13.4124 | 0.96595 | 65.3728 | 67.6774 | 17.5107 | 0.96595 | 135
bella_vista Winter | 57.4678 | 60.0122 | 17.2892 | 0.9576 | 37.5 | 37.5192 | 1.2 | 0.99949 | 36.3063 | 36.3249 | 1.162 | 0.99949 | 37.1059 | 37.1249 | 1.1875 | 0.99949 | 135
berry Summer | 10.2792 | 10.9927 | 3.8959 | 0.93509 | 8.7305 | 9.0909 | 2.5346 | 0.96035 | 7.4468 | 7.7543 | 2.1619 | 0.96035 | 7.4262 | 7.7676 | 2.2775 | 0.95605 | 30
berry Winter | 9.2563 | 9.5694 | 2.4277 | 0.96728 | 7.612 | 7.7573 | 1.4946 | 0.98126 | 7.612 | 7.7573 | 1.4946 | 0.98126 | 7.612 | 7.7467 | 1.4388 | 0.9826 | 30
blackheath Summer | 5.9499 | 6.1198 | 1.4323 | 0.97223 | 4.84 | 4.9505 | 1.04 | 0.97768 | 4.84 | 4.9505 | 1.04 | 0.97768 | 4.928 | 5.0596 | 1.1462 | 0.974 | 14
blackheath Winter | 8.1491 | 8.3533 | 1.8357 | 0.97555 | 6.76 | 6.8801 | 1.28 | 0.98254 | 6.76 | 6.8801 | 1.28 | 0.98254 | 6.76 | 6.9063 | 1.4141 | 0.97881 | 14
blackmans_flat Summer | 6.0372 | 6.6756 | 2.8488 | 0.90437 | 4.392 | 4.5286 | 1.104 | 0.96983 | 4.392 | 4.5286 | 1.104 | 0.96983 | 7.6506 | 7.8886 | 1.9231 | 0.96983 | 20
blackmans_flat Winter | 6.647 | 6.9449 | 2.0122 | 0.9571 | 5.4 | 5.559 | 1.32 | 0.9714 | 5.4 | 5.559 | 1.32 | 0.9714 | 6.1744 | 6.3783 | 1.5999 | 0.96803 | 20
blaxland Summer | 26.8826 | 27.7326 | 6.8134 | 0.96935 | 24.24 | 25.7499 | 8.688 | 0.94136 | 20.8594 | 22.1587 | 7.4763 | 0.94136 | 23.1063 | 24.5456 | 8.2817 | 0.94136 | 70
blaxland Winter | 25.2853 | 25.4376 | 2.7794 | 0.99401 | 19.44 | 19.5394 | -1.968 | 0.99491 | 19.44 | 20.0324 | 4.8356 | 0.97043 | 20.162 | 20.7764 | 5.0152 | 0.97043 | 70
bolong Summer | 3.8059 | 4.2073 | 1.7934 | 0.9046 | 2.6147 | 2.8213 | 1.0598 | 0.92676 | 2.6147 | 2.8213 | 1.0598 | 0.92676 | 2.6147 | 2.7408 | 0.82176 | 0.95399 | 12.5
bolong Winter | 3.0347 | 3.1958 | 1.0018 | 0.9496 | 4.9236 | 5.0429 | 1.0902 | 0.97635 | 4.9236 | 5.0429 | 1.0902 | 0.97635 | 4.9236 | 5.0249 | 1.0036 | 0.97985 | 12.5
bomaderry Summer | 23.845 | 26.1461 | 10.7254 | 0.91199 | 20.3148 | 21.1776 | 5.9832 | 0.95926 | 17.2144 | 17.9455 | 5.0701 | 0.95926 | 19.4395 | 20.5569 | 6.6854 | 0.94564 | 45
bomaderry Winter | 21.1851 | 21.7119 | 4.7539 | 0.97574 | 15.5427 | 15.8074 | 2.8808 | 0.98325 | 14.5076 | 14.7547 | 2.6889 | 0.98325 | 14.906 | 15.2569 | 3.2533 | 0.977 | 45
bonnyrigg Summer | 75.1901 | 79.234 | 24.9893 | 0.94896 | 49.68 | 50.9982 | 11.52 | 0.97415 | 42.3528 | 43.4765 | 9.8209 | 0.97415 | 51.99 | 53.3695 | 12.0557 | 0.97415 | 105
bonnyrigg Winter | 60.5331 | 62.7216 | 16.424 | 0.96511 | 36 | 36.0288 | 1.44 | 0.9992 | 33.8473 | 33.8744 | 1.3539 | 0.9992 | 34.273 | 34.3005 | 1.371 | 0.9992 | 105
bossley_park Summer | 42.7548 | 43.7058 | 9.0678 | 0.97824 | 29.808 | 29.9684 | 3.096 | 0.99465 | 27.6997 | 27.8487 | 2.877 | 0.99465 | 33.1783 | 33.3905 | 3.7591 | 0.99364 | 70
bossley_park Winter | 29.1298 | 29.1515 | 1.1229 | 0.99926 | 19.896 | 19.9628 | 1.632 | 0.99665 | 19.5876 | 19.6534 | 1.6067 | 0.99665 | 19.5876 | 19.6562 | 1.6411 | 0.99651 | 70
bow_bowing Summer | 61.2964 | 63.6003 | 16.9634 | 0.96377 | 46.224 | 47.4149 | 10.56 | 0.97488 | 46.224 | 47.4149 | 10.56 | 0.97488 | 45.4351 | 46.0716 | 7.6319 | 0.98618 | 105
bow_bowing Winter | 56.5211 | 57.0113 | 7.4603 | 0.9914 | 42.144 | 42.1479 | -0.576 | 0.99991 | 42.144 | 42.1479 | 0.57607 | 0.99991 | 42.144 | 42.4647 | 5.2091 | 0.99245 | 105
bowral Summer | 20.1212 | 23.081 | 11.3079 | 0.87177 | 17.2286 | 18.4833 | 6.694 | 0.93211 | 14.306 | 15.3479 | 5.5584 | 0.93211 | 15.4033 | 15.6322 | 2.6656 | 0.98535 | 32.5
bowral Winter | 23.1527 | 24.6254 | 8.3881 | 0.9402 | 19.1178 | 19.2324 | 2.0965 | 0.99404 | 19.1178 | 19.2324 | 2.0965 | 0.99404 | 19.5708 | 19.6985 | 2.2396 | 0.99352 | 32.5
bringelly Summer | 28.9829 | 31.1372 | 11.3807 | 0.93081 | 13.23 | 13.2433 | 0.594 | 0.99899 | 12.7847 | 12.7975 | 0.57401 | 0.99899 | 11.4915 | 11.6091 | 1.6483 | 0.98987 | 44
bringelly Winter | 28.3681 | 29.8153 | 9.1764 | 0.95146 | 10.008 | 10.0198 | 0.486 | 0.99882 | 9.6573 | 10.0933 | 2.9345 | 0.9568 | 8.7673 | 8.8753 | 1.3805 | 0.98783 | 44
bulli Summer | 11.2602 | 12.1469 | 4.5558 | 0.927 | 10.128 | 10.5698 | 3.024 | 0.9582 | 8.9305 | 9.3201 | 2.6665 | 0.9582 | 9.58 | 10.027 | 2.9605 | 0.95542 | 20
bulli Winter | 14.739 | 15.2447 | 3.8936 | 0.96683 | 10.656 | 10.8362 | -1.968 | 0.98337 | 10.2949 | 10.469 | 1.9013 | 0.98337 | 10.2949 | 10.4398 | 1.7337 | 0.98611 | 20
bylong Summer | 0.40309 | 0.42312 | 0.12865 | 0.95265 | 0.3996 | 0.40961 | 0.09 | 0.97556 | 0.3996 | 0.40961 | 0.09 | 0.97556 | 0.3996 | 0.41665 | 0.11796 | 0.95909 | 3
bylong Winter | 0.47173 | 0.49177 | 0.13894 | 0.95926 | 0.306 | 0.30704 | -0.0252 | 0.99663 | 0.306 | 0.30704 | 0.0252 | 0.99663 | 0.306 | 0.31193 | 0.06054 | 0.98099 | 3
cabramatta Summer | 29.5598 | 30.9451 | 9.1552 | 0.95523 | 22.104 | 22.2932 | 2.898 | 0.99151 | 20.5176 | 20.6931 | 2.69 | 0.99151 | 13.7684 | 14.2987 | 3.8579 | 0.96291 | 50
cabramatta Winter | 26.9056 | 27.184 | 3.8805 | 0.98976 | 20.466 | 20.625 | 2.556 | 0.99229 | 17.4771 | 17.6128 | 2.1827 | 0.99229 | 17.4771 | 17.7106 | 2.8665 | 0.98681 | 50
cambridge_park Summer | 32.7743 | 33.3892 | 6.3785 | 0.98158 | 23.9335 | 23.965 | 1.229 | 0.99868 | 19.9354 | 19.9617 | 1.0237 | 0.99868 | 17.887 | 18.1275 | 2.9432 | 0.98673 | 50
cambridge_park Winter | 25.6581 | 25.8707 | 3.3099 | 0.99178 | 17.7119 | 17.7445 | -1.0748 | 0.99816 | 17.7119 | 17.7445 | 1.0748 | 0.99816 | 13.2003 | 13.3854 | 2.2182 | 0.98617 | 50
camden Summer | 54.3216 | 57.1387 | 17.72 | 0.9507 | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 75
camden Winter | 43.24 | 43.7726 | 6.8077 | 0.98783 | 30.144 | 30.1495 | -0.576 | 0.99982 | 29.2827 | 29.2881 | 0.55956 | 0.99982 | na | na | na | #VALUE! | 75
campbelltown Summer | 57.6689 | 59.2869 | 13.7562 | 0.97271 | 57.11 | 59.7369 | 17.52 | 0.95603 | 51.195 | 53.5498 | 15.7053 | 0.95603 | 53.0465 | 56.961 | 20.7516 | 0.93128 | 105
campbelltown Winter | 46.9495 | 47.3966 | 6.4945 | 0.99057 | 36.59 | 36.7647 | 3.58 | 0.99525 | 36.59 | 36.7647 | 3.5798 | 0.99525 | 37.9074 | 38.1559 | 4.3479 | 0.99349 | 105
canley_vale Summer | 28.3475 | 29.7631 | 9.0699 | 0.95244 | 25.596 | 25.7698 | 2.988 | 0.99326 | 25.596 | 25.7698 | 2.988 | 0.99326 | 28.4613 | 28.6545 | 3.3225 | 0.99326 | 75
canley_vale Winter | 29.575 | 29.6536 | 2.1583 | 0.99735 | 23.076 | 23.1461 | 1.8 | 0.99697 | 22.5901 | 22.6587 | 1.7621 | 0.99697 | 22.5901 | 22.6587 | 1.7621 | 0.99697 | 45
carramar Summer | 21.0352 | 21.3986 | 3.9269 | 0.98302 | 16.992 | 17.0002 | -0.528 | 0.99952 | 15.9204 | 15.9281 | 0.49463 | 0.99952 | 17.5575 | 17.6777 | 2.0579 | 0.9932 | 50
carramar Winter | 19.2311 | 19.4491 | 2.9036 | 0.98879 | 13.632 | 13.6328 | -0.144 | 0.99994 | 13.1784 | 13.1792 | 0.13925 | 0.99994 | 13.1784 | 13.2015 | 0.77985 | 0.99825 | 50
castle_hill Summer | 36.7321 | 37.7612 | 8.7558 | 0.97275 | 21.264 | 21.6165 | 3.888 | 0.98369 | 20.0833 | 20.4162 | 3.6721 | 0.98369 | 21.356 | 21.71 | 3.9048 | 0.98369 | 75
castle_hill Winter | 30.3274 | 31.0675 | 6.7407 | 0.97618 | 19.872 | 19.9839 | 2.112 | 0.9944 | 18.2804 | 18.3833 | 1.9428 | 0.9944 | 13.7401 | 13.8175 | 1.4603 | 0.9944 | 75
cattai Summer | 15.0523 | 16.8746 | 7.6278 | 0.892 | 10.92 | 11.7435 | 4.32 | 0.92988 | 10.5683 | 11.3652 | 4.1809 | 0.92988 | 11.9017 | 12.9922 | 5.2103 | 0.91606 | 40
cattai Winter | 11.8781 | 12.6508 | 4.3534 | 0.93892 | 7.32 | 7.5381 | 1.8 | 0.97107 | 7.2585 | 7.4747 | 1.7849 | 0.97107 | 7.4929 | 7.8179 | 2.2307 | 0.95843 | 40
cheriton_avenue Summer | 43.2203 | 45.4951 | 14.2058 | 0.95 | 30.1 | 30.4495 | 4.6 | 0.98852 | 30.1 | 30.4495 | 4.6 | 0.98852 | 43.9685 | 44.479 | 6.7194 | 0.98852 | 90
cheriton_avenue Winter | 34.7383 | 36.5667 | 11.4179 | 0.95 | na | na | na | #VALUE! | na | na | na | #VALUE! | 16.2274 | 17.0815 | 5.3337 | 0.95 | 90
corrimal Summer | 14.9204 | 15.211 | 2.959 | 0.9809 | 17.78 | 17.7812 | 0.21 | 0.99993 | 14.66 | 14.661 | 0.17033 | 0.99993 | 15.6853 | 15.7167 | 0.99351 | 0.998 | 38
corrimal Winter | 20.5956 | 20.6361 | 1.2919 | 0.99804 | 16.0704 | 16.0853 | -0.6912 | 0.99908 | 15.4728 | 15.4871 | 0.6655 | 0.99908 | 15.4728 | 15.5038 | 0.98005 | 0.998 | 38
cranebrook Summer | 61.9455 | 62.473 | 8.101 | 0.99156 | 39.7288 | 39.774 | 1.8971 | 0.99886 | 37.4714 | 37.5141 | 1.7893 | 0.99886 | 37.6565 | 37.9753 | 4.9104 | 0.9916 | 75
cranebrook Winter | 38.6044 | 39.2975 | 7.3477 | 0.98236 | 35.5033 | 35.6876 | 3.622 | 0.99484 | 35.5033 | 35.6876 | 3.6219 | 0.99484 | 31.673 | 31.9495 | 4.1943 | 0.99135 | 75
culburra Summer | 9.6091 | 9.8084 | 1.9672 | 0.97968 | 10.656 | 11.2756 | 3.6864 | 0.94505 | 10.656 | 11.2756 | 3.6864 | 0.94505 | 10.656 | 11.2756 | 3.6864 | 0.94505 | 20
culburra Winter | 12.5707 | 12.9143 | 2.9593 | 0.97339 | 11.2032 | 11.5257 | 2.7072 | 0.97202 | 11.2032 | 11.5257 | 2.7072 | 0.97202 | 11.2032 | 11.5257 | 2.7072 | 0.97202 | 20
dapto Summer | 42.2882 | 43.6574 | 10.8478 | 0.96864 | 33.15 | 33.3965 | -4.05 | 0.99262 | 32.2092 | 32.4487 | 3.9352 | 0.99262 | 32.5399 | 32.7737 | 3.9076 | 0.99287 | 75
dapto Winter | 29.0564 | 29.4354 | 4.7082 | 0.98712 | 23.52 | 23.5858 | -1.76 | 0.99721 | 21.6526 | 21.7132 | 1.6208 | 0.99721 | 21.6526 | 21.9279 | 3.4636 | 0.98745 | 75
darkes_forest Summer | 1.2077 | 1.7444 | 1.2588 | 0.69231 | 0.9264 | 1.0434 | 0.48 | 0.88789 | 0.9264 | 1.0434 | 0.48 | 0.88789 | 0.3905 | 0.46635 | 0.25494 | 0.83735 | 10
darkes_forest Winter | 1.279 | 1.5572 | 0.88821 | 0.82137 | 1.5156 | 1.5909 | 0.4836 | 0.95268 | 1.5156 | 1.5909 | 0.4836 | 0.95268 | 1.5156 | 1.5806 | 0.44878 | 0.95885 | 10
doonside Summer | 50.7718 | 54.9448 | 21.0037 | 0.92405 | 27.2747 | 28.2357 | 7.3038 | 0.96596 | 22.8739 | 23.6799 | 6.1254 | 0.96596 | 40.0199 | 42.2737 | 13.6189 | 0.94669 | 50
doonside Winter | 35.3424 | 36.7232 | 9.9756 | 0.9624 | 19.688 | 20.0362 | 3.7191 | 0.98262 | 19.2353 | 19.5754 | 3.6336 | 0.98262 | 38.8687 | 39.9547 | 9.2522 | 0.97282 | 50
dundas Summer | 51.758 | 52.5653 | 9.1772 | 0.98464 | 40.7985 | 41.1086 | 5.0398 | 0.99246 | 32.2199 | 32.4648 | 3.9801 | 0.99246 | 40.3602 | 40.8373 | 6.224 | 0.98832 | 105
dundas Winter | 45.2747 | 46.077 | 8.5608 | 0.98259 | 42.2823 | 42.447 | 3.7353 | 0.99612 | 33.5345 | 33.9292 | 5.1605 | 0.98837 | 36.922 | 37.3897 | 5.8958 | 0.98749 | 105
eastern_creek Summer | 49.0502 | 54.269 | 23.2209 | 0.90383 | 16.5 | 16.9546 | 3.9 | 0.97318 | 16.5 | 16.9546 | 3.9 | 0.97318 | 18.2081 | 18.761 | 4.5211 | 0.97053 | 90
eastern_creek Winter | 41.7419 | 47.973 | 23.6436 | 0.87011 | 14.4 | 14.7092 | 3 | 0.97898 | 14.4 | 14.7092 | 3 | 0.97898 | 16.5748 | 17.0718 | 4.0894 | 0.97089 | 90
emu_plains Summer | 41.1326 | 42.9348 | 12.3088 | 0.95802 | 28.49 | 28.4907 | -0.2 | 0.99998 | 25.7776 | 25.7783 | 0.1807 | 0.99998 | 30.4954 | 30.9084 | 5.0355 | 0.98664 | 75
emu_plains Winter | 36.1229 | 36.8449 | 7.2581 | 0.98041 | 24.66 | 24.6608 | -0.2 | 0.99997 | 24.1289 | 24.1326 | 0.42672 | 0.99984 | 25.3552 | 25.8687 | 5.1286 | 0.98015 | 75
fairfield Summer | 42.1042 | 45.0497 | 16.0222 | 0.93462 | 27.42 | 27.5275 | -2.43 | 0.99609 | 27.42 | 27.5275 | 2.4304 | 0.99609 | 27.7262 | 28.5381 | 6.7586 | 0.97155 | 75
fairfield Winter | 37.0772 | 38.9624 | 11.9726 | 0.95162 | 24.13 | 24.2873 | -2.76 | 0.99352 | 24.13 | 24.2873 | 2.7597 | 0.99352 | 24.13 | 24.5261 | 4.3902 | 0.98385 | 75
gerringong Summer | 6.7209 | 7.477 | 3.2764 | 0.89887 | 5.72 | 5.8817 | 1.3695 | 0.97251 | 5.72 | 5.8817 | 1.3695 | 0.97251 | 5.7735 | 6.048 | 1.8016 | 0.9546 | 10
gerringong Winter | 6.7651 | 7.054 | 1.9981 | 0.95905 | 6.52 | 6.7 | 1.6 | 0.97313 | 6.52 | 6.7043 | 1.561 | 0.97251 | 6.52 | 6.6913 | 1.5044 | 0.9744 | 10
glenmore_park Summer | 53.2309 | 59.027 | 25.508 | 0.90181 | 37.08 | 38.3404 | 9.75 | 0.96713 | 36.5707 | 37.8138 | 9.6161 | 0.96713 | 39.5017 | 40.8445 | 10.3868 | 0.96713 | 90
glenmore_park Winter | 31.1013 | 33.0133 | 11.0719 | 0.94208 | 20.67 | 20.8535 | 2.76 | 0.9912 | 20.2351 | 20.4147 | 2.7019 | 0.9912 | 21.595 | 21.7866 | 2.8835 | 0.9912 | 90
glossodia Summer | 18.8564 | 20.7 | 8.5395 | 0.91094 | 16.13 | 17.2627 | 6.15 | 0.93438 | 14.4521 | 15.467 | 5.5104 | 0.93438 | 16.226 | 17.4954 | 6.5425 | 0.92745 | 50
glossodia Winter | 13.4634 | 14.0317 | 3.9529 | 0.9595 | 10.6 | 10.8574 | 2.35 | 0.97629 | 10.4135 | 10.6664 | 2.3088 | 0.97629 | 11.2484 | 11.6315 | 2.9607 | 0.96706 | 50
granville Summer |  |  |  | #DIV/0! | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | na
granville Winter |  |  |  | #DIV/0! | 16.6608 | 16.764 | 1.8576 | 0.99384 | 16.6608 | 16.764 | 1.8576 | 0.99384 | na | na | na | #VALUE! | 36.5
granville 132kV Summer | 27.9585 | 29.43 | 9.1895 | 0.95 | 26.7 | 27.3991 | 6.15 | 0.97448 | 26.7 | 27.3991 | 6.15 | 0.97448 | 29.6468 | 31.2071 | 9.7444 | 0.95 | 90
granville 132kV Winter | 28.9585 | 30.4826 | 9.5182 | 0.95 | na | na | na | #VALUE! | na | na | na | #VALUE! | 28.5611 | 28.8087 | 3.769 | 0.99141 | na
greystanes Summer | 27.7803 | 28.3473 | 5.641 | 0.98 | 23.1416 | 23.1487 | 0.57401 | 0.99969 | 20.3473 | 20.3535 | 0.5047 | 0.99969 | 22.1069 | 22.1512 | 1.4 | 0.998 | 50
greystanes Winter | 26.3882 | 26.3991 | 0.75601 | 0.99959 | 16.7772 | 16.8919 | 1.9653 | 0.99321 | 15.6594 | 15.7665 | 1.8343 | 0.99321 | 15.6594 | 15.6855 | 0.90288 | 0.99834 | 50
hartley_vale Summer | 0.57246 | 0.59983 | 0.17911 | 0.95438 | 0.87 | 0.89499 | 0.21 | 0.97208 | 0.87 | 0.89499 | 0.21 | 0.97208 | 0.87 | 0.8922 | 0.19777 | 0.97512 | 5
hartley_vale Winter | 0.91267 | 0.94272 | 0.23613 | 0.96812 | 1.23 | 1.2431 | 0.18 | 0.98946 | 1.23 | 1.2431 | 0.18 | 0.98946 | 1.23 | 1.2443 | 0.18792 | 0.98853 | 5
hazelbrook Summer | 9.3682 | 9.6371 | 2.2605 | 0.9721 | 7.87 | 7.9345 | -1.01 | 0.99187 | 7.87 | 7.9345 | 1.01 | 0.99187 | 8.0942 | 8.2329 | 1.5054 | 0.98314 | 50
hazelbrook Winter | 14.4969 | 14.7352 | 2.6396 | 0.98382 | 9.81 | 9.9545 | -1.69 | 0.98548 | 9.3393 | 9.4768 | 1.6089 | 0.98548 | 9.4865 | 9.6623 | 1.8348 | 0.9818 | 50
helensburgh Summer | 19.1187 | 19.9997 | 5.8707 | 0.95595 | 11.3472 | 11.3869 | 0.9504 | 0.99651 | 11.3472 | 11.3869 | 0.95039 | 0.99651 | 9.4374 | 9.4563 | 0.59777 | 0.998 | 25
helensburgh Winter | 20.1167 | 20.7554 | 5.1093 | 0.96923 | 14.1696 | 14.1791 | 0.5184 | 0.99933 | 14.1696 | 14.1791 | 0.51838 | 0.99933 | 14.1696 | 14.198 | 0.89751 | 0.998 | 25
hinchinbrook Summer | 45.3309 | 48.4296 | 17.045 | 0.93602 | 38.8 | 40.709 | 12.32 | 0.95311 | 33.5492 | 35.1999 | 10.6527 | 0.95311 | 38.1413 | 40.1267 | 12.4659 | 0.95052 | 75
hinchinbrook Winter | 41.7977 | 44.4537 | 15.1356 | 0.94025 | 23.92 | 24.2521 | 4 | 0.9863 | 23.5908 | 24.8866 | 7.9255 | 0.94793 | 31.7093 | 33.8628 | 11.8833 | 0.9364 | 75
holroyd Summer | 38.9093 | 42.1789 | 16.2827 | 0.92248 | 31.68 | 33.2148 | 9.98 | 0.95379 | 26.4692 | 27.7515 | 8.3385 | 0.95379 | 28.7229 | 30.8448 | 11.2426 | 0.93121 | 67.25
holroyd Winter | 38.8297 | 40.951 | 13.0093 | 0.9482 | 31.16 | 31.8743 | 6.71 | 0.97759 | 31.16 | 31.8743 | 6.7101 | 0.97759 | 31.16 | 32.2388 | 8.2702 | 0.96654 | 67.25
homepride Summer | 37.9505 | 39.6276 | 11.4066 | 0.95768 | 32.2012 | 32.9055 | 6.772 | 0.97859 | 32.2012 | 32.9055 | 6.772 | 0.97859 | 35.2101 | 36.8988 | 11.035 | 0.95423 | 75
homepride Winter | 32.8656 | 33.4919 | 6.4468 | 0.9813 | 22.9695 | 23.2008 | 3.2681 | 0.99003 | 22.5934 | 22.8209 | 3.2146 | 0.99003 | 29.1276 | 29.3994 | 3.9881 | 0.99076 | 75
horsley_park Summer | 13.7692 | 14.4638 | 4.4282 | 0.95198 | 14.96 | 15.2347 | 2.88 | 0.98197 | 8.7561 | 8.9169 | 1.6857 | 0.98197 | 10.9246 | 11.3414 | 3.0463 | 0.96325 | 50
horsley_park Winter | 8.9406 | 9.6518 | 3.6363 | 0.92632 | 11.44 | 11.4411 | 0.16 | 0.9999 | 11.44 | 11.4411 | 0.16001 | 0.9999 | 11.44 | 11.688 | 2.3949 | 0.97878 | 50
hoxton_park Summer | 47.9398 | 49.7738 | 13.3869 | 0.96315 | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | na
hoxton_park Winter | 32.1977 | 32.6126 | 5.1852 | 0.98728 | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | na
huskisson Summer | 27.2673 | 29.2951 | 10.7098 | 0.93078 | 22.0464 | 23.0015 | 6.5592 | 0.95848 | 22.0464 | 23.0015 | 6.5592 | 0.95848 | 23.1371 | 24.1395 | 6.8837 | 0.95848 | 40
huskisson Winter | 30.6327 | 32.3038 | 10.2555 | 0.94827 | 18.3548 | 20.3942 | 8.8896 | 0.9 | 18.3548 | 20.3942 | 8.8896 | 0.9 | 21.8486 | 24.2762 | 10.5818 | 0.9 | 40
ilford_hall Summer | 0.47014 | 0.49598 | 0.158 | 0.9479 | 0.3264 | 0.36932 | -0.1728 | 0.88379 | 0.3264 | 0.36932 | 0.1728 | 0.88379 | 0.3264 | 0.35716 | 0.145 | 0.91388 | 2.5
ilford_hall Winter | 0.66302 | 0.69542 | 0.20978 | 0.95341 | 0.432 | 0.4618 | -0.1632 | 0.93547 | 0.432 | 0.4618 | 0.1632 | 0.93547 | 0.432 | 0.45783 | 0.15161 | 0.94358 | 2.5
inner_harbour Summer | 9.268 | 10.5407 | 5.021 | 0.87926 | 8.1936 | 9.057 | 3.8592 | 0.90467 | 8.1936 | 9.057 | 3.8592 | 0.90467 | 8.1936 | 9.057 | 3.8592 | 0.90467 | 25
inner_harbour Winter | 10.8032 | 11.941 | 5.0872 | 0.90471 | 8.8704 | 9.7859 | 4.1328 | 0.90645 | 8.8704 | 9.7859 | 4.1328 | 0.90645 | 8.8704 | 9.7859 | 4.1328 | 0.90645 | 25
jamberoo Summer | 3.436 | 3.9937 | 2.0354 | 0.86038 | 3.2321 | 3.4565 | 1.2252 | 0.93508 | 2.7539 | 2.9451 | 1.0439 | 0.93508 | 2.2668 | 2.4242 | 0.85926 | 0.93508 | 3.75
jamberoo Winter | 2.9554 | 3.0929 | 0.91197 | 0.95554 | 2.3575 | 2.419 | 0.54208 | 0.97457 | 2.3575 | 2.419 | 0.54208 | 0.97457 | 2.3575 | 2.4323 | 0.59845 | 0.96926 | 3.75
jasper_road Summer | 47.4225 | 51.1877 | 19.2688 | 0.92644 | 32.8794 | 36.5327 | 15.9242 | 0.9 | 26.9622 | 29.958 | 13.0584 | 0.9 | 31.2401 | 34.7112 | 15.1303 | 0.9 | 75
jasper_road Winter | 30.5507 | 32.1703 | 10.0789 | 0.94965 | 25.6191 | 28.4657 | 12.4079 | 0.9 | 25.4948 | 28.3276 | 12.3477 | 0.9 | 20.9357 | 22.1181 | 7.1351 | 0.94654 | 75
kandos Summer | 4.8605 | 5.0217 | 1.2622 | 0.9679 | 3.8432 | 4.2703 | 1.8614 | 0.9 | 3.8432 | 4.2703 | 1.8614 | 0.9 | 4.3165 | 4.6462 | 1.7191 | 0.92903 | 10
kandos Winter | 6.1684 | 6.2655 | 1.0987 | 0.9845 | 3.995 | 4.4389 | 1.9349 | 0.9 | 3.995 | 4.4389 | 1.9349 | 0.9 | 4.3258 | 4.439 | 0.99602 | 0.9745 | 10
kangaroo_valley Summer | 2.8131 | 3.0551 | 1.1918 | 0.92078 | 2.6058 | 2.743 | 0.8565 | 0.95 | 2.23 | 2.3474 | 0.73297 | 0.95 | 2.7786 | 3.0039 | 1.1414 | 0.925 | 7.5
kangaroo_valley Winter | 3.6003 | 3.882 | 1.4518 | 0.92744 | 3.1331 | 3.298 | 1.0298 | 0.95 | 3.1331 | 3.298 | 1.0298 | 0.95 | 3.7508 | 4.1293 | 1.727 | 0.90834 | 7.5
katoomba Summer | 16.9794 | 17.7978 | 5.335 | 0.95402 | 13.644 | 14.1579 | 3.78 | 0.9637 | 13.644 | 14.1579 | 3.78 | 0.9637 | 14.2555 | 14.7341 | 3.7248 | 0.96752 | 50
katoomba Winter | 20.4957 | 21.1295 | 5.1363 | 0.97 | 17.352 | 17.7438 | 3.708 | 0.97792 | 17.352 | 17.7438 | 3.708 | 0.97792 | 18.3044 | 18.8189 | 4.3704 | 0.97266 | 50
kellyville Summer | 21.3085 | 23.4734 | 9.8463 | 0.90777 | 21.924 | 22.206 | 3.528 | 0.9873 | 19.6467 | 19.8995 | 3.1615 | 0.9873 | 21.5267 | 22.02 | 4.6348 | 0.9776 | 50
kellyville Winter | 15.2993 | 16.1311 | 5.1132 | 0.94843 | 14.22 | 14.312 | -1.62 | 0.99357 | 14.1528 | 14.2443 | 1.6123 | 0.99357 | 12.2808 | 12.3601 | 1.3973 | 0.99359 | 50
kembla_grange Summer | 9.4911 | 9.5091 | 0.5859 | 0.9981 | 3.888 | 4.1717 | 1.512 | 0.932 | 3.888 | 4.1717 | 1.512 | 0.932 | 3.888 | 4.1717 | 1.512 | 0.932 | 20
kembla_grange Winter | 7.952 | 8.8386 | 3.8583 | 0.89969 | 4.032 | 4.5741 | 2.16 | 0.88148 | 4.032 | 4.5741 | 2.16 | 0.88148 | 4.2859 | 4.8621 | 2.296 | 0.88148 | 20
kemps_creek Summer | 8.5476 | 8.7365 | 1.807 | 0.97838 | 13.752 | 13.7776 | 0.84 | 0.99814 | 13.752 | 13.7776 | 0.84001 | 0.99814 | 14.4842 | 14.7881 | 2.9828 | 0.97945 | 50
kemps_creek Winter | 9.7424 | 9.785 | 0.9121 | 0.99565 | 11.4 | 11.6499 | 2.4 | 0.97855 | 9.2595 | 9.4624 | 1.9494 | 0.97855 | 9.2595 | 9.3949 | 1.5897 | 0.98558 | 50
kenny_street Summer | 26.8603 | 30.5789 | 14.6147 | 0.8784 | 17.7401 | 19.4371 | 7.9429 | 0.91269 | 17.1447 | 18.7848 | 7.6763 | 0.91269 | 17.9234 | 19.981 | 8.8312 | 0.89702 | 50
kenny_street Winter | 22.9341 | 25.8804 | 11.9926 | 0.88616 | 14.6338 | 15.5808 | 5.3491 | 0.93922 | 14.6338 | 15.6733 | 5.6127 | 0.93368 | 14.6338 | 16.0514 | 6.5953 | 0.91169 | 50
kenthurst Summer | 31.0707 | 32.8812 | 10.7604 | 0.94494 | 21.816 | 22.179 | 3.996 | 0.98364 | 17.7997 | 18.0959 | 3.2603 | 0.98364 | 15.4093 | 15.8941 | 3.8956 | 0.9695 | 50
kenthurst Winter | 28.8632 | 30.9412 | 11.1479 | 0.93284 | 16.632 | 16.8218 | 2.52 | 0.98872 | 16.4489 | 16.6367 | 2.4923 | 0.98872 | 11.2059 | 11.4039 | 2.1159 | 0.98264 | 50
kentlyn Summer | 35.3642 | 35.5806 | 3.9186 | 0.99392 | 28.8 | 29.0066 | -3.456 | 0.99288 | 23.3088 | 23.4761 | 2.7971 | 0.99288 | 26.2702 | 26.4095 | 2.7092 | 0.99472 | 66
kentlyn Winter | 35.2945 | 35.5837 | 4.5274 | 0.99187 | 27.7632 | 27.767 | -0.4608 | 0.99986 | 26.4771 | 26.6077 | 2.6325 | 0.99509 | 26.4771 | 26.6808 | 3.2901 | 0.99237 | 66
kiama Summer | 13.9937 | 14.4652 | 3.6631 | 0.96741 | 12.4752 | 12.8846 | 3.2221 | 0.96823 | 10.1788 | 10.5128 | 2.629 | 0.96823 | 10.3313 | 10.8287 | 3.2443 | 0.95406 | 40
kiama Winter | 16.5209 | 17.0527 | 4.2256 | 0.96881 | 13.4586 | 13.6692 | 2.3905 | 0.98459 | 12.4554 | 12.6503 | 2.2123 | 0.98459 | 12.4554 | 12.7612 | 2.777 | 0.97603 | 40
kingswood Summer | 69.6719 | 74.016 | 24.9838 | 0.94131 | 54.972 | 57.755 | 17.712 | 0.95181 | 49.1582 | 51.6468 | 15.8388 | 0.95181 | 45.146 | 47.4895 | 14.7341 | 0.95065 | 75
kingswood Winter | 43.7993 | 45.5881 | 12.6447 | 0.96076 | 38.916 | 39.0146 | 2.772 | 0.99747 | 37.4006 | 38.9059 | 10.7177 | 0.96131 | 28.2336 | 29.7297 | 9.3121 | 0.94968 | 75
kurrajong Summer | 15.5338 | 16.7923 | 6.3783 | 0.92505 | 12.3552 | 13.1966 | 4.6368 | 0.93624 | 10.1842 | 10.8778 | 3.822 | 0.93624 | 11.6618 | 12.5777 | 4.7119 | 0.92718 | 30
kurrajong Winter | 15.8457 | 16.4848 | 4.5456 | 0.96123 | 9.2448 | 9.4682 | 2.0448 | 0.9764 | 9.1064 | 9.3648 | 2.1844 | 0.97241 | 9.767 | 10.0689 | 2.4472 | 0.97002 | 30
leabons_lane Summer | 25.8938 | 25.9922 | 2.2597 | 0.99621 | 20.034 | 20.0937 | 1.548 | 0.99703 | 17.3325 | 17.3841 | 1.3393 | 0.99703 | 22.8861 | 22.9888 | 2.1705 | 0.99553 | 50
leabons_lane Winter | 20.2955 | 20.3236 | 1.0675 | 0.99862 | 16.524 | 16.5438 | 0.81 | 0.9988 | 15.9067 | 15.9258 | 0.77972 | 0.9988 | 18.339 | 18.397 | 1.4607 | 0.99684 | 50
lennox Summer | 38.5004 | 38.9449 | 5.8666 | 0.98859 | 29.952 | 31.8153 | 10.728 | 0.94143 | 29.4233 | 31.4178 | 11.016 | 0.93652 | 25.6664 | 26.6121 | 7.0315 | 0.96446 | 75
lennox Winter | 29.0108 | 29.0795 | 1.9973 | 0.99764 | 26.712 | 26.7726 | -1.8 | 0.99774 | 26.712 | 26.7726 | 1.8 | 0.99774 | 27.5106 | 27.5597 | 1.6454 | 0.99822 | 75
lithgow Summer | 14.072 | 15.8415 | 7.2754 | 0.8883 | 15.708 | 15.8796 | 2.328 | 0.9892 | 15.708 | 15.8796 | 2.328 | 0.9892 | 16.5234 | 16.7072 | 2.4713 | 0.989 | 60
lithgow Winter | 18.5224 | 19.3344 | 5.5445 | 0.958 | 19.776 | 20.0514 | 3.312 | 0.98626 | 19.776 | 20.0514 | 3.312 | 0.98626 | 20.2297 | 20.5114 | 3.388 | 0.98626 | 60
liverpool Summer | 50.6538 | 51.8093 | 10.8814 | 0.9777 | 49.9207 | 50.9401 | 10.1399 | 0.97999 | 45.7232 | 46.6569 | 9.2873 | 0.97999 | 43.1446 | 44.4342 | 10.6275 | 0.97098 | 105
liverpool Winter | 45.0363 | 45.0614 | 1.5023 | 0.99944 | 37.7805 | 37.9413 | 3.4886 | 0.99576 | 36.2031 | 36.3571 | 3.3429 | 0.99576 | 33.0901 | 33.3295 | 3.9875 | 0.99282 | 105
luddenham Summer | 12.2039 | 13.6201 | 6.0474 | 0.89602 | 8.1 | 8.8552 | 3.5784 | 0.91471 | 7.3066 | 7.9878 | 3.2279 | 0.91471 | 8.0981 | 8.8531 | 3.5776 | 0.91471 | 30
luddenham Winter | 8.3703 | 9.0631 | 3.4753 | 0.92356 | 6.2352 | 6.5102 | 1.872 | 0.95777 | 5.9904 | 6.54 | 2.6243 | 0.91596 | 5.9904 | 6.54 | 2.6243 | 0.91596 | 30
macquarie_fields Summer | 42.0222 | 44.4121 | 14.3725 | 0.94619 | 28.85 | 29.2082 | -4.56 | 0.98774 | 24.4478 | 24.7513 | 3.8645 | 0.98774 | 24.2057 | 24.9857 | 6.1943 | 0.96878 | 66
macquarie_fields Winter | 36.6455 | 38.1046 | 10.4437 | 0.96171 | 24.57 | 24.7201 | -2.72 | 0.99393 | 23.3589 | 23.5016 | 2.5859 | 0.99393 | 20.3325 | 20.6646 | 3.6896 | 0.98393 | 66
maldon Summer | 26.7605 | 30.2077 | 14.0135 | 0.88589 | 20.69 | 22.1044 | -7.78 | 0.93601 | 17.8831 | 19.1057 | 6.7245 | 0.93601 | 17.0659 | 17.7654 | 4.9363 | 0.96062 | 70
maldon Winter | 20.7983 | 22.3928 | 8.2987 | 0.92879 | 17.78 | 18.4165 | -4.8 | 0.96544 | 16.8609 | 17.4645 | 4.5518 | 0.96544 | 15.8209 | 16.1806 | 3.3928 | 0.97777 | 70
mamre Summer | 50.4383 | 55.6411 | 23.4928 | 0.90649 | 32.7 | 32.9686 | 4.2 | 0.99185 | 31.3635 | 31.6212 | 4.0283 | 0.99185 | 35.4722 | 35.7636 | 4.556 | 0.99185 | 90
mamre Winter | 42.4687 | 46.0958 | 17.923 | 0.92131 | 23.7 | 23.7171 | -0.9 | 0.99928 | 23.8434 | 23.8605 | 0.90543 | 0.99928 | 30.148 | 30.1697 | 1.1448 | 0.99928 | 90
marayong Summer | 61.8668 | 63.0122 | 11.96 | 0.98182 | 37.536 | 38.1498 | 6.816 | 0.98391 | 37.536 | 38.1498 | 6.816 | 0.98391 | 37.6887 | 38.2676 | 6.6312 | 0.98487 | 75
marayong Winter | 46.4843 | 46.5676 | 2.7846 | 0.99821 | 35.76 | 35.9001 | 3.168 | 0.9961 | 35.76 | 35.9001 | 3.168 | 0.9961 | 36.0389 | 36.179 | 3.1806 | 0.99613 | 75
meadow_flat Summer | 1.128 | 1.1977 | 0.40254 | 0.94183 | 0.70722 | 0.71112 | 0.07433 | 0.99452 | 0.70722 | 0.71112 | 0.07433 | 0.99452 | 0.70722 | 0.71112 | 0.07433 | 0.99452 | 2.5
meadow_flat Winter | 2.2701 | 2.3291 | 0.52113 | 0.97465 | 0.91878 | 0.92008 | 0.0488 | 0.99859 | 0.86651 | 0.87205 | 0.0982 | 0.99364 | 0.86651 | 0.87205 | 0.0982 | 0.99364 | 2.5
minto Summer | 64.3629 | 67.8669 | 21.5252 | 0.94837 | 59.1552 | 60.7621 | 13.8816 | 0.97355 | 53.0073 | 54.4473 | 12.4389 | 0.97355 | 57.7051 | 59.8669 | 15.9428 | 0.96389 | 101
minto Winter | 51.7975 | 53.1628 | 11.9707 | 0.97432 | 49.824 | 50.064 | 4.896 | 0.99521 | 46.9802 | 47.2064 | 4.6165 | 0.99521 | 46.9802 | 47.7882 | 8.7509 | 0.98309 | 101
mittagong Summer | 23.0224 | 25.3751 | 10.6709 | 0.90728 | 13.224 | 13.7603 | 3.804 | 0.96103 | 11.6965 | 12.1708 | 3.3646 | 0.96103 | 13.0517 | 13.0521 | 0.10148 | 0.99997 | 40
mittagong Winter | 23.7562 | 25.1552 | 8.2721 | 0.94439 | 15.792 | 16.0639 | 2.943 | 0.98307 | 15.792 | 16.0639 | 2.943 | 0.98307 | 16.1211 | 16.1416 | 0.81291 | 0.99873 | 40
moorebank Summer | 59.5016 | 63.2189 | 21.3585 | 0.9412 | 38.178 | 38.344 | 3.564 | 0.99567 | 37.152 | 39.0715 | 12.096 | 0.95087 | 28.8477 | 29.9133 | 7.9128 | 0.96438 | 105
moorebank Winter | 49.5332 | 53.0446 | 18.9789 | 0.9338 | 33.237 | 33.2714 | 1.512 | 0.99897 | 33.237 | 33.2714 | 1.5119 | 0.99897 | 33.3591 | 34.1448 | 7.2824 | 0.97699 | 105
moss_vale Summer | 23.0409 | 26.0479 | 12.1495 | 0.88456 | 16.2376 | 17.3979 | 6.2472 | 0.93331 | 14.381 | 15.4087 | 5.5329 | 0.93331 | 14.7866 | 16.2443 | 6.7256 | 0.91026 | 50
moss_vale Winter | 28.4453 | 30.4941 | 10.9888 | 0.93281 | 17.4553 | 18.3069 | 5.5187 | 0.95348 | 16.9147 | 17.7399 | 5.3478 | 0.95348 | 19.1673 | 20.1487 | 6.2114 | 0.9513 | 50
mount_ousley Summer | 24.3659 | 24.4673 | 2.2251 | 0.99586 | 18.4 | 18.8298 | -4 | 0.97717 | 16.8246 | 17.345 | 4.2167 | 0.97 | 19.6218 | 20.2287 | 4.9177 | 0.97 | 70
mount_ousley Winter | 24.6466 | 24.757 | 2.3354 | 0.99554 | 18.89 | 19.0419 | -2.4 | 0.99202 | 16.1097 | 17.8996 | 7.8023 | 0.9 | 17.9097 | 19.8996 | 8.6741 | 0.9 | 70
mungerie_park Summer | 45.8908 | 48.3061 | 15.0836 | 0.95 | 42.08 | 44.5803 | 14.72 | 0.94391 | 35.7828 | 37.6661 | 11.7612 | 0.95 | 43.7231 | 46.0243 | 14.3711 | 0.95 | 135
mungerie_park Winter | 45.9272 | 48.3444 | 15.0955 | 0.95 | 22.72 | 22.9671 | 3.36 | 0.98924 | 20.4533 | 21.5297 | 6.7227 | 0.95 | 25.4443 | 26.7835 | 8.3631 | 0.95 | 135
narellan Summer | 61.8254 | 68.6949 | 29.9434 | 0.9 | 48.96 | 50.6463 | 12.96 | 0.96671 | 44.1084 | 45.6276 | 11.6758 | 0.96671 | 49.2652 | 50.962 | 13.0408 | 0.96671 | 105
narellan Winter | 53.2137 | 56.3335 | 18.4869 | 0.94462 | 29.52 | 29.6378 | -2.64 | 0.99602 | 28.4285 | 28.542 | 2.5424 | 0.99602 | 29.2024 | 29.3189 | 2.6116 | 0.99602 | 105
newton Summer | 40.3685 | 44.7758 | 19.3716 | 0.90157 | 34.704 | 36.4213 | 11.052 | 0.95285 | 31.9185 | 33.498 | 10.1649 | 0.95285 | 31.3487 | 32.9986 | 10.3038 | 0.95 | 75
newton Winter | 31.8933 | 34.3075 | 12.6422 | 0.92963 | 23.688 | 24.4214 | 5.94 | 0.96997 | 22.8253 | 23.532 | 5.7237 | 0.96997 | 20.9229 | 22.0241 | 6.877 | 0.95 | 75
north_parramatta Summer | 36.1596 | 41.7892 | 20.9481 | 0.86529 | 37.84 | 37.8818 | -1.78 | 0.9989 | 34.9794 | 35.0181 | 1.6446 | 0.9989 | 30.3945 | 30.4249 | 1.3603 | 0.999 | 110
north_parramatta Winter | 35.6831 | 42.097 | 22.3355 | 0.84764 | 28.75 | 28.7509 | -0.23 | 0.99997 | 27.8185 | 27.8194 | 0.22012 | 0.99997 | 28.378 | 28.4064 | 1.2701 | 0.999 | 110
north_richmond Summer | 19.2679 | 19.882 | 4.9033 | 0.96911 | 18.9 | 19.7876 | -5.86 | 0.95514 | 17.1265 | 17.9308 | 5.3101 | 0.95514 | 18.6802 | 19.2572 | 4.6784 | 0.97004 | 50
north_richmond Winter | 17.89 | 17.9407 | 1.3482 | 0.99717 | 14.95 | 15.3142 | -3.32 | 0.97622 | 13.9244 | 14.2637 | 3.0922 | 0.97622 | 12.8051 | 12.9577 | 1.9826 | 0.98823 | 50
north_rocks Summer | 24.9077 | 27.3332 | 11.2565 | 0.91126 | 19.296 | 19.3524 | -1.476 | 0.99709 | 17.2042 | 17.2544 | 1.316 | 0.99709 | 19.5148 | 19.6838 | 2.5738 | 0.99141 | 50
north_rocks Winter | 23.7621 | 23.9167 | 2.7151 | 0.99354 | 16.02 | 16.0912 | -1.512 | 0.99558 | 15.2384 | 15.3061 | 1.4382 | 0.99558 | 15.2384 | 15.2596 | 0.80448 | 0.99861 | 50
north_wollongong Summer | 15.3347 | 15.9912 | 4.5348 | 0.95895 | 12.7754 | 12.8814 | 1.6495 | 0.99177 | 12.7754 | 12.8814 | 1.6495 | 0.99177 | 13.1491 | 13.34 | 2.2487 | 0.98569 | 38
north_wollongong Winter | 15.5452 | 16.2065 | 4.5824 | 0.95919 | 11.5744 | 11.5794 | -0.34215 | 0.99956 | 10.7366 | 10.7413 | 0.31738 | 0.99956 | 10.7366 | 10.7678 | 0.81917 | 0.9971 | 38
northmead Summer | 26.5424 | 27.5838 | 7.5076 | 0.96225 | 23.4 | 23.5028 | 2.196 | 0.99563 | 20.2026 | 20.2914 | 1.8959 | 0.99563 | 23.545 | 23.6887 | 2.6047 | 0.99394 | 55
northmead Winter | 20.2952 | 20.4451 | 2.4718 | 0.99266 | 21.204 | 21.2297 | 1.044 | 0.99879 | 20.3297 | 20.3544 | 1.0009 | 0.99879 | 20.6483 | 20.7385 | 1.932 | 0.99565 | 55
nowra Summer | 32.6945 | 34.5453 | 11.1556 | 0.94642 | 25.3 | 25.4332 | 2.6 | 0.99476 | 23.0379 | 23.1592 | 2.3675 | 0.99476 | 25.6096 | 26.6542 | 7.3888 | 0.96081 | 70
nowra Winter | 23.1967 | 23.6081 | 4.3882 | 0.98257 | 20.4 | 20.4626 | 1.6 | 0.99694 | 18.5158 | 18.5726 | 1.4522 | 0.99694 | 19.3824 | 19.6809 | 3.4143 | 0.98484 | 70
oakdale Summer | 10.7946 | 11.9136 | 5.0409 | 0.90607 | 8.586 | 9.1353 | 3.12 | 0.93987 | 7.1573 | 7.6152 | 2.6008 | 0.93987 | 4.9074 | 5.2784 | 1.9439 | 0.92972 | 20
oakdale Winter | 9.1906 | 9.6907 | 3.0728 | 0.9484 | 7.506 | 7.7612 | 1.974 | 0.96711 | 6.7598 | 6.9896 | 1.7778 | 0.96711 | 2.5062 | 2.6198 | 0.76298 | 0.95665 | 20
parklea Summer | 91.7688 | 99.6973 | 38.9619 | 0.92047 | 84.18 | 88.166 | -26.21 | 0.95479 | 72.6895 | 76.1314 | 22.6325 | 0.95479 | 78.4013 | 82.1136 | 24.4109 | 0.95479 | 135
parklea Winter | 69.46 | 73.6981 | 24.6318 | 0.94249 | 48.89 | 48.8939 | -0.62 | 0.99992 | 47.9928 | 47.9967 | 0.60621 | 0.99992 | 48.6747 | 48.6786 | 0.61482 | 0.99992 | 135
parramatta Summer | 47.0267 | 52.0724 | 22.3613 | 0.9031 | 34.8154 | 36.8784 | 12.1615 | 0.94406 | 33.6777 | 35.6732 | 11.7641 | 0.94406 | na | na | na | #VALUE! | 75
parramatta Winter | 31.8624 | 34.6264 | 13.5563 | 0.92018 | 27.1509 | 28.6025 | 8.9963 | 0.94925 | 27.1509 | 28.6025 | 8.9963 | 0.94925 | 30.166 | 32.0161 | 10.7259 | 0.94221 | 75
penrith_11kv Summer | 51.4383 | 52.825 | 12.0244 | 0.97375 | 46.464 | 47.1586 | 8.064 | 0.98527 | 44.5552 | 45.2212 | 7.7327 | 0.98527 | 51.374 | 52.6393 | 11.4724 | 0.97596 | 130
penrith_11kv Winter | 40.251 | 40.5672 | 5.0554 | 0.9922 | 38.208 | 38.3024 | -2.688 | 0.99753 | 38.208 | 38.3024 | 2.688 | 0.99753 | 39.3991 | 39.5749 | 3.7253 | 0.99556 | 130
plumpton Summer | 43.0123 | 47.0067 | 18.9625 | 0.91502 | 29.6474 | 30.774 | 8.2508 | 0.96339 | 28.5752 | 29.6611 | 7.9524 | 0.96339 | 31.6897 | 32.894 | 8.8192 | 0.96339 | 75
plumpton Winter | 31.6174 | 32.7737 | 8.6287 | 0.96472 | 23.2733 | 23.562 | 3.677 | 0.98775 | 22.3159 | 22.5927 | 3.5258 | 0.98775 | 23.353 | 23.6427 | 3.6896 | 0.98775 | 75
port_central Summer | 18.6201 | 19.2669 | 4.9503 | 0.96643 | 12.1443 | 12.4804 | 2.8767 | 0.97307 | 11.0787 | 11.3853 | 2.6243 | 0.97307 | 12.6156 | 12.8978 | 2.6834 | 0.97812 | 38
port_central Winter | 14.8399 | 16.3162 | 6.7821 | 0.90952 | 9.8597 | 9.9151 | 1.0466 | 0.99441 | 9.8597 | 9.9151 | 1.0466 | 0.99441 | 9.8597 | 9.9326 | 1.2016 | 0.99266 | 38
port_kembla Summer | 13.1604 | 14.6889 | 6.5245 | 0.89594 | 12.3984 | 12.8827 | 3.4992 | 0.9624 | 10.7457 | 11.1654 | 3.0327 | 0.9624 | 12.1163 | 12.5896 | 3.4196 | 0.9624 | 30
port_kembla Winter | 18.6564 | 19.3725 | 5.2184 | 0.96304 | 14.6448 | 15.0083 | 3.2832 | 0.97578 | 12.3932 | 12.7009 | 2.7784 | 0.97578 | 12.3932 | 12.7009 | 2.7784 | 0.97578 | 30
portland Summer | 2.8435 | 2.8492 | 0.18011 | 0.998 | 2.796 | 2.7997 | 0.144 | 0.99868 | 2.796 | 2.7997 | 0.144 | 0.99868 | 2.8209 | 2.8295 | 0.22068 | 0.99695 | 20
portland Winter | 4.1108 | 4.119 | 0.26038 | 0.998 | 3.528 | 3.532 | 0.168 | 0.99887 | 3.528 | 3.5383 | 0.27039 | 0.99708 | 3.5529 | 3.5642 | 0.28307 | 0.99684 | 20
prestons Summer | 61.2053 | 63.9633 | 18.58 | 0.95688 | 32.4 | 34.3871 | 11.52 | 0.94221 | 26.51 | 28.1359 | 9.4258 | 0.94221 | 29.8804 | 31.779 | 10.8198 | 0.94026 | 75
prestons Winter | 39.7534 | 40.4159 | 7.2876 | 0.98361 | 20.88 | 20.9475 | -1.68 | 0.99678 | 19.2537 | 19.3159 | 1.5492 | 0.99678 | 15.5823 | 15.9371 | 3.3445 | 0.97773 | 75
prospect Summer | 30.5569 | 30.5775 | 1.1235 | 0.99932 | 29.1889 | 29.9782 | 6.8338 | 0.97367 | 26.7436 | 27.4668 | 6.2613 | 0.97367 | 27.5498 | 28.2338 | 6.177 | 0.97577 | 45
prospect Winter | 24.6366 | 24.819 | 3.0039 | 0.99265 | 21.408 | 21.524 | 2.232 | 0.99461 | 20.3037 | 20.4137 | 2.1168 | 0.99461 | 20.3037 | 20.6194 | 3.5947 | 0.98469 | 45
prospect_east Summer | 17.5741 | 18.8846 | 6.912 | 0.93061 | 9.7106 | 10.4192 | 3.7768 | 0.93199 | 9.7106 | 10.4192 | 3.7768 | 0.93199 | 9.7106 | 10.4273 | 3.7989 | 0.93127 | 50
prospect_east Winter | 11.933 | 12.7903 | 4.6036 | 0.93298 | 8.7947 | 9.3973 | 3.311 | 0.93587 | 8.7947 | 9.3973 | 3.311 | 0.93587 | 8.7947 | 9.4267 | 3.3935 | 0.93296 | 50
prospect_south Summer | 3.7391 | 4.3545 | 2.2318 | 0.85867 | 2.104 | 2.2655 | 0.84 | 0.92872 | 2.104 | 2.2655 | 0.84 | 0.92872 | 2.104 | 2.3139 | 0.96292 | 0.9093 | 50
prospect_south Winter | 2.1362 | 2.4692 | 1.2386 | 0.86511 | 2.06 | 2.2056 | 0.788 | 0.934 | 2.06 | 2.2056 | 0.788 | 0.934 | 2.06 | 2.2854 | 0.98967 | 0.90137 | 50
quakers_hill Summer | 58.8983 | 61.76 | 18.5819 | 0.95366 | 41.35 | 42.1017 | -7.92 | 0.98215 | 34.958 | 35.5935 | 6.6959 | 0.98215 | 36.3733 | 37.4586 | 8.9515 | 0.97103 | 155
quakers_hill Winter | 44.3174 | 45.1815 | 8.7938 | 0.98088 | 30.94 | 30.9656 | -1.26 | 0.99917 | 30.7579 | 30.7834 | 1.2515 | 0.99917 | 19.2106 | 19.3397 | 2.2315 | 0.99332 | 155
quarries Summer | 26.7756 | 30.438 | 14.4754 | 0.87968 | 18.26 | 18.9401 | 5.03 | 0.96409 | 15.8211 | 16.4103 | 4.3581 | 0.96409 | 24.4019 | 25.8964 | 8.6699 | 0.94229 | 70
quarries Winter | 27.4022 | 30.6733 | 13.7828 | 0.89336 | 10.77 | 11.1407 | 2.85 | 0.96673 | 10.4863 | 10.8472 | 2.7749 | 0.96673 | 14.1825 | 14.6932 | 3.8402 | 0.96524 | 70
richmond Summer | 27.3308 | 28.6867 | 8.7152 | 0.95273 | 19.272 | 19.3451 | 1.68 | 0.99622 | 18.7698 | 18.841 | 1.6362 | 0.99622 | na | na | na | #VALUE! | 50
richmond Winter | 21.7101 | 22.0475 | 3.8423 | 0.9847 | 15.072 | 15.1297 | 1.32 | 0.99619 | 14.3151 | 14.3699 | 1.2537 | 0.99619 | na | na | na | #VALUE! | 50
ringwood Summer | 7.1209 | 7.8877 | 3.3926 | 0.90278 | 5.1695 | 5.4372 | 1.6851 | 0.95076 | 4.4217 | 4.6507 | 1.4413 | 0.95076 | 4.5704 | 4.8577 | 1.6458 | 0.94086 | 25
ringwood Winter | 8.0004 | 8.3898 | 2.5263 | 0.95359 | 5.8532 | 5.9921 | 1.283 | 0.97681 | 5.3646 | 5.492 | 1.1759 | 0.97681 | 6.2457 | 6.4361 | 1.5536 | 0.97043 | 25
riverstone Summer | 55.0775 | 56.0287 | 10.2799 | 0.98302 | 13.824 | 13.8307 | 0.432 | 0.99951 | 12.4616 | 12.4676 | 0.38941 | 0.99951 | 19.7204 | 19.766 | 1.3416 | 0.99769 | 50
riverstone Winter | 36.9338 | 37.5201 | 6.6072 | 0.98437 | 18.162 | 18.1685 | 0.486 | 0.99964 | 17.1404 | 17.1466 | 0.45869 | 0.99964 | 11.3017 | 11.323 | 0.69351 | 0.99812 | 50
robertson Summer | 5.6839 | 5.9877 | 1.8831 | 0.94926 | 3.3655 | 3.5426 | 1.1062 | 0.95 | 3.3655 | 3.5426 | 1.1062 | 0.95 | 3.3655 | 3.6358 | 1.3756 | 0.92567 | 7.5
robertson Winter | 6.3101 | 6.6506 | 2.1005 | 0.94881 | 4.552 | 4.7915 | 1.4962 | 0.95 | 4.552 | 4.7915 | 1.4962 | 0.95 | 4.552 | 5.0114 | 2.0961 | 0.90833 | 7.5
rooty_hill Summer | 61.3156 | 64.9843 | 21.5255 | 0.94355 | 39.49 | 40.2223 | -7.64 | 0.98179 | 35.1207 | 35.772 | 6.7949 | 0.98179 | 35.64 | 36.3037 | 6.91 | 0.98172 | 90
rooty_hill Winter | 44.2407 | 44.6057 | 5.6946 | 0.99182 | 29.57 | 29.6149 | -1.63 | 0.99848 | 28.153 | 28.1957 | 1.552 | 0.99848 | 23.8599 | 24.0322 | 2.8726 | 0.99283 | 90
rosehill Summer | 28.626 | 29.4002 | 6.7025 | 0.97367 | 24.3 | 26.5919 | 10.8 | 0.91381 | 24.3 | 26.5919 | 10.8 | 0.91381 | 21.3603 | 21.7982 | 4.3474 | 0.97991 | 75
rosehill Winter | 24.9289 | 26.674 | 9.4896 | 0.93458 | 20.1306 | 21.1901 | 6.6166 | 0.95 | 20.1306 | 21.1901 | 6.6166 | 0.95 | 17.0415 | 17.4123 | 3.5747 | 0.9787 | 50
russell_vale Summer | 15.2163 | 16.5711 | 6.5626 | 0.91824 | 13.9373 | 14.4866 | 3.9513 | 0.96208 | 13.9373 | 14.4866 | 3.9513 | 0.96208 | 13.9373 | 14.6552 | 4.5305 | 0.95102 | 45
russell_vale Winter | 20.8085 | 21.7068 | 6.1799 | 0.95862 | 12.4744 | 12.6661 | 2.1957 | 0.98486 | 12.4744 | 12.6661 | 2.1957 | 0.98486 | 12.4744 | 12.7397 | 2.5864 | 0.97918 | 45
rydalmere Summer | 53.2258 | 54.3701 | 11.0959 | 0.97895 | 37.44 | 38.4676 | 8.832 | 0.97329 | 35.9294 | 36.9155 | 8.4757 | 0.97329 | 40.509 | 41.5202 | 9.1074 | 0.97565 | 91
rydalmere Winter | 38.2261 | 38.5718 | 5.1529 | 0.99104 | 29.28 | 29.3368 | -1.824 | 0.99807 | 28.5651 | 29.6892 | 8.0921 | 0.96214 | 29.5065 | 30.1939 | 6.4062 | 0.97723 | 91
seven_hills Summer | 45.9367 | 47.121 | 10.498 | 0.97487 | 30.0189 | 31.3138 | 8.9118 | 0.95865 | 30.0189 | 31.3138 | 8.9118 | 0.95865 | 30.0189 | 30.5676 | 5.7658 | 0.98205 | 75
seven_hills Winter | 36.8728 | 37.4231 | 6.3937 | 0.9853 | 27.5226 | 27.7152 | 3.2623 | 0.99305 | 27.5226 | 27.7152 | 3.2623 | 0.99305 | 27.5226 | 27.7154 | 3.2641 | 0.99304 | 75
shellharbour Summer | 37.1569 | 38.5301 | 10.1945 | 0.96436 | 28.722 | 28.7249 | 0.40472 | 0.9999 | 28.722 | 28.7249 | 0.4047 | 0.9999 | 30.2095 | 30.5576 | 4.5992 | 0.98861 | 65
shellharbour Winter | 35.2466 | 35.7774 | 6.1404 | 0.98516 | 23.156 | 23.2078 | 1.5496 | 0.99777 | 21.3257 | 21.3733 | 1.427 | 0.99777 | 23.7618 | 23.8853 | 2.4263 | 0.99483 | 65
sherwood Summer | 34.4695 | 35.0765 | 6.4972 | 0.9827 | 27.216 | 27.2435 | -1.224 | 0.99899 | 22.4447 | 22.4674 | 1.0094 | 0.99899 | 23.9591 | 24.0779 | 2.3889 | 0.99507 | 75
sherwood Winter | 27.9576 | 28.3308 | 4.5833 | 0.98683 | 23.256 | 23.3312 | -1.872 | 0.99678 | 22.4343 | 22.5068 | 1.8059 | 0.99678 | 18.7925 | 18.82 | 1.0169 | 0.99854 | 75
smithfield Summer | 41.7583 | 41.9613 | 4.1216 | 0.99516 | 35.46 | 35.5768 | -2.88 | 0.99672 | 29.4096 | 29.5064 | 2.3886 | 0.99672 | 32.663 | 32.7856 | 2.833 | 0.99626 | 50
smithfield Winter | 34.8068 | 35.2687 | 5.6891 | 0.9869 | 23.76 | 23.8424 | -1.98 | 0.99655 | 23.3733 | 23.4543 | 1.9478 | 0.99655 | 23.3733 | 23.7552 | 4.2424 | 0.98392 | 50
south_granville Summer | 20.8605 | 23.0245 | 9.7451 | 0.90601 | 17.892 | 18.8522 | 5.94 | 0.94906 | 16.3802 | 17.2594 | 5.4381 | 0.94906 | 18.1615 | 19.5552 | 7.2504 | 0.92873 | 40
south_granville Winter | 19.4422 | 20.5144 | 6.5452 | 0.94774 | 12.672 | 13.0113 | 2.952 | 0.97392 | 12.0251 | 12.3471 | 2.8013 | 0.97392 | 12.0251 | 12.4949 | 3.3938 | 0.9624 | 40
south_nowra Summer | 16.8732 | 19.4381 | 9.6507 | 0.86805 | 10 | 11.0494 | 4.7 | 0.90502 | 10.1897 | 11.2591 | 4.7892 | 0.90502 | 11.1229 | 12.2774 | 5.1976 | 0.90597 | 50
south_nowra Winter | 16.4208 | 18.047 | 7.4868 | 0.90989 | 10.7 | 11.2894 | 3.6 | 0.94779 | 8.8959 | 9.3859 | 2.993 | 0.94779 | 9.0209 | 9.6198 | 3.3413 | 0.93774 | 50
south_windsor Summer | 37.8789 | 38.1727 | 4.7269 | 0.9923 | 34.86 | 37.2932 | 13.25 | 0.93475 | 34.86 | 37.2932 | 13.25 | 0.93475 | 36.3504 | 37.4513 | 9.0139 | 0.9706 | 75
south_windsor Winter | 36.8765 | 36.9296 | 1.979 | 0.99856 | 25.55 | 26.4653 | -6.9 | 0.96542 | 25.55 | 26.4653 | 6.9 | 0.96542 | 26.7244 | 26.9034 | 3.0986 | 0.99335 | 75
south_wollongong Summer | 20.0501 | 22.8211 | 10.8992 | 0.87858 | 15.6437 | 15.6654 | 0.82493 | 0.99861 | 13.9639 | 13.9833 | 0.73636 | 0.99861 | 14.1382 | 14.9157 | 4.753 | 0.94787 | 38
south_wollongong Winter | 19.7662 | 20.5483 | 5.6151 | 0.96194 | 14.245 | 14.3746 | 1.9261 | 0.99098 | 14.245 | 14.3746 | 1.9261 | 0.99098 | 14.4401 | 14.8005 | 3.2463 | 0.97565 | 38
springwood Summer | 27.1892 | 29.6937 | 11.9357 | 0.91566 | 25.08 | 26.3741 | 8.16 | 0.95093 | 21.5907 | 22.7048 | 7.0247 | 0.95093 | 24.3962 | 25.6161 | 7.8107 | 0.95238 | 70
springwood Winter | 28.6899 | 29.9276 | 8.5175 | 0.95865 | 23.7 | 23.7902 | 2.07 | 0.99621 | 23.7 | 23.7902 | 2.07 | 0.99621 | 24.0481 | 24.9676 | 6.7135 | 0.96317 | 70
st_marys Summer | 47.8927 | 49.4617 | 12.3593 | 0.96828 | 36.624 | 38.2796 | 11.136 | 0.95675 | 34.008 | 35.5453 | 10.3406 | 0.95675 | 34.0136 | 35.0323 | 8.3867 | 0.97092 | 69
st_marys Winter | 35.0026 | 35.3752 | 5.121 | 0.98947 | 25.272 | 25.2721 | -0.072 | 1 | 24.1024 | 24.1025 | 0.069479 | 1 | 20.7748 | 20.8595 | 1.8777 | 0.99594 | 69
sussex_inlet Summer | 9.0216 | 10.0081 | 4.3329 | 0.90142 | 6.192 | 6.5346 | 2.088 | 0.94758 | 6.192 | 6.5346 | 2.088 | 0.94758 | 6.2206 | 6.5647 | 2.0976 | 0.94758 | 20
sussex_inlet Winter | 9.6591 | 10.3873 | 3.8208 | 0.92989 | 6.0912 | 6.1336 | 0.72 | 0.99309 | 6.0912 | 6.1336 | 0.72 | 0.99309 | 6.1211 | 6.1637 | 0.72354 | 0.99309 | 20
tahmoor Summer | 14.7102 | 16.2821 | 6.9798 | 0.90346 | 16.08 | 16.1086 | -0.96 | 0.99822 | 13.2273 | 13.2508 | 0.78969 | 0.99822 | 14.4034 | 14.4565 | 1.2379 | 0.99633 | 50
tahmoor Winter | 15.4562 | 16.4027 | 5.4912 | 0.9423 | 13.44 | 13.4935 | -1.2 | 0.99604 | 12.544 | 12.5939 | 1.12 | 0.99604 | 12.544 | 12.584 | 1.0038 | 0.99681 | 50
ulladulla Summer | 31.1432 | 32.735 | 10.0836 | 0.95137 | 25.2607 | 26.5683 | 8.2324 | 0.95078 | 25.2607 | 26.5683 | 8.2324 | 0.95078 | 25.5924 | 27.284 | 9.4576 | 0.938 | 60
ulladulla Winter | 30.793 | 32.4309 | 10.1762 | 0.9495 | 26.0208 | 26.6578 | 5.7929 | 0.9761 | 26.0208 | 26.6578 | 5.7929 | 0.9761 | 26.0208 | 27.7407 | 9.6159 | 0.938 | 60
unanderra Summer | 29.6752 | 29.8686 | 3.3927 | 0.99353 | 23.472 | 23.6309 | 2.736 | 0.99327 | 17.4173 | 17.5352 | 2.0302 | 0.99327 | 13.114 | 13.2239 | 1.7013 | 0.99169 | 36
unanderra Winter | 30.7755 | 30.8905 | 2.663 | 0.99628 | 25.3512 | 25.3616 | 0.7272 | 0.99959 | 25.3512 | 25.3616 | 0.72721 | 0.99959 | 25.3512 | 25.4228 | 1.9072 | 0.99718 | 36
warilla Summer | 21.9665 | 23.8256 | 9.2267 | 0.92197 | 18.8019 | 19.6281 | 5.635 | 0.9579 | 15.6748 | 16.3636 | 4.6978 | 0.9579 | 16.8772 | 17.9841 | 6.2121 | 0.93845 | 32.5
warilla Winter | 21.7236 | 22.6212 | 6.3093 | 0.96032 | 18.9881 | 19.3065 | 3.4921 | 0.98351 | 17.2389 | 17.528 | 3.1704 | 0.98351 | 18.2056 | 18.6824 | 4.1939 | 0.97448 | 32.5
wentworth_falls Summer | 6.7943 | 6.8825 | 1.098 | 0.98719 | 5.5584 | 5.5928 | -0.6192 | 0.99385 | 5.5584 | 5.5928 | 0.6192 | 0.99385 | 5.5584 | 5.5978 | 0.66299 | 0.99296 | 10
wentworth_falls Winter | 7.6822 | 7.7612 | 1.1045 | 0.98982 | 7.0416 | 7.1054 | -0.9504 | 0.99101 | 6.1618 | 6.2176 | 0.83165 | 0.99101 | 6.1618 | 6.2152 | 0.81288 | 0.99141 | 10
werrington Summer | 34.1906 | 39.5538 | 19.8874 | 0.86441 | 40.08 | 40.4263 | 5.28 | 0.99143 | 37.0047 | 37.3244 | 4.8749 | 0.99143 | 40.4449 | 41.2495 | 8.1075 | 0.98049 | 105
werrington Winter | 26.6296 | 27.3506 | 6.2386 | 0.97364 | 33.84 | 33.8817 | -1.68 | 0.99877 | 33.84 | 33.8817 | 1.68 | 0.99877 | 35.2925 | 35.7862 | 5.9236 | 0.98621 | 105
west_castle_hill Summer | 26.4656 | 28.6782 | 11.0458 | 0.92285 | 36.07 | 38.8941 | -14.55 | 0.92739 | 34.5817 | 37.2892 | 13.9497 | 0.92739 | 39.6722 | 42.7783 | 16.0032 | 0.92739 | 130
west_castle_hill Winter | 23.661 | 24.1874 | 5.0186 | 0.97824 | 36.42 | 37.5986 | -9.34 | 0.96865 | 35.599 | 36.7511 | 9.1296 | 0.96865 | 30.4166 | 30.9357 | 5.6438 | 0.98322 | 130
west_pennant_hills Summer | 32.4176 | 33.7275 | 9.3082 | 0.96116 | 25.104 | 25.4334 | 4.08 | 0.98705 | 20.1603 | 20.4248 | 3.2765 | 0.98705 | 34.518 | 35.3816 | 7.7693 | 0.97559 | 70
west_pennant_hills Winter | 25.6207 | 26.5326 | 6.8962 | 0.96563 | 18.768 | 18.866 | 1.92 | 0.99481 | 18.1197 | 18.1487 | 1.0248 | 0.9984 | 18.1197 | 18.6553 | 4.4378 | 0.97129 | 70
west_wetherill_11kv Summer | 26.0775 | 27.45 | 8.5713 | 0.95 | 30.4282 | 33.8091 | 14.7371 | 0.9 | 30.4282 | 33.8091 | 14.7371 | 0.9 | 30.4282 | 33.8091 | 14.7371 | 0.9 | 90
west_wetherill_11kv Winter | 30.6494 | 32.2625 | 10.074 | 0.95 | 27.9547 | 31.0608 | 13.5391 | 0.9 | 27.9547 | 31.0608 | 13.5391 | 0.9 | 27.9547 | 31.0608 | 13.5391 | 0.9 | 90
west_wollongong Summer | 11.4856 | 12.6754 | 5.3618 | 0.90613 | 19.15 | 20.1785 | -6.36 | 0.94903 | 12.6637 | 13.3438 | 4.2058 | 0.94903 | 12.7265 | 13.5551 | 4.6664 | 0.93888 | 35
west_wollongong Winter | 23.3572 | 24.1922 | 6.3013 | 0.96548 | 16.44 | 16.922 | -4.01 | 0.97152 | 15.9533 | 16.4211 | 3.8913 | 0.97152 | 16.187 | 16.6258 | 3.7946 | 0.97361 | 35
westmead Summer | 33.0511 | 33.595 | 6.0205 | 0.98381 | 23.664 | 23.6781 | 0.816 | 0.99941 | 23.0969 | 23.1106 | 0.79642 | 0.99941 | 28.4741 | 28.7043 | 3.6277 | 0.99198 | 50
westmead Winter | 22.6905 | 22.753 | 1.6854 | 0.99725 | 17.856 | 17.9261 | 1.584 | 0.99609 | 17.856 | 17.9261 | 1.584 | 0.99609 | 18.2961 | 18.4758 | 2.5707 | 0.99027 | 50
wetherill_park Summer | 35.6781 | 36.2807 | 6.5852 | 0.98339 | 29.2089 | 30.7463 | 9.6005 | 0.95 | 29.2089 | 30.7463 | 9.6005 | 0.95 | 29.2089 | 29.8355 | 6.0823 | 0.979 | 90
wetherill_park Winter | 36.2039 | 36.451 | 4.237 | 0.99322 | 28.7724 | 30.2867 | 9.457 | 0.95 | 28.7724 | 30.2867 | 9.457 | 0.95 | 28.7724 | 29.3896 | 5.9914 | 0.979 | 90
whalan Summer | 43.6205 | 45.2726 | 12.1186 | 0.96351 | 35.59 | 36.4737 | 7.98 | 0.97577 | 32.4022 | 33.2067 | 7.2654 | 0.97577 | 32.6947 | 33.5065 | 7.3309 | 0.97577 | 75
whalan Winter | 22.3144 | 22.555 | 3.2858 | 0.98933 | 24.87 | 24.9301 | 1.73 | 0.99759 | 23.0615 | 23.1172 | 1.6042 | 0.99759 | 22.1045 | 22.1579 | 1.5377 | 0.99759 | 75
windsor Summer | 26.777 | 30.1117 | 13.7734 | 0.88926 | 18.03 | 18.999 | 5.99 | 0.949 | 16.8111 | 17.7145 | 5.5851 | 0.949 | 21.2025 | 23.0591 | 9.065 | 0.91949 | 40
windsor Winter | 17.591 | 18.9041 | 6.9226 | 0.93054 | 16.86 | 17.3899 | 4.26 | 0.96953 | 16.86 | 17.3899 | 4.2602 | 0.96953 | 18.5464 | 19.3682 | 5.5819 | 0.95757 | 40
wisemans Summer | 5.9187 | 6.9961 | 3.7302 | 0.846 | 5.0772 | 5.3133 | 1.5664 | 0.95556 | 5.0772 | 5.3133 | 1.5664 | 0.95556 | 5.0772 | 5.4481 | 1.9759 | 0.93191 | 12.5
wisemans Winter | 4.6682 | 5.2739 | 2.4538 | 0.88516 | 4.2146 | 4.3842 | 1.2077 | 0.96131 | 4.2146 | 4.3842 | 1.2077 | 0.96131 | 4.2146 | 4.4249 | 1.348 | 0.95247 | 12.5
wombarra Summer | 3.8923 | 4.1411 | 1.4138 | 0.93991 | 4.2903 | 4.4142 | 1.0384 | 0.97194 | 4.2903 | 4.4142 | 1.0384 | 0.97194 | 4.2903 | 4.4463 | 1.1674 | 0.96492 | 10
wombarra Winter | 6.4472 | 6.6627 | 1.6809 | 0.96766 | 6.3767 | 6.4756 | 1.1276 | 0.98472 | 5.0455 | 5.1238 | 0.89222 | 0.98472 | 5.0455 | 5.1588 | 1.075 | 0.97805 | 10
woodpark Summer | 24.4904 | 25.3585 | 6.5782 | 0.96577 | 24.132 | 24.6502 | 5.028 | 0.97898 | 24.132 | 24.6502 | 5.028 | 0.97898 | 24.132 | 24.9642 | 6.3918 | 0.96667 | 50
woodpark Winter | 23.3373 | 23.9257 | 5.2736 | 0.97541 | 22.008 | 22.3103 | 3.66 | 0.98645 | 22.008 | 22.3103 | 3.66 | 0.98645 | 22.008 | 22.4255 | 4.307 | 0.98138 | 50
yatte_yattah Summer | 4.6489 | 5.0421 | 1.952 | 0.92202 | 3.7337 | 3.9928 | 1.415 | 0.9351 | 3.7337 | 3.9928 | 1.4151 | 0.9351 | 3.7337 | 3.9928 | 1.4151 | 0.9351 | 6.5
yatte_yattah Winter | 4.7116 | 4.997 | 1.6645 | 0.94289 | 4.2586 | 4.425 | 1.202 | 0.9624 | 4.2586 | 4.425 | 1.202 | 0.9624 | 4.2586 | 4.425 | 1.202 | 0.9624 | 6.5
yennora Summer | 18.4276 | 21.8632 | 11.7653 | 0.84286 | 17.82 | 17.881 | -1.476 | 0.99659 | 16.846 | 16.9037 | 1.3953 | 0.99659 | 16.5922 | 17.4599 | 5.4356 | 0.95031 | 50
yennora Winter | 17.6091 | 18.3622 | 5.2047 | 0.95899 | 17.208 | 17.3568 | 2.268 | 0.99143 | 17.208 | 17.3568 | 2.268 | 0.99143 | 17.208 | 17.8344 | 4.6851 | 0.96488 | 50
New Zones
berrima_junction Summer | na | na | na | #VALUE! | 1.629 | 1.7147 | 0.53542 | 0.95 | 1.629 | 1.7147 | 0.53542 | 0.95 | 1.7039 | 1.8932 | 0.82522 | 0.9 | 20
berrima_junction Winter | na | na | na | #VALUE! | 0.62468 | 0.69408 | 0.30254 | 0.9 | 0.62468 | 0.69408 | 0.30254 | 0.9 | 0.62468 | 0.69408 | 0.30254 | 0.9 | 20
cawdor Summer | na | na | na | #VALUE! | 13.7 | 14.359 | 4.3 | 0.95411 | 13.7 | 14.359 | 4.3 | 0.95411 | 19.1306 | 21.2562 | 9.2654 | 0.9 | 50
cawdor Winter | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 18.1134 | 20.126 | 8.7727 | 0.9 | 50
claremont_meadows Summer | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 26.6637 | 28.067 | 8.7639 | 0.95 | 75
claremont_meadows Winter | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 24.7656 | 26.069 | 8.14 | 0.95 | 75
east_richmond Summer | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 23.6783 | 23.9966 | 3.8955 | 0.98674 | 70
east_richmond Winter | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 15.8093 | 15.8982 | 1.6783 | 0.99441 | 70
figtree Summer | na | na | na | #VALUE! | 11.2 | 11.5447 | 2.8 | 0.97014 | 11.2 | 12.4444 | 5.4244 | 0.9 | 15.4684 | 17.1872 | 7.4917 | 0.9 | 50
figtree Winter | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 50
jordan springs Summer | na | na | na | #VALUE! | 5.7778 | 6.4198 | 2.7983 | 0.9 | 5.7778 | 6.4198 | 2.7983 | 0.9 | 7.6682 | 8.5202 | 3.7139 | 0.9 | 22
jordan springs Winter | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 6.9665 | 7.7406 | 3.374 | 0.9 | 22
nepean_zone Summer | na | na | na | #VALUE! | 33.472 | 35.291 | 11.184 | 0.94846 | 33.4013 | 35.2165 | 11.1604 | 0.94846 | 28.5202 | 30.0701 | 9.5295 | 0.94846 | 70
nepean_zone Winter | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 11.2903 | 11.2924 | 0.21575 | 0.99982 | 70
north_eastern_creek Summer | na | na | na | #VALUE! | 10.16 | 11.774 | 5.95 | 0.86292 | 10.16 | 11.774 | 5.9499 | 0.86292 | 14.4125 | 16.702 | 8.4402 | 0.86292 | 90
north_eastern_creek Winter | na | na | na | #VALUE! | 2.18 | 4.4854 | -3.92 | 0.48602 | 2.18 | 4.4854 | 3.92 | 0.48602 | 6.6152 | 7.3502 | 3.2039 | 0.9 | 90
north_warragamba Summer | na | na | na | #VALUE! | 8.76 | 9.5171 | 3.72 | 0.92044 | 8.0139 | 8.7065 | 3.4031 | 0.92044 | 8.9735 | 9.775 | 3.8766 | 0.918 | 40
north_warragamba Winter | na | na | na | #VALUE! | 7.22 | 7.5959 | 2.36 | 0.95051 | 7.0379 | 7.4043 | 2.3005 | 0.95051 | 7.0379 | 7.6665 | 3.0404 | 0.918 | 40
oran_park Summer | na | na | na | #VALUE! | 1.4217 | 1.5796 | 0.68855 | 0.9 | 1.4217 | 1.5796 | 0.68855 | 0.9 | 7.6434 | 8.4927 | 3.7019 | 0.9 | 20
oran_park Winter | na | na | na | #VALUE! | 2.9353 | 3.2614 | 1.4216 | 0.9 | 2.9353 | 3.2614 | 1.4216 | 0.9 | 6.4761 | 7.1957 | 3.1365 | 0.9 | 20
schofields Summer | na | na | na | #VALUE! | 17.1 | 17.4251 | 3.35 | 0.98134 | 15.0978 | 16.7754 | 7.3122 | 0.9 | 19.2825 | 21.425 | 9.3389 | 0.9 | 90
schofields Winter | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 16.0918 | 17.8798 | 7.7936 | 0.9 | na
west liverpool ZS Summer | na | na | na | #VALUE! | 31.9 | 33.2448 | 9.36 | 0.95955 | 31.9 | 33.2448 | 9.36 | 0.95955 | 35.5852 | 36.3296 | 7.3163 | 0.97951 | 105
west liverpool ZS Winter | na | na | na | #VALUE! | 26.4 | 26.8943 | 4 | 0.98162 | 26.4 | 26.8943 | 5.1326 | 0.98162 | 29.6343 | 29.76 | 2.7331 | 0.99577 | 105
wilton Summer | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 2.0025 | 2.225 | 0.96985 | 0.9 | 40
wilton Winter | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 2.1229 | 2.3587 | 1.0282 | 0.9 | 40
Casula Summer | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 14.4739 | 16.0821 | 7.01 | 0.9 | 70
Casula Winter | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 13.9712 | 15.5236 | 6.7666 | 0.9 | 70
Chipping_Norton Summer | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 16.7183 | 18.5759 | 8.0971 | 0.9 | 70
Chipping_Norton Winter | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 70
Denham_Court Summer | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 18 | 20 | 8.7178 | 0.9 | 60
Denham_Court Winter | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 60
Glenorie Summer | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 4.4212 | 4.6539 | 1.4532 | 0.95 | 15
Glenorie Winter | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 5.0689 | 5.3357 | 1.6661 | 0.95 | 15
Huntingwood Summer | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 2.736 | 3.04 | 1.3251 | 0.9 | 90
Huntingwood Winter | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 90
South_Leppington Summer | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 5.3832 | 5.9813 | 2.6072 | 0.9 | 45
South_Leppington Winter | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 45
The_Oaks Summer | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 3.6231 | 4.0257 | 1.7548 | 0.9 | 15
The_Oaks Winter | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 15
West_Parramatta Summer | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 53.0775 | 57.3279 | 21.6627 | 0.92586 | 135
West_Parramatta Winter | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | 135
Decommissioned since AER submission
warragamba Summer | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | na
warragamba Winter | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | na | na | na | #VALUE! | na
Note on B329: gouldj: richmond to be decomissioned and east richmond to pick up the load
Note on B331: gouldj: camden will be decomissioned and neapean zs to pick up the load
Note on B335: gouldj: camden will be decomissioned and neapean zs to pick up the load
Note on B339: gouldj: Warragamba Decomissioned in 2010 & North Warragamba established.
Note on B341: gouldj: Oran Park - Mobile Substation
Note on B345: Topsoe: Hoxton Park Zone Decomissioned and West Liverpool Zone take up the load
Note on B366: Topsoe: Decomissioned in 2010 & North Warragamba established.
Note on G50: MW Peak. MVA Peak is 19.68 with corrosponding MW value of 19.1
Note on G64: This is MW Peak. MVA peak is 10.2MVA with corrosponding 9.77MW.
Note on G73: Nepean 11kV
Note on G343: This is MW peak. MVA peak is 17.6 with corrosponding MW value of 16.93.
Note on O221: gouldj: Parramatta decomissioned 2014 summer and west parramatta comissioned
Note on O245: gouldj: Richmond decommissioned mid -late 2013 and east richmond takes up the load
Note on O246: gouldj: Richmond decommissioned mid -late 2013 and east richmond takes up the
Contents

## 3. Outcomes customer service
Endeavour Energy
Customer Service
2012-13
This information is used to monitor the service performance of the DNSP, and assist the AER understand service outcomes for customers. The information will inform the AER’s assessment of future service improvement expenditure proposals by the DNSP. The information may be used in performance reports.
Table 1: Quality of supply
2012-13
Over voltage events - due to high voltage injection
Customers receiving over-voltage - due to high voltage injection
Over voltage events - due to lightning
Customers receiving over-voltage - due to lightning
Over voltage events - due to voltage regulation or other cause
Customers receiving over-voltage - due to voltage regulation or other cause
Voltage variations - steady state (zone sub)
Voltage variations - one minute (zone sub)
Voltage variations - 10 seconds (zone sub) Min<0.7
Voltage variations - 10 seconds (zone sub) Min<0.8
Voltage variations - 10 seconds (zone sub) Min<0.9
Voltage variations - steady state (feeder)
Voltage variations - % zone subs monitored
Voltage variations - % feeders monitored
Customers - quality of supply improvement
Table 2: Complaints - technical quality of supply
2012-13
Complaints - technical quality of supply - number | 212
Complaints by category (%)
Low voltage supply
Voltage dips
Voltage swell
Voltage spike (impulsive transient)
Waveform distortion
TV or radio interference
Noise from appliances
Other
Complaints by Likely Cause (%)
Network equipment faulty
Network interference by NSP equipment
Network interference by another customer
Network limitation
Customer internal problem
No problem identified
Environmental
Other
Table 3: Customer service
2012-13
Timely provision of services
Connections made | 12
Connections not made on agreed date | 0
Timely repair of faulty streetlights
Streetlights - average monthly number "out" | 1138
Streetlights - not repaired by "fix by" date | 298
Streetlights - average number of days to repair | 3.8
Total streetlights | 194653
Call Centre Performance (number, unless stated)
Calls to call centre fault line | 374574
Calls to fault line not answered within 30 seconds | 37961
Calls to fault line - average waiting time before call answered | 29
Calls abandoned - percentage | 3.14
Call centre - number of overload events | 0
Customer complaints (number)
Complaint - reliability of supply
Complaint - technical quality of supply
Complaint - administrative process or customer service
Complaint - connection or augmentation
Complaint - other
Total complaints | 3993
Contents

## 4. General information
Endeavour Energy
General information
2012-13
The information will enable the AER to better understand the network and service performance outcomes reported by the DNSP. Network characteristics will be used to normalise other information, to assist in any benchmarking or other comparisons between DNSP financial and service performance outcomes.
Table 1: Metered supply points
| Total no. | By type of customer |  | By supply voltage
Number of metered supply points |  | Domestic | Non-domestic | Subtransmission | HV | LV
CBD | 0 | N/A | N/A | N/A | N/A | N/A
Urban | 755956.2452 | 684223.3574 | 71732.7115 | 46.1028 | 203.8769 | 755706.2654
Rural Short | 151733.6232 | 139233.3494 | 12508.4818 | 33.8087 | 51.2254 | 151648.5891
Rural Long | 298.1316 | 264.2932 | 33.8067 | 0 | 0 | 298.1316
Total | 907988 | 823721 | 84275 | 79.9116 | 255.1023 | 907652.9861
Table 2: Energy delivered
| Total GWh | By type of customer |  | By supply voltage
Energy delivered (GWh) |  | Domestic | Non-domestic | Subtransmission | HV | LV - residential | LV - non residential
CBD | 0
Urban | 0
Rural Short | 0
Rural Long | 0
Total | 16000807
Table 3: Line length
Note: where a line supplies more than one feeder type, the line length should be proportionately allocated according to the number of feeders in each category. For example if a line supplied one each of a CBD and Urban feeder, 50% of the line length would be allocated to CBD and 50% to urban.
| Total km | Underground lines |  |  | Overhead lines
Line Length (km) |  | Subtransmission | HV | LV | Subtransmission | HV | LV
CBD | 0 |  | 0 |  |  | 0
Urban | 6832 |  | 3522 |  |  | 3310
Rural Short | 8240 |  | 478 |  |  | 7762
Rural Long | 238.31 |  | 0 |  |  | 238.31
Total | 34957.31 | 301 | 4000 | 7262 | 3231 | 11310.31 | 8853
Note: 1. Feeders are categorized annually and may change over time 2. Feeders that don't meet criteria for CBD, Urban, Rural - Short, and Rural - Long, eg. Auxiliary, Bus ties etc, are excluded.
Table 4: Customer numbers
| Total no. | By supply voltage
Customer numbers |  | Subtransmission | HV | LV - residential | LV - non residential
Total customer numbers beginning of period | 883663 | 69 | 278 | 803173 | 80143
Total customer numbers end of period | 907996 | 69 | 275 | 823721 | 83931
Controlled load customers | 343065 | 0 | 0 | 343065 | 0
Total new customer connections | 13279
Total customer disconnections | 15421
Table 5: Number and capacity of transformers
Number & total capacity of transformers | Total no. | Capacity (MVA)
Distribution | 30207 | 9222.2
Zone substation | 438 | 15121
Table 6: Unmetered supply points
Number of unmetered supply points
CBD | 0
Urban | 1
Rural Short | 0
Rural Long | 0
Total | 1
Table 7: Poles and substations
Number of poles and substations
Subtransmission poles | 25888 | Note: Stay poles have been included
Distribution poles | 280616 | Note: Stay poles have been included
Subtransmission and zone substations | 184
Distribution substations | 30260
Table 8: Other information
Other information
Distribution losses (% of purchases) | 4.2%
Network Service area (sq.km) | 25120
Network Coincident Maximum Demand (MW) | 0
FTE employees | 2635.1
Note on B32: Our systems do not currently support or capture categories for lines that are other than HV – High Voltage (ie. sub transmission or LV – Low Voltage) as of the most recent AER RIN template. The categorization of HV lines is currently a manual process.
Note on C15: Note: A minor variance in customer numbers may arise due to parameters used to extract data.
Note on C59: This represents the market NMI for traffic lights. Excluded are streetlights and non market unmetered supplies which do not have an active NMI in MSATS
Contents

## 5a. Network data outage
Endeavour Energy
Nework data - outages
2012-13
The information in templates 5a,b,c,d is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Unplanned Outages
Date (DD/MM/YYYY) | Outage ID | Feeder ID / name | Feeder classification | Cause of outage | Number of customers interrupted | Duration of interruption (Mins) | Total unplanned customer minutes off supply (Mins) | Unplanned SAIDI impact | Unplanned SAIFI impact
2013-01-16 05:27PM | 1585471-1 | APA2 | Urban | Equipment Failure | 1911 | 12 | 22932 | 0.025618 | 0.0021348
2012-09-27 08:46AM | 1557324-1 | APA2 | Urban | Other | 190 | 26.1842 | 4975 | 0.0055577 | 0.00021225
2012-08-19 01:00PM | 1547279-1 | APA2 | Urban | Equipment Failure | 5 | 315 | 1575 | 0.0017595 | 5.5856e-06
2013-05-16 09:49AM | 1617763-1 | APA2 | Urban | Equipment Failure | 1 | 151 | 151 | 0.00016869 | 1.1171e-06
2013-01-16 05:27PM | 1585471-1 | APB2 | Urban | Equipment Failure | 2304 | 11.9983 | 27644 | 0.030882 | 0.0025738
2012-08-05 12:17PM | 1542984-1 | APB2 | Urban | Other | 15 | 65.4667 | 982 | 0.001097 | 1.6757e-05
2013-04-05 10:16PM | 1608279-1 | APB2 | Urban | Equipment Failure | 14 | 104 | 1456 | 0.0016265 | 1.564e-05
2013-06-08 11:25AM | 1623942-1 | APB2 | Urban | Equipment Failure | 2 | 384 | 768 | 0.00085795 | 2.2342e-06
2012-12-21 04:42PM | 1579725-1 | APB2 | Urban | Animals | 1748 | 44.746 | 78216 | 0.087377 | 0.0019527
2013-01-20 12:41AM | 1586685-1 | APB2 | Urban | Animals | 1752 | 164.0776 | 287464 | 0.32113 | 0.0019572
2013-01-16 05:27PM | 1585471-1 | APC2 | Rural Short | Equipment Failure | 1499 | 11.9973 | 17984 | 0.02009 | 0.0016746
2013-05-26 01:28PM | 1620243-1 | APC2 | Rural Short | Animals | 3 | 101 | 303 | 0.00033849 | 3.3514e-06
2013-02-04 01:28PM | 1591366-1 | APC2 | Rural Short | Other | 8 | 294.25 | 2354 | 0.0026297 | 8.937e-06
2012-07-12 04:47PM | 1537441-1 | APC2 | Rural Short | Equipment Failure | 1 | 93 | 93 | 0.00010389 | 1.1171e-06
2012-09-12 09:59AM | 1553892-1 | APC2 | Rural Short | Other | 38 | 120 | 4560 | 0.0050941 | 4.2451e-05
2013-04-18 07:57PM | 1611404-1 | APC2 | Rural Short | Weather | 2 | 125 | 250 | 0.00027928 | 2.2342e-06
2013-03-08 11:51AM | 1601996-1 | APC2 | Rural Short | Animals | 3 | 91 | 273 | 0.00030497 | 3.3514e-06
2012-09-01 02:05PM | 1551190-1 | APC2 | Rural Short | Other | 43 | 67.4884 | 2902 | 0.0032419 | 4.8036e-05
2013-02-20 01:37PM | 1595786-1 | APC2 | Rural Short | Vegetation | 57 | 92.7368 | 5286 | 0.0059051 | 6.3676e-05
2013-01-18 06:29PM | 1586314-1 | APC2 | Rural Short | Weather | 127 | 102.1181 | 12969 | 0.014488 | 0.00014187
2013-01-28 02:29PM | 1589278-1 | APC2 | Rural Short | Equipment Failure | 127 | 68.9921 | 8762 | 0.0097882 | 0.00014187
2012-09-07 05:55PM | 1552963-1 | APC2 | Rural Short | Weather | 1146 | 174.9058 | 200442 | 0.22392 | 0.0012802
2013-01-18 09:06AM | 1585876-1 | APC2 | Rural Short | Third Party Impacts | 1151 | 156.8983 | 180590 | 0.20174 | 0.0012858
2013-01-18 06:31PM | 1586316-1 | APC2 | Rural Short | Equipment Failure | 1094 | 165 | 180510 | 0.20165 | 0.0012221
2013-01-28 12:48PM | 1589263-1 | APC2 | Rural Short | Vegetation | 1151 | 47.6481 | 54843 | 0.061266 | 0.0012858
2013-01-28 02:29PM | 1589279-1 | APC2 | Rural Short | Equipment Failure | 1024 | 2 | 2048 | 0.0022879 | 0.0011439
2013-02-20 12:41PM | 1595778-1 | APC2 | Rural Short | Vegetation | 1152 | 45.8776 | 52851 | 0.059041 | 0.0012869
2013-01-16 05:27PM | 1585471-1 | APD2 | Rural Short | Equipment Failure | 1907 | 12.0005 | 22885 | 0.025565 | 0.0021303
2013-02-21 04:50PM | 1596233-1 | APD2 | Rural Short | Equipment Failure | 4 | 45 | 180 | 0.00020108 | 4.4685e-06
2012-11-27 08:03PM | 1573277-1 | APD2 | Rural Short | Weather | 40 | 66.425 | 2657 | 0.0029682 | 4.4685e-05
2012-10-11 07:08PM | 1560786-1 | APD2 | Rural Short | Third Party Impacts | 1518 | 67.5619 | 102559 | 0.11457 | 0.0016958
2013-01-16 05:27PM | 1585471-1 | APE2 | Urban | Equipment Failure | 2740 | 11.9978 | 32874 | 0.036724 | 0.0030609
2012-11-08 11:05AM | 1568199-1 | APE2 | Urban | Equipment Failure | 37 | 139.4324 | 5159 | 0.0057632 | 4.1333e-05
2013-02-20 05:48PM | 1595858-1 | APE2 | Urban | Weather | 36 | 123.4167 | 4443 | 0.0049634 | 4.0216e-05
2012-08-02 11:46AM | 1542330-1 | APE2 | Urban | Equipment Failure | 42 | 240.5 | 10101 | 0.011284 | 4.6919e-05
2013-01-06 11:45PM | 1582757-1 | APE2 | Urban | Equipment Failure | 12 | 66 | 792 | 0.00088476 | 1.3405e-05
2012-09-18 07:04AM | 1555267-1 | APE2 | Urban | Equipment Failure | 20 | 328.3 | 6566 | 0.007335 | 2.2342e-05
2012-09-22 11:01AM | 1556425-1 | APE2 | Urban | Other | 112 | 86.8929 | 9732 | 0.010872 | 0.00012512
2013-01-26 11:12AM | 1588873-1 | APE2 | Urban | Third Party Impacts | 28 | 75.25 | 2107 | 0.0023538 | 3.1279e-05
2013-05-26 05:59AM | 1620245-1 | APE2 | Urban | Equipment Failure | 28 | 344.5714 | 9648 | 0.010778 | 3.1279e-05
2013-05-25 07:39AM | 1621397-1 | APE2 | Urban | Equipment Failure | 30 | 245 | 7350 | 0.0082108 | 3.3514e-05
2013-05-24 09:10PM | 1621800-1 | APE2 | Urban | Equipment Failure | 19 | 40 | 760 | 0.00084901 | 2.1225e-05
2012-09-21 07:19PM | 1556321-1 | APE2 | Urban | Equipment Failure | 83 | 73.506 | 6101 | 0.0068155 | 9.2721e-05
2013-06-08 03:42AM | 1623909-1 | APE2 | Urban | Other | 26 | 110.5769 | 2875 | 0.0032117 | 2.9045e-05
2013-06-26 01:32PM | 1628331-1 | APE2 | Urban | Weather | 1 | 170 | 170 | 0.00018991 | 1.1171e-06
2012-11-25 10:42PM | 1572603-1 | APE2 | Urban | Third Party Impacts | 2091 | 101.8393 | 212946 | 0.23789 | 0.0023359
2013-01-16 05:27PM | 1585471-1 | APF2 | Urban | Equipment Failure | 1144 | 12 | 13728 | 0.015336 | 0.001278
2013-05-20 11:20AM | 1618710-1 | APF2 | Urban | Third Party Impacts | 13 | 30 | 390 | 0.00043568 | 1.4523e-05
2012-12-05 07:51AM | 1575593-1 | APF2 | Urban | Other | 14 | 140 | 1960 | 0.0021896 | 1.564e-05
2012-09-28 11:23AM | 1557771-1 | APF2 | Urban | Equipment Failure | 874 | 44.5 | 38893 | 0.043448 | 0.00097636
2013-06-17 07:36AM | 1625606-1 | T865 | Urban | Other | 1 | 170 | 170 | 0.00018991 | 1.1171e-06
2013-01-18 09:19PM | 1586472-1 | T865 | Urban | Weather | 24 | 186 | 4464 | 0.0049868 | 2.6811e-05
2012-10-31 10:40AM | 1565948-1 | T865 | Urban | Other | 1 | 93 | 93 | 0.00010389 | 1.1171e-06
2012-10-31 05:01PM | 1566063-1 | T865 | Urban | Equipment Failure | 6 | 79 | 474 | 0.00052951 | 6.7027e-06
2012-10-31 06:59PM | 1566082-1 | T865 | Urban | Equipment Failure | 24 | 14.9167 | 358 | 0.00039993 | 2.6811e-05
2012-12-24 05:04PM | 1580185-1 | T865 | Urban | Equipment Failure | 828 | 90.1473 | 74642 | 0.083384 | 0.00092498
2013-05-28 12:43PM | 1620984-1 | T866 | Urban | Other | 18 | 73.4444 | 1322 | 0.0014768 | 2.0108e-05
2012-07-27 07:24PM | 1541004-1 | T866 | Urban | Equipment Failure | 1 | 103 | 103 | 0.00011506 | 1.1171e-06
2013-02-26 02:28PM | 1598667-1 | T866 | Urban | Equipment Failure | 19 | 36 | 684 | 0.00076411 | 2.1225e-05
2013-06-01 10:41AM | 1622223-1 | T866 | Urban | Equipment Failure | 1 | 74 | 74 | 8.2667e-05 | 1.1171e-06
2012-07-22 06:38AM | 1539519-1 | T866 | Urban | Other | 856 | 4.4661 | 3823 | 0.0042707 | 0.00095625
2012-09-11 08:35PM | 1553839-1 | T866 | Urban | Other | 1440 | 95.0812 | 136917 | 0.15295 | 0.0016087
2012-11-17 01:03AM | 1570535-1 | T866 | Urban | Equipment Failure | 1439 | 51.4517 | 74039 | 0.08271 | 0.0016075
2013-02-14 10:06AM | 1594353-1 | T866 | Urban | Equipment Failure | 1 | 81 | 81 | 9.0487e-05 | 1.1171e-06
2013-02-09 06:23PM | 1593105-1 | T868 | Rural Short | Equipment Failure | 1 | 138 | 138 | 0.00015416 | 1.1171e-06
2012-09-21 07:31AM | 1556059-1 | T868 | Rural Short | Other | 9 | 127.1111 | 1144 | 0.001278 | 1.0054e-05
2013-05-09 04:43AM | 1615936-1 | T868 | Rural Short | Animals | 9 | 186.6667 | 1680 | 0.0018768 | 1.0054e-05
2012-07-22 05:08AM | 1539516-1 | T868 | Rural Short | Equipment Failure | 1142 | 86.9921 | 99345 | 0.11098 | 0.0012758
2013-01-28 04:57PM | 1589312-1 | T868 | Rural Short | Vegetation | 286 | 56.6713 | 16208 | 0.018106 | 0.0003195
2013-02-13 04:38PM | 1594186-1 | T868 | Rural Short | Other | 13 | 92 | 1196 | 0.0013361 | 1.4523e-05
2012-11-18 08:27PM | 1570713-1 | T868 | Rural Short | Other | 2103 | 21.7332 | 45705 | 0.051058 | 0.0023493
2013-01-13 01:47PM | 1584369-1 | T869 | Urban | Third Party Impacts | 13 | 65.6154 | 853 | 0.0009529 | 1.4523e-05
2013-03-04 05:27PM | 1600671-1 | T869 | Urban | Equipment Failure | 66 | 160.0606 | 10564 | 0.011801 | 7.373e-05
2012-07-11 09:34AM | 1536987-1 | T869 | Urban | Equipment Failure | 2062 | 56.1232 | 115726 | 0.12928 | 0.0023035
2012-09-19 10:08AM | 1555643-1 | T869 | Urban | Other | 5 | 23 | 115 | 0.00012847 | 5.5856e-06
2012-11-08 03:06AM | 1567976-1 | T869 | Urban | Vegetation | 2214 | 139.5917 | 309056 | 0.34525 | 0.0024733
2012-11-18 08:22PM | 1570735-1 | T869 | Urban | Vegetation | 2266 | 38.7665 | 87845 | 0.098133 | 0.0025314
2013-02-06 10:51AM | 1592065-1 | T869 | Urban | Other | 2110 | 50 | 105500 | 0.11786 | 0.0023571
2013-06-24 09:26AM | 1627429-1 | T870 | Urban | Equipment Failure | 1 | 310 | 310 | 0.00034631 | 1.1171e-06
2012-12-26 01:08AM | 1580613-1 | T870 | Urban | Equipment Failure | 41 | 270.3171 | 11083 | 0.012381 | 4.5802e-05
2013-05-24 02:32AM | 1619895-1 | T872 | Urban | Equipment Failure | 13 | 537.6923 | 6990 | 0.0078087 | 1.4523e-05
2013-04-18 09:33AM | 1611211-1 | T874 | Urban | Equipment Failure | 1 | 226 | 226 | 0.00025247 | 1.1171e-06
2013-01-18 07:52PM | 1586398-1 | T876 | Urban | Weather | 23 | 120.4783 | 2771 | 0.0030955 | 2.5694e-05
2012-09-30 04:21AM | 1558121-1 | T876 | Urban | Third Party Impacts | 69 | 233.8696 | 16137 | 0.018027 | 7.7081e-05
2013-05-20 09:26PM | 1618907-1 | AZ1205 | Urban | Third Party Impacts | 122 | 1638.2213 | 199863 | 0.22327 | 0.00013629
2013-06-16 01:01PM | 1625554-1 | AZ1205 | Urban | Vegetation | 18 | 108 | 1944 | 0.0021717 | 2.0108e-05
2012-12-24 10:21PM | 1580370-1 | AZ1205 | Urban | Weather | 1107 | 97.9666 | 108449 | 0.12115 | 0.0012367
2013-04-15 06:30PM | 1610484-1 | AZ1205 | Urban | Weather | 1099 | 181.9572 | 199971 | 0.22339 | 0.0012277
2013-04-15 09:31PM | 1610523-1 | AZ1205 | Urban | Weather | 994 | 18.6197 | 18508 | 0.020676 | 0.0011104
2013-04-15 10:20PM | 1612509-1 | AZ1205 | Urban | Weather | 1099 | 108 | 118692 | 0.13259 | 0.0012277
2013-01-15 09:33AM | 1585027-1 | AZ1227 | Urban | Animals | 84 | 147 | 12348 | 0.013794 | 9.3838e-05
2013-01-27 09:43AM | 1589086-1 | AZ1227 | Urban | Weather | 521 | 105.7236 | 55082 | 0.061533 | 0.00058202
2012-10-11 08:51AM | 1560517-1 | AZ1227 | Urban | Equipment Failure | 1 | 179 | 179 | 0.00019996 | 1.1171e-06
2012-10-02 02:50PM | 1560997-1 | AZ1227 | Urban | Equipment Failure | 1 | 145 | 145 | 0.00016198 | 1.1171e-06
2012-11-30 05:06PM | 1574375-1 | AZ1257 | Urban | Third Party Impacts | 22 | 144 | 3168 | 0.003539 | 2.4577e-05
2013-01-17 09:53AM | 1585616-1 | AZ1257 | Urban | Operatonal Error | 123 | 64.0163 | 7874 | 0.0087962 | 0.00013741
2013-03-07 06:52PM | 1601837-1 | AZ1264 | Urban | Equipment Failure | 18 | 60 | 1080 | 0.0012065 | 2.0108e-05
2013-04-11 08:49AM | 1609446-1 | AZ1272 | Urban | Third Party Impacts | 34 | 243.0294 | 8263 | 0.0092308 | 3.7982e-05
2013-01-18 09:39PM | 1586504-1 | AZ1272 | Urban | Vegetation | 46 | 1051 | 48346 | 0.054008 | 5.1388e-05
2013-03-04 05:23PM | 1600670-1 | AZ1272 | Urban | Third Party Impacts | 19 | 28.8947 | 549 | 0.0006133 | 2.1225e-05
2013-01-21 08:26AM | 1586836-1 | AZ1272 | Urban | Third Party Impacts | 94 | 62.6064 | 5885 | 0.0065743 | 0.00010501
2013-01-15 07:12AM | 1584994-1 | AZ1272 | Urban | Animals | 1338 | 75.2646 | 100704 | 0.1125 | 0.0014947
2013-04-12 08:49AM | 1609826-1 | AZ1272 | Urban | Other | 1 | 82 | 82 | 9.1604e-05 | 1.1171e-06
2012-08-21 11:37AM | 1547711-1 | W114 | Rural Short | Equipment Failure | 1 | 158 | 158 | 0.0001765 | 1.1171e-06
2012-09-17 11:35AM | 1555034-1 | W111 | Rural Short | Other | 29 | 113 | 3277 | 0.0036608 | 3.2396e-05
2012-11-13 01:32PM | 1569541-1 | W111 | Rural Short | Other | 1 | 103 | 103 | 0.00011506 | 1.1171e-06
2012-12-05 02:51PM | 1575846-1 | W111 | Rural Short | Weather | 6 | 106 | 636 | 0.00071049 | 6.7027e-06
2012-09-28 12:26PM | 1557803-1 | W111 | Rural Short | Other | 1 | 6 | 6 | 6.7027e-06 | 1.1171e-06
2012-07-03 09:40AM | 1535254-1 | W111 | Rural Short | Equipment Failure | 2 | 361 | 722 | 0.00080656 | 2.2342e-06
2012-07-02 10:54AM | 1534778-1 | W111 | Rural Short | Third Party Impacts | 8 | 73.875 | 591 | 0.00066022 | 8.937e-06
2012-11-08 03:59PM | 1568349-1 | W111 | Rural Short | Weather | 577 | 97.7123 | 56380 | 0.062983 | 0.00064458
2013-03-30 06:08AM | 1607076-1 | W112 | Rural Short | Equipment Failure | 12 | 160 | 1920 | 0.0021449 | 1.3405e-05
2013-01-23 07:36AM | 1587571-1 | W112 | Rural Short | Weather | 1 | 276 | 276 | 0.00030833 | 1.1171e-06
2013-05-08 08:30AM | 1617237-1 | W114 | Rural Short | Operatonal Error | 3 | 5 | 15 | 1.6757e-05 | 3.3514e-06
2012-10-29 05:32PM | 1565511-1 | 17058 | Urban | Third Party Impacts | 2 | 265.5 | 531 | 0.00059319 | 2.2342e-06
2013-06-24 08:04PM | 1627592-1 | 17058 | Urban | Weather | 1494 | 100.0703 | 149505 | 0.16702 | 0.001669
2013-04-26 05:02PM | 1613261-1 | 17061 | Urban | Equipment Failure | 17 | 442.5294 | 7523 | 0.0084041 | 1.8991e-05
2013-03-23 07:18PM | 1605804-1 | 17061 | Urban | Operatonal Error | 887 | 16.3833 | 14532 | 0.016234 | 0.00099089
2013-04-24 11:52PM | 1612929-1 | 17067 | Urban | Third Party Impacts | 1492 | 95.4933 | 142476 | 0.15916 | 0.0016667
2013-06-17 05:36PM | 1625884-1 | 17067 | Urban | Other | 24 | 108.5833 | 2606 | 0.0029112 | 2.6811e-05
2012-07-02 07:33AM | 1534711-1 | 17068 | Urban | Animals | 4 | 137 | 548 | 0.00061218 | 4.4685e-06
2013-02-07 12:00PM | 1592458-1 | 17068 | Urban | Other | 4 | 94 | 376 | 0.00042004 | 4.4685e-06
2013-05-23 11:17AM | 1619676-1 | 17070 | Urban | Other | 1 | 80 | 80 | 8.937e-05 | 1.1171e-06
2013-05-23 08:14AM | 1619569-1 | 17070 | Urban | Other | 1 | 136 | 136 | 0.00015193 | 1.1171e-06
2013-06-25 01:57PM | 1627928-1 | 17070 | Urban | Weather | 19 | 136.8947 | 2601 | 0.0029056 | 2.1225e-05
2013-02-10 01:34PM | 1593215-1 | 46748 | Urban | Equipment Failure | 2 | 260 | 520 | 0.0005809 | 2.2342e-06
2013-04-15 07:41PM | 1610497-1 | 46750 | Urban | Weather | 16 | 102 | 1632 | 0.0018231 | 1.7874e-05
2013-03-11 08:48AM | 1602481-1 | 46763 | Urban | Other | 3 | 193.6667 | 581 | 0.00064905 | 3.3514e-06
2012-11-21 06:31PM | 1571718-1 | 46768 | Urban | Equipment Failure | 185 | 71.0054 | 13136 | 0.014674 | 0.00020667
2013-03-05 03:30PM | 1601008-1 | 46772 | Urban | Equipment Failure | 2 | 97 | 194 | 0.00021672 | 2.2342e-06
2012-10-04 02:08PM | 1558933-1 | 46774 | Urban | Equipment Failure | 69 | 238 | 16422 | 0.018345 | 7.7081e-05
2013-04-15 12:25AM | 1610237-1 | 46774 | Urban | Third Party Impacts | 544 | 151.2592 | 82285 | 0.091922 | 0.00060771
2013-01-14 02:27AM | 1584619-1 | 35304 | Urban | Animals | 20 | 148.95 | 2979 | 0.0033279 | 2.2342e-05
2012-09-07 03:17PM | 1552884-1 | 35304 | Urban | Weather | 909 | 38.3102 | 34824 | 0.038903 | 0.0010155
2012-08-10 05:51PM | 1544942-1 | 35305 | Urban | Weather | 37 | 33.027 | 1222 | 0.0013651 | 4.1333e-05
2012-09-07 04:06PM | 1552918-1 | 35305 | Urban | Weather | 26 | 154 | 4004 | 0.0044729 | 2.9045e-05
2013-06-06 11:03AM | 1623425-1 | 35306 | Urban | Third Party Impacts | 1 | 103 | 103 | 0.00011506 | 1.1171e-06
2013-03-19 05:09AM | 1604462-1 | 35306 | Urban | Vegetation | 60 | 260.9167 | 15655 | 0.017489 | 6.7027e-05
2013-02-07 08:39AM | 1592348-1 | 35307 | Urban | Equipment Failure | 2 | 133 | 266 | 0.00029715 | 2.2342e-06
2012-07-04 03:18PM | 1535640-1 | 35307 | Urban | Equipment Failure | 14 | 605.5714 | 8478 | 0.0094709 | 1.564e-05
2013-02-06 12:35PM | 1592117-1 | 35307 | Urban | Other | 1 | 105 | 105 | 0.0001173 | 1.1171e-06
2012-08-17 04:01PM | 1546987-1 | 35312 | Urban | Equipment Failure | 16 | 105.5625 | 1689 | 0.0018868 | 1.7874e-05
2012-09-07 12:27PM | 1552772-1 | 35312 | Urban | Weather | 16 | 494 | 7904 | 0.0088297 | 1.7874e-05
2012-07-15 10:16AM | 1537870-1 | 35312 | Urban | Animals | 5 | 663.2 | 3316 | 0.0037044 | 5.5856e-06
2012-11-26 02:53AM | 1572612-1 | 35312 | Urban | Vegetation | 551 | 57.9165 | 31912 | 0.03565 | 0.00061553
2012-08-17 07:32PM | 1547080-1 | 35314 | Urban | Weather | 1 | 121 | 121 | 0.00013517 | 1.1171e-06
2013-01-03 11:13AM | 1581989-1 | 35314 | Urban | Third Party Impacts | 34 | 56 | 1904 | 0.002127 | 3.7982e-05
2012-08-17 12:06PM | 1546574-1 | 35314 | Urban | Weather | 424 | 73.8608 | 31317 | 0.034985 | 0.00047366
2013-03-15 12:53AM | 1603616-1 | 35314 | Urban | Animals | 426 | 13.4366 | 5724 | 0.0063944 | 0.00047589
2012-08-17 03:25PM | 1546953-1 | 35315 | Urban | Weather | 56 | 118.2679 | 6623 | 0.0073987 | 6.2559e-05
2013-04-04 02:30PM | 1607870-1 | 35315 | Urban | Third Party Impacts | 30 | 168 | 5040 | 0.0056303 | 3.3514e-05
2013-01-28 04:11PM | 1589336-1 | R256 | Urban | Weather | 38 | 1685 | 64030 | 0.071529 | 4.2451e-05
2012-07-03 10:07PM | 1535396-1 | R256 | Urban | Other | 34 | 76.7941 | 2611 | 0.0029168 | 3.7982e-05
2013-02-10 11:19AM | 1593194-1 | R256 | Urban | Third Party Impacts | 13 | 282 | 3666 | 0.0040954 | 1.4523e-05
2013-02-02 07:23AM | 1590959-1 | R256 | Urban | Other | 5 | 648 | 3240 | 0.0036195 | 5.5856e-06
2012-11-08 03:46PM | 1568339-1 | R256 | Urban | Vegetation | 1277 | 59.0329 | 75385 | 0.084214 | 0.0014266
2013-01-04 09:30AM | 1582266-1 | R257 | Urban | Equipment Failure | 46 | 63.4348 | 2918 | 0.0032598 | 5.1388e-05
2013-01-18 07:14PM | 1586355-1 | R257 | Urban | Equipment Failure | 28 | 256.6071 | 7185 | 0.0080265 | 3.1279e-05
2013-06-09 08:15AM | 1624039-1 | R257 | Urban | Equipment Failure | 1 | 177 | 177 | 0.00019773 | 1.1171e-06
2013-03-06 10:37PM | 1601543-1 | BGA2 | Rural Short | Animals | 1 | 62 | 62 | 6.9261e-05 | 1.1171e-06
2012-11-11 08:27PM | 1569096-1 | BGA2 | Rural Short | Other | 17 | 77 | 1309 | 0.0014623 | 1.8991e-05
2012-12-26 05:11AM | 1580620-1 | BGA2 | Rural Short | Other | 17 | 109.2353 | 1857 | 0.0020745 | 1.8991e-05
2013-06-10 08:07AM | 1624096-1 | BGA2 | Rural Short | Equipment Failure | 10 | 168.4 | 1684 | 0.0018812 | 1.1171e-05
2012-07-04 09:51AM | 1535477-1 | BGA2 | Rural Short | Equipment Failure | 5 | 302.8 | 1514 | 0.0016913 | 5.5856e-06
2013-02-26 11:52AM | 1598590-1 | BGA2 | Rural Short | Equipment Failure | 2 | 162 | 324 | 0.00036195 | 2.2342e-06
2012-10-25 03:52AM | 1564439-1 | BGA2 | Rural Short | Equipment Failure | 408 | 82.8211 | 33791 | 0.037749 | 0.00045578
2013-06-24 11:35PM | 1627644-1 | BGA2 | Rural Short | Vegetation | 719 | 27.8331 | 20012 | 0.022356 | 0.00080321
2012-11-18 06:39PM | 1573498-1 | BDA2 | Urban | Other | 1530 | 5.3791 | 8230 | 0.0091939 | 0.0017092
2013-01-23 09:23AM | 1591644-1 | BDA2 | Urban | Operatonal Error | 1801 | 11.3059 | 20362 | 0.022747 | 0.0020119
2012-09-14 04:33PM | 1554727-1 | BDA2 | Urban | Other | 2 | 159 | 318 | 0.00035524 | 2.2342e-06
2013-05-16 08:31AM | 1617737-1 | BDA2 | Urban | Equipment Failure | 1 | 97 | 97 | 0.00010836 | 1.1171e-06
2012-07-18 07:43PM | 1538688-1 | BDA2 | Urban | Equipment Failure | 72 | 54.0972 | 3895 | 0.0043512 | 8.0433e-05
2013-01-21 04:25PM | 1587010-1 | BDA2 | Urban | Vegetation | 1818 | 73 | 132714 | 0.14826 | 0.0020309
2012-11-18 06:39PM | 1573498-1 | BDB2 | Urban | Other | 122 | 5.377 | 656 | 0.00073283 | 0.00013629
2013-01-23 09:23AM | 1591644-1 | BDB2 | Urban | Operatonal Error | 144 | 11.2708 | 1623 | 0.0018131 | 0.00016087
2012-11-18 06:39PM | 1573498-1 | BDC2 | Rural Short | Other | 781 | 5.3764 | 4199 | 0.0046908 | 0.00087247
2013-01-23 09:23AM | 1591644-1 | BDC2 | Rural Short | Operatonal Error | 919 | 11.3036 | 10388 | 0.011605 | 0.0010266
2012-12-19 07:57AM | 1578883-1 | BWG2 | Urban | Operatonal Error | 12 | 106.25 | 1275 | 0.0014243 | 1.3405e-05
2012-12-17 05:58PM | 1578589-1 | BWH2 | Rural Short | Other | 3 | 158 | 474 | 0.00052951 | 3.3514e-06
2012-12-01 02:58PM | 1574667-1 | BWH2 | Rural Short | Weather | 3 | 300 | 900 | 0.0010054 | 3.3514e-06
2013-04-14 10:23PM | 1610229-1 | BWH2 | Rural Short | Other | 1 | 53 | 53 | 5.9207e-05 | 1.1171e-06
2012-11-15 06:18PM | 1570226-1 | BWH2 | Rural Short | Vegetation | 3 | 370 | 1110 | 0.00124 | 3.3514e-06
2012-12-23 06:55PM | 1579992-1 | BWH2 | Rural Short | Weather | 2 | 155 | 310 | 0.00034631 | 2.2342e-06
2013-03-11 06:19PM | 1602694-1 | BWH2 | Rural Short | Other | 2 | 49 | 98 | 0.00010948 | 2.2342e-06
2012-10-24 09:42AM | 1564181-1 | BWH2 | Rural Short | Other | 1 | 411 | 411 | 0.00045914 | 1.1171e-06
2012-11-28 03:08PM | 1573617-1 | BWH2 | Rural Short | Weather | 3 | 148 | 444 | 0.000496 | 3.3514e-06
2012-09-30 01:30AM | 1558120-1 | BWH2 | Rural Short | Equipment Failure | 20 | 79.15 | 1583 | 0.0017684 | 2.2342e-05
2012-11-19 09:11PM | 1571060-1 | BWH2 | Rural Short | Equipment Failure | 43 | 62 | 2666 | 0.0029782 | 4.8036e-05
2012-09-25 12:06PM | 1556887-1 | BWH2 | Rural Short | Animals | 2 | 75 | 150 | 0.00016757 | 2.2342e-06
2013-01-18 03:55PM | 1586191-1 | BWH2 | Rural Short | Vegetation | 10 | 127.1 | 1271 | 0.0014199 | 1.1171e-05
2013-04-28 11:15AM | 1613451-1 | BWH2 | Rural Short | Vegetation | 23 | 186.3478 | 4286 | 0.004788 | 2.5694e-05
2012-12-01 05:42PM | 1574701-1 | BWH2 | Rural Short | Weather | 27 | 231 | 6237 | 0.0069675 | 3.0162e-05
2013-01-19 12:02PM | 1586606-1 | BWH2 | Rural Short | Weather | 8 | 332.375 | 2659 | 0.0029704 | 8.937e-06
2012-12-23 09:49PM | 1580026-1 | BWH2 | Rural Short | Weather | 4 | 80 | 320 | 0.00035748 | 4.4685e-06
2012-11-30 07:34AM | 1574078-1 | BWH2 | Rural Short | Other | 1 | 175 | 175 | 0.0001955 | 1.1171e-06
2012-12-23 08:21PM | 1580010-1 | BWH2 | Rural Short | Weather | 2 | 89 | 178 | 0.00019885 | 2.2342e-06
2012-09-06 12:04PM | 1552386-1 | BWH2 | Rural Short | Other | 1 | 44 | 44 | 4.9153e-05 | 1.1171e-06
2012-12-24 08:15AM | 1580054-1 | BWH2 | Rural Short | Weather | 2 | 195 | 390 | 0.00043568 | 2.2342e-06
2012-12-29 07:21AM | 1581269-1 | BWH2 | Rural Short | Other | 2 | 124 | 248 | 0.00027705 | 2.2342e-06
2013-03-02 08:11PM | 1600250-1 | BWH2 | Rural Short | Equipment Failure | 24 | 87.9167 | 2110 | 0.0023571 | 2.6811e-05
2012-11-02 05:34AM | 1566513-1 | BWH2 | Rural Short | Equipment Failure | 15 | 213 | 3195 | 0.0035692 | 1.6757e-05
2012-07-30 06:45AM | 1541194-1 | BWH2 | Rural Short | Other | 18 | 140.6667 | 2532 | 0.0028285 | 2.0108e-05
2012-07-25 06:26PM | 1540400-1 | BWH2 | Rural Short | Equipment Failure | 7 | 269 | 1883 | 0.0021035 | 7.8198e-06
2013-06-28 01:43PM | 1629033-1 | BWH2 | Rural Short | Weather | 5 | 145.8 | 729 | 0.00081438 | 5.5856e-06
2012-07-06 08:08AM | 1536005-1 | 35315 | Urban | Other | 1 | 91 | 91 | 0.00010166 | 1.1171e-06
2013-04-19 10:10PM | 1611665-1 | 35315 | Urban | Equipment Failure | 29 | 59 | 1711 | 0.0019114 | 3.2396e-05
2012-07-31 02:14PM | 1541694-1 | 35324 | Urban | Operatonal Error | 0 |  | 0 | 0 | 0
2013-01-14 02:49AM | 1584621-1 | 35325 | Urban | Animals | 1 | 134 | 134 | 0.00014969 | 1.1171e-06
2012-07-31 02:14PM | 1541694-1 | 35325 | Urban | Operatonal Error | 812 | 8.6281 | 7006 | 0.0078265 | 0.0009071
2013-06-12 12:00PM | 1624595-1 | 35326 | Urban | Other | 16 | 124.25 | 1988 | 0.0022208 | 1.7874e-05
2013-05-04 02:23PM | 1614905-1 | 35326 | Urban | Vegetation | 457 | 62.1554 | 28405 | 0.031732 | 0.00051052
2012-08-17 02:01PM | 1546788-1 | 35327 | Urban | Weather | 22 | 172.2727 | 3790 | 0.0042339 | 2.4577e-05
2013-03-15 07:19AM | 1603634-1 | 35327 | Urban | Animals | 31 | 528.2581 | 16376 | 0.018294 | 3.4631e-05
2012-07-31 02:14PM | 1541694-1 | 35327 | Urban | Operatonal Error | 1356 | 8.6232 | 11693 | 0.013062 | 0.0015148
2012-10-08 09:45AM | 1559669-1 | 35333 | Urban | Other | 64 | 5.875 | 376 | 0.00042004 | 7.1496e-05
2013-05-01 03:05PM | 1614247-1 | 35335 | Urban | Equipment Failure | 18 | 75 | 1350 | 0.0015081 | 2.0108e-05
2012-12-01 03:51PM | 1574679-1 | 35335 | Urban | Other | 42 | 44 | 1848 | 0.0020644 | 4.6919e-05
2013-01-13 04:28PM | 1584401-1 | 35335 | Urban | Equipment Failure | 11 | 53.7273 | 591 | 0.00066022 | 1.2288e-05
2012-08-16 11:06AM | 1546263-1 | 35335 | Urban | Equipment Failure | 1 | 374 | 374 | 0.0004178 | 1.1171e-06
2013-01-11 05:51PM | 1584186-1 | 49319 | Urban | Other | 23 | 90.4783 | 2081 | 0.0023247 | 2.5694e-05
2012-08-29 09:29AM | 1550246-1 | 49319 | Urban | Other | 14 | 102.5714 | 1436 | 0.0016042 | 1.564e-05
2012-08-10 09:07AM | 1544377-1 | 49319 | Urban | Other | 11 | 90.4545 | 995 | 0.0011115 | 1.2288e-05
2013-06-26 01:39PM | 1628342-1 | 49319 | Urban | Equipment Failure | 9 | 57 | 513 | 0.00057308 | 1.0054e-05
2012-12-25 06:10PM | 1580565-1 | 49328 | Urban | Weather | 20 | 54 | 1080 | 0.0012065 | 2.2342e-05
2012-12-26 12:55PM | 1580679-1 | 49328 | Urban | Other | 20 | 39.45 | 789 | 0.00088141 | 2.2342e-05
2013-06-24 09:35PM | 1627614-1 | 49328 | Urban | Equipment Failure | 28 | 287.7857 | 8058 | 0.0090018 | 3.1279e-05
2012-09-08 07:31AM | 1553075-1 | 49328 | Urban | Equipment Failure | 32 | 401.1875 | 12838 | 0.014342 | 3.5748e-05
2012-12-09 08:34AM | 1576599-1 | 49328 | Urban | Other | 1 | 439 | 439 | 0.00049042 | 1.1171e-06
2013-02-08 04:49PM | 1592871-1 | 49337 | Urban | Weather | 787 | 7.399 | 5823 | 0.006505 | 0.00087917
2013-06-02 12:58PM | 1622324-1 | 49341 | Urban | Other | 18 | 93.1667 | 1677 | 0.0018734 | 2.0108e-05
2013-01-08 08:39PM | 1583398-1 | 49341 | Urban | Operatonal Error | 1571 | 2 | 3142 | 0.00351 | 0.001755
2013-05-22 06:25PM | 1619476-1 | 49348 | Urban | Other | 1 | 342 | 342 | 0.00038206 | 1.1171e-06
2012-10-16 08:18AM | 1562055-1 | 49357 | Urban | Vegetation | 13 | 252 | 3276 | 0.0036597 | 1.4523e-05
2012-12-04 02:43PM | 1575353-1 | 49357 | Urban | Equipment Failure | 1 | 196 | 196 | 0.00021896 | 1.1171e-06
2012-07-29 05:32PM | 1541157-1 | 49362 | Urban | Equipment Failure | 30 | 643.6333 | 19309 | 0.02157 | 3.3514e-05
2012-08-14 01:18PM | 1545754-1 | 49362 | Urban | Third Party Impacts | 12 | 345 | 4140 | 0.0046249 | 1.3405e-05
2012-12-20 11:23PM | 1579568-1 | X877 | Rural Short | Third Party Impacts | 23 | 701 | 16123 | 0.018011 | 2.5694e-05
2013-06-16 10:07AM | 1625521-1 | X877 | Rural Short | Equipment Failure | 1 | 76 | 76 | 8.4901e-05 | 1.1171e-06
2013-06-01 03:31PM | 1622242-1 | X877 | Rural Short | Other | 1 | 50 | 50 | 5.5856e-05 | 1.1171e-06
2013-06-18 04:59PM | 1626171-1 | X877 | Rural Short | Other | 1 | 139 | 139 | 0.00015528 | 1.1171e-06
2012-08-03 05:19PM | 1542791-1 | X877 | Rural Short | Equipment Failure | 1 | 100 | 100 | 0.00011171 | 1.1171e-06
2012-08-06 03:15PM | 1543238-1 | X877 | Rural Short | Equipment Failure | 2 | 85 | 170 | 0.00018991 | 2.2342e-06
2012-08-07 07:46PM | 1543623-1 | X877 | Rural Short | Equipment Failure | 4 | 78.25 | 313 | 0.00034966 | 4.4685e-06
2012-11-01 06:23AM | 1566136-1 | X877 | Rural Short | Other | 8 | 126 | 1008 | 0.0011261 | 8.937e-06
2013-04-29 02:00PM | 1613659-1 | X877 | Rural Short | Other | 3 | 81.3333 | 244 | 0.00027258 | 3.3514e-06
2013-01-24 06:10PM | 1588072-1 | X877 | Rural Short | Animals | 15 | 76 | 1140 | 0.0012735 | 1.6757e-05
2012-08-17 01:35PM | 1546856-1 | X877 | Rural Short | Weather | 21 | 275.9048 | 5794 | 0.0064726 | 2.346e-05
2012-09-23 12:35PM | 1556562-1 | X877 | Rural Short | Equipment Failure | 7 | 100.8571 | 706 | 0.00078869 | 7.8198e-06
2012-12-07 08:06AM | 1576272-1 | X877 | Rural Short | Other | 3 | 387 | 1161 | 0.001297 | 3.3514e-06
2013-01-08 08:18PM | 1583388-1 | X877 | Rural Short | Other | 18 | 84 | 1512 | 0.0016891 | 2.0108e-05
2012-12-20 09:45AM | 1579320-1 | X877 | Rural Short | Other | 1 | 204 | 204 | 0.00022789 | 1.1171e-06
2012-10-03 04:04PM | 1558626-1 | X877 | Rural Short | Equipment Failure | 160 | 78.5 | 12560 | 0.014031 | 0.00017874
2013-04-19 09:15AM | 1611467-1 | X877 | Rural Short | Weather | 21 | 122 | 2562 | 0.0028621 | 2.346e-05
2012-11-01 06:23AM | 1566134-1 | X877 | Rural Short | Other | 1 | 122 | 122 | 0.00013629 | 1.1171e-06
2012-07-29 01:41PM | 1541143-1 | X877 | Rural Short | Other | 2 | 113 | 226 | 0.00025247 | 2.2342e-06
2012-08-16 01:30PM | 1546302-1 | X877 | Rural Short | Other | 1 | 122 | 122 | 0.00013629 | 1.1171e-06
2012-08-11 10:41AM | 1545060-1 | X877 | Rural Short | Weather | 1375 | 59.8073 | 82235 | 0.091866 | 0.001536
2013-05-21 09:39AM | 1618970-1 | X877 | Rural Short | Operatonal Error | 1322 | 6.1278 | 8101 | 0.0090498 | 0.0014768
2012-12-13 11:29AM | 1577627-1 | R293 | Rural Short | Other | 1 | 518 | 518 | 0.00057867 | 1.1171e-06
2012-12-08 08:48AM | 1576528-1 | R293 | Rural Short | Other | 92 | 141.9783 | 13062 | 0.014592 | 0.00010278
2013-06-15 05:59PM | 1625487-1 | R293 | Rural Short | Other | 94 | 130.0745 | 12227 | 0.013659 | 0.00010501
2013-01-08 11:30PM | 1583451-1 | A337 | Urban | Equipment Failure | 10 | 391 | 3910 | 0.0043679 | 1.1171e-05
2013-01-18 07:50PM | 1586393-1 | A337 | Urban | Weather | 10 | 165.7 | 1657 | 0.0018511 | 1.1171e-05
2013-01-18 07:50PM | 1586392-1 | A337 | Urban | Weather | 25 | 169.76 | 4244 | 0.0047411 | 2.7928e-05
2012-10-03 05:12PM | 1558645-1 | A339 | Urban | Equipment Failure | 753 | 127.911 | 96317 | 0.1076 | 0.00084119
2012-10-18 04:17PM | 1562877-1 | A341 | Urban | Other | 20 | 78 | 1560 | 0.0017427 | 2.2342e-05
2013-03-05 01:07AM | 1600777-1 | A341 | Urban | Equipment Failure | 155 | 98.3161 | 15239 | 0.017024 | 0.00017315
2013-03-05 02:54AM | 1600790-1 | A341 | Urban | Equipment Failure | 31 | 469 | 14539 | 0.016242 | 3.4631e-05
2012-09-09 04:35AM | 1553242-1 | A343 | Urban | Equipment Failure | 74 | 98.5405 | 7292 | 0.008146 | 8.2667e-05
2012-11-21 09:05PM | 1571729-1 | A343 | Urban | Equipment Failure | 1 | 128 | 128 | 0.00014299 | 1.1171e-06
2013-01-30 04:04PM | 1590096-1 | A346 | Urban | Equipment Failure | 6 | 57 | 342 | 0.00038206 | 6.7027e-06
2012-09-09 04:57PM | 1553304-1 | A346 | Urban | Third Party Impacts | 544 | 16.739 | 9106 | 0.010172 | 0.00060771
2012-10-20 11:32AM | 1563290-1 | 3188 | Urban | Animals | 41 | 38 | 1558 | 0.0017405 | 4.5802e-05
2012-07-29 05:22AM | 1541087-1 | 3188 | Urban | Equipment Failure | 83 | 67.4819 | 5601 | 0.006257 | 9.2721e-05
2013-06-24 07:06AM | 1627391-1 | CV1210 | Urban | Third Party Impacts | 17 | 460 | 7820 | 0.0087359 | 1.8991e-05
2013-05-30 04:59PM | 1621810-1 | CV1236 | Urban | Equipment Failure | 1 | 145 | 145 | 0.00016198 | 1.1171e-06
2013-04-26 01:10PM | 1613145-1 | CV1236 | Urban | Equipment Failure | 1 | 1359 | 1359 | 0.0015182 | 1.1171e-06
2013-06-01 02:15PM | 1622239-1 | CV1239 | Urban | Vegetation | 28 | 67 | 1876 | 0.0020957 | 3.1279e-05
2013-02-27 11:06PM | 1599190-1 | CV1247 | Urban | Other | 123 | 63 | 7749 | 0.0086566 | 0.00013741
2012-11-05 10:35PM | 1567378-1 | D840 | Urban | Third Party Impacts | 44 | 96 | 4224 | 0.0047187 | 4.9153e-05
2013-01-18 06:36PM | 1586447-1 | D840 | Urban | Weather | 22 | 217.2727 | 4780 | 0.0053398 | 2.4577e-05
2012-07-03 12:24PM | 1535170-1 | D840 | Urban | Equipment Failure | 19 | 186 | 3534 | 0.0039479 | 2.1225e-05
2013-02-05 12:06PM | 1591707-1 | D840 | Urban | Third Party Impacts | 19 | 147 | 2793 | 0.0031201 | 2.1225e-05
2013-01-14 10:12AM | 1584688-1 | D841 | Urban | Vegetation | 82 | 58.1098 | 4765 | 0.0053231 | 9.1604e-05
2012-11-05 05:40AM | 1567031-1 | D842 | Urban | Animals | 263 | 185.0722 | 48674 | 0.054375 | 0.0002938
2012-12-04 03:43PM | 1575399-1 | D845 | Urban | Equipment Failure | 118 | 122 | 14396 | 0.016082 | 0.00013182
2012-07-03 12:44PM | 1535208-1 | D847 | Urban | Equipment Failure | 13 | 105.1538 | 1367 | 0.0015271 | 1.4523e-05
2012-11-26 09:59PM | 1572959-1 | D850 | Urban | Third Party Impacts | 68 | 42.0882 | 2862 | 0.0031972 | 7.5964e-05
2013-01-08 08:39PM | 1583399-1 | 49362 | Urban | Operatonal Error | 771 | 2 | 1542 | 0.0017226 | 0.0008613
2013-02-25 03:52PM | 1598218-1 | 49366 | Urban | Operatonal Error | 1405 | 60.0968 | 84436 | 0.094325 | 0.0015696
2013-03-14 02:28PM | 1603464-1 | 49382 | Urban | Equipment Failure | 131 | 111 | 14541 | 0.016244 | 0.00014634
2013-06-05 06:58PM | 1623279-1 | 49391 | Urban | Equipment Failure | 1 | 133 | 133 | 0.00014858 | 1.1171e-06
2012-12-19 11:06AM | 1578987-1 | BYB2 | Rural Short | Vegetation | 189 | 42.1323 | 7963 | 0.0088956 | 0.00021114
2012-12-20 05:59PM | 1579535-1 | BYB2 | Rural Short | Equipment Failure | 189 | 48.7407 | 9212 | 0.010291 | 0.00021114
2013-03-22 12:53AM | 1605331-1 | BYB2 | Rural Short | Vegetation | 189 | 285.4392 | 53948 | 0.060266 | 0.00021114
2012-08-04 06:46AM | 1542852-1 | BYB2 | Rural Short | Equipment Failure | 114 | 106.5877 | 12151 | 0.013574 | 0.00012735
2013-06-25 08:29AM | 1627717-1 | BYB2 | Rural Short | Weather | 146 | 75.1027 | 10965 | 0.012249 | 0.0001631
2013-06-17 01:08PM | 1625745-1 | BYB2 | Rural Short | Other | 1 | 48 | 48 | 5.3622e-05 | 1.1171e-06
2012-09-06 11:51AM | 1552382-1 | BYB2 | Rural Short | Weather | 34 | 87.2059 | 2965 | 0.0033123 | 3.7982e-05
2013-01-04 07:17PM | 1582476-1 | BYB2 | Rural Short | Other | 25 | 165 | 4125 | 0.0046081 | 2.7928e-05
2012-09-18 08:49PM | 1555574-1 | BYB2 | Rural Short | Other | 5 | 105 | 525 | 0.00058649 | 5.5856e-06
2013-02-28 11:08AM | 1599279-1 | BYB2 | Rural Short | Vegetation | 5 | 249 | 1245 | 0.0013908 | 5.5856e-06
2013-06-10 07:28PM | 1624155-1 | BYB2 | Rural Short | Other | 17 | 66 | 1122 | 0.0012534 | 1.8991e-05
2013-06-10 09:23PM | 1624179-1 | BYB2 | Rural Short | Equipment Failure | 50 | 1107.48 | 55374 | 0.061859 | 5.5856e-05
2012-12-31 05:32PM | 1581554-1 | BYB2 | Rural Short | Equipment Failure | 1 | 66 | 66 | 7.373e-05 | 1.1171e-06
2013-06-21 04:42PM | 1627048-1 | BYB2 | Rural Short | Vegetation | 17 | 50 | 850 | 0.00094955 | 1.8991e-05
2012-09-07 08:39PM | 1553020-1 | BYB2 | Rural Short | Weather | 684 | 152.6901 | 104440 | 0.11667 | 0.00076411
2012-11-18 06:39PM | 1573498-1 | BYC2 | Rural Short | Other | 331 | 5.3867 | 1783 | 0.0019918 | 0.00036977
2012-09-06 04:38AM | 1552197-1 | BYC2 | Rural Short | Weather | 199 | 169.9095 | 33812 | 0.037772 | 0.00022231
2012-09-07 03:08PM | 1552883-1 | BYC2 | Rural Short | Weather | 199 | 298.0251 | 59307 | 0.066253 | 0.00022231
2012-09-29 10:13AM | 1558051-1 | BYC2 | Rural Short | Vegetation | 198 | 91.7778 | 18172 | 0.0203 | 0.00022119
2013-01-09 08:24AM | 1583492-1 | BYC2 | Rural Short | Vegetation | 199 | 154.6734 | 30780 | 0.034385 | 0.00022231
2012-09-28 03:50AM | 1557658-1 | BYC2 | Rural Short | Weather | 73 | 98.4521 | 7187 | 0.0080287 | 8.155e-05
2013-06-23 12:35AM | 1627184-1 | BYC2 | Rural Short | Vegetation | 75 | 52.6 | 3945 | 0.004407 | 8.3784e-05
2013-03-28 07:02AM | 1606792-1 | BYC2 | Rural Short | Vegetation | 15 | 398.6667 | 5980 | 0.0066804 | 1.6757e-05
2013-03-10 11:21AM | 1602367-1 | BYC2 | Rural Short | Equipment Failure | 4 | 70 | 280 | 0.00031279 | 4.4685e-06
2013-02-16 01:11PM | 1594876-1 | BYC2 | Rural Short | Animals | 4 | 162 | 648 | 0.00072389 | 4.4685e-06
2012-09-01 05:33PM | 1551186-1 | BYC2 | Rural Short | Equipment Failure | 5 | 73 | 365 | 0.00040775 | 5.5856e-06
2012-09-06 11:51AM | 1552381-1 | BYC2 | Rural Short | Weather | 33 | 91.5455 | 3021 | 0.0033748 | 3.6865e-05
2013-05-30 06:09PM | 1621823-1 | BYC2 | Rural Short | Equipment Failure | 1 | 87 | 87 | 9.7189e-05 | 1.1171e-06
2012-09-29 08:58AM | 1558037-1 | BYC2 | Rural Short | Weather | 1 | 134 | 134 | 0.00014969 | 1.1171e-06
2012-08-02 07:05AM | 1542239-1 | BYC2 | Rural Short | Other | 1 | 243 | 243 | 0.00027146 | 1.1171e-06
2013-01-12 04:15AM | 1584227-1 | BYC2 | Rural Short | Vegetation | 70 | 138.2429 | 9677 | 0.01081 | 7.8198e-05
2012-12-14 04:47AM | 1577834-1 | BYC2 | Rural Short | Other | 9 | 88 | 792 | 0.00088476 | 1.0054e-05
2013-05-04 06:37AM | 1614844-1 | BYC2 | Rural Short | Weather | 33 | 310 | 10230 | 0.011428 | 3.6865e-05
2013-03-07 06:57AM | 1601601-1 | BYC2 | Rural Short | Vegetation | 1 | 374 | 374 | 0.0004178 | 1.1171e-06
2012-11-18 06:39PM | 1573498-1 | BYD2 | Rural Short | Other | 830 | 5.3747 | 4461 | 0.0049835 | 0.00092721
2012-07-28 10:58AM | 1541041-1 | BYD2 | Rural Short | Equipment Failure | 18 | 39.0556 | 703 | 0.00078534 | 2.0108e-05
2013-01-14 06:49AM | 1584635-1 | BYD2 | Rural Short | Equipment Failure | 1 | 102 | 102 | 0.00011395 | 1.1171e-06
2013-03-22 07:45PM | 1605688-1 | BYD2 | Rural Short | Weather | 3 | 99 | 297 | 0.00033178 | 3.3514e-06
2012-08-10 02:33PM | 1544712-1 | BYD2 | Rural Short | Weather | 2 | 116.5 | 233 | 0.00026029 | 2.2342e-06
2013-03-25 04:39PM | 1606180-1 | BYD2 | Rural Short | Equipment Failure | 4 | 81 | 324 | 0.00036195 | 4.4685e-06
2012-11-07 10:34AM | 1567779-1 | BYD2 | Rural Short | Equipment Failure | 117 | 21 | 2457 | 0.0027448 | 0.0001307
2013-05-15 06:45AM | 1617386-1 | BYD2 | Rural Short | Other | 82 | 193.9146 | 15901 | 0.017763 | 9.1604e-05
2013-01-09 07:58AM | 1583485-1 | BYD2 | Rural Short | Other | 1 | 486 | 486 | 0.00054292 | 1.1171e-06
2012-11-01 02:03PM | 1566323-1 | BYD2 | Rural Short | Weather | 986 | 186.3185 | 183710 | 0.20523 | 0.0011015
2013-03-23 10:26AM | 1605742-1 | BYD2 | Rural Short | Equipment Failure | 115 | 54.2087 | 6234 | 0.0069641 | 0.00012847
2012-11-18 06:39PM | 1573498-1 | BYE2 | Rural Short | Other | 189 | 5.3862 | 1018 | 0.0011372 | 0.00021114
2013-01-21 06:52AM | 1586814-1 | BYE2 | Rural Short | Other | 227 | 181.3304 | 41162 | 0.045983 | 0.00025359
2012-11-18 06:39PM | 1573498-1 | BYF2 | Rural Short | Other | 402 | 5.3806 | 2163 | 0.0024163 | 0.00044908
2013-05-04 11:53AM | 1614881-1 | BYF2 | Rural Short | Equipment Failure | 1 | 178 | 178 | 0.00019885 | 1.1171e-06
2012-11-18 06:39PM | 1573498-1 | BYG2 | Rural Short | Other | 523 | 5.3805 | 2814 | 0.0031436 | 0.00058425
2013-03-02 09:44PM | 1600257-1 | BYG2 | Rural Short | Equipment Failure | 3 | 51 | 153 | 0.00017092 | 3.3514e-06
2012-11-06 07:11PM | 1567605-1 | BYG2 | Rural Short | Weather | 6 | 83 | 498 | 0.00055633 | 6.7027e-06
2013-02-26 11:42AM | 1598586-1 | BYG2 | Rural Short | Equipment Failure | 15 | 9.4 | 141 | 0.00015751 | 1.6757e-05
2012-09-28 08:45AM | 1557692-1 | BYG2 | Rural Short | Vegetation | 11 | 85.7273 | 943 | 0.0010534 | 1.2288e-05
2013-04-22 03:36AM | 1611877-1 | BYG2 | Rural Short | Vegetation | 12 | 54 | 648 | 0.00072389 | 1.3405e-05
2012-11-01 05:13PM | 1566449-1 | BYG2 | Rural Short | Other | 1605 | 7.2162 | 11582 | 0.012938 | 0.001793
2013-06-24 11:18PM | 1627641-1 | BYG2 | Rural Short | Vegetation | 622 | 86.299 | 53678 | 0.059965 | 0.00069485
2012-11-28 06:59AM | 1573408-1 | BK1236 | Urban | Weather | 5 | 96 | 480 | 0.00053622 | 5.5856e-06
2013-05-03 04:06PM | 1614782-1 | BK1236 | Urban | Equipment Failure | 3 | 156 | 468 | 0.00052281 | 3.3514e-06
2013-04-02 11:14AM | 1607342-1 | BK1236 | Urban | Third Party Impacts | 2 | 22 | 44 | 4.9153e-05 | 2.2342e-06
2012-09-05 02:06PM | 1551999-1 | BK1236 | Urban | Weather | 77 | 132 | 10164 | 0.011354 | 8.6018e-05
2013-02-16 12:27AM | 1594807-1 | BK1236 | Urban | Equipment Failure | 1 | 79 | 79 | 8.8252e-05 | 1.1171e-06
2013-02-16 09:17AM | 1594852-1 | BK1236 | Urban | Operatonal Error | 39 | 83 | 3237 | 0.0036161 | 4.3568e-05
2012-07-19 12:20PM | 1538942-1 | BK1236 | Urban | Operatonal Error | 422 | 2.9313 | 1237 | 0.0013819 | 0.00047142
2013-02-04 01:06AM | 1591214-1 | BK1236 | Urban | Other | 942 | 0.98301 | 926 | 0.0010345 | 0.0010523
2012-09-05 02:24PM | 1552005-1 | BK1236 | Urban | Weather | 4 | 159 | 636 | 0.00071049 | 4.4685e-06
2012-10-27 06:34PM | 1565177-1 | BK1236 | Urban | Equipment Failure | 1 | 113 | 113 | 0.00012623 | 1.1171e-06
2013-03-09 03:35PM | 1602262-1 | BK1236 | Urban | Equipment Failure | 1 | 100 | 100 | 0.00011171 | 1.1171e-06
2013-01-29 09:00AM | 1593631-1 | BK1251 | Rural Short | Equipment Failure | 1 | 3060 | 3060 | 0.0034184 | 1.1171e-06
2013-01-27 07:33AM | 1589037-1 | BK1251 | Rural Short | Other | 2 | 222 | 444 | 0.000496 | 2.2342e-06
2013-02-09 06:29PM | 1593107-1 | BK1251 | Rural Short | Weather | 3 | 96 | 288 | 0.00032173 | 3.3514e-06
2012-09-16 08:12AM | 1554866-1 | BK1251 | Rural Short | Other | 1 | 117 | 117 | 0.0001307 | 1.1171e-06
2012-09-06 11:10AM | 1552367-1 | BK1251 | Rural Short | Weather | 47 | 203.9149 | 9584 | 0.010706 | 5.2505e-05
2012-11-01 09:40AM | 1566226-1 | BK1251 | Rural Short | Equipment Failure | 3 | 59.6667 | 179 | 0.00019996 | 3.3514e-06
2012-11-21 09:10AM | 1573811-1 | BK1251 | Rural Short | Equipment Failure | 12 | 60 | 720 | 0.00080433 | 1.3405e-05
2013-06-26 07:34AM | 1628149-1 | BK1251 | Rural Short | Weather | 38 | 121.5789 | 4620 | 0.0051611 | 4.2451e-05
2012-07-19 12:20PM | 1538941-1 | BK1251 | Rural Short | Operatonal Error | 1282 | 2.5827 | 3311 | 0.0036988 | 0.0014321
2012-11-03 06:08AM | 1566751-1 | BK1251 | Rural Short | Vegetation | 929 | 84 | 78036 | 0.087176 | 0.0010378
2013-06-04 04:02PM | 1622960-1 | BK1288 | Rural Short | Equipment Failure | 1 | 101 | 101 | 0.00011283 | 1.1171e-06
2013-05-30 09:10AM | 1621543-1 | BK1288 | Rural Short | Equipment Failure | 1 | 323 | 323 | 0.00036083 | 1.1171e-06
2012-11-28 07:30AM | 1573347-1 | BK1288 | Rural Short | Weather | 40 | 359.5 | 14380 | 0.016064 | 4.4685e-05
2012-12-09 06:56PM | 1576672-1 | BK1288 | Rural Short | Weather | 1 | 73 | 73 | 8.155e-05 | 1.1171e-06
2013-02-10 09:02AM | 1593180-1 | BK1288 | Rural Short | Other | 1 | 222 | 222 | 0.000248 | 1.1171e-06
2012-12-09 01:54PM | 1576645-1 | BK1288 | Rural Short | Weather | 8 | 91 | 728 | 0.00081326 | 8.937e-06
2013-02-10 12:56PM | 1593211-1 | BK1288 | Rural Short | Weather | 1362 | 71.1755 | 96941 | 0.10829 | 0.0015215
2012-10-31 06:18AM | 1565888-1 | BK1299 | Rural Short | Other | 1 | 333 | 333 | 0.000372 | 1.1171e-06
2013-05-23 08:42PM | 1619873-1 | BK1299 | Rural Short | Vegetation | 26 | 143 | 3718 | 0.0041535 | 2.9045e-05
2012-10-22 10:39AM | 1563511-1 | BK1299 | Rural Short | Animals | 62 | 6.5645 | 407 | 0.00045467 | 6.9261e-05
2012-10-30 10:26AM | 1565643-1 | BK1299 | Rural Short | Third Party Impacts | 1 | 28 | 28 | 3.1279e-05 | 1.1171e-06
2012-10-30 09:22PM | 1565860-1 | BK1299 | Rural Short | Weather | 1 | 73 | 73 | 8.155e-05 | 1.1171e-06
2013-02-10 08:34AM | 1593176-1 | BK1299 | Rural Short | Other | 8 | 318 | 2544 | 0.002842 | 8.937e-06
2012-10-30 04:52PM | 1565832-1 | BK1299 | Rural Short | Weather | 6 | 108 | 648 | 0.00072389 | 6.7027e-06
2013-02-01 03:50PM | 1590813-1 | BK1299 | Rural Short | Weather | 6 | 59 | 354 | 0.00039546 | 6.7027e-06
2013-02-10 08:00PM | 1593353-1 | BK1299 | Rural Short | Weather | 15 | 148 | 2220 | 0.00248 | 1.6757e-05
2012-11-03 04:07PM | 1566882-1 | BK1299 | Rural Short | Vegetation | 127 | 39.2441 | 4984 | 0.0055677 | 0.00014187
2013-01-13 04:04PM | 1584387-1 | BK1299 | Rural Short | Weather | 719 | 1 | 719 | 0.00080321 | 0.00080321
2012-09-10 04:41PM | 1553533-1 | BK1299 | Rural Short | Equipment Failure | 42 | 9 | 378 | 0.00042227 | 4.6919e-05
2013-05-14 12:34AM | 1617062-1 | T828 | Rural Short | Equipment Failure | 264 | 58.7803 | 15518 | 0.017335 | 0.00029492
2012-11-08 06:38PM | 1568496-1 | T828 | Rural Short | Weather | 18 | 247 | 4446 | 0.0049667 | 2.0108e-05
2013-02-06 09:17PM | 1592300-1 | T828 | Rural Short | Equipment Failure | 1 | 118 | 118 | 0.00013182 | 1.1171e-06
2012-08-29 04:43PM | 1550462-1 | T828 | Rural Short | Other | 1 | 137 | 137 | 0.00015305 | 1.1171e-06
2013-02-26 05:29PM | 1598735-1 | T828 | Rural Short | Weather | 2 | 209 | 418 | 0.00046696 | 2.2342e-06
2012-08-15 03:27PM | 1546131-1 | T828 | Rural Short | Equipment Failure | 1 | 568 | 568 | 0.00063452 | 1.1171e-06
2012-11-19 01:35PM | 1570884-1 | T828 | Rural Short | Weather | 134 | 4.2612 | 571 | 0.00063788 | 0.00014969
2013-02-10 08:01PM | 1593354-1 | T828 | Rural Short | Weather | 1 | 1162 | 1162 | 0.0012981 | 1.1171e-06
2012-11-30 06:18PM | 1574428-1 | T828 | Rural Short | Weather | 3 | 442 | 1326 | 0.0014813 | 3.3514e-06
2012-11-07 05:59PM | 1567917-1 | T828 | Rural Short | Vegetation | 14 | 62 | 868 | 0.00096966 | 1.564e-05
2012-12-25 08:17PM | 1580644-1 | T828 | Rural Short | Weather | 1 | 11270 | 11270 | 0.01259 | 1.1171e-06
2013-02-26 12:38AM | 1598437-1 | T828 | Rural Short | Weather | 14 | 398.5 | 5579 | 0.0062324 | 1.564e-05
2013-02-10 08:20PM | 1593363-1 | T828 | Rural Short | Weather | 2 | 248 | 496 | 0.00055409 | 2.2342e-06
2012-12-25 02:23PM | 1580484-1 | T828 | Rural Short | Equipment Failure | 184 | 271 | 49864 | 0.055704 | 0.00020555
2013-02-11 01:27PM | 1593577-1 | T828 | Rural Short | Weather | 5 | 223.2 | 1116 | 0.0012467 | 5.5856e-06
2013-02-25 04:11PM | 1598234-1 | T828 | Rural Short | Equipment Failure | 180 | 365.6944 | 65825 | 0.073534 | 0.00020108
2012-11-30 12:43PM | 1574212-1 | T828 | Rural Short | Equipment Failure | 1 | 67 | 67 | 7.4847e-05 | 1.1171e-06
2013-02-12 08:51AM | 1593755-1 | T828 | Rural Short | Third Party Impacts | 1 | 270 | 270 | 0.00030162 | 1.1171e-06
2013-05-14 12:34AM | 1617062-1 | T829 | Rural Short | Equipment Failure | 18 | 58.7778 | 1058 | 0.0011819 | 2.0108e-05
2013-04-17 12:30PM | 1612862-1 | T831 | Rural Short | Third Party Impacts | 2 | 90 | 180 | 0.00020108 | 2.2342e-06
2013-05-14 12:34AM | 1617062-1 | T831 | Rural Short | Equipment Failure | 1029 | 58.7813 | 60486 | 0.06757 | 0.0011495
2012-12-16 02:21PM | 1578315-1 | T831 | Rural Short | Other | 1 | 97 | 97 | 0.00010836 | 1.1171e-06
2013-02-11 05:55AM | 1593402-1 | T831 | Rural Short | Weather | 1 | 497 | 497 | 0.00055521 | 1.1171e-06
2012-09-05 04:58PM | 1552127-1 | T831 | Rural Short | Weather | 137 | 68 | 9316 | 0.010407 | 0.00015305
2013-06-04 11:33AM | 1622830-1 | T831 | Rural Short | Equipment Failure | 1 | 142 | 142 | 0.00015863 | 1.1171e-06
2012-10-03 03:48PM | 1558619-1 | T831 | Rural Short | Equipment Failure | 2 | 114 | 228 | 0.0002547 | 2.2342e-06
2013-02-12 12:25PM | 1593835-1 | T831 | Rural Short | Equipment Failure | 2 | 284 | 568 | 0.00063452 | 2.2342e-06
2013-02-10 07:44PM | 1593334-1 | T831 | Rural Short | Weather | 2 | 228 | 456 | 0.00050941 | 2.2342e-06
2012-12-22 09:32PM | 1579862-1 | T831 | Rural Short | Weather | 3 | 950 | 2850 | 0.0031838 | 3.3514e-06
2012-12-25 05:30PM | 1580561-1 | T831 | Rural Short | Weather | 3 | 1269 | 3807 | 0.0042529 | 3.3514e-06
2013-02-13 09:38AM | 1594062-1 | T831 | Rural Short | Other | 1 | 96 | 96 | 0.00010724 | 1.1171e-06
2012-12-25 03:33PM | 1580532-1 | T831 | Rural Short | Weather | 5 | 1212 | 6060 | 0.0067697 | 5.5856e-06
2012-12-26 10:44AM | 1580655-1 | T831 | Rural Short | Weather | 4 | 63.5 | 254 | 0.00028375 | 4.4685e-06
2012-09-29 08:49AM | 1558034-1 | T831 | Rural Short | Other | 9 | 81.7778 | 736 | 0.0008222 | 1.0054e-05
2012-12-25 03:15PM | 1580518-1 | T831 | Rural Short | Equipment Failure | 8 | 1393 | 11144 | 0.012449 | 8.937e-06
2012-10-26 08:30AM | 1564846-1 | T831 | Rural Short | Equipment Failure | 1 | 170 | 170 | 0.00018991 | 1.1171e-06
2013-02-10 07:58PM | 1593352-1 | T831 | Rural Short | Weather | 10 | 571 | 5710 | 0.0063788 | 1.1171e-05
2012-08-09 04:25PM | 1544201-1 | T834 | Rural Short | Equipment Failure | 3 | 158.3333 | 475 | 0.00053063 | 3.3514e-06
2013-05-14 12:34AM | 1617062-1 | T834 | Rural Short | Equipment Failure | 122 | 58.7787 | 7171 | 0.0080109 | 0.00013629
2012-11-29 03:23PM | 1573976-1 | T834 | Rural Short | Weather | 1 | 5 | 5 | 5.5856e-06 | 1.1171e-06
2013-02-08 09:02PM | 1592965-1 | T834 | Rural Short | Third Party Impacts | 1 | 55 | 55 | 6.1442e-05 | 1.1171e-06
2012-12-18 05:37PM | 1578832-1 | T834 | Rural Short | Other | 9 | 1058.3333 | 9525 | 0.010641 | 1.0054e-05
2013-02-19 06:27PM | 1595617-1 | T834 | Rural Short | Weather | 2 | 96 | 192 | 0.00021449 | 2.2342e-06
2013-03-14 09:38PM | 1603597-1 | T834 | Rural Short | Weather | 1 | 28 | 28 | 3.1279e-05 | 1.1171e-06
2012-07-02 06:02AM | 1534703-1 | T834 | Rural Short | Other | 94 | 111.5638 | 10487 | 0.011715 | 0.00010501
2012-07-01 11:55AM | 1534638-1 | T834 | Rural Short | Equipment Failure | 2 | 59.5 | 119 | 0.00013294 | 2.2342e-06
2013-05-14 12:34AM | 1617062-1 | T836 | Rural Short | Equipment Failure | 33 | 58.7879 | 1940 | 0.0021672 | 3.6865e-05
2012-07-05 06:33PM | 1535951-1 | T836 | Rural Short | Equipment Failure | 3 | 12 | 36 | 4.0216e-05 | 3.3514e-06
2013-02-10 09:57AM | 1593184-1 | T836 | Rural Short | Weather | 1 | 255 | 255 | 0.00028487 | 1.1171e-06
2013-01-22 08:00AM | 1587135-1 | T836 | Rural Short | Equipment Failure | 33 | 6 | 198 | 0.00022119 | 3.6865e-05
2013-02-10 07:26PM | 1593320-1 | T836 | Rural Short | Weather | 33 | 150.4545 | 4965 | 0.0055465 | 3.6865e-05
2012-07-19 06:30PM | 1539112-1 | R247 | Urban | Equipment Failure | 27 | 49.8889 | 1347 | 0.0015048 | 3.0162e-05
2013-04-13 01:34PM | 1610115-1 | R248 | Urban | Third Party Impacts | 1 | 162 | 162 | 0.00018097 | 1.1171e-06
2012-10-30 11:36AM | 1565684-1 | R248 | Urban | Vegetation | 26 | 13 | 338 | 0.00037759 | 2.9045e-05
2013-05-08 06:07PM | 1615895-1 | R248 | Urban | Equipment Failure | 42 | 556.2143 | 23361 | 0.026097 | 4.6919e-05
2012-11-22 10:25PM | 1572023-1 | R248 | Urban | Animals | 31 | 74.7742 | 2318 | 0.0025895 | 3.4631e-05
2012-10-14 12:49PM | 1561582-1 | R250 | Urban | Equipment Failure | 1 | 129 | 129 | 0.00014411 | 1.1171e-06
2012-07-10 06:40PM | 1536984-1 | R250 | Urban | Equipment Failure | 40 | 905.6 | 36224 | 0.040467 | 4.4685e-05
2012-11-30 08:58PM | 1574501-1 | R250 | Urban | Weather | 37 | 93.2973 | 3452 | 0.0038563 | 4.1333e-05
2012-10-11 03:53PM | 1560629-1 | R250 | Urban | Equipment Failure | 16 | 402.75 | 6444 | 0.0071987 | 1.7874e-05
2012-11-14 03:24AM | 1569672-1 | R250 | Urban | Vegetation | 1220 | 90 | 109800 | 0.12266 | 0.0013629
2013-03-09 01:32AM | 1602223-1 | R250 | Urban | Third Party Impacts | 577 | 53 | 30581 | 0.034163 | 0.00064458
2012-07-20 07:19PM | 1539428-1 | R251 | Urban | Equipment Failure | 37 | 67 | 2479 | 0.0027693 | 4.1333e-05
2013-06-23 11:33AM | 1627232-1 | R251 | Urban | Other | 1 | 321 | 321 | 0.0003586 | 1.1171e-06
2012-09-26 08:31AM | 1557067-1 | R251 | Urban | Other | 23 | 24 | 552 | 0.00061665 | 2.5694e-05
2012-10-31 09:48AM | 1565936-1 | R251 | Urban | Vegetation | 24 | 8.5833 | 206 | 0.00023013 | 2.6811e-05
2013-01-21 07:39PM | 1587093-1 | R251 | Urban | Vegetation | 323 | 22 | 7106 | 0.0079383 | 0.00036083
2013-03-30 09:17AM | 1607088-1 | R253 | Urban | Equipment Failure | 26 | 63 | 1638 | 0.0018298 | 2.9045e-05
2013-05-12 08:05PM | 1616760-1 | R253 | Urban | Equipment Failure | 30 | 27 | 810 | 0.00090487 | 3.3514e-05
2013-03-28 02:08PM | 1606871-1 | R254 | Urban | Other | 23 | 62 | 1426 | 0.001593 | 2.5694e-05
2012-07-09 12:46PM | 1536612-1 | R254 | Urban | Other | 88 | 254.4773 | 22394 | 0.025017 | 9.8307e-05
2012-08-24 09:49AM | 1549109-1 | R256 | Urban | Weather | 41 | 128.8293 | 5282 | 0.0059006 | 4.5802e-05
2012-08-29 12:26PM | 1550322-1 | R256 | Urban | Equipment Failure | 35 | 244.2857 | 8550 | 0.0095514 | 3.9099e-05
2013-01-28 01:29PM | 1589268-1 | R256 | Urban | Weather | 24 | 122 | 2928 | 0.0032709 | 2.6811e-05
2013-05-20 08:03AM | 1618657-1 | BDC2 | Rural Short | Vegetation | 13 | 347.2308 | 4514 | 0.0050427 | 1.4523e-05
2013-06-25 10:37PM | 1628103-1 | BDC2 | Rural Short | Weather | 566 | 31.8498 | 18027 | 0.020138 | 0.00063229
2013-01-18 05:59PM | 1586283-1 | BDC2 | Rural Short | Weather | 61 | 307.2951 | 18745 | 0.02094 | 6.8144e-05
2013-04-14 10:38AM | 1610190-1 | BDC2 | Rural Short | Equipment Failure | 49 | 199.5714 | 9779 | 0.010924 | 5.4739e-05
2013-05-04 08:55AM | 1614856-1 | BDC2 | Rural Short | Equipment Failure | 74 | 72.2027 | 5343 | 0.0059688 | 8.2667e-05
2012-11-25 08:52AM | 1572498-1 | BDC2 | Rural Short | Equipment Failure | 41 | 440.5122 | 18061 | 0.020176 | 4.5802e-05
2012-11-18 06:38PM | 1570685-1 | BDC2 | Rural Short | Vegetation | 1 | 1094 | 1094 | 0.0012221 | 1.1171e-06
2013-06-23 10:45AM | 1627226-1 | BDC2 | Rural Short | Equipment Failure | 21 | 422.1429 | 8865 | 0.0099033 | 2.346e-05
2012-11-23 02:47PM | 1572290-1 | BDC2 | Rural Short | Vegetation | 3 | 319 | 957 | 0.0010691 | 3.3514e-06
2012-12-28 11:11AM | 1581125-1 | BDC2 | Rural Short | Other | 3 | 80 | 240 | 0.00026811 | 3.3514e-06
2012-11-18 06:39PM | 1573498-1 | BDD2 | Urban | Other | 602 | 5.3804 | 3239 | 0.0036184 | 0.00067251
2013-01-23 09:23AM | 1591644-1 | BDD2 | Urban | Operatonal Error | 709 | 11.3047 | 8015 | 0.0089537 | 0.00079204
2012-11-18 06:39PM | 1573498-1 | BDE2 | Urban | Other | 968 | 5.3802 | 5208 | 0.005818 | 0.0010814
2013-01-23 09:23AM | 1591644-1 | BDE2 | Urban | Operatonal Error | 1140 | 11.3018 | 12884 | 0.014393 | 0.0012735
2013-02-28 05:28PM | 1599425-1 | BDE2 | Urban | Third Party Impacts | 89 | 365 | 32485 | 0.03629 | 9.9424e-05
2013-06-25 02:54PM | 1627950-1 | BDE2 | Urban | Weather | 22 | 143 | 3146 | 0.0035145 | 2.4577e-05
2013-06-26 03:06PM | 1628402-1 | BDE2 | Urban | Weather | 41 | 83 | 3403 | 0.0038016 | 4.5802e-05
2013-06-30 03:43PM | 1629393-1 | BDE2 | Urban | Equipment Failure | 22 | 205 | 4510 | 0.0050382 | 2.4577e-05
2013-06-23 06:28PM | 1627347-1 | BDE2 | Urban | Equipment Failure | 44 | 86.4545 | 3804 | 0.0042495 | 4.9153e-05
2012-07-20 03:39PM | 1539341-1 | BDE2 | Urban | Third Party Impacts | 27 | 198.2963 | 5354 | 0.0059811 | 3.0162e-05
2013-01-18 05:52PM | 1586273-1 | BDE2 | Urban | Weather | 1069 | 37.1805 | 39746 | 0.044401 | 0.0011942
2013-03-17 08:29PM | 1604196-1 | BDE2 | Urban | Animals | 1070 | 56.7364 | 60708 | 0.067818 | 0.0011953
2013-05-21 06:05AM | 1618925-1 | BDE2 | Urban | Equipment Failure | 200 | 78.23 | 15646 | 0.017478 | 0.00022342
2012-11-18 06:39PM | 1573498-1 | BDF2 | Rural Short | Other | 1036 | 5.3764 | 5570 | 0.0062224 | 0.0011573
2013-01-23 09:23AM | 1591644-1 | BDF2 | Rural Short | Operatonal Error | 1219 | 11.3043 | 13780 | 0.015394 | 0.0013618
2012-09-01 10:29AM | 1551136-1 | BDF2 | Rural Short | Vegetation | 301 | 280.6346 | 84471 | 0.094364 | 0.00033625
2012-11-11 01:31PM | 1569075-1 | BDF2 | Rural Short | Vegetation | 301 | 33 | 9933 | 0.011096 | 0.00033625
2013-01-18 05:53PM | 1586275-1 | BDF2 | Rural Short | Weather | 301 | 182.2126 | 54846 | 0.06127 | 0.00033625
2012-09-18 03:27PM | 1555451-1 | BDF2 | Rural Short | Weather | 31 | 178.9032 | 5546 | 0.0061955 | 3.4631e-05
2012-12-01 04:54PM | 1574690-1 | BDF2 | Rural Short | Equipment Failure | 64 | 123.8906 | 7929 | 0.0088576 | 7.1496e-05
2013-06-20 06:32PM | 1626770-1 | BDF2 | Rural Short | Equipment Failure | 44 | 54.1136 | 2381 | 0.0026599 | 4.9153e-05
2012-11-11 02:17PM | 1569080-1 | BDF2 | Rural Short | Other | 4 | 58 | 232 | 0.00025917 | 4.4685e-06
2012-09-01 05:20PM | 1551184-1 | BDF2 | Rural Short | Other | 8 | 52 | 416 | 0.00046472 | 8.937e-06
2012-09-01 10:29AM | 1551137-1 | BDF2 | Rural Short | Other | 1048 | 234.0095 | 245242 | 0.27396 | 0.0011707
2012-09-06 12:58PM | 1552399-1 | BDF2 | Rural Short | Weather | 4 | 80.75 | 323 | 0.00036083 | 4.4685e-06
2012-11-01 02:37PM | 1566364-1 | BDF2 | Rural Short | Vegetation | 1221 | 97.6175 | 119191 | 0.13315 | 0.001364
2013-03-28 01:01PM | 1606855-1 | BDF2 | Rural Short | Other | 1 | 315 | 315 | 0.00035189 | 1.1171e-06
2012-11-18 06:39PM | 1573498-1 | BDG2 | Rural Short | Other | 1399 | 5.3781 | 7524 | 0.0084052 | 0.0015629
2013-01-23 09:23AM | 1591644-1 | BDG2 | Rural Short | Operatonal Error | 1646 | 11.3098 | 18616 | 0.020796 | 0.0018388
2012-09-26 11:52AM | 1557114-1 | BDG2 | Rural Short | Equipment Failure | 1 | 88 | 88 | 9.8307e-05 | 1.1171e-06
2012-07-13 07:33AM | 1537533-1 | BDG2 | Rural Short | Other | 4 | 64 | 256 | 0.00028598 | 4.4685e-06
2012-11-07 07:25AM | 1567696-1 | BDG2 | Rural Short | Other | 4 | 214 | 856 | 0.00095625 | 4.4685e-06
2012-07-28 12:00PM | 1541046-1 | BDG2 | Rural Short | Operatonal Error | 7 | 152.5714 | 1068 | 0.0011931 | 7.8198e-06
2012-07-28 12:00PM | 1541051-1 | BDG2 | Rural Short | Other | 1 | 196 | 196 | 0.00021896 | 1.1171e-06
2012-09-18 03:47PM | 1555463-1 | BDG2 | Rural Short | Weather | 40 | 2.05 | 82 | 9.1604e-05 | 4.4685e-05
2013-01-08 03:29PM | 1583270-1 | BDG2 | Rural Short | Weather | 39 | 86 | 3354 | 0.0037468 | 4.3568e-05
2012-10-20 02:39PM | 1563312-1 | BDG2 | Rural Short | Equipment Failure | 51 | 2.3922 | 122 | 0.00013629 | 5.6973e-05
2012-11-18 06:42PM | 1570690-1 | BDG2 | Rural Short | Other | 1 | 62 | 62 | 6.9261e-05 | 1.1171e-06
2012-07-28 05:59PM | 1541063-1 | 8762 | Urban | Equipment Failure | 78 | 97.0769 | 7572 | 0.0084588 | 8.7135e-05
2013-05-22 11:13PM | 1619525-1 | 8762 | Urban | Equipment Failure | 1 | 62 | 62 | 6.9261e-05 | 1.1171e-06
2013-06-28 08:46AM | 1628924-1 | 8762 | Urban | Equipment Failure | 1 | 316 | 316 | 0.00035301 | 1.1171e-06
2012-08-20 08:57AM | 1547360-1 | 8762 | Urban | Equipment Failure | 1685 | 116.9662 | 197088 | 0.22017 | 0.0018823
2013-05-13 09:44AM | 1616823-1 | 8766 | Urban | Other | 1 | 463 | 463 | 0.00051723 | 1.1171e-06
2013-02-15 12:00PM | 1594687-1 | 8766 | Urban | Third Party Impacts | 15 | 324.8 | 4872 | 0.0054426 | 1.6757e-05
2013-06-24 09:21AM | 1627428-1 | 8766 | Urban | Weather | 23 | 97.2609 | 2237 | 0.002499 | 2.5694e-05
2013-06-25 04:59PM | 1628016-1 | 8766 | Urban | Weather | 15 | 67 | 1005 | 0.0011227 | 1.6757e-05
2012-10-13 08:22PM | 1561530-1 | 8766 | Urban | Other | 1 | 227 | 227 | 0.00025359 | 1.1171e-06
2013-06-22 10:55PM | 1627177-1 | 8767 | Urban | Equipment Failure | 36 | 271 | 9756 | 0.010899 | 4.0216e-05
2013-05-16 07:06AM | 1617726-1 | 8767 | Urban | Equipment Failure | 7 | 211 | 1477 | 0.00165 | 7.8198e-06
2012-12-19 12:37PM | 1579045-1 | 8767 | Urban | Other | 51 | 99.5098 | 5075 | 0.0056694 | 5.6973e-05
2012-12-03 07:55AM | 1574864-1 | 8767 | Urban | Third Party Impacts | 92 | 161.5978 | 14867 | 0.016608 | 0.00010278
2012-09-17 09:34AM | 1554992-1 | 8769 | Urban | Equipment Failure | 1 | 60 | 60 | 6.7027e-05 | 1.1171e-06
2013-04-11 07:31PM | 1609756-1 | 8770 | Urban | Equipment Failure | 34 | 94 | 3196 | 0.0035703 | 3.7982e-05
2013-01-12 03:58PM | 1584285-1 | 8770 | Urban | Equipment Failure | 30 | 147.9667 | 4439 | 0.0049589 | 3.3514e-05
2012-08-10 02:03PM | 1544629-1 | 8770 | Urban | Other | 11 | 100.4545 | 1105 | 0.0012344 | 1.2288e-05
2013-01-17 01:05PM | 1585676-1 | 8770 | Urban | Third Party Impacts | 71 | 376.0704 | 26701 | 0.029828 | 7.9316e-05
2013-01-25 03:08PM | 1588448-1 | 8770 | Urban | Equipment Failure | 47 | 296 | 13912 | 0.015541 | 5.2505e-05
2012-09-18 05:50AM | 1555258-1 | 8770 | Urban | Equipment Failure | 6 | 298.6667 | 1792 | 0.0020019 | 6.7027e-06
2012-09-29 01:30PM | 1558077-1 | 8772 | Urban | Other | 1 | 128 | 128 | 0.00014299 | 1.1171e-06
2013-01-04 02:10PM | 1582358-1 | 8772 | Urban | Other | 64 | 55.1406 | 3529 | 0.0039423 | 7.1496e-05
2012-07-14 07:00PM | 1537832-1 | 8773 | Urban | Equipment Failure | 22 | 12.5455 | 276 | 0.00030833 | 2.4577e-05
2012-07-14 07:13PM | 1537836-1 | 8773 | Urban | Equipment Failure | 22 | 318 | 6996 | 0.0078154 | 2.4577e-05
2013-01-08 04:45PM | 1583303-1 | 8773 | Urban | Equipment Failure | 1390 | 201.7741 | 280466 | 0.31331 | 0.0015528
2013-01-10 03:23PM | 1583880-1 | 8773 | Urban | Other | 25 | 62.88 | 1572 | 0.0017561 | 2.7928e-05
2012-08-11 11:49AM | 1545074-1 | 8773 | Urban | Equipment Failure | 36 | 283 | 10188 | 0.011381 | 4.0216e-05
2012-11-26 06:14PM | 1572921-1 | 8774 | Urban | Other | 1 | 18 | 18 | 2.0108e-05 | 1.1171e-06
2013-04-26 02:11AM | 1613001-1 | 8774 | Urban | Equipment Failure | 9 | 247 | 2223 | 0.0024834 | 1.0054e-05
2013-04-26 06:59AM | 1613016-1 | 8774 | Urban | Equipment Failure | 21 | 297.5714 | 6249 | 0.0069809 | 2.346e-05
2013-04-26 05:48PM | 1613267-1 | 8774 | Urban | Equipment Failure | 15 | 544.2667 | 8164 | 0.0091202 | 1.6757e-05
2012-11-25 01:57PM | 1572514-1 | 8776 | Urban | Equipment Failure | 59 | 167.8644 | 9904 | 0.011064 | 6.591e-05
2012-07-25 07:14AM | 1540151-1 | 8776 | Urban | Equipment Failure | 29 | 33.6897 | 977 | 0.0010914 | 3.2396e-05
2012-09-23 03:28AM | 1556523-1 | 8776 | Urban | Equipment Failure | 1 | 511 | 511 | 0.00057085 | 1.1171e-06
2012-12-05 08:25PM | 1575946-1 | 8776 | Urban | Third Party Impacts | 14 | 340 | 4760 | 0.0053175 | 1.564e-05
2013-02-06 06:51PM | 1592252-1 | 8776 | Urban | Other | 7 | 41 | 287 | 0.00032061 | 7.8198e-06
2013-02-07 06:00AM | 1592333-1 | 8776 | Urban | Equipment Failure | 11 | 293.1818 | 3225 | 0.0036027 | 1.2288e-05
2012-08-19 05:30PM | 1547297-1 | 8776 | Urban | Equipment Failure | 1 | 200 | 200 | 0.00022342 | 1.1171e-06
2013-06-26 02:20PM | 1628369-1 | 8777 | Urban | Weather | 1 | 379 | 379 | 0.00042339 | 1.1171e-06
2013-05-13 06:08AM | 1616782-1 | 8777 | Urban | Other | 1 | 711 | 711 | 0.00079427 | 1.1171e-06
2013-02-11 11:04PM | 1593704-1 | 8777 | Urban | Equipment Failure | 18 | 291 | 5238 | 0.0058515 | 2.0108e-05
2013-01-08 06:23PM | 1583349-1 | 8779 | Urban | Equipment Failure | 11 | 260 | 2860 | 0.003195 | 1.2288e-05
2012-11-20 01:42PM | 1571238-1 | 8779 | Urban | Equipment Failure | 106 | 175.6981 | 18624 | 0.020805 | 0.00011841
2013-06-16 05:25PM | 1625572-1 | 8779 | Urban | Equipment Failure | 1 | 97 | 97 | 0.00010836 | 1.1171e-06
2013-04-27 07:52AM | 1613316-1 | 8779 | Urban | Other | 16 | 54 | 864 | 0.00096519 | 1.7874e-05
2013-04-27 08:52AM | 1613324-1 | 8779 | Urban | Equipment Failure | 20 | 108 | 2160 | 0.002413 | 2.2342e-05
2013-03-25 08:18PM | 1606207-1 | 8779 | Urban | Equipment Failure | 21 | 60.0476 | 1261 | 0.0014087 | 2.346e-05
2013-01-18 04:02PM | 1586195-1 | 8780 | Urban | Equipment Failure | 688 | 119.7297 | 82374 | 0.092022 | 0.00076858
2012-12-23 12:25PM | 1579911-1 | 8780 | Urban | Third Party Impacts | 17 | 145 | 2465 | 0.0027537 | 1.8991e-05
2012-11-12 04:15AM | 1569104-1 | 8780 | Urban | Equipment Failure | 43 | 731.2326 | 31443 | 0.035126 | 4.8036e-05
2013-01-08 05:16PM | 1583322-1 | 8781 | Urban | Other | 1 | 39 | 39 | 4.3568e-05 | 1.1171e-06
2012-11-19 06:30PM | 1571022-1 | 52237 | Urban | Equipment Failure | 18 | 37 | 666 | 0.000744 | 2.0108e-05
2012-09-29 08:55AM | 1558035-1 | 52238 | Urban | Third Party Impacts | 25 | 463.76 | 11594 | 0.012952 | 2.7928e-05
2013-05-18 07:33PM | 1618551-1 | 52238 | Urban | Third Party Impacts | 41 | 63.7317 | 2613 | 0.002919 | 4.5802e-05
2013-02-14 06:35PM | 1594538-1 | 52238 | Urban | Third Party Impacts | 21 | 280 | 5880 | 0.0065687 | 2.346e-05
2012-07-30 04:32PM | 1541453-1 | 52238 | Urban | Third Party Impacts | 1 | 81 | 81 | 9.0487e-05 | 1.1171e-06
2013-03-03 12:17PM | 1600297-1 | 52238 | Urban | Weather | 12 | 23 | 276 | 0.00030833 | 1.3405e-05
2012-09-16 09:31AM | 1554874-1 | 27142 | Urban | Equipment Failure | 11 | 35.3636 | 389 | 0.00043456 | 1.2288e-05
2012-11-19 01:03PM | 1570872-1 | 27142 | Urban | Equipment Failure | 1 | 682 | 682 | 0.00076188 | 1.1171e-06
2013-06-29 02:53PM | 1629243-1 | L509 | Urban | Equipment Failure | 1 | 426 | 426 | 0.00047589 | 1.1171e-06
2013-01-11 03:42PM | 1584154-1 | L509 | Urban | Weather | 9 | 27.3333 | 246 | 0.00027481 | 1.0054e-05
2013-06-14 10:33AM | 1625197-1 | L513 | Urban | Other | 1 | 296 | 296 | 0.00033067 | 1.1171e-06
2013-01-11 03:02PM | 1584139-1 | L513 | Urban | Weather | 92 | 47.9457 | 4411 | 0.0049276 | 0.00010278
2013-05-31 01:17PM | 1622017-1 | L513 | Urban | Other | 1 | 355 | 355 | 0.00039658 | 1.1171e-06
2012-11-08 05:18PM | 1568418-1 | L513 | Urban | Equipment Failure | 1 | 617 | 617 | 0.00068926 | 1.1171e-06
2013-06-29 09:55PM | 1629298-1 | L516 | Urban | Equipment Failure | 26 | 335 | 8710 | 0.0097301 | 2.9045e-05
2013-06-29 11:32PM | 1629316-1 | L516 | Urban | Other | 18 | 235 | 4230 | 0.0047254 | 2.0108e-05
2012-07-14 02:00PM | 1537811-1 | L516 | Urban | Equipment Failure | 10 | 78.8 | 788 | 0.00088029 | 1.1171e-05
2012-09-26 01:41PM | 1557151-1 | 27334 | Urban | Other | 140 | 474.45 | 66423 | 0.074202 | 0.0001564
2012-11-21 04:13PM | 1571689-1 | 27334 | Urban | Other | 21 | 15 | 315 | 0.00035189 | 2.346e-05
2012-11-20 02:19PM | 1571252-1 | 27334 | Urban | Other | 19 | 27.4737 | 522 | 0.00058314 | 2.1225e-05
2012-11-08 05:02PM | 1568401-1 | 27334 | Urban | Weather | 1375 | 190.4662 | 261891 | 0.29256 | 0.001536
2012-10-13 02:23AM | 1561412-1 | 27334 | Urban | Equipment Failure | 1 | 518 | 518 | 0.00057867 | 1.1171e-06
2012-08-17 11:08AM | 1546547-1 | 27335 | Urban | Equipment Failure | 33 | 66.5455 | 2196 | 0.0024532 | 3.6865e-05
2013-01-28 10:29AM | 1589241-1 | 27335 | Urban | Weather | 12 | 134 | 1608 | 0.0017963 | 1.3405e-05
2012-11-05 02:58PM | 1567277-1 | 27335 | Urban | Third Party Impacts | 182 | 172 | 31304 | 0.03497 | 0.00020332
2012-11-08 05:36PM | 1568436-1 | 27335 | Urban | Vegetation | 335 | 125.9493 | 42193 | 0.047135 | 0.00037424
2012-09-04 11:39AM | 1551693-1 | 27340 | Urban | Other | 40 | 80.4 | 3216 | 0.0035927 | 4.4685e-05
2012-12-03 07:09AM | 1574855-1 | 27340 | Urban | Equipment Failure | 1 | 176 | 176 | 0.00019661 | 1.1171e-06
2013-05-02 12:44AM | 1614338-1 | 27340 | Urban | Equipment Failure | 21 | 856 | 17976 | 0.020081 | 2.346e-05
2012-08-14 04:30PM | 1545814-1 | 27340 | Urban | Equipment Failure | 1 | 274 | 274 | 0.00030609 | 1.1171e-06
2012-11-08 07:01PM | 1568522-1 | W182 | Urban | Weather | 4 | 1247.25 | 4989 | 0.0055733 | 4.4685e-06
2012-11-09 04:01AM | 1577098-1 | W182 | Urban | Equipment Failure | 1 | 699 | 699 | 0.00078087 | 1.1171e-06
2012-11-08 05:50PM | 1568450-1 | W182 | Urban | Weather | 1 | 158 | 158 | 0.0001765 | 1.1171e-06
2012-11-10 01:08PM | 1568998-1 | W185 | Rural Short | Other | 2 | 97 | 194 | 0.00021672 | 2.2342e-06
2013-04-07 10:38PM | 1608484-1 | W185 | Rural Short | Third Party Impacts | 2 | 31.5 | 63 | 7.0379e-05 | 2.2342e-06
2013-06-22 09:54AM | 1627109-1 | W185 | Rural Short | Equipment Failure | 1 | 147 | 147 | 0.00016422 | 1.1171e-06
2012-12-05 11:00AM | 1575671-1 | W185 | Rural Short | Weather | 261 | 67 | 17487 | 0.019535 | 0.00029157
2012-10-22 12:16PM | 1563540-1 | W185 | Rural Short | Vegetation | 156 | 61.5897 | 9608 | 0.010733 | 0.00017427
2012-11-08 05:00PM | 1568397-1 | W185 | Rural Short | Weather | 1809 | 163.2587 | 295335 | 0.32992 | 0.0020209
2012-11-19 08:06PM | 1571044-1 | W188 | Rural Short | Other | 1 | 136 | 136 | 0.00015193 | 1.1171e-06
2012-11-09 06:25AM | 1568635-1 | W188 | Rural Short | Weather | 16 | 166 | 2656 | 0.0029671 | 1.7874e-05
2012-10-20 09:18AM | 1563248-1 | W188 | Rural Short | Equipment Failure | 10 | 35.9 | 359 | 0.00040105 | 1.1171e-05
2013-01-26 01:59PM | 1588889-1 | W188 | Rural Short | Other | 11 | 53 | 583 | 0.00065128 | 1.2288e-05
2012-11-08 07:01PM | 1568520-1 | W188 | Rural Short | Vegetation | 9 | 158.8889 | 1430 | 0.0015975 | 1.0054e-05
2012-07-11 01:34AM | 1536934-1 | W188 | Rural Short | Vegetation | 339 | 58.3982 | 19797 | 0.022116 | 0.0003787
2012-11-08 08:10PM | 1568610-1 | W188 | Rural Short | Weather | 31 | 710.1935 | 22016 | 0.024595 | 3.4631e-05
2012-12-17 06:03AM | 1578375-1 | W188 | Rural Short | Equipment Failure | 42 | 91.6667 | 3850 | 0.0043009 | 4.6919e-05
2013-01-22 05:49PM | 1587420-1 | W188 | Rural Short | Operatonal Error | 629 | 2 | 1258 | 0.0014053 | 0.00070267
2012-07-09 03:24PM | 1536680-1 | W190 | Urban | Third Party Impacts | 16 | 23.8125 | 381 | 0.00042562 | 1.7874e-05
2012-09-24 11:07AM | 1556668-1 | W196 | Urban | Vegetation | 62 | 45 | 2790 | 0.0031168 | 6.9261e-05
2012-07-06 10:54AM | 1536072-1 | W196 | Urban | Equipment Failure | 12 | 305.8333 | 3670 | 0.0040998 | 1.3405e-05
2012-11-10 01:39PM | 1569003-1 | W196 | Urban | Weather | 23 | 78 | 1794 | 0.0020041 | 2.5694e-05
2013-05-17 08:40AM | 1618132-1 | W196 | Urban | Equipment Failure | 1 | 275 | 275 | 0.00030721 | 1.1171e-06
2012-09-08 08:00AM | 1553060-1 | W196 | Urban | Other | 4 | 160 | 640 | 0.00071496 | 4.4685e-06
2012-10-09 06:47PM | 1560158-1 | BWA2 | Rural Short | Equipment Failure | 11 | 68.4545 | 753 | 0.00084119 | 1.2288e-05
2012-09-14 10:00AM | 1554533-1 | BWA2 | Rural Short | Other | 41 | 32 | 1312 | 0.0014657 | 4.5802e-05
2012-09-14 10:34AM | 1554542-1 | BWA2 | Rural Short | Other | 132 | 7 | 924 | 0.0010322 | 0.00014746
2012-09-07 03:45PM | 1552907-1 | BWA2 | Rural Short | Weather | 10 | 509 | 5090 | 0.0056861 | 1.1171e-05
2013-06-17 08:58AM | 1625630-1 | BWA2 | Rural Short | Other | 1 | 86 | 86 | 9.6072e-05 | 1.1171e-06
2013-06-17 06:54PM | 1625889-1 | BWA2 | Rural Short | Other | 11 | 74.7273 | 822 | 0.00091827 | 1.2288e-05
2013-01-03 10:14AM | 1581978-1 | BWB2 | Urban | Other | 5 | 93 | 465 | 0.00051946 | 5.5856e-06
2012-07-29 08:48PM | 1541166-1 | BWB2 | Urban | Equipment Failure | 1348 | 97.3553 | 131235 | 0.14661 | 0.0015059
2013-01-09 10:32PM | 1583715-1 | BWB2 | Urban | Other | 1344 | 98.2098 | 131994 | 0.14745 | 0.0015014
2013-01-23 04:38AM | 1587553-1 | BWB2 | Urban | Weather | 1344 | 96.7872 | 130082 | 0.14532 | 0.0015014
2013-01-27 04:56AM | 1588981-1 | BWC2 | Urban | Weather | 6 | 429.5 | 2577 | 0.0028788 | 6.7027e-06
2013-01-22 09:40PM | 1587548-1 | BWC2 | Urban | Weather | 6 | 121 | 726 | 0.00081103 | 6.7027e-06
2013-05-13 02:54PM | 1616950-1 | BWC2 | Urban | Vegetation | 16 | 481.9375 | 7711 | 0.0086141 | 1.7874e-05
2013-01-22 06:28PM | 1587479-1 | BWC2 | Urban | Weather | 47 | 140 | 6580 | 0.0073506 | 5.2505e-05
2013-03-27 05:51AM | 1606507-1 | BWC2 | Urban | Animals | 9 | 220 | 1980 | 0.0022119 | 1.0054e-05
2013-04-20 09:52AM | 1611709-1 | BWC2 | Urban | Weather | 432 | 172.9236 | 74703 | 0.083452 | 0.0004826
2012-08-06 09:11AM | 1543077-1 | BWD2 | Urban | Other | 40 | 141.225 | 5649 | 0.0063106 | 4.4685e-05
2012-08-15 09:34AM | 1545934-1 | BWD2 | Urban | Equipment Failure | 58 | 107.3621 | 6227 | 0.0069563 | 6.4793e-05
2013-01-18 03:14PM | 1586172-1 | BWD2 | Urban | Weather | 30 | 87.6 | 2628 | 0.0029358 | 3.3514e-05
2013-06-25 11:08AM | 1627823-1 | BWE2 | Rural Short | Weather | 1 | 99 | 99 | 0.00011059 | 1.1171e-06
2012-10-20 09:47AM | 1563259-1 | BWE2 | Rural Short | Other | 3 | 65.6667 | 197 | 0.00022007 | 3.3514e-06
2012-11-26 08:17PM | 1572946-1 | BWE2 | Rural Short | Weather | 1 | 114 | 114 | 0.00012735 | 1.1171e-06
2013-01-04 07:56AM | 1582236-1 | BWE2 | Rural Short | Other | 2 | 142.5 | 285 | 0.00031838 | 2.2342e-06
2012-11-26 03:26PM | 1572773-1 | BWE2 | Rural Short | Weather | 7 | 143.1429 | 1002 | 0.0011194 | 7.8198e-06
2013-01-05 06:20AM | 1582526-1 | BWE2 | Rural Short | Equipment Failure | 23 | 538 | 12374 | 0.013823 | 2.5694e-05
2012-07-01 06:46AM | 1534561-1 | BWE2 | Rural Short | Other | 11 | 155.9091 | 1715 | 0.0019159 | 1.2288e-05
2013-06-25 09:10AM | 1627740-1 | BWE2 | Rural Short | Weather | 2 | 97 | 194 | 0.00021672 | 2.2342e-06
2013-06-24 10:22PM | 1627631-1 | BWE2 | Rural Short | Weather | 155 | 81.7613 | 12673 | 0.014157 | 0.00017315
2013-04-24 06:23PM | 1612900-1 | BWF2 | Rural Short | Equipment Failure | 4 | 810 | 3240 | 0.0036195 | 4.4685e-06
2012-11-05 07:24AM | 1567040-1 | BWF2 | Rural Short | Equipment Failure | 23 | 30 | 690 | 0.00077081 | 2.5694e-05
2012-11-06 05:30PM | 1567545-1 | X877 | Rural Short | Third Party Impacts | 1 | 61 | 61 | 6.8144e-05 | 1.1171e-06
2013-02-11 04:02PM | 1593637-1 | X877 | Rural Short | Other | 1 | 68 | 68 | 7.5964e-05 | 1.1171e-06
2013-03-09 06:08PM | 1602271-1 | X879 | Rural Short | Equipment Failure | 13 | 132 | 1716 | 0.001917 | 1.4523e-05
2013-05-12 02:46PM | 1616735-1 | X879 | Rural Short | Equipment Failure | 19 | 77 | 1463 | 0.0016343 | 2.1225e-05
2013-05-13 07:49PM | 1617030-1 | X879 | Rural Short | Equipment Failure | 1 | 275 | 275 | 0.00030721 | 1.1171e-06
2012-07-22 07:20PM | 1539590-1 | X879 | Rural Short | Equipment Failure | 10 | 81.6 | 816 | 0.00091157 | 1.1171e-05
2012-07-07 10:55AM | 1536283-1 | X879 | Rural Short | Third Party Impacts | 3 | 318 | 954 | 0.0010657 | 3.3514e-06
2012-07-01 12:22PM | 1534639-1 | X879 | Rural Short | Equipment Failure | 10 | 104.7 | 1047 | 0.0011696 | 1.1171e-05
2013-02-21 08:45AM | 1595972-1 | X879 | Rural Short | Third Party Impacts | 18 | 20.2222 | 364 | 0.00040663 | 2.0108e-05
2012-11-12 10:57AM | 1569161-1 | X879 | Rural Short | Vegetation | 1022 | 68.9765 | 70494 | 0.07875 | 0.0011417
2012-11-12 03:39PM | 1569282-1 | X879 | Rural Short | Operatonal Error | 11 | 96 | 1056 | 0.0011797 | 1.2288e-05
2013-01-27 04:42AM | 1588976-1 | X879 | Rural Short | Weather | 962 | 124.9407 | 120193 | 0.13427 | 0.0010747
2013-02-01 03:52PM | 1590812-1 | X879 | Rural Short | Vegetation | 1023 | 40 | 40920 | 0.045713 | 0.0011428
2012-11-06 06:23AM | 1567398-1 | X879 | Rural Short | Equipment Failure | 1 | 343 | 343 | 0.00038317 | 1.1171e-06
2013-02-03 05:49PM | 1591181-1 | X881 | Rural Short | Equipment Failure | 1 | 93 | 93 | 0.00010389 | 1.1171e-06
2013-01-19 08:56AM | 1586572-1 | X881 | Rural Short | Equipment Failure | 1 | 96 | 96 | 0.00010724 | 1.1171e-06
2013-06-11 12:10PM | 1624307-1 | X881 | Rural Short | Equipment Failure | 1 | 25 | 25 | 2.7928e-05 | 1.1171e-06
2012-11-28 12:50PM | 1573544-1 | X881 | Rural Short | Third Party Impacts | 1 | 806 | 806 | 0.0009004 | 1.1171e-06
2012-11-29 11:52AM | 1573826-1 | X881 | Rural Short | Equipment Failure | 473 | 37.6533 | 17810 | 0.019896 | 0.0005284
2013-05-26 08:30AM | 1621388-1 | X881 | Rural Short | Equipment Failure | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2013-02-25 09:26AM | 1597913-1 | X881 | Rural Short | Other | 1 | 546 | 546 | 0.00060995 | 1.1171e-06
2012-12-13 01:08PM | 1577663-1 | X883 | Rural Short | Equipment Failure | 17 | 158.4706 | 2694 | 0.0030095 | 1.8991e-05
2013-06-26 08:28PM | 1628502-1 | BLA2 | Rural Short | Other | 8 | 16.125 | 129 | 0.00014411 | 8.937e-06
2012-08-10 04:16PM | 1544864-1 | BLA2 | Rural Short | Weather | 35 | 25 | 875 | 0.00097748 | 3.9099e-05
2012-10-16 07:34AM | 1562027-1 | BLA2 | Rural Short | Third Party Impacts | 4 | 95 | 380 | 0.00042451 | 4.4685e-06
2012-07-15 06:46PM | 1537915-1 | BLA2 | Rural Short | Equipment Failure | 13 | 81.7692 | 1063 | 0.0011875 | 1.4523e-05
2013-06-24 09:34PM | 1627613-1 | BLA2 | Rural Short | Vegetation | 1484 | 63.1327 | 93689 | 0.10466 | 0.0016578
2013-03-15 03:56PM | 1603814-1 | BLA2 | Rural Short | Other | 1 | 111 | 111 | 0.000124 | 1.1171e-06
2013-01-06 07:00PM | 1582746-1 | BLB2 | Urban | Equipment Failure | 44 | 876.1136 | 38549 | 0.043064 | 4.9153e-05
2013-02-14 02:53PM | 1594477-1 | BLB2 | Urban | Equipment Failure | 1314 | 57.7139 | 75836 | 0.084718 | 0.0014679
2013-03-12 02:55PM | 1602914-1 | BLC2 | Urban | Equipment Failure | 1 | 220 | 220 | 0.00024577 | 1.1171e-06
2012-07-02 06:04PM | 1534971-1 | BLD2 | Urban | Equipment Failure | 34 | 167.7647 | 5704 | 0.0063721 | 3.7982e-05
2012-11-20 04:14PM | 1571306-1 | BLD2 | Urban | Equipment Failure | 19 | 137.7895 | 2618 | 0.0029246 | 2.1225e-05
2012-12-25 03:20PM | 1580535-1 | BLD2 | Urban | Weather | 30 | 69 | 2070 | 0.0023124 | 3.3514e-05
2012-12-28 01:04PM | 1581163-1 | BLD2 | Urban | Vegetation | 65 | 88.0308 | 5722 | 0.0063922 | 7.2613e-05
2013-02-10 01:06PM | 1593212-1 | BLD2 | Urban | Vegetation | 1392 | 36.1832 | 50367 | 0.056266 | 0.001555
2013-02-11 10:43PM | 1593702-1 | BLE2 | Urban | Equipment Failure | 5 | 522 | 2610 | 0.0029157 | 5.5856e-06
2013-01-09 12:50AM | 1583462-1 | BLE2 | Urban | Third Party Impacts | 664 | 72.9352 | 48429 | 0.054101 | 0.00074177
2013-03-17 06:08PM | 1604185-1 | BLE2 | Urban | Vegetation | 665 | 40 | 26600 | 0.029715 | 0.00074288
2012-10-19 11:08AM | 1563046-1 | R290 | Rural Short | Equipment Failure | 40 | 32.825 | 1313 | 0.0014668 | 4.4685e-05
2012-12-17 10:55AM | 1579690-1 | R290 | Rural Short | Operatonal Error | 40 | 2 | 80 | 8.937e-05 | 4.4685e-05
2013-02-10 07:36PM | 1593343-1 | R290 | Rural Short | Weather | 44 | 8.2045 | 361 | 0.00040328 | 4.9153e-05
2013-02-06 10:32AM | 1592063-1 | R290 | Rural Short | Weather | 1 | 281 | 281 | 0.00031391 | 1.1171e-06
2012-09-06 06:44PM | 1552500-1 | R290 | Rural Short | Weather | 1 | 165 | 165 | 0.00018432 | 1.1171e-06
2012-09-07 11:08AM | 1552693-1 | R290 | Rural Short | Equipment Failure | 1 | 152 | 152 | 0.0001698 | 1.1171e-06
2013-02-10 04:38PM | 1593263-1 | R290 | Rural Short | Weather | 2 | 170 | 340 | 0.00037982 | 2.2342e-06
2012-10-19 11:08AM | 1563046-1 | R293 | Rural Short | Equipment Failure | 86 | 32.8256 | 2823 | 0.0031536 | 9.6072e-05
2012-12-17 10:55AM | 1579690-1 | R293 | Rural Short | Operatonal Error | 91 | 2.011 | 183 | 0.00020443 | 0.00010166
2013-02-10 07:36PM | 1593343-1 | R293 | Rural Short | Weather | 99 | 8.2929 | 821 | 0.00091716 | 0.00011059
2012-10-14 05:27AM | 1565615-1 | R293 | Rural Short | Other | 5 | 419.6 | 2098 | 0.0023437 | 5.5856e-06
2012-12-25 04:37PM | 1580554-1 | R293 | Rural Short | Weather | 18 | 1230 | 22140 | 0.024733 | 2.0108e-05
2013-02-07 06:00PM | 1592593-1 | R293 | Rural Short | Equipment Failure | 18 | 199.6111 | 3593 | 0.0040138 | 2.0108e-05
2013-05-11 01:48PM | 1616607-1 | R293 | Rural Short | Equipment Failure | 18 | 11.7778 | 212 | 0.00023683 | 2.0108e-05
2012-07-20 12:30PM | 1539268-1 | R293 | Rural Short | Equipment Failure | 3 | 149 | 447 | 0.00049935 | 3.3514e-06
2012-12-26 02:13PM | 1580683-1 | R293 | Rural Short | Weather | 1 | 102 | 102 | 0.00011395 | 1.1171e-06
2013-02-11 08:34AM | 1593430-1 | R293 | Rural Short | Weather | 2 | 261 | 522 | 0.00058314 | 2.2342e-06
2013-05-15 10:04AM | 1617429-1 | R293 | Rural Short | Equipment Failure | 1 | 12 | 12 | 1.3405e-05 | 1.1171e-06
2013-06-16 03:07PM | 1625560-1 | R293 | Rural Short | Equipment Failure | 2 | 120 | 240 | 0.00026811 | 2.2342e-06
2013-02-13 08:18PM | 1594252-1 | R293 | Rural Short | Third Party Impacts | 2 | 1195 | 2390 | 0.0026699 | 2.2342e-06
2013-01-08 01:20PM | 1583213-1 | BWH2 | Rural Short | Weather | 7 | 147 | 1029 | 0.0011495 | 7.8198e-06
2013-06-07 11:49AM | 1623671-1 | BWH2 | Rural Short | Equipment Failure | 7 | 188 | 1316 | 0.0014701 | 7.8198e-06
2012-10-08 06:33PM | 1559853-1 | BWH2 | Rural Short | Equipment Failure | 36 | 245 | 8820 | 0.009853 | 4.0216e-05
2013-02-01 02:00PM | 1590683-1 | BWH2 | Rural Short | Weather | 28 | 355.5357 | 9955 | 0.011121 | 3.1279e-05
2012-11-14 09:04AM | 1572129-1 | BWH2 | Rural Short | Other | 14 | 68 | 952 | 0.0010635 | 1.564e-05
2013-01-16 06:00AM | 1585276-1 | BWH2 | Rural Short | Equipment Failure | 211 | 222.8578 | 47023 | 0.05253 | 0.00023571
2012-08-08 02:49PM | 1543852-1 | BWH2 | Rural Short | Equipment Failure | 284 | 105.6232 | 29997 | 0.03351 | 0.00031726
2013-02-25 03:41AM | 1597783-1 | BWH2 | Rural Short | Weather | 289 | 346.0865 | 100019 | 0.11173 | 0.00032285
2013-02-08 12:59AM | 1592644-1 | BWH2 | Rural Short | Other | 288 | 1.3819 | 398 | 0.00044461 | 0.00032173
2012-07-30 04:30PM | 1541458-1 | BWH2 | Rural Short | Equipment Failure | 116 | 72.7586 | 8440 | 0.0094285 | 0.00012959
2012-08-09 02:51PM | 1544167-1 | BWH2 | Rural Short | Vegetation | 1079 | 79 | 85241 | 0.095224 | 0.0012054
2012-08-18 04:13PM | 1547208-1 | BWH2 | Rural Short | Weather | 1079 | 118.6784 | 128054 | 0.14305 | 0.0012054
2012-09-06 10:20AM | 1552336-1 | BWH2 | Rural Short | Other | 1081 | 85.0999 | 91993 | 0.10277 | 0.0012076
2013-01-03 06:54AM | 1581937-1 | BWH2 | Rural Short | Animals | 1085 | 62.7161 | 68047 | 0.076017 | 0.0012121
2012-09-07 01:00PM | 1552750-1 | BWH2 | Rural Short | Equipment Failure | 1 | 149 | 149 | 0.00016645 | 1.1171e-06
2012-09-07 05:57PM | 1552965-1 | A346 | Urban | Equipment Failure | 1 | 1123 | 1123 | 0.0012545 | 1.1171e-06
2013-05-09 12:22PM | 1616058-1 | A347 | Urban | Vegetation | 32 | 361.2812 | 11561 | 0.012915 | 3.5748e-05
2012-07-31 02:29PM | 1541702-1 | A347 | Urban | Other | 17 | 112.1765 | 1907 | 0.0021303 | 1.8991e-05
2012-10-14 01:54PM | 1561586-1 | A347 | Urban | Other | 35 | 30 | 1050 | 0.001173 | 3.9099e-05
2013-02-26 05:35PM | 1598738-1 | C889 | Urban | Equipment Failure | 7 | 504.4286 | 3531 | 0.0039446 | 7.8198e-06
2013-01-18 07:48PM | 1586390-1 | C889 | Urban | Weather | 28 | 253 | 7084 | 0.0079137 | 3.1279e-05
2013-02-04 01:13PM | 1591358-1 | C889 | Urban | Equipment Failure | 18 | 274.6667 | 4944 | 0.005523 | 2.0108e-05
2013-01-04 05:25PM | 1582405-1 | C889 | Urban | Equipment Failure | 29 | 312.6897 | 9068 | 0.01013 | 3.2396e-05
2012-07-11 03:34AM | 1536940-1 | C889 | Urban | Equipment Failure | 17 | 222.9412 | 3790 | 0.0042339 | 1.8991e-05
2012-07-11 07:51AM | 1536960-1 | C889 | Urban | Equipment Failure | 17 | 306.1765 | 5205 | 0.0058146 | 1.8991e-05
2013-01-08 12:43PM | 1583185-1 | C889 | Urban | Equipment Failure | 1 | 136 | 136 | 0.00015193 | 1.1171e-06
2013-05-28 04:53PM | 1621148-1 | C890 | Urban | Other | 16 | 86 | 1376 | 0.0015372 | 1.7874e-05
2012-09-03 10:14AM | 1551359-1 | C890 | Urban | Equipment Failure | 14 | 329 | 4606 | 0.0051455 | 1.564e-05
2013-05-14 09:34AM | 1617112-1 | C890 | Urban | Equipment Failure | 14 | 25 | 350 | 0.00039099 | 1.564e-05
2013-05-03 12:03PM | 1614680-1 | C891 | Urban | Equipment Failure | 28 | 50.25 | 1407 | 0.0015718 | 3.1279e-05
2012-11-08 04:16PM | 1568360-1 | C891 | Urban | Weather | 820 | 219.1415 | 179696 | 0.20074 | 0.00091604
2013-04-19 04:23PM | 1611620-1 | C891 | Urban | Other | 1 | 216 | 216 | 0.0002413 | 1.1171e-06
2013-01-31 05:18PM | 1590411-1 | C893 | Urban | Other | 76 | 104 | 7904 | 0.0088297 | 8.4901e-05
2013-02-25 05:52PM | 1598296-1 | C893 | Urban | Weather | 48 | 69 | 3312 | 0.0036999 | 5.3622e-05
2012-09-19 11:41AM | 1555691-1 | C893 | Urban | Third Party Impacts | 20 | 58 | 1160 | 0.0012959 | 2.2342e-05
2013-01-29 01:10AM | 1589454-1 | C893 | Urban | Equipment Failure | 1080 | 64.8833 | 70074 | 0.078281 | 0.0012065
2013-02-06 08:08PM | 1592261-1 | C893 | Urban | Vegetation | 41 | 18 | 738 | 0.00082443 | 4.5802e-05
2012-10-27 12:48AM | 1565115-1 | A348 | Urban | Third Party Impacts | 8 | 101 | 808 | 0.00090263 | 8.937e-06
2012-10-27 10:39AM | 1565145-1 | A348 | Urban | Third Party Impacts | 8 | 300.25 | 2402 | 0.0026833 | 8.937e-06
2012-09-14 11:35AM | 1554561-1 | A348 | Urban | Other | 49 | 39 | 1911 | 0.0021348 | 5.4739e-05
2012-12-28 11:43AM | 1581140-1 | A348 | Urban | Third Party Impacts | 909 | 50.0979 | 45539 | 0.050873 | 0.0010155
2013-01-18 06:56AM | 1585847-1 | A348 | Urban | Third Party Impacts | 908 | 78.0705 | 70888 | 0.07919 | 0.0010143
2013-03-07 07:32PM | 1601855-1 | A350 | Urban | Equipment Failure | 14 | 469 | 6566 | 0.007335 | 1.564e-05
2013-03-15 08:21AM | 1603641-1 | A354 | Urban | Third Party Impacts | 25 | 265.88 | 6647 | 0.0074255 | 2.7928e-05
2012-07-21 07:12AM | 1539444-1 | C889 | Urban | Other | 7 | 69.8571 | 489 | 0.00054627 | 7.8198e-06
2013-02-13 06:11PM | 1594221-1 | C889 | Urban | Other | 7 | 51 | 357 | 0.00039881 | 7.8198e-06
2012-07-02 08:50AM | 1534725-1 | C896 | Urban | Equipment Failure | 1 | 155 | 155 | 0.00017315 | 1.1171e-06
2013-06-04 06:53PM | 1623003-1 | C896 | Urban | Equipment Failure | 1 | 94 | 94 | 0.00010501 | 1.1171e-06
2013-06-25 02:51PM | 1627949-1 | C896 | Urban | Equipment Failure | 1 | 162 | 162 | 0.00018097 | 1.1171e-06
2013-03-13 10:16AM | 1603103-1 | C896 | Urban | Equipment Failure | 20 | 326.25 | 6525 | 0.0072892 | 2.2342e-05
2012-09-07 09:28AM | 1552656-1 | C896 | Urban | Equipment Failure | 1 | 219 | 219 | 0.00024465 | 1.1171e-06
2013-01-08 01:12PM | 1583211-1 | C896 | Urban | Equipment Failure | 1 | 165 | 165 | 0.00018432 | 1.1171e-06
2013-03-07 11:11AM | 1601683-1 | C896 | Urban | Other | 1 | 330 | 330 | 0.00036865 | 1.1171e-06
2012-09-13 10:35AM | 1554263-1 | C897 | Urban | Equipment Failure | 1 | 119 | 119 | 0.00013294 | 1.1171e-06
2013-02-08 07:58PM | 1592953-1 | C899 | Urban | Other | 18 | 182.9444 | 3293 | 0.0036787 | 2.0108e-05
2013-01-27 11:52AM | 1589116-1 | C899 | Urban | Other | 5 | 92 | 460 | 0.00051388 | 5.5856e-06
2013-01-27 02:17AM | 1588953-1 | C899 | Urban | Equipment Failure | 69 | 428 | 29532 | 0.032991 | 7.7081e-05
2013-06-29 11:00PM | 1629307-1 | C899 | Urban | Equipment Failure | 1 | 682 | 682 | 0.00076188 | 1.1171e-06
2012-12-16 03:57PM | 1578321-1 | C899 | Urban | Equipment Failure | 31 | 92.871 | 2879 | 0.0032162 | 3.4631e-05
2012-09-24 11:34AM | 1556672-1 | C900 | Urban | Vegetation | 128 | 103.8594 | 13294 | 0.014851 | 0.00014299
2012-07-14 11:12AM | 1537794-1 | C900 | Urban | Equipment Failure | 53 | 220.8868 | 11707 | 0.013078 | 5.9207e-05
2012-07-18 11:00PM | 1538706-1 | C900 | Urban | Equipment Failure | 76 | 194.7895 | 14804 | 0.016538 | 8.4901e-05
2012-07-19 03:28PM | 1539012-1 | C900 | Urban | Equipment Failure | 1 | 297 | 297 | 0.00033178 | 1.1171e-06
2013-05-06 03:36PM | 1615241-1 | C900 | Urban | Third Party Impacts | 123 | 152 | 18696 | 0.020886 | 0.00013741
2012-11-25 06:24AM | 1572493-1 | C900 | Urban | Weather | 26 | 84 | 2184 | 0.0024398 | 2.9045e-05
2012-11-26 08:42PM | 1572951-1 | C900 | Urban | Equipment Failure | 42 | 182.1667 | 7651 | 0.0085471 | 4.6919e-05
2013-04-30 02:43PM | 1613938-1 | C900 | Urban | Equipment Failure | 1 | 42 | 42 | 4.6919e-05 | 1.1171e-06
2012-10-24 11:10AM | 1564218-1 | C900 | Urban | Other | 266 | 179.8872 | 47850 | 0.053454 | 0.00029715
2013-06-23 04:23PM | 1627280-1 | M389 | Urban | Equipment Failure | 86 | 369.4419 | 31772 | 0.035493 | 9.6072e-05
2013-03-26 05:16PM | 1606456-1 | M389 | Urban | Other | 1 | 30 | 30 | 3.3514e-05 | 1.1171e-06
2012-08-17 01:41PM | 1546759-1 | M389 | Urban | Weather | 1087 | 80.1426 | 87115 | 0.097318 | 0.0012143
2012-09-27 12:02PM | 1557521-1 | M391 | Rural Short | Equipment Failure | 4 | 56.75 | 227 | 0.00025359 | 4.4685e-06
2012-09-05 02:27PM | 1556153-1 | M393 | Urban | Third Party Impacts | 1143 | 17.0857 | 19529 | 0.021816 | 0.0012769
2012-07-08 05:23PM | 1536462-1 | M393 | Urban | Third Party Impacts | 3 | 76.6667 | 230 | 0.00025694 | 3.3514e-06
2012-08-20 12:31PM | 1547448-1 | M394 | Urban | Equipment Failure | 17 | 78.2353 | 1330 | 0.0014858 | 1.8991e-05
2013-02-25 05:20PM | 1598278-1 | M394 | Urban | Equipment Failure | 14 | 231 | 3234 | 0.0036128 | 1.564e-05
2012-09-24 02:16PM | 1556715-1 | M394 | Urban | Equipment Failure | 1 | 48 | 48 | 5.3622e-05 | 1.1171e-06
2013-01-28 02:05PM | 1589273-1 | M394 | Urban | Equipment Failure | 1171 | 61.9334 | 72524 | 0.081018 | 0.0013081
2013-02-13 08:11PM | 1594249-1 | M396 | Urban | Equipment Failure | 30 | 215.4667 | 6464 | 0.0072211 | 3.3514e-05
2012-09-05 02:27PM | 1556153-1 | M396 | Urban | Third Party Impacts | 273 | 17.1026 | 4669 | 0.0052158 | 0.00030497
2013-01-29 05:07AM | 1589467-1 | M396 | Urban | Equipment Failure | 274 | 120.8978 | 33126 | 0.037006 | 0.00030609
2013-01-02 11:34AM | 1581770-1 | M397 | Urban | Equipment Failure | 34 | 368.1471 | 12517 | 0.013983 | 3.7982e-05
2012-09-05 02:27PM | 1556153-1 | M397 | Urban | Third Party Impacts | 622 | 17.0691 | 10617 | 0.01186 | 0.00069485
2012-11-11 06:18PM | 1569091-1 | M397 | Urban | Other | 1 | 124 | 124 | 0.00013852 | 1.1171e-06
2012-09-05 02:27PM | 1556153-1 | R212 | Urban | Third Party Impacts | 272 | 17.1029 | 4652 | 0.0051968 | 0.00030386
2012-08-10 01:02PM | 1544535-1 | R212 | Urban | Weather | 543 | 303.453 | 164775 | 0.18407 | 0.0006066
2012-07-21 05:04PM | 1539489-1 | R214 | Urban | Other | 1 | 206 | 206 | 0.00023013 | 1.1171e-06
2012-09-21 07:34PM | 1556319-1 | R214 | Urban | Equipment Failure | 1 | 127 | 127 | 0.00014187 | 1.1171e-06
2012-07-12 08:55AM | 1537269-1 | R214 | Urban | Equipment Failure | 10 | 233.5 | 2335 | 0.0026085 | 1.1171e-05
2012-07-12 12:17PM | 1537357-1 | R214 | Urban | Other | 23 | 161.4348 | 3713 | 0.0041479 | 2.5694e-05
2012-09-05 02:27PM | 1556153-1 | R214 | Urban | Third Party Impacts | 1865 | 17.0777 | 31850 | 0.03558 | 0.0020834
2012-12-23 02:10PM | 1579917-1 | R214 | Urban | Equipment Failure | 1 | 46 | 46 | 5.1388e-05 | 1.1171e-06
2012-09-23 10:05AM | 1556538-1 | R215 | Urban | Equipment Failure | 82 | 137.8415 | 11303 | 0.012627 | 9.1604e-05
2013-05-01 08:15AM | 1614077-1 | R215 | Urban | Third Party Impacts | 80 | 27 | 2160 | 0.002413 | 8.937e-05
2013-01-19 05:00AM | 1586540-1 | R215 | Urban | Weather | 56 | 444 | 24864 | 0.027776 | 6.2559e-05
2013-02-10 02:48PM | 1593238-1 | R215 | Urban | Weather | 1 | 268 | 268 | 0.00029939 | 1.1171e-06
2012-08-03 04:05AM | 1542498-1 | R215 | Urban | Equipment Failure | 38 | 155.6316 | 5914 | 0.0066066 | 4.2451e-05
2012-07-18 07:56PM | 1538690-1 | R215 | Urban | Other | 3 | 64.6667 | 194 | 0.00021672 | 3.3514e-06
2012-09-05 02:27PM | 1556153-1 | R215 | Urban | Third Party Impacts | 641 | 17.0671 | 10940 | 0.012221 | 0.00071607
2013-01-19 11:26AM | 1586597-1 | R215 | Urban | Equipment Failure | 648 | 41.4614 | 26867 | 0.030014 | 0.00072389
2013-01-29 05:07AM | 1589468-1 | R215 | Urban | Equipment Failure | 641 | 114.8331 | 73608 | 0.082229 | 0.00071607
2013-01-29 04:21PM | 1589777-1 | R215 | Urban | Equipment Failure | 550 | 36 | 19800 | 0.022119 | 0.00061442
2013-01-11 11:20AM | 1584067-1 | CT1202 | Urban | Weather | 12 | 114.1667 | 1370 | 0.0015305 | 1.3405e-05
2013-01-18 11:35AM | 1585944-1 | CT1202 | Urban | Equipment Failure | 11 | 42 | 462 | 0.00051611 | 1.2288e-05
2013-01-19 09:38AM | 1586579-1 | CT1202 | Urban | Equipment Failure | 12 | 176 | 2112 | 0.0023594 | 1.3405e-05
2012-11-18 12:07PM | 1570555-1 | CT1202 | Urban | Equipment Failure | 11 | 96 | 1056 | 0.0011797 | 1.2288e-05
2013-01-13 11:29AM | 1584357-1 | CT1202 | Urban | Equipment Failure | 3 | 180.3333 | 541 | 0.00060436 | 3.3514e-06
2013-03-20 10:22PM | 1605032-1 | CT1203 | Urban | Third Party Impacts | 63 | 143 | 9009 | 0.010064 | 7.0379e-05
2012-09-08 12:48PM | 1553163-1 | CT1203 | Urban | Third Party Impacts | 3 | 157 | 471 | 0.00052616 | 3.3514e-06
2012-11-02 09:37AM | 1566551-1 | CT1203 | Urban | Equipment Failure | 1 | 194 | 194 | 0.00021672 | 1.1171e-06
2013-04-07 07:29AM | 1608413-1 | CT1206 | Urban | Other | 20 | 176.65 | 3533 | 0.0039468 | 2.2342e-05
2013-01-21 04:24PM | 1587009-1 | CT1206 | Urban | Equipment Failure | 83 | 86 | 7138 | 0.007974 | 9.2721e-05
2013-03-18 04:35PM | 1604415-1 | CT1206 | Urban | Other | 20 | 107 | 2140 | 0.0023906 | 2.2342e-05
2012-09-21 01:45PM | 1556236-1 | CT1206 | Urban | Other | 174 | 131.4483 | 22872 | 0.025551 | 0.00019438
2013-02-02 07:26PM | 1591109-1 | CT1206 | Urban | Third Party Impacts | 1 | 306 | 306 | 0.00034184 | 1.1171e-06
2013-01-18 05:08PM | 1586245-1 | CT1206 | Urban | Equipment Failure | 1566 | 78 | 122148 | 0.13645 | 0.0017494
2012-12-20 01:34PM | 1579422-1 | CT1225 | Urban | Equipment Failure | 26 | 89 | 2314 | 0.002585 | 2.9045e-05
2012-07-10 04:07PM | 1536895-1 | CT1225 | Urban | Equipment Failure | 32 | 78.25 | 2504 | 0.0027973 | 3.5748e-05
2013-06-26 11:19AM | 1628269-1 | CT1225 | Urban | Equipment Failure | 1 | 152 | 152 | 0.0001698 | 1.1171e-06
2013-01-31 04:40PM | 1590393-1 | CT1225 | Urban | Third Party Impacts | 2 | 1406 | 2812 | 0.0031413 | 2.2342e-06
2013-06-24 12:56AM | 1627374-1 | CT1225 | Urban | Other | 8 | 492.5 | 3940 | 0.0044015 | 8.937e-06
2012-09-04 10:37AM | 1551662-1 | CT1225 | Urban | Third Party Impacts | 5 | 385.4 | 1927 | 0.0021527 | 5.5856e-06
2012-08-03 01:51PM | 1542679-1 | CT1225 | Urban | Operatonal Error | 11 | 121.8182 | 1340 | 0.0014969 | 1.2288e-05
2012-08-17 01:22PM | 1546743-1 | CT1225 | Urban | Equipment Failure | 1743 | 179.2306 | 312399 | 0.34899 | 0.0019471
2012-09-11 11:00AM | 1553638-1 | CT1225 | Urban | Operatonal Error | 75 | 103.1733 | 7738 | 0.0086443 | 8.3784e-05
2013-02-16 03:08PM | 1594881-1 | CT1225 | Urban | Equipment Failure | 1 | 163 | 163 | 0.00018209 | 1.1171e-06
2012-12-22 03:13PM | 1579807-1 | CT1233 | Urban | Equipment Failure | 13 | 55 | 715 | 0.00079874 | 1.4523e-05
2012-12-22 04:52PM | 1579818-1 | CT1233 | Urban | Equipment Failure | 18 | 121.3333 | 2184 | 0.0024398 | 2.0108e-05
2013-03-11 02:36PM | 1602644-1 | CT1233 | Urban | Equipment Failure | 1 | 58 | 58 | 6.4793e-05 | 1.1171e-06
2012-11-28 01:22PM | 1573549-1 | CT1233 | Urban | Equipment Failure | 2 | 256.5 | 513 | 0.00057308 | 2.2342e-06
2013-06-06 08:22AM | 1623349-1 | CT1233 | Urban | Equipment Failure | 2 | 512 | 1024 | 0.0011439 | 2.2342e-06
2013-06-04 04:21PM | 1622967-1 | CT1262 | Rural Short | Third Party Impacts | 4 | 32 | 128 | 0.00014299 | 4.4685e-06
2012-09-17 08:47PM | 1555234-1 | CT1262 | Rural Short | Weather | 23 | 80 | 1840 | 0.0020555 | 2.5694e-05
2013-01-10 01:30PM | 1583845-1 | CT1262 | Rural Short | Other | 4 | 49.75 | 199 | 0.00022231 | 4.4685e-06
2013-02-06 09:50AM | 1592047-1 | CT1262 | Rural Short | Equipment Failure | 1 | 83 | 83 | 9.2721e-05 | 1.1171e-06
2013-03-11 08:42AM | 1602477-1 | CT1262 | Rural Short | Other | 7 | 177 | 1239 | 0.0013841 | 7.8198e-06
2012-09-17 03:21PM | 1555129-1 | CT1262 | Rural Short | Third Party Impacts | 630 | 118.5 | 74655 | 0.083399 | 0.00070379
2012-12-24 07:21PM | 1580269-1 | CT1262 | Rural Short | Weather | 610 | 112.7934 | 68804 | 0.076862 | 0.00068144
2012-11-19 10:16AM | 1570799-1 | CT1273 | Urban | Third Party Impacts | 43 | 255.7209 | 10996 | 0.012284 | 4.8036e-05
2012-12-25 07:33PM | 1580577-1 | CT1273 | Urban | Weather | 33 | 110 | 3630 | 0.0040551 | 3.6865e-05
2012-09-25 08:25PM | 1557011-1 | CT1296 | Urban | Equipment Failure | 1 | 206 | 206 | 0.00023013 | 1.1171e-06
2012-12-10 09:54AM | 1576744-1 | CT1296 | Urban | Equipment Failure | 60 | 96.7167 | 5803 | 0.0064826 | 6.7027e-05
2012-09-29 03:54PM | 1558088-1 | CT1296 | Urban | Equipment Failure | 100 | 80.81 | 8081 | 0.0090274 | 0.00011171
2012-12-24 09:35PM | 1580334-1 | CT1296 | Urban | Equipment Failure | 22 | 37.0909 | 816 | 0.00091157 | 2.4577e-05
2013-02-12 09:58AM | 1593774-1 | CT1296 | Urban | Equipment Failure | 1 | 252 | 252 | 0.00028151 | 1.1171e-06
2012-11-27 12:47PM | 1573102-1 | 1125 | Urban | Equipment Failure | 104 | 229.0288 | 23819 | 0.026609 | 0.00011618
2013-01-18 05:35PM | 1586269-1 | 1125 | Urban | Equipment Failure | 70 | 118.0286 | 8262 | 0.0092296 | 7.8198e-05
2012-07-07 05:52AM | 1536237-1 | 1125 | Urban | Equipment Failure | 22 | 413.8182 | 9104 | 0.01017 | 2.4577e-05
2012-10-17 08:29PM | 1562678-1 | 1125 | Urban | Equipment Failure | 19 | 23.5789 | 448 | 0.00050047 | 2.1225e-05
2012-10-17 10:14PM | 1562680-1 | 1125 | Urban | Other | 27 | 59.2222 | 1599 | 0.0017863 | 3.0162e-05
2012-10-10 08:35AM | 1560249-1 | 1125 | Urban | Equipment Failure | 1 | 102 | 102 | 0.00011395 | 1.1171e-06
2012-11-27 02:01PM | 1573097-1 | 1125 | Urban | Other | 52 | 41 | 2132 | 0.0023817 | 5.809e-05
2012-08-17 03:21PM | 1546947-1 | 1129 | Urban | Weather | 63 | 60.4127 | 3806 | 0.0042518 | 7.0379e-05
2012-10-26 09:40PM | 1565103-1 | 1131 | Urban | Third Party Impacts | 122 | 489.459 | 59714 | 0.066708 | 0.00013629
2012-07-09 11:42PM | 1536723-1 | 1131 | Urban | Equipment Failure | 56 | 65.0893 | 3645 | 0.0040719 | 6.2559e-05
2013-02-10 09:07PM | 1593374-1 | 1131 | Urban | Weather | 10 | 89 | 890 | 0.00099424 | 1.1171e-05
2012-07-06 10:19AM | 1536068-1 | 1133 | Urban | Equipment Failure | 1 | 264 | 264 | 0.00029492 | 1.1171e-06
2012-07-27 06:58PM | 1540999-1 | 3184 | Urban | Equipment Failure | 67 | 50.8209 | 3405 | 0.0038038 | 7.4847e-05
2012-10-15 06:43PM | 1561956-1 | 3185 | Urban | Equipment Failure | 77 | 114.7922 | 8839 | 0.0098742 | 8.6018e-05
2012-08-17 01:04PM | 1546712-1 | 3185 | Urban | Weather | 455 | 150.9538 | 68684 | 0.076728 | 0.00050829
2012-12-05 08:46PM | 1575951-1 | 3185 | Urban | Equipment Failure | 165 | 1 | 165 | 0.00018432 | 0.00018432
2013-05-08 07:33PM | 1615909-1 | 3187 | Urban | Other | 43 | 42 | 1806 | 0.0020175 | 4.8036e-05
2013-02-21 08:06AM | 1595959-1 | CRA2 | Urban | Other | 1 | 126 | 126 | 0.00014076 | 1.1171e-06
2013-02-09 08:53AM | 1593002-1 | CRA2 | Urban | Equipment Failure | 624 | 49 | 30576 | 0.034157 | 0.00069708
2013-01-22 03:11PM | 1587321-1 | CRA2 | Urban | Weather | 2265 | 32.8817 | 74477 | 0.0832 | 0.0025303
2013-01-22 04:50PM | 1587387-1 | CRA2 | Urban | Weather | 1664 | 67.5162 | 112347 | 0.12551 | 0.0018589
2013-04-16 01:16AM | 1610560-1 | CRA2 | Urban | Other | 2285 | 4.7895 | 10944 | 0.012226 | 0.0025526
2013-01-28 09:35AM | 1589232-1 | CRA2 | Urban | Equipment Failure | 1 | 313 | 313 | 0.00034966 | 1.1171e-06
2012-11-10 11:29AM | 1568987-1 | CRB2 | Urban | Equipment Failure | 30 | 82 | 2460 | 0.0027481 | 3.3514e-05
2012-11-03 12:17AM | 1566722-1 | CRB2 | Urban | Equipment Failure | 76 | 182.0395 | 13835 | 0.015455 | 8.4901e-05
2013-06-26 09:03AM | 1628181-1 | CRB2 | Urban | Equipment Failure | 1 | 352 | 352 | 0.00039323 | 1.1171e-06
2013-01-22 03:19PM | 1587331-1 | CRB2 | Urban | Weather | 2507 | 27 | 67689 | 0.075617 | 0.0028006
2013-03-12 03:16AM | 1602733-1 | CRB2 | Urban | Animals | 3816 | 109.6913 | 418582 | 0.46761 | 0.0042629
2013-06-12 03:12PM | 1624686-1 | CRB2 | Urban | Equipment Failure | 130 | 98.8077 | 12845 | 0.014349 | 0.00014523
2013-06-12 05:03PM | 1624711-1 | CRB2 | Urban | Equipment Failure | 138 | 43 | 5934 | 0.006629 | 0.00015416
2012-11-24 07:12PM | 1572471-1 | CRB2 | Urban | Other | 1 | 139 | 139 | 0.00015528 | 1.1171e-06
2013-03-07 10:56AM | 1601675-1 | CRB2 | Urban | Equipment Failure | 1 | 273 | 273 | 0.00030497 | 1.1171e-06
2012-11-21 06:11AM | 1571455-1 | CRC2 | Urban | Other | 11 | 256 | 2816 | 0.0031458 | 1.2288e-05
2013-04-08 01:35PM | 1608610-1 | CRD2 | Urban | Other | 89 | 262 | 23318 | 0.026049 | 9.9424e-05
2012-07-26 05:40PM | 1540664-1 | CRD2 | Urban | Equipment Failure | 555 | 119 | 66045 | 0.07378 | 0.00062
2013-05-29 11:35AM | 1621341-1 | CRE2 | Urban | Other | 25 | 62 | 1550 | 0.0017315 | 2.7928e-05
2013-01-30 11:54AM | 1590002-1 | CRE2 | Urban | Equipment Failure | 43 | 187.3023 | 8054 | 0.0089973 | 4.8036e-05
2013-03-07 11:09AM | 1601681-1 | 2809 | Urban | Vegetation | 13 | 117 | 1521 | 0.0016991 | 1.4523e-05
2013-06-23 08:46AM | 1627206-1 | 2810 | Urban | Weather | 1 | 46 | 46 | 5.1388e-05 | 1.1171e-06
2013-01-31 02:40AM | 1590157-1 | 2812 | Urban | Third Party Impacts | 1307 | 144.6327 | 189035 | 0.21117 | 0.0014601
2013-01-31 02:41AM | 1590176-1 | 2812 | Urban | Third Party Impacts | 72 | 383 | 27576 | 0.030806 | 8.0433e-05
2013-01-22 01:08AM | 1587126-1 | 2812 | Urban | Other | 128 | 346 | 44288 | 0.049475 | 0.00014299
2013-04-10 04:40PM | 1609301-1 | 2812 | Urban | Other | 1 | 11 | 11 | 1.2288e-05 | 1.1171e-06
2012-11-18 04:00PM | 1570588-1 | 2813 | Urban | Equipment Failure | 839 | 85.5495 | 71776 | 0.080182 | 0.00093726
2013-01-06 04:52PM | 1582737-1 | 2813 | Urban | Other | 30 | 92.6 | 2778 | 0.0031034 | 3.3514e-05
2012-10-01 12:14PM | 1558217-1 | 2813 | Urban | Animals | 21 | 17.619 | 370 | 0.00041333 | 2.346e-05
2013-01-13 05:01PM | 1584433-1 | 2815 | Urban | Weather | 1325 | 106.4581 | 141057 | 0.15758 | 0.0014802
2013-01-13 07:44PM | 1584513-1 | 2815 | Urban | Weather | 1325 | 114.9125 | 152259 | 0.17009 | 0.0014802
2013-05-23 10:53AM | 1619669-1 | 2815 | Urban | Other | 132 | 71 | 9372 | 0.01047 | 0.00014746
2013-05-23 01:53PM | 1619753-1 | 2815 | Urban | Equipment Failure | 1 | 249 | 249 | 0.00027816 | 1.1171e-06
2013-03-26 10:55PM | 1606484-1 | 2816 | Urban | Other | 793 | 0.49937 | 396 | 0.00044238 | 0.00088588
2013-05-24 03:21PM | 1620130-1 | 2816 | Urban | Equipment Failure | 186 | 11.8333 | 2201 | 0.0024588 | 0.00020778
2012-09-12 03:23PM | 1554095-1 | 2816 | Urban | Operatonal Error | 1 | 304 | 304 | 0.0003396 | 1.1171e-06
2012-11-03 06:02AM | 1566749-1 | 2816 | Urban | Equipment Failure | 18 | 331.6111 | 5969 | 0.0066681 | 2.0108e-05
2013-05-22 10:30AM | 1619317-1 | 5494 | Urban | Other | 1 | 213 | 213 | 0.00023795 | 1.1171e-06
2012-11-03 08:23AM | 1566823-1 | 5494 | Urban | Equipment Failure | 23 | 322.0435 | 7407 | 0.0082745 | 2.5694e-05
2012-12-19 09:29AM | 1578911-1 | 5495 | Urban | Vegetation | 1392 | 53.8103 | 74904 | 0.083677 | 0.001555
2013-01-31 08:14PM | 1590495-1 | 5495 | Urban | Animals | 1394 | 14.3242 | 19968 | 0.022307 | 0.0015573
2013-06-25 06:43PM | 1628047-1 | 5495 | Urban | Weather | 1579 | 138.4604 | 218629 | 0.24423 | 0.0017639
2012-08-15 10:57PM | 1546155-1 | 5496 | Urban | Vegetation | 66 | 181.8788 | 12004 | 0.01341 | 7.373e-05
2012-07-18 09:12PM | 1538701-1 | 5496 | Urban | Third Party Impacts | 66 | 242.9394 | 16034 | 0.017912 | 7.373e-05
2012-10-16 02:28PM | 1562221-1 | 5496 | Urban | Equipment Failure | 29 | 40 | 1160 | 0.0012959 | 3.2396e-05
2012-08-06 04:44PM | 1543249-1 | 5496 | Urban | Third Party Impacts | 933 | 111.7524 | 104265 | 0.11648 | 0.0010423
2012-12-28 05:27PM | 1581245-1 | 5496 | Urban | Equipment Failure | 680 | 39 | 26520 | 0.029626 | 0.00075964
2012-11-04 08:34AM | 1566946-1 | 3187 | Urban | Other | 11 | 601.6364 | 6618 | 0.0073931 | 1.2288e-05
2013-02-01 02:57PM | 1590739-1 | 3187 | Urban | Equipment Failure | 1 | 65 | 65 | 7.2613e-05 | 1.1171e-06
2013-03-10 07:47AM | 1602310-1 | D852 | Urban | Vegetation | 32 | 296 | 9472 | 0.010581 | 3.5748e-05
2013-06-23 07:03PM | 1627357-1 | D852 | Urban | Other | 35 | 41.4286 | 1450 | 0.0016198 | 3.9099e-05
2013-05-30 08:45AM | 1621535-1 | D852 | Urban | Animals | 67 | 52 | 3484 | 0.003892 | 7.4847e-05
2013-04-08 04:05PM | 1608652-1 | D852 | Urban | Equipment Failure | 1 | 325 | 325 | 0.00036306 | 1.1171e-06
2013-01-07 08:24AM | 1582772-1 | D852 | Urban | Third Party Impacts | 33 | 305.7879 | 10091 | 0.011273 | 3.6865e-05
2013-01-28 01:56AM | 1589191-1 | D852 | Urban | Animals | 1364 | 134.3321 | 183229 | 0.20469 | 0.0015238
2013-03-28 08:35PM | 1606969-1 | D852 | Urban | Animals | 1365 | 109 | 148785 | 0.16621 | 0.0015249
2012-09-14 03:13PM | 1554702-1 | C824 | Urban | Other | 18 | 265 | 4770 | 0.0053287 | 2.0108e-05
2013-01-08 10:29PM | 1583441-1 | C824 | Urban | Equipment Failure | 25 | 416 | 10400 | 0.011618 | 2.7928e-05
2012-10-23 09:25AM | 1563892-1 | DP1269 | Urban | Other | 1 | 25 | 25 | 2.7928e-05 | 1.1171e-06
2013-06-28 11:31AM | 1628981-1 | DP1269 | Urban | Equipment Failure | 58 | 35 | 2030 | 0.0022678 | 6.4793e-05
2013-03-28 02:34PM | 1606875-1 | DP1269 | Urban | Other | 68 | 66 | 4488 | 0.0050136 | 7.5964e-05
2012-11-30 11:51PM | 1574519-1 | DP1269 | Urban | Weather | 1550 | 189.0297 | 292996 | 0.32731 | 0.0017315
2013-02-06 08:30PM | 1594752-1 | DP1273 | Urban | Operatonal Error | 252 | 13.2778 | 3346 | 0.0037379 | 0.00028151
2012-12-17 11:08PM | 1578610-1 | DP1273 | Urban | Other | 250 | 87.128 | 21782 | 0.024333 | 0.00027928
2013-02-06 08:30PM | 1594752-1 | DP1284 | Rural Short | Operatonal Error | 1345 | 13.2989 | 17887 | 0.019982 | 0.0015025
2013-02-22 11:34AM | 1596385-1 | DP1284 | Rural Short | Equipment Failure | 7 | 116.2857 | 814 | 0.00090934 | 7.8198e-06
2012-07-30 11:21PM | 1541519-1 | DP1284 | Rural Short | Equipment Failure | 3 | 98 | 294 | 0.00032843 | 3.3514e-06
2012-12-11 10:44PM | 1577233-1 | DP1284 | Rural Short | Equipment Failure | 1322 | 115.0098 | 152043 | 0.16985 | 0.0014768
2013-02-25 06:47PM | 1598379-1 | DP1284 | Rural Short | Equipment Failure | 2659 | 105.9507 | 281723 | 0.31472 | 0.0029704
2013-02-06 08:30PM | 1594752-1 | DP1295 | Urban | Operatonal Error | 800 | 13.2963 | 10637 | 0.011883 | 0.0008937
2013-05-10 04:30AM | 1616235-1 | DP1295 | Urban | Other | 5 | 95.8 | 479 | 0.0005351 | 5.5856e-06
2013-01-08 10:30PM | 1583442-1 | 7530 | Rural Short | Other | 2 | 2276 | 4552 | 0.0050851 | 2.2342e-06
2012-07-25 08:14AM | 1540165-1 | TZ9653 | Rural Short | Equipment Failure | 3 | 21.6667 | 65 | 7.2613e-05 | 3.3514e-06
2012-11-18 06:39PM | 1570686-1 | TZ9653 | Rural Short | Vegetation | 3 | 381 | 1143 | 0.0012769 | 3.3514e-06
2012-10-11 01:16PM | 1564032-1 | 7977 | Urban | Third Party Impacts | 160 | 5 | 800 | 0.0008937 | 0.00017874
2012-10-15 03:53PM | 1561917-1 | 7977 | Urban | Equipment Failure | 33 | 210.5152 | 6947 | 0.0077606 | 3.6865e-05
2013-01-19 07:40AM | 1586554-1 | HBD2 | Urban | Third Party Impacts | 4 | 180 | 720 | 0.00080433 | 4.4685e-06
2013-04-26 07:05AM | 1613020-1 | 48161 | Urban | Equipment Failure | 22 | 115 | 2530 | 0.0028263 | 2.4577e-05
2013-01-07 06:18AM | 1582764-1 | 48161 | Urban | Equipment Failure | 28 | 62.8214 | 1759 | 0.001965 | 3.1279e-05
2012-11-26 05:35PM | 1572829-1 | 48161 | Urban | Weather | 1070 | 71.8131 | 76840 | 0.085839 | 0.0011953
2012-12-21 01:10AM | 1579572-1 | 48161 | Urban | Equipment Failure | 30 | 72 | 2160 | 0.002413 | 3.3514e-05
2012-09-30 02:31PM | 1558170-1 | 48161 | Urban | Other | 1 | 150 | 150 | 0.00016757 | 1.1171e-06
2012-07-28 04:48PM | 1541060-1 | 48168 | Urban | Other | 35 | 58.1429 | 2035 | 0.0022733 | 3.9099e-05
2012-10-22 09:38AM | 1563496-1 | 48168 | Urban | Equipment Failure | 34 | 41.4706 | 1410 | 0.0015751 | 3.7982e-05
2013-01-25 04:52PM | 1588724-1 | 48178 | Urban | Other | 7 | 62 | 434 | 0.00048483 | 7.8198e-06
2013-01-25 08:44PM | 1588833-1 | 48178 | Urban | Equipment Failure | 1 | 175 | 175 | 0.0001955 | 1.1171e-06
2012-07-17 03:34PM | 1538420-1 | 48180 | Urban | Other | 2 | 117.5 | 235 | 0.00026252 | 2.2342e-06
2013-04-15 06:09PM | 1610477-1 | 48185 | Rural Short | Weather | 486 | 85.0658 | 41342 | 0.046184 | 0.00054292
2013-05-31 03:02PM | 1622113-1 | 48187 | Urban | Other | 1 | 270 | 270 | 0.00030162 | 1.1171e-06
2012-10-30 06:51AM | 1565583-1 | 48189 | Urban | Third Party Impacts | 38 | 94 | 3572 | 0.0039904 | 4.2451e-05
2012-11-30 03:50PM | 1574304-1 | 48189 | Urban | Equipment Failure | 2397 | 2.6829 | 6431 | 0.0071842 | 0.0026777
2013-04-09 08:09AM | 1608723-1 | 77674 | Rural Short | Other | 362 | 27.0138 | 9779 | 0.010924 | 0.0004044
2013-04-09 10:42AM | 1608833-1 | 77674 | Rural Short | Equipment Failure | 22 | 37 | 814 | 0.00090934 | 2.4577e-05
2012-08-24 06:25AM | 1551596-1 | X213 | Rural Short | Operatonal Error | 78 | 4.0128 | 313 | 0.00034966 | 8.7135e-05
2013-06-17 05:15PM | 1625844-1 | X213 | Rural Short | Equipment Failure | 28 | 41.4286 | 1160 | 0.0012959 | 3.1279e-05
2013-02-10 07:36PM | 1593343-1 | X213 | Rural Short | Weather | 84 | 8.2738 | 695 | 0.0007764 | 9.3838e-05
2012-09-08 03:00PM | 1553188-1 | X213 | Rural Short | Equipment Failure | 1 | 136 | 136 | 0.00015193 | 1.1171e-06
2013-03-14 02:27PM | 1603462-1 | X213 | Rural Short | Other | 1 | 87 | 87 | 9.7189e-05 | 1.1171e-06
2012-11-04 09:47AM | 1566956-1 | X213 | Rural Short | Other | 1 | 105 | 105 | 0.0001173 | 1.1171e-06
2012-11-17 06:17PM | 1573014-1 | X213 | Rural Short | Other | 2 | 173 | 346 | 0.00038652 | 2.2342e-06
2013-02-07 11:20AM | 1592391-1 | X213 | Rural Short | Third Party Impacts | 8 | 41.75 | 334 | 0.00037312 | 8.937e-06
2013-04-10 09:02AM | 1609085-1 | X213 | Rural Short | Weather | 1 | 431 | 431 | 0.00048148 | 1.1171e-06
2012-10-23 09:13AM | 1563888-1 | X213 | Rural Short | Other | 31 | 257.9355 | 7996 | 0.0089325 | 3.4631e-05
2013-01-18 04:36PM | 1586220-1 | X213 | Rural Short | Weather | 16 | 498.125 | 7970 | 0.0089034 | 1.7874e-05
2013-03-02 07:23AM | 1600132-1 | X213 | Rural Short | Third Party Impacts | 39 | 393.0769 | 15330 | 0.017125 | 4.3568e-05
2013-02-10 08:29PM | 1593368-1 | X213 | Rural Short | Weather | 2 | 157 | 314 | 0.00035078 | 2.2342e-06
2013-03-14 08:22PM | 1603592-1 | X213 | Rural Short | Other | 3 | 188 | 564 | 0.00063006 | 3.3514e-06
2012-08-24 06:25AM | 1551596-1 | X217 | Rural Short | Operatonal Error | 205 | 4.0049 | 821 | 0.00091716 | 0.00022901
2013-06-17 05:15PM | 1625844-1 | X217 | Rural Short | Equipment Failure | 73 | 41.6712 | 3042 | 0.0033983 | 8.155e-05
2012-12-23 05:21PM | 1579965-1 | X217 | Rural Short | Other | 1 | 161 | 161 | 0.00017986 | 1.1171e-06
2012-11-08 05:03PM | 1568403-1 | X217 | Rural Short | Weather | 56 | 197.0536 | 11035 | 0.012327 | 6.2559e-05
2012-09-29 08:35AM | 1558031-1 | X217 | Rural Short | Weather | 1 | 123 | 123 | 0.00013741 | 1.1171e-06
2012-10-05 10:30AM | 1562152-1 | X217 | Rural Short | Weather | 1 | 50 | 50 | 5.5856e-05 | 1.1171e-06
2013-06-06 07:12AM | 1623335-1 | X217 | Rural Short | Equipment Failure | 1 | 125 | 125 | 0.00013964 | 1.1171e-06
2013-02-02 08:17AM | 1590969-1 | X217 | Rural Short | Weather | 1 | 145 | 145 | 0.00016198 | 1.1171e-06
2012-09-29 10:37AM | 1558058-1 | X217 | Rural Short | Weather | 1 | 4 | 4 | 4.4685e-06 | 1.1171e-06
2013-06-24 05:23PM | 1627573-1 | C832 | Urban | Weather | 19 | 70.3158 | 1336 | 0.0014925 | 2.1225e-05
2012-10-03 03:46PM | 1558617-1 | C832 | Urban | Equipment Failure | 403 | 63.7643 | 25697 | 0.028707 | 0.0004502
2012-11-16 08:41PM | 1570499-1 | C832 | Urban | Equipment Failure | 403 | 251.0273 | 101164 | 0.11301 | 0.0004502
2013-02-01 04:53PM | 1590843-1 | C832 | Urban | Equipment Failure | 583 | 9.5283 | 5555 | 0.0062056 | 0.00065128
2012-09-18 05:40AM | 1555254-1 | 8633 | Rural Short | Weather | 1 | 142 | 142 | 0.00015863 | 1.1171e-06
2012-12-25 07:22AM | 1580412-1 | 8633 | Rural Short | Equipment Failure | 3 | 348 | 1044 | 0.0011663 | 3.3514e-06
2012-08-10 10:03AM | 1544400-1 | 8633 | Rural Short | Weather | 211 | 53.0995 | 11204 | 0.012516 | 0.00023571
2013-05-26 08:05AM | 1620215-1 | 8633 | Rural Short | Other | 45 | 22.1778 | 998 | 0.0011149 | 5.027e-05
2013-02-07 01:00PM | 1592495-1 | 8634 | Rural Short | Animals | 4 | 328 | 1312 | 0.0014657 | 4.4685e-06
2012-08-17 05:39PM | 1547045-1 | 8634 | Rural Short | Weather | 9 | 1269.7778 | 11428 | 0.012766 | 1.0054e-05
2012-12-23 04:07AM | 1579879-1 | 8634 | Rural Short | Other | 644 | 36.0171 | 23195 | 0.025912 | 0.00071943
2012-10-20 05:02PM | 1563329-1 | 8634 | Rural Short | Vegetation | 2 | 333 | 666 | 0.000744 | 2.2342e-06
2012-11-21 01:16PM | 1571614-1 | 8634 | Rural Short | Equipment Failure | 2 | 128 | 256 | 0.00028598 | 2.2342e-06
2012-08-25 09:12AM | 1551940-1 | 8634 | Rural Short | Equipment Failure | 23 | 318 | 7314 | 0.0081706 | 2.5694e-05
2012-11-21 12:03PM | 1573628-1 | 8634 | Rural Short | Equipment Failure | 219 | 4 | 876 | 0.0009786 | 0.00024465
2013-02-07 08:29AM | 1595162-1 | 8634 | Rural Short | Other | 261 | 83 | 21663 | 0.0242 | 0.00029157
2012-11-26 04:39PM | 1572813-1 | 8634 | Rural Short | Weather | 466 | 216.6223 | 100946 | 0.11277 | 0.00052058
2012-11-30 11:46PM | 1574518-1 | 8634 | Rural Short | Equipment Failure | 670 | 3.9134 | 2622 | 0.0029291 | 0.00074847
2012-12-01 11:21AM | 1574625-1 | 8634 | Rural Short | Weather | 670 | 7 | 4690 | 0.0052393 | 0.00074847
2013-01-06 12:03AM | 1582684-1 | 8634 | Rural Short | Vegetation | 467 | 149.2527 | 69701 | 0.077864 | 0.0005217
2012-12-01 01:52PM | 1574654-1 | 8634 | Rural Short | Other | 129 | 144 | 18576 | 0.020752 | 0.00014411
2013-01-31 08:00AM | 1590426-1 | 8634 | Rural Short | Other | 11 | 117 | 1287 | 0.0014377 | 1.2288e-05
2013-03-11 12:12PM | 1602598-1 | 8634 | Rural Short | Other | 1 | 218 | 218 | 0.00024353 | 1.1171e-06
2012-09-07 02:00PM | 1556728-1 | 8634 | Rural Short | Weather | 12 | 15 | 180 | 0.00020108 | 1.3405e-05
2013-03-06 01:26PM | 1601334-1 | 8634 | Rural Short | Vegetation | 12 | 60 | 720 | 0.00080433 | 1.3405e-05
2013-06-26 07:03AM | 1628142-1 | 8634 | Rural Short | Weather | 21 | 290.6667 | 6104 | 0.0068189 | 2.346e-05
2012-08-17 01:40PM | 1546757-1 | 8634 | Rural Short | Weather | 7 | 516.2857 | 3614 | 0.0040373 | 7.8198e-06
2013-02-25 01:21PM | 1598109-1 | 8634 | Rural Short | Weather | 5 | 3605 | 18025 | 0.020136 | 5.5856e-06
2013-05-13 07:18AM | 1616791-1 | 8635 | Rural Short | Equipment Failure | 5 | 118.4 | 592 | 0.00066134 | 5.5856e-06
2012-11-25 01:22PM | 1572511-1 | 8635 | Rural Short | Other | 11 | 177 | 1947 | 0.002175 | 1.2288e-05
2012-12-06 08:14PM | 1576231-1 | 8635 | Rural Short | Other | 10 | 64 | 640 | 0.00071496 | 1.1171e-05
2013-02-01 10:29AM | 1590595-1 | 8635 | Rural Short | Other | 10 | 240 | 2400 | 0.0026811 | 1.1171e-05
2013-02-05 07:57PM | 1591861-1 | 8635 | Rural Short | Other | 16 | 106 | 1696 | 0.0018946 | 1.7874e-05
2013-01-29 08:07AM | 1589499-1 | 8635 | Rural Short | Vegetation | 1 | 140 | 140 | 0.0001564 | 1.1171e-06
2013-02-08 03:08PM | 1592853-1 | 8635 | Rural Short | Other | 1 | 145 | 145 | 0.00016198 | 1.1171e-06
2012-12-24 04:53PM | 1580183-1 | 8635 | Rural Short | Weather | 75 | 540.1467 | 40511 | 0.045256 | 8.3784e-05
2013-01-19 05:01PM | 1586643-1 | 8635 | Rural Short | Vegetation | 729 | 172.0494 | 125424 | 0.14011 | 0.00081438
2013-02-19 07:24PM | 1595630-1 | 8635 | Rural Short | Third Party Impacts | 16 | 340.9375 | 5455 | 0.0060939 | 1.7874e-05
2012-11-25 09:10PM | 1572562-1 | 8635 | Rural Short | Vegetation | 8 | 344 | 2752 | 0.0030743 | 8.937e-06
2013-05-04 12:58PM | 1614888-1 | 8635 | Rural Short | Other | 1 | 88 | 88 | 9.8307e-05 | 1.1171e-06
2012-10-11 08:14AM | 1560507-1 | 8635 | Rural Short | Third Party Impacts | 90 | 103.7444 | 9337 | 0.010431 | 0.00010054
2012-10-20 03:06PM | 1563316-1 | 8635 | Rural Short | Vegetation | 193 | 130.4093 | 25169 | 0.028117 | 0.0002156
2012-11-27 09:10PM | 1573335-1 | 8635 | Rural Short | Vegetation | 75 | 304.96 | 22872 | 0.025551 | 8.3784e-05
2013-06-14 11:33AM | 1625257-1 | 8635 | Rural Short | Other | 75 | 64.84 | 4863 | 0.0054326 | 8.3784e-05
2013-01-19 10:22PM | 1586679-1 | 8635 | Rural Short | Vegetation | 4 | 123.25 | 493 | 0.00055074 | 4.4685e-06
2012-09-13 06:27PM | 1554446-1 | 8635 | Rural Short | Other | 1 | 337 | 337 | 0.00037647 | 1.1171e-06
2012-10-19 05:22PM | 1563197-1 | 8636 | Rural Short | Equipment Failure | 2 | 126 | 252 | 0.00028151 | 2.2342e-06
2013-05-13 10:39AM | 1616854-1 | 8636 | Rural Short | Equipment Failure | 5 | 283.8 | 1419 | 0.0015852 | 5.5856e-06
2012-08-31 12:29PM | 1550944-1 | 8636 | Rural Short | Other | 2 | 63.5 | 127 | 0.00014187 | 2.2342e-06
2012-07-05 12:48PM | 1535858-1 | 8636 | Rural Short | Vegetation | 475 | 68.3158 | 32450 | 0.036251 | 0.00053063
2013-03-11 12:12PM | 1602597-1 | 8636 | Rural Short | Operatonal Error | 533 | 52.7767 | 28130 | 0.031425 | 0.00059542
2012-11-01 11:31AM | 1566201-1 | 8636 | Rural Short | Other | 504 | 166.8492 | 84092 | 0.093941 | 0.00056303
2012-11-30 06:05PM | 1574415-1 | 8636 | Rural Short | Weather | 504 | 416.9524 | 210144 | 0.23476 | 0.00056303
2012-12-06 01:04PM | 1576124-1 | 8636 | Rural Short | Other | 3 | 96 | 288 | 0.00032173 | 3.3514e-06
2012-08-17 05:11PM | 1547034-1 | 8636 | Rural Short | Weather | 165 | 36.8 | 6072 | 0.0067832 | 0.00018432
2012-11-01 11:25AM | 1566190-1 | 8636 | Rural Short | Equipment Failure | 165 | 180.5576 | 29792 | 0.033281 | 0.00018432
2013-03-24 05:53PM | 1605890-1 | 8636 | Rural Short | Vegetation | 165 | 20.0182 | 3303 | 0.0036898 | 0.00018432
2012-11-03 09:29AM | 1566839-1 | 8636 | Rural Short | Other | 26 | 243.2308 | 6324 | 0.0070647 | 2.9045e-05
2012-08-26 03:43PM | 1549557-1 | 8637 | Rural Short | Equipment Failure | 1 | 247 | 247 | 0.00027593 | 1.1171e-06
2012-12-01 09:40AM | 1574608-1 | 8637 | Rural Short | Weather | 5 | 236 | 1180 | 0.0013182 | 5.5856e-06
2012-12-24 07:02PM | 1580257-1 | 8637 | Rural Short | Other | 4 | 138.25 | 553 | 0.00061777 | 4.4685e-06
2012-10-16 03:31AM | 1562000-1 | 8637 | Rural Short | Third Party Impacts | 209 | 91 | 19019 | 0.021247 | 0.00023348
2012-11-30 05:59PM | 1574406-1 | 8637 | Rural Short | Weather | 210 | 141.8952 | 29798 | 0.033288 | 0.0002346
2013-06-02 03:44AM | 1622267-1 | 8637 | Rural Short | Vegetation | 81 | 189.4444 | 15345 | 0.017142 | 9.0487e-05
2013-02-27 07:23PM | 1599156-1 | CD1204 | Urban | Other | 563 | 4.6412 | 2613 | 0.002919 | 0.00062894
2013-02-04 04:56PM | 1591481-1 | CD1204 | Urban | Weather | 580 | 96.3707 | 55895 | 0.062441 | 0.00064793
2013-03-25 06:49AM | 1605930-1 | CD1204 | Urban | Other | 1 | 183 | 183 | 0.00020443 | 1.1171e-06
2012-12-24 09:17PM | 1580327-1 | CD1230 | Rural Short | Weather | 800 | 177.6387 | 142111 | 0.15876 | 0.0008937
2012-12-25 03:26AM | 1580400-1 | CD1234 | Urban | Weather | 92 | 42 | 3864 | 0.0043166 | 0.00010278
2012-12-24 03:55PM | 1580150-1 | CD1234 | Urban | Weather | 10 | 146.5 | 1465 | 0.0016366 | 1.1171e-05
2013-01-19 07:00AM | 1586547-1 | CD1234 | Urban | Equipment Failure | 10 | 317 | 3170 | 0.0035413 | 1.1171e-05
2013-05-28 04:17PM | 1621090-1 | CD1234 | Urban | Equipment Failure | 10 | 29.7 | 297 | 0.00033178 | 1.1171e-05
2013-03-08 04:54PM | 1602117-1 | CD1234 | Urban | Third Party Impacts | 2 | 359 | 718 | 0.00080209 | 2.2342e-06
2013-05-31 03:55PM | 1622132-1 | CD1267 | Urban | Other | 3 | 56 | 168 | 0.00018768 | 3.3514e-06
2012-12-18 01:15PM | 1578757-1 | CD1271 | Urban | Third Party Impacts | 2 | 124.5 | 249 | 0.00027816 | 2.2342e-06
2013-04-09 09:23AM | 1608743-1 | CD1271 | Urban | Other | 1 | 109 | 109 | 0.00012177 | 1.1171e-06
2013-01-06 03:46PM | 1582728-1 | CD1271 | Urban | Vegetation | 422 | 25.6659 | 10831 | 0.0121 | 0.00047142
2013-03-04 08:11AM | 1600401-1 | CD1297 | Urban | Equipment Failure | 36 | 97 | 3492 | 0.003901 | 4.0216e-05
2013-06-09 05:22AM | 1624029-1 | CD1297 | Urban | Equipment Failure | 28 | 392.3214 | 10985 | 0.012272 | 3.1279e-05
2012-10-07 07:54PM | 1559555-1 | R218 | Rural Short | Equipment Failure | 4 | 111.25 | 445 | 0.00049712 | 4.4685e-06
2012-09-05 08:43AM | 1551889-1 | R218 | Rural Short | Other | 2 | 245 | 490 | 0.00054739 | 2.2342e-06
2012-08-16 06:03PM | 1546433-1 | R218 | Rural Short | Equipment Failure | 48 | 171.1042 | 8213 | 0.0091749 | 5.3622e-05
2012-08-31 04:36PM | 1551072-1 | R218 | Rural Short | Third Party Impacts | 1 | 1183 | 1183 | 0.0013216 | 1.1171e-06
2012-10-06 06:51PM | 1559484-1 | R218 | Rural Short | Equipment Failure | 2 | 98.5 | 197 | 0.00022007 | 2.2342e-06
2012-07-31 10:45AM | 1541625-1 | R218 | Rural Short | Other | 1 | 100 | 100 | 0.00011171 | 1.1171e-06
2012-12-02 11:06PM | 1574832-1 | R218 | Rural Short | Equipment Failure | 66 | 175.8485 | 11606 | 0.012965 | 7.373e-05
2012-09-28 01:19AM | 1557666-1 | R218 | Rural Short | Weather | 2 | 395.5 | 791 | 0.00088364 | 2.2342e-06
2012-11-16 04:53AM | 1570257-1 | R218 | Rural Short | Other | 38 | 100 | 3800 | 0.0042451 | 4.2451e-05
2012-08-10 12:01PM | 1544483-1 | R218 | Rural Short | Equipment Failure | 1235 | 211.7061 | 261457 | 0.29208 | 0.0013796
2012-09-17 04:01PM | 1555145-1 | R218 | Rural Short | Weather | 1232 | 63.0479 | 77675 | 0.086772 | 0.0013763
2012-09-12 02:00PM | 1554124-1 | 27202 | Urban | Other | 21 | 60 | 1260 | 0.0014076 | 2.346e-05
2012-07-06 10:37AM | 1536070-1 | 27202 | Urban | Other | 24 | 284.0417 | 6817 | 0.0076154 | 2.6811e-05
2013-02-20 04:10PM | 1595843-1 | CJ1204 | Urban | Equipment Failure | 28 | 210.3571 | 5890 | 0.0065798 | 3.1279e-05
2013-05-16 12:15PM | 1617834-1 | CJ1204 | Urban | Vegetation | 16 | 42 | 672 | 0.0007507 | 1.7874e-05
2013-02-04 10:15AM | 1591321-1 | CJ1204 | Urban | Other | 15 | 150.1333 | 2252 | 0.0025158 | 1.6757e-05
2013-03-28 03:16PM | 1606902-1 | CJ1204 | Urban | Vegetation | 13 | 156 | 2028 | 0.0022655 | 1.4523e-05
2013-05-22 07:48PM | 1619502-1 | CJ1204 | Urban | Other | 1 | 475 | 475 | 0.00053063 | 1.1171e-06
2013-05-04 05:52AM | 1614838-1 | CJ1241 | Urban | Other | 22 | 157 | 3454 | 0.0038585 | 2.4577e-05
2013-04-05 05:13PM | 1608200-1 | CJ1241 | Urban | Vegetation | 91 | 55.7253 | 5071 | 0.0056649 | 0.00010166
2012-12-14 08:48AM | 1577867-1 | CJ1241 | Urban | Other | 1161 | 4 | 4644 | 0.0051879 | 0.001297
2013-04-09 11:21AM | 1608848-1 | CJ1245 | Urban | Equipment Failure | 60 | 206.35 | 12381 | 0.013831 | 6.7027e-05
2013-01-22 01:14PM | 1587230-1 | CJ1245 | Urban | Operatonal Error | 8 | 75 | 600 | 0.00067027 | 8.937e-06
2013-06-26 01:23PM | 1628328-1 | CJ1245 | Urban | Equipment Failure | 1 | 1355 | 1355 | 0.0015137 | 1.1171e-06
2013-03-03 05:29AM | 1600268-1 | CJ1245 | Urban | Other | 7 | 217 | 1519 | 0.0016969 | 7.8198e-06
2013-06-29 03:43PM | 1629251-1 | CJ1245 | Urban | Other | 8 | 204 | 1632 | 0.0018231 | 8.937e-06
2013-06-29 05:17PM | 1629266-1 | CJ1245 | Urban | Third Party Impacts | 15 | 52.7333 | 791 | 0.00088364 | 1.6757e-05
2013-06-28 06:52AM | 1628900-1 | CJ1249 | Urban | Third Party Impacts | 53 | 601.6226 | 31886 | 0.03562 | 5.9207e-05
2013-01-18 03:23PM | 1586175-1 | CJ1249 | Urban | Weather | 20 | 167 | 3340 | 0.0037312 | 2.2342e-05
2013-06-18 01:18PM | 1626094-1 | CJ1249 | Urban | Equipment Failure | 12 | 41.6667 | 500 | 0.00055856 | 1.3405e-05
2012-12-05 10:00AM | 1575649-1 | CJ1267 | Urban | Weather | 41 | 290 | 11890 | 0.013283 | 4.5802e-05
2013-02-12 11:30AM | 1593806-1 | CJ1267 | Urban | Other | 1 | 44 | 44 | 4.9153e-05 | 1.1171e-06
2012-12-09 02:15PM | 1576640-1 | CJ1286 | Urban | Weather | 22 | 75 | 1650 | 0.0018432 | 2.4577e-05
2013-05-06 03:22PM | 1615237-1 | 9026 | Urban | Equipment Failure | 142 | 13.5 | 1917 | 0.0021415 | 0.00015863
2012-08-19 03:42PM | 1547291-1 | 9030 | Urban | Equipment Failure | 1 | 185 | 185 | 0.00020667 | 1.1171e-06
2012-09-20 11:07PM | 1556039-1 | 17038 | Urban | Third Party Impacts | 1907 | 3.9612 | 7554 | 0.0084387 | 0.0021303
2012-10-21 01:53PM | 1563420-1 | 17038 | Urban | Equipment Failure | 48 | 149.6042 | 7181 | 0.008022 | 5.3622e-05
2013-06-11 08:51PM | 1624424-1 | CS1206 | Urban | Equipment Failure | 33 | 116 | 3828 | 0.0042763 | 3.6865e-05
2013-06-19 07:31AM | 1626218-1 | CS1276 | Urban | Operatonal Error | 2045 | 5 | 10225 | 0.011423 | 0.0022845
2013-06-29 12:05AM | 1629182-1 | CS1280 | Urban | Equipment Failure | 20 | 439 | 8780 | 0.0098083 | 2.2342e-05
2013-01-24 02:41PM | 1588016-1 | CRA2 | Urban | Equipment Failure | 89 | 266.9101 | 23755 | 0.026537 | 9.9424e-05
2013-05-17 04:52PM | 1618362-1 | CRA2 | Urban | Equipment Failure | 1 | 169 | 169 | 0.00018879 | 1.1171e-06
2013-05-01 06:53PM | 1614324-1 | CRA2 | Urban | Equipment Failure | 25 | 52 | 1300 | 0.0014523 | 2.7928e-05
2013-01-30 06:27AM | 1589907-1 | CRA2 | Urban | Other | 64 | 122 | 7808 | 0.0087225 | 7.1496e-05
2013-02-21 06:19AM | 1595913-1 | CRA2 | Urban | Other | 64 | 91.2656 | 5841 | 0.0065251 | 7.1496e-05
2013-06-25 05:45AM | 1627674-1 | CRA2 | Urban | Weather | 64 | 82 | 5248 | 0.0058626 | 7.1496e-05
2013-01-14 09:27AM | 1584668-1 | CRA2 | Urban | Equipment Failure | 30 | 537 | 16110 | 0.017997 | 3.3514e-05
2013-05-14 07:33PM | 1617343-1 | CRF2 | Urban | Equipment Failure | 1 | 151 | 151 | 0.00016869 | 1.1171e-06
2012-08-18 10:15PM | 1548292-1 | CRF2 | Urban | Operatonal Error | 8 | 1 | 8 | 8.937e-06 | 8.937e-06
2013-06-28 11:25AM | 1628977-1 | CRF2 | Urban | Equipment Failure | 1664 | 56.5871 | 94161 | 0.10519 | 0.0018589
2013-02-11 06:02PM | 1593668-1 | C811 | Urban | Equipment Failure | 18 | 216.7222 | 3901 | 0.0043579 | 2.0108e-05
2013-03-29 11:52AM | 1607022-1 | C812 | Urban | Other | 30 | 104 | 3120 | 0.0034854 | 3.3514e-05
2013-04-10 10:34PM | 1609373-1 | C812 | Urban | Equipment Failure | 52 | 380 | 19760 | 0.022074 | 5.809e-05
2013-05-13 12:31PM | 1616887-1 | C812 | Urban | Third Party Impacts | 76 | 116.4737 | 8852 | 0.0098887 | 8.4901e-05
2013-06-25 04:25PM | 1628005-1 | C812 | Urban | Equipment Failure | 1 | 101 | 101 | 0.00011283 | 1.1171e-06
2013-06-14 08:30PM | 1627539-1 | C812 | Urban | Other | 127 | 7 | 889 | 0.00099312 | 0.00014187
2013-01-04 10:44AM | 1582286-1 | C814 | Rural Short | Equipment Failure | 1 | 121 | 121 | 0.00013517 | 1.1171e-06
2013-01-22 08:21PM | 1587516-1 | C814 | Rural Short | Equipment Failure | 12 | 46 | 552 | 0.00061665 | 1.3405e-05
2013-04-20 12:57PM | 1611745-1 | C814 | Rural Short | Equipment Failure | 1 | 138 | 138 | 0.00015416 | 1.1171e-06
2013-05-10 10:50AM | 1616331-1 | C814 | Rural Short | Other | 4 | 80 | 320 | 0.00035748 | 4.4685e-06
2012-10-22 01:56PM | 1563587-1 | C814 | Rural Short | Other | 15 | 161.8 | 2427 | 0.0027113 | 1.6757e-05
2013-05-22 09:29AM | 1619283-1 | C814 | Rural Short | Operatonal Error | 146 | 37.8973 | 5533 | 0.006181 | 0.0001631
2013-03-08 02:37PM | 1602065-1 | L526 | Urban | Third Party Impacts | 15 | 333 | 4995 | 0.00558 | 1.6757e-05
2012-11-19 07:09PM | 1571027-1 | L526 | Urban | Equipment Failure | 13 | 80.8462 | 1051 | 0.0011741 | 1.4523e-05
2012-11-24 06:07PM | 1572461-1 | L526 | Urban | Vegetation | 1510 | 89.2497 | 134767 | 0.15055 | 0.0016869
2012-11-08 05:55PM | 1568451-1 | S785 | Urban | Weather | 21 | 271.9048 | 5710 | 0.0063788 | 2.346e-05
2012-11-08 06:25PM | 1568486-1 | S785 | Urban | Other | 1220 | 8.9 | 10858 | 0.01213 | 0.0013629
2013-03-28 06:42AM | 1606790-1 | S786 | Rural Short | Equipment Failure | 7 | 178 | 1246 | 0.0013919 | 7.8198e-06
2012-10-18 01:14AM | 1562688-1 | S786 | Rural Short | Other | 9 | 362 | 3258 | 0.0036396 | 1.0054e-05
2012-09-18 06:09PM | 1555549-1 | S786 | Rural Short | Weather | 6 | 115.1667 | 691 | 0.00077193 | 6.7027e-06
2012-12-06 03:29PM | 1576185-1 | S786 | Rural Short | Vegetation | 547 | 33.1664 | 18142 | 0.020267 | 0.00061106
2013-03-02 07:05PM | 1600244-1 | S786 | Rural Short | Animals | 11 | 97 | 1067 | 0.001192 | 1.2288e-05
2012-09-12 06:14AM | 1553859-1 | S788 | Rural Short | Other | 16 | 105 | 1680 | 0.0018768 | 1.7874e-05
2012-09-16 11:38AM | 1554885-1 | S788 | Rural Short | Animals | 16 | 118.625 | 1898 | 0.0021203 | 1.7874e-05
2012-11-08 08:21PM | 1568570-1 | S788 | Rural Short | Weather | 17 | 270.1765 | 4593 | 0.0051309 | 1.8991e-05
2012-08-24 06:06AM | 1549004-1 | S788 | Rural Short | Other | 10 | 231.7 | 2317 | 0.0025884 | 1.1171e-05
2013-01-18 08:15PM | 1586411-1 | S788 | Rural Short | Weather | 8 | 311.5 | 2492 | 0.0027839 | 8.937e-06
2013-01-31 09:37PM | 1590518-1 | S788 | Rural Short | Equipment Failure | 21 | 299 | 6279 | 0.0070144 | 2.346e-05
2012-08-22 03:25PM | 1548164-1 | S788 | Rural Short | Equipment Failure | 1 | 158 | 158 | 0.0001765 | 1.1171e-06
2012-07-10 11:05AM | 1536800-1 | S788 | Rural Short | Third Party Impacts | 759 | 102.3689 | 77698 | 0.086798 | 0.00084789
2012-11-08 04:09PM | 1568353-1 | S788 | Rural Short | Weather | 814 | 109.6609 | 89264 | 0.099719 | 0.00090934
2012-11-27 07:58PM | 1573264-1 | S788 | Rural Short | Weather | 814 | 94.3329 | 76787 | 0.08578 | 0.00090934
2012-11-08 08:37PM | 1568575-1 | S788 | Rural Short | Weather | 1 | 188 | 188 | 0.00021002 | 1.1171e-06
2012-08-03 04:08PM | 1542774-1 | S790 | Rural Short | Operatonal Error | 966 | 2.1325 | 2060 | 0.0023013 | 0.0010791
2012-10-08 02:00PM | 1562743-1 | S790 | Rural Short | Equipment Failure | 278 | 12.3453 | 3432 | 0.003834 | 0.00031056
2012-07-07 09:57AM | 1536276-1 | CLA2 | Rural Short | Equipment Failure | 10 | 20.1 | 201 | 0.00022454 | 1.1171e-05
2013-04-04 04:07PM | 1607898-1 | CLA2 | Rural Short | Equipment Failure | 119 | 33.4118 | 3976 | 0.0044417 | 0.00013294
2012-09-03 10:57AM | 1551367-1 | CLA2 | Rural Short | Other | 60 | 98 | 5880 | 0.0065687 | 6.7027e-05
2012-10-09 06:52AM | 1559902-1 | CLA2 | Rural Short | Equipment Failure | 5 | 683.8 | 3419 | 0.0038194 | 5.5856e-06
2012-10-27 01:55PM | 1565161-1 | CLA2 | Rural Short | Vegetation | 5 | 79.8 | 399 | 0.00044573 | 5.5856e-06
2013-01-27 07:15AM | 1589032-1 | CLA2 | Rural Short | Weather | 2 | 82 | 164 | 0.00018321 | 2.2342e-06
2012-09-09 06:30PM | 1553312-1 | CLA2 | Rural Short | Equipment Failure | 74 | 160.5946 | 11884 | 0.013276 | 8.2667e-05
2013-06-18 12:01PM | 1626064-1 | CLA2 | Rural Short | Operatonal Error | 926 | 5.0162 | 4645 | 0.005189 | 0.0010345
2013-03-29 06:42PM | 1607042-1 | CLB2 | Rural Short | Equipment Failure | 9 | 133 | 1197 | 0.0013372 | 1.0054e-05
2013-05-02 02:57PM | 1614543-1 | CLB2 | Rural Short | Other | 1223 | 1 | 1223 | 0.0013662 | 0.0013662
2013-06-18 12:01PM | 1626065-1 | CLB2 | Rural Short | Operatonal Error | 843 | 5 | 4215 | 0.0047087 | 0.00094173
2013-04-26 05:43PM | 1613266-1 | CLB2 | Rural Short | Equipment Failure | 1 | 122 | 122 | 0.00013629 | 1.1171e-06
2012-07-01 08:20PM | 1534684-1 | CLC2 | Rural Short | Equipment Failure | 78 | 24.3077 | 1896 | 0.0021181 | 8.7135e-05
2013-01-27 06:43AM | 1588998-1 | CLC2 | Rural Short | Other | 81 | 54 | 4374 | 0.0048863 | 9.0487e-05
2012-09-08 08:24AM | 1553085-1 | CLC2 | Rural Short | Animals | 8 | 250.75 | 2006 | 0.0022409 | 8.937e-06
2012-07-23 01:18PM | 1539755-1 | CLC2 | Rural Short | Equipment Failure | 98 | 42.9082 | 4205 | 0.0046975 | 0.00010948
2012-11-26 09:00AM | 1572643-1 | CLC2 | Rural Short | Equipment Failure | 102 | 108.3922 | 11056 | 0.012351 | 0.00011395
2013-02-08 04:13AM | 1592652-1 | CLC2 | Rural Short | Other | 1 | 316 | 316 | 0.00035301 | 1.1171e-06
2012-11-25 10:09PM | 1572596-1 | CLC2 | Rural Short | Equipment Failure | 234 | 111.0513 | 25986 | 0.029029 | 0.00026141
2013-01-24 03:46AM | 1587836-1 | CLC2 | Rural Short | Equipment Failure | 48 | 200 | 9600 | 0.010724 | 5.3622e-05
2013-03-14 01:17PM | 1603429-1 | CLC2 | Rural Short | Operatonal Error | 78 | 17 | 1326 | 0.0014813 | 8.7135e-05
2012-12-15 01:40PM | 1578166-1 | CLC2 | Rural Short | Equipment Failure | 1214 | 179.2166 | 217569 | 0.24305 | 0.0013562
2013-02-26 09:14PM | 1598806-1 | CLC2 | Rural Short | Equipment Failure | 1222 | 86.82 | 106094 | 0.11852 | 0.0013651
2013-02-17 01:38PM | 1594994-1 | CLC2 | Rural Short | Vegetation | 2329 | 68.1825 | 158797 | 0.1774 | 0.0026018
2013-04-24 02:37AM | 1612609-1 | CLD2 | Rural Short | Other | 1 | 59 | 59 | 6.591e-05 | 1.1171e-06
2012-08-16 09:43AM | 1546226-1 | CLD2 | Rural Short | Third Party Impacts | 1498 | 26.5995 | 39846 | 0.044513 | 0.0016734
2012-10-16 01:31PM | 1562200-1 | CLD2 | Rural Short | Other | 1499 | 2 | 2998 | 0.0033491 | 0.0016746
2013-04-11 02:20PM | 1609624-1 | CLD2 | Rural Short | Vegetation | 587 | 93 | 54591 | 0.060985 | 0.00065575
2013-03-15 05:02PM | 1603838-1 | CLD2 | Rural Short | Equipment Failure | 1 | 98 | 98 | 0.00010948 | 1.1171e-06
2012-07-26 05:56PM | 1540681-1 | CLD2 | Rural Short | Equipment Failure | 143 | 82.7343 | 11831 | 0.013217 | 0.00015975
2012-12-25 07:17AM | 1580411-1 | CLD2 | Rural Short | Vegetation | 103 | 21 | 2163 | 0.0024163 | 0.00011506
2013-02-22 05:10AM | 1596288-1 | CLD2 | Rural Short | Equipment Failure | 928 | 82.0851 | 76175 | 0.085097 | 0.0010367
2013-02-06 08:30PM | 1594752-1 | DP1206 | Urban | Operatonal Error | 1357 | 13.2992 | 18047 | 0.020161 | 0.0015159
2012-11-09 09:15PM | 1568946-1 | DP1206 | Urban | Other | 44 | 42 | 1848 | 0.0020644 | 4.9153e-05
2013-02-06 08:30PM | 1594752-1 | DP1210 | Rural Short | Operatonal Error | 1859 | 13.3007 | 24726 | 0.027622 | 0.0020767
2013-02-14 11:11AM | 1594385-1 | DP1210 | Rural Short | Equipment Failure | 2 | 261 | 522 | 0.00058314 | 2.2342e-06
2012-12-27 11:08AM | 1580837-1 | DP1210 | Rural Short | Other | 1 | 60 | 60 | 6.7027e-05 | 1.1171e-06
2012-08-24 09:19AM | 1549088-1 | DP1210 | Rural Short | Weather | 61 | 238.377 | 14541 | 0.016244 | 6.8144e-05
2013-03-05 09:32AM | 1600832-1 | DP1210 | Rural Short | Third Party Impacts | 3 | 59.6667 | 179 | 0.00019996 | 3.3514e-06
2012-09-07 07:53PM | 1553009-1 | DP1210 | Rural Short | Weather | 1 | 191 | 191 | 0.00021337 | 1.1171e-06
2013-02-06 08:30PM | 1594752-1 | DP1221 | Urban | Operatonal Error | 876 | 13.2945 | 11646 | 0.01301 | 0.0009786
2012-07-07 02:19AM | 1536234-1 | DP1221 | Urban | Other | 779 | 129.0578 | 100536 | 0.11231 | 0.00087024
2012-08-17 06:29PM | 1547064-1 | DP1221 | Urban | Weather | 873 | 99.0309 | 86454 | 0.096579 | 0.00097525
2013-02-06 08:30PM | 1594752-1 | DP1236 | Urban | Operatonal Error | 1554 | 13.2967 | 20663 | 0.023083 | 0.001736
2012-09-12 01:40PM | 1554025-1 | DP1236 | Urban | Other | 31 | 58 | 1798 | 0.0020086 | 3.4631e-05
2013-06-15 09:32PM | 1625497-1 | DP1236 | Urban | Equipment Failure | 9 | 133 | 1197 | 0.0013372 | 1.0054e-05
2012-09-18 06:46AM | 1555264-1 | DP1236 | Urban | Animals | 1555 | 3.7203 | 5785 | 0.0064625 | 0.0017371
2012-10-19 11:13AM | 1563017-1 | DP1236 | Urban | Animals | 1555 | 1 | 1555 | 0.0017371 | 0.0017371
2012-11-13 06:19PM | 1569626-1 | DP1236 | Urban | Animals | 2421 | 71.0182 | 171935 | 0.19207 | 0.0027045
2012-12-05 07:22AM | 1575568-1 | DP1236 | Urban | Other | 2421 | 2 | 4842 | 0.0054091 | 0.0027045
2013-02-06 08:30PM | 1594752-1 | DP1243 | Urban | Operatonal Error | 1337 | 13.2992 | 17781 | 0.019864 | 0.0014936
2013-01-18 06:25PM | 1586308-1 | DP1243 | Urban | Equipment Failure | 31 | 256.871 | 7963 | 0.0088956 | 3.4631e-05
2013-06-17 11:07AM | 1625700-1 | DP1243 | Urban | Other | 48 | 36.6875 | 1761 | 0.0019672 | 5.3622e-05
2013-02-06 08:30PM | 1594752-1 | DP1258 | Urban | Operatonal Error | 1347 | 13.2992 | 17914 | 0.020012 | 0.0015048
2013-04-19 01:19PM | 1611549-1 | DP1258 | Urban | Equipment Failure | 6 | 141.6667 | 850 | 0.00094955 | 6.7027e-06
2013-02-06 08:30PM | 1594752-1 | DP1269 | Urban | Operatonal Error | 1550 | 13.2968 | 20610 | 0.023024 | 0.0017315
2013-04-28 06:20AM | 1613427-1 | DP1269 | Urban | Third Party Impacts | 1 | 259 | 259 | 0.00028933 | 1.1171e-06
2013-01-15 03:20PM | 1585160-1 | TZ9653 | Rural Short | Third Party Impacts | 1 | 98 | 98 | 0.00010948 | 1.1171e-06
2013-02-21 08:53PM | 1596265-1 | DFA2 | Rural Short | Equipment Failure | 59 | 251.0339 | 14811 | 0.016546 | 6.591e-05
2012-12-28 03:44PM | 1581214-1 | DFA2 | Rural Short | Equipment Failure | 5 | 1810.2 | 9051 | 0.010111 | 5.5856e-06
2012-08-21 02:56AM | 1547619-1 | DFA2 | Rural Short | Equipment Failure | 36 | 139 | 5004 | 0.0055901 | 4.0216e-05
2012-10-01 06:23AM | 1558197-1 | DFA2 | Rural Short | Animals | 36 | 76.2778 | 2746 | 0.0030676 | 4.0216e-05
2012-12-05 03:02PM | 1575865-1 | DFA2 | Rural Short | Other | 36 | 89 | 3204 | 0.0035793 | 4.0216e-05
2012-09-28 03:22AM | 1557656-1 | DFA2 | Rural Short | Other | 59 | 90.3729 | 5332 | 0.0059565 | 6.591e-05
2012-12-28 06:30PM | 1581252-1 | DFA2 | Rural Short | Equipment Failure | 59 | 3.5593 | 210 | 0.0002346 | 6.591e-05
2013-04-05 09:39AM | 1608066-1 | DFC2 | Rural Short | Other | 3 | 90 | 270 | 0.00030162 | 3.3514e-06
2012-09-28 03:22AM | 1557657-1 | DFC2 | Rural Short | Other | 2 | 92.5 | 185 | 0.00020667 | 2.2342e-06
2012-12-04 07:31AM | 1578503-1 | 7091 | Rural Short | Other | 12 | 191.5 | 2298 | 0.0025671 | 1.3405e-05
2012-08-17 02:08PM | 1546796-1 | 2819 | Urban | Weather | 1 | 194 | 194 | 0.00021672 | 1.1171e-06
2012-12-20 04:35PM | 1579503-1 | 2819 | Urban | Vegetation | 1484 | 69.1988 | 102691 | 0.11472 | 0.0016578
2013-04-17 01:18PM | 1611001-1 | 2819 | Urban | Equipment Failure | 90 | 80.7778 | 7270 | 0.0081215 | 0.00010054
2013-01-13 04:10PM | 1584389-1 | 2819 | Urban | Vegetation | 773 | 89 | 68797 | 0.076855 | 0.00086353
2012-09-22 02:17PM | 1556438-1 | 2819 | Urban | Equipment Failure | 1 | 89 | 89 | 9.9424e-05 | 1.1171e-06
2012-08-17 12:33PM | 1546655-1 | 2820 | Urban | Weather | 20 | 240.05 | 4801 | 0.0053633 | 2.2342e-05
2012-11-07 08:04PM | 1567943-1 | 2820 | Urban | Other | 10 | 55 | 550 | 0.00061442 | 1.1171e-05
2013-01-11 09:13AM | 1583972-1 | 2820 | Urban | Vegetation | 82 | 210.6098 | 17270 | 0.019293 | 9.1604e-05
2013-01-18 04:00PM | 1586192-1 | 2820 | Urban | Equipment Failure | 44 | 233.9318 | 10293 | 0.011499 | 4.9153e-05
2013-02-17 08:18AM | 1594920-1 | 2820 | Urban | Equipment Failure | 1 | 66 | 66 | 7.373e-05 | 1.1171e-06
2012-07-04 05:45PM | 1535694-1 | 2825 | Urban | Operatonal Error | 1 | 128 | 128 | 0.00014299 | 1.1171e-06
2013-01-30 07:09PM | 1590126-1 | 2825 | Urban | Third Party Impacts | 3 | 120 | 360 | 0.00040216 | 3.3514e-06
2013-02-22 09:54PM | 1596548-1 | 2825 | Urban | Third Party Impacts | 90 | 39.5333 | 3558 | 0.0039747 | 0.00010054
2013-03-18 07:02AM | 1604266-1 | 2828 | Urban | Equipment Failure | 23 | 228 | 5244 | 0.0058582 | 2.5694e-05
2013-01-03 05:04PM | 1582098-1 | 2828 | Urban | Vegetation | 427 | 38.1148 | 16275 | 0.018181 | 0.00047701
2013-03-19 03:02PM | 1604604-1 | 2829 | Urban | Equipment Failure | 39 | 178 | 6942 | 0.007755 | 4.3568e-05
2013-01-18 06:31PM | 1586317-1 | 2829 | Urban | Weather | 27 | 237.2222 | 6405 | 0.0071552 | 3.0162e-05
2012-11-02 11:18PM | 1566719-1 | 2829 | Urban | Third Party Impacts | 22 | 453.5455 | 9978 | 0.011147 | 2.4577e-05
2013-01-04 04:04PM | 1582389-1 | 2829 | Urban | Equipment Failure | 1 | 459 | 459 | 0.00051276 | 1.1171e-06
2013-01-18 02:45AM | 1585832-1 | 2829 | Urban | Other | 128 | 50.9297 | 6519 | 0.0072825 | 0.00014299
2013-01-29 12:15PM | 1589688-1 | 2829 | Urban | Equipment Failure | 99 | 176 | 17424 | 0.019465 | 0.00011059
2013-03-11 05:54AM | 1602462-1 | 7994 | Urban | Other | 68 | 107.3529 | 7300 | 0.008155 | 7.5964e-05
2013-02-19 04:55PM | 1595538-1 | 7994 | Urban | Third Party Impacts | 33 | 43.1515 | 1424 | 0.0015908 | 3.6865e-05
2012-08-27 01:01PM | 1549734-1 | 7994 | Urban | Other | 12 | 299.75 | 3597 | 0.0040183 | 1.3405e-05
2012-09-02 07:40AM | 1551234-1 | 7994 | Urban | Other | 1 | 372 | 372 | 0.00041557 | 1.1171e-06
2012-11-07 06:29PM | 1567927-1 | 7994 | Urban | Equipment Failure | 1 | 241 | 241 | 0.00026923 | 1.1171e-06
2013-06-25 06:57PM | 1628054-1 | 2806 | Urban | Equipment Failure | 21 | 55.0476 | 1156 | 0.0012914 | 2.346e-05
2013-03-02 11:47AM | 1600178-1 | 2806 | Urban | Equipment Failure | 1276 | 72.2978 | 92252 | 0.10306 | 0.0014254
2013-04-07 11:45PM | 1608486-1 | 2807 | Urban | Equipment Failure | 39 | 175.6923 | 6852 | 0.0076545 | 4.3568e-05
2013-04-08 07:20AM | 1608493-1 | 2807 | Urban | Equipment Failure | 21 | 358 | 7518 | 0.0083985 | 2.346e-05
2013-06-13 01:25PM | 1624931-1 | 2807 | Urban | Third Party Impacts | 27 | 189.3704 | 5113 | 0.0057118 | 3.0162e-05
2012-08-03 08:52AM | 1542536-1 | 2807 | Urban | Third Party Impacts | 2277 | 33.9504 | 77305 | 0.086359 | 0.0025437
2012-12-26 06:55AM | 1580625-1 | 2807 | Urban | Equipment Failure | 31 | 142.6774 | 4423 | 0.004941 | 3.4631e-05
2012-12-26 10:02AM | 1580649-1 | 2807 | Urban | Equipment Failure | 31 | 50 | 1550 | 0.0017315 | 3.4631e-05
2013-02-09 05:28PM | 1593103-1 | 2807 | Urban | Equipment Failure | 1 | 176 | 176 | 0.00019661 | 1.1171e-06
2012-08-17 11:48AM | 1546558-1 | 2809 | Urban | Weather | 606 | 43.9637 | 26642 | 0.029762 | 0.00067697
2012-12-02 03:14PM | 1574789-1 | 2809 | Urban | Equipment Failure | 33 | 115 | 3795 | 0.0042395 | 3.6865e-05
2013-03-10 09:44AM | 1602346-1 | 5496 | Urban | Other | 52 | 132 | 6864 | 0.0076679 | 5.809e-05
2012-07-09 07:45PM | 1536712-1 | 5496 | Urban | Equipment Failure | 60 | 134.5 | 8070 | 0.0090152 | 6.7027e-05
2012-12-29 08:02PM | 1581336-1 | 5496 | Urban | Equipment Failure | 1 | 132 | 132 | 0.00014746 | 1.1171e-06
2013-03-02 01:22AM | 1600114-1 | 5496 | Urban | Equipment Failure | 312 | 203.4455 | 63475 | 0.070909 | 0.00034854
2012-07-20 10:01PM | 1539434-1 | 5498 | Urban | Equipment Failure | 1 | 142 | 142 | 0.00015863 | 1.1171e-06
2013-03-26 04:45PM | 1606448-1 | F601 | Urban | Third Party Impacts | 57 | 319.8947 | 18234 | 0.02037 | 6.3676e-05
2012-07-04 12:24PM | 1535551-1 | F602 | Urban | Equipment Failure | 70 | 84.2714 | 5899 | 0.0065899 | 7.8198e-05
2013-06-25 10:53PM | 1628112-1 | F602 | Urban | Equipment Failure | 41 | 101 | 4141 | 0.004626 | 4.5802e-05
2012-12-13 07:05AM | 1577562-1 | F603 | Urban | Equipment Failure | 1 | 275 | 275 | 0.00030721 | 1.1171e-06
2012-10-23 02:17PM | 1564015-1 | F603 | Urban | Other | 71 | 124.338 | 8828 | 0.0098619 | 7.9316e-05
2013-02-13 12:25PM | 1594115-1 | 54656 | Urban | Third Party Impacts | 1 | 95 | 95 | 0.00010613 | 1.1171e-06
2012-08-12 05:01PM | 1545216-1 | 54695 | Urban | Other | 1 | 34 | 34 | 3.7982e-05 | 1.1171e-06
2012-11-29 03:47PM | 1573984-1 | NE1216 | Urban | Other | 2 | 123 | 246 | 0.00027481 | 2.2342e-06
2012-11-30 03:00PM | 1574289-1 | 55354 | Rural Short | Equipment Failure | 17 | 112.4706 | 1912 | 0.0021359 | 1.8991e-05
2012-09-05 04:37PM | 1552124-1 | 55354 | Rural Short | Other | 1 | 39 | 39 | 4.3568e-05 | 1.1171e-06
2012-09-05 02:46PM | 1552043-1 | 55354 | Rural Short | Weather | 382 | 102 | 38964 | 0.043527 | 0.00042674
2013-03-05 06:17AM | 1600789-1 | 55354 | Rural Short | Equipment Failure | 385 | 16 | 6160 | 0.0068815 | 0.00043009
2013-01-01 04:47PM | 1581641-1 | 55354 | Rural Short | Vegetation | 1059 | 29.6166 | 31364 | 0.035037 | 0.001183
2013-04-09 10:29AM | 1608828-1 | 55354 | Rural Short | Equipment Failure | 55 | 0.72727 | 40 | 4.4685e-05 | 6.1442e-05
2013-01-09 02:14AM | 1583468-1 | 55361 | Urban | Vegetation | 13 | 176.3846 | 2293 | 0.0025616 | 1.4523e-05
2012-08-26 08:19AM | 1549517-1 | 55361 | Urban | Other | 17 | 111.6471 | 1898 | 0.0021203 | 1.8991e-05
2013-05-01 11:17AM | 1614151-1 | C851 | Urban | Other | 17 | 92 | 1564 | 0.0017472 | 1.8991e-05
2013-01-02 07:38PM | 1581904-1 | C851 | Urban | Animals | 888 | 18.3164 | 16265 | 0.01817 | 0.000992
2013-03-20 07:02PM | 1605013-1 | C854 | Urban | Other | 58 | 75 | 4350 | 0.0048595 | 6.4793e-05
2013-02-26 12:20AM | 1598436-1 | FF1217 | Urban | Third Party Impacts | 11 | 473.3636 | 5207 | 0.0058168 | 1.2288e-05
2012-12-23 07:26PM | 1579997-1 | FF1217 | Urban | Other | 1 | 231 | 231 | 0.00025805 | 1.1171e-06
2012-10-28 02:00PM | 1565226-1 | FF1243 | Urban | Equipment Failure | 80 | 90.575 | 7246 | 0.0080947 | 8.937e-05
2012-12-20 08:45AM | 1579307-1 | FF1269 | Urban | Equipment Failure | 10 | 157.5 | 1575 | 0.0017595 | 1.1171e-05
2013-01-11 03:36PM | 1584160-1 | FF1269 | Urban | Third Party Impacts | 37 | 120.027 | 4441 | 0.0049611 | 4.1333e-05
2012-08-17 02:01PM | 1546787-1 | FF1280 | Urban | Weather | 1 | 317 | 317 | 0.00035413 | 1.1171e-06
2012-08-18 12:18AM | 1547110-1 | FF1280 | Urban | Other | 2 | 68 | 136 | 0.00015193 | 2.2342e-06
2013-04-20 07:12AM | 1611680-1 | FT1203 | Urban | Other | 28 | 19 | 532 | 0.00059431 | 3.1279e-05
2013-03-31 07:57PM | 1607173-1 | FT1204 | Urban | Animals | 64 | 46 | 2944 | 0.0032888 | 7.1496e-05
2013-04-09 12:21PM | 1608866-1 | FT1206 | Urban | Equipment Failure | 301 | 31.6312 | 9521 | 0.010636 | 0.00033625
2013-06-26 02:05PM | 1628357-1 | FT1206 | Urban | Other | 1 | 71 | 71 | 7.9316e-05 | 1.1171e-06
2013-01-22 08:56PM | 1587525-1 | FT1206 | Urban | Weather | 1 | 75 | 75 | 8.3784e-05 | 1.1171e-06
2013-01-22 10:00PM | 1592404-1 | FT1206 | Urban | Weather | 1 | 975 | 975 | 0.0010892 | 1.1171e-06
2013-02-20 06:24PM | 1595863-1 | FT1206 | Urban | Other | 54 | 46.8148 | 2528 | 0.0028241 | 6.0324e-05
2013-05-10 11:20AM | 1616337-1 | FT1208 | Urban | Equipment Failure | 33 | 19.9091 | 657 | 0.00073395 | 3.6865e-05
2013-03-22 03:56PM | 1605558-1 | FT1208 | Urban | Animals | 55 | 172 | 9460 | 0.010568 | 6.1442e-05
2013-04-06 03:44PM | 1608323-1 | FT1209 | Urban | Other | 93 | 39 | 3627 | 0.0040518 | 0.00010389
2013-04-07 10:34AM | 1608428-1 | FT1209 | Urban | Equipment Failure | 93 | 98.6022 | 9170 | 0.010244 | 0.00010389
2013-04-12 11:23PM | 1610060-1 | FT1210 | Urban | Other | 20 | 110 | 2200 | 0.0024577 | 2.2342e-05
2012-08-10 01:25PM | 1547722-1 | GG1232 | Rural Short | Weather | 1215 | 72.0486 | 87539 | 0.097792 | 0.0013573
2013-01-16 05:27PM | 1585471-1 | GG1232 | Rural Short | Equipment Failure | 1232 | 11.9968 | 14780 | 0.016511 | 0.0013763
2013-06-25 12:34PM | 1627898-1 | GG1232 | Rural Short | Other | 1 | 131 | 131 | 0.00014634 | 1.1171e-06
2012-10-02 11:16AM | 1558335-1 | GG1232 | Rural Short | Equipment Failure | 6 | 175.6667 | 1054 | 0.0011774 | 6.7027e-06
2012-07-03 09:22PM | 1535393-1 | GG1232 | Rural Short | Equipment Failure | 39 | 99.5128 | 3881 | 0.0043355 | 4.3568e-05
2013-01-19 07:23PM | 1586664-1 | GG1232 | Rural Short | Equipment Failure | 5 | 350.2 | 1751 | 0.0019561 | 5.5856e-06
2013-01-11 02:50AM | 1583930-1 | GG1232 | Rural Short | Equipment Failure | 81 | 70.9259 | 5745 | 0.0064179 | 9.0487e-05
2013-03-17 03:21PM | 1604173-1 | GG1232 | Rural Short | Equipment Failure | 14 | 22 | 308 | 0.00034407 | 1.564e-05
2012-12-11 02:29PM | 1577115-1 | GG1232 | Rural Short | Equipment Failure | 1 | 173 | 173 | 0.00019326 | 1.1171e-06
2013-02-25 05:26AM | 1597787-1 | GG1232 | Rural Short | Weather | 1 | 313 | 313 | 0.00034966 | 1.1171e-06
2012-08-10 01:25PM | 1547722-1 | GG1258 | Urban | Weather | 1192 | 72.0336 | 85864 | 0.09592 | 0.0013316
2013-01-16 05:27PM | 1585471-1 | GG1258 | Urban | Equipment Failure | 1208 | 12.0008 | 14497 | 0.016195 | 0.0013495
2013-01-29 04:21AM | 1589462-1 | GG1258 | Urban | Weather | 1024 | 291.1191 | 298106 | 0.33302 | 0.0011439
2013-01-16 05:27PM | 1585471-1 | GG1269 | Rural Short | Equipment Failure | 1127 | 12 | 13524 | 0.015108 | 0.001259
2013-05-01 06:35AM | 1614066-1 | GG1269 | Rural Short | Vegetation | 3 | 294 | 882 | 0.0009853 | 3.3514e-06
2013-03-02 06:12PM | 1600238-1 | GG1269 | Rural Short | Equipment Failure | 34 | 205.1471 | 6975 | 0.0077919 | 3.7982e-05
2013-04-20 08:05AM | 1611689-1 | GG1269 | Rural Short | Weather | 40 | 172.25 | 6890 | 0.007697 | 4.4685e-05
2012-09-28 06:28PM | 1557964-1 | GG1269 | Rural Short | Other | 4 | 127.5 | 510 | 0.00056973 | 4.4685e-06
2013-01-30 06:08AM | 1589980-1 | GG1269 | Rural Short | Equipment Failure | 561 | 289 | 162129 | 0.18112 | 0.0006267
2013-02-11 07:44AM | 1593418-1 | GG1269 | Rural Short | Equipment Failure | 1 | 306 | 306 | 0.00034184 | 1.1171e-06
2012-08-10 01:25PM | 1547722-1 | GG1295 | Rural Short | Weather | 293 | 72.0717 | 21117 | 0.02359 | 0.00032732
2013-01-16 05:27PM | 1585471-1 | GG1295 | Rural Short | Equipment Failure | 297 | 12.0034 | 3565 | 0.0039825 | 0.00033178
2013-01-13 04:16PM | 1584393-1 | GG1295 | Rural Short | Weather | 136 | 1.4632 | 199 | 0.00022231 | 0.00015193
2013-03-28 12:31PM | 1606850-1 | GG1295 | Rural Short | Vegetation | 136 | 15.5074 | 2109 | 0.002356 | 0.00015193
2013-04-26 05:29AM | 1613006-1 | GG1295 | Rural Short | Vegetation | 136 | 28.3971 | 3862 | 0.0043143 | 0.00015193
2013-05-02 05:59AM | 1614348-1 | GG1295 | Rural Short | Operatonal Error | 1 | 130 | 130 | 0.00014523 | 1.1171e-06
2012-09-07 05:24PM | 1552955-1 | GG1295 | Rural Short | Equipment Failure | 5 | 85 | 425 | 0.00047478 | 5.5856e-06
2012-07-30 04:31PM | 1541452-1 | GG1295 | Rural Short | Equipment Failure | 4 | 93.75 | 375 | 0.00041892 | 4.4685e-06
2013-01-28 03:30PM | 1589292-1 | GG1295 | Rural Short | Weather | 2 | 122 | 244 | 0.00027258 | 2.2342e-06
2013-04-01 11:39AM | 1607213-1 | GG1295 | Rural Short | Vegetation | 91 | 107 | 9737 | 0.010877 | 0.00010166
2013-06-06 09:19PM | 1623563-1 | L941 | Rural Short | Other | 111 | 2.8739 | 319 | 0.00035636 | 0.000124
2012-11-24 01:59AM | 1572384-1 | L942 | Rural Short | Equipment Failure | 45 | 119 | 5355 | 0.0059822 | 5.027e-05
2012-12-09 07:36PM | 1576675-1 | L942 | Rural Short | Other | 45 | 61 | 2745 | 0.0030665 | 5.027e-05
2013-02-01 02:20PM | 1590702-1 | L942 | Rural Short | Weather | 465 | 91 | 42315 | 0.047271 | 0.00051946
2013-05-22 06:24PM | 1619475-1 | L946 | Rural Short | Vegetation | 19 | 74 | 1406 | 0.0015707 | 2.1225e-05
2012-12-24 06:02PM | 1580226-1 | L946 | Rural Short | Other | 17 | 263.1765 | 4474 | 0.004998 | 1.8991e-05
2013-01-18 09:51PM | 1586502-1 | L946 | Rural Short | Weather | 4 | 236.25 | 945 | 0.0010557 | 4.4685e-06
2012-11-26 06:52PM | 1572935-1 | L946 | Rural Short | Weather | 1 | 42 | 42 | 4.6919e-05 | 1.1171e-06
2012-12-24 04:26PM | 1580165-1 | L946 | Rural Short | Weather | 257 | 6.9144 | 1777 | 0.0019851 | 0.0002871
2013-01-21 09:32AM | 1586871-1 | L946 | Rural Short | Vegetation | 257 | 55.1595 | 14176 | 0.015836 | 0.0002871
2012-08-17 05:06PM | 1547025-1 | L946 | Rural Short | Weather | 39 | 63.5128 | 2477 | 0.0027671 | 4.3568e-05
2013-03-16 04:08PM | 1604008-1 | L947 | Rural Short | Equipment Failure | 28 | 90 | 2520 | 0.0028151 | 3.1279e-05
2012-11-30 06:03PM | 1574412-1 | L947 | Rural Short | Weather | 2 | 556 | 1112 | 0.0012422 | 2.2342e-06
2012-10-17 01:11PM | 1562476-1 | L947 | Rural Short | Other | 9 | 38 | 342 | 0.00038206 | 1.0054e-05
2012-11-30 08:41PM | 1574495-1 | L947 | Rural Short | Weather | 3 | 755.3333 | 2266 | 0.0025314 | 3.3514e-06
2012-08-29 01:23PM | 1550330-1 | L947 | Rural Short | Other | 235 | 31.6809 | 7445 | 0.008317 | 0.00026252
2012-10-20 01:33PM | 1563305-1 | L947 | Rural Short | Other | 70 | 145.9571 | 10217 | 0.011414 | 7.8198e-05
2013-06-02 06:41PM | 1622392-1 | L947 | Rural Short | Operatonal Error | 482 | 17.4813 | 8426 | 0.0094129 | 0.00053845
2012-08-26 09:48AM | 1549535-1 | GV1223 | Urban | Equipment Failure | 1 | 176 | 176 | 0.00019661 | 1.1171e-06
2012-08-17 01:09PM | 1546720-1 | GV1234 | Urban | Equipment Failure | 108 | 120.5648 | 13021 | 0.014546 | 0.00012065
2012-08-09 04:56PM | 1544218-1 | GV1241 | Urban | Vegetation | 85 | 149.0118 | 12666 | 0.014149 | 9.4955e-05
2012-08-17 12:57PM | 1546699-1 | GV1241 | Urban | Equipment Failure | 86 | 218 | 18748 | 0.020944 | 9.6072e-05
2012-08-17 01:26PM | 1546746-1 | GV1241 | Urban | Weather | 78 | 273.359 | 21322 | 0.023819 | 8.7135e-05
2012-09-05 08:13PM | 1552167-1 | GV1278 | Urban | Equipment Failure | 52 | 11.0769 | 576 | 0.00064346 | 5.809e-05
2013-04-12 11:39AM | 1609883-1 | GV1282 | Urban | Equipment Failure | 8 | 373 | 2984 | 0.0033335 | 8.937e-06
2013-01-12 09:31PM | 1584326-1 | GV1282 | Urban | Equipment Failure | 112 | 103.3661 | 11577 | 0.012933 | 0.00012512
2013-05-19 11:27AM | 1618589-1 | GV1282 | Urban | Third Party Impacts | 31 | 514 | 15934 | 0.0178 | 3.4631e-05
2012-11-22 02:40PM | 1571939-1 | GV1282 | Urban | Third Party Impacts | 11 | 180 | 1980 | 0.0022119 | 1.2288e-05
2012-09-25 01:41PM | 1556936-1 | 7962 | Urban | Equipment Failure | 1 | 66 | 66 | 7.373e-05 | 1.1171e-06
2012-09-15 12:21PM | 1554804-1 | 7962 | Urban | Equipment Failure | 41 | 45 | 1845 | 0.0020611 | 4.5802e-05
2012-09-13 06:37PM | 1554447-1 | 7962 | Urban | Equipment Failure | 852 | 111.6162 | 95097 | 0.10623 | 0.00095179
2012-11-30 06:50PM | 1574448-1 | 7962 | Urban | Weather | 793 | 98.9382 | 78458 | 0.087647 | 0.00088588
2012-09-16 12:08AM | 1554855-1 | 7962 | Urban | Equipment Failure | 952 | 216.0221 | 205653 | 0.22974 | 0.0010635
2012-09-21 06:17PM | 1558515-1 | 7962 | Urban | Operatonal Error | 951 | 3.0011 | 2854 | 0.0031883 | 0.0010624
2012-10-11 01:16PM | 1564032-1 | 7962 | Urban | Third Party Impacts | 952 | 4.9989 | 4759 | 0.0053164 | 0.0010635
2012-09-16 12:08AM | 1554855-1 | 7964 | Urban | Equipment Failure | 322 | 216.1429 | 69598 | 0.077749 | 0.00035971
2012-09-21 06:17PM | 1558515-1 | 7964 | Urban | Operatonal Error | 322 | 3 | 966 | 0.0010791 | 0.00035971
2012-10-11 01:16PM | 1564032-1 | 7964 | Urban | Third Party Impacts | 322 | 5.0031 | 1611 | 0.0017997 | 0.00035971
2012-10-11 01:27PM | 1560655-1 | 7966 | Urban | Other | 485 | 51.099 | 24783 | 0.027686 | 0.0005418
2012-09-16 12:08AM | 1554855-1 | 7966 | Urban | Equipment Failure | 580 | 215.8276 | 125180 | 0.13984 | 0.00064793
2012-09-21 06:17PM | 1558515-1 | 7966 | Urban | Operatonal Error | 579 | 3 | 1737 | 0.0019404 | 0.00064681
2012-10-11 01:16PM | 1564032-1 | 7966 | Urban | Third Party Impacts | 579 | 5.0035 | 2897 | 0.0032363 | 0.00064681
2012-09-16 12:08AM | 1554855-1 | 7967 | Urban | Equipment Failure | 109 | 215.055 | 23441 | 0.026186 | 0.00012177
2012-09-21 06:17PM | 1558515-1 | 7967 | Urban | Operatonal Error | 108 | 3.0093 | 325 | 0.00036306 | 0.00012065
2012-10-11 01:16PM | 1564032-1 | 7967 | Urban | Third Party Impacts | 108 | 5.0185 | 542 | 0.00060548 | 0.00012065
2012-11-30 05:12PM | 1574380-1 | 7970 | Urban | Equipment Failure | 67 | 125.0746 | 8380 | 0.0093615 | 7.4847e-05
2012-08-17 02:29PM | 1546858-1 | 7970 | Urban | Weather | 52 | 324.3077 | 16864 | 0.018839 | 5.809e-05
2012-11-16 09:33AM | 1570295-1 | 7970 | Urban | Equipment Failure | 29 | 369 | 10701 | 0.011954 | 3.2396e-05
2013-01-18 02:44PM | 1586098-1 | 7970 | Urban | Equipment Failure | 730 | 109.7753 | 80136 | 0.089522 | 0.0008155
2013-02-16 06:26PM | 1594890-1 | 7970 | Urban | Equipment Failure | 729 | 25 | 18225 | 0.02036 | 0.00081438
2012-12-02 03:46PM | 1574795-1 | 7970 | Urban | Equipment Failure | 130 | 98.1077 | 12754 | 0.014248 | 0.00014523
2012-09-16 12:08AM | 1554855-1 | 7970 | Urban | Equipment Failure | 818 | 215.9584 | 176654 | 0.19734 | 0.0009138
2012-09-21 06:17PM | 1558515-1 | 7970 | Urban | Operatonal Error | 817 | 3.0012 | 2452 | 0.0027392 | 0.00091269
2012-10-11 01:16PM | 1564032-1 | 7970 | Urban | Third Party Impacts | 818 | 4.9976 | 4088 | 0.0045668 | 0.0009138
2012-12-03 10:47AM | 1574981-1 | 7972 | Urban | Equipment Failure | 595 | 51.4706 | 30625 | 0.034212 | 0.00066469
2012-09-16 12:08AM | 1554855-1 | 7972 | Urban | Equipment Failure | 668 | 215.9746 | 144271 | 0.16117 | 0.00074624
2012-09-21 06:17PM | 1558515-1 | 7972 | Urban | Operatonal Error | 667 | 3.0015 | 2002 | 0.0022365 | 0.00074512
2012-10-11 01:16PM | 1564032-1 | 7972 | Urban | Third Party Impacts | 668 | 4.9985 | 3339 | 0.0037301 | 0.00074624
2012-09-16 12:08AM | 1554855-1 | 7973 | Urban | Equipment Failure | 348 | 215.9655 | 75156 | 0.083958 | 0.00038876
2012-09-21 06:17PM | 1558515-1 | 7973 | Urban | Operatonal Error | 348 | 2.9971 | 1043 | 0.0011652 | 0.00038876
2012-10-11 01:16PM | 1564032-1 | 7973 | Urban | Third Party Impacts | 348 | 4.9971 | 1739 | 0.0019427 | 0.00038876
2013-06-24 06:53AM | 1627384-1 | 7974 | Urban | Equipment Failure | 29 | 27.1724 | 788 | 0.00088029 | 3.2396e-05
2012-09-16 12:08AM | 1554855-1 | 7974 | Urban | Equipment Failure | 1038 | 216.0511 | 224261 | 0.25053 | 0.0011596
2012-09-21 06:17PM | 1558515-1 | 7974 | Urban | Operatonal Error | 1037 | 3.001 | 3112 | 0.0034765 | 0.0011585
2012-10-11 01:16PM | 1564032-1 | 7974 | Urban | Third Party Impacts | 1038 | 5 | 5190 | 0.0057979 | 0.0011596
2013-03-12 06:32PM | 1602975-1 | 7976 | Urban | Equipment Failure | 73 | 154 | 11242 | 0.012559 | 8.155e-05
2012-09-07 02:32PM | 1552817-1 | 7976 | Urban | Equipment Failure | 47 | 181 | 8507 | 0.0095033 | 5.2505e-05
2013-06-24 05:11AM | 1627383-1 | 7976 | Urban | Other | 47 | 136 | 6392 | 0.0071406 | 5.2505e-05
2013-06-30 07:26AM | 1629328-1 | 7976 | Urban | Equipment Failure | 1219 | 7.9385 | 9677 | 0.01081 | 0.0013618
2012-09-16 12:08AM | 1554855-1 | 7976 | Urban | Equipment Failure | 1363 | 215.9516 | 294342 | 0.32882 | 0.0015226
2012-09-21 06:17PM | 1558515-1 | 7976 | Urban | Operatonal Error | 1362 | 2.9993 | 4085 | 0.0045634 | 0.0015215
2012-10-11 01:16PM | 1564032-1 | 7976 | Urban | Third Party Impacts | 1362 | 5.0015 | 6812 | 0.0076098 | 0.0015215
2012-08-21 11:15AM | 1547698-1 | 7976 | Urban | Equipment Failure | 37 | 296.0541 | 10954 | 0.012237 | 4.1333e-05
2013-04-29 08:52AM | 1613558-1 | 7977 | Urban | Third Party Impacts | 4 | 110 | 440 | 0.00049153 | 4.4685e-06
2013-05-21 09:11AM | 1618963-1 | 7977 | Urban | Other | 1 | 65 | 65 | 7.2613e-05 | 1.1171e-06
2013-02-20 05:10PM | 1595849-1 | 7977 | Urban | Third Party Impacts | 4 | 338.75 | 1355 | 0.0015137 | 4.4685e-06
2012-09-16 12:08AM | 1554855-1 | 7977 | Urban | Equipment Failure | 160 | 215.9812 | 34557 | 0.038604 | 0.00017874
2012-09-21 06:17PM | 1558515-1 | 7977 | Urban | Operatonal Error | 160 | 3 | 480 | 0.00053622 | 0.00017874
2012-11-30 04:12PM | 1574329-1 | 48189 | Urban | Weather | 2397 | 50.1665 | 120249 | 0.13433 | 0.0026777
2013-01-18 08:37PM | 1586427-1 | 48196 | Rural Short | Vegetation | 17 | 782.2941 | 13299 | 0.014857 | 1.8991e-05
2013-05-30 02:14PM | 1621715-1 | 48196 | Rural Short | Operatonal Error | 6 | 112 | 672 | 0.0007507 | 6.7027e-06
2013-06-02 11:32AM | 1622309-1 | 48196 | Rural Short | Equipment Failure | 6 | 101 | 606 | 0.00067697 | 6.7027e-06
2013-01-28 12:28AM | 1589183-1 | 48196 | Rural Short | Third Party Impacts | 14 | 451 | 6314 | 0.0070535 | 1.564e-05
2012-08-17 01:40PM | 1546758-1 | 48196 | Rural Short | Weather | 735 | 234.3578 | 172253 | 0.19243 | 0.00082108
2013-04-15 08:35PM | 1610508-1 | 48196 | Rural Short | Weather | 746 | 276.3995 | 206194 | 0.23034 | 0.00083337
2012-09-18 11:09AM | 1555336-1 | 48203 | Urban | Other | 40 | 21 | 840 | 0.00093838 | 4.4685e-05
2013-02-05 02:02PM | 1591749-1 | 48203 | Urban | Operatonal Error | 1 | 149 | 149 | 0.00016645 | 1.1171e-06
2013-02-25 09:48AM | 1597927-1 | 48203 | Urban | Equipment Failure | 470 | 396.366 | 186292 | 0.20811 | 0.00052505
2013-06-20 08:19AM | 1626499-1 | 48205 | Urban | Equipment Failure | 20 | 41.35 | 827 | 0.00092386 | 2.2342e-05
2013-01-13 12:56PM | 1584365-1 | 48205 | Urban | Other | 15 | 145.8667 | 2188 | 0.0024443 | 1.6757e-05
2012-08-17 01:25PM | 1546744-1 | 3106 | Urban | Weather | 7 | 247.8571 | 1735 | 0.0019382 | 7.8198e-06
2013-02-10 10:28PM | 1593389-1 | HR1206 | Urban | Equipment Failure | 111 | 86 | 9546 | 0.010664 | 0.000124
2012-10-23 05:59AM | 1563783-1 | HR1210 | Urban | Other | 1469 | 51.7665 | 76045 | 0.084951 | 0.001641
2013-04-05 05:17PM | 1608201-1 | HR1243 | Urban | Other | 69 | 41 | 2829 | 0.0031603 | 7.7081e-05
2013-01-27 08:22AM | 1589044-1 | HR1247 | Urban | Weather | 23 | 97 | 2231 | 0.0024923 | 2.5694e-05
2013-02-21 02:33PM | 1596200-1 | HR1269 | Urban | Other | 1 | 61 | 61 | 6.8144e-05 | 1.1171e-06
2012-10-28 11:28AM | 1565213-1 | HR1269 | Urban | Equipment Failure | 87 | 128.3908 | 11170 | 0.012478 | 9.7189e-05
2012-11-25 08:18PM | 1572541-1 | HR1269 | Urban | Other | 53 | 57.6038 | 3053 | 0.0034106 | 5.9207e-05
2013-04-25 10:53AM | 1612957-1 | HR1269 | Urban | Equipment Failure | 21 | 69 | 1449 | 0.0016187 | 2.346e-05
2012-12-31 12:49PM | 1581497-1 | HR1269 | Urban | Third Party Impacts | 2124 | 103.9402 | 220769 | 0.24663 | 0.0023728
2013-01-12 01:50PM | 1584274-1 | HR1276 | Urban | Equipment Failure | 65 | 84.9231 | 5520 | 0.0061665 | 7.2613e-05
2013-01-02 09:30AM | 1581716-1 | 35442 | Urban | Equipment Failure | 34 | 297.5 | 10115 | 0.0113 | 3.7982e-05
2013-04-13 11:53AM | 1610109-1 | 35443 | Urban | Third Party Impacts | 32 | 43 | 1376 | 0.0015372 | 3.5748e-05
2013-04-21 02:19PM | 1611821-1 | 35443 | Urban | Other | 38 | 22.7895 | 866 | 0.00096743 | 4.2451e-05
2012-11-19 08:12PM | 1571049-1 | 35444 | Urban | Third Party Impacts | 143 | 62.2098 | 8896 | 0.0099379 | 0.00015975
2012-12-19 06:10PM | 1579174-1 | A314 | Urban | Vegetation | 13 | 163.4615 | 2125 | 0.0023739 | 1.4523e-05
2013-03-28 02:52PM | 1606880-1 | A315 | Urban | Other | 1 | 313 | 313 | 0.00034966 | 1.1171e-06
2013-04-30 11:19AM | 1613889-1 | A315 | Urban | Other | 1 | 144 | 144 | 0.00016087 | 1.1171e-06
2013-04-10 02:45PM | 1609254-1 | A317 | Urban | Vegetation | 77 | 53 | 4081 | 0.004559 | 8.6018e-05
2012-10-24 06:23AM | 1564126-1 | A322 | Urban | Other | 82 | 86.1585 | 7065 | 0.0078925 | 9.1604e-05
2013-03-15 06:51PM | 1603905-1 | A324 | Urban | Vegetation | 55 | 92 | 5060 | 0.0056526 | 6.1442e-05
2013-01-01 06:09AM | 1581593-1 | A324 | Urban | Other | 21 | 25.3333 | 532 | 0.00059431 | 2.346e-05
2013-02-03 07:16PM | 1591191-1 | A324 | Urban | Other | 57 | 96 | 5472 | 0.0061129 | 6.3676e-05
2012-08-28 11:04AM | 1549975-1 | A325 | Urban | Equipment Failure | 102 | 324.1471 | 33063 | 0.036935 | 0.00011395
2013-03-26 01:59PM | 1606363-1 | A325 | Urban | Equipment Failure | 40 | 59.8 | 2392 | 0.0026722 | 4.4685e-05
2012-10-16 07:55AM | 1562033-1 | A325 | Urban | Equipment Failure | 33 | 173 | 5709 | 0.0063776 | 3.6865e-05
2012-08-12 04:25PM | 1545206-1 | 8711 | Rural Short | Other | 1 | 33 | 33 | 3.6865e-05 | 1.1171e-06
2013-01-18 02:08PM | 1586074-1 | 8711 | Rural Short | Equipment Failure | 62 | 333 | 20646 | 0.023064 | 6.9261e-05
2012-08-12 04:19PM | 1545205-1 | 8716 | Urban | Equipment Failure | 2231 | 65.8498 | 146911 | 0.16412 | 0.0024923
2012-11-08 04:30PM | 1568368-1 | 8718 | Urban | Weather | 195 | 153.8462 | 30000 | 0.033514 | 0.00021784
2012-08-10 01:18PM | 1544544-1 | 8721 | Urban | Other | 15 | 102.1333 | 1532 | 0.0017114 | 1.6757e-05
2012-09-13 05:02PM | 1554428-1 | HKA2 | Rural Short | Other | 3 | 143 | 429 | 0.00047924 | 3.3514e-06
2013-01-18 08:26PM | 1586419-1 | HKA2 | Rural Short | Equipment Failure | 2 | 192.5 | 385 | 0.00043009 | 2.2342e-06
2013-03-19 08:06PM | 1604675-1 | HKA2 | Rural Short | Other | 5 | 35.2 | 176 | 0.00019661 | 5.5856e-06
2013-01-29 10:21AM | 1589623-1 | HKA2 | Rural Short | Vegetation | 35 | 71 | 2485 | 0.002776 | 3.9099e-05
2013-05-28 06:37PM | 1621171-1 | HKA2 | Rural Short | Equipment Failure | 2 | 187 | 374 | 0.0004178 | 2.2342e-06
2013-04-15 05:59AM | 1610242-1 | HKA2 | Rural Short | Other | 1 | 433 | 433 | 0.00048371 | 1.1171e-06
2012-09-03 03:57PM | 1551524-1 | HKA2 | Rural Short | Equipment Failure | 36 | 72 | 2592 | 0.0028956 | 4.0216e-05
2013-05-28 03:21PM | 1621071-1 | HKA2 | Rural Short | Third Party Impacts | 74 | 78.9595 | 5843 | 0.0065273 | 8.2667e-05
2012-12-09 05:06PM | 1576662-1 | HKA2 | Rural Short | Vegetation | 378 | 43 | 16254 | 0.018158 | 0.00042227
2013-01-23 07:29AM | 1587569-1 | HKA2 | Rural Short | Operatonal Error | 378 | 2.5159 | 951 | 0.0010624 | 0.00042227
2013-04-08 04:05PM | 1608653-1 | HKA2 | Rural Short | Other | 378 | 2 | 756 | 0.00084454 | 0.00042227
2012-12-04 03:25PM | 1575383-1 | HKA2 | Rural Short | Other | 382 | 127.8796 | 48850 | 0.054571 | 0.00042674
2013-06-25 10:05AM | 1627780-1 | HKA2 | Rural Short | Weather | 14 | 84 | 1176 | 0.0013137 | 1.564e-05
2013-06-27 06:17PM | 1628834-1 | HKA2 | Rural Short | Equipment Failure | 13 | 199.3846 | 2592 | 0.0028956 | 1.4523e-05
2012-09-06 02:25AM | 1552192-1 | HKA2 | Rural Short | Weather | 458 | 52.0393 | 23834 | 0.026625 | 0.00051164
2013-04-08 05:14PM | 1608669-1 | HKA2 | Rural Short | Operatonal Error | 768 | 7 | 5376 | 0.0060056 | 0.00085795
2012-10-17 07:44PM | 1562673-1 | HKC2 | Rural Short | Equipment Failure | 26 | 807 | 20982 | 0.023439 | 2.9045e-05
2013-06-14 01:27PM | 1625291-1 | HKC2 | Rural Short | Equipment Failure | 63 | 63.6825 | 4012 | 0.0044819 | 7.0379e-05
2013-01-13 06:04PM | 1584471-1 | HKC2 | Rural Short | Equipment Failure | 803 | 176.6824 | 141876 | 0.15849 | 0.00089705
2013-01-18 06:38PM | 1586331-1 | HKC2 | Rural Short | Vegetation | 803 | 119 | 95557 | 0.10675 | 0.00089705
2013-06-24 09:55PM | 1627627-1 | HKC2 | Rural Short | Weather | 803 | 268.5156 | 215618 | 0.24087 | 0.00089705
2012-09-15 07:22AM | 1554773-1 | HKD2 | Rural Short | Other | 7 | 110 | 770 | 0.00086018 | 7.8198e-06
2013-01-18 01:36PM | 1586060-1 | HKE2 | Rural Short | Other | 933 | 14 | 13062 | 0.014592 | 0.0010423
2013-01-29 09:19PM | 1589876-1 | HKE2 | Rural Short | Third Party Impacts | 933 | 92.0793 | 85910 | 0.095972 | 0.0010423
2013-05-30 09:15AM | 1621574-1 | HKE2 | Rural Short | Equipment Failure | 74 | 57 | 4218 | 0.004712 | 8.2667e-05
2013-01-08 06:37PM | 1583361-1 | HKE2 | Rural Short | Equipment Failure | 45 | 102 | 4590 | 0.0051276 | 5.027e-05
2013-01-09 02:33PM | 1583642-1 | HKE2 | Rural Short | Equipment Failure | 70 | 167.0429 | 11693 | 0.013062 | 7.8198e-05
2012-10-01 10:58AM | 1558212-1 | HKE2 | Rural Short | Equipment Failure | 29 | 108.5172 | 3147 | 0.0035156 | 3.2396e-05
2013-01-04 03:04PM | 1582369-1 | HKE2 | Rural Short | Equipment Failure | 22 | 165 | 3630 | 0.0040551 | 2.4577e-05
2012-11-01 08:49PM | 1566497-1 | HKE2 | Rural Short | Other | 9 | 67.2222 | 605 | 0.00067586 | 1.0054e-05
2013-02-19 06:08AM | 1595285-1 | HKE2 | Rural Short | Animals | 9 | 306 | 2754 | 0.0030765 | 1.0054e-05
2013-01-08 06:39PM | 1583357-1 | HKE2 | Rural Short | Other | 1 | 100 | 100 | 0.00011171 | 1.1171e-06
2013-02-03 07:56PM | 1591196-1 | HKF2 | Urban | Equipment Failure | 1 | 75 | 75 | 8.3784e-05 | 1.1171e-06
2012-12-24 06:51PM | 1580249-1 | HKF2 | Urban | Weather | 103 | 93.1942 | 9599 | 0.010723 | 0.00011506
2012-08-10 08:41PM | 1544989-1 | HKF2 | Urban | Equipment Failure | 2 | 123.5 | 247 | 0.00027593 | 2.2342e-06
2012-09-25 10:21AM | 1556858-1 | HKF2 | Urban | Other | 1 | 89 | 89 | 9.9424e-05 | 1.1171e-06
2013-01-02 04:02AM | 1581670-1 | HKF2 | Urban | Animals | 2323 | 79.2333 | 184059 | 0.20562 | 0.0025951
2013-06-24 09:06PM | 1627609-1 | HKF2 | Urban | Weather | 2327 | 55.1998 | 128450 | 0.14349 | 0.0025995
2012-09-02 12:21PM | 1551285-1 | HKF2 | Urban | Equipment Failure | 91 | 5 | 455 | 0.00050829 | 0.00010166
2012-09-24 07:47AM | 1556615-1 | HKG2 | Urban | Other | 9 | 126.1111 | 1135 | 0.0012679 | 1.0054e-05
2012-09-24 05:35AM | 1556606-1 | HKG2 | Urban | Other | 1 | 258 | 258 | 0.00028822 | 1.1171e-06
2012-11-01 02:09PM | 1566327-1 | HKG2 | Urban | Vegetation | 96 | 25.9583 | 2492 | 0.0027839 | 0.00010724
2013-04-14 03:14AM | 1610173-1 | HKG2 | Urban | Other | 32 | 26 | 832 | 0.00092944 | 3.5748e-05
2012-12-12 05:40AM | 1577260-1 | HKG2 | Urban | Equipment Failure | 55 | 17 | 935 | 0.0010445 | 6.1442e-05
2013-01-22 04:21PM | 1587365-1 | HKG2 | Urban | Weather | 2726 | 101.036 | 275424 | 0.30768 | 0.0030453
2012-08-24 06:25AM | 1551596-1 | 77674 | Rural Short | Operatonal Error | 22 | 4.0909 | 90 | 0.00010054 | 2.4577e-05
2013-06-17 05:15PM | 1625844-1 | 77674 | Rural Short | Equipment Failure | 8 | 41.375 | 331 | 0.00036977 | 8.937e-06
2013-01-25 05:54AM | 1588104-1 | GG1295 | Rural Short | Equipment Failure | 7 | 195 | 1365 | 0.0015249 | 7.8198e-06
2013-04-05 09:01AM | 1608057-1 | S764 | Rural Short | Vegetation | 41 | 52 | 2132 | 0.0023817 | 4.5802e-05
2013-05-25 05:57PM | 1620304-1 | S764 | Rural Short | Other | 8 | 123 | 984 | 0.0010992 | 8.937e-06
2013-05-26 06:10PM | 1620383-1 | S764 | Rural Short | Equipment Failure | 8 | 94 | 752 | 0.00084007 | 8.937e-06
2012-12-02 03:40PM | 1574794-1 | S764 | Rural Short | Equipment Failure | 1 | 82 | 82 | 9.1604e-05 | 1.1171e-06
2013-01-06 03:27PM | 1582723-1 | S764 | Rural Short | Vegetation | 625 | 78.5264 | 49079 | 0.054827 | 0.0006982
2013-02-25 05:27PM | 1598285-1 | S764 | Rural Short | Weather | 625 | 162.3824 | 101489 | 0.11338 | 0.0006982
2012-08-22 09:09AM | 1547990-1 | S765 | Urban | Third Party Impacts | 12 | 194 | 2328 | 0.0026007 | 1.3405e-05
2012-08-22 08:24AM | 1547976-1 | S765 | Urban | Third Party Impacts | 5 | 275 | 1375 | 0.001536 | 5.5856e-06
2012-08-22 10:17AM | 1548031-1 | S765 | Urban | Third Party Impacts | 6 | 220 | 1320 | 0.0014746 | 6.7027e-06
2013-03-28 08:43PM | 1606972-1 | S765 | Urban | Vegetation | 74 | 47 | 3478 | 0.0038853 | 8.2667e-05
2013-02-25 03:27PM | 1598209-1 | S766 | Urban | Other | 17 | 39.7647 | 676 | 0.00075517 | 1.8991e-05
2013-06-21 02:08PM | 1626959-1 | S768 | Urban | Equipment Failure | 1 | 206 | 206 | 0.00023013 | 1.1171e-06
2013-06-18 08:23AM | 1625983-1 | S774 | Urban | Third Party Impacts | 21 | 94 | 1974 | 0.0022052 | 2.346e-05
2012-07-29 11:17AM | 1541125-1 | S775 | Urban | Third Party Impacts | 32 | 169.0625 | 5410 | 0.0060436 | 3.5748e-05
2013-02-22 02:24PM | 1596497-1 | S775 | Urban | Third Party Impacts | 89 | 334.6629 | 29785 | 0.033273 | 9.9424e-05
2013-05-30 11:20AM | 1621665-1 | S776 | Urban | Other | 1 | 165 | 165 | 0.00018432 | 1.1171e-06
2012-07-02 04:02PM | 1534945-1 | S776 | Urban | Other | 21 | 179.2857 | 3765 | 0.004206 | 2.346e-05
2012-07-02 03:44PM | 1534936-1 | S776 | Urban | Other | 20 | 350.65 | 7013 | 0.0078344 | 2.2342e-05
2013-03-12 03:03AM | 1602731-1 | S776 | Urban | Equipment Failure | 6 | 491 | 2946 | 0.003291 | 6.7027e-06
2013-06-21 08:34AM | 1626817-1 | L940 | Rural Short | Other | 12 | 61 | 732 | 0.00081773 | 1.3405e-05
2012-11-30 11:02PM | 1574512-1 | L940 | Rural Short | Weather | 6 | 1102.6667 | 6616 | 0.0073909 | 6.7027e-06
2012-08-17 06:19PM | 1547060-1 | L940 | Rural Short | Weather | 5 | 135.6 | 678 | 0.00075741 | 5.5856e-06
2012-11-30 06:09PM | 1574418-1 | L940 | Rural Short | Other | 8 | 427.75 | 3422 | 0.0038228 | 8.937e-06
2012-12-01 06:41AM | 1574551-1 | L940 | Rural Short | Weather | 4 | 840 | 3360 | 0.0037535 | 4.4685e-06
2013-01-02 12:08PM | 1581812-1 | L940 | Rural Short | Other | 550 | 155.1491 | 85332 | 0.095326 | 0.00061442
2012-08-17 02:35PM | 1546863-1 | L940 | Rural Short | Weather | 46 | 144.5217 | 6648 | 0.0074266 | 5.1388e-05
2012-12-19 04:41PM | 1579127-1 | L940 | Rural Short | Operatonal Error | 127 | 28.6142 | 3634 | 0.0040596 | 0.00014187
2012-11-30 06:01PM | 1574511-1 | L940 | Rural Short | Weather | 176 | 982.6591 | 172948 | 0.1932 | 0.00019661
2012-12-01 02:04AM | 1574532-1 | L940 | Rural Short | Weather | 550 | 4 | 2200 | 0.0024577 | 0.00061442
2012-11-30 06:10PM | 1574429-1 | L941 | Rural Short | Weather | 9 | 1521.3333 | 13692 | 0.015296 | 1.0054e-05
2013-04-15 10:09PM | 1610537-1 | L941 | Rural Short | Weather | 2 | 371 | 742 | 0.0008289 | 2.2342e-06
2012-08-17 02:19PM | 1546828-1 | L941 | Rural Short | Weather | 161 | 115.3665 | 18574 | 0.020749 | 0.00017986
2012-11-17 03:19PM | 1571234-1 | L941 | Rural Short | Other | 161 | 156.9627 | 25271 | 0.028231 | 0.00017986
2013-01-21 06:13AM | 1586811-1 | L948 | Rural Short | Equipment Failure | 1 | 297 | 297 | 0.00033178 | 1.1171e-06
2012-09-06 06:05PM | 1552494-1 | L948 | Rural Short | Third Party Impacts | 33 | 198.0909 | 6537 | 0.0073026 | 3.6865e-05
2012-12-02 09:59AM | 1574763-1 | L948 | Rural Short | Weather | 1 | 176 | 176 | 0.00019661 | 1.1171e-06
2013-04-24 08:00AM | 1612645-1 | L948 | Rural Short | Other | 5 | 100 | 500 | 0.00055856 | 5.5856e-06
2013-06-11 07:06AM | 1624181-1 | L948 | Rural Short | Other | 2 | 119 | 238 | 0.00026587 | 2.2342e-06
2012-11-18 03:20PM | 1570583-1 | L948 | Rural Short | Other | 6 | 4 | 24 | 2.6811e-05 | 6.7027e-06
2012-11-30 05:52PM | 1574414-1 | L948 | Rural Short | Weather | 426 | 526.5446 | 224308 | 0.25058 | 0.00047589
2013-05-04 03:30PM | 1614917-1 | L948 | Rural Short | Vegetation | 428 | 56.2617 | 24080 | 0.0269 | 0.00047813
2013-06-04 12:14AM | 1622695-1 | L948 | Rural Short | Other | 274 | 0.21533 | 59 | 6.591e-05 | 0.00030609
2012-09-28 10:19AM | 1557757-1 | L948 | Rural Short | Vegetation | 112 | 358.9911 | 40207 | 0.044916 | 0.00012512
2012-07-09 04:50PM | 1536693-1 | 4883 | Urban | Other | 69 | 119.4058 | 8239 | 0.009204 | 7.7081e-05
2012-07-01 02:04PM | 1534649-1 | 4887 | Urban | Equipment Failure | 27 | 175.3333 | 4734 | 0.0052884 | 3.0162e-05
2012-08-17 02:37PM | 1546867-1 | GV1208 | Urban | Weather | 54 | 150.1481 | 8108 | 0.0090576 | 6.0324e-05
2013-03-22 04:19PM | 1605564-1 | GV1223 | Urban | Weather | 841 | 264.1034 | 222111 | 0.24812 | 0.0009395
2013-03-08 11:42AM | 1601995-1 | GV1223 | Urban | Other | 106 | 111 | 11766 | 0.013144 | 0.00011841
2012-12-25 01:43PM | 1580475-1 | GV1223 | Urban | Equipment Failure | 1 | 140 | 140 | 0.0001564 | 1.1171e-06
2012-10-22 04:11PM | 1563689-1 | GV1223 | Urban | Weather | 1410 | 53.9333 | 76046 | 0.084953 | 0.0015751
2012-09-16 12:08AM | 1554855-1 | 7979 | Urban | Equipment Failure | 339 | 215.9971 | 73223 | 0.081799 | 0.0003787
2012-09-21 06:17PM | 1558515-1 | 7979 | Urban | Operatonal Error | 339 | 2.9971 | 1016 | 0.001135 | 0.0003787
2012-10-11 01:16PM | 1564032-1 | 7979 | Urban | Third Party Impacts | 339 | 4.9971 | 1694 | 0.0018924 | 0.0003787
2013-02-11 08:36AM | 1593431-1 | R260 | Rural Short | Weather | 4 | 129 | 516 | 0.00057643 | 4.4685e-06
2013-02-11 06:38AM | 1593404-1 | R260 | Rural Short | Weather | 5 | 251 | 1255 | 0.001402 | 5.5856e-06
2012-09-08 12:38PM | 1553161-1 | R260 | Rural Short | Other | 2 | 19.5 | 39 | 4.3568e-05 | 2.2342e-06
2013-04-03 02:48PM | 1607640-1 | R260 | Rural Short | Vegetation | 3 | 366 | 1098 | 0.0012266 | 3.3514e-06
2013-02-25 06:35AM | 1597807-1 | R260 | Rural Short | Equipment Failure | 1 | 237 | 237 | 0.00026476 | 1.1171e-06
2013-03-19 11:00AM | 1604529-1 | R260 | Rural Short | Third Party Impacts | 2 | 36.5 | 73 | 8.155e-05 | 2.2342e-06
2012-09-06 09:17AM | 1552206-1 | R260 | Rural Short | Weather | 18 | 263.6667 | 4746 | 0.0053019 | 2.0108e-05
2013-02-08 05:29PM | 1592886-1 | R260 | Rural Short | Other | 8 | 4.625 | 37 | 4.1333e-05 | 8.937e-06
2012-12-05 08:42AM | 1575601-1 | R260 | Rural Short | Operatonal Error | 33 | 5 | 165 | 0.00018432 | 3.6865e-05
2013-02-01 09:26AM | 1590565-1 | R260 | Rural Short | Vegetation | 3 | 133 | 399 | 0.00044573 | 3.3514e-06
2012-07-19 06:30PM | 1539113-1 | R260 | Rural Short | Other | 574 | 51.3432 | 29471 | 0.032923 | 0.00064123
2012-07-21 05:31PM | 1539492-1 | R260 | Rural Short | Other | 1 | 74 | 74 | 8.2667e-05 | 1.1171e-06
2012-09-07 10:57PM | 1553051-1 | R260 | Rural Short | Weather | 290 | 661.6207 | 191870 | 0.21434 | 0.00032396
2013-02-10 07:33PM | 1593340-1 | R260 | Rural Short | Weather | 295 | 133 | 39235 | 0.04383 | 0.00032955
2013-03-24 04:30AM | 1606621-1 | 796 | Rural Short | Other | 1 | 252 | 252 | 0.00028151 | 1.1171e-06
2013-04-26 06:09AM | 1613013-1 | W118 | Urban | Equipment Failure | 736 | 51.0326 | 37560 | 0.041959 | 0.0008222
2012-09-08 08:13AM | 1553082-1 | W118 | Urban | Equipment Failure | 47 | 303.8298 | 14280 | 0.015952 | 5.2505e-05
2013-04-22 10:11AM | 1611961-1 | W118 | Urban | Third Party Impacts | 48 | 80.5 | 3864 | 0.0043166 | 5.3622e-05
2012-09-07 10:05PM | 1553038-1 | W118 | Urban | Weather | 733 | 3.4379 | 2520 | 0.0028151 | 0.00081885
2013-04-05 12:05AM | 1608018-1 | W118 | Urban | Equipment Failure | 640 | 40.2156 | 25738 | 0.028752 | 0.00071496
2012-10-02 11:33AM | 1558339-1 | W118 | Urban | Vegetation | 79 | 169.1266 | 13361 | 0.014926 | 8.8252e-05
2013-04-26 06:09AM | 1613013-1 | W120 | Urban | Equipment Failure | 1215 | 51.0156 | 61984 | 0.069244 | 0.0013573
2012-08-28 04:39PM | 1550091-1 | W120 | Urban | Equipment Failure | 30 | 19.0333 | 571 | 0.00063788 | 3.3514e-05
2012-12-09 12:16PM | 1576615-1 | W120 | Urban | Equipment Failure | 14 | 120 | 1680 | 0.0018768 | 1.564e-05
2013-06-29 01:12PM | 1629237-1 | W120 | Urban | Equipment Failure | 30 | 97 | 2910 | 0.0032508 | 3.3514e-05
2013-05-13 12:57PM | 1616902-1 | W120 | Urban | Equipment Failure | 43 | 199.186 | 8565 | 0.0095681 | 4.8036e-05
2013-02-10 07:01AM | 1593162-1 | W120 | Urban | Other | 87 | 275 | 23925 | 0.026727 | 9.7189e-05
2013-01-01 05:38AM | 1581592-1 | W120 | Urban | Animals | 1 | 170 | 170 | 0.00018991 | 1.1171e-06
2013-02-22 09:24AM | 1596342-1 | W120 | Urban | Equipment Failure | 140 | 77.85 | 10899 | 0.012175 | 0.0001564
2012-12-12 12:39PM | 1577420-1 | W120 | Urban | Equipment Failure | 1 | 77 | 77 | 8.6018e-05 | 1.1171e-06
2013-02-09 09:58AM | 1593023-1 | W120 | Urban | Equipment Failure | 1 | 163 | 163 | 0.00018209 | 1.1171e-06
2013-04-26 06:09AM | 1613013-1 | W123 | Urban | Equipment Failure | 1004 | 51.005 | 51209 | 0.057207 | 0.0011216
2012-08-18 12:33AM | 1547111-1 | W123 | Urban | Equipment Failure | 116 | 123 | 14268 | 0.015939 | 0.00012959
2013-04-26 06:09AM | 1613013-1 | W124 | Rural Short | Equipment Failure | 1100 | 50.9845 | 56083 | 0.062651 | 0.0012288
2012-07-16 02:54PM | 1538096-1 | W124 | Rural Short | Equipment Failure | 3 | 48.6667 | 146 | 0.0001631 | 3.3514e-06
2012-09-08 07:46AM | 1553079-1 | W124 | Rural Short | Other | 1 | 475 | 475 | 0.00053063 | 1.1171e-06
2012-12-24 03:31PM | 1580143-1 | W124 | Rural Short | Third Party Impacts | 21 | 116.0476 | 2437 | 0.0027224 | 2.346e-05
2012-08-05 04:34AM | 1542958-1 | W124 | Rural Short | Other | 22 | 362.5455 | 7976 | 0.0089101 | 2.4577e-05
2012-12-04 03:40PM | 1575395-1 | W124 | Rural Short | Equipment Failure | 21 | 472.1429 | 9915 | 0.011076 | 2.346e-05
2012-09-07 10:12PM | 1553042-1 | W124 | Rural Short | Weather | 71 | 599 | 42529 | 0.04751 | 7.9316e-05
2013-04-26 06:09AM | 1613013-1 | W126 | Rural Short | Equipment Failure | 81 | 51.3086 | 4156 | 0.0046428 | 9.0487e-05
2013-04-26 06:09AM | 1613013-1 | W127 | Rural Short | Equipment Failure | 806 | 50.9938 | 41101 | 0.045915 | 0.0009004
2013-02-10 06:11AM | 1593158-1 | W127 | Rural Short | Other | 3 | 369 | 1107 | 0.0012367 | 3.3514e-06
2012-11-23 04:16PM | 1572291-1 | W127 | Rural Short | Other | 11 | 115 | 1265 | 0.0014132 | 1.2288e-05
2013-05-05 01:04PM | 1614997-1 | W127 | Rural Short | Vegetation | 11 | 98 | 1078 | 0.0012043 | 1.2288e-05
2012-11-22 04:37PM | 1571972-1 | W127 | Rural Short | Equipment Failure | 109 | 5.945 | 648 | 0.00072389 | 0.00012177
2013-05-16 11:17PM | 1618100-1 | W127 | Rural Short | Equipment Failure | 141 | 259.0851 | 36531 | 0.04081 | 0.00015751
2012-12-27 09:26AM | 1580778-1 | HBA2 | Rural Short | Equipment Failure | 62 | 169.1613 | 10488 | 0.011716 | 6.9261e-05
2012-09-30 12:18PM | 1558154-1 | HBA2 | Rural Short | Other | 3 | 198 | 594 | 0.00066357 | 3.3514e-06
2012-12-02 08:42AM | 1574751-1 | HBA2 | Rural Short | Other | 17 | 135 | 2295 | 0.0025638 | 1.8991e-05
2012-12-02 08:44PM | 1574820-1 | HBA2 | Rural Short | Other | 17 | 162 | 2754 | 0.0030765 | 1.8991e-05
2013-01-27 09:21AM | 1589079-1 | HBA2 | Rural Short | Equipment Failure | 153 | 124.3268 | 19022 | 0.02125 | 0.00017092
2013-01-27 04:17AM | 1588965-1 | HBA2 | Rural Short | Equipment Failure | 153 | 223.6013 | 34211 | 0.038218 | 0.00017092
2013-01-18 04:59PM | 1586253-1 | HBA2 | Rural Short | Third Party Impacts | 439 | 201.5125 | 88464 | 0.098825 | 0.00049042
2013-01-28 12:44AM | 1589185-1 | HBA2 | Rural Short | Weather | 446 | 62.435 | 27846 | 0.031107 | 0.00049824
2013-06-17 05:15PM | 1625837-1 | HBB2 | Urban | Vegetation | 103 | 11.4757 | 1182 | 0.0013204 | 0.00011506
2012-11-23 11:14PM | 1572380-1 | HBB2 | Urban | Equipment Failure | 1 | 23 | 23 | 2.5694e-05 | 1.1171e-06
2012-11-16 07:54PM | 1570484-1 | HBB2 | Urban | Other | 62 | 50 | 3100 | 0.0034631 | 6.9261e-05
2012-12-25 03:17PM | 1580521-1 | HBB2 | Urban | Weather | 138 | 111.6667 | 15410 | 0.017215 | 0.00015416
2013-06-18 08:39AM | 1626016-1 | HBC2 | Urban | Other | 1 | 290 | 290 | 0.00032396 | 1.1171e-06
2013-01-28 08:18AM | 1589218-1 | HBC2 | Urban | Equipment Failure | 61 | 59.9344 | 3656 | 0.0040842 | 6.8144e-05
2012-08-10 11:24AM | 1544445-1 | HBC2 | Urban | Other | 141 | 7.8794 | 1111 | 0.0012411 | 0.00015751
2013-02-07 08:00PM | 1592623-1 | HBC2 | Urban | Other | 57 | 53 | 3021 | 0.0033748 | 6.3676e-05
2012-08-10 02:05PM | 1544636-1 | HBC2 | Urban | Other | 64 | 126.4375 | 8092 | 0.0090397 | 7.1496e-05
2012-12-25 03:39AM | 1580401-1 | HBC2 | Urban | Weather | 802 | 149.2332 | 119685 | 0.1337 | 0.00089593
2013-02-20 05:03AM | 1595656-1 | HBC2 | Urban | Equipment Failure | 803 | 97.9601 | 78662 | 0.087875 | 0.00089705
2013-01-18 04:34PM | 1586213-1 | HBD2 | Urban | Vegetation | 7 | 434.7143 | 3043 | 0.0033994 | 7.8198e-06
2013-02-10 07:36PM | 1593343-1 | 77674 | Rural Short | Weather | 24 | 8.2917 | 199 | 0.00022231 | 2.6811e-05
2012-10-19 11:08AM | 1563012-1 | 77674 | Rural Short | Other | 22 | 243.4091 | 5355 | 0.0059822 | 2.4577e-05
2013-03-14 10:26PM | 1603601-1 | 77674 | Rural Short | Other | 204 | 188.25 | 38403 | 0.042901 | 0.00022789
2012-10-05 09:15AM | 1562148-1 | X217 | Rural Short | Weather | 1 | 45 | 45 | 5.027e-05 | 1.1171e-06
2013-02-04 08:40AM | 1591237-1 | X217 | Rural Short | Other | 1 | 186 | 186 | 0.00020778 | 1.1171e-06
2013-02-10 07:46PM | 1593337-1 | X217 | Rural Short | Weather | 1 | 11 | 11 | 1.2288e-05 | 1.1171e-06
2013-06-16 04:22PM | 1625568-1 | X217 | Rural Short | Other | 2 | 147 | 294 | 0.00032843 | 2.2342e-06
2012-07-30 07:11PM | 1541502-1 | X217 | Rural Short | Equipment Failure | 46 | 73.6957 | 3390 | 0.003787 | 5.1388e-05
2012-08-28 07:31PM | 1550159-1 | X217 | Rural Short | Other | 2 | 102.5 | 205 | 0.00022901 | 2.2342e-06
2013-03-04 04:34PM | 1600660-1 | X217 | Rural Short | Third Party Impacts | 236 | 1.2331 | 291 | 0.00032508 | 0.00026364
2013-02-10 07:36PM | 1593343-1 | X492 | Rural Long | Weather | 317 | 8.2871 | 2627 | 0.0029347 | 0.00035413
2013-05-23 08:38AM | 1619578-1 | X492 | Rural Long | Other | 121 | 109.0661 | 13197 | 0.014743 | 0.00013517
2013-02-21 12:36PM | 1596105-1 | X492 | Rural Long | Other | 14 | 95.5714 | 1338 | 0.0014947 | 1.564e-05
2012-07-07 02:17AM | 1536233-1 | X492 | Rural Long | Other | 215 | 1 | 215 | 0.00024018 | 0.00024018
2012-08-26 06:19PM | 1549568-1 | X492 | Rural Long | Other | 295 | 98.322 | 29005 | 0.032402 | 0.00032955
2012-07-26 11:32AM | 1540503-1 | X492 | Rural Long | Equipment Failure | 6 | 352 | 2112 | 0.0023594 | 6.7027e-06
2012-12-14 04:26PM | 1578059-1 | X492 | Rural Long | Equipment Failure | 1 | 99 | 99 | 0.00011059 | 1.1171e-06
2013-02-11 07:11AM | 1593409-1 | X492 | Rural Long | Weather | 1 | 565 | 565 | 0.00063117 | 1.1171e-06
2013-02-01 04:54PM | 1590844-1 | X492 | Rural Long | Weather | 1 | 143 | 143 | 0.00015975 | 1.1171e-06
2013-01-04 12:42PM | 1582324-1 | X492 | Rural Long | Other | 1 | 159 | 159 | 0.00017762 | 1.1171e-06
2013-05-18 10:09AM | 1618444-1 | X492 | Rural Long | Other | 3 | 98 | 294 | 0.00032843 | 3.3514e-06
2013-05-26 04:46PM | 1620365-1 | X492 | Rural Long | Equipment Failure | 3 | 177 | 531 | 0.00059319 | 3.3514e-06
2013-03-25 05:13PM | 1606182-1 | X492 | Rural Long | Equipment Failure | 1 | 179 | 179 | 0.00019996 | 1.1171e-06
2013-01-25 10:23PM | 1588840-1 | X492 | Rural Long | Other | 2 | 125 | 250 | 0.00027928 | 2.2342e-06
2013-05-11 03:27PM | 1616612-1 | X492 | Rural Long | Equipment Failure | 1 | 185 | 185 | 0.00020667 | 1.1171e-06
2013-01-25 10:26PM | 1588841-1 | X492 | Rural Long | Other | 1 | 123 | 123 | 0.00013741 | 1.1171e-06
2012-08-29 08:22AM | 1550216-1 | X492 | Rural Long | Other | 25 | 37.48 | 937 | 0.0010467 | 2.7928e-05
2013-05-08 03:37PM | 1615860-1 | X492 | Rural Long | Other | 1 | 205 | 205 | 0.00022901 | 1.1171e-06
2012-11-30 01:18PM | 1574229-1 | X492 | Rural Long | Other | 1 | 30 | 30 | 3.3514e-05 | 1.1171e-06
2013-04-29 01:21PM | 1613652-1 | X492 | Rural Long | Equipment Failure | 1 | 2 | 2 | 2.2342e-06 | 1.1171e-06
2013-02-07 05:00PM | 1592584-1 | X492 | Rural Long | Weather | 1 | 113 | 113 | 0.00012623 | 1.1171e-06
2013-02-10 08:16PM | 1593360-1 | X492 | Rural Long | Weather | 198 | 3.1162 | 617 | 0.00068926 | 0.00022119
2013-02-05 04:58PM | 1591827-1 | X492 | Rural Long | Equipment Failure | 50 | 118.66 | 5933 | 0.0066279 | 5.5856e-05
2012-12-29 09:24AM | 1581278-1 | X492 | Rural Long | Other | 3 | 110.6667 | 332 | 0.00037088 | 3.3514e-06
2012-11-13 09:23AM | 1569431-1 | X492 | Rural Long | Weather | 10 | 120 | 1200 | 0.0013405 | 1.1171e-05
2013-01-25 07:28PM | 1588824-1 | X492 | Rural Long | Animals | 10 | 167 | 1670 | 0.0018656 | 1.1171e-05
2013-02-10 08:27PM | 1593366-1 | X492 | Rural Long | Weather | 10 | 158 | 1580 | 0.001765 | 1.1171e-05
2013-03-08 11:20AM | 1604866-1 | X492 | Rural Long | Equipment Failure | 5 | 50 | 250 | 0.00027928 | 5.5856e-06
2012-07-13 02:22PM | 1537628-1 | X492 | Rural Long | Equipment Failure | 5 | 62 | 310 | 0.00034631 | 5.5856e-06
2012-08-06 05:59AM | 1543044-1 | J493 | Urban | Other | 11 | 117 | 1287 | 0.0014377 | 1.2288e-05
2013-01-28 03:17PM | 1589289-1 | J493 | Urban | Other | 11 | 111 | 1221 | 0.001364 | 1.2288e-05
2013-02-05 09:52AM | 1591625-1 | J493 | Urban | Equipment Failure | 11 | 243 | 2673 | 0.0029861 | 1.2288e-05
2013-02-06 10:20PM | 1592304-1 | J493 | Urban | Other | 11 | 38 | 418 | 0.00046696 | 1.2288e-05
2013-02-14 12:26PM | 1594417-1 | J493 | Urban | Other | 11 | 86 | 946 | 0.0010568 | 1.2288e-05
2013-04-16 12:58AM | 1610566-1 | J493 | Urban | Other | 24 | 452 | 10848 | 0.012119 | 2.6811e-05
2012-11-22 10:34AM | 1571843-1 | J493 | Urban | Other | 21 | 48.9524 | 1028 | 0.0011484 | 2.346e-05
2012-12-23 06:15PM | 1579979-1 | J493 | Urban | Equipment Failure | 1 | 417 | 417 | 0.00046584 | 1.1171e-06
2012-08-10 02:51PM | 1544745-1 | J495 | Urban | Weather | 7 | 54.5714 | 382 | 0.00042674 | 7.8198e-06
2013-01-17 11:13AM | 1585642-1 | J495 | Urban | Equipment Failure | 42 | 37.119 | 1559 | 0.0017416 | 4.6919e-05
2012-08-11 01:44PM | 1545093-1 | J495 | Urban | Weather | 4 | 231 | 924 | 0.0010322 | 4.4685e-06
2012-10-20 02:36PM | 1563311-1 | J495 | Urban | Other | 11 | 133.9091 | 1473 | 0.0016455 | 1.2288e-05
2012-09-15 11:28AM | 1554802-1 | J495 | Urban | Equipment Failure | 1 | 222 | 222 | 0.000248 | 1.1171e-06
2012-12-16 11:35AM | 1578246-1 | J496 | Urban | Equipment Failure | 1 | 384 | 384 | 0.00042897 | 1.1171e-06
2012-11-27 09:07PM | 1573333-1 | J496 | Urban | Weather | 93 | 49 | 4557 | 0.0050907 | 0.00010389
2012-07-02 12:19PM | 1534831-1 | J496 | Urban | Equipment Failure | 873 | 66.3975 | 57965 | 0.064754 | 0.00097525
2012-11-27 09:38PM | 1573339-1 | J496 | Urban | Weather | 70 | 2.4143 | 169 | 0.00018879 | 7.8198e-05
2013-02-06 10:55AM | 1592067-1 | J496 | Urban | Other | 1 | 34 | 34 | 3.7982e-05 | 1.1171e-06
2013-05-04 04:13PM | 1614922-1 | J497 | Urban | Vegetation | 5 | 130 | 650 | 0.00072613 | 5.5856e-06
2012-12-02 05:43PM | 1574808-1 | L582 | Rural Short | Equipment Failure | 60 | 103 | 6180 | 0.0069038 | 6.7027e-05
2012-12-25 04:48AM | 1580405-1 | L582 | Rural Short | Weather | 1 | 55 | 55 | 6.1442e-05 | 1.1171e-06
2012-12-27 11:50AM | 1580844-1 | L582 | Rural Short | Weather | 1 | 132 | 132 | 0.00014746 | 1.1171e-06
2012-12-28 02:33PM | 1581189-1 | L582 | Rural Short | Other | 1 | 122 | 122 | 0.00013629 | 1.1171e-06
2012-09-11 08:45PM | 1553840-1 | L582 | Rural Short | Equipment Failure | 1 | 173 | 173 | 0.00019326 | 1.1171e-06
2012-12-15 10:34PM | 1578218-1 | L582 | Rural Short | Equipment Failure | 1 | 131 | 131 | 0.00014634 | 1.1171e-06
2012-09-06 07:44PM | 1552511-1 | L582 | Rural Short | Equipment Failure | 1 | 197 | 197 | 0.00022007 | 1.1171e-06
2012-09-25 04:37PM | 1556983-1 | L582 | Rural Short | Equipment Failure | 8 | 32.75 | 262 | 0.00029269 | 8.937e-06
2013-02-18 05:07PM | 1595244-1 | L582 | Rural Short | Weather | 1 | 94 | 94 | 0.00010501 | 1.1171e-06
2012-08-10 01:25PM | 1547722-1 | JBA2 | Rural Short | Weather | 786 | 72.0789 | 56654 | 0.063289 | 0.00087806
2013-01-16 05:27PM | 1585471-1 | JBA2 | Rural Short | Equipment Failure | 797 | 12.0025 | 9566 | 0.010686 | 0.00089034
2012-12-08 11:08PM | 1576583-1 | JBA2 | Rural Short | Other | 4 | 1 | 4 | 4.4685e-06 | 4.4685e-06
2013-01-19 02:28PM | 1586626-1 | JBA2 | Rural Short | Vegetation | 5 | 22.8 | 114 | 0.00012735 | 5.5856e-06
2013-06-02 08:19AM | 1622277-1 | JBA2 | Rural Short | Vegetation | 3 | 87.3333 | 262 | 0.00029269 | 3.3514e-06
2012-08-10 11:04AM | 1544424-1 | JBA2 | Rural Short | Other | 1 | 327 | 327 | 0.0003653 | 1.1171e-06
2012-08-10 11:14AM | 1544433-1 | JBA2 | Rural Short | Other | 1 | 320 | 320 | 0.00035748 | 1.1171e-06
2012-10-16 07:45PM | 1562323-1 | JBA2 | Rural Short | Animals | 3 | 75 | 225 | 0.00025135 | 3.3514e-06
2012-10-07 07:43AM | 1559511-1 | JBA2 | Rural Short | Weather | 2 | 110.5 | 221 | 0.00024688 | 2.2342e-06
2012-10-06 08:16PM | 1559487-1 | JBA2 | Rural Short | Weather | 52 | 146.5192 | 7619 | 0.0085113 | 5.809e-05
2012-10-21 12:01AM | 1563360-1 | JBA2 | Rural Short | Equipment Failure | 55 | 234.2545 | 12884 | 0.014393 | 6.1442e-05
2013-04-19 06:40PM | 1611651-1 | JBA2 | Rural Short | Weather | 52 | 72 | 3744 | 0.0041825 | 5.809e-05
2013-02-01 07:37AM | 1590542-1 | JBA2 | Rural Short | Vegetation | 59 | 48.8136 | 2880 | 0.0032173 | 6.591e-05
2012-09-25 01:10PM | 1556920-1 | JBA2 | Rural Short | Equipment Failure | 30 | 31.9667 | 959 | 0.0010713 | 3.3514e-05
2012-08-21 07:19AM | 1547641-1 | JBA2 | Rural Short | Third Party Impacts | 14 | 92 | 1288 | 0.0014389 | 1.564e-05
2012-09-10 06:52AM | 1553332-1 | JBA2 | Rural Short | Equipment Failure | 14 | 170.7143 | 2390 | 0.0026699 | 1.564e-05
2012-10-21 02:16PM | 1563428-1 | JBA2 | Rural Short | Vegetation | 55 | 201.0727 | 11059 | 0.012354 | 6.1442e-05
2012-12-01 07:11AM | 1574597-1 | JBA2 | Rural Short | Weather | 57 | 324 | 18468 | 0.020631 | 6.3676e-05
2013-03-04 01:24PM | 1600587-1 | JBA2 | Rural Short | Equipment Failure | 18 | 190.8333 | 3435 | 0.0038373 | 2.0108e-05
2013-03-04 03:13PM | 1600639-1 | JBA2 | Rural Short | Equipment Failure | 39 | 9.5897 | 374 | 0.0004178 | 4.3568e-05
2013-05-23 03:38AM | 1619536-1 | JBA2 | Rural Short | Vegetation | 57 | 171.6842 | 9786 | 0.010932 | 6.3676e-05
2012-12-01 03:59AM | 1574550-1 | JBA2 | Rural Short | Weather | 18 | 295 | 5310 | 0.0059319 | 2.0108e-05
2013-02-07 12:00PM | 1592453-1 | JBA2 | Rural Short | Other | 18 | 56.6667 | 1020 | 0.0011395 | 2.0108e-05
2013-03-04 11:37PM | 1600769-1 | JBA2 | Rural Short | Animals | 28 | 124.8214 | 3495 | 0.0039043 | 3.1279e-05
2013-01-27 04:18AM | 1588966-1 | JBA2 | Rural Short | Weather | 618 | 98.432 | 60831 | 0.067956 | 0.00069038
2012-08-10 01:25PM | 1547722-1 | JBB2 | Rural Short | Weather | 397 | 71.9395 | 28560 | 0.031905 | 0.0004435
2013-01-16 05:27PM | 1585471-1 | JBB2 | Rural Short | Equipment Failure | 402 | 11.995 | 4822 | 0.0053868 | 0.00044908
2012-08-28 07:14AM | 1549908-1 | JBB2 | Rural Short | Other | 7 | 59.1429 | 414 | 0.00046249 | 7.8198e-06
2012-11-19 07:22AM | 1570761-1 | JBB2 | Rural Short | Other | 1 | 342 | 342 | 0.00038206 | 1.1171e-06
2012-11-19 03:01PM | 1570913-1 | JBB2 | Rural Short | Equipment Failure | 3 | 209 | 627 | 0.00070043 | 3.3514e-06
2013-04-07 06:52AM | 1608412-1 | JBB2 | Rural Short | Animals | 1 | 113 | 113 | 0.00012623 | 1.1171e-06
2012-12-06 06:22AM | 1575989-1 | JBB2 | Rural Short | Other | 1 | 283 | 283 | 0.00031614 | 1.1171e-06
2013-04-22 06:35PM | 1612222-1 | JBB2 | Rural Short | Other | 4 | 67 | 268 | 0.00029939 | 4.4685e-06
2013-01-23 08:18AM | 1587577-1 | JBB2 | Rural Short | Equipment Failure | 1 | 183 | 183 | 0.00020443 | 1.1171e-06
2012-08-11 08:20AM | 1545028-1 | JBB2 | Rural Short | Other | 1 | 98 | 98 | 0.00010948 | 1.1171e-06
2013-02-02 03:53PM | 1591083-1 | JBB2 | Rural Short | Animals | 2 | 158 | 316 | 0.00035301 | 2.2342e-06
2012-08-12 10:35AM | 1545179-1 | JBB2 | Rural Short | Equipment Failure | 1 | 74 | 74 | 8.2667e-05 | 1.1171e-06
2013-01-22 07:00PM | 1587495-1 | JBB2 | Rural Short | Weather | 2 | 61 | 122 | 0.00013629 | 2.2342e-06
2012-08-11 01:46PM | 1545094-1 | JBB2 | Rural Short | Weather | 5 | 74.6 | 373 | 0.00041669 | 5.5856e-06
2012-08-22 10:21PM | 1548222-1 | JBB2 | Rural Short | Equipment Failure | 5 | 127.4 | 637 | 0.00071161 | 5.5856e-06
2013-04-09 09:22AM | 1608742-1 | JBB2 | Rural Short | Other | 2 | 130.5 | 261 | 0.00029157 | 2.2342e-06
2012-09-07 10:01PM | 1553037-1 | JBB2 | Rural Short | Weather | 16 | 120 | 1920 | 0.0021449 | 1.7874e-05
2012-08-11 07:48PM | 1545134-1 | JBB2 | Rural Short | Equipment Failure | 51 | 268.098 | 13673 | 0.015274 | 5.6973e-05
2012-08-31 05:26AM | 1550849-1 | JBB2 | Rural Short | Weather | 51 | 278.8431 | 14221 | 0.015887 | 5.6973e-05
2012-12-12 10:02PM | 1577537-1 | JBB2 | Rural Short | Other | 53 | 1 | 53 | 5.9207e-05 | 5.9207e-05
2012-11-18 11:28PM | 1570747-1 | JBB2 | Rural Short | Equipment Failure | 49 | 25.3265 | 1241 | 0.0013863 | 5.4739e-05
2012-12-20 05:00PM | 1579525-1 | JBB2 | Rural Short | Equipment Failure | 50 | 96.72 | 4836 | 0.0054024 | 5.5856e-05
2012-08-10 01:25PM | 1544550-1 | JBB2 | Rural Short | Weather | 307 | 287.4104 | 88235 | 0.098569 | 0.00034296
2012-08-11 04:47PM | 1545117-1 | JBB2 | Rural Short | Equipment Failure | 17 | 198.1176 | 3368 | 0.0037625 | 1.8991e-05
2013-05-25 11:02PM | 1620211-1 | JBB2 | Rural Short | Animals | 319 | 117.6897 | 37543 | 0.04194 | 0.00035636
2013-03-10 06:04AM | 1602291-1 | 55864 | Urban | Equipment Failure | 177 | 93.113 | 16481 | 0.018411 | 0.00019773
2012-08-20 10:36PM | 1547618-1 | 55866 | Urban | Equipment Failure | 54 | 291.6111 | 15747 | 0.017591 | 6.0324e-05
2012-08-21 08:32AM | 1547653-1 | 55866 | Urban | Equipment Failure | 53 | 4.2075 | 223 | 0.00024912 | 5.9207e-05
2013-03-10 06:04AM | 1602291-1 | 55866 | Urban | Equipment Failure | 438 | 92.9269 | 40702 | 0.045469 | 0.0004893
2013-03-14 05:17PM | 1603509-1 | 55867 | Urban | Equipment Failure | 26 | 348 | 9048 | 0.010108 | 2.9045e-05
2012-08-02 01:28PM | 1542359-1 | 55867 | Urban | Equipment Failure | 26 | 63.3462 | 1647 | 0.0018399 | 2.9045e-05
2013-01-08 09:18PM | 1583417-1 | 55867 | Urban | Equipment Failure | 25 | 280 | 7000 | 0.0078198 | 2.7928e-05
2013-03-10 06:04AM | 1602291-1 | 55867 | Urban | Equipment Failure | 848 | 92.9894 | 78855 | 0.08809 | 0.00094732
2012-11-12 07:45AM | 1569109-1 | 55867 | Urban | Equipment Failure | 1 | 128 | 128 | 0.00014299 | 1.1171e-06
2013-02-08 08:06PM | 1592954-1 | 55870 | Urban | Vegetation | 33 | 116.5758 | 3847 | 0.0042976 | 3.6865e-05
2013-06-11 03:33PM | 1624365-1 | 55870 | Urban | Equipment Failure | 45 | 70.4444 | 3170 | 0.0035413 | 5.027e-05
2012-08-10 03:37PM | 1544820-1 | 55870 | Urban | Weather | 1 | 274 | 274 | 0.00030609 | 1.1171e-06
2013-03-10 06:04AM | 1602291-1 | 55870 | Urban | Equipment Failure | 807 | 92.974 | 75030 | 0.083818 | 0.00090152
2013-03-28 11:39PM | 1606990-1 | 55874 | Urban | Equipment Failure | 93 | 58 | 5394 | 0.0060257 | 0.00010389
2013-06-25 05:04AM | 1627668-1 | 55874 | Urban | Weather | 36 | 132 | 4752 | 0.0053086 | 4.0216e-05
2013-03-10 06:04AM | 1602291-1 | 55874 | Urban | Equipment Failure | 1303 | 93.013 | 121196 | 0.13539 | 0.0014556
2012-07-25 06:51AM | 1540148-1 | 55874 | Urban | Equipment Failure | 10 | 196.1 | 1961 | 0.0021907 | 1.1171e-05
2013-05-22 05:02AM | 1619203-1 | 55874 | Urban | Animals | 1331 | 2.5755 | 3428 | 0.0038295 | 0.0014869
2012-08-21 11:20AM | 1547706-1 | 55875 | Urban | Equipment Failure | 53 | 94.5094 | 5009 | 0.0055957 | 5.9207e-05
2012-08-07 10:04PM | 1543637-1 | 55875 | Urban | Equipment Failure | 16 | 106.3125 | 1701 | 0.0019002 | 1.7874e-05
2012-08-26 11:31PM | 1549581-1 | 55875 | Urban | Animals | 29 | 38.8966 | 1128 | 0.0012601 | 3.2396e-05
2013-02-18 07:47PM | 1595263-1 | 55875 | Urban | Equipment Failure | 61 | 53 | 3233 | 0.0036116 | 6.8144e-05
2012-08-09 08:46AM | 1543972-1 | 55875 | Urban | Other | 16 | 57.4375 | 919 | 0.0010266 | 1.7874e-05
2013-03-10 06:04AM | 1602291-1 | 55875 | Urban | Equipment Failure | 900 | 92.9789 | 83681 | 0.093482 | 0.0010054
2013-04-15 01:28PM | 1610382-1 | 55876 | Urban | Equipment Failure | 50 | 146 | 7300 | 0.008155 | 5.5856e-05
2013-03-10 06:04AM | 1602291-1 | 55876 | Urban | Equipment Failure | 1463 | 92.9856 | 136038 | 0.15197 | 0.0016343
2012-11-27 07:12PM | 1573216-1 | 55879 | Urban | Vegetation | 20 | 128 | 2560 | 0.0028598 | 2.2342e-05
2013-03-10 06:04AM | 1602291-1 | 55879 | Urban | Equipment Failure | 629 | 92.938 | 58458 | 0.065305 | 0.00070267
2012-11-22 06:26PM | 1572005-1 | 55879 | Urban | Equipment Failure | 1 | 180 | 180 | 0.00020108 | 1.1171e-06
2013-01-12 04:10PM | 1584286-1 | 55880 | Urban | Equipment Failure | 21 | 198.5238 | 4169 | 0.0046573 | 2.346e-05
2013-03-10 06:04AM | 1602291-1 | 55880 | Urban | Equipment Failure | 249 | 92.8835 | 23128 | 0.025837 | 0.00027816
2013-06-11 05:59PM | 1624404-1 | 55885 | Urban | Equipment Failure | 1 | 203 | 203 | 0.00022678 | 1.1171e-06
2013-05-12 01:10PM | 1616730-1 | 55885 | Urban | Equipment Failure | 1 | 204 | 204 | 0.00022789 | 1.1171e-06
2013-03-10 06:04AM | 1602291-1 | 55885 | Urban | Equipment Failure | 1855 | 93.0199 | 172552 | 0.19276 | 0.0020723
2012-07-10 11:19AM | 1536804-1 | 55885 | Urban | Equipment Failure | 5 | 7.2 | 36 | 4.0216e-05 | 5.5856e-06
2012-08-18 10:06AM | 1547148-1 | 55885 | Urban | Equipment Failure | 127 | 8 | 1016 | 0.001135 | 0.00014187
2012-11-13 11:25PM | 1569655-1 | 55885 | Urban | Animals | 1894 | 0.6019 | 1140 | 0.0012735 | 0.0021158
2013-03-10 06:04AM | 1602291-1 | 55888 | Urban | Equipment Failure | 224 | 93.0893 | 20852 | 0.023294 | 0.00025023
2013-03-10 06:04AM | 1602291-1 | 55890 | Urban | Equipment Failure | 1519 | 92.975 | 141229 | 0.15777 | 0.0016969
2012-11-19 09:54AM | 1570789-1 | 55890 | Urban | Vegetation | 42 | 200 | 8400 | 0.0093838 | 4.6919e-05
2013-02-04 08:26PM | 1591533-1 | 55890 | Urban | Equipment Failure | 1524 | 93.9396 | 143164 | 0.15993 | 0.0017025
2013-02-04 08:59PM | 1591547-1 | 55890 | Urban | Equipment Failure | 138 | 267.1159 | 36862 | 0.041179 | 0.00015416
2013-03-27 11:02AM | 1606608-1 | 55890 | Urban | Vegetation | 2305 | 42.2664 | 97424 | 0.10883 | 0.002575
2012-09-07 11:54PM | 1553057-1 | 55890 | Urban | Weather | 1 | 577 | 577 | 0.00064458 | 1.1171e-06
2013-06-04 11:47AM | 1622835-1 | 55891 | Urban | Vegetation | 39 | 163 | 6357 | 0.0071015 | 4.3568e-05
2012-11-12 09:35PM | 1569384-1 | 55891 | Urban | Equipment Failure | 37 | 125 | 4625 | 0.0051667 | 4.1333e-05
2013-03-10 06:04AM | 1602291-1 | 55891 | Urban | Equipment Failure | 177 | 93.113 | 16481 | 0.018411 | 0.00019773
2012-10-19 11:08AM | 1563046-1 | 76225 | Rural Short | Equipment Failure | 28 | 32.8214 | 919 | 0.0010266 | 3.1279e-05
2012-12-17 10:55AM | 1579690-1 | 76225 | Rural Short | Operatonal Error | 28 | 2 | 56 | 6.2559e-05 | 3.1279e-05
2013-02-10 07:36PM | 1593343-1 | 76225 | Rural Short | Weather | 30 | 8.4333 | 253 | 0.00028263 | 3.3514e-05
2013-02-09 09:07PM | 1593120-1 | 76225 | Rural Short | Weather | 9 | 198 | 1782 | 0.0019907 | 1.0054e-05
2013-04-10 11:35AM | 1609189-1 | 76225 | Rural Short | Other | 1 | 202 | 202 | 0.00022566 | 1.1171e-06
2013-01-18 06:50PM | 1586339-1 | 76225 | Rural Short | Weather | 28 | 720.5 | 20174 | 0.022537 | 3.1279e-05
2013-02-18 02:22PM | 1595172-1 | 87218 | Rural Short | Operatonal Error | 236 | 34.9831 | 8256 | 0.0092229 | 0.00026364
2013-02-10 07:36PM | 1593343-1 | 87218 | Rural Short | Weather | 256 | 8.2852 | 2121 | 0.0023694 | 0.00028598
2013-06-17 05:15PM | 1625844-1 | 87218 | Rural Short | Equipment Failure | 85 | 41.6353 | 3539 | 0.0039535 | 9.4955e-05
2013-03-02 08:30AM | 1600143-1 | 87218 | Rural Short | Weather | 30 | 117.2333 | 3517 | 0.0039289 | 3.3514e-05
2013-02-18 02:22PM | 1595172-1 | 87220 | Rural Short | Operatonal Error | 714 | 34.9832 | 24978 | 0.027903 | 0.00079762
2013-02-10 07:36PM | 1593343-1 | 87220 | Rural Short | Weather | 774 | 8.292 | 6418 | 0.0071697 | 0.00086465
2013-06-15 07:52PM | 1625494-1 | 87220 | Rural Short | Other | 39 | 93 | 3627 | 0.0040518 | 4.3568e-05
2013-06-17 05:15PM | 1625844-1 | 87220 | Rural Short | Equipment Failure | 258 | 41.5039 | 10708 | 0.011962 | 0.00028822
2013-04-27 06:37PM | 1613415-1 | 87220 | Rural Short | Equipment Failure | 5 | 56.4 | 282 | 0.00031503 | 5.5856e-06
2013-06-13 09:21AM | 1624848-1 | 87222 | Rural Short | Other | 1 | 293 | 293 | 0.00032732 | 1.1171e-06
2013-06-29 12:48PM | 1629235-1 | 87222 | Rural Short | Weather | 1 | 125 | 125 | 0.00013964 | 1.1171e-06
2013-06-08 09:18AM | 1623925-1 | 87222 | Rural Short | Equipment Failure | 484 | 309.4318 | 149765 | 0.16731 | 0.00054069
2013-06-29 12:47PM | 1629234-1 | 87223 | Rural Short | Weather | 21 | 124 | 2604 | 0.002909 | 2.346e-05
2012-08-29 08:16AM | 1552239-1 | X459 | Rural Short | Operatonal Error | 425 | 10.9906 | 4671 | 0.0052181 | 0.00047478
2013-02-18 02:22PM | 1595172-1 | X459 | Rural Short | Operatonal Error | 722 | 34.9848 | 25259 | 0.028217 | 0.00080656
2013-02-10 07:36PM | 1593343-1 | X459 | Rural Short | Weather | 783 | 8.2899 | 6491 | 0.0072512 | 0.0008747
2013-02-06 05:10PM | 1594742-1 | X459 | Rural Short | Operatonal Error | 719 | 15 | 10785 | 0.012048 | 0.00080321
2012-08-29 08:16AM | 1552239-1 | X463 | Rural Short | Operatonal Error | 289 | 11.0035 | 3180 | 0.0035524 | 0.00032285
2012-11-20 12:36PM | 1571217-1 | X463 | Rural Short | Other | 288 | 14.7639 | 4252 | 0.00475 | 0.00032173
2012-10-19 11:08AM | 1563046-1 | X473 | Rural Short | Equipment Failure | 701 | 33.0128 | 23142 | 0.025852 | 0.0007831
2012-12-17 10:55AM | 1579690-1 | X473 | Rural Short | Operatonal Error | 709 | 2.0014 | 1419 | 0.0015852 | 0.00079204
2012-08-29 08:16AM | 1552239-1 | X473 | Rural Short | Operatonal Error | 709 | 10.9944 | 7795 | 0.008708 | 0.00079204
2013-01-02 08:12PM | 1581913-1 | X473 | Rural Short | Other | 2 | 87 | 174 | 0.00019438 | 2.2342e-06
2013-01-17 09:47PM | 1585814-1 | X473 | Rural Short | Equipment Failure | 39 | 109.6154 | 4275 | 0.0047757 | 4.3568e-05
2013-02-01 02:09PM | 1590691-1 | X473 | Rural Short | Other | 39 | 96 | 3744 | 0.0041825 | 4.3568e-05
2013-01-22 09:57PM | 1587538-1 | X473 | Rural Short | Weather | 29 | 716.2414 | 20771 | 0.023204 | 3.2396e-05
2013-01-23 06:16PM | 1587813-1 | X473 | Rural Short | Other | 29 | 1.2759 | 37 | 4.1333e-05 | 3.2396e-05
2012-09-30 08:42PM | 1558189-1 | X473 | Rural Short | Equipment Failure | 6 | 105 | 630 | 0.00070379 | 6.7027e-06
2012-11-20 07:16PM | 1571396-1 | X473 | Rural Short | Equipment Failure | 701 | 72.2839 | 50671 | 0.056606 | 0.0007831
2012-12-25 08:40PM | 1580590-1 | X473 | Rural Short | Weather | 6 | 836 | 5016 | 0.0056035 | 6.7027e-06
2012-11-20 08:40PM | 1571425-1 | X473 | Rural Short | Equipment Failure | 164 | 42.2134 | 6923 | 0.0077338 | 0.00018321
2012-07-06 09:26AM | 1536029-1 | X473 | Rural Short | Equipment Failure | 11 | 48.1818 | 530 | 0.00059207 | 1.2288e-05
2012-11-21 07:12PM | 1571721-1 | X473 | Rural Short | Other | 1 | 134 | 134 | 0.00014969 | 1.1171e-06
2012-11-21 08:56AM | 1571493-1 | X473 | Rural Short | Other | 6 | 134 | 804 | 0.00089816 | 6.7027e-06
2013-02-07 06:59AM | 1592336-1 | X473 | Rural Short | Third Party Impacts | 1 | 311 | 311 | 0.00034742 | 1.1171e-06
2013-01-23 03:27PM | 1587780-1 | X473 | Rural Short | Weather | 1 | 197 | 197 | 0.00022007 | 1.1171e-06
2012-07-30 05:27PM | 1541472-1 | X473 | Rural Short | Equipment Failure | 61 | 138.2131 | 8431 | 0.0094184 | 6.8144e-05
2012-09-28 05:15AM | 1557659-1 | X473 | Rural Short | Equipment Failure | 50 | 219.04 | 10952 | 0.012235 | 5.5856e-05
2012-10-09 07:35PM | 1560166-1 | X473 | Rural Short | Operatonal Error | 99 | 123.798 | 12256 | 0.013691 | 0.00011059
2012-10-19 11:08AM | 1563046-1 | X479 | Rural Short | Equipment Failure | 231 | 32.9697 | 7616 | 0.008508 | 0.00025805
2012-12-17 10:55AM | 1579690-1 | X479 | Rural Short | Operatonal Error | 233 | 2 | 466 | 0.00052058 | 0.00026029
2012-08-29 08:16AM | 1552239-1 | X479 | Rural Short | Operatonal Error | 232 | 10.9957 | 2551 | 0.0028498 | 0.00025917
2012-10-06 08:54AM | 1559427-1 | X479 | Rural Short | Equipment Failure | 1 | 147 | 147 | 0.00016422 | 1.1171e-06
2012-10-19 11:08AM | 1563046-1 | X492 | Rural Long | Equipment Failure | 289 | 33.0519 | 9552 | 0.010671 | 0.00032285
2012-12-17 10:55AM | 1579690-1 | X492 | Rural Long | Operatonal Error | 292 | 2 | 584 | 0.0006524 | 0.0003262
2012-08-29 08:16AM | 1552239-1 | X492 | Rural Long | Operatonal Error | 292 | 11.0034 | 3213 | 0.0035893 | 0.0003262
2013-01-18 06:47PM | 1586388-1 | X492 | Rural Long | Equipment Failure | 882 | 97.2937 | 85813 | 0.095863 | 0.0009853
2013-02-18 02:22PM | 1595172-1 | X492 | Rural Long | Operatonal Error | 292 | 35.0103 | 10223 | 0.01142 | 0.0003262
2012-10-21 11:39AM | 1563404-1 | X492 | Rural Long | Vegetation | 280 | 84.7321 | 23725 | 0.026504 | 0.00031279
2013-02-01 02:25PM | 1590706-1 | X492 | Rural Long | Weather | 300 | 51.0533 | 15316 | 0.01711 | 0.00033514
2012-10-19 11:08AM | 1563046-1 | X802 | Rural Short | Equipment Failure | 181 | 33.0055 | 5974 | 0.0066737 | 0.0002022
2012-12-17 10:55AM | 1579690-1 | X802 | Rural Short | Operatonal Error | 183 | 1.9945 | 365 | 0.00040775 | 0.00020443
2013-02-12 08:31AM | 1593753-1 | X802 | Rural Short | Other | 9 | 296 | 2664 | 0.002976 | 1.0054e-05
2012-08-29 08:16AM | 1552239-1 | X802 | Rural Short | Operatonal Error | 183 | 10.9836 | 2010 | 0.0022454 | 0.00020443
2013-01-18 06:47PM | 1586388-1 | X802 | Rural Short | Equipment Failure | 551 | 97.4047 | 53670 | 0.059956 | 0.00061553
2013-02-18 02:22PM | 1595172-1 | X802 | Rural Short | Operatonal Error | 183 | 34.9399 | 6394 | 0.0071429 | 0.00020443
2013-02-10 07:36PM | 1593343-1 | X802 | Rural Short | Weather | 198 | 8.298 | 1643 | 0.0018354 | 0.00022119
2012-07-17 10:40AM | 1538306-1 | X802 | Rural Short | Other | 38 | 176.7632 | 6717 | 0.0075037 | 4.2451e-05
2013-03-06 02:57PM | 1601379-1 | X802 | Rural Short | Equipment Failure | 18 | 320 | 5760 | 0.0064346 | 2.0108e-05
2013-06-25 08:50PM | 1628091-1 | X802 | Rural Short | Equipment Failure | 32 | 145.875 | 4668 | 0.0052147 | 3.5748e-05
2013-02-04 02:01PM | 1591377-1 | X802 | Rural Short | Other | 1 | 53 | 53 | 5.9207e-05 | 1.1171e-06
2013-04-16 08:50PM | 1610842-1 | X802 | Rural Short | Weather | 1 | 83 | 83 | 9.2721e-05 | 1.1171e-06
2013-04-17 09:57AM | 1610923-1 | X802 | Rural Short | Other | 1 | 282 | 282 | 0.00031503 | 1.1171e-06
2013-02-07 04:27PM | 1592568-1 | J499 | Urban | Equipment Failure | 18 | 47.5 | 855 | 0.00095514 | 2.0108e-05
2012-12-23 08:38PM | 1580015-1 | J499 | Urban | Third Party Impacts | 16 | 93 | 1488 | 0.0016623 | 1.7874e-05
2013-01-02 02:22PM | 1581858-1 | J499 | Urban | Third Party Impacts | 26 | 21.6154 | 562 | 0.00062782 | 2.9045e-05
2013-01-21 07:19PM | 1587090-1 | J499 | Urban | Third Party Impacts | 52 | 56 | 2912 | 0.0032531 | 5.809e-05
2012-07-15 11:21AM | 1537876-1 | J499 | Urban | Other | 17 | 427.8824 | 7274 | 0.0081259 | 1.8991e-05
2012-12-16 11:12AM | 1578243-1 | J499 | Urban | Third Party Impacts | 49 | 34.898 | 1710 | 0.0019103 | 5.4739e-05
2013-02-04 02:33PM | 1591439-1 | J499 | Urban | Other | 25 | 27.8 | 695 | 0.0007764 | 2.7928e-05
2012-10-16 02:00PM | 1562211-1 | J499 | Urban | Equipment Failure | 17 | 156 | 2652 | 0.0029626 | 1.8991e-05
2012-10-05 12:37PM | 1559304-1 | J499 | Urban | Equipment Failure | 952 | 62.4842 | 59485 | 0.066452 | 0.0010635
2012-09-07 10:17AM | 1552675-1 | J500 | Urban | Other | 55 | 48.7455 | 2681 | 0.002995 | 6.1442e-05
2013-05-22 11:19PM | 1619527-1 | J500 | Urban | Equipment Failure | 1 | 546 | 546 | 0.00060995 | 1.1171e-06
2013-06-21 01:03PM | 1626943-1 | J500 | Urban | Equipment Failure | 1 | 94 | 94 | 0.00010501 | 1.1171e-06
2013-06-15 11:57AM | 1625453-1 | J502 | Urban | Equipment Failure | 44 | 161.1818 | 7092 | 0.0079226 | 4.9153e-05
2012-11-07 11:32AM | 1567810-1 | J502 | Urban | Other | 46 | 257 | 11822 | 0.013207 | 5.1388e-05
2012-11-15 09:57AM | 1570028-1 | J502 | Urban | Equipment Failure | 17 | 32.1176 | 546 | 0.00060995 | 1.8991e-05
2013-04-04 05:09PM | 1607910-1 | J502 | Urban | Other | 1 | 959 | 959 | 0.0010713 | 1.1171e-06
2013-01-02 03:33PM | 1581876-1 | J503 | Urban | Other | 40 | 93 | 3720 | 0.0041557 | 4.4685e-05
2013-01-05 04:47PM | 1582626-1 | J503 | Urban | Equipment Failure | 7 | 175 | 1225 | 0.0013685 | 7.8198e-06
2012-12-05 12:39PM | 1575757-1 | 61617 | Rural Short | Weather | 450 | 99 | 44550 | 0.049768 | 0.0005027
2012-09-05 02:27PM | 1556153-1 | 61617 | Rural Short | Third Party Impacts | 448 | 17.0804 | 7652 | 0.0085482 | 0.00050047
2012-12-19 01:35PM | 1579071-1 | 61617 | Rural Short | Equipment Failure | 14 | 111.4286 | 1560 | 0.0017427 | 1.564e-05
2013-02-16 04:41AM | 1594822-1 | 61617 | Rural Short | Other | 20 | 345 | 6900 | 0.0077081 | 2.2342e-05
2013-01-15 08:54AM | 1585010-1 | 35503 | Urban | Equipment Failure | 5 | 50.4 | 252 | 0.00028151 | 5.5856e-06
2013-01-11 08:29PM | 1584203-1 | 35503 | Urban | Equipment Failure | 28 | 23.9286 | 670 | 0.00074847 | 3.1279e-05
2013-03-06 11:55AM | 1601249-1 | 35511 | Urban | Equipment Failure | 493 | 10.1075 | 4983 | 0.0055666 | 0.00055074
2013-04-23 02:00PM | 1612467-1 | 35514 | Urban | Other | 2 | 138 | 276 | 0.00030833 | 2.2342e-06
2012-09-15 08:14AM | 1554779-1 | L584 | Rural Short | Animals | 1 | 287 | 287 | 0.00032061 | 1.1171e-06
2013-03-07 09:10AM | 1601627-1 | L584 | Rural Short | Third Party Impacts | 5 | 115.8 | 579 | 0.00064681 | 5.5856e-06
2013-03-08 10:02AM | 1601972-1 | L584 | Rural Short | Third Party Impacts | 1 | 90 | 90 | 0.00010054 | 1.1171e-06
2013-03-09 01:57AM | 1602221-1 | L584 | Rural Short | Third Party Impacts | 1 | 61 | 61 | 6.8144e-05 | 1.1171e-06
2013-02-01 03:24PM | 1590788-1 | L584 | Rural Short | Weather | 2 | 131 | 262 | 0.00029269 | 2.2342e-06
2013-02-01 06:41PM | 1590881-1 | L584 | Rural Short | Other | 2 | 98 | 196 | 0.00021896 | 2.2342e-06
2012-12-25 02:43PM | 1580494-1 | L584 | Rural Short | Weather | 256 | 147 | 37632 | 0.042039 | 0.00028598
2013-01-17 06:30PM | 1590072-1 | L584 | Rural Short | Third Party Impacts | 2 | 20 | 40 | 4.4685e-05 | 2.2342e-06
2013-02-09 11:51PM | 1593143-1 | L584 | Rural Short | Weather | 18 | 596 | 10728 | 0.011984 | 2.0108e-05
2012-11-28 06:11AM | 1573403-1 | 35514 | Urban | Weather | 2 | 298 | 596 | 0.0006658 | 2.2342e-06
2012-12-23 08:45PM | 1580018-1 | 35514 | Urban | Equipment Failure | 1 | 228 | 228 | 0.0002547 | 1.1171e-06
2012-10-10 09:46AM | 1560284-1 | 35519 | Urban | Equipment Failure | 21 | 43.8571 | 921 | 0.0010289 | 2.346e-05
2012-12-09 07:20AM | 1576592-1 | 35519 | Urban | Equipment Failure | 1 | 206 | 206 | 0.00023013 | 1.1171e-06
2012-12-12 02:37PM | 1577478-1 | 35519 | Urban | Equipment Failure | 1 | 102 | 102 | 0.00011395 | 1.1171e-06
2012-12-25 01:33AM | 1580396-1 | 35524 | Urban | Other | 5 | 332 | 1660 | 0.0018544 | 5.5856e-06
2013-01-06 02:32AM | 1582689-1 | 35524 | Urban | Equipment Failure | 5 | 365.2 | 1826 | 0.0020399 | 5.5856e-06
2012-09-25 08:46PM | 1557014-1 | 35524 | Urban | Other | 689 | 2.6662 | 1837 | 0.0020521 | 0.0007697
2012-12-11 12:41PM | 1577051-1 | 35524 | Urban | Equipment Failure | 1 | 55 | 55 | 6.1442e-05 | 1.1171e-06
2012-10-30 01:37PM | 1565770-1 | 35528 | Urban | Equipment Failure | 14 | 123 | 1722 | 0.0019237 | 1.564e-05
2012-11-19 09:13AM | 1570782-1 | 35528 | Urban | Other | 1 | 260 | 260 | 0.00029045 | 1.1171e-06
2013-01-28 11:01PM | 1589414-1 | 35528 | Urban | Weather | 1 | 95 | 95 | 0.00010613 | 1.1171e-06
2012-10-23 07:02AM | 1563818-1 | 35530 | Urban | Other | 9 | 85.5556 | 770 | 0.00086018 | 1.0054e-05
2012-07-22 05:45PM | 1539580-1 | 35530 | Urban | Equipment Failure | 1 | 32 | 32 | 3.5748e-05 | 1.1171e-06
2013-01-22 02:24PM | 1587270-1 | 1950 | Urban | Weather | 12 | 72 | 864 | 0.00096519 | 1.3405e-05
2013-01-04 12:51PM | 1582328-1 | 1950 | Urban | Other | 5 | 29 | 145 | 0.00016198 | 5.5856e-06
2012-09-24 11:23PM | 1556768-1 | 1952 | Urban | Third Party Impacts | 712 | 36 | 25632 | 0.028634 | 0.00079539
2012-09-08 10:50AM | 1553134-1 | 1952 | Urban | Weather | 39 | 77.0769 | 3006 | 0.0033581 | 4.3568e-05
2012-07-31 06:05PM | 1541846-1 | 1953 | Urban | Equipment Failure | 12 | 85.5833 | 1027 | 0.0011473 | 1.3405e-05
2013-06-04 08:55AM | 1622734-1 | 1954 | Urban | Other | 1 | 91 | 91 | 0.00010166 | 1.1171e-06
2012-08-06 05:07PM | 1543255-1 | 1956 | Urban | Third Party Impacts | 31 | 74.2258 | 2301 | 0.0025705 | 3.4631e-05
2013-06-01 07:06PM | 1622257-1 | 1957 | Urban | Equipment Failure | 2 | 339 | 678 | 0.00075741 | 2.2342e-06
2012-10-22 06:54PM | 1563744-1 | 1957 | Urban | Equipment Failure | 56 | 82.625 | 4627 | 0.0051689 | 6.2559e-05
2013-01-18 11:47PM | 1586525-1 | 1957 | Urban | Vegetation | 1415 | 63.9124 | 90436 | 0.10103 | 0.0015807
2013-05-20 12:17PM | 1618738-1 | 1957 | Urban | Vegetation | 22 | 93 | 2046 | 0.0022856 | 2.4577e-05
2012-09-24 11:23PM | 1556769-1 | 1958 | Urban | Third Party Impacts | 152 | 37 | 5624 | 0.0062827 | 0.0001698
2012-09-11 10:56AM | 1553635-1 | 1958 | Urban | Other | 1 | 159 | 159 | 0.00017762 | 1.1171e-06
2012-12-07 11:36AM | 1576326-1 | 1958 | Urban | Equipment Failure | 1 | 174 | 174 | 0.00019438 | 1.1171e-06
2012-11-05 05:19PM | 1567328-1 | X802 | Rural Short | Equipment Failure | 1 | 155 | 155 | 0.00017315 | 1.1171e-06
2012-08-09 05:58PM | 1544239-1 | X802 | Rural Short | Other | 73 | 45.7534 | 3340 | 0.0037312 | 8.155e-05
2013-03-13 07:28PM | 1603268-1 | X802 | Rural Short | Other | 9 | 55 | 495 | 0.00055297 | 1.0054e-05
2012-07-28 07:49PM | 1541070-1 | X802 | Rural Short | Equipment Failure | 49 | 243.1224 | 11913 | 0.013308 | 5.4739e-05
2012-11-20 06:46PM | 1571398-1 | X802 | Rural Short | Equipment Failure | 187 | 80.1283 | 14984 | 0.016739 | 0.0002089
2012-10-19 11:08AM | 1563046-1 | X459 | Rural Short | Equipment Failure | 421 | 32.981 | 13885 | 0.015511 | 0.00047031
2012-12-17 10:55AM | 1579690-1 | X459 | Rural Short | Operatonal Error | 433 | 1.9977 | 865 | 0.00096631 | 0.00048371
2012-10-19 11:08AM | 1563046-1 | X463 | Rural Short | Equipment Failure | 284 | 33.0563 | 9388 | 0.010488 | 0.00031726
2012-12-17 10:55AM | 1579690-1 | X463 | Rural Short | Operatonal Error | 289 | 2 | 578 | 0.0006457 | 0.00032285
2012-11-18 06:39PM | 1573498-1 | KVA2 | Rural Short | Other | 289 | 5.3841 | 1556 | 0.0017382 | 0.00032285
2012-12-13 05:59PM | 1577744-1 | KVA2 | Rural Short | Other | 1 | 114 | 114 | 0.00012735 | 1.1171e-06
2012-09-28 10:26AM | 1557754-1 | KVA2 | Rural Short | Vegetation | 103 | 171.0485 | 17618 | 0.019681 | 0.00011506
2012-12-21 06:18PM | 1579740-1 | KVA2 | Rural Short | Vegetation | 103 | 93 | 9579 | 0.010701 | 0.00011506
2013-02-15 01:37AM | 1594563-1 | KVA2 | Rural Short | Vegetation | 103 | 87.2913 | 8991 | 0.010044 | 0.00011506
2012-10-18 09:51PM | 1562929-1 | KVA2 | Rural Short | Other | 20 | 113 | 2260 | 0.0025247 | 2.2342e-05
2012-09-28 06:22AM | 1557669-1 | KVA2 | Rural Short | Weather | 24 | 220.25 | 5286 | 0.0059051 | 2.6811e-05
2012-11-10 02:40PM | 1569010-1 | KVA2 | Rural Short | Equipment Failure | 20 | 116 | 2320 | 0.0025917 | 2.2342e-05
2013-01-10 09:52AM | 1583812-1 | KVA2 | Rural Short | Vegetation | 24 | 215 | 5160 | 0.0057643 | 2.6811e-05
2013-02-15 07:29AM | 1594585-1 | KVA2 | Rural Short | Vegetation | 12 | 552 | 6624 | 0.0073998 | 1.3405e-05
2012-10-23 08:56AM | 1563881-1 | KVA2 | Rural Short | Other | 1 | 176 | 176 | 0.00019661 | 1.1171e-06
2013-02-26 05:11PM | 1598726-1 | KVA2 | Rural Short | Equipment Failure | 18 | 88 | 1584 | 0.0017695 | 2.0108e-05
2012-10-02 08:08PM | 1558453-1 | KVA2 | Rural Short | Equipment Failure | 1 | 139 | 139 | 0.00015528 | 1.1171e-06
2013-02-19 02:53PM | 1595475-1 | KVA2 | Rural Short | Equipment Failure | 4 | 23.25 | 93 | 0.00010389 | 4.4685e-06
2012-12-22 07:37PM | 1579859-1 | KVA2 | Rural Short | Equipment Failure | 32 | 57 | 1824 | 0.0020376 | 3.5748e-05
2013-03-05 05:15PM | 1601030-1 | KVA2 | Rural Short | Equipment Failure | 58 | 23 | 1334 | 0.0014902 | 6.4793e-05
2013-04-14 05:01AM | 1610174-1 | KVA2 | Rural Short | Other | 126 | 73 | 9198 | 0.010275 | 0.00014076
2012-11-18 06:39PM | 1573498-1 | KVB2 | Rural Short | Other | 321 | 5.3832 | 1728 | 0.0019304 | 0.0003586
2013-02-13 10:13AM | 1594080-1 | KVB2 | Rural Short | Other | 2 | 112 | 224 | 0.00025023 | 2.2342e-06
2013-03-11 06:10PM | 1602693-1 | KVB2 | Rural Short | Weather | 2 | 68.5 | 137 | 0.00015305 | 2.2342e-06
2012-08-09 05:40PM | 1544236-1 | KVB2 | Rural Short | Weather | 339 | 204.0678 | 69179 | 0.077281 | 0.0003787
2012-08-31 07:30PM | 1551102-1 | KVB2 | Rural Short | Vegetation | 213 | 69.9437 | 14898 | 0.016643 | 0.00023795
2012-12-31 11:47PM | 1581584-1 | KVB2 | Rural Short | Vegetation | 214 | 8.4299 | 1804 | 0.0020153 | 0.00023906
2012-10-23 07:25AM | 1563840-1 | KVB2 | Rural Short | Other | 1 | 274 | 274 | 0.00030609 | 1.1171e-06
2012-08-08 01:24PM | 1543811-1 | KVB2 | Rural Short | Equipment Failure | 4 | 151 | 604 | 0.00067474 | 4.4685e-06
2012-11-18 06:42PM | 1570689-1 | KVB2 | Rural Short | Vegetation | 5 | 219.2 | 1096 | 0.0012244 | 5.5856e-06
2013-03-29 02:12PM | 1607030-1 | KVB2 | Rural Short | Equipment Failure | 2 | 246 | 492 | 0.00054962 | 2.2342e-06
2013-06-26 08:38AM | 1628171-1 | KVB2 | Rural Short | Weather | 11 | 169 | 1859 | 0.0020767 | 1.2288e-05
2012-08-31 07:29PM | 1551101-1 | KVB2 | Rural Short | Vegetation | 90 | 166.3333 | 14970 | 0.016723 | 0.00010054
2013-01-23 03:16PM | 1587776-1 | KVB2 | Rural Short | Vegetation | 22 | 40.4091 | 889 | 0.00099312 | 2.4577e-05
2013-01-18 08:22PM | 1586414-1 | KVB2 | Rural Short | Vegetation | 33 | 274.3939 | 9055 | 0.010116 | 3.6865e-05
2012-08-07 11:55AM | 1543455-1 | KVB2 | Rural Short | Vegetation | 133 | 92.4436 | 12295 | 0.013735 | 0.00014858
2012-08-10 11:18AM | 1544436-1 | KVB2 | Rural Short | Weather | 2 | 121 | 242 | 0.00027034 | 2.2342e-06
2013-01-21 04:19PM | 1587005-1 | KVB2 | Rural Short | Vegetation | 2 | 133 | 266 | 0.00029715 | 2.2342e-06
2013-03-22 12:35AM | 1605327-1 | KVB2 | Rural Short | Vegetation | 385 | 39.9792 | 15392 | 0.017195 | 0.00043009
2012-11-18 06:39PM | 1573498-1 | KVC2 | Rural Short | Other | 107 | 5.3738 | 575 | 0.00064234 | 0.00011953
2013-02-15 12:30PM | 1594700-1 | KVC2 | Rural Short | Other | 1 | 307 | 307 | 0.00034296 | 1.1171e-06
2013-01-19 02:58AM | 1586535-1 | KVC2 | Rural Short | Vegetation | 3 | 542 | 1626 | 0.0018164 | 3.3514e-06
2012-10-26 04:12AM | 1564773-1 | KVC2 | Rural Short | Other | 127 | 77 | 9779 | 0.010924 | 0.00014187
2012-11-18 07:18PM | 1570705-1 | KVC2 | Rural Short | Vegetation | 40 | 542.425 | 21697 | 0.024238 | 4.4685e-05
2013-04-15 09:40PM | 1610526-1 | KVC2 | Rural Short | Vegetation | 40 | 107.65 | 4306 | 0.0048103 | 4.4685e-05
2013-03-06 04:29PM | 1601463-1 | KVC2 | Rural Short | Other | 2 | 99 | 198 | 0.00022119 | 2.2342e-06
2013-01-19 12:06PM | 1586607-1 | KVC2 | Rural Short | Vegetation | 31 | 25.4194 | 788 | 0.00088029 | 3.4631e-05
2013-02-28 04:07PM | 1599392-1 | KVC2 | Rural Short | Vegetation | 31 | 107 | 3317 | 0.0037055 | 3.4631e-05
2012-11-18 06:39PM | 1573498-1 | KVD2 | Rural Short | Other | 78 | 5.3974 | 421 | 0.00047031 | 8.7135e-05
2012-12-23 06:05PM | 1579975-1 | KVD2 | Rural Short | Weather | 61 | 21.6885 | 1323 | 0.0014779 | 6.8144e-05
2013-03-21 10:39PM | 1605318-1 | KVD2 | Rural Short | Other | 11 | 906.2727 | 9969 | 0.011137 | 1.2288e-05
2012-12-19 04:20PM | 1579189-1 | KVD2 | Rural Short | Operatonal Error | 5 | 236.4 | 1182 | 0.0013204 | 5.5856e-06
2013-02-25 08:31PM | 1598404-1 | KVD2 | Rural Short | Other | 1 | 285 | 285 | 0.00031838 | 1.1171e-06
2012-10-14 05:46PM | 1561601-1 | 10241 | Urban | Vegetation | 1142 | 32.6497 | 37286 | 0.041653 | 0.0012758
2013-01-25 04:27PM | 1588585-1 | 10241 | Urban | Vegetation | 1143 | 31 | 35433 | 0.039583 | 0.0012769
2012-08-29 09:20PM | 1552438-1 | 10241 | Urban | Equipment Failure | 15 | 123 | 1845 | 0.0020611 | 1.6757e-05
2013-05-28 08:19AM | 1620897-1 | 10242 | Urban | Equipment Failure | 21 | 81 | 1701 | 0.0019002 | 2.346e-05
2013-04-03 03:34PM | 1607654-1 | 10242 | Urban | Equipment Failure | 1296 | 44.6551 | 57873 | 0.064651 | 0.0014478
2013-02-20 04:04PM | 1595824-1 | 10242 | Urban | Vegetation | 1296 | 39.6042 | 51327 | 0.057338 | 0.0014478
2013-02-25 07:31AM | 1597832-1 | 10242 | Urban | Weather | 1 | 183 | 183 | 0.00020443 | 1.1171e-06
2012-10-13 11:21AM | 1561471-1 | 10244 | Rural Short | Other | 28 | 49.1429 | 1376 | 0.0015372 | 3.1279e-05
2012-09-08 09:22AM | 1553094-1 | 10244 | Rural Short | Other | 2 | 149 | 298 | 0.0003329 | 2.2342e-06
2013-05-12 01:16AM | 1616696-1 | 10244 | Rural Short | Third Party Impacts | 911 | 55.8924 | 50918 | 0.056882 | 0.0010177
2013-05-12 08:00PM | 1616758-1 | 10244 | Rural Short | Equipment Failure | 376 | 83 | 31208 | 0.034863 | 0.00042004
2012-09-07 11:59PM | 1553058-1 | 10244 | Rural Short | Weather | 219 | 487.2877 | 106716 | 0.11921 | 0.00024465
2013-06-07 10:57AM | 1623640-1 | 10245 | Rural Short | Other | 1 | 174 | 174 | 0.00019438 | 1.1171e-06
2012-07-23 07:15PM | 1539863-1 | 10245 | Rural Short | Animals | 69 | 73.2609 | 5055 | 0.005647 | 7.7081e-05
2012-07-21 11:43PM | 1539511-1 | 10245 | Rural Short | Animals | 50 | 78.4 | 3920 | 0.0043791 | 5.5856e-05
2012-12-24 05:37AM | 1580038-1 | 10245 | Rural Short | Equipment Failure | 881 | 194.9398 | 171742 | 0.19186 | 0.00098418
2013-06-23 12:39PM | 1627238-1 | 10245 | Rural Short | Other | 1 | 102 | 102 | 0.00011395 | 1.1171e-06
2012-10-14 08:17AM | 1561558-1 | 10247 | Urban | Other | 19 | 229.9474 | 4369 | 0.0048807 | 2.1225e-05
2013-03-22 05:01PM | 1605582-1 | 10247 | Urban | Third Party Impacts | 1 | 181 | 181 | 0.0002022 | 1.1171e-06
2013-01-16 12:59AM | 1585271-1 | 10250 | Urban | Animals | 47 | 81.8085 | 3845 | 0.0042953 | 5.2505e-05
2012-09-06 03:07PM | 1552451-1 | 10250 | Urban | Weather | 958 | 54.9165 | 52610 | 0.058772 | 0.0010702
2013-05-06 10:38PM | 1615295-1 | 10250 | Urban | Other | 122 | 78.1475 | 9534 | 0.010651 | 0.00013629
2013-05-29 01:03PM | 1621365-1 | 10251 | Urban | Other | 1 | 52 | 52 | 5.809e-05 | 1.1171e-06
2012-10-15 09:14PM | 1561979-1 | 10251 | Urban | Vegetation | 116 | 61.8276 | 7172 | 0.008012 | 0.00012959
2013-02-10 06:14AM | 1593159-1 | 10251 | Urban | Animals | 1396 | 113.1669 | 157981 | 0.17648 | 0.0015595
2013-05-18 07:34AM | 1618425-1 | 10251 | Urban | Equipment Failure | 1397 | 139.8203 | 195329 | 0.21821 | 0.0015606
2012-12-23 07:26PM | 1579998-1 | 10251 | Urban | Weather | 97 | 127 | 12319 | 0.013762 | 0.00010836
2012-11-30 03:13AM | 1574050-1 | 10251 | Urban | Equipment Failure | 419 | 28 | 11732 | 0.013106 | 0.00046807
2013-03-10 06:02AM | 1602298-1 | 8647 | Urban | Operatonal Error | 603 | 15.01 | 9051 | 0.010111 | 0.00067362
2012-11-03 06:30AM | 1566756-1 | 8648 | Urban | Vegetation | 990 | 55.7333 | 55176 | 0.061638 | 0.0011059
2013-05-15 08:20AM | 1617399-1 | 8648 | Urban | Other | 23 | 129.1739 | 2971 | 0.003319 | 2.5694e-05
2012-12-27 09:24AM | 1580780-1 | 8648 | Urban | Equipment Failure | 10 | 336 | 3360 | 0.0037535 | 1.1171e-05
2013-03-10 06:02AM | 1602298-1 | 8648 | Urban | Operatonal Error | 794 | 15.0025 | 11912 | 0.013307 | 0.00088699
2012-08-17 12:38PM | 1546668-1 | 8650 | Urban | Weather | 1 | 533 | 533 | 0.00059542 | 1.1171e-06
2013-03-10 06:02AM | 1602298-1 | 8650 | Urban | Operatonal Error | 76 | 14.9342 | 1135 | 0.0012679 | 8.4901e-05
2012-08-29 07:58PM | 1550503-1 | 8651 | Urban | Equipment Failure | 1 | 92 | 92 | 0.00010278 | 1.1171e-06
2012-09-30 05:26AM | 1558122-1 | 8651 | Urban | Equipment Failure | 1 | 284 | 284 | 0.00031726 | 1.1171e-06
2013-03-10 06:02AM | 1602298-1 | 8651 | Urban | Operatonal Error | 584 | 15.0068 | 8764 | 0.0097904 | 0.0006524
2013-03-10 06:02AM | 1602298-1 | 8652 | Urban | Operatonal Error | 719 | 15.0097 | 10792 | 0.012056 | 0.00080321
2013-02-06 08:30PM | 1594752-1 | 25449 | Rural Short | Operatonal Error | 140 | 13.2786 | 1859 | 0.0020767 | 0.0001564
2012-07-04 06:19PM | 1535706-1 | 25449 | Rural Short | Third Party Impacts | 113 | 78.6018 | 8882 | 0.0099223 | 0.00012623
2012-12-05 11:28AM | 1575689-1 | 25449 | Rural Short | Vegetation | 147 | 43.1973 | 6350 | 0.0070937 | 0.00016422
2012-10-07 07:34AM | 1559509-1 | 25449 | Rural Short | Other | 23 | 139.2609 | 3203 | 0.0035781 | 2.5694e-05
2012-11-03 04:07PM | 1566892-1 | 25449 | Rural Short | Animals | 23 | 57.7391 | 1328 | 0.0014835 | 2.5694e-05
2013-04-09 05:04AM | 1608716-1 | 25449 | Rural Short | Third Party Impacts | 119 | 76.3529 | 9086 | 0.01015 | 0.00013294
2013-02-06 08:30PM | 1594752-1 | 25450 | Urban | Operatonal Error | 1181 | 13.3014 | 15709 | 0.017549 | 0.0013193
2012-12-24 07:19PM | 1580267-1 | 25450 | Urban | Weather | 1189 | 76.1733 | 90570 | 0.10118 | 0.0013283
2013-06-06 05:13AM | 1623320-1 | 25450 | Urban | Third Party Impacts | 18 | 173 | 3114 | 0.0034787 | 2.0108e-05
2013-04-29 11:30AM | 1613616-1 | 25450 | Urban | Third Party Impacts | 6 | 116.8333 | 701 | 0.0007831 | 6.7027e-06
2013-02-06 08:30PM | 1594752-1 | 25451 | Rural Short | Operatonal Error | 25 | 13.28 | 332 | 0.00037088 | 2.7928e-05
2013-03-06 08:19AM | 1601161-1 | 25451 | Rural Short | Other | 16 | 200.1875 | 3203 | 0.0035781 | 1.7874e-05
2013-06-24 11:42AM | 1627472-1 | KC1214 | Rural Short | Equipment Failure | 1 | 57 | 57 | 6.3676e-05 | 1.1171e-06
2013-03-15 04:30PM | 1603825-1 | KC1214 | Rural Short | Third Party Impacts | 8 | 180 | 1440 | 0.0016087 | 8.937e-06
2013-03-21 01:41PM | 1605190-1 | KC1214 | Rural Short | Equipment Failure | 8 | 41 | 328 | 0.00036642 | 8.937e-06
2012-07-10 09:27AM | 1536760-1 | KC1214 | Rural Short | Third Party Impacts | 7 | 62.7143 | 439 | 0.00049042 | 7.8198e-06
2012-08-07 08:17PM | 1543609-1 | KC1214 | Rural Short | Equipment Failure | 9 | 76.5556 | 689 | 0.0007697 | 1.0054e-05
2012-12-09 03:40PM | 1576652-1 | KC1214 | Rural Short | Other | 1 | 145 | 145 | 0.00016198 | 1.1171e-06
2012-12-20 07:36PM | 1579552-1 | KC1221 | Rural Short | Other | 11 | 101 | 1111 | 0.0012411 | 1.2288e-05
2012-08-10 03:42PM | 1544825-1 | KC1221 | Rural Short | Weather | 443 | 187.6433 | 83126 | 0.092862 | 0.00049488
2012-12-25 07:38AM | 1580417-1 | KC1236 | Rural Short | Weather | 4 | 131 | 524 | 0.00058537 | 4.4685e-06
2012-12-21 09:19AM | 1579613-1 | KC1236 | Rural Short | Other | 2 | 81 | 162 | 0.00018097 | 2.2342e-06
2013-01-28 08:12AM | 1589217-1 | KC1236 | Rural Short | Vegetation | 1 | 182 | 182 | 0.00020332 | 1.1171e-06
2013-01-09 11:09AM | 1583580-1 | KC1236 | Rural Short | Weather | 7 | 232.2857 | 1626 | 0.0018164 | 7.8198e-06
2013-04-24 03:16AM | 1612610-1 | KC1236 | Rural Short | Other | 95 | 203.2526 | 19309 | 0.02157 | 0.00010613
2013-04-24 10:36PM | 1612920-1 | KC1236 | Rural Short | Other | 95 | 0.97895 | 93 | 0.00010389 | 0.00010613
2013-02-06 03:05PM | 1592203-1 | KC1236 | Rural Short | Other | 11 | 178 | 1958 | 0.0021873 | 1.2288e-05
2013-04-10 11:29AM | 1609184-1 | KC1236 | Rural Short | Other | 12 | 133 | 1596 | 0.0017829 | 1.3405e-05
2013-04-25 06:51AM | 1612941-1 | KC1236 | Rural Short | Animals | 11 | 102 | 1122 | 0.0012534 | 1.2288e-05
2012-08-01 12:47PM | 1542026-1 | KC1236 | Rural Short | Equipment Failure | 232 | 84.8621 | 19688 | 0.021994 | 0.00025917
2012-09-07 04:18PM | 1552924-1 | KC1262 | Rural Short | Other | 1 | 369 | 369 | 0.00041222 | 1.1171e-06
2012-11-26 03:55PM | 1572795-1 | KC1262 | Rural Short | Weather | 170 | 57.2471 | 9732 | 0.010872 | 0.00018991
2013-05-20 12:58PM | 1618754-1 | KC1262 | Rural Short | Other | 1 | 100 | 100 | 0.00011171 | 1.1171e-06
2012-09-13 04:45AM | 1554184-1 | KC1262 | Rural Short | Equipment Failure | 3 | 101 | 303 | 0.00033849 | 3.3514e-06
2013-05-05 03:50PM | 1615020-1 | KC1284 | Rural Short | Vegetation | 1 | 264 | 264 | 0.00029492 | 1.1171e-06
2013-03-28 08:03AM | 1606801-1 | KC1284 | Rural Short | Equipment Failure | 25 | 191.92 | 4798 | 0.0053599 | 2.7928e-05
2013-02-03 11:04AM | 1591153-1 | KC1284 | Rural Short | Other | 9 | 348 | 3132 | 0.0034988 | 1.0054e-05
2013-06-23 08:40AM | 1627204-1 | KC1284 | Rural Short | Other | 1 | 285 | 285 | 0.00031838 | 1.1171e-06
2012-12-08 01:57PM | 1576551-1 | KC1284 | Rural Short | Vegetation | 308 | 50.0974 | 15430 | 0.017237 | 0.00034407
2012-11-05 07:12PM | 1567342-1 | KC1284 | Rural Short | Vegetation | 1 | 84 | 84 | 9.3838e-05 | 1.1171e-06
2013-01-14 05:22AM | 1584627-1 | KC1288 | Rural Short | Weather | 18 | 298.6111 | 5375 | 0.0060045 | 2.0108e-05
2012-11-16 08:12PM | 1570492-1 | KC1288 | Rural Short | Equipment Failure | 128 | 125.1016 | 16013 | 0.017888 | 0.00014299
2013-01-13 07:25PM | 1584504-1 | KC1288 | Rural Short | Equipment Failure | 350 | 137.4571 | 48110 | 0.053745 | 0.00039099
2012-11-08 09:50AM | 1569436-1 | KYA2 | Urban | Third Party Impacts | 1 | 210 | 210 | 0.0002346 | 1.1171e-06
2013-05-15 12:07PM | 1617472-1 | KYE2 | Urban | Equipment Failure | 5 | 63.2 | 316 | 0.00035301 | 5.5856e-06
2013-01-22 03:00PM | 1587304-1 | KYF2 | Urban | Weather | 298 | 3 | 894 | 0.00099871 | 0.0003329
2013-01-22 03:00PM | 1587305-1 | KYH2 | Urban | Weather | 320 | 4 | 1280 | 0.0014299 | 0.00035748
2013-06-30 11:23AM | 1629346-1 | S735 | Rural Short | Operatonal Error | 805 | 8.6509 | 6964 | 0.0077796 | 0.00089928
2013-01-22 04:01PM | 1587359-1 | S737 | Rural Short | Weather | 21 | 137 | 2877 | 0.003214 | 2.346e-05
2013-03-12 12:05PM | 1602844-1 | S737 | Rural Short | Equipment Failure | 9 | 188 | 1692 | 0.0018902 | 1.0054e-05
2013-01-13 05:56PM | 1584466-1 | S737 | Rural Short | Equipment Failure | 8 | 21 | 168 | 0.00018768 | 8.937e-06
2013-02-10 09:25PM | 1593380-1 | S737 | Rural Short | Equipment Failure | 4 | 115 | 460 | 0.00051388 | 4.4685e-06
2013-06-30 11:23AM | 1629346-1 | S737 | Rural Short | Operatonal Error | 885 | 8.6475 | 7653 | 0.0085493 | 0.00098865
2012-12-05 04:34PM | 1575892-1 | S738 | Rural Short | Other | 20 | 255.85 | 5117 | 0.0057163 | 2.2342e-05
2013-02-07 09:00PM | 1592634-1 | S738 | Rural Short | Equipment Failure | 6 | 126 | 756 | 0.00084454 | 6.7027e-06
2012-09-21 09:31PM | 1556329-1 | S738 | Rural Short | Equipment Failure | 1 | 152 | 152 | 0.0001698 | 1.1171e-06
2013-01-01 12:08AM | 1581586-1 | S738 | Rural Short | Vegetation | 28 | 721 | 20188 | 0.022552 | 3.1279e-05
2013-02-02 06:13PM | 1591102-1 | S738 | Rural Short | Equipment Failure | 33 | 34 | 1122 | 0.0012534 | 3.6865e-05
2013-06-30 11:23AM | 1629346-1 | S738 | Rural Short | Operatonal Error | 448 | 8.6496 | 3875 | 0.0043288 | 0.00050047
2013-05-26 09:36AM | 1620221-1 | S738 | Rural Short | Equipment Failure | 78 | 28.6795 | 2237 | 0.002499 | 8.7135e-05
2013-03-12 01:55PM | 1602883-1 | S738 | Rural Short | Vegetation | 967 | 78 | 75426 | 0.08426 | 0.0010803
2013-04-19 04:52PM | 1611625-1 | S738 | Rural Short | Weather | 967 | 94 | 90898 | 0.10154 | 0.0010803
2012-12-23 06:47PM | 1579989-1 | S740 | Rural Short | Vegetation | 1 | 250 | 250 | 0.00027928 | 1.1171e-06
2013-06-30 11:23AM | 1629346-1 | S740 | Rural Short | Operatonal Error | 714 | 8.6541 | 6179 | 0.0069027 | 0.00079762
2012-09-07 01:03PM | 1552753-1 | S740 | Rural Short | Weather | 117 | 98.453 | 11519 | 0.012868 | 0.0001307
2013-01-09 05:59AM | 1583472-1 | S740 | Rural Short | Other | 117 | 46.1624 | 5401 | 0.0060336 | 0.0001307
2013-02-10 09:29PM | 1593382-1 | S740 | Rural Short | Weather | 117 | 66.3162 | 7759 | 0.0086677 | 0.0001307
2013-04-19 12:35PM | 1611530-1 | S740 | Rural Short | Weather | 117 | 70 | 8190 | 0.0091492 | 0.0001307
2013-05-23 01:15AM | 1619533-1 | S740 | Rural Short | Vegetation | 439 | 72.7335 | 31930 | 0.03567 | 0.00049042
2012-10-19 05:32PM | 1563199-1 | S741 | Rural Short | Other | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2012-12-01 02:37PM | 1574657-1 | S741 | Rural Short | Other | 8 | 52 | 416 | 0.00046472 | 8.937e-06
2012-10-15 08:19AM | 1561646-1 | S741 | Rural Short | Vegetation | 6 | 54.5 | 327 | 0.0003653 | 6.7027e-06
2013-06-30 11:23AM | 1629346-1 | S741 | Rural Short | Operatonal Error | 856 | 8.6519 | 7406 | 0.0082734 | 0.00095625
2012-08-17 02:41PM | 1546869-1 | S741 | Rural Short | Weather | 1 | 207 | 207 | 0.00023124 | 1.1171e-06
2012-08-13 08:48AM | 1545317-1 | S741 | Rural Short | Vegetation | 17 | 41.9412 | 713 | 0.00079651 | 1.8991e-05
2012-09-28 10:14PM | 1557997-1 | S741 | Rural Short | Equipment Failure | 164 | 5.1524 | 845 | 0.00094397 | 0.00018321
2012-08-10 05:12PM | 1544907-1 | S743 | Rural Short | Weather | 15 | 67.3333 | 1010 | 0.0011283 | 1.6757e-05
2012-08-24 05:02PM | 1549314-1 | S743 | Rural Short | Weather | 9 | 103.8889 | 935 | 0.0010445 | 1.0054e-05
2012-08-25 11:29AM | 1549450-1 | S743 | Rural Short | Equipment Failure | 1 | 321 | 321 | 0.0003586 | 1.1171e-06
2013-06-06 03:01PM | 1623504-1 | S743 | Rural Short | Other | 1 | 103 | 103 | 0.00011506 | 1.1171e-06
2012-07-27 07:17PM | 1541002-1 | S743 | Rural Short | Other | 1 | 135 | 135 | 0.00015081 | 1.1171e-06
2013-06-30 11:23AM | 1629346-1 | S743 | Rural Short | Operatonal Error | 717 | 8.6541 | 6205 | 0.0069317 | 0.00080098
2012-08-24 08:16AM | 1549060-1 | S743 | Rural Short | Weather | 15 | 99 | 1485 | 0.0016589 | 1.6757e-05
2012-11-09 05:14PM | 1568907-1 | S743 | Rural Short | Other | 1 | 240 | 240 | 0.00026811 | 1.1171e-06
2013-01-28 06:39AM | 1589207-1 | S743 | Rural Short | Equipment Failure | 32 | 39 | 1248 | 0.0013942 | 3.5748e-05
2012-10-29 06:25PM | 1565528-1 | S743 | Rural Short | Vegetation | 837 | 62.7324 | 52507 | 0.058657 | 0.00093503
2012-11-14 08:25AM | 1569709-1 | S743 | Rural Short | Animals | 1 | 383 | 383 | 0.00042786 | 1.1171e-06
2013-06-30 11:23AM | 1629346-1 | S744 | Urban | Operatonal Error | 570 | 8.6561 | 4934 | 0.0055119 | 0.00063676
2013-01-24 05:11PM | 1588064-1 | S744 | Urban | Equipment Failure | 25 | 70.12 | 1753 | 0.0019583 | 2.7928e-05
2013-06-17 12:10PM | 1628710-1 | S744 | Urban | Equipment Failure | 1 | 20 | 20 | 2.2342e-05 | 1.1171e-06
2013-04-06 11:31PM | 1608404-1 | J489 | Urban | Equipment Failure | 14 | 185 | 2590 | 0.0028933 | 1.564e-05
2013-06-27 07:59AM | 1628550-1 | J489 | Urban | Equipment Failure | 335 | 73.3612 | 24576 | 0.027454 | 0.00037424
2012-11-08 06:00PM | 1568457-1 | J489 | Urban | Weather | 97 | 302 | 29294 | 0.032725 | 0.00010836
2012-11-21 08:40AM | 1571488-1 | J489 | Urban | Other | 1 | 325 | 325 | 0.00036306 | 1.1171e-06
2012-09-28 09:39AM | 1557703-1 | J491 | Urban | Other | 1 | 41 | 41 | 4.5802e-05 | 1.1171e-06
2013-02-21 07:19PM | 1596254-1 | J491 | Urban | Other | 5 | 90 | 450 | 0.0005027 | 5.5856e-06
2013-01-16 08:11AM | 1585302-1 | J491 | Urban | Other | 70 | 103.5286 | 7247 | 0.0080958 | 7.8198e-05
2013-06-13 01:16PM | 1624929-1 | J491 | Urban | Equipment Failure | 12 | 59.9167 | 719 | 0.00080321 | 1.3405e-05
2012-11-21 03:39PM | 1571681-1 | J492 | Urban | Vegetation | 1 | 197 | 197 | 0.00022007 | 1.1171e-06
2012-07-04 03:51PM | 1535650-1 | J493 | Urban | Other | 47 | 44.5319 | 2093 | 0.0023381 | 5.2505e-05
2013-02-01 02:17PM | 1590699-1 | J493 | Urban | Equipment Failure | 24 | 32.9583 | 791 | 0.00088364 | 2.6811e-05
2013-03-19 01:47PM | 1604586-1 | J497 | Urban | Vegetation | 8 | 26.625 | 213 | 0.00023795 | 8.937e-06
2013-05-24 02:49PM | 1620112-1 | J497 | Urban | Equipment Failure | 1 | 203 | 203 | 0.00022678 | 1.1171e-06
2012-09-10 03:55AM | 1553328-1 | J499 | Urban | Other | 14 | 262 | 3668 | 0.0040976 | 1.564e-05
2012-09-10 08:54AM | 1553364-1 | J499 | Urban | Equipment Failure | 14 | 248 | 3472 | 0.0038786 | 1.564e-05
2012-11-06 06:49AM | 1567406-1 | J499 | Urban | Other | 9 | 117 | 1053 | 0.0011763 | 1.0054e-05
2012-11-06 01:06PM | 1567488-1 | J499 | Urban | Equipment Failure | 1 | 260 | 260 | 0.00029045 | 1.1171e-06
2012-11-07 09:02AM | 1567721-1 | J499 | Urban | Equipment Failure | 35 | 189.5143 | 6633 | 0.0074099 | 3.9099e-05
2013-01-21 08:45PM | 1587099-1 | J499 | Urban | Other | 42 | 45 | 1890 | 0.0021114 | 4.6919e-05
2013-06-05 08:12PM | 1623289-1 | J499 | Urban | Equipment Failure | 19 | 568 | 10792 | 0.012056 | 2.1225e-05
2013-01-27 04:48AM | 1588978-1 | J503 | Urban | Other | 62 | 181 | 11222 | 0.012536 | 6.9261e-05
2013-01-27 11:57AM | 1589119-1 | J503 | Urban | Other | 7 | 161 | 1127 | 0.001259 | 7.8198e-06
2013-01-28 01:07AM | 1589188-1 | J503 | Urban | Weather | 20 | 221 | 4420 | 0.0049377 | 2.2342e-05
2012-07-01 09:20AM | 1534588-1 | J504 | Urban | Equipment Failure | 51 | 179 | 9129 | 0.010198 | 5.6973e-05
2013-06-22 01:41AM | 1627084-1 | J504 | Urban | Equipment Failure | 51 | 297 | 15147 | 0.016921 | 5.6973e-05
2012-09-04 10:34AM | 1551660-1 | J504 | Urban | Other | 1 | 16 | 16 | 1.7874e-05 | 1.1171e-06
2013-06-14 03:26PM | 1625342-1 | J504 | Urban | Vegetation | 1296 | 118.6304 | 153745 | 0.17175 | 0.0014478
2012-12-25 12:09AM | 1580383-1 | J504 | Urban | Equipment Failure | 1 | 510 | 510 | 0.00056973 | 1.1171e-06
2013-01-16 05:27PM | 1585471-1 | KMA2 | Urban | Equipment Failure | 1838 | 11.9984 | 22053 | 0.024636 | 0.0020533
2013-06-27 05:10PM | 1628815-1 | KMA2 | Urban | Equipment Failure | 80 | 178.35 | 14268 | 0.015939 | 8.937e-05
2013-05-29 01:55AM | 1621306-1 | KMA2 | Urban | Equipment Failure | 32 | 773 | 24736 | 0.027633 | 3.5748e-05
2012-08-10 08:20PM | 1544983-1 | KMA2 | Urban | Weather | 103 | 260 | 26780 | 0.029916 | 0.00011506
2013-04-08 02:56PM | 1608633-1 | KMA2 | Urban | Other | 40 | 14 | 560 | 0.00062559 | 4.4685e-05
2012-08-10 03:48PM | 1544865-1 | KMA2 | Urban | Weather | 1384 | 154.2132 | 213431 | 0.23843 | 0.0015461
2012-08-11 08:37AM | 1545049-1 | KMA2 | Urban | Weather | 1384 | 209.0275 | 289294 | 0.32318 | 0.0015461
2013-01-16 05:27PM | 1585471-1 | KMB2 | Urban | Equipment Failure | 1902 | 11.9989 | 22822 | 0.025495 | 0.0021248
2013-01-10 02:09PM | 1583848-1 | KMB2 | Urban | Equipment Failure | 105 | 208.619 | 21905 | 0.024471 | 0.0001173
2012-09-25 05:33PM | 1556999-1 | KMB2 | Urban | Equipment Failure | 2 | 61 | 122 | 0.00013629 | 2.2342e-06
2012-10-06 05:57AM | 1559408-1 | KMB2 | Urban | Weather | 1430 | 128.6497 | 183969 | 0.20552 | 0.0015975
2013-01-07 01:38PM | 1582902-1 | KMB2 | Urban | Equipment Failure | 1430 | 38.2259 | 54663 | 0.061065 | 0.0015975
2013-01-10 07:10AM | 1583746-1 | KMB2 | Urban | Operatonal Error | 1431 | 14.2998 | 20463 | 0.02286 | 0.0015986
2013-01-10 02:38PM | 1583857-1 | KMB2 | Urban | Equipment Failure | 1360 | 4.4331 | 6029 | 0.0067351 | 0.0015193
2012-08-21 09:36AM | 1547672-1 | KMB2 | Urban | Equipment Failure | 1 | 48 | 48 | 5.3622e-05 | 1.1171e-06
2013-03-18 05:12PM | 1604427-1 | KMB2 | Urban | Other | 1 | 78 | 78 | 8.7135e-05 | 1.1171e-06
2013-01-16 05:27PM | 1585471-1 | KMC2 | Urban | Equipment Failure | 597 | 11.9966 | 7162 | 0.0080008 | 0.00066692
2013-06-23 08:10AM | 1627195-1 | KMC2 | Urban | Equipment Failure | 10 | 207.9 | 2079 | 0.0023225 | 1.1171e-05
2013-04-11 09:46AM | 1609470-1 | KMC2 | Urban | Other | 1 | 257 | 257 | 0.0002871 | 1.1171e-06
2013-01-16 05:27PM | 1585471-1 | KMD2 | Urban | Equipment Failure | 1713 | 12.0023 | 20560 | 0.022968 | 0.0019136
2012-10-04 03:31PM | 1559001-1 | KMD2 | Urban | Equipment Failure | 61 | 4 | 244 | 0.00027258 | 6.8144e-05
2013-05-02 06:13PM | 1614591-1 | KMD2 | Urban | Other | 35 | 59 | 2065 | 0.0023069 | 3.9099e-05
2013-06-12 02:50PM | 1624677-1 | KMD2 | Urban | Other | 35 | 140.6571 | 4923 | 0.0054996 | 3.9099e-05
2013-03-31 07:29AM | 1607137-1 | KMD2 | Urban | Animals | 385 | 58 | 22330 | 0.024945 | 0.00043009
2013-01-16 05:27PM | 1585471-1 | KME2 | Rural Short | Equipment Failure | 1116 | 12.0054 | 13398 | 0.014967 | 0.0012467
2013-01-23 07:48AM | 1587574-1 | KME2 | Rural Short | Other | 1 | 299 | 299 | 0.00033402 | 1.1171e-06
2013-03-28 08:35AM | 1606811-1 | KME2 | Rural Short | Equipment Failure | 5 | 203.4 | 1017 | 0.0011361 | 5.5856e-06
2013-01-10 02:38PM | 1583858-1 | KME2 | Rural Short | Equipment Failure | 849 | 3.9329 | 3339 | 0.0037301 | 0.00094843
2013-06-29 11:46PM | 1629319-1 | KME2 | Rural Short | Animals | 865 | 183.5676 | 158786 | 0.17738 | 0.00096631
2013-06-27 09:13AM | 1628560-1 | KME2 | Rural Short | Equipment Failure | 61 | 23.5246 | 1435 | 0.0016031 | 6.8144e-05
2013-02-17 06:45PM | 1595015-1 | KME2 | Rural Short | Equipment Failure | 1 | 119 | 119 | 0.00013294 | 1.1171e-06
2013-01-16 05:27PM | 1585471-1 | KMF2 | Urban | Equipment Failure | 1899 | 12.0016 | 22791 | 0.02546 | 0.0021214
2013-01-17 11:36AM | 1585650-1 | KMF2 | Urban | Equipment Failure | 58 | 134.5172 | 7802 | 0.0087158 | 6.4793e-05
2012-07-13 08:49AM | 1537547-1 | KMF2 | Urban | Equipment Failure | 52 | 64.6154 | 3360 | 0.0037535 | 5.809e-05
2013-06-25 03:12PM | 1627974-1 | KMF2 | Urban | Equipment Failure | 1 | 188 | 188 | 0.00021002 | 1.1171e-06
2012-08-11 11:31AM | 1545072-1 | KMF2 | Urban | Equipment Failure | 1451 | 2.9828 | 4328 | 0.0048349 | 0.0016209
2013-03-15 02:31AM | 1603622-1 | KMF2 | Urban | Equipment Failure | 1452 | 107.292 | 155788 | 0.17403 | 0.0016221
2012-07-16 10:01AM | 1537997-1 | 9016 | Urban | Other | 109 | 146.9083 | 16013 | 0.017888 | 0.00012177
2013-02-25 05:44PM | 1598293-1 | 9017 | Urban | Weather | 52 | 100 | 5200 | 0.005809 | 5.809e-05
2012-11-14 10:21AM | 1569763-1 | 9019 | Urban | Equipment Failure | 37 | 55 | 2035 | 0.0022733 | 4.1333e-05
2013-05-22 08:28AM | 1619228-1 | 9019 | Urban | Other | 1 | 149 | 149 | 0.00016645 | 1.1171e-06
2012-07-31 05:52PM | 1541847-1 | 9019 | Urban | Other | 1976 | 120.7257 | 238554 | 0.26649 | 0.0022074
2012-10-01 01:56AM | 1558192-1 | 9019 | Urban | Other | 1 | 599 | 599 | 0.00066915 | 1.1171e-06
2012-10-08 04:07PM | 1559823-1 | 9019 | Urban | Other | 1 | 243 | 243 | 0.00027146 | 1.1171e-06
2013-03-10 03:19PM | 1602376-1 | 9019 | Urban | Other | 1 | 352 | 352 | 0.00039323 | 1.1171e-06
2013-02-03 07:07PM | 1591190-1 | 9020 | Urban | Other | 18 | 76.2222 | 1372 | 0.0015327 | 2.0108e-05
2013-05-31 10:09PM | 1622181-1 | 9020 | Urban | Other | 1 | 143 | 143 | 0.00015975 | 1.1171e-06
2013-01-09 12:46PM | 1583611-1 | 9020 | Urban | Equipment Failure | 14 | 126.6429 | 1773 | 0.0019807 | 1.564e-05
2013-01-09 03:06PM | 1583664-1 | 9020 | Urban | Equipment Failure | 14 | 519.1429 | 7268 | 0.0081192 | 1.564e-05
2013-02-08 05:43PM | 1592889-1 | 9020 | Urban | Equipment Failure | 20 | 200.85 | 4017 | 0.0044875 | 2.2342e-05
2012-12-24 03:55PM | 1580149-1 | 9022 | Urban | Weather | 1006 | 63.831 | 64214 | 0.071735 | 0.0011238
2013-05-06 04:03PM | 1615249-1 | 9025 | Urban | Other | 37 | 81 | 2997 | 0.003348 | 4.1333e-05
2013-06-23 06:22AM | 1627193-1 | 9025 | Urban | Equipment Failure | 58 | 69.8103 | 4049 | 0.0045232 | 6.4793e-05
2012-08-04 03:23PM | 1542920-1 | 9025 | Urban | Equipment Failure | 30 | 133.9333 | 4018 | 0.0044886 | 3.3514e-05
2012-10-04 08:02AM | 1558794-1 | 9025 | Urban | Other | 86 | 321.8256 | 27677 | 0.030919 | 9.6072e-05
2012-10-14 12:23AM | 1561546-1 | 9025 | Urban | Other | 10 | 364.1 | 3641 | 0.0040674 | 1.1171e-05
2013-06-13 07:03AM | 1624826-1 | 9025 | Urban | Equipment Failure | 1 | 115 | 115 | 0.00012847 | 1.1171e-06
2013-06-23 12:19PM | 1627236-1 | 9025 | Urban | Equipment Failure | 58 | 246.0172 | 14269 | 0.01594 | 6.4793e-05
2013-06-25 11:59AM | 1627888-1 | 9025 | Urban | Weather | 16 | 290 | 4640 | 0.0051834 | 1.7874e-05
2013-06-24 08:46PM | 1627604-1 | 9025 | Urban | Equipment Failure | 17 | 255.7059 | 4347 | 0.0048561 | 1.8991e-05
2013-02-26 10:21AM | 1598544-1 | 9025 | Urban | Other | 61 | 45 | 2745 | 0.0030665 | 6.8144e-05
2012-12-07 05:50PM | 1576486-1 | 9025 | Urban | Other | 40 | 81 | 3240 | 0.0036195 | 4.4685e-05
2012-08-29 08:55AM | 1550240-1 | 9027 | Urban | Equipment Failure | 6 | 198.8333 | 1193 | 0.0013327 | 6.7027e-06
2012-12-22 09:03AM | 1579771-1 | 9029 | Urban | Equipment Failure | 36 | 57 | 2052 | 0.0022923 | 4.0216e-05
2013-02-25 05:52PM | 1598297-1 | 9030 | Urban | Weather | 835 | 15.0862 | 12597 | 0.014072 | 0.0009328
2012-07-19 08:14AM | 1538735-1 | 9032 | Urban | Equipment Failure | 1246 | 118.7745 | 147993 | 0.16533 | 0.0013919
2013-01-27 04:11AM | 1588964-1 | 9032 | Urban | Third Party Impacts | 1329 | 80.2423 | 106642 | 0.11913 | 0.0014847
2013-05-20 11:17AM | 1618708-1 | 9032 | Urban | Equipment Failure | 69 | 65.0145 | 4486 | 0.0050114 | 7.7081e-05
2013-02-28 10:23AM | 1599262-1 | 9032 | Urban | Vegetation | 2 | 16 | 32 | 3.5748e-05 | 2.2342e-06
2012-12-28 09:56AM | 1581047-1 | 9033 | Urban | Equipment Failure | 935 | 5.0396 | 4712 | 0.0052639 | 0.0010445
2013-03-04 05:26AM | 1600369-1 | 9033 | Urban | Equipment Failure | 1104 | 69.4149 | 76634 | 0.085609 | 0.0012333
2012-12-20 10:59AM | 1579348-1 | 9034 | Urban | Equipment Failure | 68 | 305 | 20740 | 0.023169 | 7.5964e-05
2013-01-18 04:49PM | 1586224-1 | 9034 | Urban | Weather | 2 | 170.5 | 341 | 0.00038094 | 2.2342e-06
2013-02-25 05:03PM | 1598267-1 | 9034 | Urban | Weather | 2 | 212 | 424 | 0.00047366 | 2.2342e-06
2013-02-27 05:59PM | 1599141-1 | 9034 | Urban | Other | 2 | 77 | 154 | 0.00017204 | 2.2342e-06
2013-04-16 04:41AM | 1610582-1 | 8798 | Rural Short | Weather | 15 | 189 | 2835 | 0.003167 | 1.6757e-05
2012-09-11 09:27AM | 1553604-1 | 8798 | Rural Short | Other | 1 | 53 | 53 | 5.9207e-05 | 1.1171e-06
2012-10-29 07:39PM | 1565539-1 | 8798 | Rural Short | Equipment Failure | 15 | 52.0667 | 781 | 0.00087247 | 1.6757e-05
2012-12-04 05:22PM | 1575438-1 | 8798 | Rural Short | Third Party Impacts | 1081 | 115.2442 | 124579 | 0.13917 | 0.0012076
2013-04-15 09:29PM | 1610522-1 | 8798 | Rural Short | Weather | 207 | 156.343 | 32363 | 0.036153 | 0.00023124
2013-03-10 04:17PM | 1602387-1 | 8798 | Rural Short | Operatonal Error | 1 | 65 | 65 | 7.2613e-05 | 1.1171e-06
2012-12-02 09:26AM | 1574759-1 | 8799 | Rural Short | Vegetation | 28 | 172 | 4816 | 0.00538 | 3.1279e-05
2013-01-26 05:24AM | 1588848-1 | 8799 | Rural Short | Other | 38 | 66 | 2508 | 0.0028017 | 4.2451e-05
2012-12-15 08:37AM | 1578137-1 | 8799 | Rural Short | Other | 9 | 160 | 1440 | 0.0016087 | 1.0054e-05
2012-11-08 11:14PM | 1568616-1 | 8799 | Rural Short | Weather | 45 | 680 | 30600 | 0.034184 | 5.027e-05
2012-11-27 08:01AM | 1572991-1 | 8799 | Rural Short | Weather | 2 | 492 | 984 | 0.0010992 | 2.2342e-06
2012-12-09 08:03AM | 1576596-1 | 8799 | Rural Short | Other | 1 | 191 | 191 | 0.00021337 | 1.1171e-06
2013-01-26 04:18PM | 1588899-1 | 8799 | Rural Short | Equipment Failure | 48 | 144.25 | 6924 | 0.0077349 | 5.3622e-05
2012-09-06 03:42PM | 1552402-1 | 8799 | Rural Short | Weather | 4 | 321 | 1284 | 0.0014344 | 4.4685e-06
2012-12-23 05:01PM | 1579952-1 | 8799 | Rural Short | Vegetation | 1093 | 135.2754 | 147856 | 0.16517 | 0.001221
2012-12-25 08:36AM | 1580427-1 | 8799 | Rural Short | Weather | 1093 | 122.7136 | 134126 | 0.14983 | 0.001221
2013-05-28 02:33PM | 1621037-1 | 8799 | Rural Short | Vegetation | 289 | 3.0588 | 884 | 0.00098753 | 0.00032285
2012-11-26 05:57PM | 1572843-1 | 8799 | Rural Short | Weather | 15 | 135.7333 | 2036 | 0.0022745 | 1.6757e-05
2012-10-28 11:00AM | 1565210-1 | 8799 | Rural Short | Other | 5 | 81.4 | 407 | 0.00045467 | 5.5856e-06
2012-11-26 05:01PM | 1572820-1 | 8799 | Rural Short | Weather | 19 | 164.4737 | 3125 | 0.003491 | 2.1225e-05
2013-02-01 03:02PM | 1590746-1 | 8801 | Rural Short | Weather | 9 | 174 | 1566 | 0.0017494 | 1.0054e-05
2012-12-03 03:11PM | 1575063-1 | 8801 | Rural Short | Other | 9 | 65.1111 | 586 | 0.00065463 | 1.0054e-05
2013-02-19 05:36PM | 1601342-1 | 8801 | Rural Short | Operatonal Error | 89 | 39 | 3471 | 0.0038775 | 9.9424e-05
2013-01-01 11:39AM | 1581621-1 | 8801 | Rural Short | Vegetation | 168 | 170.7798 | 28691 | 0.032051 | 0.00018768
2013-01-12 05:23PM | 1584297-1 | 8801 | Rural Short | Vegetation | 168 | 169.5833 | 28490 | 0.031827 | 0.00018768
2013-02-10 07:05PM | 1593298-1 | 8801 | Rural Short | Weather | 167 | 205 | 34235 | 0.038245 | 0.00018656
2012-08-24 02:05PM | 1549203-1 | 8801 | Rural Short | Weather | 4 | 108.25 | 433 | 0.00048371 | 4.4685e-06
2012-11-26 04:23PM | 1572809-1 | 8801 | Rural Short | Weather | 334 | 185.3353 | 61902 | 0.069152 | 0.00037312
2013-02-10 07:05PM | 1593299-1 | 8801 | Rural Short | Weather | 167 | 204 | 34068 | 0.038058 | 0.00018656
2013-05-28 02:34PM | 1621038-1 | 8801 | Rural Short | Vegetation | 1080 | 86.1444 | 93036 | 0.10393 | 0.0012065
2013-01-10 10:45PM | 1583923-1 | 8802 | Rural Short | Other | 12 | 47.4167 | 569 | 0.00063564 | 1.3405e-05
2012-09-10 04:10PM | 1553518-1 | 8802 | Rural Short | Equipment Failure | 11 | 183.8182 | 2022 | 0.0022588 | 1.2288e-05
2012-07-08 09:30AM | 1536397-1 | 8802 | Rural Short | Equipment Failure | 10 | 48.1 | 481 | 0.00053733 | 1.1171e-05
2013-02-17 07:31AM | 1594922-1 | 8802 | Rural Short | Equipment Failure | 13 | 115 | 1495 | 0.0016701 | 1.4523e-05
2012-10-06 06:42PM | 1559479-1 | 8802 | Rural Short | Other | 3 | 146.3333 | 439 | 0.00049042 | 3.3514e-06
2012-12-01 10:10AM | 1574614-1 | 8802 | Rural Short | Weather | 3 | 350 | 1050 | 0.001173 | 3.3514e-06
2012-08-17 02:27PM | 1546852-1 | 8802 | Rural Short | Weather | 648 | 197.0833 | 127710 | 0.14267 | 0.00072389
2013-04-08 04:29PM | 1608658-1 | 8802 | Rural Short | Vegetation | 653 | 110 | 71830 | 0.080243 | 0.00072948
2013-03-23 07:36PM | 1605814-1 | 8802 | Rural Short | Other | 1038 | 123.6291 | 128327 | 0.14336 | 0.0011596
2012-12-25 03:52PM | 1580544-1 | 8802 | Rural Short | Weather | 265 | 27 | 7155 | 0.007993 | 0.00029604
2012-11-30 07:15PM | 1574465-1 | 8802 | Rural Short | Weather | 1 | 281 | 281 | 0.00031391 | 1.1171e-06
2012-12-01 01:29AM | 1574526-1 | 8802 | Rural Short | Weather | 3 | 511 | 1533 | 0.0017125 | 3.3514e-06
2012-11-30 07:38PM | 1574474-1 | 8802 | Rural Short | Weather | 1 | 252 | 252 | 0.00028151 | 1.1171e-06
2012-11-08 12:25PM | 1568264-1 | 5867 | Urban | Third Party Impacts | 35 | 145.5714 | 5095 | 0.0056917 | 3.9099e-05
2012-08-10 05:06PM | 1544903-1 | 5872 | Urban | Weather | 732 | 90.7773 | 66449 | 0.074232 | 0.00081773
2013-04-12 11:39PM | 1610063-1 | 5872 | Urban | Equipment Failure | 426 | 69 | 29394 | 0.032837 | 0.00047589
2013-05-17 03:02PM | 1618327-1 | 5872 | Urban | Equipment Failure | 733 | 62.4106 | 45747 | 0.051105 | 0.00081885
2013-04-27 07:57AM | 1613317-1 | 5874 | Urban | Equipment Failure | 1420 | 104.0366 | 147732 | 0.16503 | 0.0015863
2013-01-26 05:20PM | 1588912-1 | 5875 | Urban | Vegetation | 25 | 98 | 2450 | 0.0027369 | 2.7928e-05
2013-03-26 03:20PM | 1606420-1 | 5877 | Urban | Equipment Failure | 222 | 1 | 222 | 0.000248 | 0.000248
2012-07-11 10:37AM | 1537045-1 | 19870 | Urban | Other | 123 | 28.748 | 3536 | 0.0039501 | 0.00013741
2013-03-17 10:30AM | 1604084-1 | 19871 | Urban | Other | 1 | 123 | 123 | 0.00013741 | 1.1171e-06
2013-03-18 10:14AM | 1604306-1 | 19871 | Urban | Equipment Failure | 1 | 95 | 95 | 0.00010613 | 1.1171e-06
2013-03-19 10:36AM | 1604520-1 | 19871 | Urban | Equipment Failure | 76 | 202.1711 | 15365 | 0.017165 | 8.4901e-05
2013-03-20 10:59AM | 1604873-1 | 19871 | Urban | Other | 76 | 77 | 5852 | 0.0065374 | 8.4901e-05
2013-05-09 04:55PM | 1617422-1 | 19871 | Urban | Other | 4 | 1 | 4 | 4.4685e-06 | 4.4685e-06
2012-08-10 03:00PM | 1544758-1 | 19871 | Urban | Weather | 1140 | 61.9877 | 70666 | 0.078942 | 0.0012735
2012-09-23 03:49PM | 1556580-1 | B773 | Urban | Other | 1 | 128 | 128 | 0.00014299 | 1.1171e-06
2013-02-20 12:26PM | 1595750-1 | B773 | Urban | Other | 29 | 100.3793 | 2911 | 0.0032519 | 3.2396e-05
2012-07-17 09:02AM | 1538266-1 | B776 | Urban | Third Party Impacts | 22 | 76.7727 | 1689 | 0.0018868 | 2.4577e-05
2013-01-17 04:44PM | 1585689-1 | B776 | Urban | Third Party Impacts | 6 | 39.8333 | 239 | 0.00026699 | 6.7027e-06
2013-04-02 01:11PM | 1607380-1 | B776 | Urban | Equipment Failure | 48 | 182.6667 | 8768 | 0.0097949 | 5.3622e-05
2013-05-08 04:33AM | 1615657-1 | B776 | Urban | Animals | 2400 | 151.6033 | 363848 | 0.40646 | 0.0026811
2012-11-08 02:10PM | 1568308-1 | B778 | Urban | Other | 52 | 97.0192 | 5045 | 0.0056359 | 5.809e-05
2013-04-13 01:49PM | 1610123-1 | L579 | Rural Short | Equipment Failure | 831 | 83.2659 | 69194 | 0.077298 | 0.00092833
2013-04-13 01:49PM | 1610123-1 | L580 | Urban | Equipment Failure | 144 | 83.0903 | 11965 | 0.013366 | 0.00016087
2013-04-13 01:49PM | 1610123-1 | L582 | Rural Short | Equipment Failure | 1216 | 83.2558 | 101239 | 0.1131 | 0.0013584
2012-07-02 02:20PM | 1534992-1 | L582 | Rural Short | Third Party Impacts | 5 | 13 | 65 | 7.2613e-05 | 5.5856e-06
2012-07-08 06:45AM | 1536389-1 | L582 | Rural Short | Equipment Failure | 82 | 115.7561 | 9492 | 0.010604 | 9.1604e-05
2012-11-28 07:34PM | 1573688-1 | L582 | Rural Short | Weather | 82 | 91.9634 | 7541 | 0.0084242 | 9.1604e-05
2013-02-18 05:10PM | 1595246-1 | L582 | Rural Short | Weather | 1 | 110 | 110 | 0.00012288 | 1.1171e-06
2013-02-27 03:48PM | 1599114-1 | L582 | Rural Short | Weather | 3 | 146 | 438 | 0.0004893 | 3.3514e-06
2013-01-30 12:35PM | 1590023-1 | L582 | Rural Short | Third Party Impacts | 6 | 43 | 258 | 0.00028822 | 6.7027e-06
2013-02-22 03:38PM | 1596511-1 | L582 | Rural Short | Other | 1 | 96 | 96 | 0.00010724 | 1.1171e-06
2013-01-30 12:38PM | 1590024-1 | L582 | Rural Short | Third Party Impacts | 3 | 93 | 279 | 0.00031168 | 3.3514e-06
2013-01-20 03:28AM | 1586687-1 | L582 | Rural Short | Vegetation | 1 | 347 | 347 | 0.00038764 | 1.1171e-06
2013-03-16 03:09PM | 1603997-1 | L582 | Rural Short | Equipment Failure | 87 | 178.3103 | 15513 | 0.01733 | 9.7189e-05
2012-09-07 11:36PM | 1553055-1 | L582 | Rural Short | Weather | 282 | 547.0426 | 154266 | 0.17233 | 0.00031503
2012-12-15 03:13AM | 1578105-1 | L582 | Rural Short | Vegetation | 281 | 115.2278 | 32379 | 0.036171 | 0.00031391
2013-04-04 11:58AM | 1607792-1 | L582 | Rural Short | Equipment Failure | 286 | 156.0909 | 44642 | 0.04987 | 0.0003195
2012-11-27 05:09AM | 1572968-1 | L582 | Rural Short | Equipment Failure | 19 | 323.8947 | 6154 | 0.0068748 | 2.1225e-05
2013-02-14 04:47PM | 1594513-1 | L582 | Rural Short | Equipment Failure | 3 | 82 | 246 | 0.00027481 | 3.3514e-06
2013-03-26 11:52PM | 1606493-1 | L582 | Rural Short | Animals | 42 | 107.0476 | 4496 | 0.0050226 | 4.6919e-05
2013-03-15 04:40PM | 1603830-1 | L582 | Rural Short | Equipment Failure | 1 | 154 | 154 | 0.00017204 | 1.1171e-06
2013-04-13 01:49PM | 1610123-1 | L584 | Rural Short | Equipment Failure | 375 | 83.224 | 31209 | 0.034864 | 0.00041892
2012-08-31 07:30AM | 1550871-1 | L584 | Rural Short | Other | 1 | 63 | 63 | 7.0379e-05 | 1.1171e-06
2012-11-02 06:59PM | 1566706-1 | L584 | Rural Short | Other | 3 | 145 | 435 | 0.00048595 | 3.3514e-06
2013-06-24 06:55AM | 1627405-1 | L591 | Rural Short | Weather | 4 | 136.25 | 545 | 0.00060883 | 4.4685e-06
2012-08-14 07:18AM | 1545597-1 | L591 | Rural Short | Equipment Failure | 10 | 100.1 | 1001 | 0.0011182 | 1.1171e-05
2012-12-26 08:54AM | 1580638-1 | L591 | Rural Short | Weather | 2 | 119 | 238 | 0.00026587 | 2.2342e-06
2013-01-13 03:38PM | 1584377-1 | L591 | Rural Short | Weather | 210 | 0.5 | 105 | 0.0001173 | 0.0002346
2013-01-14 07:47PM | 1584931-1 | L591 | Rural Short | Weather | 1 | 91 | 91 | 0.00010166 | 1.1171e-06
2012-07-20 04:12PM | 1539353-1 | L591 | Rural Short | Equipment Failure | 3 | 68.6667 | 206 | 0.00023013 | 3.3514e-06
2012-07-25 03:03PM | 1540312-1 | L591 | Rural Short | Equipment Failure | 11 | 63.1818 | 695 | 0.0007764 | 1.2288e-05
2012-07-12 09:03AM | 1537272-1 | L591 | Rural Short | Third Party Impacts | 130 | 0.66154 | 86 | 9.6072e-05 | 0.00014523
2012-08-17 11:41PM | 1547105-1 | L591 | Rural Short | Weather | 179 | 415.933 | 74452 | 0.083172 | 0.00019996
2012-11-20 08:44AM | 1571145-1 | L591 | Rural Short | Other | 174 | 20 | 3480 | 0.0038876 | 0.00019438
2013-03-28 10:30AM | 1607672-1 | L591 | Rural Short | Equipment Failure | 7 | 155 | 1085 | 0.0012121 | 7.8198e-06
2013-02-11 04:29AM | 1593401-1 | L591 | Rural Short | Equipment Failure | 179 | 19 | 3401 | 0.0037993 | 0.00019996
2013-03-07 11:48AM | 1601736-1 | L591 | Rural Short | Other | 13 | 103 | 1339 | 0.0014958 | 1.4523e-05
2013-03-07 03:29PM | 1601791-1 | L591 | Rural Short | Operatonal Error | 13 | 303 | 3939 | 0.0044003 | 1.4523e-05
2013-01-07 08:59AM | 1582785-1 | L591 | Rural Short | Other | 3 | 87.6667 | 263 | 0.0002938 | 3.3514e-06
2012-07-23 11:30AM | 1539696-1 | L591 | Rural Short | Equipment Failure | 30 | 59.9 | 1797 | 0.0020075 | 3.3514e-05
2013-01-04 01:23PM | 1582331-1 | L591 | Rural Short | Vegetation | 3 | 54 | 162 | 0.00018097 | 3.3514e-06
2012-12-22 05:44PM | 1579832-1 | L591 | Rural Short | Weather | 13 | 989 | 12857 | 0.014363 | 1.4523e-05
2013-02-25 05:55PM | 1598299-1 | L591 | Rural Short | Weather | 13 | 419 | 5447 | 0.006085 | 1.4523e-05
2012-09-08 02:08AM | 1553063-1 | L591 | Rural Short | Weather | 42 | 476 | 19992 | 0.022333 | 4.6919e-05
2013-02-22 06:48AM | 1596307-1 | L591 | Rural Short | Vegetation | 42 | 27.5 | 1155 | 0.0012903 | 4.6919e-05
2013-04-13 01:49PM | 1610123-1 | M399 | Rural Short | Equipment Failure | 1067 | 83.2765 | 88856 | 0.099263 | 0.001192
2012-08-10 10:17AM | 1544403-1 | M399 | Rural Short | Equipment Failure | 8 | 192 | 1536 | 0.0017159 | 8.937e-06
2012-09-30 04:36PM | 1558178-1 | M399 | Rural Short | Equipment Failure | 19 | 113.2632 | 2152 | 0.002404 | 2.1225e-05
2012-10-06 02:05PM | 1559454-1 | M399 | Rural Short | Vegetation | 24 | 99.3333 | 2384 | 0.0026632 | 2.6811e-05
2012-12-04 09:44AM | 1575244-1 | M399 | Rural Short | Other | 24 | 339 | 8136 | 0.0090889 | 2.6811e-05
2013-03-18 04:53PM | 1604424-1 | M399 | Rural Short | Third Party Impacts | 10 | 22 | 220 | 0.00024577 | 1.1171e-05
2013-04-09 05:14PM | 1608990-1 | M399 | Rural Short | Third Party Impacts | 2 | 45.5 | 91 | 0.00010166 | 2.2342e-06
2013-02-10 07:44PM | 1593335-1 | M399 | Rural Short | Weather | 106 | 435.5 | 46163 | 0.05157 | 0.00011841
2012-07-20 08:29AM | 1539180-1 | M399 | Rural Short | Third Party Impacts | 11 | 364.8182 | 4013 | 0.004483 | 1.2288e-05
2013-04-13 01:49PM | 1610123-1 | M400 | Urban | Equipment Failure | 766 | 83.2324 | 63756 | 0.071223 | 0.00085571
2012-11-20 04:26PM | 1571311-1 | 3326 | Urban | Third Party Impacts | 38 | 177.3158 | 6738 | 0.0075272 | 4.2451e-05
2012-10-17 11:36AM | 1562450-1 | 35569 | Urban | Other | 9 | 72.8889 | 656 | 0.00073283 | 1.0054e-05
2012-09-17 01:19PM | 1555055-1 | 35569 | Urban | Vegetation | 43 | 54 | 2322 | 0.002594 | 4.8036e-05
2013-04-28 03:21PM | 1613475-1 | 35569 | Urban | Vegetation | 25 | 76 | 1900 | 0.0021225 | 2.7928e-05
2012-08-17 01:53PM | 1546771-1 | 35569 | Urban | Weather | 1435 | 200.8 | 288148 | 0.3219 | 0.0016031
2013-04-28 12:28PM | 1613458-1 | 35569 | Urban | Vegetation | 1439 | 92.1035 | 132537 | 0.14806 | 0.0016075
2012-09-05 02:27PM | 1556153-1 | 35990 | Rural Short | Third Party Impacts | 1119 | 17.0867 | 19120 | 0.021359 | 0.0012501
2013-06-10 10:00PM | 1624167-1 | 35990 | Rural Short | Other | 27 | 100 | 2700 | 0.0030162 | 3.0162e-05
2012-11-08 11:49AM | 1568216-1 | 35990 | Rural Short | Equipment Failure | 1 | 273 | 273 | 0.00030497 | 1.1171e-06
2012-11-27 07:32PM | 1573226-1 | 35991 | Rural Short | Weather | 1 | 247 | 247 | 0.00027593 | 1.1171e-06
2012-09-05 02:27PM | 1556153-1 | 35991 | Rural Short | Third Party Impacts | 1 | 17 | 17 | 1.8991e-05 | 1.1171e-06
2012-11-27 07:32PM | 1573226-1 | 61617 | Rural Short | Weather | 448 | 247.4643 | 110864 | 0.12385 | 0.00050047
2012-12-05 10:06AM | 1575646-1 | 61617 | Rural Short | Weather | 450 | 121 | 54450 | 0.060827 | 0.0005027
2013-04-13 01:49PM | 1610123-1 | L585 | Rural Short | Equipment Failure | 743 | 83.218 | 61831 | 0.069073 | 0.00083002
2012-12-25 11:57PM | 1580611-1 | L585 | Rural Short | Weather | 3 | 33 | 99 | 0.00011059 | 3.3514e-06
2012-12-27 11:19AM | 1580840-1 | L585 | Rural Short | Equipment Failure | 9 | 41.5556 | 374 | 0.0004178 | 1.0054e-05
2012-11-07 06:34PM | 1567928-1 | L585 | Rural Short | Equipment Failure | 1 | 321 | 321 | 0.0003586 | 1.1171e-06
2013-04-13 01:49PM | 1610123-1 | L588 | Rural Short | Equipment Failure | 1041 | 83.2671 | 86681 | 0.096833 | 0.0011629
2013-03-22 09:10AM | 1605374-1 | L588 | Rural Short | Other | 1 | 74 | 74 | 8.2667e-05 | 1.1171e-06
2013-05-19 11:36AM | 1618591-1 | L588 | Rural Short | Equipment Failure | 1 | 95 | 95 | 0.00010613 | 1.1171e-06
2013-04-07 03:07PM | 1608451-1 | L588 | Rural Short | Weather | 3 | 67.6667 | 203 | 0.00022678 | 3.3514e-06
2013-05-27 11:31AM | 1620529-1 | L588 | Rural Short | Other | 138 | 49.7754 | 6869 | 0.0076735 | 0.00015416
2013-04-05 06:37PM | 1608264-1 | L588 | Rural Short | Equipment Failure | 6 | 141 | 846 | 0.00094508 | 6.7027e-06
2013-06-18 05:27PM | 1626174-1 | L588 | Rural Short | Equipment Failure | 4 | 372 | 1488 | 0.0016623 | 4.4685e-06
2012-10-20 11:22AM | 1563286-1 | L588 | Rural Short | Animals | 1 | 133 | 133 | 0.00014858 | 1.1171e-06
2012-11-28 10:07AM | 1573474-1 | L588 | Rural Short | Equipment Failure | 3 | 335.6667 | 1007 | 0.0011249 | 3.3514e-06
2013-04-07 03:36PM | 1608456-1 | L588 | Rural Short | Weather | 5 | 87.2 | 436 | 0.00048706 | 5.5856e-06
2013-05-10 02:28PM | 1616404-1 | L588 | Rural Short | Other | 83 | 58.4458 | 4851 | 0.0054191 | 9.2721e-05
2012-12-22 03:15PM | 1579809-1 | L588 | Rural Short | Weather | 6 | 259 | 1554 | 0.001736 | 6.7027e-06
2012-12-23 06:56AM | 1579884-1 | L588 | Rural Short | Weather | 8 | 159 | 1272 | 0.001421 | 8.937e-06
2012-12-14 08:33AM | 1577861-1 | L588 | Rural Short | Other | 8 | 25 | 200 | 0.00022342 | 8.937e-06
2012-10-03 02:23PM | 1558593-1 | L588 | Rural Short | Equipment Failure | 1041 | 28.3333 | 29495 | 0.032949 | 0.0011629
2012-12-03 10:56AM | 1574987-1 | L588 | Rural Short | Vegetation | 8 | 135.75 | 1086 | 0.0012132 | 8.937e-06
2012-12-14 11:31AM | 1577913-1 | L588 | Rural Short | Equipment Failure | 4 | 90 | 360 | 0.00040216 | 4.4685e-06
2013-01-09 07:37AM | 1583484-1 | L588 | Rural Short | Other | 1 | 221 | 221 | 0.00024688 | 1.1171e-06
2013-01-08 06:16PM | 1583348-1 | L588 | Rural Short | Vegetation | 406 | 69.3793 | 28168 | 0.031467 | 0.00045355
2013-02-09 07:56AM | 1592994-1 | L588 | Rural Short | Weather | 38 | 118.8421 | 4516 | 0.0050449 | 4.2451e-05
2013-04-13 01:49PM | 1610123-1 | L590 | Rural Short | Equipment Failure | 78 | 83.6667 | 6526 | 0.0072903 | 8.7135e-05
2013-04-13 01:49PM | 1610123-1 | L591 | Rural Short | Equipment Failure | 1442 | 83.2628 | 120065 | 0.13413 | 0.0016109
2012-12-05 01:10PM | 1575774-1 | L591 | Rural Short | Vegetation | 34 | 104 | 3536 | 0.0039501 | 3.7982e-05
2013-05-10 08:17AM | 1616251-1 | L591 | Rural Short | Equipment Failure | 65 | 99 | 6435 | 0.0071887 | 7.2613e-05
2013-02-26 07:14AM | 1598475-1 | L591 | Rural Short | Other | 1 | 53 | 53 | 5.9207e-05 | 1.1171e-06
2013-02-26 11:17AM | 1598572-1 | L591 | Rural Short | Other | 1 | 120 | 120 | 0.00013405 | 1.1171e-06
2013-02-26 06:36PM | 1598790-1 | L591 | Rural Short | Other | 1 | 236 | 236 | 0.00026364 | 1.1171e-06
2013-02-10 08:12PM | 1593358-1 | L591 | Rural Short | Weather | 1 | 956 | 956 | 0.001068 | 1.1171e-06
2013-01-22 06:30PM | 1587480-1 | L591 | Rural Short | Weather | 2 | 296 | 592 | 0.00066134 | 2.2342e-06
2012-09-27 09:49AM | 1557340-1 | L591 | Rural Short | Equipment Failure | 1 | 116 | 116 | 0.00012959 | 1.1171e-06
2013-04-17 06:46AM | 1610865-1 | L591 | Rural Short | Other | 1 | 403 | 403 | 0.0004502 | 1.1171e-06
2012-11-15 01:15PM | 1570089-1 | 35569 | Urban | Other | 11 | 210 | 2310 | 0.0025805 | 1.2288e-05
2012-10-16 08:11PM | 1562329-1 | 35569 | Urban | Equipment Failure | 1 | 102 | 102 | 0.00011395 | 1.1171e-06
2012-12-19 07:44AM | 1578881-1 | 35571 | Urban | Other | 67 | 156.8358 | 10508 | 0.011739 | 7.4847e-05
2012-12-05 02:18PM | 1575807-1 | 35571 | Urban | Other | 16 | 95 | 1520 | 0.001698 | 1.7874e-05
2013-03-18 11:46AM | 1604355-1 | 35571 | Urban | Equipment Failure | 1 | 351 | 351 | 0.00039211 | 1.1171e-06
2012-10-13 04:55PM | 1561509-1 | D819 | Urban | Equipment Failure | 51 | 76.2353 | 3888 | 0.0043434 | 5.6973e-05
2012-08-06 02:19AM | 1543035-1 | D819 | Urban | Equipment Failure | 724 | 78.0953 | 56541 | 0.063163 | 0.00080879
2012-11-28 07:57PM | 1573692-1 | D820 | Urban | Other | 62 | 35 | 2170 | 0.0024242 | 6.9261e-05
2013-05-28 11:24AM | 1620955-1 | D820 | Urban | Third Party Impacts | 53 | 380.3585 | 20159 | 0.02252 | 5.9207e-05
2013-02-25 02:22PM | 1598156-1 | D820 | Urban | Other | 1 | 303 | 303 | 0.00033849 | 1.1171e-06
2012-08-20 12:51AM | 1547317-1 | D820 | Urban | Third Party Impacts | 1304 | 167.4402 | 218342 | 0.24391 | 0.0014567
2012-07-20 09:00AM | 1539187-1 | D823 | Urban | Other | 7 | 69.8571 | 489 | 0.00054627 | 7.8198e-06
2013-06-26 02:10PM | 1628359-1 | D823 | Urban | Equipment Failure | 14 | 99 | 1386 | 0.0015483 | 1.564e-05
2013-06-26 05:14PM | 1628458-1 | D823 | Urban | Equipment Failure | 14 | 148 | 2072 | 0.0023147 | 1.564e-05
2013-06-26 10:42PM | 1628508-1 | D823 | Urban | Equipment Failure | 14 | 97 | 1358 | 0.001517 | 1.564e-05
2013-06-27 06:43AM | 1628522-1 | D823 | Urban | Equipment Failure | 14 | 301 | 4214 | 0.0047075 | 1.564e-05
2012-08-30 05:06PM | 1550780-1 | D823 | Urban | Equipment Failure | 1 | 201 | 201 | 0.00022454 | 1.1171e-06
2013-01-09 08:08AM | 1583487-1 | D824 | Urban | Other | 12 | 75 | 900 | 0.0010054 | 1.3405e-05
2013-02-27 12:27PM | 1598995-1 | D827 | Urban | Equipment Failure | 1 | 149 | 149 | 0.00016645 | 1.1171e-06
2013-04-01 02:02PM | 1607223-1 | D828 | Urban | Other | 78 | 64 | 4992 | 0.0055767 | 8.7135e-05
2013-06-29 01:24PM | 1629239-1 | D828 | Urban | Other | 2 | 70 | 140 | 0.0001564 | 2.2342e-06
2012-12-01 06:20PM | 1574704-1 | D830 | Urban | Equipment Failure | 37 | 115 | 4255 | 0.0047533 | 4.1333e-05
2012-07-02 01:10PM | 1534863-1 | D830 | Urban | Other | 49 | 81 | 3969 | 0.0044338 | 5.4739e-05
2012-08-05 01:31PM | 1542993-1 | D830 | Urban | Equipment Failure | 19 | 86.1053 | 1636 | 0.0018276 | 2.1225e-05
2013-01-28 05:50PM | 1589337-1 | D830 | Urban | Equipment Failure | 13 | 554 | 7202 | 0.0080455 | 1.4523e-05
2013-05-18 10:00PM | 1618556-1 | D830 | Urban | Equipment Failure | 8 | 121 | 968 | 0.0010814 | 8.937e-06
2012-11-02 10:59AM | 1566617-1 | D830 | Urban | Third Party Impacts | 200 | 245.17 | 49034 | 0.054777 | 0.00022342
2013-04-29 06:20AM | 1613520-1 | D830 | Urban | Equipment Failure | 2033 | 46 | 93518 | 0.10447 | 0.0022711
2013-02-01 10:40AM | 1590600-1 | D831 | Urban | Equipment Failure | 13 | 433 | 5629 | 0.0062883 | 1.4523e-05
2012-10-07 05:48PM | 1559547-1 | D831 | Urban | Equipment Failure | 20 | 158.7 | 3174 | 0.0035457 | 2.2342e-05
2012-08-31 03:42AM | 1550847-1 | D831 | Urban | Equipment Failure | 1865 | 111.0231 | 207058 | 0.23131 | 0.0020834
2012-11-05 10:21AM | 1567147-1 | D831 | Urban | Third Party Impacts | 1877 | 91.6255 | 171981 | 0.19212 | 0.0020968
2013-05-10 09:07AM | 1616275-1 | D831 | Urban | Equipment Failure | 1880 | 51.3404 | 96520 | 0.10782 | 0.0021002
2012-08-06 02:43PM | 1543217-1 | D832 | Urban | Other | 26 | 17.8077 | 463 | 0.00051723 | 2.9045e-05
2012-11-30 12:08PM | 1574199-1 | D832 | Urban | Weather | 27 | 61.3333 | 1656 | 0.00185 | 3.0162e-05
2013-03-07 11:23AM | 1601693-1 | A095 | Rural Short | Vegetation | 4 | 557 | 2228 | 0.0024889 | 4.4685e-06
2013-05-15 07:18AM | 1617390-1 | A095 | Rural Short | Other | 5 | 77.2 | 386 | 0.00043121 | 5.5856e-06
2012-11-18 09:58AM | 1570550-1 | A095 | Rural Short | Vegetation | 3 | 63 | 189 | 0.00021114 | 3.3514e-06
2012-08-17 01:46PM | 1546765-1 | A095 | Rural Short | Weather | 184 | 45 | 8280 | 0.0092498 | 0.00020555
2012-10-04 07:34AM | 1558789-1 | A095 | Rural Short | Other | 1 | 63 | 63 | 7.0379e-05 | 1.1171e-06
2012-10-15 04:05PM | 1561919-1 | A096 | Rural Short | Other | 826 | 95.0508 | 78512 | 0.087707 | 0.00092274
2013-05-24 11:33AM | 1619976-1 | A096 | Rural Short | Equipment Failure | 1 | 278 | 278 | 0.00031056 | 1.1171e-06
2013-01-27 03:11PM | 1589142-1 | A096 | Rural Short | Vegetation | 6 | 202 | 1212 | 0.0013539 | 6.7027e-06
2013-05-02 11:43AM | 1614475-1 | A096 | Rural Short | Equipment Failure | 56 | 25 | 1400 | 0.001564 | 6.2559e-05
2013-03-20 03:00AM | 1604702-1 | A096 | Rural Short | Other | 46 | 76.2609 | 3508 | 0.0039189 | 5.1388e-05
2012-10-15 02:30PM | 1561841-1 | A096 | Rural Short | Vegetation | 1 | 98 | 98 | 0.00010948 | 1.1171e-06
2013-04-19 10:01PM | 1611663-1 | A096 | Rural Short | Other | 1 | 162 | 162 | 0.00018097 | 1.1171e-06
2013-02-27 01:37PM | 1599007-1 | A096 | Rural Short | Other | 1 | 374 | 374 | 0.0004178 | 1.1171e-06
2013-03-09 05:10PM | 1602268-1 | A096 | Rural Short | Vegetation | 1 | 95 | 95 | 0.00010613 | 1.1171e-06
2012-12-13 05:58PM | 1577743-1 | A098 | Rural Short | Equipment Failure | 18 | 472 | 8496 | 0.0094911 | 2.0108e-05
2013-04-14 12:58AM | 1610172-1 | A098 | Rural Short | Equipment Failure | 1 | 429 | 429 | 0.00047924 | 1.1171e-06
2013-01-21 04:21PM | 1587007-1 | A098 | Rural Short | Equipment Failure | 7 | 114 | 798 | 0.00089146 | 7.8198e-06
2012-07-04 09:29AM | 1535470-1 | A098 | Rural Short | Equipment Failure | 5 | 80 | 400 | 0.00044685 | 5.5856e-06
2012-08-07 10:00AM | 1543391-1 | A098 | Rural Short | Equipment Failure | 5 | 303.4 | 1517 | 0.0016947 | 5.5856e-06
2012-08-15 05:00PM | 1547663-1 | A098 | Rural Short | Third Party Impacts | 12 | 120 | 1440 | 0.0016087 | 1.3405e-05
2013-03-20 06:36PM | 1605009-1 | A098 | Rural Short | Third Party Impacts | 4 | 255.75 | 1023 | 0.0011428 | 4.4685e-06
2012-10-08 07:25PM | 1559860-1 | A098 | Rural Short | Equipment Failure | 1 | 236 | 236 | 0.00026364 | 1.1171e-06
2012-08-20 03:50PM | 1547579-1 | J506 | Urban | Equipment Failure | 14 | 175.0714 | 2451 | 0.0027381 | 1.564e-05
2013-05-24 03:26PM | 1620132-1 | J506 | Urban | Equipment Failure | 1 | 193 | 193 | 0.0002156 | 1.1171e-06
2012-11-29 04:01PM | 1573989-1 | J506 | Urban | Other | 28 | 37.3571 | 1046 | 0.0011685 | 3.1279e-05
2013-05-17 09:10AM | 1618143-1 | J506 | Urban | Equipment Failure | 19 | 36 | 684 | 0.00076411 | 2.1225e-05
2013-02-05 03:42PM | 1591810-1 | J506 | Urban | Equipment Failure | 1 | 251 | 251 | 0.0002804 | 1.1171e-06
2012-08-22 01:40PM | 1548082-1 | J507 | Urban | Other | 16 | 33 | 528 | 0.00058984 | 1.7874e-05
2013-05-28 09:20AM | 1620910-1 | J507 | Urban | Equipment Failure | 39 | 107.9487 | 4210 | 0.0047031 | 4.3568e-05
2012-10-20 10:56AM | 1563277-1 | J507 | Urban | Vegetation | 55 | 65.4 | 3597 | 0.0040183 | 6.1442e-05
2013-02-25 04:09PM | 1598232-1 | J509 | Urban | Weather | 130 | 153 | 19890 | 0.02222 | 0.00014523
2013-03-04 01:13PM | 1600634-1 | J509 | Urban | Equipment Failure | 78 | 1128.3718 | 88013 | 0.098321 | 8.7135e-05
2013-01-05 06:09AM | 1582525-1 | J510 | Urban | Equipment Failure | 9 | 58 | 522 | 0.00058314 | 1.0054e-05
2013-01-09 12:55PM | 1583616-1 | J510 | Urban | Other | 9 | 52.5556 | 473 | 0.0005284 | 1.0054e-05
2013-01-09 01:55PM | 1583626-1 | J510 | Urban | Other | 9 | 79.2222 | 713 | 0.00079651 | 1.0054e-05
2013-01-09 11:09PM | 1583718-1 | J510 | Urban | Equipment Failure | 15 | 329.9333 | 4949 | 0.0055286 | 1.6757e-05
2013-01-29 10:53PM | 1589887-1 | J510 | Urban | Equipment Failure | 38 | 297.0263 | 11287 | 0.012609 | 4.2451e-05
2012-09-09 10:40AM | 1553272-1 | J510 | Urban | Other | 1 | 37 | 37 | 4.1333e-05 | 1.1171e-06
2012-10-17 09:27AM | 1562389-1 | J510 | Urban | Equipment Failure | 16 | 25.75 | 412 | 0.00046025 | 1.7874e-05
2012-09-06 10:15AM | 1552334-1 | J510 | Urban | Equipment Failure | 1 | 311 | 311 | 0.00034742 | 1.1171e-06
2012-10-17 04:26PM | 1562603-1 | J510 | Urban | Equipment Failure | 21 | 30.381 | 638 | 0.00071272 | 2.346e-05
2012-10-17 07:44PM | 1562674-1 | J510 | Urban | Equipment Failure | 1 | 16 | 16 | 1.7874e-05 | 1.1171e-06
2012-11-27 08:14PM | 1575879-1 | J510 | Urban | Other | 142 | 1 | 142 | 0.00015863 | 0.00015863
2013-06-25 05:30PM | 1628026-1 | J512 | Urban | Weather | 74 | 69 | 5106 | 0.005704 | 8.2667e-05
2013-06-07 10:12AM | 1623626-1 | J512 | Urban | Other | 5 | 121.4 | 607 | 0.00067809 | 5.5856e-06
2013-05-15 05:02PM | 1617648-1 | J514 | Urban | Other | 9 | 134 | 1206 | 0.0013472 | 1.0054e-05
2012-12-12 11:59AM | 1577396-1 | J514 | Urban | Equipment Failure | 26 | 230.3462 | 5989 | 0.0066904 | 2.9045e-05
2013-04-09 04:32AM | 1608711-1 | J514 | Urban | Equipment Failure | 23 | 204.3913 | 4701 | 0.0052516 | 2.5694e-05
2013-01-28 11:24AM | 1589251-1 | J514 | Urban | Equipment Failure | 1 | 197 | 197 | 0.00022007 | 1.1171e-06
2012-08-31 10:18AM | 1550909-1 | J514 | Urban | Other | 13 | 52.6154 | 684 | 0.00076411 | 1.4523e-05
2012-07-04 04:53PM | 1535684-1 | J514 | Urban | Other | 60 | 207.1667 | 12430 | 0.013886 | 6.7027e-05
2013-03-04 03:24AM | 1600780-1 | J514 | Urban | Other | 10 | 232.3 | 2323 | 0.0025951 | 1.1171e-05
2012-08-22 01:13PM | 1548074-1 | J514 | Urban | Other | 20 | 26.05 | 521 | 0.00058202 | 2.2342e-05
2013-03-04 12:50PM | 1600567-1 | J514 | Urban | Equipment Failure | 2301 | 66.2069 | 152342 | 0.17018 | 0.0025705
2013-04-03 09:49AM | 1607516-1 | J515 | Urban | Equipment Failure | 1 | 265 | 265 | 0.00029604 | 1.1171e-06
2012-12-25 11:33PM | 1580609-1 | J516 | Urban | Equipment Failure | 21 | 271 | 5691 | 0.0063575 | 2.346e-05
2013-01-27 09:33PM | 1589174-1 | J516 | Urban | Other | 38 | 145.6316 | 5534 | 0.0061821 | 4.2451e-05
2013-01-28 10:52AM | 1589248-1 | J516 | Urban | Weather | 38 | 314.0789 | 11935 | 0.013333 | 4.2451e-05
2013-02-01 08:26PM | 1590908-1 | J516 | Urban | Other | 40 | 36 | 1440 | 0.0016087 | 4.4685e-05
2013-02-02 02:35AM | 1590951-1 | J516 | Urban | Equipment Failure | 21 | 582.7143 | 12237 | 0.01367 | 2.346e-05
2013-06-28 04:09PM | 1629118-1 | J516 | Urban | Equipment Failure | 1 | 230 | 230 | 0.00025694 | 1.1171e-06
2012-10-17 01:07PM | 1562475-1 | J516 | Urban | Animals | 1356 | 52.0442 | 70572 | 0.078837 | 0.0015148
2012-11-08 06:46PM | 1568504-1 | J516 | Urban | Weather | 1 | 364 | 364 | 0.00040663 | 1.1171e-06
2013-02-25 07:32AM | 1597842-1 | M388 | Urban | Weather | 20 | 130 | 2600 | 0.0029045 | 2.2342e-05
2012-09-09 09:32AM | 1553263-1 | M388 | Urban | Third Party Impacts | 18 | 55.5 | 999 | 0.001116 | 2.0108e-05
2012-08-04 10:21AM | 1542880-1 | M388 | Urban | Equipment Failure | 15 | 162 | 2430 | 0.0027146 | 1.6757e-05
2012-08-04 10:21AM | 1542881-1 | M388 | Urban | Equipment Failure | 16 | 162 | 2592 | 0.0028956 | 1.7874e-05
2012-08-04 01:26PM | 1542909-1 | M388 | Urban | Other | 1010 | 10.3158 | 10419 | 0.011639 | 0.0011283
2012-11-27 07:32PM | 1573226-1 | 35980 | Rural Short | Weather | 436 | 247.4794 | 107901 | 0.12054 | 0.00048706
2013-01-22 04:02PM | 1587360-1 | 35980 | Rural Short | Weather | 2 | 98 | 196 | 0.00021896 | 2.2342e-06
2012-11-21 03:15PM | 1571676-1 | 35980 | Rural Short | Third Party Impacts | 3 | 51 | 153 | 0.00017092 | 3.3514e-06
2012-09-15 09:59PM | 1554847-1 | 35980 | Rural Short | Equipment Failure | 4 | 73 | 292 | 0.0003262 | 4.4685e-06
2012-09-05 02:27PM | 1556153-1 | 35980 | Rural Short | Third Party Impacts | 436 | 17.0803 | 7447 | 0.0083192 | 0.00048706
2012-11-16 04:17PM | 1570453-1 | 35980 | Rural Short | Other | 1 | 374 | 374 | 0.0004178 | 1.1171e-06
2012-11-27 07:32PM | 1573226-1 | 35981 | Rural Short | Weather | 438 | 247.4772 | 108395 | 0.12109 | 0.0004893
2013-06-13 08:37AM | 1624839-1 | 35981 | Rural Short | Other | 5 | 82 | 410 | 0.00045802 | 5.5856e-06
2012-09-05 02:27PM | 1556153-1 | 35981 | Rural Short | Third Party Impacts | 438 | 17.0799 | 7481 | 0.0083572 | 0.0004893
2012-11-27 07:32PM | 1573226-1 | 35982 | Rural Short | Weather | 403 | 247.5261 | 99753 | 0.11144 | 0.0004502
2013-01-18 12:37PM | 1585991-1 | 35982 | Rural Short | Equipment Failure | 2 | 306.5 | 613 | 0.00068479 | 2.2342e-06
2013-02-01 06:56PM | 1590885-1 | 35982 | Rural Short | Weather | 4 | 139 | 556 | 0.00062112 | 4.4685e-06
| 1580160-1 | 35982 | Rural Short | Weather | 13 | 173 | 2249 | 0.0025124 | 1.4523e-05
2013-05-24 10:42AM | 1619951-1 | 35982 | Rural Short | Equipment Failure | 14 | 45.8571 | 642 | 0.00071719 | 1.564e-05
2013-03-23 06:38AM | 1605717-1 | 35982 | Rural Short | Other | 3 | 140.3333 | 421 | 0.00047031 | 3.3514e-06
2012-12-24 04:21PM | 1580161-1 | 35982 | Rural Short | Weather | 3 | 173.6667 | 521 | 0.00058202 | 3.3514e-06
2012-09-28 07:00PM | 1557967-1 | 35982 | Rural Short | Other | 1 | 292 | 292 | 0.0003262 | 1.1171e-06
2012-11-28 06:28AM | 1573406-1 | 35982 | Rural Short | Equipment Failure | 3 | 547 | 1641 | 0.0018332 | 3.3514e-06
2012-11-14 02:14PM | 1569825-1 | 35982 | Rural Short | Equipment Failure | 5 | 35.8 | 179 | 0.00019996 | 5.5856e-06
2013-01-22 03:19PM | 1587328-1 | 35982 | Rural Short | Weather | 407 | 35.1376 | 14301 | 0.015976 | 0.00045467
2013-02-01 07:47PM | 1590897-1 | 35982 | Rural Short | Weather | 2 | 172 | 344 | 0.00038429 | 2.2342e-06
2012-11-19 10:47AM | 1570812-1 | 35982 | Rural Short | Other | 5 | 123.8 | 619 | 0.0006915 | 5.5856e-06
2012-09-05 02:27PM | 1556153-1 | 35982 | Rural Short | Third Party Impacts | 403 | 17.0844 | 6885 | 0.0076914 | 0.0004502
2012-09-18 01:23AM | 1555248-1 | 35983 | Rural Short | Weather | 2 | 52 | 104 | 0.00011618 | 2.2342e-06
2012-11-27 07:32PM | 1573226-1 | 35983 | Rural Short | Weather | 980 | 247.4173 | 242469 | 0.27087 | 0.0010948
2013-04-16 06:09AM | 1610580-1 | 35983 | Rural Short | Equipment Failure | 1 | 290 | 290 | 0.00032396 | 1.1171e-06
2013-01-25 01:46AM | 1588099-1 | 35983 | Rural Short | Other | 4 | 98 | 392 | 0.00043791 | 4.4685e-06
2012-12-13 12:25PM | 1577645-1 | 35983 | Rural Short | Other | 2 | 162 | 324 | 0.00036195 | 2.2342e-06
2013-04-20 08:38AM | 1611696-1 | 35983 | Rural Short | Third Party Impacts | 72 | 209 | 15048 | 0.01681 | 8.0433e-05
2012-09-17 04:05PM | 1555146-1 | 35983 | Rural Short | Weather | 199 | 156 | 31044 | 0.03468 | 0.00022231
2012-11-28 12:25AM | 1573357-1 | 35983 | Rural Short | Weather | 198 | 145.5455 | 28818 | 0.032193 | 0.00022119
2012-11-28 08:12AM | 1573420-1 | 35983 | Rural Short | Weather | 198 | 118 | 23364 | 0.0261 | 0.00022119
2012-09-05 02:27PM | 1556153-1 | 35983 | Rural Short | Third Party Impacts | 980 | 17.0755 | 16734 | 0.018694 | 0.0010948
2012-09-03 02:05PM | 1551416-1 | 35988 | Rural Short | Other | 1 | 163 | 163 | 0.00018209 | 1.1171e-06
2012-11-27 07:32PM | 1573226-1 | 35988 | Rural Short | Weather | 596 | 247.3272 | 147407 | 0.16467 | 0.0006658
2013-02-03 05:58PM | 1591182-1 | 35988 | Rural Short | Third Party Impacts | 5 | 115.2 | 576 | 0.00064346 | 5.5856e-06
2012-08-31 12:40PM | 1550951-1 | 35988 | Rural Short | Weather | 5 | 95.2 | 476 | 0.00053175 | 5.5856e-06
2012-08-10 08:06PM | 1544982-1 | 35988 | Rural Short | Equipment Failure | 1 | 391 | 391 | 0.00043679 | 1.1171e-06
2012-12-24 03:51PM | 1580148-1 | 35988 | Rural Short | Weather | 9 | 107.5556 | 968 | 0.0010814 | 1.0054e-05
2013-06-06 11:04AM | 1623426-1 | 35988 | Rural Short | Other | 1 | 33 | 33 | 3.6865e-05 | 1.1171e-06
2012-12-24 03:37PM | 1580145-1 | 35988 | Rural Short | Weather | 9 | 100.2222 | 902 | 0.0010076 | 1.0054e-05
2012-11-27 11:41PM | 1573352-1 | 35988 | Rural Short | Weather | 140 | 302.1929 | 42307 | 0.047262 | 0.0001564
2012-09-13 10:00AM | 1554258-1 | 35988 | Rural Short | Equipment Failure | 14 | 210.5714 | 2948 | 0.0032933 | 1.564e-05
2013-05-23 11:12AM | 1619674-1 | 35988 | Rural Short | Equipment Failure | 24 | 103.75 | 2490 | 0.0027816 | 2.6811e-05
2013-05-22 06:17PM | 1619505-1 | 35988 | Rural Short | Equipment Failure | 383 | 2.0392 | 781 | 0.00087247 | 0.00042786
2012-11-27 07:32PM | 1573226-1 | 35989 | Rural Short | Weather | 875 | 247.1954 | 216296 | 0.24163 | 0.00097748
2013-01-31 06:26AM | 1590165-1 | 35989 | Rural Short | Equipment Failure | 2 | 72 | 144 | 0.00016087 | 2.2342e-06
2012-12-22 01:51PM | 1579801-1 | 35989 | Rural Short | Vegetation | 5 | 125 | 625 | 0.0006982 | 5.5856e-06
2012-11-28 12:15PM | 1573531-1 | 35989 | Rural Short | Weather | 1 | 106 | 106 | 0.00011841 | 1.1171e-06
2012-11-19 07:14AM | 1570758-1 | 35989 | Rural Short | Equipment Failure | 1 | 155 | 155 | 0.00017315 | 1.1171e-06
2012-09-20 03:06PM | 1555959-1 | 35989 | Rural Short | Equipment Failure | 3 | 157.6667 | 473 | 0.0005284 | 3.3514e-06
2012-09-05 02:27PM | 1556153-1 | 35989 | Rural Short | Third Party Impacts | 874 | 17.0801 | 14928 | 0.016676 | 0.00097636
2012-11-19 10:17PM | 1571062-1 | 35989 | Rural Short | Other | 10 | 77.3 | 773 | 0.00086353 | 1.1171e-05
2012-12-28 06:52PM | 1581256-1 | 35989 | Rural Short | Animals | 10 | 95 | 950 | 0.0010613 | 1.1171e-05
2012-12-24 05:24PM | 1580201-1 | 35989 | Rural Short | Weather | 30 | 42.0333 | 1261 | 0.0014087 | 3.3514e-05
2012-08-10 11:24AM | 1544446-1 | 35989 | Rural Short | Weather | 556 | 146.1637 | 81267 | 0.090785 | 0.00062112
2012-12-23 07:10PM | 1579995-1 | 35990 | Rural Short | Weather | 2 | 375 | 750 | 0.00083784 | 2.2342e-06
2012-11-27 07:32PM | 1573226-1 | 35990 | Rural Short | Weather | 1120 | 247.3545 | 277037 | 0.30948 | 0.0012512
2013-02-18 08:25AM | 1595044-1 | 35990 | Rural Short | Equipment Failure | 48 | 68 | 3264 | 0.0036463 | 5.3622e-05
2013-02-20 08:32AM | 1595683-1 | 35990 | Rural Short | Equipment Failure | 50 | 112.02 | 5601 | 0.006257 | 5.5856e-05
2013-02-06 07:53PM | 1592255-1 | 35990 | Rural Short | Equipment Failure | 2 | 886 | 1772 | 0.0019795 | 2.2342e-06
2013-05-24 08:03AM | 1619906-1 | 35990 | Rural Short | Equipment Failure | 7 | 324.8571 | 2274 | 0.0025403 | 7.8198e-06
2012-07-04 09:12AM | 1535459-1 | 35990 | Rural Short | Other | 1 | 99 | 99 | 0.00011059 | 1.1171e-06
2012-11-02 08:23AM | 1566534-1 | 35990 | Rural Short | Other | 1 | 108 | 108 | 0.00012065 | 1.1171e-06
2012-11-28 06:06AM | 1573395-1 | 35990 | Rural Short | Weather | 4 | 214 | 856 | 0.00095625 | 4.4685e-06
2013-01-01 04:34PM | 1581639-1 | 35990 | Rural Short | Weather | 4 | 74.5 | 298 | 0.0003329 | 4.4685e-06
2013-03-13 12:50PM | 1605148-1 | 35990 | Rural Short | Other | 1 | 55 | 55 | 6.1442e-05 | 1.1171e-06
2012-07-13 12:56AM | 1537483-1 | 35990 | Rural Short | Third Party Impacts | 1009 | 127.8157 | 128966 | 0.14407 | 0.0011272
2013-01-31 06:37AM | 1590173-1 | 35990 | Rural Short | Equipment Failure | 1125 | 253.8436 | 285574 | 0.31902 | 0.0012568
2013-04-30 02:41PM | 1613937-1 | 35990 | Rural Short | Third Party Impacts | 1 | 224 | 224 | 0.00025023 | 1.1171e-06
2012-11-27 08:42PM | 1573326-1 | 35514 | Urban | Weather | 64 | 379.6875 | 24300 | 0.027146 | 7.1496e-05
2013-05-13 01:28AM | 1616776-1 | 35514 | Urban | Equipment Failure | 20 | 0.4 | 8 | 8.937e-06 | 2.2342e-05
2013-06-12 08:05AM | 1624453-1 | 35514 | Urban | Equipment Failure | 201 | 86.9851 | 17484 | 0.019532 | 0.00022454
2013-04-19 09:21PM | 1611659-1 | 1959 | Urban | Equipment Failure | 20 | 163 | 3260 | 0.0036418 | 2.2342e-05
2013-01-12 02:05AM | 1584224-1 | 1959 | Urban | Other | 38 | 361.7632 | 13747 | 0.015357 | 4.2451e-05
2013-02-21 01:07PM | 1596118-1 | 1962 | Urban | Equipment Failure | 16 | 101.1875 | 1619 | 0.0018086 | 1.7874e-05
2013-02-05 08:17AM | 1591600-1 | 1962 | Urban | Equipment Failure | 22 | 144 | 3168 | 0.003539 | 2.4577e-05
2013-03-22 12:02PM | 1605476-1 | 1962 | Urban | Vegetation | 1888 | 26.4497 | 49937 | 0.055786 | 0.0021091
2013-04-10 04:52AM | 1609034-1 | 1962 | Urban | Equipment Failure | 1888 | 85.4899 | 161405 | 0.18031 | 0.0021091
2013-06-16 03:47PM | 1625562-1 | 1962 | Urban | Other | 1846 | 1 | 1846 | 0.0020622 | 0.0020622
2012-08-11 11:53PM | 1545145-1 | 1962 | Urban | Equipment Failure | 48 | 569.8958 | 27355 | 0.030559 | 5.3622e-05
2012-11-25 09:02AM | 1572500-1 | 1962 | Urban | Equipment Failure | 2 | 64 | 128 | 0.00014299 | 2.2342e-06
2013-01-07 09:28AM | 1582794-1 | MVC2 | Rural Short | Other | 1 | 143 | 143 | 0.00015975 | 1.1171e-06
2013-04-28 08:00PM | 1613507-1 | MVC2 | Rural Short | Other | 2 | 71.5 | 143 | 0.00015975 | 2.2342e-06
2013-05-12 03:28PM | 1616739-1 | MVC2 | Rural Short | Equipment Failure | 1 | 103 | 103 | 0.00011506 | 1.1171e-06
2012-10-19 02:50PM | 1563162-1 | MVC2 | Rural Short | Other | 3 | 113 | 339 | 0.0003787 | 3.3514e-06
2012-07-10 09:44AM | 1536769-1 | MVC2 | Rural Short | Other | 1 | 75 | 75 | 8.3784e-05 | 1.1171e-06
2012-12-28 01:53PM | 1581179-1 | MVC2 | Rural Short | Weather | 2 | 45 | 90 | 0.00010054 | 2.2342e-06
2012-08-16 07:17AM | 1546191-1 | MVC2 | Rural Short | Other | 8 | 84.875 | 679 | 0.00075852 | 8.937e-06
2012-12-23 06:42PM | 1579987-1 | MVC2 | Rural Short | Weather | 3 | 161 | 483 | 0.00053957 | 3.3514e-06
2013-01-14 11:05AM | 1584703-1 | MVC2 | Rural Short | Equipment Failure | 1 | 87 | 87 | 9.7189e-05 | 1.1171e-06
2013-04-20 06:20AM | 1611677-1 | MVC2 | Rural Short | Equipment Failure | 4 | 161 | 644 | 0.00071943 | 4.4685e-06
2012-12-23 07:49PM | 1580002-1 | MVC2 | Rural Short | Weather | 4 | 235 | 940 | 0.0010501 | 4.4685e-06
2013-04-27 03:38PM | 1613407-1 | MVC2 | Rural Short | Equipment Failure | 2 | 73 | 146 | 0.0001631 | 2.2342e-06
2012-11-14 08:58AM | 1569721-1 | MVC2 | Rural Short | Other | 2 | 325 | 650 | 0.00072613 | 2.2342e-06
2012-12-23 06:04PM | 1579974-1 | MVC2 | Rural Short | Weather | 14 | 136 | 1904 | 0.002127 | 1.564e-05
2013-03-31 09:06PM | 1607184-1 | MVC2 | Rural Short | Other | 1 | 218 | 218 | 0.00024353 | 1.1171e-06
2013-04-22 01:23PM | 1612102-1 | MVC2 | Rural Short | Vegetation | 16 | 79 | 1264 | 0.001412 | 1.7874e-05
2012-07-06 06:57AM | 1535999-1 | MVC2 | Rural Short | Equipment Failure | 11 | 45.7273 | 503 | 0.00056191 | 1.2288e-05
2012-12-23 04:43PM | 1579944-1 | MVC2 | Rural Short | Weather | 46 | 111 | 5106 | 0.005704 | 5.1388e-05
2012-08-17 07:57PM | 1547088-1 | L537 | Urban | Weather | 1 | 41 | 41 | 4.5802e-05 | 1.1171e-06
2012-09-07 12:39PM | 1552733-1 | L537 | Urban | Weather | 1639 | 63.9103 | 104749 | 0.11702 | 0.001831
2012-09-07 01:30PM | 1552773-1 | L537 | Urban | Weather | 69 | 86 | 5934 | 0.006629 | 7.7081e-05
2013-04-09 02:48PM | 1608931-1 | L537 | Urban | Equipment Failure | 949 | 45.4658 | 43147 | 0.0482 | 0.0010601
2013-04-02 10:29AM | 1607325-1 | L537 | Urban | Other | 1 | 166 | 166 | 0.00018544 | 1.1171e-06
2012-11-07 09:09AM | 1567722-1 | L540 | Urban | Third Party Impacts | 2 | 289 | 578 | 0.0006457 | 2.2342e-06
2012-08-10 01:31PM | 1544564-1 | L543 | Urban | Weather | 1735 | 110.483 | 191688 | 0.21414 | 0.0019382
2013-04-17 06:26AM | 1610861-1 | L544 | Urban | Other | 50 | 197.94 | 9897 | 0.011056 | 5.5856e-05
2013-06-01 09:28AM | 1622214-1 | 16649 | Urban | Equipment Failure | 21 | 219 | 4599 | 0.0051376 | 2.346e-05
2013-06-22 09:08AM | 1627102-1 | 16649 | Urban | Equipment Failure | 21 | 284 | 5964 | 0.0066625 | 2.346e-05
2012-09-30 01:17PM | 1558162-1 | 16651 | Urban | Equipment Failure | 1 | 89 | 89 | 9.9424e-05 | 1.1171e-06
2012-11-27 10:19PM | 1573345-1 | 16653 | Urban | Weather | 23 | 172 | 3956 | 0.0044193 | 2.5694e-05
2012-08-12 03:01PM | 1545201-1 | 16653 | Urban | Other | 18 | 87.7778 | 1580 | 0.001765 | 2.0108e-05
2013-01-28 07:51AM | 1589212-1 | 16653 | Urban | Vegetation | 1623 | 44 | 71412 | 0.079776 | 0.0018131
2012-11-08 07:15AM | 1568159-1 | 16653 | Urban | Other | 1 | 161 | 161 | 0.00017986 | 1.1171e-06
2012-09-13 03:54PM | 1554409-1 | 16660 | Urban | Other | 44 | 75 | 3300 | 0.0036865 | 4.9153e-05
2013-01-14 08:24PM | 1584935-1 | 16660 | Urban | Third Party Impacts | 94 | 365.8723 | 34392 | 0.03842 | 0.00010501
2013-06-02 09:36AM | 1622287-1 | 16660 | Urban | Equipment Failure | 1 | 184 | 184 | 0.00020555 | 1.1171e-06
2013-02-25 07:35PM | 1598392-1 | 16660 | Urban | Other | 1 | 103 | 103 | 0.00011506 | 1.1171e-06
2013-01-18 06:16PM | 1586299-1 | 16666 | Urban | Weather | 38 | 249.4737 | 9480 | 0.01059 | 4.2451e-05
2013-06-27 12:25PM | 1628670-1 | 35388 | Urban | Equipment Failure | 1 | 314 | 314 | 0.00035078 | 1.1171e-06
2013-05-18 08:30PM | 1618554-1 | 35388 | Urban | Equipment Failure | 1 | 1170 | 1170 | 0.001307 | 1.1171e-06
2012-09-17 04:09AM | 1554942-1 | 35403 | Urban | Third Party Impacts | 1600 | 135.31 | 216496 | 0.24185 | 0.0017874
2012-09-20 06:04AM | 1555843-1 | 57040 | Urban | Equipment Failure | 41 | 59.7317 | 2449 | 0.0027358 | 4.5802e-05
2013-06-15 07:56AM | 1625420-1 | 10286 | Rural Short | Other | 12 | 76 | 912 | 0.0010188 | 1.3405e-05
2012-11-05 06:27AM | 1567037-1 | PKC2 | Urban | Equipment Failure | 856 | 12.6379 | 10818 | 0.012085 | 0.00095625
2013-05-19 05:42PM | 1618621-1 | PKC2 | Urban | Animals | 857 | 60 | 51420 | 0.057442 | 0.00095737
2013-04-30 05:53AM | 1613808-1 | PKC2 | Urban | Third Party Impacts | 4 | 185.5 | 742 | 0.0008289 | 4.4685e-06
2012-11-09 01:40PM | 1568869-1 | PKD2 | Urban | Equipment Failure | 60 | 89 | 5340 | 0.0059654 | 6.7027e-05
2013-02-01 03:13PM | 1590770-1 | PKD2 | Urban | Equipment Failure | 1 | 124 | 124 | 0.00013852 | 1.1171e-06
2012-08-15 03:07PM | 1546094-1 | PKE2 | Urban | Equipment Failure | 1 | 50 | 50 | 5.5856e-05 | 1.1171e-06
2012-11-27 04:23PM | 1573152-1 | PKE2 | Urban | Equipment Failure | 38 | 158.3421 | 6017 | 0.0067217 | 4.2451e-05
2012-11-03 06:06PM | 1566903-1 | PKE2 | Urban | Equipment Failure | 224 | 218.25 | 48888 | 0.054614 | 0.00025023
2012-12-03 04:15AM | 1574843-1 | PKE2 | Urban | Equipment Failure | 1649 | 186.077 | 306841 | 0.34278 | 0.0018421
2013-02-25 09:25PM | 1598413-1 | PKE2 | Urban | Third Party Impacts | 1611 | 111.8982 | 180268 | 0.20138 | 0.0017997
2012-08-13 08:00PM | 1545554-1 | PKF2 | Urban | Equipment Failure | 1 | 105 | 105 | 0.0001173 | 1.1171e-06
2012-10-22 06:14PM | 1563737-1 | PKF2 | Urban | Equipment Failure | 763 | 38.1992 | 29146 | 0.03256 | 0.00085236
2013-01-13 10:18PM | 1584573-1 | PKF2 | Urban | Equipment Failure | 162 | 90 | 14580 | 0.016288 | 0.00018097
2013-06-02 04:15PM | 1622363-1 | PKF2 | Urban | Other | 765 | 29 | 22185 | 0.024783 | 0.0008546
2013-05-13 06:52AM | 1616788-1 | T838 | Rural Short | Equipment Failure | 22 | 181.0909 | 3984 | 0.0044506 | 2.4577e-05
2012-07-01 05:30PM | 1534667-1 | T838 | Rural Short | Animals | 29 | 101.7931 | 2952 | 0.0032977 | 3.2396e-05
2013-02-09 10:03PM | 1593130-1 | T838 | Rural Short | Weather | 631 | 162.8669 | 102769 | 0.11481 | 0.0007049
2013-03-31 09:58PM | 1607187-1 | T838 | Rural Short | Equipment Failure | 631 | 104.2536 | 65784 | 0.073489 | 0.0007049
2013-05-18 12:51PM | 1618519-1 | 1962 | Urban | Operatonal Error | 1 | 55 | 55 | 6.1442e-05 | 1.1171e-06
2012-12-23 04:02PM | 1579929-1 | 1963 | Urban | Equipment Failure | 1 | 4 | 4 | 4.4685e-06 | 1.1171e-06
2012-12-23 06:40PM | 1579986-1 | 7910 | Rural Short | Other | 1 | 293 | 293 | 0.00032732 | 1.1171e-06
2013-01-04 05:17PM | 1582403-1 | 7910 | Rural Short | Vegetation | 1 | 424 | 424 | 0.00047366 | 1.1171e-06
2013-01-11 04:30PM | 1584169-1 | 7910 | Rural Short | Other | 1 | 46 | 46 | 5.1388e-05 | 1.1171e-06
2012-11-26 02:13PM | 1572745-1 | MG1267 | Rural Short | Weather | 2634 | 46.0847 | 121387 | 0.1356 | 0.0029425
2012-12-25 09:30AM | 1580440-1 | 57444 | Rural Short | Weather | 2 | 111 | 222 | 0.000248 | 2.2342e-06
2012-07-26 05:24PM | 1540661-1 | 57444 | Rural Short | Equipment Failure | 27 | 1052.3704 | 28414 | 0.031742 | 3.0162e-05
2012-11-27 07:30PM | 1573220-1 | 57444 | Rural Short | Vegetation | 56 | 148.3214 | 8306 | 0.0092788 | 6.2559e-05
2012-11-28 06:42PM | 1573675-1 | 57444 | Rural Short | Weather | 56 | 533.75 | 29890 | 0.033391 | 6.2559e-05
2013-02-16 07:20AM | 1594836-1 | 57448 | Rural Short | Animals | 2 | 129 | 258 | 0.00028822 | 2.2342e-06
2012-07-13 07:21PM | 1537716-1 | 57448 | Rural Short | Equipment Failure | 1 | 304 | 304 | 0.0003396 | 1.1171e-06
2012-12-28 04:03PM | 1581221-1 | 57448 | Rural Short | Equipment Failure | 1 | 191 | 191 | 0.00021337 | 1.1171e-06
2012-12-06 06:17AM | 1575988-1 | 57448 | Rural Short | Other | 1 | 273 | 273 | 0.00030497 | 1.1171e-06
2013-02-10 02:53PM | 1593240-1 | 57448 | Rural Short | Weather | 2 | 112 | 224 | 0.00025023 | 2.2342e-06
2012-12-10 09:50AM | 1579334-1 | 57448 | Rural Short | Other | 2 | 60 | 120 | 0.00013405 | 2.2342e-06
2012-12-10 11:00AM | 1579343-1 | 57448 | Rural Short | Other | 1 | 45 | 45 | 5.027e-05 | 1.1171e-06
2012-12-10 11:40AM | 1579345-1 | 57448 | Rural Short | Other | 2 | 40 | 80 | 8.937e-05 | 2.2342e-06
2012-12-25 03:19PM | 1580522-1 | 57448 | Rural Short | Weather | 1 | 1246 | 1246 | 0.0013919 | 1.1171e-06
2012-11-23 10:00AM | 1575065-1 | 57448 | Rural Short | Other | 5 | 47 | 235 | 0.00026252 | 5.5856e-06
2012-12-25 03:03PM | 1580555-1 | 57448 | Rural Short | Weather | 1 | 199 | 199 | 0.00022231 | 1.1171e-06
2013-02-09 09:50PM | 1593128-1 | 57448 | Rural Short | Weather | 32 | 856 | 27392 | 0.0306 | 3.5748e-05
2013-06-29 07:46PM | 1631788-1 | 57448 | Rural Short | Operatonal Error | 127 | 1 | 127 | 0.00014187 | 0.00014187
2012-07-12 03:05PM | 1537422-1 | 57448 | Rural Short | Equipment Failure | 30 | 348.2333 | 10447 | 0.011671 | 3.3514e-05
2013-02-08 06:19PM | 1592940-1 | 57448 | Rural Short | Weather | 25 | 108.2 | 2705 | 0.0030218 | 2.7928e-05
2013-03-02 03:47AM | 1600121-1 | W163 | Rural Short | Weather | 28 | 415 | 11620 | 0.012981 | 3.1279e-05
2012-12-07 05:22PM | 1576485-1 | W163 | Rural Short | Other | 1 | 96 | 96 | 0.00010724 | 1.1171e-06
2012-11-30 06:20AM | 1574060-1 | W163 | Rural Short | Weather | 1 | 311 | 311 | 0.00034742 | 1.1171e-06
2013-02-01 03:37PM | 1590795-1 | W163 | Rural Short | Weather | 1 | 1123 | 1123 | 0.0012545 | 1.1171e-06
2013-04-16 06:00PM | 1610805-1 | W163 | Rural Short | Equipment Failure | 1 | 213 | 213 | 0.00023795 | 1.1171e-06
2013-03-23 10:15PM | 1605830-1 | W163 | Rural Short | Equipment Failure | 1 | 107 | 107 | 0.00011953 | 1.1171e-06
2013-03-08 12:40PM | 1602023-1 | W163 | Rural Short | Other | 1 | 117 | 117 | 0.0001307 | 1.1171e-06
2012-12-25 09:30PM | 1580602-1 | W163 | Rural Short | Weather | 2 | 895 | 1790 | 0.0019996 | 2.2342e-06
2012-08-24 03:52PM | 1549281-1 | W163 | Rural Short | Weather | 5 | 134.2 | 671 | 0.00074959 | 5.5856e-06
2012-11-29 06:09PM | 1574024-1 | W163 | Rural Short | Weather | 4 | 101 | 404 | 0.00045132 | 4.4685e-06
2013-02-01 05:15PM | 1590852-1 | W163 | Rural Short | Weather | 2 | 21 | 42 | 4.6919e-05 | 2.2342e-06
2012-12-08 08:32PM | 1576579-1 | W163 | Rural Short | Equipment Failure | 4 | 69 | 276 | 0.00030833 | 4.4685e-06
2012-12-25 01:53PM | 1580476-1 | W163 | Rural Short | Weather | 22 | 407 | 8954 | 0.010003 | 2.4577e-05
2013-03-02 02:50PM | 1600207-1 | W163 | Rural Short | Weather | 17 | 414.3529 | 7044 | 0.007869 | 1.8991e-05
2012-11-28 06:40PM | 1573673-1 | W163 | Rural Short | Weather | 190 | 621.5474 | 118094 | 0.13193 | 0.00021225
2013-02-01 01:52PM | 1590677-1 | W163 | Rural Short | Weather | 88 | 217 | 19096 | 0.021333 | 9.8307e-05
2013-02-10 07:19PM | 1593312-1 | W163 | Rural Short | Weather | 85 | 217 | 18445 | 0.020605 | 9.4955e-05
2013-05-14 01:59PM | 1617241-1 | W163 | Rural Short | Vegetation | 89 | 272.2022 | 24226 | 0.027063 | 9.9424e-05
2012-11-28 08:29PM | 1573703-1 | W164 | Rural Short | Weather | 2 | 325 | 650 | 0.00072613 | 2.2342e-06
2012-11-29 01:56AM | 1573722-1 | W164 | Rural Short | Weather | 1 | 670 | 670 | 0.00074847 | 1.1171e-06
2012-11-28 07:22PM | 1573684-1 | W164 | Rural Short | Weather | 1 | 390 | 390 | 0.00043568 | 1.1171e-06
2012-11-29 01:56AM | 1573723-1 | W164 | Rural Short | Weather | 1 | 817 | 817 | 0.00091269 | 1.1171e-06
2012-12-26 04:16PM | 1580696-1 | W164 | Rural Short | Weather | 1 | 157 | 157 | 0.00017539 | 1.1171e-06
2012-12-25 03:12PM | 1580516-1 | W164 | Rural Short | Weather | 14 | 279 | 3906 | 0.0043635 | 1.564e-05
2012-12-25 08:04PM | 1580584-1 | W164 | Rural Short | Weather | 14 | 1076 | 15064 | 0.016828 | 1.564e-05
2012-08-07 04:06AM | 1543322-1 | J459 | Urban | Equipment Failure | 1 | 365 | 365 | 0.00040775 | 1.1171e-06
2012-11-26 12:26PM | 1572724-1 | J459 | Urban | Third Party Impacts | 105 | 90.381 | 9490 | 0.010601 | 0.0001173
2013-06-11 07:24PM | 1624412-1 | J459 | Urban | Equipment Failure | 1 | 109 | 109 | 0.00012177 | 1.1171e-06
2013-01-31 04:21PM | 1590410-1 | J459 | Urban | Equipment Failure | 8 | 149 | 1192 | 0.0013316 | 8.937e-06
2013-02-09 10:42PM | 1593134-1 | J459 | Urban | Other | 8 | 150 | 1200 | 0.0013405 | 8.937e-06
2013-06-03 09:14AM | 1622441-1 | J459 | Urban | Equipment Failure | 1 | 192 | 192 | 0.00021449 | 1.1171e-06
2012-10-23 03:07PM | 1564036-1 | J459 | Urban | Other | 9 | 44.7778 | 403 | 0.0004502 | 1.0054e-05
2013-06-07 06:40PM | 1623888-1 | J459 | Urban | Equipment Failure | 21 | 35 | 735 | 0.00082108 | 2.346e-05
2012-08-09 02:18PM | 1544143-1 | J459 | Urban | Equipment Failure | 21 | 72.4286 | 1521 | 0.0016991 | 2.346e-05
2013-06-06 01:21PM | 1623468-1 | J459 | Urban | Equipment Failure | 2 | 206 | 412 | 0.00046025 | 2.2342e-06
2013-03-16 03:53PM | 1604005-1 | J459 | Urban | Equipment Failure | 1814 | 44 | 79816 | 0.089164 | 0.0020265
2013-02-25 09:01AM | 1597899-1 | J459 | Urban | Equipment Failure | 1 | 284 | 284 | 0.00031726 | 1.1171e-06
2013-03-07 02:39PM | 1601773-1 | J459 | Urban | Equipment Failure | 1 | 137 | 137 | 0.00015305 | 1.1171e-06
2012-10-03 04:45AM | 1558481-1 | J460 | Urban | Animals | 59 | 48.7966 | 2879 | 0.0032162 | 6.591e-05
2012-10-07 03:31PM | 1559538-1 | J465 | Urban | Equipment Failure | 1 | 154 | 154 | 0.00017204 | 1.1171e-06
2013-06-23 11:27AM | 1627231-1 | J465 | Urban | Equipment Failure | 1 | 195 | 195 | 0.00021784 | 1.1171e-06
2013-06-20 11:58AM | 1626614-1 | J465 | Urban | Third Party Impacts | 102 | 288.5784 | 29435 | 0.032882 | 0.00011395
2012-10-28 01:18PM | 1565223-1 | J465 | Urban | Weather | 70 | 58.0286 | 4062 | 0.0045377 | 7.8198e-05
2013-06-20 01:25PM | 1626640-1 | J465 | Urban | Third Party Impacts | 15 | 216.4667 | 3247 | 0.0036273 | 1.6757e-05
2012-11-08 05:00PM | 1568400-1 | J465 | Urban | Weather | 1588 | 111 | 176268 | 0.19691 | 0.001774
2012-11-30 09:31PM | 1574504-1 | J465 | Urban | Equipment Failure | 1 | 76 | 76 | 8.4901e-05 | 1.1171e-06
2013-06-26 08:19AM | 1628162-1 | J467 | Urban | Weather | 7 | 98 | 686 | 0.00076634 | 7.8198e-06
2013-06-28 09:29PM | 1629166-1 | J467 | Urban | Weather | 7 | 88.7143 | 621 | 0.00069373 | 7.8198e-06
2012-11-25 02:22PM | 1572517-1 | J468 | Urban | Equipment Failure | 21 | 243 | 5103 | 0.0057007 | 2.346e-05
2012-10-13 12:16PM | 1561479-1 | J468 | Urban | Equipment Failure | 1 | 198 | 198 | 0.00022119 | 1.1171e-06
2013-01-27 02:33PM | 1589136-1 | J469 | Urban | Third Party Impacts | 16 | 34.5 | 552 | 0.00061665 | 1.7874e-05
2012-10-30 07:07PM | 1565847-1 | J469 | Urban | Equipment Failure | 30 | 158 | 4740 | 0.0052951 | 3.3514e-05
2012-08-17 03:14PM | 1546936-1 | J469 | Urban | Weather | 10 | 94.3 | 943 | 0.0010534 | 1.1171e-05
2012-11-08 05:25PM | 1568428-1 | J469 | Urban | Weather | 1 | 342 | 342 | 0.00038206 | 1.1171e-06
2012-11-08 05:45PM | 1568444-1 | J469 | Urban | Weather | 1 | 316 | 316 | 0.00035301 | 1.1171e-06
2012-11-08 05:49PM | 1568448-1 | J469 | Urban | Weather | 37 | 309.5946 | 11455 | 0.012797 | 4.1333e-05
2012-12-12 04:27PM | 1577510-1 | J469 | Urban | Equipment Failure | 1 | 170 | 170 | 0.00018991 | 1.1171e-06
2013-03-13 08:22PM | 1603275-1 | J472 | Urban | Equipment Failure | 32 | 117.6562 | 3765 | 0.004206 | 3.5748e-05
2012-10-14 07:16PM | 1561610-1 | J472 | Urban | Other | 100 | 46.88 | 4688 | 0.0052371 | 0.00011171
2013-03-13 08:29PM | 1603276-1 | J472 | Urban | Equipment Failure | 14 | 233.7143 | 3272 | 0.0036552 | 1.564e-05
2013-05-09 04:38PM | 1616136-1 | J473 | Urban | Third Party Impacts | 20 | 86.1 | 1722 | 0.0019237 | 2.2342e-05
2012-08-31 05:07PM | 1551078-1 | J473 | Urban | Equipment Failure | 1 | 253 | 253 | 0.00028263 | 1.1171e-06
2012-12-13 01:14PM | 1577667-1 | J474 | Urban | Equipment Failure | 17 | 57 | 969 | 0.0010825 | 1.8991e-05
2013-06-16 05:05PM | 1625571-1 | J474 | Urban | Equipment Failure | 1 | 115 | 115 | 0.00012847 | 1.1171e-06
2012-10-18 10:56AM | 1562760-1 | J474 | Urban | Third Party Impacts | 103 | 69 | 7107 | 0.0079394 | 0.00011506
2013-06-21 01:49PM | 1626951-1 | J474 | Urban | Equipment Failure | 1 | 224 | 224 | 0.00025023 | 1.1171e-06
2012-12-21 03:13PM | 1579712-1 | J474 | Urban | Third Party Impacts | 34 | 108 | 3672 | 0.0041021 | 3.7982e-05
2013-02-09 11:00PM | 1593139-1 | J474 | Urban | Third Party Impacts | 14 | 365 | 5110 | 0.0057085 | 1.564e-05
2012-10-03 08:32AM | 1558499-1 | J474 | Urban | Equipment Failure | 1 | 345 | 345 | 0.00038541 | 1.1171e-06
2013-02-27 06:06PM | 1599145-1 | J474 | Urban | Equipment Failure | 1 | 223 | 223 | 0.00024912 | 1.1171e-06
2012-08-08 07:09AM | 1543683-1 | J477 | Rural Short | Other | 6 | 155.8333 | 935 | 0.0010445 | 6.7027e-06
2012-10-25 07:20AM | 1564473-1 | J477 | Rural Short | Other | 9 | 128 | 1152 | 0.0012869 | 1.0054e-05
2012-10-25 08:10AM | 1564502-1 | J477 | Rural Short | Vegetation | 5 | 19 | 95 | 0.00010613 | 5.5856e-06
2012-11-18 08:31PM | 1570718-1 | J477 | Rural Short | Vegetation | 1302 | 76.5998 | 99733 | 0.11141 | 0.0014545
2012-12-22 05:26AM | 1579760-1 | J477 | Rural Short | Animals | 29 | 120 | 3480 | 0.0038876 | 3.2396e-05
2013-02-01 03:20PM | 1590809-1 | J477 | Rural Short | Vegetation | 29 | 70 | 2030 | 0.0022678 | 3.2396e-05
2012-12-21 08:04PM | 1579743-1 | J477 | Rural Short | Equipment Failure | 1 | 86 | 86 | 9.6072e-05 | 1.1171e-06
2013-01-21 11:47AM | 1586927-1 | J478 | Urban | Third Party Impacts | 96 | 292.8333 | 28112 | 0.031404 | 0.00010724
2013-02-26 05:45AM | 1598444-1 | J478 | Urban | Equipment Failure | 47 | 246.1064 | 11567 | 0.012922 | 5.2505e-05
2013-02-09 04:26PM | 1593090-1 | J478 | Urban | Equipment Failure | 10 | 51 | 510 | 0.00056973 | 1.1171e-05
2013-02-09 06:26PM | 1593106-1 | J478 | Urban | Equipment Failure | 10 | 585.8 | 5858 | 0.0065441 | 1.1171e-05
2013-03-02 02:36AM | 1600117-1 | J478 | Urban | Other | 22 | 235 | 5170 | 0.0057755 | 2.4577e-05
2013-03-22 01:25AM | 1605333-1 | J478 | Urban | Other | 13 | 258 | 3354 | 0.0037468 | 1.4523e-05
2013-06-26 04:51AM | 1628131-1 | J478 | Urban | Equipment Failure | 12 | 187 | 2244 | 0.0025068 | 1.3405e-05
2013-01-28 05:55PM | 1589340-1 | J478 | Urban | Equipment Failure | 1 | 178 | 178 | 0.00019885 | 1.1171e-06
2013-01-15 10:37AM | 1585063-1 | J480 | Urban | Other | 3 | 85.3333 | 256 | 0.00028598 | 3.3514e-06
2012-12-31 10:00AM | 1581461-1 | J481 | Urban | Equipment Failure | 93 | 148.8387 | 13842 | 0.015463 | 0.00010389
2013-03-18 03:02PM | 1604437-1 | J482 | Urban | Equipment Failure | 41 | 272 | 11152 | 0.012458 | 4.5802e-05
2013-02-02 05:43PM | 1591096-1 | J482 | Urban | Animals | 777 | 36 | 27972 | 0.031248 | 0.000868
2013-06-08 11:58AM | 1623948-1 | J482 | Urban | Third Party Impacts | 805 | 17.6708 | 14225 | 0.015891 | 0.00089928
2012-11-07 10:13PM | 1567963-1 | J482 | Urban | Equipment Failure | 1 | 209 | 209 | 0.00023348 | 1.1171e-06
2013-02-22 04:05PM | 1596514-1 | J483 | Urban | Other | 75 | 118.7067 | 8903 | 0.0099457 | 8.3784e-05
2013-01-30 06:10PM | 1590125-1 | J483 | Urban | Other | 11 | 81 | 891 | 0.00099535 | 1.2288e-05
2013-05-14 10:00PM | 1617355-1 | J483 | Urban | Other | 20 | 105 | 2100 | 0.002346 | 2.2342e-05
2012-08-27 10:28AM | 1549692-1 | J483 | Urban | Equipment Failure | 1 | 241 | 241 | 0.00026923 | 1.1171e-06
2012-09-17 11:04AM | 1555028-1 | J483 | Urban | Equipment Failure | 1 | 451 | 451 | 0.00050382 | 1.1171e-06
2012-08-22 08:07PM | 1548214-1 | MG1208 | Urban | Other | 8 | 88 | 704 | 0.00078645 | 8.937e-06
2013-04-09 05:03PM | 1608987-1 | MG1208 | Urban | Third Party Impacts | 24 | 98.6667 | 2368 | 0.0026453 | 2.6811e-05
2012-09-06 08:05PM | 1552525-1 | MG1208 | Urban | Equipment Failure | 1926 | 149.0665 | 287102 | 0.32073 | 0.0021516
2013-03-07 05:59PM | 1601831-1 | MG1208 | Urban | Equipment Failure | 1 | 165 | 165 | 0.00018432 | 1.1171e-06
2012-08-17 01:17PM | 1546732-1 | MG1219 | Rural Short | Other | 1 | 136 | 136 | 0.00015193 | 1.1171e-06
2012-08-17 11:48AM | 1546561-1 | MG1219 | Rural Short | Other | 1 | 225 | 225 | 0.00025135 | 1.1171e-06
2012-12-23 09:06PM | 1580021-1 | MG1219 | Rural Short | Weather | 3 | 302 | 906 | 0.0010121 | 3.3514e-06
2013-01-22 03:03PM | 1587310-1 | MG1219 | Rural Short | Other | 46 | 237 | 10902 | 0.012179 | 5.1388e-05
2013-01-04 05:17PM | 1582402-1 | MG1219 | Rural Short | Vegetation | 559 | 184.6064 | 103195 | 0.11528 | 0.00062447
2013-01-10 03:59PM | 1583885-1 | MG1219 | Rural Short | Operatonal Error | 105 | 2.5333 | 266 | 0.00029715 | 0.0001173
2013-02-19 10:06AM | 1595378-1 | MG1267 | Rural Short | Other | 1 | 29 | 29 | 3.2396e-05 | 1.1171e-06
2013-01-22 03:35PM | 1587344-1 | MG1267 | Rural Short | Weather | 24 | 238 | 5712 | 0.006381 | 2.6811e-05
2013-01-24 07:00PM | 1588077-1 | MG1267 | Rural Short | Equipment Failure | 1 | 76 | 76 | 8.4901e-05 | 1.1171e-06
2013-04-23 11:15PM | 1612613-1 | MG1267 | Rural Short | Equipment Failure | 36 | 445 | 16020 | 0.017896 | 4.0216e-05
2013-04-17 07:51AM | 1610883-1 | MG1267 | Rural Short | Other | 35 | 78.7429 | 2756 | 0.0030788 | 3.9099e-05
2012-12-25 05:29PM | 1580560-1 | MG1267 | Rural Short | Weather | 4 | 98 | 392 | 0.00043791 | 4.4685e-06
2013-05-22 12:18PM | 1620606-1 | MG1267 | Rural Short | Equipment Failure | 5 | 37 | 185 | 0.00020667 | 5.5856e-06
2013-06-24 11:43PM | 1627648-1 | MG1267 | Rural Short | Vegetation | 792 | 211.6187 | 167602 | 0.18723 | 0.00088476
2012-09-06 10:17AM | 1552335-1 | MG1267 | Rural Short | Weather | 577 | 10.2617 | 5921 | 0.0066145 | 0.00064458
2013-02-09 01:47AM | 1592980-1 | MG1267 | Rural Short | Equipment Failure | 153 | 180.1373 | 27561 | 0.030789 | 0.00017092
2013-01-09 05:55PM | 1583696-1 | MG1282 | Rural Short | Other | 7 | 23.1429 | 162 | 0.00018097 | 7.8198e-06
2013-01-09 03:21PM | 1583662-1 | MG1282 | Rural Short | Third Party Impacts | 2 | 20 | 40 | 4.4685e-05 | 2.2342e-06
2013-01-22 09:44PM | 1587536-1 | MG1286 | Rural Short | Weather | 9 | 747.4444 | 6727 | 0.0075149 | 1.0054e-05
2012-12-05 09:16AM | 1575618-1 | MG1286 | Rural Short | Weather | 373 | 139.1528 | 51904 | 0.057983 | 0.00041669
2013-05-23 08:05PM | 1619867-1 | MG1286 | Rural Short | Vegetation | 7 | 106 | 742 | 0.0008289 | 7.8198e-06
2012-07-15 11:42AM | 1537884-1 | MGB2 | Urban | Other | 199 | 74.2462 | 14775 | 0.016505 | 0.00022231
2012-08-14 04:46AM | 1545585-1 | MGC2 | Rural Short | Animals | 7 | 154 | 1078 | 0.0012043 | 7.8198e-06
2012-07-24 05:58PM | 1540115-1 | MGC2 | Rural Short | Equipment Failure | 1 | 79 | 79 | 8.8252e-05 | 1.1171e-06
2012-08-26 05:13PM | 1549565-1 | MGC2 | Rural Short | Equipment Failure | 3 | 193.6667 | 581 | 0.00064905 | 3.3514e-06
2012-09-19 12:57PM | 1555720-1 | MGC2 | Rural Short | Other | 1 | 279 | 279 | 0.00031168 | 1.1171e-06
2012-07-05 02:46PM | 1535899-1 | MGE2 | Rural Short | Equipment Failure | 1 | 172 | 172 | 0.00019214 | 1.1171e-06
2012-08-21 04:35PM | 1547818-1 | MGE2 | Rural Short | Equipment Failure | 4 | 139 | 556 | 0.00062112 | 4.4685e-06
2012-09-07 03:45PM | 1552953-1 | MGE2 | Rural Short | Weather | 372 | 0.29032 | 108 | 0.00012065 | 0.00041557
2012-11-26 03:23PM | 1572769-1 | MGF2 | Rural Short | Other | 1 | 11 | 11 | 1.2288e-05 | 1.1171e-06
2012-09-27 05:56PM | 1557622-1 | MGF2 | Rural Short | Vegetation | 46 | 98 | 4508 | 0.005036 | 5.1388e-05
2012-12-13 05:58AM | 1577556-1 | MGF2 | Rural Short | Animals | 1089 | 129.4114 | 140929 | 0.15743 | 0.0012165
2012-09-10 08:36AM | 1553358-1 | MGF2 | Rural Short | Equipment Failure | 1 | 134 | 134 | 0.00014969 | 1.1171e-06
2013-06-16 08:12AM | 1625513-1 | 53312 | Urban | Equipment Failure | 1 | 67 | 67 | 7.4847e-05 | 1.1171e-06
2013-04-16 07:37AM | 1610600-1 | 53314 | Urban | Weather | 22 | 192 | 4224 | 0.0047187 | 2.4577e-05
2012-10-30 09:54AM | 1567777-1 | MC1252 | Rural Short | Third Party Impacts | 369 | 129.4146 | 47754 | 0.053347 | 0.00041222
2013-04-02 09:39AM | 1607302-1 | MC1252 | Rural Short | Other | 6 | 56 | 336 | 0.00037535 | 6.7027e-06
2012-09-11 06:25PM | 1553828-1 | MC1252 | Rural Short | Equipment Failure | 10 | 1070.7 | 10707 | 0.011961 | 1.1171e-05
2012-09-30 08:37PM | 1558188-1 | MC1252 | Rural Short | Equipment Failure | 10 | 368.5 | 3685 | 0.0041166 | 1.1171e-05
2012-10-30 09:54AM | 1567777-1 | MC1278 | Rural Short | Third Party Impacts | 22 | 130.8636 | 2879 | 0.0032162 | 2.4577e-05
2013-05-13 10:41AM | 1616856-1 | MC1278 | Rural Short | Third Party Impacts | 28 | 83.1071 | 2327 | 0.0025995 | 3.1279e-05
2012-07-30 08:14AM | 1541207-1 | 6419 | Urban | Other | 1784 | 71.6026 | 127739 | 0.1427 | 0.0019929
2013-03-04 11:44AM | 1600547-1 | 6420 | Urban | Equipment Failure | 28 | 86.7143 | 2428 | 0.0027124 | 3.1279e-05
2012-10-15 03:02PM | 1561900-1 | 6420 | Urban | Equipment Failure | 269 | 33.5725 | 9031 | 0.010089 | 0.00030051
2013-01-18 03:04PM | 1586167-1 | 6420 | Urban | Weather | 17 | 51 | 867 | 0.00096854 | 1.8991e-05
2013-05-28 02:31PM | 1621030-1 | 6421 | Urban | Third Party Impacts | 26 | 119.0769 | 3096 | 0.0034586 | 2.9045e-05
2013-06-01 05:39PM | 1622254-1 | 6421 | Urban | Equipment Failure | 71 | 303 | 21513 | 0.024033 | 7.9316e-05
2013-06-26 06:35AM | 1628141-1 | 6421 | Urban | Equipment Failure | 1 | 694 | 694 | 0.00077528 | 1.1171e-06
2012-07-30 08:05AM | 1541204-1 | 6421 | Urban | Equipment Failure | 122 | 18.7295 | 2285 | 0.0025526 | 0.00013629
2012-08-17 07:52AM | 1546467-1 | 6421 | Urban | Equipment Failure | 426 | 123.5822 | 52646 | 0.058812 | 0.00047589
2012-08-30 06:24PM | 1550798-1 | 6421 | Urban | Equipment Failure | 119 | 163.9328 | 19508 | 0.021793 | 0.00013294
2012-12-03 10:00AM | 1574964-1 | 6421 | Urban | Operatonal Error | 559 | 5 | 2795 | 0.0031224 | 0.00062447
2012-12-03 10:48AM | 1574982-1 | 6421 | Urban | Equipment Failure | 15 | 1.6 | 24 | 2.6811e-05 | 1.6757e-05
2012-12-29 08:50AM | 1581274-1 | 6421 | Urban | Animals | 563 | 78.444 | 44164 | 0.049336 | 0.00062894
2013-03-19 11:22PM | 1604696-1 | 6421 | Urban | Animals | 570 | 108.3947 | 61785 | 0.069021 | 0.00063676
2012-08-08 01:11PM | 1543804-1 | 6421 | Urban | Other | 41 | 155.561 | 6378 | 0.007125 | 4.5802e-05
2013-02-05 08:01PM | 1591864-1 | 6421 | Urban | Other | 1 | 506 | 506 | 0.00056526 | 1.1171e-06
2012-09-25 03:37PM | 1556963-1 | 6423 | Urban | Operatonal Error | 62 | 213.1774 | 13217 | 0.014765 | 6.9261e-05
2012-07-30 09:16AM | 1541249-1 | 6424 | Urban | Equipment Failure | 761 | 40.3995 | 30744 | 0.034345 | 0.00085013
2012-08-31 10:46AM | 1550912-1 | 6424 | Urban | Third Party Impacts | 78 | 233.4103 | 18206 | 0.020338 | 8.7135e-05
2013-06-27 09:55AM | 1628600-1 | 6424 | Urban | Equipment Failure | 21 | 422.4286 | 8871 | 0.00991 | 2.346e-05
2012-12-23 07:12PM | 1579996-1 | 6430 | Urban | Equipment Failure | 25 | 82.96 | 2074 | 0.0023169 | 2.7928e-05
2013-01-13 09:12PM | 1584539-1 | 6430 | Urban | Equipment Failure | 30 | 70.0667 | 2102 | 0.0023482 | 3.3514e-05
2013-04-15 06:30PM | 1610483-1 | 6430 | Urban | Weather | 735 | 200.6 | 147441 | 0.16471 | 0.00082108
2012-10-20 07:00AM | 1563230-1 | B743 | Urban | Third Party Impacts | 26 | 89.5385 | 2328 | 0.0026007 | 2.9045e-05
2012-09-24 06:54AM | 1556610-1 | B743 | Urban | Third Party Impacts | 5 | 162.6 | 813 | 0.00090822 | 5.5856e-06
2012-09-24 08:44AM | 1556622-1 | B743 | Urban | Other | 1 | 52 | 52 | 5.809e-05 | 1.1171e-06
2012-07-04 06:21AM | 1535412-1 | B743 | Urban | Other | 21 | 534.8571 | 11232 | 0.012547 | 2.346e-05
2013-04-16 09:20AM | 1610616-1 | B743 | Urban | Equipment Failure | 2 | 662.5 | 1325 | 0.0014802 | 2.2342e-06
2013-06-06 03:59AM | 1623317-1 | B743 | Urban | Animals | 1033 | 70.2033 | 72520 | 0.081014 | 0.001154
2013-06-23 04:05PM | 1627269-1 | B743 | Urban | Animals | 1161 | 142.031 | 164898 | 0.18421 | 0.001297
2012-12-12 02:35PM | 1577481-1 | B745 | Urban | Third Party Impacts | 63 | 451.8571 | 28467 | 0.031801 | 7.0379e-05
2013-02-19 05:25AM | 1595281-1 | B746 | Urban | Third Party Impacts | 52 | 139 | 7228 | 0.0080745 | 5.809e-05
2012-08-13 09:23AM | 1545328-1 | B747 | Urban | Vegetation | 5 | 252.4 | 1262 | 0.0014098 | 5.5856e-06
2012-08-22 04:51AM | 1547945-1 | B747 | Urban | Other | 43 | 149.907 | 6446 | 0.007201 | 4.8036e-05
2013-03-12 01:20PM | 1602861-1 | B747 | Urban | Other | 94 | 105 | 9870 | 0.011026 | 0.00010501
2012-11-10 09:24AM | 1568973-1 | B747 | Urban | Equipment Failure | 1 | 322 | 322 | 0.00035971 | 1.1171e-06
2013-03-13 07:45AM | 1604966-1 | 7908 | Rural Short | Weather | 1 | 538 | 538 | 0.00060101 | 1.1171e-06
2013-06-19 08:09AM | 1628361-1 | MVB2 | Rural Short | Operatonal Error | 1088 | 1.0064 | 1095 | 0.0012232 | 0.0012154
2012-08-19 09:06AM | 1547257-1 | MVB2 | Rural Short | Equipment Failure | 26 | 227 | 5902 | 0.0065932 | 2.9045e-05
2012-08-31 11:03AM | 1550923-1 | MVB2 | Rural Short | Animals | 2 | 119 | 238 | 0.00026587 | 2.2342e-06
2013-05-01 09:06AM | 1614085-1 | MVB2 | Rural Short | Other | 1 | 157 | 157 | 0.00017539 | 1.1171e-06
2012-12-28 02:28PM | 1581248-1 | MVB2 | Rural Short | Weather | 3 | 242 | 726 | 0.00081103 | 3.3514e-06
2013-01-27 07:25AM | 1589035-1 | MVB2 | Rural Short | Other | 1 | 182 | 182 | 0.00020332 | 1.1171e-06
2013-02-26 11:46AM | 1598587-1 | MVB2 | Rural Short | Other | 2 | 175 | 350 | 0.00039099 | 2.2342e-06
2013-04-14 02:03PM | 1610207-1 | MVB2 | Rural Short | Equipment Failure | 1 | 81 | 81 | 9.0487e-05 | 1.1171e-06
2012-11-30 03:40PM | 1574298-1 | MVB2 | Rural Short | Weather | 2 | 118.5 | 237 | 0.00026476 | 2.2342e-06
2012-09-09 05:09PM | 1553307-1 | MVB2 | Rural Short | Equipment Failure | 1 | 88 | 88 | 9.8307e-05 | 1.1171e-06
2013-01-27 05:33AM | 1588989-1 | MVB2 | Rural Short | Other | 7 | 398 | 2786 | 0.0031123 | 7.8198e-06
2013-02-11 11:13AM | 1593490-1 | MVB2 | Rural Short | Other | 2 | 112 | 224 | 0.00025023 | 2.2342e-06
2013-05-13 06:05AM | 1616781-1 | MVB2 | Rural Short | Other | 1 | 157 | 157 | 0.00017539 | 1.1171e-06
2013-01-07 04:26PM | 1583005-1 | MVB2 | Rural Short | Equipment Failure | 1 | 89 | 89 | 9.9424e-05 | 1.1171e-06
2012-11-27 08:02PM | 1573273-1 | MVB2 | Rural Short | Weather | 3 | 88 | 264 | 0.00029492 | 3.3514e-06
2012-12-18 05:24AM | 1578652-1 | MVB2 | Rural Short | Vegetation | 9 | 410 | 3690 | 0.0041222 | 1.0054e-05
2012-12-11 06:20PM | 1577198-1 | MVB2 | Rural Short | Equipment Failure | 31 | 191 | 5921 | 0.0066145 | 3.4631e-05
2012-12-30 03:45AM | 1581345-1 | MVB2 | Rural Short | Other | 9 | 274.6667 | 2472 | 0.0027615 | 1.0054e-05
2012-12-23 08:01PM | 1580006-1 | MVB2 | Rural Short | Weather | 25 | 161 | 4025 | 0.0044964 | 2.7928e-05
2013-01-27 04:53AM | 1588980-1 | MVB2 | Rural Short | Other | 25 | 337 | 8425 | 0.0094117 | 2.7928e-05
2013-06-19 03:03PM | 1626405-1 | MVB2 | Rural Short | Equipment Failure | 25 | 204 | 5100 | 0.0056973 | 2.7928e-05
2012-12-05 01:09PM | 1575768-1 | MVB2 | Rural Short | Vegetation | 44 | 322 | 14168 | 0.015827 | 4.9153e-05
2012-09-02 09:56AM | 1551274-1 | MVB2 | Rural Short | Equipment Failure | 2 | 193 | 386 | 0.00043121 | 2.2342e-06
2012-12-28 02:12PM | 1581187-1 | MVB2 | Rural Short | Equipment Failure | 225 | 102.7422 | 23117 | 0.025824 | 0.00025135
2012-09-29 06:34AM | 1558018-1 | MVB2 | Rural Short | Equipment Failure | 31 | 208.9677 | 6478 | 0.0072367 | 3.4631e-05
2013-05-11 03:26AM | 1616561-1 | MVB2 | Rural Short | Equipment Failure | 1094 | 189.0055 | 206772 | 0.23099 | 0.0012221
2013-06-19 08:09AM | 1628361-1 | MVC2 | Rural Short | Operatonal Error | 754 | 1.0066 | 759 | 0.00084789 | 0.00084231
2013-01-21 07:36AM | 1586817-1 | MVC2 | Rural Short | Equipment Failure | 122 | 55.4836 | 6769 | 0.0075618 | 0.00013629
2013-05-18 10:38AM | 1618449-1 | MVC2 | Rural Short | Third Party Impacts | 122 | 83.9836 | 10246 | 0.011446 | 0.00013629
2013-06-19 08:09AM | 1628361-1 | MVD2 | Rural Short | Operatonal Error | 1504 | 1.0066 | 1514 | 0.0016913 | 0.0016801
2013-02-21 12:24PM | 1596104-1 | MVD2 | Rural Short | Other | 8 | 126 | 1008 | 0.0011261 | 8.937e-06
2012-11-16 09:01AM | 1570286-1 | MVD2 | Rural Short | Other | 14 | 141 | 1974 | 0.0022052 | 1.564e-05
2012-08-20 08:38AM | 1547351-1 | MVD2 | Rural Short | Other | 1 | 92 | 92 | 0.00010278 | 1.1171e-06
2013-06-25 06:54AM | 1627726-1 | MVD2 | Rural Short | Weather | 72 | 503 | 36216 | 0.040458 | 8.0433e-05
2012-08-24 05:26PM | 1549322-1 | MVD2 | Rural Short | Other | 2 | 206.5 | 413 | 0.00046137 | 2.2342e-06
2012-09-08 03:59PM | 1553195-1 | MVD2 | Rural Short | Weather | 2 | 256 | 512 | 0.00057197 | 2.2342e-06
2012-10-08 06:37AM | 1559645-1 | MVD2 | Rural Short | Equipment Failure | 36 | 154.4444 | 5560 | 0.0062112 | 4.0216e-05
2012-09-15 07:27PM | 1554842-1 | MVD2 | Rural Short | Other | 18 | 123 | 2214 | 0.0024733 | 2.0108e-05
2012-09-02 11:28AM | 1551282-1 | MVD2 | Rural Short | Other | 32 | 79 | 2528 | 0.0028241 | 3.5748e-05
2012-12-25 03:48PM | 1580536-1 | MVD2 | Rural Short | Weather | 1469 | 39 | 57291 | 0.064001 | 0.001641
2012-12-11 10:51AM | 1577024-1 | MVD2 | Rural Short | Equipment Failure | 1 | 124 | 124 | 0.00013852 | 1.1171e-06
2013-06-19 08:09AM | 1628361-1 | MVE2 | Rural Short | Operatonal Error | 466 | 1.0064 | 469 | 0.00052393 | 0.00052058
2013-05-06 09:43AM | 1615091-1 | MVE2 | Rural Short | Other | 1 | 83 | 83 | 9.2721e-05 | 1.1171e-06
2013-06-20 12:40PM | 1626622-1 | MVE2 | Rural Short | Other | 1 | 162 | 162 | 0.00018097 | 1.1171e-06
2012-10-16 02:01PM | 1562212-1 | MVE2 | Rural Short | Other | 1 | 108 | 108 | 0.00012065 | 1.1171e-06
2012-12-29 08:02AM | 1581270-1 | MVE2 | Rural Short | Other | 2 | 56.5 | 113 | 0.00012623 | 2.2342e-06
2013-03-22 07:24PM | 1605684-1 | MVE2 | Rural Short | Other | 2 | 169 | 338 | 0.00037759 | 2.2342e-06
2013-03-30 07:03AM | 1607075-1 | MVE2 | Rural Short | Other | 2 | 74 | 148 | 0.00016533 | 2.2342e-06
2013-05-27 06:53AM | 1620435-1 | MVE2 | Rural Short | Other | 2 | 98 | 196 | 0.00021896 | 2.2342e-06
2013-05-28 07:41AM | 1620891-1 | MVE2 | Rural Short | Other | 2 | 77 | 154 | 0.00017204 | 2.2342e-06
2012-07-03 07:54AM | 1535064-1 | MVE2 | Rural Short | Animals | 1 | 138 | 138 | 0.00015416 | 1.1171e-06
2013-06-19 08:09AM | 1628361-1 | MVF2 | Rural Short | Operatonal Error | 1041 | 1.0067 | 1048 | 0.0011707 | 0.0011629
2013-02-01 05:26PM | 1590857-1 | MVF2 | Rural Short | Weather | 1 | 70 | 70 | 7.8198e-05 | 1.1171e-06
2012-12-25 11:08AM | 1580453-1 | MVF2 | Rural Short | Weather | 1 | 109 | 109 | 0.00012177 | 1.1171e-06
2012-12-25 01:10PM | 1580465-1 | MVF2 | Rural Short | Weather | 1 | 340 | 340 | 0.00037982 | 1.1171e-06
2012-08-22 03:47PM | 1548171-1 | MVF2 | Rural Short | Other | 1 | 81 | 81 | 9.0487e-05 | 1.1171e-06
2012-09-08 06:49AM | 1553072-1 | MVF2 | Rural Short | Equipment Failure | 16 | 248.25 | 3972 | 0.0044372 | 1.7874e-05
2012-07-02 03:45PM | 1534937-1 | MVF2 | Rural Short | Equipment Failure | 5 | 42.8 | 214 | 0.00023906 | 5.5856e-06
2013-05-15 10:17AM | 1617435-1 | MVF2 | Rural Short | Animals | 5 | 169 | 845 | 0.00094397 | 5.5856e-06
2012-12-25 12:56PM | 1580464-1 | MVF2 | Rural Short | Weather | 1 | 2 | 2 | 2.2342e-06 | 1.1171e-06
2012-08-13 08:24AM | 1545310-1 | MVF2 | Rural Short | Other | 88 | 336.8636 | 29644 | 0.033116 | 9.8307e-05
2012-12-28 11:56AM | 1581146-1 | MVF2 | Rural Short | Equipment Failure | 1 | 129 | 129 | 0.00014411 | 1.1171e-06
2013-01-17 05:25PM | 1585775-1 | MVF2 | Rural Short | Other | 22 | 180.8182 | 3978 | 0.0044439 | 2.4577e-05
2013-02-01 01:46PM | 1590671-1 | MVF2 | Rural Short | Other | 1 | 79 | 79 | 8.8252e-05 | 1.1171e-06
2012-08-06 03:34PM | 1543235-1 | MVF2 | Rural Short | Other | 4 | 102.75 | 411 | 0.00045914 | 4.4685e-06
2012-09-06 07:21AM | 1552211-1 | MVF2 | Rural Short | Other | 1 | 325 | 325 | 0.00036306 | 1.1171e-06
2012-10-16 06:37AM | 1562011-1 | MVF2 | Rural Short | Animals | 1 | 123 | 123 | 0.00013741 | 1.1171e-06
2013-02-15 06:37PM | 1594795-1 | MVF2 | Rural Short | Equipment Failure | 33 | 184.5758 | 6091 | 0.0068044 | 3.6865e-05
2013-05-21 09:44PM | 1619184-1 | MVF2 | Rural Short | Other | 5 | 144 | 720 | 0.00080433 | 5.5856e-06
2012-08-10 07:16AM | 1544356-1 | MVF2 | Rural Short | Vegetation | 16 | 335.875 | 5374 | 0.0060034 | 1.7874e-05
2013-02-11 11:01AM | 1593486-1 | MVF2 | Rural Short | Vegetation | 25 | 263 | 6575 | 0.0073451 | 2.7928e-05
2012-10-18 10:37AM | 1562758-1 | MVF2 | Rural Short | Other | 1 | 56 | 56 | 6.2559e-05 | 1.1171e-06
2013-02-14 10:54PM | 1594557-1 | MVF2 | Rural Short | Equipment Failure | 1 | 94 | 94 | 0.00010501 | 1.1171e-06
2013-06-19 08:09AM | 1628361-1 | MVG2 | Urban | Operatonal Error | 12 | 1 | 12 | 1.3405e-05 | 1.3405e-05
2013-06-19 08:09AM | 1628361-1 | MVH2 | Rural Short | Operatonal Error | 1507 | 1.0066 | 1517 | 0.0016947 | 0.0016835
2013-01-22 06:24PM | 1587475-1 | MVH2 | Rural Short | Weather | 1 | 160 | 160 | 0.00017874 | 1.1171e-06
2013-01-27 07:23AM | 1589046-1 | MVH2 | Rural Short | Equipment Failure | 45 | 383 | 17235 | 0.019254 | 5.027e-05
2013-03-02 06:35PM | 1600242-1 | MVH2 | Rural Short | Equipment Failure | 142 | 580.9155 | 82490 | 0.092151 | 0.00015863
2013-03-03 10:14PM | 1600365-1 | MVH2 | Rural Short | Equipment Failure | 20 | 117 | 2340 | 0.0026141 | 2.2342e-05
2012-08-10 04:25PM | 1544871-1 | MVH2 | Rural Short | Operatonal Error | 6 | 150.5 | 903 | 0.0010088 | 6.7027e-06
2012-12-20 11:58AM | 1579369-1 | MVH2 | Rural Short | Other | 60 | 64 | 3840 | 0.0042897 | 6.7027e-05
2013-02-27 06:28PM | 1599148-1 | MVH2 | Rural Short | Other | 33 | 112 | 3696 | 0.0041289 | 3.6865e-05
2013-01-22 07:22PM | 1587499-1 | MVH2 | Rural Short | Equipment Failure | 1 | 805 | 805 | 0.00089928 | 1.1171e-06
2013-01-24 07:24PM | 1588080-1 | MVH2 | Rural Short | Equipment Failure | 1 | 203 | 203 | 0.00022678 | 1.1171e-06
2012-07-03 05:42PM | 1535337-1 | MVH2 | Rural Short | Equipment Failure | 83 | 205.7952 | 17081 | 0.019082 | 9.2721e-05
2012-07-09 12:06PM | 1536604-1 | MVH2 | Rural Short | Other | 37 | 53.9459 | 1996 | 0.0022298 | 4.1333e-05
2013-01-22 06:03PM | 1587465-1 | MVH2 | Rural Short | Weather | 1 | 151 | 151 | 0.00016869 | 1.1171e-06
2013-01-30 04:29PM | 1590107-1 | MVH2 | Rural Short | Equipment Failure | 9 | 48 | 432 | 0.0004826 | 1.0054e-05
2012-08-06 07:31AM | 1543051-1 | MVH2 | Rural Short | Other | 12 | 120 | 1440 | 0.0016087 | 1.3405e-05
2013-01-22 06:06PM | 1587467-1 | MVH2 | Rural Short | Weather | 1 | 179 | 179 | 0.00019996 | 1.1171e-06
2012-11-25 05:41PM | 1572527-1 | MVH2 | Rural Short | Third Party Impacts | 156 | 33.7628 | 5267 | 0.0058839 | 0.00017427
2013-03-16 07:53PM | 1604047-1 | MVH2 | Rural Short | Other | 156 | 91 | 14196 | 0.015859 | 0.00017427
2013-06-24 11:29PM | 1627642-1 | MVH2 | Rural Short | Weather | 182 | 85.7473 | 15606 | 0.017434 | 0.00020332
2012-07-18 05:29PM | 1538662-1 | MVH2 | Rural Short | Equipment Failure | 1310 | 2.216 | 2903 | 0.003243 | 0.0014634
2012-08-05 01:06AM | 1542955-1 | MVH2 | Rural Short | Animals | 1459 | 41.4503 | 60476 | 0.067559 | 0.0016299
2012-10-14 07:49AM | 1561554-1 | MVH2 | Rural Short | Equipment Failure | 1544 | 84.068 | 129801 | 0.145 | 0.0017248
2013-01-03 07:53PM | 1582182-1 | MVH2 | Rural Short | Animals | 1485 | 50.4828 | 74967 | 0.083747 | 0.0016589
2012-11-16 09:49AM | 1570299-1 | MVH2 | Rural Short | Other | 1 | 95 | 95 | 0.00010613 | 1.1171e-06
2012-09-28 06:43AM | 1557672-1 | MYE2 | Rural Short | Equipment Failure | 1 | 69 | 69 | 7.7081e-05 | 1.1171e-06
2013-02-15 06:52AM | 1594578-1 | MYK2 | Urban | Equipment Failure | 20 | 474.5 | 9490 | 0.010601 | 2.2342e-05
2012-07-15 11:42AM | 1537883-1 | MYM2 | Urban | Other | 45 | 68.6889 | 3091 | 0.003453 | 5.027e-05
2012-11-29 11:16AM | 1573823-1 | MYM2 | Urban | Other | 10 | 61.7 | 617 | 0.00068926 | 1.1171e-05
2012-10-29 03:23PM | 1565485-1 | MYM2 | Urban | Third Party Impacts | 42 | 150.8571 | 6336 | 0.0070781 | 4.6919e-05
2013-04-26 11:04AM | 1613090-1 | MYQ2 | Urban | Vegetation | 65 | 17 | 1105 | 0.0012344 | 7.2613e-05
2012-10-03 11:40PM | 1558748-1 | MYQ2 | Urban | Other | 56 | 99.2857 | 5560 | 0.0062112 | 6.2559e-05
2012-12-20 03:41PM | 1579482-1 | MYQ2 | Urban | Other | 32 | 88 | 2816 | 0.0031458 | 3.5748e-05
2012-08-16 12:24PM | 1546287-1 | MYQ2 | Urban | Equipment Failure | 1 | 174 | 174 | 0.00019438 | 1.1171e-06
2013-02-22 05:06PM | 1596521-1 | MR2206 | Urban | Third Party Impacts | 66 | 63.9697 | 4222 | 0.0047165 | 7.373e-05
2013-02-22 02:12PM | 1596493-1 | MR2206 | Urban | Equipment Failure | 66 | 117.2424 | 7738 | 0.0086443 | 7.373e-05
2012-09-20 11:47PM | 1556050-1 | MR2206 | Urban | Third Party Impacts | 1 | 631 | 631 | 0.0007049 | 1.1171e-06
2012-09-19 01:59AM | 1555581-1 | MR2224 | Urban | Third Party Impacts | 4 | 100 | 400 | 0.00044685 | 4.4685e-06
2013-01-27 10:03AM | 1589088-1 | MR2224 | Urban | Other | 4 | 157 | 628 | 0.00070155 | 4.4685e-06
2013-01-14 01:18PM | 1584768-1 | MR2224 | Urban | Weather | 4 | 86 | 344 | 0.00038429 | 4.4685e-06
2013-01-14 03:25PM | 1584828-1 | MR2224 | Urban | Other | 1 | 117 | 117 | 0.0001307 | 1.1171e-06
2012-09-19 04:22AM | 1555587-1 | MR2224 | Urban | Other | 12 | 251 | 3012 | 0.0033648 | 1.3405e-05
2012-09-18 05:11PM | 1555496-1 | MR2224 | Urban | Other | 2 | 307 | 614 | 0.00068591 | 2.2342e-06
2013-06-28 10:32PM | 1629172-1 | MR2224 | Urban | Equipment Failure | 10 | 161.4 | 1614 | 0.001803 | 1.1171e-05
2012-07-06 04:47AM | 1535991-1 | MR2224 | Urban | Third Party Impacts | 278 | 71.0108 | 19741 | 0.022053 | 0.00031056
2013-03-13 05:16AM | 1603012-1 | MR2224 | Urban | Vegetation | 181 | 80.8785 | 14639 | 0.016354 | 0.0002022
2013-04-16 12:33PM | 1610721-1 | MR2224 | Urban | Other | 823 | 3.4496 | 2839 | 0.0031715 | 0.00091939
2012-09-19 05:06AM | 1555589-1 | MR2224 | Urban | Other | 1 | 631 | 631 | 0.0007049 | 1.1171e-06
2013-01-13 06:21PM | 1584481-1 | MR2225 | Urban | Weather | 12 | 92.75 | 1113 | 0.0012434 | 1.3405e-05
2012-07-04 10:51PM | 1535742-1 | MR2232 | Urban | Equipment Failure | 11 | 119 | 1309 | 0.0014623 | 1.2288e-05
2013-01-28 12:42PM | 1589260-1 | MR2232 | Urban | Equipment Failure | 1 | 310 | 310 | 0.00034631 | 1.1171e-06
2012-09-18 04:07PM | 1555469-1 | MR2232 | Urban | Weather | 20 | 169.95 | 3399 | 0.0037971 | 2.2342e-05
2012-07-26 06:17PM | 1540678-1 | MR2232 | Urban | Equipment Failure | 6 | 61.5 | 369 | 0.00041222 | 6.7027e-06
2013-05-16 09:10AM | 1617754-1 | MR2232 | Urban | Equipment Failure | 1 | 193 | 193 | 0.0002156 | 1.1171e-06
2012-08-06 09:30AM | 1543085-1 | MR2232 | Urban | Vegetation | 1 | 130 | 130 | 0.00014523 | 1.1171e-06
2013-02-09 11:56PM | 1593145-1 | MR2232 | Urban | Other | 1 | 532 | 532 | 0.00059431 | 1.1171e-06
2012-09-27 02:46PM | 1557557-1 | MR2232 | Urban | Vegetation | 6 | 121.1667 | 727 | 0.00081215 | 6.7027e-06
2012-12-24 05:12PM | 1580190-1 | MR2232 | Urban | Other | 139 | 73.9568 | 10280 | 0.011484 | 0.00015528
2012-08-10 05:17PM | 1544911-1 | MR2232 | Urban | Weather | 635 | 408.5685 | 259441 | 0.28983 | 0.00070937
2012-08-10 06:34PM | 1544961-1 | MR2232 | Urban | Weather | 286 | 0.94755 | 271 | 0.00030274 | 0.0003195
2012-08-17 12:34PM | 1546658-1 | MR2232 | Urban | Weather | 635 | 250.9165 | 159332 | 0.17799 | 0.00070937
2012-12-09 01:01PM | 1576618-1 | MR2232 | Urban | Vegetation | 636 | 99 | 62964 | 0.070338 | 0.00071049
2013-01-08 09:57PM | 1583424-1 | MR2232 | Urban | Equipment Failure | 636 | 199.9843 | 127190 | 0.14209 | 0.00071049
2013-03-26 06:17AM | 1606236-1 | MR2232 | Urban | Vegetation | 638 | 148.9561 | 95034 | 0.10616 | 0.00071272
2013-05-19 09:26PM | 1618640-1 | MR2232 | Urban | Other | 316 | 76.6456 | 24220 | 0.027057 | 0.00035301
2013-05-20 05:59PM | 1618836-1 | MR2232 | Urban | Other | 316 | 81.3703 | 25713 | 0.028725 | 0.00035301
2012-09-18 03:31PM | 1555453-1 | MR2232 | Urban | Weather | 1388 | 33.7666 | 46868 | 0.052357 | 0.0015506
2013-01-12 03:42PM | 1584284-1 | MR2232 | Urban | Weather | 583 | 62.6158 | 36505 | 0.04078 | 0.00065128
2013-04-16 09:47AM | 1610627-1 | MR2232 | Urban | Vegetation | 1222 | 184.7021 | 225706 | 0.25214 | 0.0013651
2013-01-29 08:02AM | 1589496-1 | MR2292 | Urban | Equipment Failure | 907 | 64.9603 | 58919 | 0.06582 | 0.0010132
2013-04-12 12:59PM | 1609949-1 | MR2292 | Urban | Equipment Failure | 842 | 31 | 26102 | 0.029159 | 0.00094062
2013-01-01 12:06PM | 1581611-1 | MR2298 | Urban | Other | 12 | 340.9167 | 4091 | 0.0045701 | 1.3405e-05
2012-09-24 06:29PM | 1556751-1 | MR2299 | Urban | Other | 1 | 257 | 257 | 0.0002871 | 1.1171e-06
2013-01-11 03:57PM | 1584163-1 | MR2299 | Urban | Weather | 24 | 75.7083 | 1817 | 0.0020298 | 2.6811e-05
2012-09-03 11:38AM | 1551375-1 | 27027 | Urban | Equipment Failure | 1 | 152 | 152 | 0.0001698 | 1.1171e-06
2013-03-06 01:21PM | 1601327-1 | 27028 | Urban | Operatonal Error | 553 | 4.6492 | 2571 | 0.0028721 | 0.00061777
2013-06-26 03:05PM | 1628398-1 | 27031 | Urban | Equipment Failure | 1 | 194 | 194 | 0.00021672 | 1.1171e-06
2013-06-27 10:10AM | 1628604-1 | 27031 | Urban | Equipment Failure | 1 | 469 | 469 | 0.00052393 | 1.1171e-06
2013-01-29 02:58AM | 1589457-1 | 27031 | Urban | Equipment Failure | 1 | 44 | 44 | 4.9153e-05 | 1.1171e-06
2013-02-25 08:01PM | 1598398-1 | 27031 | Urban | Equipment Failure | 1 | 302 | 302 | 0.00033737 | 1.1171e-06
2013-01-16 06:46AM | 1585507-1 | 27032 | Urban | Equipment Failure | 34 | 71.7941 | 2441 | 0.0027269 | 3.7982e-05
2012-12-24 06:53PM | 1580250-1 | 27036 | Urban | Weather | 436 | 72.0115 | 31397 | 0.035074 | 0.00048706
2012-09-05 02:27PM | 1556153-1 | 27036 | Urban | Third Party Impacts | 413 | 17.0823 | 7055 | 0.0078813 | 0.00046137
2012-08-22 07:10PM | 1548211-1 | 27036 | Urban | Equipment Failure | 1 | 54 | 54 | 6.0324e-05 | 1.1171e-06
2012-09-10 06:39PM | 1553550-1 | 27036 | Urban | Equipment Failure | 1 | 204 | 204 | 0.00022789 | 1.1171e-06
2013-06-19 06:43PM | 1626455-1 | 27039 | Urban | Equipment Failure | 1 | 108 | 108 | 0.00012065 | 1.1171e-06
2013-01-16 07:41AM | 1585297-1 | 27039 | Urban | Equipment Failure | 91 | 170.3077 | 15498 | 0.017313 | 0.00010166
2013-01-17 07:33AM | 1585580-1 | 27039 | Urban | Other | 1411 | 62.4996 | 88187 | 0.098515 | 0.0015763
2012-08-27 04:12PM | 1549804-1 | 27040 | Urban | Other | 1074 | 20.9832 | 22536 | 0.025175 | 0.0011998
2012-10-13 11:45AM | 1561476-1 | 27040 | Urban | Equipment Failure | 1 | 228 | 228 | 0.0002547 | 1.1171e-06
2012-08-25 08:08AM | 1549425-1 | 55167 | Urban | Other | 7 | 242 | 1694 | 0.0018924 | 7.8198e-06
2013-01-18 06:26PM | 1586313-1 | 55167 | Urban | Weather | 19 | 243.6842 | 4630 | 0.0051723 | 2.1225e-05
2012-10-17 01:45AM | 1562347-1 | 55175 | Urban | Other | 16 | 32.375 | 518 | 0.00057867 | 1.7874e-05
2012-09-29 06:59AM | 1558027-1 | 55175 | Urban | Other | 17 | 62.2353 | 1058 | 0.0011819 | 1.8991e-05
2013-03-16 05:51PM | 1604028-1 | 55177 | Urban | Equipment Failure | 32 | 152 | 4864 | 0.0054337 | 3.5748e-05
2012-10-09 04:42PM | 1560136-1 | M390 | Urban | Equipment Failure | 94 | 120.766 | 11352 | 0.012682 | 0.00010501
2013-02-06 08:49PM | 1592297-1 | 20717 | Urban | Equipment Failure | 1 | 711 | 711 | 0.00079427 | 1.1171e-06
2013-03-25 08:30AM | 1605944-1 | 20719 | Urban | Other | 31 | 175.8387 | 5451 | 0.0060894 | 3.4631e-05
2012-09-21 01:01PM | 1556212-1 | 20722 | Urban | Equipment Failure | 33 | 97.8485 | 3229 | 0.0036072 | 3.6865e-05
2013-01-18 06:00PM | 1586284-1 | 20722 | Urban | Equipment Failure | 16 | 230.75 | 3692 | 0.0041244 | 1.7874e-05
2013-05-11 10:08AM | 1616581-1 | 20722 | Urban | Equipment Failure | 12 | 72 | 864 | 0.00096519 | 1.3405e-05
2012-09-21 06:05AM | 1556053-1 | 20722 | Urban | Animals | 1322 | 47.8328 | 63235 | 0.070641 | 0.0014768
2013-02-04 11:50PM | 1591565-1 | 20722 | Urban | Animals | 538 | 82.8401 | 44568 | 0.049788 | 0.00060101
2013-05-06 10:12AM | 1615151-1 | 20725 | Urban | Equipment Failure | 11 | 307.8182 | 3386 | 0.0037826 | 1.2288e-05
2012-11-09 05:51PM | 1568913-1 | 20725 | Urban | Operatonal Error | 94 | 49 | 4606 | 0.0051455 | 0.00010501
2012-09-25 11:59AM | 1556879-1 | 20725 | Urban | Vegetation | 1505 | 31.1256 | 46844 | 0.05233 | 0.0016813
2012-11-08 04:21PM | 1568362-1 | 20725 | Urban | Weather | 1633 | 231.1317 | 377438 | 0.42164 | 0.0018243
2012-10-16 09:24AM | 1562076-1 | 20725 | Urban | Other | 1 | 137 | 137 | 0.00015305 | 1.1171e-06
2012-11-09 02:59AM | 1568612-1 | 20725 | Urban | Other | 1 | 998 | 998 | 0.0011149 | 1.1171e-06
2012-09-05 05:30PM | 1552138-1 | 3105 | Urban | Operatonal Error | 479 | 3 | 1437 | 0.0016053 | 0.0005351
2013-02-09 07:45PM | 1593110-1 | 8675 | Urban | Equipment Failure | 3 | 302 | 906 | 0.0010121 | 3.3514e-06
2013-04-11 11:38AM | 1609559-1 | 8675 | Urban | Equipment Failure | 59 | 47 | 2773 | 0.0030978 | 6.591e-05
2012-08-29 06:41AM | 1550192-1 | 8676 | Urban | Equipment Failure | 1 | 374 | 374 | 0.0004178 | 1.1171e-06
2012-10-16 09:09AM | 1562064-1 | 8677 | Urban | Third Party Impacts | 1 | 209 | 209 | 0.00023348 | 1.1171e-06
2013-05-01 01:37PM | 1614188-1 | 8679 | Urban | Equipment Failure | 10 | 427 | 4270 | 0.0047701 | 1.1171e-05
2013-04-18 08:34AM | 1611193-1 | 8679 | Urban | Other | 12 | 119 | 1428 | 0.0015952 | 1.3405e-05
2013-06-03 01:06PM | 1622572-1 | 8679 | Urban | Equipment Failure | 1 | 276 | 276 | 0.00030833 | 1.1171e-06
2013-06-29 05:03PM | 1629262-1 | 8679 | Urban | Equipment Failure | 6 | 232 | 1392 | 0.001555 | 6.7027e-06
2013-04-18 01:00AM | 1611142-1 | 8679 | Urban | Equipment Failure | 28 | 544 | 15232 | 0.017016 | 3.1279e-05
2013-01-06 06:13PM | 1582739-1 | 8679 | Urban | Weather | 12 | 85.1667 | 1022 | 0.0011417 | 1.3405e-05
2012-09-14 01:31PM | 1554636-1 | 8679 | Urban | Animals | 129 | 129 | 16641 | 0.01859 | 0.00014411
2012-07-31 12:03AM | 1541526-1 | 8679 | Urban | Equipment Failure | 1 | 567 | 567 | 0.00063341 | 1.1171e-06
2012-11-22 04:15PM | 1571965-1 | 8679 | Urban | Other | 1 | 98 | 98 | 0.00010948 | 1.1171e-06
2012-08-04 06:40AM | 1542851-1 | 8680 | Urban | Third Party Impacts | 9 | 315.7778 | 2842 | 0.0031749 | 1.0054e-05
2012-09-17 07:08PM | 1555218-1 | RWB2 | Rural Short | Equipment Failure | 8 | 87 | 696 | 0.00077752 | 8.937e-06
2013-04-22 07:30PM | 1612230-1 | RWB2 | Rural Short | Equipment Failure | 1 | 101 | 101 | 0.00011283 | 1.1171e-06
2012-07-16 08:33AM | 1537976-1 | RWB2 | Rural Short | Other | 1 | 107 | 107 | 0.00011953 | 1.1171e-06
2012-08-17 09:09AM | 1546483-1 | RWB2 | Rural Short | Other | 26 | 17.9615 | 467 | 0.0005217 | 2.9045e-05
2013-03-19 03:33PM | 1604615-1 | RWB2 | Rural Short | Equipment Failure | 1 | 115 | 115 | 0.00012847 | 1.1171e-06
2013-02-01 07:46PM | 1590903-1 | RWB2 | Rural Short | Weather | 22 | 173 | 3806 | 0.0042518 | 2.4577e-05
2013-02-27 11:05PM | 1599189-1 | RWB2 | Rural Short | Other | 1 | 117 | 117 | 0.0001307 | 1.1171e-06
2013-02-01 03:31PM | 1590792-1 | RWC2 | Rural Short | Weather | 4 | 252 | 1008 | 0.0011261 | 4.4685e-06
2013-01-19 08:25AM | 1586566-1 | RWC2 | Rural Short | Other | 2 | 357 | 714 | 0.00079762 | 2.2342e-06
2013-02-25 06:43PM | 1598376-1 | RWC2 | Rural Short | Other | 4 | 84 | 336 | 0.00037535 | 4.4685e-06
2013-02-03 04:53PM | 1591175-1 | RWC2 | Rural Short | Other | 1 | 120 | 120 | 0.00013405 | 1.1171e-06
2013-02-04 10:31AM | 1591324-1 | RWC2 | Rural Short | Equipment Failure | 1 | 408 | 408 | 0.00045578 | 1.1171e-06
2013-01-18 04:55PM | 1586233-1 | RWC2 | Rural Short | Vegetation | 7 | 327.8571 | 2295 | 0.0025638 | 7.8198e-06
2013-04-29 07:47AM | 1613544-1 | RWC2 | Rural Short | Operatonal Error | 125 | 7 | 875 | 0.00097748 | 0.00013964
2013-02-25 11:33AM | 1598002-1 | RWD2 | Rural Short | Other | 6 | 296 | 1776 | 0.001984 | 6.7027e-06
2013-01-12 06:09PM | 1584314-1 | RWD2 | Rural Short | Equipment Failure | 1 | 80 | 80 | 8.937e-05 | 1.1171e-06
2012-12-25 12:06AM | 1580382-1 | RWD2 | Rural Short | Equipment Failure | 1 | 612 | 612 | 0.00068368 | 1.1171e-06
2012-11-11 03:52PM | 1569086-1 | RWD2 | Rural Short | Third Party Impacts | 3 | 232 | 696 | 0.00077752 | 3.3514e-06
2012-09-15 08:07PM | 1554845-1 | RWD2 | Rural Short | Other | 1 | 107 | 107 | 0.00011953 | 1.1171e-06
2013-01-14 10:58AM | 1584699-1 | RWD2 | Rural Short | Equipment Failure | 4 | 271.5 | 1086 | 0.0012132 | 4.4685e-06
2012-12-25 02:39PM | 1580492-1 | RWD2 | Rural Short | Weather | 3 | 95 | 285 | 0.00031838 | 3.3514e-06
2012-12-24 01:28PM | 1580147-1 | RWD2 | Rural Short | Weather | 2 | 204 | 408 | 0.00045578 | 2.2342e-06
2013-03-17 11:12AM | 1604090-1 | RWD2 | Rural Short | Other | 12 | 52 | 624 | 0.00069708 | 1.3405e-05
2013-01-22 06:05PM | 1587466-1 | RWD2 | Rural Short | Weather | 2 | 255 | 510 | 0.00056973 | 2.2342e-06
2013-01-22 07:31PM | 1587501-1 | RWD2 | Rural Short | Weather | 1 | 167 | 167 | 0.00018656 | 1.1171e-06
2012-12-23 05:17PM | 1579961-1 | RWD2 | Rural Short | Weather | 2 | 1013 | 2026 | 0.0022633 | 2.2342e-06
2012-12-27 01:21PM | 1580894-1 | RWD2 | Rural Short | Other | 2 | 83.5 | 167 | 0.00018656 | 2.2342e-06
2013-02-10 06:32PM | 1593285-1 | RWD2 | Rural Short | Weather | 1 | 178 | 178 | 0.00019885 | 1.1171e-06
2013-02-05 10:42PM | 1591884-1 | RWD2 | Rural Short | Animals | 15 | 86 | 1290 | 0.0014411 | 1.6757e-05
2012-10-04 05:14PM | 1559024-1 | RWD2 | Rural Short | Other | 4 | 139 | 556 | 0.00062112 | 4.4685e-06
2012-12-24 07:55PM | 1580306-1 | RWD2 | Rural Short | Weather | 267 | 222.8839 | 59510 | 0.06648 | 0.00029827
2012-12-23 09:07PM | 1580022-1 | RWD2 | Rural Short | Weather | 138 | 4 | 552 | 0.00061665 | 0.00015416
2012-07-24 04:27PM | 1540097-1 | RWD2 | Rural Short | Equipment Failure | 29 | 42.3448 | 1228 | 0.0013718 | 3.2396e-05
2012-12-24 07:23AM | 1580044-1 | RWD2 | Rural Short | Weather | 6 | 509.1667 | 3055 | 0.0034128 | 6.7027e-06
2013-01-08 04:31PM | 1583294-1 | RWD2 | Rural Short | Vegetation | 18 | 124 | 2232 | 0.0024934 | 2.0108e-05
2013-01-05 09:40AM | 1582548-1 | RWD2 | Rural Short | Vegetation | 552 | 134.5688 | 74282 | 0.082982 | 0.00061665
2012-09-05 02:27PM | 1556153-1 | M390 | Urban | Third Party Impacts | 1065 | 17.0732 | 18183 | 0.020313 | 0.0011897
2012-12-15 12:43AM | 1578101-1 | NN1214 | Rural Short | Equipment Failure | 302 | 66.7748 | 20166 | 0.022528 | 0.00033737
2012-12-05 12:34PM | 1575750-1 | NN1233 | Urban | Vegetation | 5 | 81 | 405 | 0.00045243 | 5.5856e-06
2013-01-07 03:39PM | 1582994-1 | NN1233 | Urban | Equipment Failure | 1 | 106 | 106 | 0.00011841 | 1.1171e-06
2013-04-20 11:43AM | 1611736-1 | NN1233 | Urban | Weather | 258 | 89 | 22962 | 0.025651 | 0.00028822
2013-05-22 06:55PM | 1619484-1 | NN1233 | Urban | Equipment Failure | 259 | 110.1699 | 28534 | 0.031876 | 0.00028933
2013-01-31 05:37PM | 1590416-1 | NN1233 | Urban | Operatonal Error | 698 | 2 | 1396 | 0.0015595 | 0.00077975
2013-01-29 06:20AM | 1589477-1 | NN1255 | Urban | Equipment Failure | 43 | 72.814 | 3131 | 0.0034977 | 4.8036e-05
2013-01-29 09:37AM | 1589546-1 | NN1255 | Urban | Equipment Failure | 9 | 92 | 828 | 0.00092498 | 1.0054e-05
2013-01-31 04:06PM | 1590374-1 | NN1255 | Urban | Equipment Failure | 9 | 132 | 1188 | 0.0013271 | 1.0054e-05
2013-01-04 03:28PM | 1582375-1 | NN1255 | Urban | Other | 1074 | 97.4097 | 104618 | 0.11687 | 0.0011998
2013-01-08 06:44PM | 1583359-1 | NN1277 | Urban | Other | 42 | 77 | 3234 | 0.0036128 | 4.6919e-05
2013-01-19 06:15AM | 1586546-1 | NN1277 | Urban | Weather | 10 | 254.7 | 2547 | 0.0028453 | 1.1171e-05
2013-01-21 08:11AM | 1586825-1 | NN1277 | Urban | Other | 10 | 42 | 420 | 0.00046919 | 1.1171e-05
2013-02-20 12:36PM | 1595772-1 | NN1277 | Urban | Third Party Impacts | 42 | 23.1905 | 974 | 0.0010881 | 4.6919e-05
2012-07-15 02:50PM | 1537898-1 | R216 | Rural Short | Vegetation | 5 | 62 | 310 | 0.00034631 | 5.5856e-06
2012-10-03 08:58AM | 1558508-1 | R216 | Rural Short | Other | 1 | 102 | 102 | 0.00011395 | 1.1171e-06
2012-09-05 02:27PM | 1556153-1 | R216 | Rural Short | Third Party Impacts | 1166 | 17.0849 | 19921 | 0.022254 | 0.0013026
2013-01-10 02:39PM | 1583861-1 | 46395 | Urban | Third Party Impacts | 33 | 100.4545 | 3315 | 0.0037033 | 3.6865e-05
2012-07-11 03:39PM | 1537137-1 | 46395 | Urban | Animals | 1225 | 0.49959 | 612 | 0.00068368 | 0.0013685
2012-12-05 04:25PM | 1575889-1 | 46395 | Urban | Equipment Failure | 1 | 191 | 191 | 0.00021337 | 1.1171e-06
2012-07-12 07:26PM | 1537468-1 | L533 | Urban | Third Party Impacts | 250 | 66.476 | 16619 | 0.018565 | 0.00027928
2013-06-21 01:15AM | 1626793-1 | L534 | Urban | Equipment Failure | 75 | 179 | 13425 | 0.014997 | 8.3784e-05
2013-06-04 10:30AM | 1622800-1 | L534 | Urban | Operatonal Error | 1 | 385 | 385 | 0.00043009 | 1.1171e-06
2013-06-05 05:44AM | 1623054-1 | L537 | Urban | Equipment Failure | 30 | 229 | 6870 | 0.0076746 | 3.3514e-05
2012-07-25 07:25AM | 1540152-1 | L537 | Urban | Third Party Impacts | 37 | 24.9189 | 922 | 0.00103 | 4.1333e-05
2013-01-18 08:40AM | 1585865-1 | 10286 | Rural Short | Vegetation | 443 | 124 | 54932 | 0.061366 | 0.00049488
2013-02-19 06:54PM | 1595627-1 | 27446 | Rural Short | Other | 42 | 123 | 5166 | 0.005771 | 4.6919e-05
2013-05-11 10:17AM | 1616585-1 | 27446 | Rural Short | Other | 24 | 15 | 360 | 0.00040216 | 2.6811e-05
2013-02-12 01:29PM | 1593843-1 | 27446 | Rural Short | Other | 1 | 77 | 77 | 8.6018e-05 | 1.1171e-06
2012-10-22 06:16AM | 1563469-1 | 27447 | Urban | Animals | 514 | 32.465 | 16687 | 0.018641 | 0.0005742
2013-02-13 08:15AM | 1594037-1 | 27454 | Rural Short | Equipment Failure | 5 | 474 | 2370 | 0.0026476 | 5.5856e-06
2013-03-26 04:11PM | 1606435-1 | 27454 | Rural Short | Other | 5 | 165 | 825 | 0.00092162 | 5.5856e-06
2012-09-04 11:15AM | 1551684-1 | 27454 | Rural Short | Equipment Failure | 1 | 70 | 70 | 7.8198e-05 | 1.1171e-06
2013-02-02 08:52AM | 1590974-1 | 27454 | Rural Short | Weather | 5 | 220 | 1100 | 0.0012288 | 5.5856e-06
2013-02-27 06:02PM | 1599184-1 | 27454 | Rural Short | Vegetation | 7 | 37.5714 | 263 | 0.0002938 | 7.8198e-06
2013-03-22 05:21PM | 1605589-1 | 27454 | Rural Short | Vegetation | 294 | 155.8265 | 45813 | 0.051179 | 0.00032843
2013-04-16 12:59PM | 1610726-1 | 27454 | Rural Short | Weather | 2 | 245 | 490 | 0.00054739 | 2.2342e-06
2012-10-05 03:01PM | 1559338-1 | 27454 | Rural Short | Other | 1 | 571 | 571 | 0.00063788 | 1.1171e-06
2012-12-12 08:15AM | 1579351-1 | 27454 | Rural Short | Equipment Failure | 13 | 130 | 1690 | 0.0018879 | 1.4523e-05
2012-09-02 07:24AM | 1551233-1 | 27454 | Rural Short | Other | 7 | 140 | 980 | 0.0010948 | 7.8198e-06
2013-04-22 09:59PM | 1612239-1 | 8734 | Urban | Equipment Failure | 52 | 90 | 4680 | 0.0052281 | 5.809e-05
2013-05-17 07:56PM | 1618394-1 | 8734 | Urban | Equipment Failure | 52 | 140 | 7280 | 0.0081326 | 5.809e-05
2012-08-16 01:02PM | 1546299-1 | 8734 | Urban | Other | 1 | 301 | 301 | 0.00033625 | 1.1171e-06
2012-08-10 03:57PM | 1544846-1 | 8735 | Urban | Weather | 556 | 70.6331 | 39272 | 0.043872 | 0.00062112
2012-10-16 02:04AM | 1561997-1 | 8735 | Urban | Other | 556 | 96.9065 | 53880 | 0.06019 | 0.00062112
2012-07-01 07:39PM | 1534680-1 | 8737 | Urban | Equipment Failure | 59 | 54.0678 | 3190 | 0.0035636 | 6.591e-05
2012-07-01 09:20PM | 1534688-1 | 8737 | Urban | Equipment Failure | 44 | 265.5455 | 11684 | 0.013052 | 4.9153e-05
2012-11-26 12:08AM | 1572606-1 | 8737 | Urban | Equipment Failure | 66 | 50.3333 | 3322 | 0.0037111 | 7.373e-05
2012-10-13 08:55AM | 1561443-1 | 8737 | Urban | Equipment Failure | 1 | 696 | 696 | 0.00077752 | 1.1171e-06
2012-11-09 06:41PM | 1568921-1 | 8738 | Urban | Equipment Failure | 23 | 302 | 6946 | 0.0077595 | 2.5694e-05
2012-09-05 03:53PM | 1552108-1 | 8738 | Urban | Other | 65 | 35 | 2275 | 0.0025414 | 7.2613e-05
2012-11-13 12:52AM | 1569397-1 | 8738 | Urban | Equipment Failure | 1276 | 6 | 7656 | 0.0085527 | 0.0014254
2013-02-19 03:23PM | 1595507-1 | 8738 | Urban | Vegetation | 1278 | 53.4577 | 68319 | 0.076321 | 0.0014277
2013-02-27 04:16PM | 1599123-1 | 8738 | Urban | Operatonal Error | 14 | 109 | 1526 | 0.0017047 | 1.564e-05
2013-02-28 07:27PM | 1599448-1 | 8741 | Urban | Equipment Failure | 403 | 303.1563 | 122172 | 0.13648 | 0.0004502
2013-01-05 06:48AM | 1582530-1 | 8743 | Urban | Vegetation | 15 | 101 | 1515 | 0.0016924 | 1.6757e-05
2012-12-08 03:58AM | 1576512-1 | 8743 | Urban | Other | 744 | 105.6022 | 78568 | 0.08777 | 0.00083114
2012-12-08 10:41AM | 1576540-1 | 8743 | Urban | Vegetation | 744 | 0.9328 | 694 | 0.00077528 | 0.00083114
2013-05-27 10:02PM | 1620839-1 | 8743 | Urban | Equipment Failure | 743 | 93.0135 | 69109 | 0.077203 | 0.00083002
2013-02-14 09:56AM | 1594461-1 | NG1210 | Rural Short | Equipment Failure | 2 | 544 | 1088 | 0.0012154 | 2.2342e-06
2013-05-05 08:12AM | 1614972-1 | NG1210 | Rural Short | Animals | 12 | 88 | 1056 | 0.0011797 | 1.3405e-05
2013-03-12 09:59AM | 1602788-1 | NG1210 | Rural Short | Other | 1 | 176 | 176 | 0.00019661 | 1.1171e-06
2013-06-28 08:00AM | 1631409-1 | NG1210 | Rural Short | Operatonal Error | 20 | 120 | 2400 | 0.0026811 | 2.2342e-05
2013-04-09 12:46PM | 1608884-1 | NG1210 | Rural Short | Other | 6 | 211 | 1266 | 0.0014143 | 6.7027e-06
2013-05-16 03:54PM | 1617987-1 | NG1210 | Rural Short | Third Party Impacts | 233 | 33 | 7689 | 0.0085895 | 0.00026029
2013-06-17 09:45PM | 1625911-1 | NG1210 | Rural Short | Other | 233 | 0.98283 | 229 | 0.00025582 | 0.00026029
2012-07-11 08:31AM | 1536970-1 | NG1210 | Rural Short | Equipment Failure | 5 | 101.4 | 507 | 0.00056638 | 5.5856e-06
2013-02-01 05:06PM | 1590847-1 | NG1247 | Urban | Weather | 67 | 127 | 8509 | 0.0095056 | 7.4847e-05
2012-12-24 10:08PM | 1580368-1 | NG1247 | Urban | Vegetation | 7 | 161.5714 | 1131 | 0.0012635 | 7.8198e-06
2012-12-24 05:24PM | 1580202-1 | NG1247 | Urban | Weather | 872 | 43.4163 | 37859 | 0.042293 | 0.00097413
2013-01-18 05:04PM | 1586241-1 | NG1262 | Urban | Equipment Failure | 11 | 246 | 2706 | 0.0030229 | 1.2288e-05
2013-06-11 05:52AM | 1624177-1 | NG1262 | Urban | Third Party Impacts | 1 | 443 | 443 | 0.00049488 | 1.1171e-06
2013-03-14 03:31PM | 1603494-1 | NG1262 | Urban | Other | 40 | 149 | 5960 | 0.006658 | 4.4685e-05
2012-10-04 02:05PM | 1558932-1 | NG1262 | Urban | Equipment Failure | 15 | 251 | 3765 | 0.004206 | 1.6757e-05
2013-01-03 11:21AM | 1581994-1 | NG1299 | Rural Short | Third Party Impacts | 4 | 25 | 100 | 0.00011171 | 4.4685e-06
2012-11-06 02:07AM | 1567385-1 | NG1299 | Rural Short | Other | 3 | 345.6667 | 1037 | 0.0011585 | 3.3514e-06
2013-05-28 12:19PM | 1620978-1 | NG1299 | Rural Short | Third Party Impacts | 4 | 58.25 | 233 | 0.00026029 | 4.4685e-06
2013-03-08 12:34PM | 1602021-1 | NG1299 | Rural Short | Third Party Impacts | 4 | 288.5 | 1154 | 0.0012892 | 4.4685e-06
2013-05-28 01:16PM | 1620993-1 | NG1299 | Rural Short | Third Party Impacts | 13 | 17.3077 | 225 | 0.00025135 | 1.4523e-05
2012-08-24 09:38AM | 1549102-1 | NG1299 | Rural Short | Weather | 3 | 121.3333 | 364 | 0.00040663 | 3.3514e-06
2012-11-05 09:20PM | 1567364-1 | NG1299 | Rural Short | Weather | 181 | 90 | 16290 | 0.018198 | 0.0002022
2013-04-16 03:32AM | 1610565-1 | NG1299 | Rural Short | Weather | 77 | 463.1039 | 35659 | 0.039835 | 8.6018e-05
2012-07-24 03:16PM | 1540077-1 | NWA2 | Urban | Other | 2 | 54 | 108 | 0.00012065 | 2.2342e-06
2012-08-18 11:19AM | 1547167-1 | NWA2 | Urban | Equipment Failure | 6 | 79 | 474 | 0.00052951 | 6.7027e-06
2012-12-17 12:17PM | 1578466-1 | NWA2 | Urban | Operatonal Error | 1664 | 2 | 3328 | 0.0037178 | 0.0018589
2013-06-24 09:19PM | 1627618-1 | NWA2 | Urban | Vegetation | 1666 | 28.7497 | 47897 | 0.053507 | 0.0018611
2013-01-30 08:01AM | 1589920-1 | NWA2 | Urban | Equipment Failure | 1 | 764 | 764 | 0.00085348 | 1.1171e-06
2012-07-24 06:57AM | 1539894-1 | NWD2 | Urban | Equipment Failure | 194 | 78.732 | 15274 | 0.017063 | 0.00021672
2012-12-17 12:17PM | 1578467-1 | NWD2 | Urban | Operatonal Error | 2473 | 2 | 4946 | 0.0055253 | 0.0027626
2013-01-08 08:06PM | 1583384-1 | NWD2 | Urban | Equipment Failure | 1526 | 61.8388 | 94366 | 0.10542 | 0.0017047
2012-09-07 07:22PM | 1553004-1 | NWE2 | Urban | Weather | 1 | 123 | 123 | 0.00013741 | 1.1171e-06
2012-07-16 07:17AM | 1537954-1 | NWF2 | Urban | Third Party Impacts | 52 | 276.8846 | 14398 | 0.016084 | 5.809e-05
2013-01-11 08:16AM | 1583954-1 | NWF2 | Urban | Animals | 1381 | 28.0666 | 38760 | 0.0433 | 0.0015427
2013-02-08 05:41PM | 1592888-1 | NWF2 | Urban | Animals | 1381 | 29.1999 | 40325 | 0.045048 | 0.0015427
2013-03-23 02:13AM | 1605713-1 | 3347 | Urban | Equipment Failure | 1 | 378 | 378 | 0.00042227 | 1.1171e-06
2012-09-05 02:29AM | 1551858-1 | 3347 | Urban | Third Party Impacts | 74 | 242 | 17908 | 0.020005 | 8.2667e-05
2012-07-10 01:35AM | 1536724-1 | 3351 | Urban | Equipment Failure | 3069 | 53.1114 | 162999 | 0.18209 | 0.0034284
2013-05-29 05:55PM | 1621471-1 | 3351 | Urban | Equipment Failure | 1 | 285 | 285 | 0.00031838 | 1.1171e-06
2012-10-02 11:37AM | 1558342-1 | 3351 | Urban | Other | 1 | 201 | 201 | 0.00022454 | 1.1171e-06
2012-08-13 10:57PM | 1545573-1 | 3353 | Urban | Equipment Failure | 1074 | 116.7682 | 125409 | 0.1401 | 0.0011998
2012-08-14 01:11AM | 1545583-1 | 3353 | Urban | Equipment Failure | 78 | 13 | 1014 | 0.0011328 | 8.7135e-05
2012-11-09 07:22AM | 1568648-1 | 3353 | Urban | Equipment Failure | 848 | 19.3656 | 16422 | 0.018345 | 0.00094732
2013-02-27 02:03PM | 1599017-1 | 3353 | Urban | Equipment Failure | 1993 | 13.9097 | 27722 | 0.030969 | 0.0022264
2012-11-09 12:36PM | 1568817-1 | 3353 | Urban | Equipment Failure | 3 | 108 | 324 | 0.00036195 | 3.3514e-06
2013-06-26 02:03PM | 1628356-1 | 3357 | Urban | Vegetation | 1 | 134 | 134 | 0.00014969 | 1.1171e-06
2013-03-03 12:29PM | 1600303-1 | 3357 | Urban | Vegetation | 26 | 211 | 5486 | 0.0061285 | 2.9045e-05
2012-11-16 07:02AM | 1570270-1 | 3358 | Urban | Other | 13 | 151 | 1963 | 0.0021929 | 1.4523e-05
2012-07-31 11:25PM | 1541881-1 | 3360 | Urban | Third Party Impacts | 81 | 353.716 | 28651 | 0.032007 | 9.0487e-05
2013-02-20 12:16PM | 1595748-1 | 3360 | Urban | Other | 63 | 70.0794 | 4415 | 0.0049321 | 7.0379e-05
2013-01-27 10:28AM | 1589094-1 | 3360 | Urban | Equipment Failure | 78 | 164 | 12792 | 0.01429 | 8.7135e-05
2013-02-26 07:34AM | 1598478-1 | 3360 | Urban | Third Party Impacts | 64 | 124.8438 | 7990 | 0.0089258 | 7.1496e-05
2013-01-18 06:11PM | 1586295-1 | NA1207 | Rural Short | Vegetation | 118 | 180 | 21240 | 0.023728 | 0.00013182
2012-10-10 02:12PM | 1560364-1 | NA1207 | Rural Short | Animals | 2 | 71 | 142 | 0.00015863 | 2.2342e-06
2012-09-15 12:41PM | 1554807-1 | NA1207 | Rural Short | Animals | 2 | 6.5 | 13 | 1.4523e-05 | 2.2342e-06
2013-06-02 06:08PM | 1622373-1 | NA1207 | Rural Short | Equipment Failure | 1 | 37 | 37 | 4.1333e-05 | 1.1171e-06
2013-02-13 05:23AM | 1593966-1 | NA1207 | Rural Short | Third Party Impacts | 10 | 107 | 1070 | 0.0011953 | 1.1171e-05
2012-11-12 12:03PM | 1569234-1 | NA1207 | Rural Short | Equipment Failure | 3 | 177 | 531 | 0.00059319 | 3.3514e-06
2013-06-24 11:42PM | 1627645-1 | NA1207 | Rural Short | Weather | 460 | 95.4 | 43884 | 0.049024 | 0.00051388
2013-06-25 05:43AM | 1627673-1 | NA1207 | Rural Short | Weather | 121 | 160.6281 | 19436 | 0.021712 | 0.00013517
2013-06-25 08:59AM | 1627739-1 | NA1207 | Rural Short | Operatonal Error | 121 | 146.3967 | 17714 | 0.019789 | 0.00013517
2013-01-08 04:53PM | 1583310-1 | NA1214 | Urban | Equipment Failure | 694 | 50.1801 | 34825 | 0.038904 | 0.00077528
2013-02-20 03:38PM | 1595817-1 | NA1214 | Urban | Equipment Failure | 694 | 45.1801 | 31355 | 0.035027 | 0.00077528
2012-10-13 03:13AM | 1561431-1 | NA1218 | Urban | Equipment Failure | 27 | 318.3333 | 8595 | 0.0096016 | 3.0162e-05
2013-02-06 11:25AM | 1592074-1 | NA1218 | Urban | Equipment Failure | 1 | 109 | 109 | 0.00012177 | 1.1171e-06
2013-04-19 11:32AM | 1611514-1 | NA1266 | Urban | Equipment Failure | 23 | 478 | 10994 | 0.012282 | 2.5694e-05
2013-04-20 08:42AM | 1611697-1 | NA1266 | Urban | Equipment Failure | 56 | 290 | 16240 | 0.018142 | 6.2559e-05
2013-05-17 12:23PM | 1618381-1 | NA1266 | Urban | Equipment Failure | 54 | 1249 | 67446 | 0.075345 | 6.0324e-05
2013-03-08 11:07AM | 1601983-1 | NA1266 | Urban | Other | 1 | 269 | 269 | 0.00030051 | 1.1171e-06
2013-04-27 12:54PM | 1613394-1 | NA1270 | Rural Short | Other | 150 | 101.2333 | 15185 | 0.016963 | 0.00016757
2012-08-22 05:29PM | 1548193-1 | NA1270 | Rural Short | Other | 5 | 132.4 | 662 | 0.00073953 | 5.5856e-06
2013-01-28 01:40PM | 1589270-1 | NA1270 | Rural Short | Weather | 2 | 54 | 108 | 0.00012065 | 2.2342e-06
2012-08-24 03:01PM | 1549252-1 | NA1270 | Rural Short | Weather | 14 | 34 | 476 | 0.00053175 | 1.564e-05
2012-12-05 08:16AM | 1575592-1 | NA1270 | Rural Short | Operatonal Error | 649 | 2 | 1298 | 0.00145 | 0.00072501
2013-05-19 04:06PM | 1618614-1 | NA1281 | Urban | Third Party Impacts | 72 | 124.8333 | 8988 | 0.010041 | 8.0433e-05
2013-04-26 04:58AM | 1613003-1 | NA1281 | Urban | Equipment Failure | 90 | 122 | 10980 | 0.012266 | 0.00010054
2013-06-21 08:59AM | 1626827-1 | NA1281 | Urban | Other | 39 | 273.9487 | 10684 | 0.011935 | 4.3568e-05
2012-11-06 09:25AM | 1567428-1 | NA1281 | Urban | Equipment Failure | 1 | 46 | 46 | 5.1388e-05 | 1.1171e-06
2012-11-22 08:31AM | 1571770-1 | H745 | Rural Short | Other | 4 | 215 | 860 | 0.00096072 | 4.4685e-06
2012-12-27 01:40PM | 1580899-1 | H745 | Rural Short | Weather | 2 | 394.5 | 789 | 0.00088141 | 2.2342e-06
2012-09-17 04:35PM | 1557607-1 | H745 | Rural Short | Weather | 1669 | 12 | 20028 | 0.022374 | 0.0018645
2012-09-13 01:11PM | 1554298-1 | H745 | Rural Short | Other | 2 | 100 | 200 | 0.00022342 | 2.2342e-06
2013-06-29 05:00PM | 1629260-1 | H745 | Rural Short | Equipment Failure | 1 | 189 | 189 | 0.00021114 | 1.1171e-06
2013-04-12 03:30PM | 1610015-1 | H745 | Rural Short | Equipment Failure | 5 | 68 | 340 | 0.00037982 | 5.5856e-06
2012-12-25 01:26PM | 1580471-1 | H745 | Rural Short | Weather | 16 | 106 | 1696 | 0.0018946 | 1.7874e-05
2012-07-16 10:04AM | 1538000-1 | H745 | Rural Short | Equipment Failure | 4 | 71.25 | 285 | 0.00031838 | 4.4685e-06
2013-03-29 10:04AM | 1607017-1 | H745 | Rural Short | Other | 1 | 101 | 101 | 0.00011283 | 1.1171e-06
2013-01-21 06:49AM | 1586813-1 | H745 | Rural Short | Equipment Failure | 1 | 23 | 23 | 2.5694e-05 | 1.1171e-06
2013-01-23 10:57AM | 1587669-1 | H745 | Rural Short | Weather | 1 | 238 | 238 | 0.00026587 | 1.1171e-06
2012-11-16 09:07PM | 1570503-1 | H745 | Rural Short | Vegetation | 826 | 39.0412 | 32248 | 0.036025 | 0.00092274
2012-09-17 06:01PM | 1555197-1 | H745 | Rural Short | Equipment Failure | 30 | 343.4 | 10302 | 0.011509 | 3.3514e-05
2013-03-12 03:58PM | 1602944-1 | H745 | Rural Short | Equipment Failure | 1 | 365 | 365 | 0.00040775 | 1.1171e-06
2012-09-17 04:35PM | 1557607-1 | P608 | Rural Short | Weather | 871 | 12 | 10452 | 0.011676 | 0.00097301
2012-11-30 10:17AM | 1574161-1 | P608 | Rural Short | Equipment Failure | 4 | 350 | 1400 | 0.001564 | 4.4685e-06
2012-10-04 01:33PM | 1558925-1 | P608 | Rural Short | Third Party Impacts | 10 | 36 | 360 | 0.00040216 | 1.1171e-05
2013-02-12 04:14PM | 1593909-1 | P608 | Rural Short | Operatonal Error | 10 | 53 | 530 | 0.00059207 | 1.1171e-05
2013-04-16 10:49AM | 1610690-1 | P608 | Rural Short | Other | 6 | 142 | 852 | 0.00095179 | 6.7027e-06
2012-10-04 07:50AM | 1558790-1 | P608 | Rural Short | Equipment Failure | 1 | 464 | 464 | 0.00051834 | 1.1171e-06
2012-09-06 09:40AM | 1552288-1 | P608 | Rural Short | Weather | 3 | 76.3333 | 229 | 0.00025582 | 3.3514e-06
2013-04-11 07:27AM | 1609424-1 | P608 | Rural Short | Other | 3 | 104 | 312 | 0.00034854 | 3.3514e-06
2013-03-15 12:40PM | 1603755-1 | P608 | Rural Short | Equipment Failure | 7 | 72 | 504 | 0.00056303 | 7.8198e-06
2012-11-03 07:46AM | 1566817-1 | P608 | Rural Short | Other | 136 | 179.2868 | 24383 | 0.027239 | 0.00015193
2012-11-14 03:19AM | 1569671-1 | P608 | Rural Short | Vegetation | 136 | 97 | 13192 | 0.014737 | 0.00015193
2012-08-10 02:31PM | 1544710-1 | P608 | Rural Short | Weather | 388 | 120.2706 | 46665 | 0.05213 | 0.00043344
2013-01-25 03:08PM | 1588449-1 | P608 | Rural Short | Operatonal Error | 613 | 61 | 37393 | 0.041772 | 0.00068479
2013-01-25 04:55PM | 1588775-1 | P608 | Rural Short | Equipment Failure | 387 | 9 | 3483 | 0.0038909 | 0.00043233
2013-02-18 05:06PM | 1595243-1 | P608 | Rural Short | Weather | 32 | 93 | 2976 | 0.0033245 | 3.5748e-05
2012-11-30 04:17PM | 1574323-1 | P608 | Rural Short | Equipment Failure | 663 | 85.3333 | 56576 | 0.063202 | 0.00074065
2013-05-06 07:02PM | 1615277-1 | 25774 | Urban | Other | 12 | 30.5 | 366 | 0.00040887 | 1.3405e-05
2012-10-13 04:54AM | 1561427-1 | 25774 | Urban | Third Party Impacts | 17 | 327.4118 | 5566 | 0.0062179 | 1.8991e-05
2013-01-08 06:48PM | 1583360-1 | 25774 | Urban | Weather | 55 | 94 | 5170 | 0.0057755 | 6.1442e-05
2012-11-14 08:15AM | 1569704-1 | 25774 | Urban | Third Party Impacts | 13 | 112 | 1456 | 0.0016265 | 1.4523e-05
2013-03-20 08:47PM | 1605029-1 | 25775 | Urban | Other | 1 | 155 | 155 | 0.00017315 | 1.1171e-06
2013-01-28 11:32PM | 1589419-1 | 25775 | Urban | Equipment Failure | 205 | 116.7122 | 23926 | 0.026728 | 0.00022901
2013-01-12 07:00AM | 1584230-1 | 25779 | Urban | Equipment Failure | 21 | 100.0952 | 2102 | 0.0023482 | 2.346e-05
2013-04-20 11:25AM | 1611729-1 | 25780 | Urban | Equipment Failure | 36 | 125 | 4500 | 0.005027 | 4.0216e-05
2012-10-24 10:33AM | 1564203-1 | 25783 | Urban | Third Party Impacts | 11 | 145.8182 | 1604 | 0.0017919 | 1.2288e-05
2012-10-26 10:27AM | 1564877-1 | 25783 | Urban | Third Party Impacts | 1 | 60 | 60 | 6.7027e-05 | 1.1171e-06
2013-04-18 11:51AM | 1611261-1 | 25784 | Urban | Third Party Impacts | 15 | 146 | 2190 | 0.0024465 | 1.6757e-05
2013-06-05 02:30PM | 1623199-1 | 25784 | Urban | Equipment Failure | 6 | 18 | 108 | 0.00012065 | 6.7027e-06
2013-05-28 08:26AM | 1620899-1 | 41363 | Urban | Equipment Failure | 1 | 163 | 163 | 0.00018209 | 1.1171e-06
2012-10-02 11:55AM | 1558347-1 | 41363 | Urban | Equipment Failure | 1 | 83 | 83 | 9.2721e-05 | 1.1171e-06
2012-10-14 04:43AM | 1561549-1 | 5464 | Urban | Equipment Failure | 807 | 78.1896 | 63099 | 0.070489 | 0.00090152
2013-04-22 02:07PM | 1612105-1 | 5464 | Urban | Third Party Impacts | 95 | 285.7263 | 27144 | 0.030323 | 0.00010613
2013-06-24 06:25PM | 1627585-1 | 5464 | Urban | Equipment Failure | 1 | 182 | 182 | 0.00020332 | 1.1171e-06
2012-11-16 10:59AM | 1570327-1 | 5464 | Urban | Equipment Failure | 5 | 366 | 1830 | 0.0020443 | 5.5856e-06
2012-11-19 09:11PM | 1571059-1 | 5464 | Urban | Equipment Failure | 7 | 149 | 1043 | 0.0011652 | 7.8198e-06
2012-07-16 08:25AM | 1537962-1 | 5467 | Urban | Other | 21 | 79.8571 | 1677 | 0.0018734 | 2.346e-05
2013-05-06 07:00AM | 1616930-1 | 5472 | Urban | Equipment Failure | 40 | 159 | 6360 | 0.0071049 | 4.4685e-05
2013-01-08 08:15PM | 1583387-1 | 5475 | Urban | Weather | 10 | 845.5 | 8455 | 0.0094452 | 1.1171e-05
2013-06-28 10:53AM | 1628967-1 | 19898 | Urban | Third Party Impacts | 6 | 97.1667 | 583 | 0.00065128 | 6.7027e-06
2013-06-02 10:23AM | 1622289-1 | 19898 | Urban | Weather | 156 | 78.9679 | 12319 | 0.013762 | 0.00017427
2013-05-21 08:15PM | 1619169-1 | 20717 | Urban | Equipment Failure | 12 | 339 | 4068 | 0.0045444 | 1.3405e-05
2013-04-05 01:03AM | 1608022-1 | 8680 | Urban | Other | 1 | 777 | 777 | 0.000868 | 1.1171e-06
2012-08-12 05:21PM | 1545226-1 | 8680 | Urban | Equipment Failure | 12 | 344.5833 | 4135 | 0.0046193 | 1.3405e-05
2012-09-08 04:21PM | 1553202-1 | 8683 | Urban | Third Party Impacts | 42 | 36.4048 | 1529 | 0.0017081 | 4.6919e-05
2012-09-26 01:35PM | 1557145-1 | 8685 | Urban | Other | 20 | 51.4 | 1028 | 0.0011484 | 2.2342e-05
2012-10-04 10:25PM | 1559078-1 | 8685 | Urban | Other | 10 | 45 | 450 | 0.0005027 | 1.1171e-05
2012-10-08 04:12PM | 1559824-1 | 8685 | Urban | Equipment Failure | 67 | 334.1343 | 22387 | 0.025009 | 7.4847e-05
2013-03-14 04:42PM | 1603508-1 | 8685 | Urban | Equipment Failure | 5 | 417.8 | 2089 | 0.0023337 | 5.5856e-06
2012-07-24 01:19PM | 1540025-1 | 8685 | Urban | Equipment Failure | 20 | 160.5 | 3210 | 0.003586 | 2.2342e-05
2012-10-17 12:57PM | 1562517-1 | 8685 | Urban | Equipment Failure | 47 | 345 | 16215 | 0.018114 | 5.2505e-05
2013-01-04 04:40PM | 1582396-1 | 8685 | Urban | Other | 67 | 189.4478 | 12693 | 0.01418 | 7.4847e-05
2012-12-30 03:50PM | 1581376-1 | 8685 | Urban | Equipment Failure | 31 | 115.5484 | 3582 | 0.0040015 | 3.4631e-05
2012-10-25 10:33AM | 1564536-1 | 8685 | Urban | Equipment Failure | 7 | 194 | 1358 | 0.001517 | 7.8198e-06
2012-08-02 06:25PM | 1542475-1 | 8685 | Urban | Equipment Failure | 1 | 92 | 92 | 0.00010278 | 1.1171e-06
2012-10-27 10:39AM | 1565146-1 | 8685 | Urban | Equipment Failure | 1 | 271 | 271 | 0.00030274 | 1.1171e-06
2012-09-09 12:08PM | 1553281-1 | 8686 | Urban | Third Party Impacts | 33 | 109.7273 | 3621 | 0.0040451 | 3.6865e-05
2012-09-23 06:42PM | 1556590-1 | 8689 | Urban | Equipment Failure | 48 | 93.6042 | 4493 | 0.0050192 | 5.3622e-05
2012-07-03 07:19AM | 1535053-1 | 8689 | Urban | Equipment Failure | 628 | 75.1879 | 47218 | 0.052748 | 0.00070155
2013-04-15 05:34PM | 1610472-1 | 8690 | Urban | Vegetation | 798 | 11.6842 | 9324 | 0.010416 | 0.00089146
2013-01-03 05:37PM | 1582112-1 | 8693 | Urban | Equipment Failure | 1021 | 53.0568 | 54171 | 0.060516 | 0.0011406
2013-04-09 03:39PM | 1608957-1 | 8693 | Urban | Equipment Failure | 393 | 22.8651 | 8986 | 0.010038 | 0.00043903
2012-09-18 12:15PM | 1555368-1 | 8694 | Urban | Equipment Failure | 1 | 121 | 121 | 0.00013517 | 1.1171e-06
2013-01-14 04:21PM | 1584849-1 | 8694 | Urban | Equipment Failure | 18 | 178.2778 | 3209 | 0.0035848 | 2.0108e-05
2013-02-10 07:40PM | 1593332-1 | 8694 | Urban | Equipment Failure | 47 | 315 | 14805 | 0.016539 | 5.2505e-05
2012-09-13 08:21AM | 1554211-1 | 8694 | Urban | Equipment Failure | 1 | 163 | 163 | 0.00018209 | 1.1171e-06
2013-02-27 11:42AM | 1598956-1 | 8694 | Urban | Equipment Failure | 4 | 227.25 | 909 | 0.0010155 | 4.4685e-06
2013-01-07 11:47PM | 1583033-1 | PCA2 | Urban | Equipment Failure | 1 | 116 | 116 | 0.00012959 | 1.1171e-06
2013-01-23 09:52PM | 1587828-1 | PCA2 | Urban | Equipment Failure | 1 | 94 | 94 | 0.00010501 | 1.1171e-06
2013-02-26 12:44AM | 1598438-1 | PCA2 | Urban | Equipment Failure | 68 | 62.2941 | 4236 | 0.0047321 | 7.5964e-05
2012-08-18 10:31PM | 1547242-1 | PCB2 | Urban | Other | 20 | 76 | 1520 | 0.001698 | 2.2342e-05
2013-01-05 12:58PM | 1582605-1 | PCB2 | Urban | Equipment Failure | 25 | 51.88 | 1297 | 0.0014489 | 2.7928e-05
2013-02-03 08:26PM | 1591197-1 | PCB2 | Urban | Equipment Failure | 58 | 125.1897 | 7261 | 0.0081114 | 6.4793e-05
2012-07-24 02:20PM | 1540035-1 | PCB2 | Urban | Equipment Failure | 29 | 68 | 1972 | 0.002203 | 3.2396e-05
2012-10-31 02:36AM | 1565870-1 | PCB2 | Urban | Equipment Failure | 2264 | 184.5013 | 417711 | 0.46663 | 0.0025292
2013-03-05 04:31AM | 1600782-1 | PCB2 | Urban | Equipment Failure | 158 | 108 | 17064 | 0.019063 | 0.0001765
2012-11-19 10:47PM | 1571064-1 | PCB2 | Urban | Equipment Failure | 98 | 175.2449 | 17174 | 0.019185 | 0.00010948
2012-10-31 04:47AM | 1565887-1 | PCC2 | Urban | Equipment Failure | 573 | 219.5009 | 125774 | 0.1405 | 0.00064011
2012-11-18 09:59PM | 1570744-1 | PCC2 | Urban | Equipment Failure | 1053 | 106.6838 | 112338 | 0.1255 | 0.0011763
2013-02-06 10:10PM | 1592303-1 | PCD2 | Urban | Equipment Failure | 54 | 145.4815 | 7856 | 0.0087761 | 6.0324e-05
2012-08-10 03:27PM | 1544806-1 | PCD2 | Urban | Equipment Failure | 1 | 90 | 90 | 0.00010054 | 1.1171e-06
2012-08-11 09:44PM | 1545141-1 | PCD2 | Urban | Equipment Failure | 98 | 186.2653 | 18254 | 0.020392 | 0.00010948
2012-10-29 09:42AM | 1565317-1 | PCD2 | Urban | Equipment Failure | 25 | 119.12 | 2978 | 0.0033268 | 2.7928e-05
2012-12-23 04:35PM | 1579938-1 | PCD2 | Urban | Equipment Failure | 195 | 51.7692 | 10095 | 0.011277 | 0.00021784
2013-05-17 09:42AM | 1618157-1 | PCE2 | Urban | Other | 1 | 250 | 250 | 0.00027928 | 1.1171e-06
2013-06-24 01:29PM | 1627504-1 | PCE2 | Urban | Equipment Failure | 27 | 94.0741 | 2540 | 0.0028375 | 3.0162e-05
2013-01-08 12:55AM | 1583034-1 | PCF2 | Urban | Other | 38 | 97 | 3686 | 0.0041177 | 4.2451e-05
2012-07-19 06:35AM | 1538722-1 | PCF2 | Urban | Equipment Failure | 32 | 469.1875 | 15014 | 0.016772 | 3.5748e-05
2013-01-18 02:05AM | 1585833-1 | PKA2 | Urban | Equipment Failure | 90 | 88.7 | 7983 | 0.008918 | 0.00010054
2013-06-22 11:48AM | 1627120-1 | PKA2 | Urban | Equipment Failure | 41 | 171 | 7011 | 0.0078321 | 4.5802e-05
2013-04-28 03:20PM | 1615158-1 | PKB2 | Urban | Equipment Failure | 1 | 90 | 90 | 0.00010054 | 1.1171e-06
2013-06-03 12:06PM | 1622554-1 | PKC2 | Urban | Equipment Failure | 1 | 151 | 151 | 0.00016869 | 1.1171e-06
2012-09-04 02:37AM | 1551565-1 | PKC2 | Urban | Equipment Failure | 861 | 168.3113 | 144916 | 0.16189 | 0.00096184
2012-10-06 05:05AM | 1559405-1 | PKC2 | Urban | Equipment Failure | 318 | 49.4025 | 15710 | 0.01755 | 0.00035524
2012-12-26 10:33AM | 1580653-1 | T841 | Rural Short | Weather | 1 | 165 | 165 | 0.00018432 | 1.1171e-06
2012-07-22 09:02AM | 1539525-1 | T841 | Rural Short | Equipment Failure | 1 | 137 | 137 | 0.00015305 | 1.1171e-06
2012-12-27 04:52PM | 1580941-1 | T841 | Rural Short | Weather | 2 | 92.5 | 185 | 0.00020667 | 2.2342e-06
2012-12-26 03:35PM | 1580690-1 | T841 | Rural Short | Weather | 1 | 134 | 134 | 0.00014969 | 1.1171e-06
2012-12-25 02:41PM | 1580493-1 | T841 | Rural Short | Weather | 78 | 497 | 38766 | 0.043306 | 8.7135e-05
2013-02-04 02:33PM | 1591440-1 | T842 | Rural Short | Equipment Failure | 2 | 1177 | 2354 | 0.0026297 | 2.2342e-06
2013-03-24 11:49AM | 1605863-1 | T842 | Rural Short | Other | 3 | 69.3333 | 208 | 0.00023236 | 3.3514e-06
2013-02-10 07:38PM | 1593328-1 | T842 | Rural Short | Weather | 1 | 989 | 989 | 0.0011048 | 1.1171e-06
2013-01-22 06:06PM | 1587468-1 | T842 | Rural Short | Weather | 1 | 142 | 142 | 0.00015863 | 1.1171e-06
2013-01-11 10:27AM | 1584044-1 | T842 | Rural Short | Equipment Failure | 1 | 174 | 174 | 0.00019438 | 1.1171e-06
2012-12-27 06:27PM | 1580950-1 | T842 | Rural Short | Weather | 1 | 58 | 58 | 6.4793e-05 | 1.1171e-06
2012-12-28 01:34PM | 1581171-1 | T842 | Rural Short | Equipment Failure | 1 | 71 | 71 | 7.9316e-05 | 1.1171e-06
2012-12-25 09:11PM | 1580600-1 | T842 | Rural Short | Weather | 1 | 904 | 904 | 0.0010099 | 1.1171e-06
2012-12-25 02:12PM | 1580482-1 | T842 | Rural Short | Weather | 6 | 280 | 1680 | 0.0018768 | 6.7027e-06
2012-12-22 06:22PM | 1579840-1 | T842 | Rural Short | Weather | 19 | 1020 | 19380 | 0.02165 | 2.1225e-05
2012-12-23 05:17AM | 1579880-1 | T842 | Rural Short | Weather | 13 | 358.8462 | 4665 | 0.0052114 | 1.4523e-05
2012-12-22 05:39PM | 1579837-1 | T842 | Rural Short | Weather | 12 | 976.5833 | 11719 | 0.013092 | 1.3405e-05
2013-02-11 06:51AM | 1593407-1 | T842 | Rural Short | Weather | 12 | 263 | 3156 | 0.0035256 | 1.3405e-05
2013-02-25 05:07PM | 1598269-1 | T842 | Rural Short | Other | 10 | 331 | 3310 | 0.0036977 | 1.1171e-05
2013-06-11 11:24PM | 1624430-1 | 25737 | Urban | Equipment Failure | 1 | 425 | 425 | 0.00047478 | 1.1171e-06
2013-06-26 04:12PM | 1628428-1 | 25737 | Urban | Weather | 2 | 1410 | 2820 | 0.0031503 | 2.2342e-06
2013-01-08 04:15PM | 1583289-1 | 25738 | Urban | Weather | 23 | 35 | 805 | 0.00089928 | 2.5694e-05
2013-02-19 02:19PM | 1595462-1 | 25738 | Urban | Equipment Failure | 113 | 113.6106 | 12838 | 0.014342 | 0.00012623
2012-09-23 03:06PM | 1556572-1 | 25738 | Urban | Animals | 1012 | 30.583 | 30950 | 0.034575 | 0.0011305
2013-05-31 11:48PM | 1622197-1 | 25739 | Rural Short | Third Party Impacts | 14 | 363.1429 | 5084 | 0.0056794 | 1.564e-05
2013-02-19 11:56AM | 1595410-1 | 25739 | Rural Short | Third Party Impacts | 54 | 8.1852 | 442 | 0.00049377 | 6.0324e-05
2013-02-10 06:29PM | 1593284-1 | RVF2 | Urban | Weather | 10 | 249 | 2490 | 0.0027816 | 1.1171e-05
2013-01-13 09:42PM | 1584553-1 | RVF2 | Urban | Weather | 2544 | 0.0078616 | 20 | 2.2342e-05 | 0.002842
2013-01-22 03:11PM | 1587319-1 | RVF2 | Urban | Weather | 2544 | 88 | 223872 | 0.25009 | 0.002842
2012-07-10 04:25PM | 1536909-1 | S590 | Urban | Equipment Failure | 31 | 230.9355 | 7159 | 0.0079975 | 3.4631e-05
2013-01-28 11:55PM | 1589428-1 | S591 | Urban | Other | 71 | 150 | 10650 | 0.011897 | 7.9316e-05
2012-08-31 11:03AM | 1550928-1 | S591 | Urban | Vegetation | 35 | 226.4 | 7924 | 0.0088521 | 3.9099e-05
2013-01-07 03:07PM | 1582985-1 | S591 | Urban | Weather | 44 | 84 | 3696 | 0.0041289 | 4.9153e-05
2012-08-10 01:04PM | 1544538-1 | S594 | Urban | Weather | 96 | 296 | 28416 | 0.031744 | 0.00010724
2012-10-05 09:06AM | 1559199-1 | S594 | Urban | Third Party Impacts | 25 | 81.24 | 2031 | 0.0022689 | 2.7928e-05
2013-01-04 09:25PM | 1582490-1 | S594 | Urban | Animals | 1495 | 92.2087 | 137852 | 0.154 | 0.0016701
2012-09-07 11:50AM | 1552703-1 | S596 | Urban | Third Party Impacts | 19 | 163 | 3097 | 0.0034597 | 2.1225e-05
2012-11-06 08:02AM | 1567410-1 | S596 | Urban | Other | 17 | 151 | 2567 | 0.0028676 | 1.8991e-05
2012-11-07 09:53PM | 1567960-1 | S596 | Urban | Equipment Failure | 19 | 104 | 1976 | 0.0022074 | 2.1225e-05
2012-07-30 04:34PM | 1541456-1 | S598 | Urban | Equipment Failure | 133 | 47.1128 | 6266 | 0.0069999 | 0.00014858
2012-08-28 05:01PM | 1550096-1 | S599 | Urban | Third Party Impacts | 19 | 312.4211 | 5936 | 0.0066312 | 2.1225e-05
2012-12-13 11:40PM | 1577823-1 | S599 | Urban | Other | 93 | 108 | 10044 | 0.01122 | 0.00010389
2013-02-25 10:15AM | 1597949-1 | S599 | Urban | Equipment Failure | 1 | 270 | 270 | 0.00030162 | 1.1171e-06
2013-03-07 07:42AM | 1601611-1 | S606 | Urban | Equipment Failure | 13 | 208 | 2704 | 0.0030207 | 1.4523e-05
2012-12-07 10:20AM | 1579293-1 | S674 | Urban | Equipment Failure | 128 | 475 | 60800 | 0.067921 | 0.00014299
2012-07-12 09:04PM | 1537479-1 | S674 | Urban | Equipment Failure | 70 | 39.6571 | 2776 | 0.0031011 | 7.8198e-05
2012-09-07 12:33PM | 1552725-1 | S674 | Urban | Weather | 101 | 202 | 20402 | 0.022791 | 0.00011283
2012-11-03 07:11AM | 1566811-1 | S674 | Urban | Equipment Failure | 2 | 395.5 | 791 | 0.00088364 | 2.2342e-06
2012-12-22 12:04AM | 1579752-1 | S674 | Urban | Equipment Failure | 70 | 284 | 19880 | 0.022208 | 7.8198e-05
2012-08-10 11:33AM | 1544458-1 | S674 | Urban | Weather | 51 | 167.4902 | 8542 | 0.0095424 | 5.6973e-05
2012-07-05 09:21PM | 1535976-1 | 8620 | Urban | Equipment Failure | 853 | 162.5826 | 138683 | 0.15493 | 0.0009529
2013-04-20 08:12AM | 1611690-1 | A055 | Rural Short | Equipment Failure | 6 | 88 | 528 | 0.00058984 | 6.7027e-06
2012-11-20 09:14AM | 1571152-1 | RBA2 | Rural Short | Other | 2 | 140.5 | 281 | 0.00031391 | 2.2342e-06
2013-03-18 10:39AM | 1604320-1 | RBA2 | Rural Short | Other | 2 | 309 | 618 | 0.00069038 | 2.2342e-06
2012-11-08 12:37PM | 1568275-1 | RBA2 | Rural Short | Other | 1 | 223 | 223 | 0.00024912 | 1.1171e-06
2012-12-08 05:45PM | 1576571-1 | RBA2 | Rural Short | Other | 1 | 93 | 93 | 0.00010389 | 1.1171e-06
2013-04-06 04:05PM | 1608324-1 | RBA2 | Rural Short | Other | 1 | 104 | 104 | 0.00011618 | 1.1171e-06
2012-12-05 11:29AM | 1575694-1 | RBA2 | Rural Short | Vegetation | 88 | 280.2841 | 24665 | 0.027554 | 9.8307e-05
2012-09-26 09:26AM | 1557080-1 | RBA2 | Rural Short | Animals | 6 | 67.1667 | 403 | 0.0004502 | 6.7027e-06
2013-02-22 01:36PM | 1596476-1 | RBA2 | Rural Short | Other | 1 | 66 | 66 | 7.373e-05 | 1.1171e-06
2012-11-15 12:38PM | 1570082-1 | RBA2 | Rural Short | Other | 19 | 246 | 4674 | 0.0052214 | 2.1225e-05
2012-11-22 10:39AM | 1571844-1 | RBA2 | Rural Short | Vegetation | 14 | 95 | 1330 | 0.0014858 | 1.564e-05
2012-12-17 04:52PM | 1578578-1 | RBA2 | Rural Short | Equipment Failure | 462 | 153.5671 | 70948 | 0.079257 | 0.00051611
2013-01-22 05:37PM | 1587415-1 | RBB2 | Rural Short | Weather | 2 | 173 | 346 | 0.00038652 | 2.2342e-06
2012-09-06 06:13PM | 1552495-1 | RBD2 | Rural Short | Weather | 1 | 156 | 156 | 0.00017427 | 1.1171e-06
2012-12-25 03:20PM | 1580523-1 | RBD2 | Rural Short | Weather | 3 | 166 | 498 | 0.00055633 | 3.3514e-06
2012-09-19 06:23PM | 1555798-1 | RBD2 | Rural Short | Other | 1 | 980 | 980 | 0.0010948 | 1.1171e-06
2012-08-27 06:21PM | 1549872-1 | RBE2 | Rural Short | Other | 2 | 91.5 | 183 | 0.00020443 | 2.2342e-06
2013-02-25 10:15AM | 1597951-1 | RBE2 | Rural Short | Equipment Failure | 1 | 187 | 187 | 0.0002089 | 1.1171e-06
2012-12-23 09:17PM | 1580023-1 | 25739 | Rural Short | Other | 1 | 93 | 93 | 0.00010389 | 1.1171e-06
2013-01-15 11:33AM | 1585077-1 | 25740 | Urban | Other | 13 | 99.8462 | 1298 | 0.00145 | 1.4523e-05
2013-06-25 01:35PM | 1627921-1 | 25741 | Urban | Equipment Failure | 1 | 189 | 189 | 0.00021114 | 1.1171e-06
2012-09-06 12:55PM | 1552398-1 | 25741 | Urban | Equipment Failure | 51 | 72.2157 | 3683 | 0.0041144 | 5.6973e-05
2012-12-01 05:02PM | 1574692-1 | 25741 | Urban | Other | 22 | 52.5455 | 1156 | 0.0012914 | 2.4577e-05
2012-11-23 12:28PM | 1572191-1 | 25744 | Rural Short | Vegetation | 6 | 31.8333 | 191 | 0.00021337 | 6.7027e-06
2013-03-19 01:01PM | 1604576-1 | 25744 | Rural Short | Vegetation | 11 | 10.3636 | 114 | 0.00012735 | 1.2288e-05
2013-04-11 09:57PM | 1609791-1 | 25744 | Rural Short | Other | 17 | 647 | 10999 | 0.012287 | 1.8991e-05
2012-09-06 08:25PM | 1552535-1 | 25746 | Urban | Equipment Failure | 1 | 173 | 173 | 0.00019326 | 1.1171e-06
2012-07-06 11:45PM | 1536231-1 | 25747 | Rural Short | Equipment Failure | 61 | 129 | 7869 | 0.0087906 | 6.8144e-05
2012-09-27 08:39PM | 1557644-1 | 25747 | Rural Short | Third Party Impacts | 8 | 103.375 | 827 | 0.00092386 | 8.937e-06
2013-02-16 02:41PM | 1594879-1 | 25747 | Rural Short | Third Party Impacts | 32 | 289 | 9248 | 0.010331 | 3.5748e-05
2013-03-08 06:00PM | 1602194-1 | 25747 | Rural Short | Other | 1 | 30 | 30 | 3.3514e-05 | 1.1171e-06
2012-11-09 09:45AM | 1568697-1 | 25747 | Rural Short | Third Party Impacts | 1619 | 76.9321 | 124553 | 0.13914 | 0.0018086
2012-08-24 06:07PM | 1549338-1 | 53801 | Urban | Other | 1 | 155 | 155 | 0.00017315 | 1.1171e-06
2013-03-31 01:46PM | 1607162-1 | 53803 | Urban | Equipment Failure | 17 | 23.2353 | 395 | 0.00044126 | 1.8991e-05
2012-11-10 03:33PM | 1569014-1 | 53803 | Urban | Other | 33 | 58 | 1914 | 0.0021382 | 3.6865e-05
2013-03-05 08:42PM | 1601122-1 | 53803 | Urban | Equipment Failure | 1 | 271 | 271 | 0.00030274 | 1.1171e-06
2013-01-20 06:56AM | 1586694-1 | B201 | Urban | Other | 59 | 186 | 10974 | 0.012259 | 6.591e-05
2013-01-29 04:35AM | 1589463-1 | B201 | Urban | Equipment Failure | 84 | 270.8333 | 22750 | 0.025414 | 9.3838e-05
2013-05-31 04:15PM | 1622137-1 | B201 | Urban | Equipment Failure | 97 | 224.5979 | 21786 | 0.024338 | 0.00010836
2012-10-16 06:15PM | 1562308-1 | B201 | Urban | Equipment Failure | 10 | 127.6 | 1276 | 0.0014254 | 1.1171e-05
2012-09-28 07:32AM | 1557677-1 | B201 | Urban | Other | 1 | 325 | 325 | 0.00036306 | 1.1171e-06
2013-01-18 12:56PM | 1586015-1 | B201 | Urban | Equipment Failure | 1530 | 95.6431 | 146334 | 0.16347 | 0.0017092
2012-10-06 09:00AM | 1559428-1 | B201 | Urban | Other | 1 | 240 | 240 | 0.00026811 | 1.1171e-06
2012-11-18 03:03PM | 1570579-1 | B201 | Urban | Other | 1 | 3 | 3 | 3.3514e-06 | 1.1171e-06
2012-10-19 02:18PM | 1563115-1 | B202 | Urban | Other | 4 | 81.75 | 327 | 0.0003653 | 4.4685e-06
2013-02-25 02:11PM | 1598148-1 | B202 | Urban | Other | 4 | 106 | 424 | 0.00047366 | 4.4685e-06
2013-01-18 12:56PM | 1586015-1 | B202 | Urban | Equipment Failure | 55 | 95.6364 | 5260 | 0.0058761 | 6.1442e-05
2013-02-26 06:51AM | 1598470-1 | B202 | Urban | Other | 1 | 95 | 95 | 0.00010613 | 1.1171e-06
2013-01-18 12:56PM | 1586015-1 | B204 | Urban | Equipment Failure | 262 | 95.7176 | 25078 | 0.028015 | 0.00029269
2013-06-06 02:56PM | 1623502-1 | B204 | Urban | Equipment Failure | 23 | 107 | 2461 | 0.0027492 | 2.5694e-05
2013-01-21 06:03AM | 1586810-1 | B204 | Urban | Equipment Failure | 1 | 47 | 47 | 5.2505e-05 | 1.1171e-06
2013-04-18 07:59AM | 1611175-1 | B204 | Urban | Equipment Failure | 267 | 60.3745 | 16120 | 0.018008 | 0.00029827
2013-01-18 12:56PM | 1586015-1 | B205 | Urban | Equipment Failure | 600 | 95.6467 | 57388 | 0.064109 | 0.00067027
2013-01-18 12:56PM | 1586015-1 | B207 | Urban | Equipment Failure | 51 | 95.7647 | 4884 | 0.005456 | 5.6973e-05
2012-09-21 01:43PM | 1556232-1 | B210 | Urban | Other | 47 | 102.617 | 4823 | 0.0053879 | 5.2505e-05
2012-07-19 11:28PM | 1539147-1 | B210 | Urban | Equipment Failure | 44 | 68.2045 | 3001 | 0.0033525 | 4.9153e-05
2013-01-23 09:13AM | 1587606-1 | B210 | Urban | Equipment Failure | 59 | 55 | 3245 | 0.0036251 | 6.591e-05
2013-04-14 12:20PM | 1610196-1 | B211 | Urban | Equipment Failure | 6 | 127.3333 | 764 | 0.00085348 | 6.7027e-06
2012-07-19 08:31PM | 1539136-1 | B214 | Urban | Equipment Failure | 70 | 1.3571 | 95 | 0.00010613 | 7.8198e-05
2012-09-04 10:52AM | 1551671-1 | B214 | Urban | Equipment Failure | 1 | 322 | 322 | 0.00035971 | 1.1171e-06
2012-12-01 08:13AM | 1574565-1 | B214 | Urban | Animals | 1461 | 77 | 112497 | 0.12567 | 0.0016321
2013-06-11 09:28AM | 1624254-1 | B214 | Urban | Equipment Failure | 753 | 159 | 119727 | 0.13375 | 0.00084119
2012-11-02 11:27AM | 1566625-1 | B215 | Urban | Other | 47 | 62 | 2914 | 0.0032553 | 5.2505e-05
2012-09-21 01:40PM | 1556231-1 | B217 | Urban | Other | 9 | 163.3333 | 1470 | 0.0016422 | 1.0054e-05
2012-07-15 03:05AM | 1537854-1 | B217 | Urban | Other | 40 | 105.15 | 4206 | 0.0046986 | 4.4685e-05
2013-04-17 12:17AM | 1610852-1 | B217 | Urban | Equipment Failure | 49 | 76.2245 | 3735 | 0.0041724 | 5.4739e-05
2013-03-07 02:03PM | 1601766-1 | B217 | Urban | Equipment Failure | 58 | 300 | 17400 | 0.019438 | 6.4793e-05
2013-03-18 10:37AM | 1604319-1 | B217 | Urban | Equipment Failure | 1261 | 95.9159 | 120950 | 0.13512 | 0.0014087
2012-08-17 03:18PM | 1546961-1 | 48999 | Urban | Weather | 1 | 326 | 326 | 0.00036418 | 1.1171e-06
2013-03-09 04:34PM | 1602265-1 | 49001 | Urban | Equipment Failure | 20 | 234 | 4680 | 0.0052281 | 2.2342e-05
2013-01-31 07:38PM | 1590488-1 | 49001 | Urban | Equipment Failure | 3 | 372 | 1116 | 0.0012467 | 3.3514e-06
2012-09-22 09:33AM | 1556363-1 | 49001 | Urban | Equipment Failure | 807 | 77.223 | 62319 | 0.069618 | 0.00090152
2012-10-19 08:27PM | 1563214-1 | 49008 | Urban | Equipment Failure | 107 | 1598.3738 | 171026 | 0.19106 | 0.00011953
2013-01-08 05:59PM | 1583337-1 | 49008 | Urban | Equipment Failure | 41 | 121 | 4961 | 0.005542 | 4.5802e-05
2012-10-30 08:35AM | 1565596-1 | 49008 | Urban | Third Party Impacts | 25 | 114.72 | 2868 | 0.0032039 | 2.7928e-05
2013-01-30 07:24AM | 1589914-1 | 49008 | Urban | Other | 17 | 103 | 1751 | 0.0019561 | 1.8991e-05
2013-01-30 05:08PM | 1590116-1 | 49008 | Urban | Other | 1 | 280 | 280 | 0.00031279 | 1.1171e-06
2013-06-13 08:18AM | 1624836-1 | 49010 | Urban | Equipment Failure | 1 | 374 | 374 | 0.0004178 | 1.1171e-06
2012-09-13 05:58PM | 1554439-1 | B709 | Urban | Equipment Failure | 1 | 134 | 134 | 0.00014969 | 1.1171e-06
2012-07-03 10:30AM | 1535131-1 | B710 | Urban | Other | 1 | 70 | 70 | 7.8198e-05 | 1.1171e-06
2013-02-07 11:00PM | 1592640-1 | B710 | Urban | Equipment Failure | 6 | 132 | 792 | 0.00088476 | 6.7027e-06
2012-08-17 08:34PM | 1547094-1 | B715 | Urban | Weather | 1 | 21 | 21 | 2.346e-05 | 1.1171e-06
2013-06-26 12:26PM | 1628298-1 | B715 | Urban | Equipment Failure | 1 | 251 | 251 | 0.0002804 | 1.1171e-06
2012-08-17 12:41PM | 1546678-1 | B715 | Urban | Equipment Failure | 1200 | 129.4408 | 155329 | 0.17352 | 0.0013405
2013-04-15 10:22PM | 1610540-1 | B718 | Urban | Weather | 12 | 51 | 612 | 0.00068368 | 1.3405e-05
2012-10-08 04:17PM | 1559826-1 | B718 | Urban | Other | 1 | 206 | 206 | 0.00023013 | 1.1171e-06
2013-02-10 04:31AM | 1593156-1 | B720 | Urban | Equipment Failure | 11 | 479 | 5269 | 0.0058861 | 1.2288e-05
2012-11-08 03:58PM | 1568348-1 | 35001 | Urban | Vegetation | 1 | 338 | 338 | 0.00037759 | 1.1171e-06
2012-08-17 04:30PM | 1547003-1 | 35001 | Urban | Operatonal Error | 1177 | 2.1164 | 2491 | 0.0027827 | 0.0013149
2013-04-02 04:39PM | 1607422-1 | 35001 | Urban | Other | 1 | 48 | 48 | 5.3622e-05 | 1.1171e-06
2012-08-17 12:31PM | 1546644-1 | 35005 | Urban | Equipment Failure | 444 | 240.8649 | 106944 | 0.11947 | 0.000496
2013-02-01 03:02PM | 1594177-1 | 4368 | Rural Short | Weather | 719 | 36.9944 | 26599 | 0.029714 | 0.00080321
2012-11-16 01:00AM | 1570256-1 | 4368 | Rural Short | Third Party Impacts | 478 | 100.7908 | 48178 | 0.053821 | 0.00053398
2013-05-17 04:36PM | 1618359-1 | 4368 | Rural Short | Equipment Failure | 2 | 3849 | 7698 | 0.0085996 | 2.2342e-06
2012-11-30 02:11PM | 1574261-1 | 4368 | Rural Short | Weather | 1 | 87 | 87 | 9.7189e-05 | 1.1171e-06
2013-02-01 03:02PM | 1594177-1 | 4369 | Urban | Weather | 1 | 37 | 37 | 4.1333e-05 | 1.1171e-06
2013-02-01 03:02PM | 1594177-1 | 4370 | Urban | Weather | 716 | 36.9944 | 26488 | 0.02959 | 0.00079986
2012-07-04 06:58PM | 1535656-1 | 4370 | Urban | Equipment Failure | 9 | 49.5556 | 446 | 0.00049824 | 1.0054e-05
2013-01-02 11:04AM | 1581760-1 | 4370 | Urban | Equipment Failure | 30 | 344 | 10320 | 0.011529 | 3.3514e-05
2013-01-08 07:24PM | 1583373-1 | 4370 | Urban | Weather | 25 | 165 | 4125 | 0.0046081 | 2.7928e-05
2013-03-27 11:58AM | 1606625-1 | 4370 | Urban | Other | 75 | 68.0133 | 5101 | 0.0056984 | 8.3784e-05
2013-01-30 01:41PM | 1590039-1 | 4370 | Urban | Other | 1 | 110 | 110 | 0.00012288 | 1.1171e-06
2013-02-01 03:02PM | 1594177-1 | 4372 | Urban | Weather | 1050 | 37.0105 | 38861 | 0.043412 | 0.001173
2013-04-15 09:11PM | 1610516-1 | 4372 | Urban | Weather | 1050 | 145.9267 | 153223 | 0.17117 | 0.001173
2012-11-27 06:12AM | 1572974-1 | 4372 | Urban | Other | 10 | 68 | 680 | 0.00075964 | 1.1171e-05
2013-06-06 09:13AM | 1623370-1 | 4372 | Urban | Other | 1 | 123 | 123 | 0.00013741 | 1.1171e-06
2013-02-01 03:02PM | 1594177-1 | 4374 | Urban | Weather | 346 | 37.0462 | 12818 | 0.014319 | 0.00038652
2013-02-01 03:02PM | 1594177-1 | 4375 | Urban | Weather | 410 | 36.9561 | 15152 | 0.016927 | 0.00045802
2012-12-06 06:47PM | 1576222-1 | 4375 | Urban | Operatonal Error | 412 | 2.3981 | 988 | 0.0011037 | 0.00046025
2013-06-25 07:11PM | 1628059-1 | RW1218 | Rural Short | Weather | 505 | 416.5802 | 210373 | 0.23501 | 0.00056415
2013-06-26 01:13AM | 1628130-1 | RW1255 | Rural Short | Weather | 48 | 507.0417 | 24338 | 0.027188 | 5.3622e-05
2013-05-20 06:50AM | 1618652-1 | RW1281 | Rural Short | Other | 4 | 299 | 1196 | 0.0013361 | 4.4685e-06
2013-06-04 12:22PM | 1622851-1 | RW1281 | Rural Short | Equipment Failure | 4 | 93 | 372 | 0.00041557 | 4.4685e-06
2013-06-24 07:07AM | 1627392-1 | RW1281 | Rural Short | Weather | 2 | 173 | 346 | 0.00038652 | 2.2342e-06
2013-06-21 06:49AM | 1626801-1 | RW1281 | Rural Short | Equipment Failure | 31 | 185.4516 | 5749 | 0.0064223 | 3.4631e-05
2013-04-30 06:53AM | 1613824-1 | RW1292 | Rural Short | Vegetation | 9 | 97 | 873 | 0.00097525 | 1.0054e-05
2013-06-25 09:05AM | 1627771-1 | RW1292 | Rural Short | Weather | 37 | 109 | 4033 | 0.0045053 | 4.1333e-05
2013-05-04 12:25PM | 1614892-1 | RW1292 | Rural Short | Other | 14 | 123 | 1722 | 0.0019237 | 1.564e-05
2013-06-25 07:07AM | 1627688-1 | RW1292 | Rural Short | Weather | 22 | 268 | 5896 | 0.0065865 | 2.4577e-05
2013-06-25 12:44AM | 1627661-1 | RW1292 | Rural Short | Weather | 24 | 343 | 8232 | 0.0091961 | 2.6811e-05
2013-05-07 06:35PM | 1615596-1 | RW1292 | Rural Short | Vegetation | 1614 | 85.7813 | 138451 | 0.15467 | 0.001803
2013-06-25 07:45PM | 1628071-1 | RW1292 | Rural Short | Weather | 1733 | 139.4409 | 241651 | 0.26995 | 0.001936
2012-12-23 04:36PM | 1579940-1 | RWA2 | Rural Short | Weather | 4 | 84 | 336 | 0.00037535 | 4.4685e-06
2012-10-13 01:41PM | 1561489-1 | RWA2 | Rural Short | Equipment Failure | 1 | 60 | 60 | 6.7027e-05 | 1.1171e-06
2013-02-07 10:00AM | 1592381-1 | RWA2 | Rural Short | Other | 1 | 111 | 111 | 0.000124 | 1.1171e-06
2012-07-19 11:30AM | 1538930-1 | RWA2 | Rural Short | Equipment Failure | 1 | 120 | 120 | 0.00013405 | 1.1171e-06
2012-12-29 08:07AM | 1581271-1 | RWA2 | Rural Short | Other | 1 | 113 | 113 | 0.00012623 | 1.1171e-06
2013-03-15 08:46AM | 1603647-1 | RWA2 | Rural Short | Weather | 1 | 194 | 194 | 0.00021672 | 1.1171e-06
2013-02-25 02:45AM | 1597781-1 | RWA2 | Rural Short | Weather | 3 | 48 | 144 | 0.00016087 | 3.3514e-06
2013-02-25 06:32AM | 1597805-1 | RWA2 | Rural Short | Weather | 3 | 308 | 924 | 0.0010322 | 3.3514e-06
2012-12-23 05:02PM | 1580025-1 | RWA2 | Rural Short | Weather | 1 | 993 | 993 | 0.0011093 | 1.1171e-06
2013-04-16 02:33PM | 1610757-1 | RWA2 | Rural Short | Other | 2 | 78 | 156 | 0.00017427 | 2.2342e-06
2013-04-22 10:14AM | 1611964-1 | RWA2 | Rural Short | Other | 1 | 166 | 166 | 0.00018544 | 1.1171e-06
2012-10-21 05:22AM | 1563372-1 | RWA2 | Rural Short | Animals | 1 | 214 | 214 | 0.00023906 | 1.1171e-06
2013-04-16 02:31PM | 1610756-1 | RWA2 | Rural Short | Other | 1 | 80 | 80 | 8.937e-05 | 1.1171e-06
2013-03-22 06:54PM | 1605673-1 | RWA2 | Rural Short | Weather | 24 | 86 | 2064 | 0.0023057 | 2.6811e-05
2012-12-26 08:44AM | 1580636-1 | RWB2 | Rural Short | Weather | 2 | 95 | 190 | 0.00021225 | 2.2342e-06
2012-09-16 05:13PM | 1554909-1 | RWB2 | Rural Short | Equipment Failure | 1 | 775 | 775 | 0.00086577 | 1.1171e-06
2012-12-15 10:37PM | 1578219-1 | RWB2 | Rural Short | Equipment Failure | 34 | 69 | 2346 | 0.0026208 | 3.7982e-05
2013-04-16 07:30AM | 1612700-1 | RWE2 | Rural Short | Equipment Failure | 74 | 136.5135 | 10102 | 0.011285 | 8.2667e-05
2012-08-26 08:35AM | 1549521-1 | RWE2 | Rural Short | Vegetation | 7 | 23.5714 | 165 | 0.00018432 | 7.8198e-06
2012-12-12 09:48AM | 1577329-1 | RWE2 | Rural Short | Equipment Failure | 1 | 183 | 183 | 0.00020443 | 1.1171e-06
2012-12-15 07:22PM | 1578198-1 | A046 | Urban | Vegetation | 2 | 423 | 846 | 0.00094508 | 2.2342e-06
2013-04-01 12:33PM | 1607218-1 | A046 | Urban | Equipment Failure | 34 | 93 | 3162 | 0.0035323 | 3.7982e-05
2012-11-28 09:03PM | 1573711-1 | A046 | Urban | Equipment Failure | 89 | 57.5955 | 5126 | 0.0057264 | 9.9424e-05
2013-02-25 06:33AM | 1597806-1 | A046 | Urban | Equipment Failure | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-01-19 03:53PM | 1586636-1 | A048 | Urban | Equipment Failure | 12 | 50.4167 | 605 | 0.00067586 | 1.3405e-05
2012-08-07 06:45AM | 1543346-1 | A048 | Urban | Equipment Failure | 22 | 163.3636 | 3594 | 0.0040149 | 2.4577e-05
2013-01-27 01:57PM | 1589132-1 | A048 | Urban | Other | 29 | 214 | 6206 | 0.0069328 | 3.2396e-05
2013-04-29 08:29AM | 1613553-1 | A048 | Urban | Equipment Failure | 2 | 195 | 390 | 0.00043568 | 2.2342e-06
2012-09-19 04:54AM | 1555588-1 | A048 | Urban | Weather | 3 | 152 | 456 | 0.00050941 | 3.3514e-06
2012-12-01 02:40PM | 1574660-1 | A048 | Urban | Equipment Failure | 2 | 270 | 540 | 0.00060324 | 2.2342e-06
2012-10-21 04:31AM | 1563369-1 | A049 | Rural Short | Equipment Failure | 1 | 203 | 203 | 0.00022678 | 1.1171e-06
2012-10-21 01:40AM | 1563362-1 | A049 | Rural Short | Other | 1270 | 81.8244 | 103917 | 0.11609 | 0.0014187
2012-10-21 04:31AM | 1563387-1 | A049 | Rural Short | Equipment Failure | 356 | 203.3146 | 72380 | 0.080857 | 0.00039769
2013-02-25 02:42PM | 1598173-1 | A051 | Rural Short | Other | 14 | 239 | 3346 | 0.0037379 | 1.564e-05
2013-04-23 06:30AM | 1612288-1 | A051 | Rural Short | Equipment Failure | 11 | 145.0909 | 1596 | 0.0017829 | 1.2288e-05
2012-11-30 06:12PM | 1574422-1 | A051 | Rural Short | Weather | 561 | 5 | 2805 | 0.0031335 | 0.0006267
2012-12-24 03:38PM | 1580146-1 | A051 | Rural Short | Weather | 562 | 4.2331 | 2379 | 0.0026576 | 0.00062782
2013-03-05 07:30PM | 1601101-1 | A051 | Rural Short | Third Party Impacts | 562 | 155.4146 | 87343 | 0.097573 | 0.00062782
2013-04-11 05:47AM | 1609394-1 | A051 | Rural Short | Equipment Failure | 571 | 132.4133 | 75608 | 0.084463 | 0.00063788
2013-04-11 08:20AM | 1609435-1 | A051 | Rural Short | Equipment Failure | 91 | 79 | 7189 | 0.008031 | 0.00010166
2013-01-13 08:04PM | 1584519-1 | A052 | Rural Short | Other | 6 | 206.6667 | 1240 | 0.0013852 | 6.7027e-06
2013-01-14 02:05AM | 1584618-1 | A052 | Rural Short | Equipment Failure | 6 | 449 | 2694 | 0.0030095 | 6.7027e-06
2012-12-21 02:11PM | 1579697-1 | A052 | Rural Short | Equipment Failure | 6 | 189 | 1134 | 0.0012668 | 6.7027e-06
2012-07-29 09:15AM | 1541112-1 | A052 | Rural Short | Other | 12 | 0.91667 | 11 | 1.2288e-05 | 1.3405e-05
2013-04-08 11:08AM | 1608555-1 | A052 | Rural Short | Other | 17 | 152 | 2584 | 0.0028866 | 1.8991e-05
2013-02-16 04:35PM | 1594887-1 | RBB2 | Rural Short | Other | 1 | 82 | 82 | 9.1604e-05 | 1.1171e-06
2012-08-20 03:55PM | 1547562-1 | RBB2 | Rural Short | Equipment Failure | 131 | 79.7939 | 10453 | 0.011677 | 0.00014634
2012-10-11 07:27PM | 1560790-1 | RBB2 | Rural Short | Weather | 132 | 214.6667 | 28336 | 0.031655 | 0.00014746
2012-12-17 04:53PM | 1578580-1 | RBB2 | Rural Short | Other | 134 | 210.3433 | 28186 | 0.031487 | 0.00014969
2012-09-13 09:38AM | 1554239-1 | RBB2 | Rural Short | Other | 1 | 71 | 71 | 7.9316e-05 | 1.1171e-06
2012-11-30 05:55PM | 1574401-1 | RBB2 | Rural Short | Weather | 1 | 122 | 122 | 0.00013629 | 1.1171e-06
2012-07-18 11:52AM | 1538580-1 | RBB2 | Rural Short | Other | 2 | 100 | 200 | 0.00022342 | 2.2342e-06
2013-01-22 04:34PM | 1587376-1 | RBB2 | Rural Short | Weather | 20 | 400 | 8000 | 0.008937 | 2.2342e-05
2012-10-25 06:31AM | 1564465-1 | RBB2 | Rural Short | Animals | 1 | 238 | 238 | 0.00026587 | 1.1171e-06
2013-02-14 06:09AM | 1594275-1 | RBB2 | Rural Short | Other | 1 | 226 | 226 | 0.00025247 | 1.1171e-06
2013-01-22 10:37PM | 1587544-1 | RBB2 | Rural Short | Weather | 2 | 79 | 158 | 0.0001765 | 2.2342e-06
2012-11-08 07:46PM | 1568548-1 | RBB2 | Rural Short | Weather | 34 | 102 | 3468 | 0.0038742 | 3.7982e-05
2013-02-27 02:47PM | 1599102-1 | RBB2 | Rural Short | Other | 33 | 137 | 4521 | 0.0050505 | 3.6865e-05
2012-09-07 10:11PM | 1553061-1 | RBB2 | Rural Short | Other | 18 | 652 | 11736 | 0.013111 | 2.0108e-05
2013-04-12 02:14PM | 1609974-1 | RBB2 | Rural Short | Operatonal Error | 6 | 95 | 570 | 0.00063676 | 6.7027e-06
2013-04-19 10:04AM | 1611482-1 | RBB2 | Rural Short | Other | 14 | 18 | 252 | 0.00028151 | 1.564e-05
2013-04-20 07:15AM | 1611682-1 | RBB2 | Rural Short | Vegetation | 18 | 276 | 4968 | 0.0055499 | 2.0108e-05
2012-07-16 09:36PM | 1538213-1 | RBB2 | Rural Short | Other | 266 | 76.3496 | 20309 | 0.022688 | 0.00029715
2012-10-23 02:03PM | 1564011-1 | RBB2 | Rural Short | Equipment Failure | 2 | 108.5 | 217 | 0.00024242 | 2.2342e-06
2012-10-22 06:31AM | 1563474-1 | RBB2 | Rural Short | Equipment Failure | 132 | 166.0076 | 21913 | 0.024479 | 0.00014746
2012-12-03 03:00PM | 1575183-1 | RBC2 | Rural Short | Equipment Failure | 2 | 291 | 582 | 0.00065016 | 2.2342e-06
2013-06-25 03:36PM | 1627984-1 | RBC2 | Rural Short | Third Party Impacts | 3 | 82 | 246 | 0.00027481 | 3.3514e-06
2013-02-16 06:28AM | 1594819-1 | RBC2 | Rural Short | Equipment Failure | 17 | 257 | 4369 | 0.0048807 | 1.8991e-05
2012-11-07 04:48PM | 1567900-1 | RBC2 | Rural Short | Vegetation | 33 | 304.0303 | 10033 | 0.011208 | 3.6865e-05
2013-06-24 04:44PM | 1627565-1 | RBC2 | Rural Short | Third Party Impacts | 476 | 183.7647 | 87472 | 0.097717 | 0.00053175
2013-04-15 10:27PM | 1610541-1 | RBD2 | Rural Short | Weather | 8 | 52 | 416 | 0.00046472 | 8.937e-06
2013-02-26 02:56PM | 1598680-1 | RBD2 | Rural Short | Other | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-06-19 03:52PM | 1626421-1 | T884 | Urban | Equipment Failure | 259 | 2 | 518 | 0.00057867 | 0.00028933
2012-07-24 10:07AM | 1539934-1 | T884 | Urban | Equipment Failure | 15 | 294.8 | 4422 | 0.0049399 | 1.6757e-05
2013-01-13 04:38PM | 1584407-1 | T887 | Urban | Weather | 89 | 18.2584 | 1625 | 0.0018153 | 9.9424e-05
2013-06-17 06:12PM | 1625881-1 | T888 | Urban | Other | 21 | 172.2381 | 3617 | 0.0040406 | 2.346e-05
2012-12-19 08:18PM | 1579192-1 | T888 | Urban | Equipment Failure | 617 | 90.5284 | 55856 | 0.062398 | 0.00068926
2013-01-13 11:48PM | 1584599-1 | T889 | Urban | Equipment Failure | 57 | 64.2281 | 3661 | 0.0040898 | 6.3676e-05
2012-12-19 08:18PM | 1579192-1 | T890 | Urban | Equipment Failure | 1512 | 90.5132 | 136856 | 0.15288 | 0.0016891
2013-06-29 09:05AM | 1629207-1 | T890 | Urban | Equipment Failure | 1 | 239 | 239 | 0.00026699 | 1.1171e-06
2013-03-02 02:20PM | 1600205-1 | T890 | Urban | Other | 1 | 202 | 202 | 0.00022566 | 1.1171e-06
2013-01-25 01:54PM | 1588238-1 | T890 | Urban | Other | 27 | 39 | 1053 | 0.0011763 | 3.0162e-05
2012-12-01 08:52AM | 1574583-1 | T890 | Urban | Equipment Failure | 1 | 180 | 180 | 0.00020108 | 1.1171e-06
2013-03-22 02:15PM | 1605524-1 | T892 | Urban | Equipment Failure | 61 | 31.0164 | 1892 | 0.0021136 | 6.8144e-05
2013-04-05 12:23PM | 1608120-1 | T893 | Urban | Third Party Impacts | 80 | 76.6 | 6128 | 0.0068457 | 8.937e-05
2012-12-10 03:34PM | 1576831-1 | T893 | Urban | Vegetation | 947 | 29.1331 | 27589 | 0.03082 | 0.0010579
2013-06-25 10:14AM | 1627788-1 | T894 | Urban | Equipment Failure | 1 | 272 | 272 | 0.00030386 | 1.1171e-06
2012-08-07 07:02AM | 1543349-1 | T895 | Urban | Equipment Failure | 8 | 32.375 | 259 | 0.00028933 | 8.937e-06
2013-02-04 12:00PM | 1591339-1 | T895 | Urban | Equipment Failure | 1 | 518 | 518 | 0.00057867 | 1.1171e-06
2013-01-13 04:39PM | 1584409-1 | T900 | Urban | Weather | 1120 | 18.3161 | 20514 | 0.022917 | 0.0012512
2013-01-07 05:55AM | 1582763-1 | RS1203 | Urban | Other | 3 | 111.6667 | 335 | 0.00037424 | 3.3514e-06
2013-04-19 04:39PM | 1611630-1 | RS1203 | Urban | Animals | 46 | 120 | 5520 | 0.0061665 | 5.1388e-05
2012-09-28 02:29PM | 1557857-1 | RS1203 | Urban | Equipment Failure | 1 | 253 | 253 | 0.00028263 | 1.1171e-06
2013-04-04 12:24PM | 1607807-1 | RS1203 | Urban | Other | 21 | 160 | 3360 | 0.0037535 | 2.346e-05
2013-04-04 06:34AM | 1607711-1 | RS1203 | Urban | Third Party Impacts | 629 | 57 | 35853 | 0.040052 | 0.00070267
2012-08-03 08:51AM | 1542535-1 | RS1207 | Urban | Other | 3 | 306 | 918 | 0.0010255 | 3.3514e-06
2012-11-05 03:13PM | 1567284-1 | RS1207 | Urban | Other | 44 | 122 | 5368 | 0.0059967 | 4.9153e-05
2013-01-06 11:48PM | 1582758-1 | RS1207 | Urban | Other | 1 | 44 | 44 | 4.9153e-05 | 1.1171e-06
2012-09-07 02:39PM | 1552823-1 | RS1296 | Urban | Weather | 1 | 294 | 294 | 0.00032843 | 1.1171e-06
2012-09-19 03:27AM | 1555586-1 | RV1280 | Urban | Third Party Impacts | 159 | 77 | 12243 | 0.013677 | 0.00017762
2013-04-03 03:23AM | 1607477-1 | RV1280 | Urban | Third Party Impacts | 25 | 817 | 20425 | 0.022817 | 2.7928e-05
2012-11-18 12:08AM | 1573036-1 | RVC2 | Urban | Third Party Impacts | 74 | 170 | 12580 | 0.014053 | 8.2667e-05
2013-04-18 09:26PM | 1611415-1 | RVC2 | Urban | Weather | 69 | 62 | 4278 | 0.004779 | 7.7081e-05
2013-05-24 11:08AM | 1619964-1 | RVC2 | Urban | Equipment Failure | 113 | 143.3805 | 16202 | 0.0181 | 0.00012623
2013-06-20 06:06PM | 1626766-1 | RVC2 | Urban | Equipment Failure | 69 | 123 | 8487 | 0.009481 | 7.7081e-05
2012-07-16 10:56PM | 1538219-1 | RVC2 | Urban | Equipment Failure | 61 | 226.918 | 13842 | 0.015463 | 6.8144e-05
2012-09-06 07:36PM | 1552509-1 | RVC2 | Urban | Equipment Failure | 3071 | 6.3999 | 19654 | 0.021956 | 0.0034307
2013-01-08 10:41AM | 1583131-1 | RVC2 | Urban | Vegetation | 183 | 91 | 16653 | 0.018603 | 0.00020443
2013-01-22 03:03PM | 1587307-1 | RVC2 | Urban | Weather | 3068 | 59.8211 | 183531 | 0.20503 | 0.0034273
2013-05-24 12:49PM | 1620069-1 | RVC2 | Urban | Equipment Failure | 2954 | 2.6165 | 7729 | 0.0086342 | 0.0033
2012-12-04 04:18PM | 1575410-1 | RVD2 | Urban | Equipment Failure | 41 | 153.3659 | 6288 | 0.0070245 | 4.5802e-05
2013-01-18 08:21AM | 1585856-1 | RVD2 | Urban | Third Party Impacts | 20 | 384 | 7680 | 0.0085795 | 2.2342e-05
2012-08-17 06:42PM | 1547067-1 | RVD2 | Urban | Weather | 2214 | 48.4499 | 107268 | 0.11983 | 0.0024733
2013-01-29 09:33AM | 1589541-1 | RVD2 | Urban | Equipment Failure | 2043 | 72.327 | 147764 | 0.16507 | 0.0022823
2013-01-18 11:30AM | 1585955-1 | RVF2 | Urban | Other | 11 | 52.5455 | 578 | 0.0006457 | 1.2288e-05
2012-10-13 07:27AM | 1561430-1 | RVF2 | Urban | Other | 27 | 80.6667 | 2178 | 0.0024331 | 3.0162e-05
2013-01-29 05:50AM | 1589472-1 | RVF2 | Urban | Other | 13 | 140.3846 | 1825 | 0.0020387 | 1.4523e-05
2013-02-06 05:08AM | 1591961-1 | RVF2 | Urban | Other | 30 | 76 | 2280 | 0.002547 | 3.3514e-05
2012-08-03 05:10AM | 1542500-1 | 8620 | Urban | Other | 41 | 597.0244 | 24478 | 0.027345 | 4.5802e-05
2012-09-05 01:35PM | 1551993-1 | 8620 | Urban | Vegetation | 15 | 101 | 1515 | 0.0016924 | 1.6757e-05
2012-08-28 10:12AM | 1549959-1 | 8620 | Urban | Other | 7 | 72.8571 | 510 | 0.00056973 | 7.8198e-06
2012-12-13 09:32AM | 1577592-1 | B748 | Urban | Other | 1 | 266 | 266 | 0.00029715 | 1.1171e-06
2013-01-29 08:38AM | 1589509-1 | B748 | Urban | Equipment Failure | 1 | 261 | 261 | 0.00029157 | 1.1171e-06
2013-01-28 08:10PM | 1589369-1 | B748 | Urban | Weather | 1008 | 113.2034 | 114109 | 0.12747 | 0.0011261
2013-06-27 08:47AM | 1628553-1 | L504 | Urban | Equipment Failure | 6 | 132.8333 | 797 | 0.00089034 | 6.7027e-06
2012-07-19 06:38PM | 1539119-1 | SHD2 | Urban | Equipment Failure | 21 | 323.1905 | 6787 | 0.0075819 | 2.346e-05
2012-12-12 08:03AM | 1577297-1 | SHD2 | Urban | Third Party Impacts | 17 | 7 | 119 | 0.00013294 | 1.8991e-05
2013-04-30 06:32AM | 1613819-1 | SHD2 | Urban | Equipment Failure | 18 | 40.8889 | 736 | 0.0008222 | 2.0108e-05
2012-12-23 09:03PM | 1580020-1 | SHD2 | Urban | Equipment Failure | 87 | 133.5287 | 11617 | 0.012978 | 9.7189e-05
2013-01-16 05:27PM | 1585471-1 | SHE2 | Urban | Equipment Failure | 2003 | 11.998 | 24032 | 0.026847 | 0.0022376
2013-01-01 05:38PM | 1581649-1 | SHE2 | Urban | Third Party Impacts | 54 | 115.8148 | 6254 | 0.0069865 | 6.0324e-05
2012-11-14 08:42AM | 1569717-1 | SHE2 | Urban | Equipment Failure | 154 | 72.3052 | 11135 | 0.012439 | 0.00017204
2013-02-16 08:04PM | 1594897-1 | SHE2 | Urban | Equipment Failure | 1 | 129 | 129 | 0.00014411 | 1.1171e-06
2013-01-16 05:27PM | 1585471-1 | SHF2 | Urban | Equipment Failure | 270 | 11.9852 | 3236 | 0.003615 | 0.00030162
2013-01-16 05:27PM | 1585471-1 | SHG2 | Urban | Equipment Failure | 542 | 11.9982 | 6503 | 0.0072646 | 0.00060548
2012-08-24 05:50PM | 1549331-1 | SHG2 | Urban | Third Party Impacts | 24 | 88 | 2112 | 0.0023594 | 2.6811e-05
2013-01-16 05:27PM | 1585471-1 | SHH2 | Urban | Equipment Failure | 342 | 11.9854 | 4099 | 0.0045791 | 0.00038206
2012-12-14 12:19PM | 1577980-1 | SHH2 | Urban | Animals | 6 | 227 | 1362 | 0.0015215 | 6.7027e-06
2013-01-15 11:57AM | 1585095-1 | SHH2 | Urban | Animals | 1 | 54 | 54 | 6.0324e-05 | 1.1171e-06
2012-08-10 11:13AM | 1544432-1 | SHH2 | Urban | Weather | 273 | 181.6117 | 49580 | 0.055387 | 0.00030497
2013-01-27 07:41AM | 1589038-1 | SHH2 | Urban | Weather | 24 | 246.8333 | 5924 | 0.0066178 | 2.6811e-05
2013-01-27 03:10AM | 1588961-1 | SHH2 | Urban | Weather | 276 | 89.8986 | 24812 | 0.027718 | 0.00030833
2013-01-16 05:27PM | 1585471-1 | SHJ2 | Rural Short | Equipment Failure | 1702 | 11.9971 | 20419 | 0.02281 | 0.0019013
2012-10-06 08:16PM | 1559488-1 | SHJ2 | Rural Short | Weather | 5 | 482.6 | 2413 | 0.0026956 | 5.5856e-06
2012-09-28 07:59AM | 1557680-1 | SHJ2 | Rural Short | Weather | 3 | 101.6667 | 305 | 0.00034072 | 3.3514e-06
2012-10-02 10:36AM | 1558323-1 | SHJ2 | Rural Short | Equipment Failure | 2 | 316.5 | 633 | 0.00070714 | 2.2342e-06
2013-03-17 05:19PM | 1604180-1 | SHJ2 | Rural Short | Equipment Failure | 11 | 73 | 803 | 0.00089705 | 1.2288e-05
2012-10-07 10:36AM | 1559523-1 | SHJ2 | Rural Short | Other | 5 | 114.8 | 574 | 0.00064123 | 5.5856e-06
2012-09-28 01:09AM | 1557655-1 | SHJ2 | Rural Short | Weather | 6 | 175.3333 | 1052 | 0.0011752 | 6.7027e-06
2013-06-19 04:49PM | 1626435-1 | SHJ2 | Rural Short | Animals | 6 | 202 | 1212 | 0.0013539 | 6.7027e-06
2012-10-06 08:09PM | 1559486-1 | SHJ2 | Rural Short | Weather | 80 | 1 | 80 | 8.937e-05 | 8.937e-05
2013-01-16 05:27PM | 1585471-1 | SHK2 | Urban | Equipment Failure | 1560 | 12.0019 | 18723 | 0.020916 | 0.0017427
2012-08-02 12:19PM | 1542339-1 | SHK2 | Urban | Third Party Impacts | 1124 | 232.9306 | 261814 | 0.29248 | 0.0012556
2012-12-17 08:34PM | 1578602-1 | SHK2 | Urban | Animals | 1175 | 69.234 | 81350 | 0.090878 | 0.0013126
2013-04-07 09:46PM | 1608475-1 | SHK2 | Urban | Animals | 1171 | 5.5337 | 6480 | 0.0072389 | 0.0013081
2012-09-07 02:13PM | 1552804-1 | 9046 | Urban | Equipment Failure | 20 | 154.65 | 3093 | 0.0034553 | 2.2342e-05
2013-01-11 05:54PM | 1584188-1 | 9047 | Urban | Weather | 40 | 40.725 | 1629 | 0.0018198 | 4.4685e-05
2013-01-11 10:25PM | 1584214-1 | 9047 | Urban | Equipment Failure | 166 | 51.5482 | 8557 | 0.0095592 | 0.00018544
2013-01-18 03:50PM | 1586185-1 | 9047 | Urban | Weather | 48 | 86.2917 | 4142 | 0.0046271 | 5.3622e-05
2013-01-18 05:55PM | 1586277-1 | 9047 | Urban | Weather | 48 | 456.0625 | 21891 | 0.024455 | 5.3622e-05
2012-08-17 01:35PM | 1546753-1 | 9047 | Urban | Equipment Failure | 44 | 196.7273 | 8656 | 0.0096698 | 4.9153e-05
2012-08-07 05:35PM | 1543570-1 | 9047 | Urban | Equipment Failure | 118 | 29.4661 | 3477 | 0.0038842 | 0.00013182
2013-01-08 05:59PM | 1583338-1 | 9049 | Urban | Other | 97 | 98 | 9506 | 0.010619 | 0.00010836
2013-04-10 09:37AM | 1609109-1 | 9049 | Urban | Other | 98 | 45 | 4410 | 0.0049265 | 0.00010948
2012-07-04 06:44PM | 1535722-1 | 9049 | Urban | Equipment Failure | 193 | 62.829 | 12126 | 0.013546 | 0.0002156
2012-07-22 04:36PM | 1539573-1 | 9049 | Urban | Other | 30 | 73.3667 | 2201 | 0.0024588 | 3.3514e-05
2012-11-08 07:21PM | 1568533-1 | 9049 | Urban | Third Party Impacts | 1208 | 90.082 | 108819 | 0.12156 | 0.0013495
2013-04-22 07:24AM | 1611896-1 | 9049 | Urban | Equipment Failure | 849 | 57.735 | 49017 | 0.054758 | 0.00094843
2013-03-12 12:02AM | 1602730-1 | 9050 | Urban | Other | 96 | 115 | 11040 | 0.012333 | 0.00010724
2012-10-21 05:21PM | 1563440-1 | 9050 | Urban | Third Party Impacts | 51 | 316.3725 | 16135 | 0.018025 | 5.6973e-05
2012-12-13 04:58PM | 1577735-1 | 9050 | Urban | Equipment Failure | 92 | 241 | 22172 | 0.024769 | 0.00010278
2013-04-26 10:05AM | 1613058-1 | 9050 | Urban | Equipment Failure | 1600 | 155.5637 | 248902 | 0.27805 | 0.0017874
2013-02-27 08:00PM | 1599173-1 | 9052 | Urban | Other | 68 | 74 | 5032 | 0.0056213 | 7.5964e-05
2012-11-08 09:57PM | 1568587-1 | 9052 | Urban | Third Party Impacts | 1106 | 157.5515 | 174252 | 0.19466 | 0.0012355
2013-03-22 04:55PM | 1605579-1 | 9055 | Urban | Weather | 7 | 160 | 1120 | 0.0012512 | 7.8198e-06
2013-04-26 04:09PM | 1613252-1 | 9055 | Urban | Other | 190 | 130 | 24700 | 0.027593 | 0.00021225
2013-05-13 05:43PM | 1616956-1 | 9056 | Urban | Equipment Failure | 47 | 77.1064 | 3624 | 0.0040484 | 5.2505e-05
2012-08-17 06:28PM | 1547063-1 | 9056 | Urban | Weather | 1 | 62 | 62 | 6.9261e-05 | 1.1171e-06
2013-04-04 05:39PM | 1607917-1 | 9056 | Urban | Equipment Failure | 27 | 176 | 4752 | 0.0053086 | 3.0162e-05
2013-01-19 12:54PM | 1586614-1 | 9057 | Urban | Vegetation | 27 | 44.5926 | 1204 | 0.001345 | 3.0162e-05
2013-02-07 04:00PM | 1592567-1 | 9059 | Urban | Other | 1 | 74 | 74 | 8.2667e-05 | 1.1171e-06
2013-03-20 03:59PM | 1604971-1 | 9059 | Urban | Third Party Impacts | 27 | 55 | 1485 | 0.0016589 | 3.0162e-05
2012-10-16 04:47PM | 1562293-1 | 9059 | Urban | Third Party Impacts | 19 | 98 | 1862 | 0.0020801 | 2.1225e-05
2012-11-16 01:43PM | 1570395-1 | 9059 | Urban | Third Party Impacts | 599 | 92 | 55108 | 0.061562 | 0.00066915
2013-01-14 12:03PM | 1584720-1 | 9059 | Urban | Equipment Failure | 970 | 162.3577 | 157487 | 0.17593 | 0.0010836
2012-07-11 12:22AM | 1536933-1 | 9060 | Urban | Equipment Failure | 233 | 740.3648 | 172505 | 0.19271 | 0.00026029
2012-12-04 10:46AM | 1575259-1 | 9060 | Urban | Other | 1370 | 2.9832 | 4087 | 0.0045657 | 0.0015305
2012-12-20 02:27PM | 1579441-1 | 9060 | Urban | Equipment Failure | 19 | 140 | 2660 | 0.0029715 | 2.1225e-05
2013-01-18 12:01PM | 1585966-1 | 9060 | Urban | Weather | 27 | 65.0741 | 1757 | 0.0019628 | 3.0162e-05
2013-03-15 10:57AM | 1603696-1 | 9062 | Urban | Equipment Failure | 75 | 174.1333 | 13060 | 0.01459 | 8.3784e-05
2012-10-29 05:29AM | 1565272-1 | 9062 | Urban | Animals | 103 | 58.0971 | 5984 | 0.0066848 | 0.00011506
2013-05-22 10:30AM | 1620954-1 | 7532 | Rural Short | Equipment Failure | 1 | 162 | 162 | 0.00018097 | 1.1171e-06
2012-12-30 08:02AM | 1581349-1 | 7507 | Urban | Other | 2 | 10 | 20 | 2.2342e-05 | 2.2342e-06
2012-10-30 04:44PM | 1565833-1 | 49914 | Urban | Other | 69 | 132 | 9108 | 0.010175 | 7.7081e-05
2012-08-14 09:00AM | 1545628-1 | 49914 | Urban | Equipment Failure | 109 | 28.3945 | 3095 | 0.0034575 | 0.00012177
2012-08-14 07:52AM | 1545604-1 | 49914 | Urban | Equipment Failure | 639 | 14.8732 | 9504 | 0.010617 | 0.00071384
2012-08-14 07:59AM | 1545606-1 | 49914 | Urban | Equipment Failure | 639 | 86.8607 | 55504 | 0.062005 | 0.00071384
2012-10-08 11:40AM | 1559710-1 | 49915 | Urban | Third Party Impacts | 4 | 267.5 | 1070 | 0.0011953 | 4.4685e-06
2013-03-16 05:57PM | 1604029-1 | 49915 | Urban | Equipment Failure | 1 | 173 | 173 | 0.00019326 | 1.1171e-06
2012-07-05 08:51PM | 1535971-1 | 49916 | Urban | Equipment Failure | 14 | 426.5 | 5971 | 0.0066703 | 1.564e-05
2013-02-11 08:40AM | 1593434-1 | 49916 | Urban | Other | 1 | 713 | 713 | 0.00079651 | 1.1171e-06
2013-04-28 11:31PM | 1613517-1 | 49918 | Urban | Equipment Failure | 40 | 41.775 | 1671 | 0.0018667 | 4.4685e-05
2012-08-15 12:01PM | 1546014-1 | 68179 | Urban | Equipment Failure | 850 | 94.2329 | 80098 | 0.089479 | 0.00094955
2012-09-23 10:37AM | 1556544-1 | 68179 | Urban | Operatonal Error | 848 | 33.75 | 28620 | 0.031972 | 0.00094732
2012-07-11 10:51AM | 1537049-1 | 68181 | Urban | Vegetation | 57 | 66.2105 | 3774 | 0.004216 | 6.3676e-05
2013-06-14 06:22PM | 1625380-1 | 68181 | Urban | Equipment Failure | 1 | 255 | 255 | 0.00028487 | 1.1171e-06
2013-06-05 04:24PM | 1623254-1 | 68181 | Urban | Equipment Failure | 1 | 164 | 164 | 0.00018321 | 1.1171e-06
2013-03-27 06:59PM | 1606743-1 | 68181 | Urban | Equipment Failure | 995 | 6.2482 | 6217 | 0.0069451 | 0.0011115
2013-03-27 07:11PM | 1606746-1 | 68181 | Urban | Equipment Failure | 529 | 8.4083 | 4448 | 0.0049689 | 0.00059096
2013-03-27 11:38PM | 1606780-1 | 68181 | Urban | Equipment Failure | 410 | 3.0146 | 1236 | 0.0013808 | 0.00045802
2013-03-27 08:48PM | 1606764-1 | 68181 | Urban | Equipment Failure | 57 | 57.5439 | 3280 | 0.0036642 | 6.3676e-05
2013-03-27 10:08PM | 1606775-1 | 68181 | Urban | Operatonal Error | 1470 | 21.783 | 32021 | 0.035771 | 0.0016422
2013-02-14 07:14PM | 1594544-1 | 68181 | Urban | Equipment Failure | 1 | 186 | 186 | 0.00020778 | 1.1171e-06
2012-12-05 04:18AM | 1575538-1 | 68188 | Urban | Equipment Failure | 26 | 209 | 5434 | 0.0060704 | 2.9045e-05
2013-01-13 08:16AM | 1584338-1 | 68188 | Urban | Equipment Failure | 23 | 85.2174 | 1960 | 0.0021896 | 2.5694e-05
2013-01-04 08:25AM | 1582241-1 | 68188 | Urban | Equipment Failure | 211 | 171.3555 | 36156 | 0.040391 | 0.00023571
2013-02-10 10:27PM | 1593387-1 | 68190 | Urban | Equipment Failure | 38 | 29.0526 | 1104 | 0.0012333 | 4.2451e-05
2012-10-20 01:20PM | 1563302-1 | 68195 | Urban | Animals | 45 | 80.4667 | 3621 | 0.0040451 | 5.027e-05
2013-04-18 02:24PM | 1611298-1 | 68195 | Urban | Equipment Failure | 77 | 99.6753 | 7675 | 0.0085739 | 8.6018e-05
2012-07-13 01:48AM | 1537487-1 | 68195 | Urban | Equipment Failure | 17 | 212 | 3604 | 0.0040261 | 1.8991e-05
2012-11-21 03:16PM | 1571674-1 | 68195 | Urban | Other | 81 | 75 | 6075 | 0.0067865 | 9.0487e-05
2012-11-26 03:46PM | 1572787-1 | 68195 | Urban | Weather | 987 | 122.7234 | 121128 | 0.13531 | 0.0011026
2012-09-27 02:33PM | 1557569-1 | 68197 | Urban | Other | 59 | 134.1525 | 7915 | 0.008842 | 6.591e-05
2012-07-06 06:41AM | 1535996-1 | 68204 | Urban | Equipment Failure | 1 | 74 | 74 | 8.2667e-05 | 1.1171e-06
2013-01-17 10:25PM | 1585817-1 | 68204 | Urban | Equipment Failure | 56 | 33.9107 | 1899 | 0.0021214 | 6.2559e-05
2012-09-26 10:16PM | 1557264-1 | 68204 | Urban | Equipment Failure | 1 | 306 | 306 | 0.00034184 | 1.1171e-06
2013-03-28 09:18AM | 1606817-1 | 68204 | Urban | Equipment Failure | 1 | 251 | 251 | 0.0002804 | 1.1171e-06
2012-10-02 08:14PM | 1558454-1 | 68204 | Urban | Equipment Failure | 1 | 195 | 195 | 0.00021784 | 1.1171e-06
2012-08-28 11:02AM | 1549973-1 | L514 | Urban | Equipment Failure | 25 | 53.36 | 1334 | 0.0014902 | 2.7928e-05
2013-01-18 04:04PM | 1586196-1 | 1105 | Urban | Third Party Impacts | 64 | 118.4062 | 7578 | 0.0084655 | 7.1496e-05
2013-06-11 07:27PM | 1624413-1 | 1105 | Urban | Equipment Failure | 223 | 228.6099 | 50980 | 0.056951 | 0.00024912
2013-01-08 04:43PM | 1583302-1 | 1105 | Urban | Vegetation | 1143 | 65.8758 | 75296 | 0.084115 | 0.0012769
2013-02-25 05:49PM | 1598295-1 | 5498 | Urban | Equipment Failure | 1 | 246 | 246 | 0.00027481 | 1.1171e-06
2013-01-18 04:11PM | 1586199-1 | 1106 | Urban | Weather | 86 | 127.3953 | 10956 | 0.012239 | 9.6072e-05
2012-07-03 05:51PM | 1535339-1 | 1106 | Urban | Equipment Failure | 104 | 110.9135 | 11535 | 0.012886 | 0.00011618
2012-07-11 02:02AM | 1536936-1 | 1106 | Urban | Equipment Failure | 64 | 159.0781 | 10181 | 0.011373 | 7.1496e-05
2013-04-08 01:27PM | 1608607-1 | 1106 | Urban | Third Party Impacts | 1 | 185 | 185 | 0.00020667 | 1.1171e-06
2012-08-28 01:53PM | 1550031-1 | 1109 | Urban | Other | 47 | 0.51064 | 24 | 2.6811e-05 | 5.2505e-05
2012-11-30 12:36PM | 1574209-1 | 1109 | Urban | Equipment Failure | 45 | 161.2222 | 7255 | 0.0081047 | 5.027e-05
2012-11-25 03:46PM | 1572521-1 | 1109 | Urban | Equipment Failure | 46 | 74 | 3404 | 0.0038027 | 5.1388e-05
2012-11-30 06:15PM | 1574427-1 | 1109 | Urban | Weather | 27 | 51.6667 | 1395 | 0.0015584 | 3.0162e-05
2012-12-01 03:20PM | 1574673-1 | 1109 | Urban | Weather | 73 | 71 | 5183 | 0.00579 | 8.155e-05
2013-02-05 09:57PM | 1591882-1 | 1112 | Urban | Equipment Failure | 1 | 81 | 81 | 9.0487e-05 | 1.1171e-06
2012-12-21 01:39PM | 1581986-1 | SN1208 | Urban | Operatonal Error | 325 | 3 | 975 | 0.0010892 | 0.00036306
2013-01-31 08:14AM | 1593570-1 | SN1208 | Urban | Operatonal Error | 326 | 1 | 326 | 0.00036418 | 0.00036418
2013-05-11 12:41PM | 1616602-1 | SN1208 | Urban | Equipment Failure | 1 | 139 | 139 | 0.00015528 | 1.1171e-06
2012-12-21 01:39PM | 1581986-1 | SN1219 | Urban | Operatonal Error | 41 | 3 | 123 | 0.00013741 | 4.5802e-05
2013-01-31 08:14AM | 1593570-1 | SN1219 | Urban | Operatonal Error | 41 | 1 | 41 | 4.5802e-05 | 4.5802e-05
2012-12-21 01:39PM | 1581986-1 | SN1230 | Rural Short | Operatonal Error | 364 | 3 | 1092 | 0.0012199 | 0.00040663
2013-01-31 08:14AM | 1593570-1 | SN1230 | Rural Short | Operatonal Error | 366 | 1 | 366 | 0.00040887 | 0.00040887
2012-10-18 04:22PM | 1562881-1 | SN1230 | Rural Short | Vegetation | 555 | 9.3333 | 5180 | 0.0057867 | 0.00062
2012-10-28 02:24PM | 1565229-1 | SN1230 | Rural Short | Other | 78 | 90.2949 | 7043 | 0.0078679 | 8.7135e-05
2013-01-17 03:38PM | 1585755-1 | SN1230 | Rural Short | Equipment Failure | 79 | 61.9494 | 4894 | 0.0054672 | 8.8252e-05
2013-01-08 08:07PM | 1583385-1 | SN1252 | Urban | Other | 1 | 24 | 24 | 2.6811e-05 | 1.1171e-06
2012-12-21 01:39PM | 1581986-1 | SN1271 | Urban | Operatonal Error | 598 | 3.0017 | 1795 | 0.0020052 | 0.00066804
2013-01-31 08:14AM | 1593570-1 | SN1271 | Urban | Operatonal Error | 601 | 1 | 601 | 0.00067139 | 0.00067139
2013-05-15 06:41PM | 1617671-1 | SN1271 | Urban | Equipment Failure | 39 | 58.6154 | 2286 | 0.0025537 | 4.3568e-05
2012-12-21 01:39PM | 1581986-1 | SN1282 | Rural Short | Operatonal Error | 28 | 3 | 84 | 9.3838e-05 | 3.1279e-05
2013-01-31 08:14AM | 1593570-1 | SN1282 | Rural Short | Operatonal Error | 28 | 1 | 28 | 3.1279e-05 | 3.1279e-05
2013-01-08 11:37PM | 1583453-1 | SN1282 | Rural Short | Third Party Impacts | 29 | 504.3448 | 14626 | 0.016339 | 3.2396e-05
2012-10-24 09:09AM | 1564168-1 | 46473 | Rural Short | Equipment Failure | 1 | 287 | 287 | 0.00032061 | 1.1171e-06
2013-02-07 10:00PM | 1592637-1 | SZ1322 | Urban | Vegetation | 1 | 882 | 882 | 0.0009853 | 1.1171e-06
2013-06-16 04:13PM | 1625567-1 | SZ1332 | Rural Short | Other | 23 | 162 | 3726 | 0.0041624 | 2.5694e-05
2013-01-12 10:25AM | 1584247-1 | SZ1332 | Rural Short | Weather | 713 | 78.0505 | 55650 | 0.062168 | 0.00079651
2013-04-17 11:26AM | 1610959-1 | SZ1342 | Urban | Other | 3 | 141.6667 | 425 | 0.00047478 | 3.3514e-06
2013-01-28 10:42PM | 1589410-1 | SZ1342 | Urban | Other | 921 | 3 | 2763 | 0.0030866 | 0.0010289
2013-02-01 03:02PM | 1590744-1 | SZ1352 | Urban | Weather | 1900 | 104.9221 | 199352 | 0.2227 | 0.0021225
2012-08-15 03:55PM | 1546109-1 | T852 | Rural Short | Other | 42 | 51.881 | 2179 | 0.0024342 | 4.6919e-05
2012-07-02 06:40AM | 1534704-1 | T852 | Rural Short | Equipment Failure | 9 | 130 | 1170 | 0.001307 | 1.0054e-05
2012-07-26 09:27AM | 1540462-1 | T852 | Rural Short | Third Party Impacts | 20 | 65.1 | 1302 | 0.0014545 | 2.2342e-05
2012-07-02 12:38PM | 1534836-1 | T854 | Urban | Third Party Impacts | 663 | 39 | 25857 | 0.028885 | 0.00074065
2012-09-05 02:00PM | 1551995-1 | SWC2 | Urban | Other | 53 | 44 | 2332 | 0.0026051 | 5.9207e-05
2012-07-10 03:19AM | 1536730-1 | SWC2 | Urban | Equipment Failure | 72 | 127.5833 | 9186 | 0.010262 | 8.0433e-05
2013-05-29 12:25PM | 1621353-1 | SWC2 | Urban | Equipment Failure | 19 | 156 | 2964 | 0.0033111 | 2.1225e-05
2013-01-22 09:58AM | 1587173-1 | SWC2 | Urban | Equipment Failure | 69 | 52.0725 | 3593 | 0.0040138 | 7.7081e-05
2012-11-11 07:11AM | 1569051-1 | SWC2 | Urban | Other | 109 | 61 | 6649 | 0.0074277 | 0.00012177
2013-06-23 08:15AM | 1627196-1 | SWC2 | Urban | Equipment Failure | 1910 | 178.5115 | 340957 | 0.38089 | 0.0021337
2012-10-27 11:30AM | 1565151-1 | SWD2 | Urban | Equipment Failure | 19 | 62 | 1178 | 0.001316 | 2.1225e-05
2013-05-23 07:01AM | 1619554-1 | SWD2 | Urban | Equipment Failure | 570 | 126.5211 | 72117 | 0.080563 | 0.00063676
2012-10-03 06:43PM | 1558710-1 | SWE2 | Urban | Equipment Failure | 40 | 63.55 | 2542 | 0.0028397 | 4.4685e-05
2012-07-15 03:20PM | 1537901-1 | SWE2 | Urban | Equipment Failure | 199 | 19.8342 | 3947 | 0.0044093 | 0.00022231
2012-07-15 06:30PM | 1537913-1 | SWE2 | Urban | Operatonal Error | 136 | 42.4485 | 5773 | 0.0064491 | 0.00015193
2013-05-20 05:17PM | 1618824-1 | SWG2 | Urban | Equipment Failure | 87 | 148.1494 | 12889 | 0.014399 | 9.7189e-05
2013-01-29 02:57AM | 1589456-1 | 19856 | Urban | Other | 22 | 40.2727 | 886 | 0.00098977 | 2.4577e-05
2012-11-14 09:06PM | 1569975-1 | 19856 | Urban | Equipment Failure | 2 | 73 | 146 | 0.0001631 | 2.2342e-06
2013-01-28 05:58PM | 1589341-1 | 19856 | Urban | Third Party Impacts | 1325 | 95.7358 | 126850 | 0.14171 | 0.0014802
2013-05-15 11:49AM | 1617466-1 | 19856 | Urban | Vegetation | 1324 | 29.4902 | 39045 | 0.043618 | 0.0014791
2012-08-17 12:19PM | 1546593-1 | 19856 | Urban | Weather | 861 | 145.0279 | 124869 | 0.13949 | 0.00096184
2013-02-28 07:42PM | 1599459-1 | 19856 | Urban | Vegetation | 541 | 55 | 29755 | 0.03324 | 0.00060436
2013-04-15 09:10PM | 1610515-1 | 19856 | Urban | Equipment Failure | 543 | 140.5801 | 76335 | 0.085275 | 0.0006066
2012-11-07 11:22AM | 1567800-1 | 19856 | Urban | Equipment Failure | 3 | 189.3333 | 568 | 0.00063452 | 3.3514e-06
2013-01-28 09:54PM | 1589403-1 | 19857 | Urban | Other | 23 | 66 | 1518 | 0.0016958 | 2.5694e-05
2012-09-12 05:36PM | 1554126-1 | 19857 | Urban | Other | 1 | 401 | 401 | 0.00044797 | 1.1171e-06
2013-05-22 12:24AM | 1619199-1 | 19857 | Urban | Other | 2439 | 173.1033 | 422199 | 0.47165 | 0.0027247
2013-03-08 08:07AM | 1601882-1 | 19857 | Urban | Equipment Failure | 1 | 232 | 232 | 0.00025917 | 1.1171e-06
2013-06-23 11:21AM | 1627230-1 | 35693 | Rural Short | Third Party Impacts | 2 | 237 | 474 | 0.00052951 | 2.2342e-06
2013-01-08 12:31PM | 1583180-1 | RWD2 | Rural Short | Vegetation | 552 | 38.8533 | 21447 | 0.023959 | 0.00061665
2013-05-06 12:01PM | 1615180-1 | RWE2 | Rural Short | Other | 4 | 210.25 | 841 | 0.0009395 | 4.4685e-06
2013-02-25 12:13AM | 1597778-1 | RWE2 | Rural Short | Weather | 1 | 183 | 183 | 0.00020443 | 1.1171e-06
2012-12-23 05:02PM | 1579953-1 | RWE2 | Rural Short | Weather | 1 | 458 | 458 | 0.00051164 | 1.1171e-06
2012-12-29 05:34PM | 1581328-1 | RWE2 | Rural Short | Equipment Failure | 1 | 103 | 103 | 0.00011506 | 1.1171e-06
2012-12-23 07:49PM | 1580001-1 | RWE2 | Rural Short | Weather | 3 | 1031 | 3093 | 0.0034553 | 3.3514e-06
2012-12-24 04:54PM | 1580179-1 | RWE2 | Rural Short | Weather | 3 | 55.3333 | 166 | 0.00018544 | 3.3514e-06
2013-05-16 10:56AM | 1617794-1 | RWE2 | Rural Short | Other | 1 | 63 | 63 | 7.0379e-05 | 1.1171e-06
2012-10-30 07:16PM | 1565850-1 | RWE2 | Rural Short | Weather | 2 | 211 | 422 | 0.00047142 | 2.2342e-06
2012-11-18 07:32AM | 1570545-1 | RWE2 | Rural Short | Other | 2 | 132 | 264 | 0.00029492 | 2.2342e-06
2013-03-27 07:11AM | 1606510-1 | RWE2 | Rural Short | Animals | 1 | 431 | 431 | 0.00048148 | 1.1171e-06
2012-10-30 07:17PM | 1565851-1 | RWE2 | Rural Short | Weather | 3 | 169 | 507 | 0.00056638 | 3.3514e-06
2012-11-01 01:13PM | 1566299-1 | RWE2 | Rural Short | Weather | 1 | 456 | 456 | 0.00050941 | 1.1171e-06
2013-03-12 03:20PM | 1602932-1 | RWE2 | Rural Short | Vegetation | 8 | 165 | 1320 | 0.0014746 | 8.937e-06
2013-03-31 08:08PM | 1607179-1 | RWE2 | Rural Short | Other | 31 | 197 | 6107 | 0.0068223 | 3.4631e-05
2012-11-03 02:09AM | 1566737-1 | RWE2 | Rural Short | Vegetation | 159 | 105.9371 | 16844 | 0.018817 | 0.00017762
2013-01-09 09:37AM | 1583513-1 | RWE2 | Rural Short | Vegetation | 5 | 40.6 | 203 | 0.00022678 | 5.5856e-06
2013-05-19 01:48PM | 1618598-1 | RWE2 | Rural Short | Vegetation | 5 | 193.4 | 967 | 0.0010803 | 5.5856e-06
2013-01-13 05:14PM | 1584444-1 | A052 | Rural Short | Weather | 1 | 194 | 194 | 0.00021672 | 1.1171e-06
2013-01-14 09:25AM | 1584666-1 | A052 | Rural Short | Equipment Failure | 3 | 382.6667 | 1148 | 0.0012825 | 3.3514e-06
2013-03-02 08:26AM | 1600141-1 | A052 | Rural Short | Equipment Failure | 1 | 1870 | 1870 | 0.002089 | 1.1171e-06
2013-06-09 07:53AM | 1624037-1 | A052 | Rural Short | Vegetation | 11 | 206 | 2266 | 0.0025314 | 1.2288e-05
2012-08-09 04:49PM | 1544213-1 | A052 | Rural Short | Other | 610 | 117.1492 | 71461 | 0.079831 | 0.00068144
2012-07-28 11:00AM | 1541080-1 | A052 | Rural Short | Third Party Impacts | 660 | 671.4379 | 443149 | 0.49505 | 0.0007373
2012-09-07 10:06AM | 1552672-1 | A053 | Rural Short | Weather | 19 | 87 | 1653 | 0.0018466 | 2.1225e-05
2013-05-14 12:46PM | 1617210-1 | A055 | Rural Short | Other | 4 | 50 | 200 | 0.00022342 | 4.4685e-06
2012-12-25 08:48PM | 1580592-1 | A055 | Rural Short | Weather | 6 | 91 | 546 | 0.00060995 | 6.7027e-06
2012-12-14 04:15PM | 1578060-1 | A055 | Rural Short | Other | 16 | 124 | 1984 | 0.0022164 | 1.7874e-05
2012-11-30 06:47PM | 1574445-1 | A055 | Rural Short | Weather | 16 | 103.5 | 1656 | 0.00185 | 1.7874e-05
2013-05-12 06:47AM | 1616704-1 | A055 | Rural Short | Equipment Failure | 9 | 223 | 2007 | 0.0022421 | 1.0054e-05
2012-11-30 07:38PM | 1574486-1 | A055 | Rural Short | Weather | 16 | 50.9375 | 815 | 0.00091045 | 1.7874e-05
2013-02-01 11:47AM | 1590620-1 | RBE2 | Rural Short | Vegetation | 339 | 3 | 1017 | 0.0011361 | 0.0003787
2013-01-18 12:23PM | 1585975-1 | T882 | Urban | Equipment Failure | 21 | 290.5238 | 6101 | 0.0068155 | 2.346e-05
2012-12-19 08:18PM | 1579192-1 | T882 | Urban | Equipment Failure | 668 | 90.4222 | 60402 | 0.067476 | 0.00074624
2013-06-25 05:07PM | 1628021-1 | T882 | Urban | Equipment Failure | 1 | 281 | 281 | 0.00031391 | 1.1171e-06
2012-12-19 08:18PM | 1579192-1 | T883 | Urban | Equipment Failure | 1290 | 90.4822 | 116722 | 0.13039 | 0.0014411
2013-05-10 10:10AM | 1616312-1 | T883 | Urban | Third Party Impacts | 43 | 350.907 | 15089 | 0.016856 | 4.8036e-05
2013-01-13 04:39PM | 1584408-1 | T883 | Urban | Weather | 1259 | 17.2327 | 21696 | 0.024237 | 0.0014065
2013-01-13 08:16PM | 1584528-1 | T883 | Urban | Weather | 1 | 128 | 128 | 0.00014299 | 1.1171e-06
2013-06-10 03:44PM | 1624135-1 | T883 | Urban | Animals | 2380 | 77.7324 | 185003 | 0.20667 | 0.0026587
2012-12-19 08:18PM | 1579192-1 | T884 | Urban | Equipment Failure | 276 | 90.4312 | 24959 | 0.027882 | 0.00030833
2012-11-26 08:25AM | 1572636-1 | T884 | Urban | Animals | 9 | 213.2222 | 1919 | 0.0021438 | 1.0054e-05
2012-07-08 10:56AM | 1536409-1 | T884 | Urban | Third Party Impacts | 402 | 5.204 | 2092 | 0.002337 | 0.00044908
2012-09-04 01:37PM | 1551733-1 | B712 | Urban | Equipment Failure | 1 | 200 | 200 | 0.00022342 | 1.1171e-06
2012-11-13 08:06AM | 1569420-1 | B712 | Urban | Equipment Failure | 2 | 164 | 328 | 0.00036642 | 2.2342e-06
2013-03-29 09:35PM | 1607061-1 | SC1204 | Urban | Third Party Impacts | 690 | 50.1159 | 34580 | 0.03863 | 0.00077081
2013-04-19 06:21PM | 1611646-1 | SC1238 | Urban | Equipment Failure | 3 | 276 | 828 | 0.00092498 | 3.3514e-06
2012-07-26 11:46PM | 1540701-1 | WL1280 | Urban | Third Party Impacts | 332 | 94 | 31208 | 0.034863 | 0.00037088
2013-01-29 04:59AM | 1589465-1 | WL1292 | Urban | Equipment Failure | 31 | 209 | 6479 | 0.0072378 | 3.4631e-05
2013-01-27 03:35PM | 1589144-1 | WL1292 | Urban | Equipment Failure | 45 | 117 | 5265 | 0.0058816 | 5.027e-05
2013-05-20 08:51PM | 1618903-1 | WL1292 | Urban | Third Party Impacts | 2106 | 113.7479 | 239553 | 0.26761 | 0.0023527
2013-02-02 07:56PM | 1591113-1 | WL1295 | Urban | Other | 12 | 26 | 312 | 0.00034854 | 1.3405e-05
2013-06-01 08:05AM | 1622207-1 | WL1299 | Urban | Equipment Failure | 1 | 58 | 58 | 6.4793e-05 | 1.1171e-06
2013-02-25 09:54AM | 1597935-1 | WL1299 | Urban | Other | 1 | 511 | 511 | 0.00057085 | 1.1171e-06
2012-10-05 11:34AM | 1559256-1 | X858 | Urban | Equipment Failure | 1373 | 61.5462 | 84503 | 0.0944 | 0.0015338
2012-10-24 10:48AM | 1564209-1 | X859 | Urban | Other | 18 | 162 | 2916 | 0.0032575 | 2.0108e-05
2012-09-17 09:09AM | 1554985-1 | X863 | Urban | Equipment Failure | 9 | 53 | 477 | 0.00053287 | 1.0054e-05
2013-04-20 12:09PM | 1611739-1 | X867 | Urban | Vegetation | 19 | 160 | 3040 | 0.003396 | 2.1225e-05
2013-06-02 10:41AM | 1622296-1 | X867 | Urban | Equipment Failure | 33 | 119.3939 | 3940 | 0.0044015 | 3.6865e-05
2013-06-20 05:56AM | 1626477-1 | X867 | Urban | Equipment Failure | 1 | 155 | 155 | 0.00017315 | 1.1171e-06
2013-05-20 01:09PM | 1618758-1 | X867 | Urban | Equipment Failure | 1 | 231 | 231 | 0.00025805 | 1.1171e-06
2013-03-08 06:09PM | 1602186-1 | X867 | Urban | Equipment Failure | 1 | 323 | 323 | 0.00036083 | 1.1171e-06
2013-03-22 11:30AM | 1605462-1 | X870 | Urban | Equipment Failure | 23 | 257.0435 | 5912 | 0.0066044 | 2.5694e-05
2013-06-22 08:43AM | 1627097-1 | X870 | Urban | Equipment Failure | 78 | 339 | 26442 | 0.029539 | 8.7135e-05
2012-08-23 01:26PM | 1548409-1 | 8801 | Rural Short | Weather | 690 | 104.9899 | 72443 | 0.080928 | 0.00077081
2012-08-23 01:27PM | 1548412-1 | 8802 | Rural Short | Weather | 648 | 243.4599 | 157762 | 0.17624 | 0.00072389
2012-08-23 01:30PM | 1548415-1 | 8636 | Rural Short | Weather | 490 | 449.1388 | 220078 | 0.24585 | 0.00054739
2012-08-23 01:31PM | 1548421-1 | A055 | Rural Short | Weather | 725 | 137.2841 | 99531 | 0.11119 | 0.00080991
2012-08-23 01:33PM | 1548428-1 | R256 | Urban | Other | 23 | 338.6522 | 7789 | 0.0087012 | 2.5694e-05
2012-08-23 01:34PM | 1548433-1 | 8635 | Rural Short | Weather | 92 | 332.5652 | 30596 | 0.034179 | 0.00010278
2012-08-23 01:37PM | 1548441-1 | X877 | Rural Short | Weather | 13 | 104.8462 | 1363 | 0.0015226 | 1.4523e-05
2012-08-23 01:41PM | 1548458-1 | 2809 | Urban | Weather | 606 | 43.6997 | 26482 | 0.029584 | 0.00067697
2012-08-23 01:42PM | 1548460-1 | A049 | Rural Short | Weather | 1262 | 198.2702 | 250217 | 0.27952 | 0.0014098
2012-08-23 01:50PM | 1548480-1 | S738 | Rural Short | Weather | 966 | 147.2867 | 142279 | 0.15894 | 0.0010791
2012-08-23 01:55PM | 1548491-1 | 9025 | Urban | Weather | 177 | 29 | 5133 | 0.0057342 | 0.00019773
2013-02-24 02:58AM | 1597118-1 | KMA2 | Urban | Weather | 1410 | 607.4702 | 856533 | 0.95685 | 0.0015751
2013-02-24 02:58AM | 1597119-1 | KMF2 | Urban | Weather | 1452 | 662.5241 | 961985 | 1.0747 | 0.0016221
2013-02-24 02:59AM | 1597121-1 | BK1299 | Rural Short | Weather | 42 | 827.4762 | 34754 | 0.038824 | 4.6919e-05
2013-02-24 03:00AM | 1597122-1 | JBB2 | Rural Short | Weather | 308 | 500.0487 | 154015 | 0.17205 | 0.00034407
2013-02-24 03:03AM | 1597123-1 | JBA2 | Rural Short | Weather | 618 | 401.3932 | 248061 | 0.27711 | 0.00069038
2013-02-24 03:27AM | 1597129-1 | BYG2 | Rural Short | Weather | 621 | 498.7681 | 309735 | 0.34601 | 0.00069373
2013-02-24 03:27AM | 1597130-1 | BYD2 | Rural Short | Weather | 1421 | 490.7854 | 697406 | 0.77909 | 0.0015874
2013-02-24 03:36AM | 1597134-1 | BGA2 | Rural Short | Vegetation | 717 | 544.5621 | 390451 | 0.43618 | 0.00080098
2013-02-24 03:37AM | 1597136-1 | BDB2 | Urban | Other | 148 | 250.027 | 37004 | 0.041338 | 0.00016533
2013-02-24 03:44AM | 1597138-1 | NA1281 | Urban | Equipment Failure | 2252 | 300.7997 | 677401 | 0.75674 | 0.0025158
2013-02-24 03:48AM | 1597140-1 | CLA2 | Rural Short | Weather | 119 | 237.6387 | 28279 | 0.031591 | 0.00013294
2013-02-24 03:54AM | 1597142-1 | SN1271 | Urban | Weather | 599 | 331.2154 | 198398 | 0.22163 | 0.00066915
2013-05-14 05:55PM | 1617321-1 | SC1238 | Urban | Equipment Failure | 3 | 86 | 258 | 0.00028822 | 3.3514e-06
2013-01-17 10:33AM | 1585629-1 | SC1238 | Urban | Other | 49 | 112.1429 | 5495 | 0.0061386 | 5.4739e-05
2012-12-28 12:10PM | 1581153-1 | SC1238 | Urban | Other | 2 | 172.5 | 345 | 0.00038541 | 2.2342e-06
2013-02-19 07:28PM | 1595631-1 | SC1241 | Urban | Other | 11 | 248 | 2728 | 0.0030475 | 1.2288e-05
2013-01-14 05:26PM | 1584869-1 | SC1241 | Urban | Equipment Failure | 1130 | 119.0265 | 134500 | 0.15025 | 0.0012623
2013-06-02 10:50AM | 1625219-1 | 5501 | Rural Short | Weather | 799 | 10.6145 | 8481 | 0.0094743 | 0.00089258
2013-06-19 07:18AM | 1626215-1 | 5501 | Rural Short | Equipment Failure | 1 | 32 | 32 | 3.5748e-05 | 1.1171e-06
2012-08-14 06:51PM | 1545853-1 | 5501 | Rural Short | Equipment Failure | 1 | 225 | 225 | 0.00025135 | 1.1171e-06
2012-09-11 03:39PM | 1553795-1 | 5503 | Urban | Other | 1 | 255 | 255 | 0.00028487 | 1.1171e-06
2013-06-02 10:50AM | 1625219-1 | 5503 | Urban | Weather | 649 | 10.621 | 6893 | 0.0077003 | 0.00072501
2012-11-02 04:41PM | 1566696-1 | 5503 | Urban | Third Party Impacts | 9 | 23.5556 | 212 | 0.00023683 | 1.0054e-05
2013-06-02 10:50AM | 1625219-1 | 5504 | Urban | Weather | 92 | 10.587 | 974 | 0.0010881 | 0.00010278
2012-10-17 02:58AM | 1562350-1 | 5506 | Urban | Equipment Failure | 1283 | 126.2728 | 162008 | 0.18098 | 0.0014333
2012-07-27 01:03PM | 1540895-1 | 5506 | Urban | Other | 2 | 312.5 | 625 | 0.0006982 | 2.2342e-06
2013-06-02 10:50AM | 1625219-1 | 5506 | Urban | Weather | 1036 | 10.6187 | 11001 | 0.012289 | 0.0011573
2013-03-08 09:27AM | 1601906-1 | 5506 | Urban | Equipment Failure | 4 | 156 | 624 | 0.00069708 | 4.4685e-06
2012-11-24 03:17PM | 1572444-1 | 5506 | Urban | Third Party Impacts | 1 | 54 | 54 | 6.0324e-05 | 1.1171e-06
2013-04-10 10:42AM | 1609170-1 | 5507 | Urban | Animals | 153 | 46 | 7038 | 0.0078623 | 0.00017092
2013-06-02 10:50AM | 1625219-1 | 5507 | Urban | Weather | 123 | 10.626 | 1307 | 0.0014601 | 0.00013741
2013-02-26 07:13AM | 1598474-1 | 5509 | Urban | Third Party Impacts | 2 | 568 | 1136 | 0.001269 | 2.2342e-06
2013-06-24 12:12PM | 1627488-1 | 5509 | Urban | Equipment Failure | 1 | 275 | 275 | 0.00030721 | 1.1171e-06
2013-01-28 09:40PM | 1589398-1 | 5509 | Urban | Equipment Failure | 13 | 74 | 962 | 0.0010747 | 1.4523e-05
2012-10-28 11:42AM | 1565217-1 | 5509 | Urban | Other | 1 | 428 | 428 | 0.00047813 | 1.1171e-06
2013-06-02 10:50AM | 1625219-1 | 5509 | Urban | Weather | 879 | 10.62 | 9335 | 0.010428 | 0.00098195
2013-04-15 04:44PM | 1610465-1 | 5510 | Urban | Equipment Failure | 1 | 165 | 165 | 0.00018432 | 1.1171e-06
2013-06-02 10:50AM | 1625219-1 | 5510 | Urban | Weather | 653 | 10.6202 | 6935 | 0.0077472 | 0.00072948
2013-06-05 12:56PM | 1623158-1 | 5510 | Urban | Equipment Failure | 19 | 89 | 1691 | 0.001889 | 2.1225e-05
2013-06-06 09:34PM | 1623564-1 | 5510 | Urban | Equipment Failure | 14 | 106 | 1484 | 0.0016578 | 1.564e-05
2012-12-09 01:29AM | 1576585-1 | 17035 | Urban | Equipment Failure | 26 | 299 | 7774 | 0.0086845 | 2.9045e-05
2013-01-08 10:33AM | 1583126-1 | 17035 | Urban | Equipment Failure | 20 | 142 | 2840 | 0.0031726 | 2.2342e-05
2013-06-02 10:50AM | 1625219-1 | 17035 | Urban | Weather | 1158 | 10.614 | 12291 | 0.013731 | 0.0012936
2013-01-31 10:22AM | 1590218-1 | 17035 | Urban | Equipment Failure | 3 | 156 | 468 | 0.00052281 | 3.3514e-06
2012-10-24 08:01PM | 1564398-1 | 17037 | Urban | Equipment Failure | 1 | 270 | 270 | 0.00030162 | 1.1171e-06
2013-06-02 10:50AM | 1625219-1 | 17037 | Urban | Weather | 500 | 10.626 | 5313 | 0.0059353 | 0.00055856
2012-11-07 10:18PM | 1567964-1 | 17037 | Urban | Equipment Failure | 1 | 203 | 203 | 0.00022678 | 1.1171e-06
2012-11-18 11:30AM | 1570554-1 | 17037 | Urban | Other | 1 | 188 | 188 | 0.00021002 | 1.1171e-06
2012-12-25 07:28PM | 1580576-1 | 17037 | Urban | Equipment Failure | 1 | 253 | 253 | 0.00028263 | 1.1171e-06
2013-06-02 10:50AM | 1625219-1 | 17038 | Urban | Weather | 1623 | 10.6198 | 17236 | 0.019255 | 0.0018131
2013-06-02 10:50AM | 1625219-1 | 17039 | Urban | Weather | 726 | 10.6116 | 7704 | 0.0086063 | 0.00081103
2012-07-15 01:21AM | 1537850-1 | 17039 | Urban | Third Party Impacts | 891 | 118.1324 | 105256 | 0.11758 | 0.00099535
2012-07-26 09:26AM | 1540461-1 | 17039 | Urban | Equipment Failure | 891 | 56.9158 | 50712 | 0.056651 | 0.00099535
2013-06-27 04:04PM | 1628763-1 | 17039 | Urban | Equipment Failure | 1 | 157 | 157 | 0.00017539 | 1.1171e-06
2013-06-17 09:16AM | 1628718-1 | SXA2 | Urban | Operatonal Error | 1290 | 9 | 11610 | 0.01297 | 0.0014411
2013-01-08 07:37PM | 1583379-1 | SXA2 | Urban | Equipment Failure | 79 | 871 | 68809 | 0.076868 | 8.8252e-05
2012-08-15 08:19AM | 1545920-1 | SXA2 | Urban | Third Party Impacts | 12 | 115 | 1380 | 0.0015416 | 1.3405e-05
2013-06-21 07:16PM | 1627110-1 | SXA2 | Urban | Other | 3 | 1055 | 3165 | 0.0035357 | 3.3514e-06
2013-01-08 02:00PM | 1583228-1 | SXA2 | Urban | Other | 13 | 64 | 832 | 0.00092944 | 1.4523e-05
2013-06-17 09:16AM | 1628718-1 | SXB2 | Rural Short | Operatonal Error | 987 | 8.997 | 8880 | 0.00992 | 0.0011026
2012-08-26 08:18PM | 1549576-1 | SXB2 | Rural Short | Other | 133 | 138.0301 | 18358 | 0.020508 | 0.00014858
2013-03-16 01:33AM | 1603937-1 | SXB2 | Rural Short | Equipment Failure | 100 | 173.7 | 17370 | 0.019404 | 0.00011171
2012-08-01 08:43AM | 1541929-1 | SXB2 | Rural Short | Other | 35 | 153.2 | 5362 | 0.00599 | 3.9099e-05
2012-09-01 06:29AM | 1551118-1 | SXB2 | Rural Short | Other | 30 | 167 | 5010 | 0.0055968 | 3.3514e-05
2012-09-22 09:30AM | 1556362-1 | SXB2 | Rural Short | Other | 96 | 75.2812 | 7227 | 0.0080734 | 0.00010724
2012-12-17 08:12AM | 1578383-1 | SXB2 | Rural Short | Equipment Failure | 980 | 88 | 86240 | 0.09634 | 0.0010948
2013-02-28 08:29AM | 1599224-1 | SXB2 | Rural Short | Weather | 980 | 69.6306 | 68238 | 0.07623 | 0.0010948
2013-06-17 09:16AM | 1628718-1 | SXC2 | Rural Short | Operatonal Error | 408 | 9.0025 | 3673 | 0.0041032 | 0.00045578
2013-01-01 08:13AM | 1581594-1 | SXC2 | Rural Short | Other | 1 | 114 | 114 | 0.00012735 | 1.1171e-06
2012-12-29 01:37PM | 1581307-1 | SXC2 | Rural Short | Vegetation | 8 | 143 | 1144 | 0.001278 | 8.937e-06
2013-01-08 06:24PM | 1583350-1 | SXC2 | Rural Short | Other | 8 | 1396 | 11168 | 0.012476 | 8.937e-06
2013-02-25 04:06PM | 1598288-1 | SXC2 | Rural Short | Weather | 4 | 390 | 1560 | 0.0017427 | 4.4685e-06
2013-01-11 05:18PM | 1584179-1 | SXC2 | Rural Short | Other | 8 | 93.25 | 746 | 0.00083337 | 8.937e-06
2013-03-14 07:50AM | 1603318-1 | SXC2 | Rural Short | Other | 6 | 125 | 750 | 0.00083784 | 6.7027e-06
2013-06-23 09:58AM | 1627219-1 | SXC2 | Rural Short | Equipment Failure | 61 | 143.3607 | 8745 | 0.0097692 | 6.8144e-05
2012-08-09 03:47PM | 1544186-1 | SXC2 | Rural Short | Weather | 407 | 53.1327 | 21625 | 0.024158 | 0.00045467
2012-11-16 06:47AM | 1570268-1 | SXC2 | Rural Short | Other | 1 | 327 | 327 | 0.0003653 | 1.1171e-06
2013-06-17 09:16AM | 1628718-1 | SXD2 | Rural Short | Operatonal Error | 772 | 9.0026 | 6950 | 0.007764 | 0.00086242
2013-02-15 06:23PM | 1594778-1 | SXD2 | Rural Short | Other | 83 | 176.6747 | 14664 | 0.016381 | 9.2721e-05
2013-01-21 01:27PM | 1586957-1 | SXD2 | Rural Short | Other | 1 | 96 | 96 | 0.00010724 | 1.1171e-06
2012-08-14 09:55AM | 1545648-1 | SXD2 | Rural Short | Equipment Failure | 14 | 410 | 5740 | 0.0064123 | 1.564e-05
2013-01-18 06:06PM | 1586291-1 | SXD2 | Rural Short | Weather | 3 | 246 | 738 | 0.00082443 | 3.3514e-06
2012-09-19 10:05AM | 1555641-1 | SXD2 | Rural Short | Equipment Failure | 281 | 236.847 | 66554 | 0.074349 | 0.00031391
2012-09-07 07:58PM | 1553012-1 | SXD2 | Rural Short | Equipment Failure | 14 | 180.2143 | 2523 | 0.0028185 | 1.564e-05
2012-09-07 01:46PM | 1552812-1 | 35815 | Rural Short | Weather | 19 | 121 | 2299 | 0.0025683 | 2.1225e-05
2012-09-07 09:02PM | 1553025-1 | 35815 | Rural Short | Weather | 500 | 93.08 | 46540 | 0.051991 | 0.00055856
2013-02-01 02:36PM | 1590748-1 | 35815 | Rural Short | Weather | 505 | 79.5228 | 40159 | 0.044862 | 0.00056415
2012-09-05 02:27PM | 1556153-1 | 35815 | Rural Short | Third Party Impacts | 507 | 17.075 | 8657 | 0.0096709 | 0.00056638
2013-05-11 08:16AM | 1616567-1 | 35816 | Rural Short | Equipment Failure | 1 | 137 | 137 | 0.00015305 | 1.1171e-06
2013-03-26 02:24PM | 1606374-1 | 35816 | Rural Short | Equipment Failure | 11 | 90 | 990 | 0.0011059 | 1.2288e-05
2012-07-22 01:14PM | 1539551-1 | 35816 | Rural Short | Equipment Failure | 55 | 300.6 | 16533 | 0.018469 | 6.1442e-05
2013-02-02 06:22PM | 1591106-1 | 35816 | Rural Short | Equipment Failure | 10 | 124 | 1240 | 0.0013852 | 1.1171e-05
2013-02-13 06:57PM | 1594225-1 | 35816 | Rural Short | Other | 16 | 98 | 1568 | 0.0017516 | 1.7874e-05
2013-05-28 09:54PM | 1621190-1 | 35816 | Rural Short | Third Party Impacts | 7 | 88 | 616 | 0.00068815 | 7.8198e-06
2013-02-10 03:41PM | 1593250-1 | 35816 | Rural Short | Weather | 21 | 123 | 2583 | 0.0028855 | 2.346e-05
2013-02-18 06:06PM | 1595253-1 | 35816 | Rural Short | Weather | 7 | 68 | 476 | 0.00053175 | 7.8198e-06
2012-09-23 11:38AM | 1556559-1 | 35816 | Rural Short | Equipment Failure | 522 | 9.5881 | 5005 | 0.0055912 | 0.00058314
2013-02-02 01:36PM | 1591056-1 | 35816 | Rural Short | Vegetation | 1058 | 105.2401 | 111344 | 0.12438 | 0.0011819
2012-10-28 10:42PM | 1565259-1 | 35816 | Rural Short | Third Party Impacts | 32 | 369.9375 | 11838 | 0.013224 | 3.5748e-05
2012-09-05 02:27PM | 1556153-1 | 35816 | Rural Short | Third Party Impacts | 1057 | 17.0738 | 18047 | 0.020161 | 0.0011808
2012-11-16 08:18PM | 1570493-1 | 35816 | Rural Short | Weather | 1 | 385 | 385 | 0.00043009 | 1.1171e-06
2013-02-19 05:44PM | 1595549-1 | 35818 | Rural Short | Equipment Failure | 34 | 96 | 3264 | 0.0036463 | 3.7982e-05
2013-04-13 12:32AM | 1610078-1 | 35818 | Rural Short | Equipment Failure | 59 | 122 | 7198 | 0.008041 | 6.591e-05
2013-01-11 09:40AM | 1583988-1 | 35818 | Rural Short | Third Party Impacts | 9 | 55.5556 | 500 | 0.00055856 | 1.0054e-05
2012-07-12 07:58PM | 1537476-1 | 35818 | Rural Short | Equipment Failure | 18 | 54.9444 | 989 | 0.0011048 | 2.0108e-05
2012-09-08 09:43AM | 1553108-1 | 35818 | Rural Short | Weather | 1 | 382 | 382 | 0.00042674 | 1.1171e-06
2012-10-07 05:33AM | 1559506-1 | 35818 | Rural Short | Equipment Failure | 1 | 395 | 395 | 0.00044126 | 1.1171e-06
2013-01-18 01:40PM | 1586084-1 | 35818 | Rural Short | Equipment Failure | 1985 | 80.3516 | 159498 | 0.17818 | 0.0022175
2012-09-05 02:27PM | 1556153-1 | 35818 | Rural Short | Third Party Impacts | 1337 | 17.0793 | 22835 | 0.025509 | 0.0014936
2012-11-01 03:30PM | 1566414-1 | 35818 | Rural Short | Vegetation | 23 | 57.8261 | 1330 | 0.0014858 | 2.5694e-05
2013-01-01 03:32PM | 1581634-1 | 35824 | Rural Short | Other | 43 | 64.3953 | 2769 | 0.0030933 | 4.8036e-05
2012-09-05 02:27PM | 1556153-1 | 35824 | Rural Short | Third Party Impacts | 1081 | 17.0731 | 18456 | 0.020618 | 0.0012076
2012-09-05 02:27PM | 1556153-1 | 35825 | Rural Short | Third Party Impacts | 1094 | 17.0878 | 18694 | 0.020883 | 0.0012221
2012-12-24 07:43PM | 1580289-1 | ULE2 | Rural Short | Weather | 1147 | 230.6827 | 264593 | 0.29558 | 0.0012813
2012-11-18 01:42PM | 1570558-1 | ULE2 | Rural Short | Vegetation | 3 | 162 | 486 | 0.00054292 | 3.3514e-06
2012-10-11 12:34PM | 1560690-1 | ULE2 | Rural Short | Weather | 5 | 160 | 800 | 0.0008937 | 5.5856e-06
2012-10-30 12:06PM | 1565756-1 | ULE2 | Rural Short | Equipment Failure | 6 | 6 | 36 | 4.0216e-05 | 6.7027e-06
2013-02-22 12:14PM | 1596451-1 | ULE2 | Rural Short | Other | 1 | 90 | 90 | 0.00010054 | 1.1171e-06
2013-04-15 06:09PM | 1610479-1 | ULE2 | Rural Short | Weather | 7 | 98 | 686 | 0.00076634 | 7.8198e-06
2012-07-30 05:55PM | 1541485-1 | ULE2 | Rural Short | Equipment Failure | 4 | 69.5 | 278 | 0.00031056 | 4.4685e-06
2012-09-05 08:55PM | 1552172-1 | ULE2 | Rural Short | Equipment Failure | 244 | 137.8934 | 33646 | 0.037587 | 0.00027258
2012-09-28 05:44PM | 1557957-1 | ULE2 | Rural Short | Weather | 242 | 195.3264 | 47269 | 0.052805 | 0.00027034
2013-01-18 09:28AM | 1585886-1 | ULE2 | Rural Short | Animals | 1445 | 17 | 24565 | 0.027442 | 0.0016142
2012-12-18 12:48PM | 1578750-1 | ULF2 | Urban | Equipment Failure | 48 | 311.1667 | 14936 | 0.016685 | 5.3622e-05
2013-03-02 11:50AM | 1600179-1 | ULF2 | Urban | Equipment Failure | 38 | 42.1316 | 1601 | 0.0017885 | 4.2451e-05
2012-08-17 12:17PM | 1546721-1 | ULF2 | Urban | Weather | 29 | 100.4138 | 2912 | 0.0032531 | 3.2396e-05
2013-01-23 06:22AM | 1587563-1 | ULH2 | Urban | Equipment Failure | 21 | 93 | 1953 | 0.0021817 | 2.346e-05
2013-02-25 06:30AM | 1597804-1 | ULH2 | Urban | Weather | 41 | 158 | 6478 | 0.0072367 | 4.5802e-05
2012-12-14 01:38PM | 1577995-1 | ULH2 | Urban | Equipment Failure | 54 | 175 | 9450 | 0.010557 | 6.0324e-05
2012-12-16 12:41PM | 1578306-1 | ULH2 | Urban | Equipment Failure | 71 | 403 | 28613 | 0.031964 | 7.9316e-05
2012-08-19 06:18PM | 1547299-1 | ULH2 | Urban | Equipment Failure | 24 | 178 | 4272 | 0.0047723 | 2.6811e-05
2013-06-15 06:56AM | 1625413-1 | ULH2 | Urban | Animals | 24 | 91 | 2184 | 0.0024398 | 2.6811e-05
2012-12-18 09:42PM | 1578849-1 | ULH2 | Urban | Animals | 2164 | 1 | 2164 | 0.0024174 | 0.0024174
2013-02-28 07:30PM | 1599450-1 | ULJ2 | Rural Short | Other | 3 | 144 | 432 | 0.0004826 | 3.3514e-06
2012-12-27 04:46PM | 1580939-1 | ULJ2 | Rural Short | Weather | 1 | 139 | 139 | 0.00015528 | 1.1171e-06
2012-08-24 10:15AM | 1549121-1 | ULJ2 | Rural Short | Equipment Failure | 150 | 107.22 | 16083 | 0.017967 | 0.00016757
2012-09-28 07:26PM | 1557970-1 | ULJ2 | Rural Short | Other | 27 | 132.5926 | 3580 | 0.0039993 | 3.0162e-05
2013-01-18 05:17PM | 1586257-1 | ULJ2 | Rural Short | Other | 27 | 175.4074 | 4736 | 0.0052907 | 3.0162e-05
2013-06-24 09:39PM | 1627616-1 | ULJ2 | Rural Short | Weather | 27 | 246.5556 | 6657 | 0.0074367 | 3.0162e-05
2013-06-25 05:34AM | 1627672-1 | ULJ2 | Rural Short | Weather | 27 | 163 | 4401 | 0.0049164 | 3.0162e-05
2013-06-25 08:54AM | 1627727-1 | ULJ2 | Rural Short | Weather | 27 | 244 | 6588 | 0.0073596 | 3.0162e-05
2012-12-16 11:14AM | 1578244-1 | ULJ2 | Rural Short | Other | 1 | 1501 | 1501 | 0.0016768 | 1.1171e-06
2013-01-13 06:18PM | 1584476-1 | ULJ2 | Rural Short | Equipment Failure | 1 | 35 | 35 | 3.9099e-05 | 1.1171e-06
2013-04-15 07:32PM | 1610493-1 | ULJ2 | Rural Short | Weather | 2 | 81 | 162 | 0.00018097 | 2.2342e-06
2012-10-14 08:38AM | 1561559-1 | ULJ2 | Rural Short | Equipment Failure | 83 | 176.2892 | 14632 | 0.016346 | 9.2721e-05
2013-04-16 09:28AM | 1610619-1 | ULJ2 | Rural Short | Weather | 5 | 142 | 710 | 0.00079316 | 5.5856e-06
2013-02-12 07:24AM | 1593747-1 | ULJ2 | Rural Short | Other | 5 | 83 | 415 | 0.0004636 | 5.5856e-06
2013-04-25 10:23AM | 1612949-1 | ULJ2 | Rural Short | Other | 5 | 54 | 270 | 0.00030162 | 5.5856e-06
2012-12-24 07:57PM | 1580300-1 | ULJ2 | Rural Short | Weather | 21 | 172.9524 | 3632 | 0.0040574 | 2.346e-05
2012-12-24 08:12PM | 1580310-1 | ULJ2 | Rural Short | Weather | 1045 | 36.7158 | 38368 | 0.042862 | 0.0011674
2013-02-25 09:09AM | 1597905-1 | ULJ2 | Rural Short | Other | 1 | 331 | 331 | 0.00036977 | 1.1171e-06
2013-01-18 04:44PM | 1586222-1 | ULL2 | Rural Short | Weather | 467 | 92.06 | 42992 | 0.048027 | 0.0005217
2013-06-09 03:01AM | 1624026-1 | ULL2 | Rural Short | Third Party Impacts | 95 | 87 | 8265 | 0.009233 | 0.00010613
2012-08-10 11:31AM | 1544461-1 | ULL2 | Rural Short | Weather | 77 | 61.3377 | 4723 | 0.0052762 | 8.6018e-05
2012-07-14 12:19AM | 1537731-1 | ULL2 | Rural Short | Equipment Failure | 53 | 115.6226 | 6128 | 0.0068457 | 5.9207e-05
2012-07-29 08:31PM | 1541164-1 | ULL2 | Rural Short | Equipment Failure | 106 | 124.0943 | 13154 | 0.014695 | 0.00011841
2013-01-28 12:49PM | 1589264-1 | ULL2 | Rural Short | Weather | 8 | 300 | 2400 | 0.0026811 | 8.937e-06
2013-06-25 07:17AM | 1627691-1 | ULL2 | Rural Short | Weather | 8 | 251 | 2008 | 0.0022432 | 8.937e-06
2013-01-25 01:26PM | 1588221-1 | UNB2 | Urban | Operatonal Error | 15 | 31 | 465 | 0.00051946 | 1.6757e-05
2013-01-25 11:39AM | 1588170-1 | UNB2 | Urban | Other | 15 | 43 | 645 | 0.00072054 | 1.6757e-05
2012-07-21 05:14PM | 1539490-1 | UNB2 | Urban | Equipment Failure | 17 | 91.4118 | 1554 | 0.001736 | 1.8991e-05
2012-11-18 02:37PM | 1570571-1 | UNC2 | Urban | Vegetation | 383 | 29 | 11107 | 0.012408 | 0.00042786
2012-12-14 09:29AM | 1577876-1 | UNC2 | Urban | Animals | 8 | 70 | 560 | 0.00062559 | 8.937e-06
2012-11-29 12:13PM | 1573832-1 | UNC2 | Urban | Vegetation | 54 | 148.2407 | 8005 | 0.0089425 | 6.0324e-05
2012-09-11 08:00AM | 1557193-1 | UNC2 | Urban | Operatonal Error | 252 | 30 | 7560 | 0.0084454 | 0.00028151
2012-11-21 05:33AM | 1571448-1 | UNC2 | Urban | Other | 1934 | 49.4943 | 95722 | 0.10693 | 0.0021605
2013-03-16 07:05AM | 1603941-1 | UND2 | Urban | Equipment Failure | 5 | 55 | 275 | 0.00030721 | 5.5856e-06
2013-03-15 05:42AM | 1603625-1 | UND2 | Urban | Equipment Failure | 5 | 370 | 1850 | 0.0020667 | 5.5856e-06
2013-06-21 05:50AM | 1626796-1 | UNE2 | Urban | Equipment Failure | 88 | 226.9659 | 19973 | 0.022312 | 9.8307e-05
2012-07-02 08:44PM | 1534997-1 | UNF2 | Urban | Third Party Impacts | 1596 | 69.463 | 110863 | 0.12385 | 0.0017829
2012-12-26 03:05PM | 1580687-1 | UNF2 | Urban | Equipment Failure | 582 | 45.9038 | 26716 | 0.029845 | 0.00065016
2012-08-15 06:01PM | 1546133-1 | UNG2 | Urban | Equipment Failure | 1 | 30 | 30 | 3.3514e-05 | 1.1171e-06
2012-08-07 02:17AM | 1543318-1 | UNG2 | Urban | Equipment Failure | 13 | 34.1538 | 444 | 0.000496 | 1.4523e-05
2013-01-22 04:37PM | 1587378-1 | UNG2 | Urban | Equipment Failure | 2 | 144 | 288 | 0.00032173 | 2.2342e-06
2013-01-28 09:22AM | 1589228-1 | UNG2 | Urban | Third Party Impacts | 187 | 161 | 30107 | 0.033633 | 0.0002089
2012-10-06 08:27PM | 1559489-1 | UNG2 | Urban | Weather | 1535 | 24.1166 | 37019 | 0.041355 | 0.0017148
2012-10-10 03:59PM | 1560412-1 | UNG2 | Urban | Equipment Failure | 140 | 116.8643 | 16361 | 0.018277 | 0.0001564
2012-08-13 02:17PM | 1545442-1 | UNG2 | Urban | Third Party Impacts | 31 | 95.3871 | 2957 | 0.0033033 | 3.4631e-05
2013-02-20 07:34PM | 1595877-1 | UNH2 | Urban | Weather | 71 | 13.8873 | 986 | 0.0011015 | 7.9316e-05
2013-04-16 07:29PM | 1610835-1 | UNH2 | Urban | Equipment Failure | 398 | 93.7739 | 37322 | 0.041693 | 0.00044461
2013-02-19 06:33PM | 1595620-1 | UNJ2 | Urban | Equipment Failure | 4 | 128 | 512 | 0.00057197 | 4.4685e-06
2012-09-16 10:04PM | 1554921-1 | UNJ2 | Urban | Third Party Impacts | 1347 | 53.2665 | 71750 | 0.080153 | 0.0015048
2013-02-01 02:49PM | 1590732-1 | UNJ2 | Urban | Weather | 1338 | 20.5964 | 27558 | 0.030786 | 0.0014947
2013-01-16 05:27PM | 1585471-1 | WRA2 | Urban | Equipment Failure | 1903 | 12.0011 | 22838 | 0.025513 | 0.0021259
2013-03-24 09:27PM | 1605910-1 | WRA2 | Urban | Third Party Impacts | 54 | 108.8704 | 5879 | 0.0065675 | 6.0324e-05
2012-12-11 10:51AM | 1577025-1 | WRA2 | Urban | Vegetation | 19 | 92 | 1748 | 0.0019527 | 2.1225e-05
2012-12-11 01:50PM | 1577085-1 | WRA2 | Urban | Vegetation | 51 | 72 | 3672 | 0.0041021 | 5.6973e-05
2013-02-19 01:50PM | 1595458-1 | WRA2 | Urban | Equipment Failure | 76 | 121 | 9196 | 0.010273 | 8.4901e-05
2012-08-10 03:03PM | 1544801-1 | WRA2 | Urban | Weather | 1454 | 101.3769 | 147402 | 0.16467 | 0.0016243
2013-05-03 03:31PM | 1614773-1 | WRA2 | Urban | Equipment Failure | 186 | 2.5161 | 468 | 0.00052281 | 0.00020778
2013-04-03 01:07PM | 1607617-1 | WRA2 | Urban | Other | 1 | 290 | 290 | 0.00032396 | 1.1171e-06
2013-01-16 05:27PM | 1585471-1 | WRC2 | Urban | Equipment Failure | 2315 | 12.0022 | 27785 | 0.031039 | 0.0025861
2013-04-16 12:07PM | 1610714-1 | WRC2 | Urban | Equipment Failure | 1 | 116 | 116 | 0.00012959 | 1.1171e-06
2013-03-29 03:54AM | 1606995-1 | WRC2 | Urban | Equipment Failure | 14 | 8 | 112 | 0.00012512 | 1.564e-05
2013-03-30 05:46AM | 1607072-1 | WRC2 | Urban | Equipment Failure | 36 | 85 | 3060 | 0.0034184 | 4.0216e-05
2013-06-16 05:39PM | 1625576-1 | WRC2 | Urban | Third Party Impacts | 41 | 225 | 9225 | 0.010305 | 4.5802e-05
2013-03-29 04:02AM | 1606996-1 | WRC2 | Urban | Equipment Failure | 1747 | 135.6817 | 237036 | 0.2648 | 0.0019516
2013-01-16 05:27PM | 1585471-1 | WRD2 | Urban | Equipment Failure | 2162 | 12.0019 | 25948 | 0.028987 | 0.0024152
2013-06-23 07:01PM | 1627356-1 | WRD2 | Urban | Equipment Failure | 1 | 44 | 44 | 4.9153e-05 | 1.1171e-06
2013-01-16 05:27PM | 1585471-1 | WRE2 | Urban | Equipment Failure | 2386 | 12.0008 | 28634 | 0.031988 | 0.0026654
2012-08-19 02:21PM | 1547284-1 | WRE2 | Urban | Vegetation | 61 | 39 | 2379 | 0.0026576 | 6.8144e-05
2013-05-26 10:33PM | 1620415-1 | WRE2 | Urban | Equipment Failure | 10 | 116 | 1160 | 0.0012959 | 1.1171e-05
2012-10-22 01:44PM | 1563575-1 | WRE2 | Urban | Equipment Failure | 751 | 52.5925 | 39497 | 0.044123 | 0.00083896
2013-04-10 06:52PM | 1609335-1 | WRE2 | Urban | Equipment Failure | 1825 | 97.6099 | 178138 | 0.199 | 0.0020387
2013-05-16 04:25PM | 1617997-1 | WRE2 | Urban | Equipment Failure | 1824 | 38.6645 | 70524 | 0.078784 | 0.0020376
2013-05-16 08:02PM | 1618076-1 | WRE2 | Urban | Equipment Failure | 350 | 138.9371 | 48628 | 0.054323 | 0.00039099
2013-06-02 01:44PM | 1622345-1 | WRE2 | Urban | Equipment Failure | 1153 | 39.6366 | 45701 | 0.051053 | 0.001288
2013-01-16 05:27PM | 1585471-1 | WRF2 | Urban | Equipment Failure | 2381 | 11.9996 | 28571 | 0.031917 | 0.0026599
2013-04-18 08:29AM | 1611186-1 | WRF2 | Urban | Equipment Failure | 45 | 95 | 4275 | 0.0047757 | 5.027e-05
2012-07-25 02:23PM | 1540283-1 | WRF2 | Urban | Equipment Failure | 166 | 121.7108 | 20204 | 0.02257 | 0.00018544
2013-01-16 07:57PM | 1585544-1 | WRF2 | Urban | Animals | 1 | 37 | 37 | 4.1333e-05 | 1.1171e-06
2012-12-14 06:31AM | 1577845-1 | WRF2 | Urban | Equipment Failure | 1 | 552 | 552 | 0.00061665 | 1.1171e-06
2013-01-16 05:27PM | 1585471-1 | WRG2 | Urban | Equipment Failure | 353 | 12.0142 | 4241 | 0.0047377 | 0.00039434
2013-02-10 01:38PM | 1593216-1 | R208 | Rural Short | Weather | 1055 | 173.6436 | 183194 | 0.20465 | 0.0011786
2013-06-14 05:07PM | 1625366-1 | R208 | Rural Short | Third Party Impacts | 3 | 32.6667 | 98 | 0.00010948 | 3.3514e-06
2013-03-08 08:22PM | 1602200-1 | R208 | Rural Short | Equipment Failure | 105 | 81 | 8505 | 0.0095011 | 0.0001173
2013-06-21 10:45AM | 1626897-1 | R208 | Rural Short | Vegetation | 683 | 167.7833 | 114596 | 0.12802 | 0.00076299
2012-11-04 04:04PM | 1566990-1 | R208 | Rural Short | Third Party Impacts | 1054 | 75.0161 | 79067 | 0.088327 | 0.0011774
2012-12-24 07:34PM | 1580278-1 | R208 | Rural Short | Third Party Impacts | 3 | 215.6667 | 647 | 0.00072278 | 3.3514e-06
2013-02-10 01:38PM | 1593216-1 | R210 | Rural Short | Weather | 1159 | 173.629 | 201236 | 0.2248 | 0.0012947
2013-02-10 01:38PM | 1593216-1 | R211 | Rural Short | Weather | 1321 | 173.6101 | 229339 | 0.2562 | 0.0014757
2012-09-29 01:37PM | 1558078-1 | R211 | Rural Short | Equipment Failure | 1 | 152 | 152 | 0.0001698 | 1.1171e-06
2012-10-30 04:41PM | 1565827-1 | R211 | Rural Short | Weather | 1 | 170 | 170 | 0.00018991 | 1.1171e-06
2013-04-28 02:37AM | 1613426-1 | R211 | Rural Short | Other | 44 | 85.25 | 3751 | 0.0041903 | 4.9153e-05
2013-06-20 12:03PM | 1626616-1 | R211 | Rural Short | Other | 1 | 95 | 95 | 0.00010613 | 1.1171e-06
2013-01-22 07:40PM | 1592375-1 | R211 | Rural Short | Operatonal Error | 180 | 7 | 1260 | 0.0014076 | 0.00020108
2013-05-28 11:39AM | 1620963-1 | R211 | Rural Short | Equipment Failure | 823 | 21.4666 | 17667 | 0.019736 | 0.00091939
2012-12-27 11:55PM | 1580981-1 | R211 | Rural Short | Equipment Failure | 363 | 57.4325 | 20848 | 0.02329 | 0.00040551
2013-01-20 12:32PM | 1586760-1 | R211 | Rural Short | Vegetation | 1321 | 58.3664 | 77102 | 0.086132 | 0.0014757
2013-05-07 09:49AM | 1615341-1 | R211 | Rural Short | Equipment Failure | 44 | 221 | 9724 | 0.010863 | 4.9153e-05
2013-05-28 11:38PM | 1621206-1 | R211 | Rural Short | Equipment Failure | 823 | 151.3196 | 124536 | 0.13912 | 0.00091939
2012-12-01 05:21PM | 1574696-1 | R211 | Rural Short | Other | 1 | 110 | 110 | 0.00012288 | 1.1171e-06
2012-09-15 11:16AM | 1554801-1 | 3100 | Urban | Equipment Failure | 167 | 40 | 6680 | 0.0074624 | 0.00018656
2013-01-21 10:29AM | 1586902-1 | 35761 | Urban | Equipment Failure | 1 | 541 | 541 | 0.00060436 | 1.1171e-06
2012-11-13 11:00AM | 1569471-1 | 35762 | Urban | Other | 49 | 143 | 7007 | 0.0078277 | 5.4739e-05
2013-06-04 01:15PM | 1622871-1 | 35762 | Urban | Equipment Failure | 1 | 303 | 303 | 0.00033849 | 1.1171e-06
2013-02-10 09:23PM | 1593391-1 | 35762 | Urban | Equipment Failure | 65 | 347 | 22555 | 0.025197 | 7.2613e-05
2012-11-13 11:45AM | 1569480-1 | 35762 | Urban | Other | 1752 | 20 | 35040 | 0.039144 | 0.0019572
2013-01-01 02:15PM | 1581625-1 | 35762 | Urban | Equipment Failure | 9 | 0.55556 | 5 | 5.5856e-06 | 1.0054e-05
2013-02-25 04:01PM | 1598222-1 | 35763 | Urban | Equipment Failure | 13 | 111 | 1443 | 0.001612 | 1.4523e-05
2013-04-16 10:25AM | 1610676-1 | 35763 | Urban | Other | 26 | 102 | 2652 | 0.0029626 | 2.9045e-05
2012-08-14 12:59PM | 1545728-1 | 35763 | Urban | Third Party Impacts | 252 | 90.0079 | 22682 | 0.025339 | 0.00028151
2013-01-15 09:38AM | 1585029-1 | 35763 | Urban | Equipment Failure | 504 | 244.131 | 123042 | 0.13745 | 0.00056303
2013-01-04 10:48AM | 1582287-1 | 35764 | Urban | Other | 2 | 133 | 266 | 0.00029715 | 2.2342e-06
2013-01-02 02:34PM | 1581862-1 | 35764 | Urban | Third Party Impacts | 48 | 41.0417 | 1970 | 0.0022007 | 5.3622e-05
2013-03-06 02:29PM | 1601361-1 | 35764 | Urban | Third Party Impacts | 48 | 111.4375 | 5349 | 0.0059755 | 5.3622e-05
2012-08-25 02:51PM | 1549469-1 | 35765 | Urban | Other | 12 | 111 | 1332 | 0.001488 | 1.3405e-05
2012-11-10 12:06PM | 1568991-1 | 35765 | Urban | Equipment Failure | 21 | 86 | 1806 | 0.0020175 | 2.346e-05
2013-03-29 10:32AM | 1607019-1 | 35765 | Urban | Equipment Failure | 11 | 82 | 902 | 0.0010076 | 1.2288e-05
2012-09-05 03:06PM | 1552087-1 | 35766 | Urban | Other | 79 | 101.8734 | 8048 | 0.0089906 | 8.8252e-05
2012-11-13 12:49PM | 1569535-1 | 35767 | Urban | Other | 45 | 70 | 3150 | 0.0035189 | 5.027e-05
2012-11-13 10:02AM | 1569449-1 | 35767 | Urban | Third Party Impacts | 513 | 124.5419 | 63890 | 0.071373 | 0.00057308
2013-01-13 04:57PM | 1584428-1 | 35767 | Urban | Weather | 509 | 34.7741 | 17700 | 0.019773 | 0.00056861
2013-03-11 01:33PM | 1602621-1 | 35769 | Urban | Other | 18 | 366.9444 | 6605 | 0.0073786 | 2.0108e-05
2012-07-12 06:35PM | 1537465-1 | 35769 | Urban | Third Party Impacts | 7 | 12.2857 | 86 | 9.6072e-05 | 7.8198e-06
2012-08-02 09:08AM | 1542281-1 | 35769 | Urban | Third Party Impacts | 77 | 223.5714 | 17215 | 0.019231 | 8.6018e-05
2013-03-21 07:45PM | 1605303-1 | 35771 | Urban | Third Party Impacts | 119 | 57.9664 | 6898 | 0.0077059 | 0.00013294
2013-06-30 01:12PM | 1629369-1 | 35773 | Urban | Equipment Failure | 6 | 75 | 450 | 0.0005027 | 6.7027e-06
2012-12-11 11:45PM | 1577244-1 | 27201 | Urban | Other | 151 | 1.0993 | 166 | 0.00018544 | 0.00016869
2012-12-12 09:33PM | 1577536-1 | 27201 | Urban | Other | 151 | 1 | 151 | 0.00016869 | 0.00016869
2013-04-25 02:55AM | 1612935-1 | 27201 | Urban | Animals | 258 | 123.9612 | 31982 | 0.035728 | 0.00028822
2012-11-14 12:38PM | 1569803-1 | S328 | Urban | Equipment Failure | 2 | 117 | 234 | 0.00026141 | 2.2342e-06
2012-07-23 04:18PM | 1539795-1 | S334 | Urban | Other | 32 | 206.25 | 6600 | 0.007373 | 3.5748e-05
2013-06-02 10:27AM | 1622291-1 | S334 | Urban | Vegetation | 53 | 30.4906 | 1616 | 0.0018053 | 5.9207e-05
2013-03-20 03:09PM | 1604961-1 | WL1217 | Urban | Weather | 29 | 38 | 1102 | 0.0012311 | 3.2396e-05
2012-09-08 09:16AM | 1553093-1 | WL1217 | Urban | Equipment Failure | 1549 | 53.4661 | 82819 | 0.092519 | 0.0017304
2013-04-05 04:54PM | 1608194-1 | WL1218 | Urban | Equipment Failure | 21 | 115 | 2415 | 0.0026978 | 2.346e-05
2012-11-26 06:15PM | 1572924-1 | WL1218 | Urban | Weather | 621 | 129.8164 | 80616 | 0.090058 | 0.00069373
2013-02-26 09:18AM | 1598509-1 | WL1236 | Urban | Vegetation | 7 | 99 | 693 | 0.00077416 | 7.8198e-06
2012-11-05 01:09PM | 1567231-1 | WL1236 | Urban | Other | 78 | 72 | 5616 | 0.0062737 | 8.7135e-05
2013-03-16 04:25PM | 1604012-1 | WL1236 | Urban | Other | 9 | 217 | 1953 | 0.0021817 | 1.0054e-05
2012-11-08 12:52AM | 1567966-1 | WL1236 | Urban | Other | 26 | 68.3462 | 1777 | 0.0019851 | 2.9045e-05
2013-05-20 12:12PM | 1618735-1 | WL1236 | Urban | Other | 21 | 62 | 1302 | 0.0014545 | 2.346e-05
2013-06-26 07:48AM | 1628150-1 | WL1251 | Urban | Other | 7 | 24 | 168 | 0.00018768 | 7.8198e-06
2013-01-08 01:43PM | 1583222-1 | WL1277 | Urban | Equipment Failure | 1 | 135 | 135 | 0.00015081 | 1.1171e-06
2013-03-17 03:19PM | 1604172-1 | SC1241 | Urban | Other | 434 | 1 | 434 | 0.00048483 | 0.00048483
2012-12-24 05:27PM | 1580205-1 | SC1271 | Urban | Weather | 8 | 48.75 | 390 | 0.00043568 | 8.937e-06
2013-02-09 04:54PM | 1593095-1 | SC1289 | Urban | Equipment Failure | 20 | 115.2 | 2304 | 0.0025738 | 2.2342e-05
2013-01-09 01:05AM | 1583464-1 | SC1289 | Urban | Other | 18 | 30.1667 | 543 | 0.0006066 | 2.0108e-05
2012-12-07 04:44AM | 1576248-1 | SC1289 | Urban | Animals | 134 | 361.5 | 48441 | 0.054114 | 0.00014969
2012-07-25 08:01AM | 1540161-1 | A054 | Urban | Equipment Failure | 63 | 439.7937 | 27707 | 0.030952 | 7.0379e-05
2012-11-10 12:21PM | 1568995-1 | SC1238 | Urban | Other | 1 | 197 | 197 | 0.00022007 | 1.1171e-06
2012-08-24 03:30PM | 1549265-1 | 8610 | Urban | Other | 151 | 48.1391 | 7269 | 0.0081203 | 0.00016869
2012-08-24 08:53PM | 1549371-1 | 8610 | Urban | Other | 1 | 48 | 48 | 5.3622e-05 | 1.1171e-06
2012-08-24 09:12AM | 1549081-1 | 8610 | Urban | Weather | 1571 | 157.7244 | 247785 | 0.27681 | 0.001755
2012-10-04 11:33AM | 1558855-1 | 8614 | Urban | Equipment Failure | 13 | 324 | 4212 | 0.0047053 | 1.4523e-05
2012-08-24 09:30AM | 1549108-1 | 8615 | Urban | Other | 1 | 288 | 288 | 0.00032173 | 1.1171e-06
2012-08-10 04:26PM | 1544937-1 | 8615 | Urban | Weather | 26 | 118.3846 | 3078 | 0.0034385 | 2.9045e-05
2013-01-13 04:46PM | 1584415-1 | 8615 | Urban | Weather | 619 | 105.9596 | 65589 | 0.073271 | 0.0006915
2012-08-10 04:12PM | 1544859-1 | 8617 | Urban | Other | 1 | 477 | 477 | 0.00053287 | 1.1171e-06
2012-07-02 12:38PM | 1534851-1 | 8620 | Urban | Other | 13 | 112 | 1456 | 0.0016265 | 1.4523e-05
2012-08-18 09:05AM | 1547136-1 | 8620 | Urban | Equipment Failure | 16 | 97 | 1552 | 0.0017338 | 1.7874e-05
2012-07-05 08:15PM | 1535962-1 | 8620 | Urban | Equipment Failure | 904 | 65.0719 | 58825 | 0.065715 | 0.0010099
2013-01-16 05:27PM | 1585471-1 | SHA2 | Urban | Equipment Failure | 2046 | 11.999 | 24550 | 0.027425 | 0.0022856
2012-10-05 08:40AM | 1559182-1 | SHA2 | Urban | Equipment Failure | 15 | 285.2667 | 4279 | 0.0047802 | 1.6757e-05
2012-07-08 05:43PM | 1536470-1 | SHA2 | Urban | Equipment Failure | 1 | 2 | 2 | 2.2342e-06 | 1.1171e-06
2012-07-08 05:02PM | 1536449-1 | SHA2 | Urban | Animals | 1194 | 91.5829 | 109350 | 0.12216 | 0.0013338
2013-01-16 05:27PM | 1585471-1 | SHB2 | Urban | Equipment Failure | 1442 | 12.0035 | 17309 | 0.019336 | 0.0016109
2012-07-08 05:02PM | 1536447-1 | SHB2 | Urban | Animals | 1209 | 88.7328 | 107278 | 0.11984 | 0.0013506
2012-07-30 10:55AM | 1541275-1 | SHB2 | Urban | Equipment Failure | 1219 | 67.4307 | 82198 | 0.091825 | 0.0013618
2012-11-19 12:28PM | 1570849-1 | SHB2 | Urban | Equipment Failure | 1103 | 60.7325 | 66988 | 0.074834 | 0.0012322
2013-01-16 05:27PM | 1585471-1 | SHC2 | Urban | Equipment Failure | 1488 | 12.002 | 17859 | 0.019951 | 0.0016623
2012-07-08 05:02PM | 1536448-1 | SHC2 | Urban | Animals | 1045 | 79.8325 | 83425 | 0.093196 | 0.0011674
2012-11-18 08:45AM | 1573553-1 | SHC2 | Urban | Other | 63 | 10 | 630 | 0.00070379 | 7.0379e-05
2013-01-16 05:27PM | 1585471-1 | SHD2 | Urban | Equipment Failure | 1543 | 12.0013 | 18518 | 0.020687 | 0.0017237
2012-08-10 11:12AM | 1544435-1 | SHD2 | Urban | Weather | 39 | 230 | 8970 | 0.010021 | 4.3568e-05
2012-12-29 06:51PM | 1581332-1 | SHD2 | Urban | Equipment Failure | 42 | 260.5476 | 10943 | 0.012225 | 4.6919e-05
2013-03-23 11:36AM | 1605751-1 | SN1230 | Rural Short | Vegetation | 79 | 93.1139 | 7356 | 0.0082175 | 8.8252e-05
2013-06-12 05:27PM | 1624720-1 | SN1230 | Rural Short | Other | 6 | 218 | 1308 | 0.0014612 | 6.7027e-06
2012-08-16 04:49PM | 1546360-1 | SN1230 | Rural Short | Equipment Failure | 2 | 87.5 | 175 | 0.0001955 | 2.2342e-06
2012-10-27 03:46PM | 1565168-1 | SN1230 | Rural Short | Other | 5 | 95 | 475 | 0.00053063 | 5.5856e-06
2013-02-25 08:01AM | 1597873-1 | SN1230 | Rural Short | Weather | 3 | 277 | 831 | 0.00092833 | 3.3514e-06
2013-05-31 08:19PM | 1622176-1 | SN1230 | Rural Short | Other | 7 | 67.1429 | 470 | 0.00052505 | 7.8198e-06
2013-02-03 06:55PM | 1591187-1 | SN1230 | Rural Short | Other | 1 | 95 | 95 | 0.00010613 | 1.1171e-06
2012-12-21 01:39PM | 1581986-1 | SN1252 | Urban | Operatonal Error | 68 | 2.9853 | 203 | 0.00022678 | 7.5964e-05
2013-01-31 08:14AM | 1593570-1 | SN1252 | Urban | Operatonal Error | 68 | 1 | 68 | 7.5964e-05 | 7.5964e-05
2012-12-24 11:17AM | 1580094-1 | 46475 | Rural Short | Vegetation | 6 | 120.5 | 723 | 0.00080768 | 6.7027e-06
2012-09-28 01:52PM | 1557833-1 | 46475 | Rural Short | Weather | 1861 | 0.49973 | 930 | 0.0010389 | 0.002079
2013-01-28 04:34PM | 1589302-1 | 46475 | Rural Short | Equipment Failure | 1218 | 106 | 129108 | 0.14423 | 0.0013607
2013-01-19 06:02AM | 1586542-1 | 46477 | Urban | Equipment Failure | 19 | 121.2632 | 2304 | 0.0025738 | 2.1225e-05
2012-11-30 06:25PM | 1574433-1 | 46477 | Urban | Weather | 16 | 73.5625 | 1177 | 0.0013149 | 1.7874e-05
2013-05-26 01:53PM | 1620262-1 | 46481 | Urban | Third Party Impacts | 47 | 207.5957 | 9757 | 0.0109 | 5.2505e-05
2012-10-06 08:38AM | 1559422-1 | 46481 | Urban | Equipment Failure | 1 | 227 | 227 | 0.00025359 | 1.1171e-06
2012-08-11 07:52PM | 1545136-1 | 46485 | Urban | Other | 1 | 159 | 159 | 0.00017762 | 1.1171e-06
2012-10-05 03:36PM | 1559358-1 | 46487 | Rural Short | Other | 28 | 148.3929 | 4155 | 0.0046416 | 3.1279e-05
2012-11-05 07:22PM | 1567344-1 | 46487 | Rural Short | Third Party Impacts | 11 | 141 | 1551 | 0.0017327 | 1.2288e-05
2012-12-16 01:28PM | 1578311-1 | 46487 | Rural Short | Other | 3 | 59 | 177 | 0.00019773 | 3.3514e-06
2013-03-13 10:20AM | 1603105-1 | SZ1132 | Rural Short | Equipment Failure | 12 | 333 | 3996 | 0.004464 | 1.3405e-05
2013-03-13 07:59AM | 1603048-1 | SZ1132 | Rural Short | Animals | 342 | 225.9181 | 77264 | 0.086313 | 0.00038206
2013-04-16 05:53AM | 1610570-1 | SZ1132 | Rural Short | Equipment Failure | 342 | 123.4649 | 42225 | 0.04717 | 0.00038206
2013-04-22 07:17AM | 1611894-1 | SZ1132 | Rural Short | Equipment Failure | 342 | 147.193 | 50340 | 0.056236 | 0.00038206
2013-03-16 09:01AM | 1603946-1 | SZ1132 | Rural Short | Third Party Impacts | 9 | 265 | 2385 | 0.0026643 | 1.0054e-05
2013-04-29 01:58PM | 1613657-1 | SZ1142 | Rural Short | Equipment Failure | 26 | 115 | 2990 | 0.0033402 | 2.9045e-05
2013-02-02 03:20PM | 1593914-1 | SZ1142 | Rural Short | Operatonal Error | 218 | 5 | 1090 | 0.0012177 | 0.00024353
2013-06-20 02:05PM | 1626653-1 | SZ1152 | Urban | Third Party Impacts | 19 | 85 | 1615 | 0.0018041 | 2.1225e-05
2013-06-27 12:01PM | 1628634-1 | SZ1242 | Urban | Equipment Failure | 1 | 14950 | 14950 | 0.016701 | 1.1171e-06
2013-02-18 04:25PM | 1595235-1 | SZ1242 | Urban | Weather | 6 | 370 | 2220 | 0.00248 | 6.7027e-06
2013-01-14 09:45AM | 1584676-1 | SZ1242 | Urban | Third Party Impacts | 2 | 93 | 186 | 0.00020778 | 2.2342e-06
2012-10-04 02:36PM | 1558992-1 | SZ1242 | Urban | Vegetation | 120 | 190 | 22800 | 0.02547 | 0.00013405
2013-06-26 02:30PM | 1628518-1 | SZ1242 | Urban | Other | 1 | 2420 | 2420 | 0.0027034 | 1.1171e-06
2012-10-07 01:45PM | 1559536-1 | SZ1252 | Rural Short | Vegetation | 10 | 170.1 | 1701 | 0.0019002 | 1.1171e-05
2013-06-13 06:40PM | 1625097-1 | 35695 | Rural Short | Equipment Failure | 1 | 83 | 83 | 9.2721e-05 | 1.1171e-06
2013-01-22 03:48PM | 1587348-1 | 35695 | Rural Short | Weather | 20 | 79 | 1580 | 0.001765 | 2.2342e-05
2012-08-17 05:18PM | 1547039-1 | 35695 | Rural Short | Weather | 396 | 104.7348 | 41475 | 0.046333 | 0.00044238
2013-01-27 05:55AM | 1588991-1 | 35695 | Rural Short | Vegetation | 363 | 35.416 | 12856 | 0.014362 | 0.00040551
2013-04-19 12:49AM | 1611432-1 | 35695 | Rural Short | Vegetation | 75 | 115.6 | 8670 | 0.0096854 | 8.3784e-05
2012-10-16 01:15PM | 1562188-1 | 35695 | Rural Short | Equipment Failure | 1 | 231 | 231 | 0.00025805 | 1.1171e-06
2012-08-01 04:03PM | 1542120-1 | 35696 | Urban | Equipment Failure | 27 | 22.0741 | 596 | 0.0006658 | 3.0162e-05
2012-07-17 02:35PM | 1538409-1 | 35701 | Urban | Equipment Failure | 1 | 245 | 245 | 0.00027369 | 1.1171e-06
2013-05-16 12:54PM | 1617865-1 | 35701 | Urban | Equipment Failure | 1 | 295 | 295 | 0.00032955 | 1.1171e-06
2012-08-17 02:11PM | 1546805-1 | 35701 | Urban | Weather | 12 | 204.8333 | 2458 | 0.0027459 | 1.3405e-05
2012-11-25 08:53PM | 1572545-1 | 35701 | Urban | Equipment Failure | 1826 | 57.9168 | 105756 | 0.11814 | 0.0020399
2012-11-16 09:45AM | 1570298-1 | 35701 | Urban | Vegetation | 293 | 43 | 12599 | 0.014075 | 0.00032732
2012-12-05 07:21AM | 1575616-1 | 35701 | Urban | Vegetation | 175 | 143 | 25025 | 0.027956 | 0.0001955
2012-09-06 07:07PM | 1552506-1 | 35702 | Urban | Other | 1 | 152 | 152 | 0.0001698 | 1.1171e-06
2012-08-17 05:18PM | 1547040-1 | 35702 | Urban | Weather | 860 | 115.3 | 99158 | 0.11077 | 0.00096072
2012-12-05 10:01AM | 1575638-1 | 35702 | Urban | Vegetation | 860 | 153.9128 | 132365 | 0.14787 | 0.00096072
2013-06-02 10:50AM | 1625219-1 | 5499 | Urban | Weather | 2 | 8.5 | 17 | 1.8991e-05 | 2.2342e-06
2013-05-15 04:30PM | 1617638-1 | 5500 | Urban | Other | 76 | 26.7763 | 2035 | 0.0022733 | 8.4901e-05
2013-05-17 05:29PM | 1618368-1 | 5500 | Urban | Operatonal Error | 15 | 94 | 1410 | 0.0015751 | 1.6757e-05
2013-06-02 10:50AM | 1625219-1 | 5500 | Urban | Weather | 595 | 10.6084 | 6312 | 0.0070513 | 0.00066469
2013-01-03 07:47AM | 1581949-1 | 5500 | Urban | Equipment Failure | 16 | 441.25 | 7060 | 0.0078869 | 1.7874e-05
2013-06-12 04:36AM | 1624441-1 | 5501 | Rural Short | Equipment Failure | 3 | 67.6667 | 203 | 0.00022678 | 3.3514e-06
2013-01-28 02:29PM | 1589280-1 | 5501 | Rural Short | Other | 987 | 87 | 85869 | 0.095926 | 0.0011026
2013-05-30 04:40AM | 1621494-1 | 5501 | Rural Short | Equipment Failure | 16 | 395 | 6320 | 0.0070602 | 1.7874e-05
2013-02-10 11:32PM | 1593392-1 | 35825 | Rural Short | Vegetation | 416 | 77.7332 | 32337 | 0.036124 | 0.00046472
2013-05-21 08:55AM | 1618958-1 | 35825 | Rural Short | Equipment Failure | 8 | 231.25 | 1850 | 0.0020667 | 8.937e-06
2012-09-28 05:24PM | 1557949-1 | 35827 | Rural Short | Other | 1 | 82 | 82 | 9.1604e-05 | 1.1171e-06
2012-10-16 02:58AM | 1561999-1 | 35827 | Rural Short | Other | 16 | 152 | 2432 | 0.0027168 | 1.7874e-05
2013-01-24 08:37AM | 1587860-1 | 35827 | Rural Short | Equipment Failure | 6 | 140.3333 | 842 | 0.00094062 | 6.7027e-06
2012-09-28 03:45PM | 1557915-1 | 35827 | Rural Short | Vegetation | 152 | 108.0658 | 16426 | 0.01835 | 0.0001698
2012-09-05 02:27PM | 1556153-1 | 35827 | Rural Short | Third Party Impacts | 152 | 17.0395 | 2590 | 0.0028933 | 0.0001698
2012-10-06 06:02PM | 1562436-1 | 845 | Rural Short | Weather | 1 | 54 | 54 | 6.0324e-05 | 1.1171e-06
2013-05-25 11:00AM | 1620355-1 | OA1207 | Rural Short | Equipment Failure | 1 | 285 | 285 | 0.00031838 | 1.1171e-06
2013-06-29 10:29AM | 1629215-1 | OA1207 | Rural Short | Other | 2 | 124 | 248 | 0.00027705 | 2.2342e-06
2013-05-15 03:30PM | 1617581-1 | OA1207 | Rural Short | Vegetation | 45 | 90 | 4050 | 0.0045243 | 5.027e-05
2013-06-30 11:33AM | 1629350-1 | OA1233 | Rural Short | Equipment Failure | 4 | 68 | 272 | 0.00030386 | 4.4685e-06
2013-06-30 03:16PM | 1629390-1 | OA1233 | Rural Short | Equipment Failure | 4 | 71 | 284 | 0.00031726 | 4.4685e-06
2012-10-27 07:08AM | 1565123-1 | ULC2 | Rural Short | Animals | 55 | 76 | 4180 | 0.0046696 | 6.1442e-05
2012-09-07 04:07PM | 1552920-1 | ULC2 | Rural Short | Weather | 5 | 68 | 340 | 0.00037982 | 5.5856e-06
2013-01-22 05:21PM | 1587405-1 | ULC2 | Rural Short | Weather | 2726 | 64.5994 | 176098 | 0.19672 | 0.0030453
2013-01-31 03:58PM | 1590369-1 | ULC2 | Rural Short | Vegetation | 2655 | 17 | 45135 | 0.050421 | 0.002966
2012-12-26 02:15PM | 1580684-1 | ULD2 | Urban | Equipment Failure | 57 | 172.386 | 9826 | 0.010977 | 6.3676e-05
2012-09-03 12:49PM | 1551398-1 | ULD2 | Urban | Other | 57 | 58 | 3306 | 0.0036932 | 6.3676e-05
2012-08-10 10:51AM | 1544417-1 | ULE2 | Rural Short | Weather | 465 | 11 | 5115 | 0.0057141 | 0.00051946
2013-06-25 01:13PM | 1627906-1 | ULE2 | Rural Short | Weather | 18 | 56.4444 | 1016 | 0.001135 | 2.0108e-05
2012-11-07 02:20AM | 1567661-1 | ULE2 | Rural Short | Equipment Failure | 147 | 243.1973 | 35750 | 0.039937 | 0.00016422
2012-09-28 03:09PM | 1557894-1 | ULE2 | Rural Short | Other | 242 | 2.0331 | 492 | 0.00054962 | 0.00027034
2013-02-25 07:37AM | 1597847-1 | ULE2 | Rural Short | Weather | 2 | 344 | 688 | 0.00076858 | 2.2342e-06
2012-08-31 01:13PM | 1550967-1 | ULE2 | Rural Short | Weather | 1146 | 79.5428 | 91156 | 0.10183 | 0.0012802
2013-01-16 05:27PM | 1585471-1 | WRB2 | Urban | Equipment Failure | 1725 | 12.0012 | 20702 | 0.023127 | 0.001927
2012-11-26 07:00PM | 1572937-1 | WRB2 | Urban | Equipment Failure | 41 | 27.7317 | 1137 | 0.0012702 | 4.5802e-05
2013-03-02 08:05PM | 1600248-1 | WRB2 | Urban | Equipment Failure | 31 | 10.3548 | 321 | 0.0003586 | 3.4631e-05
2012-08-01 01:58PM | 1542059-1 | WRB2 | Urban | Equipment Failure | 776 | 45.2822 | 35139 | 0.039254 | 0.00086689
2012-08-01 02:39PM | 1542087-1 | WRB2 | Urban | Equipment Failure | 539 | 2.0501 | 1105 | 0.0012344 | 0.00060213
2012-12-14 10:11AM | 1577891-1 | WRB2 | Urban | Equipment Failure | 141 | 135.2057 | 19064 | 0.021297 | 0.00015751
2013-01-27 08:25AM | 1589047-1 | WRB2 | Urban | Equipment Failure | 99 | 18.9697 | 1878 | 0.002098 | 0.00011059
2012-11-21 12:40PM | 1571601-1 | WRB2 | Urban | Other | 1 | 116 | 116 | 0.00012959 | 1.1171e-06
2013-04-05 01:50PM | 1611455-1 | 35773 | Urban | Third Party Impacts | 2 | 30 | 60 | 6.7027e-05 | 2.2342e-06
2013-02-06 08:32PM | 1592264-1 | 41533 | Rural Short | Animals | 1 | 138 | 138 | 0.00015416 | 1.1171e-06
2012-12-25 07:59AM | 1580422-1 | 41533 | Rural Short | Weather | 9 | 76 | 684 | 0.00076411 | 1.0054e-05
2012-11-28 07:11AM | 1573413-1 | 41533 | Rural Short | Weather | 16 | 293.1875 | 4691 | 0.0052404 | 1.7874e-05
2012-08-17 12:16PM | 1546584-1 | 41533 | Rural Short | Weather | 72 | 58.9583 | 4245 | 0.0047422 | 8.0433e-05
2012-12-28 06:39AM | 1580999-1 | 41533 | Rural Short | Equipment Failure | 47 | 112.6383 | 5294 | 0.005914 | 5.2505e-05
2013-06-26 01:16PM | 1628326-1 | 41533 | Rural Short | Equipment Failure | 17 | 70 | 1190 | 0.0013294 | 1.8991e-05
2012-08-09 10:04AM | 1544062-1 | 41535 | Urban | Vegetation | 71 | 35.7887 | 2541 | 0.0028386 | 7.9316e-05
2013-02-25 06:50PM | 1598380-1 | 41535 | Urban | Weather | 62 | 150 | 9300 | 0.010389 | 6.9261e-05
2013-01-27 01:33PM | 1589129-1 | 41535 | Urban | Other | 19 | 68 | 1292 | 0.0014433 | 2.1225e-05
2013-05-13 07:57PM | 1617033-1 | 41535 | Urban | Equipment Failure | 43 | 129.2791 | 5559 | 0.0062101 | 4.8036e-05
2012-08-24 06:53AM | 1549023-1 | 41537 | Urban | Weather | 1 | 123 | 123 | 0.00013741 | 1.1171e-06
2013-01-28 09:27PM | 1589404-1 | 41537 | Urban | Other | 48 | 113 | 5424 | 0.0060593 | 5.3622e-05
2013-01-23 09:53AM | 1587630-1 | 41537 | Urban | Other | 27 | 114 | 3078 | 0.0034385 | 3.0162e-05
2013-06-17 09:13AM | 1625671-1 | 41537 | Urban | Other | 22 | 77.7273 | 1710 | 0.0019103 | 2.4577e-05
2012-08-06 01:02PM | 1543151-1 | 41537 | Urban | Third Party Impacts | 1198 | 82.6828 | 99054 | 0.11066 | 0.0013383
2013-06-23 11:01PM | 1627368-1 | 27187 | Urban | Equipment Failure | 1 | 100 | 100 | 0.00011171 | 1.1171e-06
2012-10-22 03:52PM | 1563679-1 | 27187 | Urban | Weather | 602 | 81.2658 | 48922 | 0.054652 | 0.00067251
2012-09-21 03:40PM | 1556298-1 | 27191 | Urban | Other | 16 | 50.9375 | 815 | 0.00091045 | 1.7874e-05
2012-10-20 08:39AM | 1563242-1 | 27191 | Urban | Animals | 2 | 178 | 356 | 0.00039769 | 2.2342e-06
2012-10-22 03:52PM | 1563678-1 | 27191 | Urban | Weather | 989 | 80.8665 | 79977 | 0.089344 | 0.0011048
2013-02-08 04:49PM | 1592870-1 | 27191 | Urban | Weather | 1031 | 8.3327 | 8591 | 0.0095972 | 0.0011518
2013-02-12 11:02AM | 1593797-1 | 27191 | Urban | Operatonal Error | 158 | 6 | 948 | 0.001059 | 0.0001765
2012-10-29 11:57AM | 1565411-1 | 27194 | Urban | Equipment Failure | 3 | 42 | 126 | 0.00014076 | 3.3514e-06
2012-10-24 01:35PM | 1564264-1 | 27194 | Urban | Equipment Failure | 22 | 444.6364 | 9782 | 0.010928 | 2.4577e-05
2012-08-22 12:14PM | 1548061-1 | 27194 | Urban | Other | 6 | 199 | 1194 | 0.0013338 | 6.7027e-06
2012-08-11 09:33AM | 1545043-1 | X871 | Urban | Weather | 38 | 29.5526 | 1123 | 0.0012545 | 4.2451e-05
2012-07-01 10:46AM | 1534618-1 | X871 | Urban | Vegetation | 822 | 35 | 28770 | 0.03214 | 0.00091827
2012-11-07 06:20PM | 1567925-1 | WX1210 | Urban | Equipment Failure | 44 | 30.5 | 1342 | 0.0014992 | 4.9153e-05
2013-06-25 11:06AM | 1627820-1 | WX1228 | Urban | Weather | 6 | 255.6667 | 1534 | 0.0017137 | 6.7027e-06
2012-07-16 12:16AM | 1537938-1 | WX1244 | Urban | Other | 16 | 738.25 | 11812 | 0.013195 | 1.7874e-05
2013-01-18 12:50PM | 1586011-1 | WX1244 | Urban | Equipment Failure | 4 | 72.5 | 290 | 0.00032396 | 4.4685e-06
2013-02-11 01:44PM | 1593581-1 | WX1244 | Urban | Equipment Failure | 4 | 60 | 240 | 0.00026811 | 4.4685e-06
2012-07-27 03:46AM | 1540714-1 | WX1244 | Urban | Equipment Failure | 16 | 262.3125 | 4197 | 0.0046886 | 1.7874e-05
2013-06-27 10:19AM | 1628606-1 | WX1244 | Urban | Equipment Failure | 9 | 10 | 90 | 0.00010054 | 1.0054e-05
2012-10-26 06:31AM | 1564828-1 | WX1244 | Urban | Equipment Failure | 4 | 128.25 | 513 | 0.00057308 | 4.4685e-06
2013-01-14 11:03AM | 1584702-1 | WX1254 | Urban | Equipment Failure | 58 | 240.8276 | 13968 | 0.015604 | 6.4793e-05
2013-03-26 02:05PM | 1606364-1 | WX1258 | Urban | Other | 12 | 134.4167 | 1613 | 0.0018019 | 1.3405e-05
2013-04-11 08:01PM | 1609763-1 | WX1258 | Urban | Equipment Failure | 12 | 313 | 3756 | 0.0041959 | 1.3405e-05
2012-11-16 04:45PM | 1570457-1 | WX1258 | Urban | Other | 7 | 101 | 707 | 0.0007898 | 7.8198e-06
2012-12-15 06:00AM | 1578110-1 | WX1258 | Urban | Equipment Failure | 961 | 249.6015 | 239867 | 0.26796 | 0.0010736
2012-12-15 11:19AM | 1578149-1 | WX1258 | Urban | Other | 1 | 174 | 174 | 0.00019438 | 1.1171e-06
2012-11-16 07:25PM | 1570480-1 | WX1258 | Urban | Equipment Failure | 1 | 125 | 125 | 0.00013964 | 1.1171e-06
2013-04-21 06:19PM | 1611853-1 | WX1280 | Urban | Other | 22 | 65 | 1430 | 0.0015975 | 2.4577e-05
2012-12-05 04:15PM | 1575883-1 | WWB2 | Urban | Other | 10 | 82 | 820 | 0.00091604 | 1.1171e-05
2013-05-16 07:44PM | 1618072-1 | WWB2 | Urban | Animals | 29 | 144 | 4176 | 0.0046651 | 3.2396e-05
2013-01-07 09:25PM | 1583024-1 | WWB2 | Urban | Animals | 29 | 46.4483 | 1347 | 0.0015048 | 3.2396e-05
2013-06-10 07:45PM | 1624159-1 | WWB2 | Urban | Equipment Failure | 110 | 10.6364 | 1170 | 0.001307 | 0.00012288
2012-07-11 10:07AM | 1537025-1 | WWB2 | Urban | Animals | 1777 | 69.0287 | 122664 | 0.13703 | 0.0019851
2012-07-16 02:40AM | 1537940-1 | WWB2 | Urban | Vegetation | 1777 | 143.6331 | 255236 | 0.28513 | 0.0019851
2012-08-08 11:44PM | 1543922-1 | WWB2 | Urban | Animals | 1803 | 124.2795 | 224076 | 0.25032 | 0.0020142
2012-11-04 05:42PM | 1567000-1 | WWC2 | Urban | Other | 32 | 72 | 2304 | 0.0025738 | 3.5748e-05
2013-02-27 05:06PM | 1599131-1 | WWD2 | Urban | Other | 36 | 37 | 1332 | 0.001488 | 4.0216e-05
2013-06-22 05:40PM | 1627149-1 | WWE2 | Urban | Equipment Failure | 35 | 74 | 2590 | 0.0028933 | 3.9099e-05
2012-07-20 03:02PM | 1539327-1 | WWE2 | Urban | Third Party Impacts | 112 | 142.5089 | 15961 | 0.01783 | 0.00012512
2013-01-12 04:09AM | 1584226-1 | WWE2 | Urban | Equipment Failure | 2105 | 8 | 16840 | 0.018812 | 0.0023515
2013-01-23 10:14AM | 1587642-1 | WWE2 | Urban | Equipment Failure | 114 | 44 | 5016 | 0.0056035 | 0.00012735
2012-09-01 11:23PM | 1551215-1 | WWF2 | Urban | Equipment Failure | 124 | 62 | 7688 | 0.0085884 | 0.00013852
2013-01-16 02:55AM | 1585273-1 | WWF2 | Urban | Other | 7 | 153 | 1071 | 0.0011964 | 7.8198e-06
2012-08-04 11:28AM | 1542893-1 | WWF2 | Urban | Equipment Failure | 22 | 163.6364 | 3600 | 0.0040216 | 2.4577e-05
2013-01-14 12:28AM | 1584605-1 | WWF2 | Urban | Equipment Failure | 25 | 143.8 | 3595 | 0.004016 | 2.7928e-05
2013-01-12 04:09AM | 1584225-1 | WWF2 | Urban | Equipment Failure | 2166 | 8 | 17328 | 0.019357 | 0.0024197
2013-06-27 09:47AM | 1628594-1 | B762 | Urban | Third Party Impacts | 1 | 718 | 718 | 0.00080209 | 1.1171e-06
2013-03-11 06:54AM | 1602464-1 | WQ1208 | Urban | Other | 4 | 138.5 | 554 | 0.00061888 | 4.4685e-06
2012-11-15 12:44PM | 1570084-1 | WQ1208 | Urban | Equipment Failure | 5 | 200.2 | 1001 | 0.0011182 | 5.5856e-06
2013-05-23 01:55PM | 1619756-1 | WQ1212 | Urban | Equipment Failure | 19 | 185 | 3515 | 0.0039267 | 2.1225e-05
2013-02-21 09:57AM | 1596008-1 | WQ1227 | Urban | Third Party Impacts | 26 | 168 | 4368 | 0.0048796 | 2.9045e-05
2013-03-27 07:43PM | 1606758-1 | WQ1249 | Urban | Other | 1 | 26 | 26 | 2.9045e-05 | 1.1171e-06
2013-06-24 01:02PM | 1627498-1 | WQ1249 | Urban | Equipment Failure | 1 | 217 | 217 | 0.00024242 | 1.1171e-06
2013-02-21 09:01AM | 1601169-1 | WQ1249 | Urban | Operatonal Error | 530 | 14.9642 | 7931 | 0.0088599 | 0.00059207
2013-01-25 07:34PM | 1588827-1 | WQ1249 | Urban | Equipment Failure | 1 | 117 | 117 | 0.0001307 | 1.1171e-06
2012-11-16 09:03AM | 1570287-1 | WQ1260 | Urban | Equipment Failure | 7 | 568 | 3976 | 0.0044417 | 7.8198e-06
2013-01-14 01:02AM | 1584610-1 | WQ1260 | Urban | Equipment Failure | 125 | 173.304 | 21663 | 0.0242 | 0.00013964
2013-05-21 09:58PM | 1619187-1 | WQ1264 | Urban | Equipment Failure | 14 | 197 | 2758 | 0.003081 | 1.564e-05
2013-02-21 09:01AM | 1601169-1 | WQ1275 | Urban | Operatonal Error | 29 | 14.8621 | 431 | 0.00048148 | 3.2396e-05
2013-02-21 09:01AM | 1601169-1 | WQ1286 | Urban | Operatonal Error | 32 | 14.8438 | 475 | 0.00053063 | 3.5748e-05
2013-02-08 01:23AM | 1592646-1 | WH1213 | Urban | Equipment Failure | 140 | 1.8786 | 263 | 0.0002938 | 0.0001564
2013-02-07 10:00PM | 1592638-1 | WH1220 | Urban | Equipment Failure | 186 | 155.2097 | 28869 | 0.03225 | 0.00020778
2013-05-06 04:39AM | 1615049-1 | WH1220 | Urban | Equipment Failure | 186 | 63.5699 | 11824 | 0.013209 | 0.00020778
2012-10-19 05:46PM | 1563201-1 | WH1224 | Urban | Other | 3 | 166.6667 | 500 | 0.00055856 | 3.3514e-06
2013-02-22 02:40AM | 1596283-1 | WH1224 | Urban | Equipment Failure | 974 | 46.4979 | 45289 | 0.050593 | 0.0010881
2012-09-07 05:26PM | 1552956-1 | WH1261 | Urban | Weather | 1 | 134 | 134 | 0.00014969 | 1.1171e-06
2012-10-16 08:29PM | 1562338-1 | WH1276 | Urban | Equipment Failure | 63 | 84.4444 | 5320 | 0.0059431 | 7.0379e-05
2013-05-09 10:15PM | 1616211-1 | WH1294 | Urban | Other | 80 | 82.275 | 6582 | 0.0073529 | 8.937e-05
2012-08-24 07:21AM | 1549034-1 | WH1294 | Urban | Weather | 44 | 49 | 2156 | 0.0024085 | 4.9153e-05
2013-02-25 05:01PM | 1598264-1 | WH1294 | Urban | Other | 1843 | 95.1449 | 175352 | 0.19589 | 0.0020589
2013-01-13 06:37PM | 1584489-1 | WH1298 | Urban | Weather | 162 | 20.0062 | 3241 | 0.0036206 | 0.00018097
2013-01-14 03:47PM | 1584834-1 | WH1298 | Urban | Weather | 114 | 66.0789 | 7533 | 0.0084153 | 0.00012735
2013-03-18 06:10AM | 1604261-1 | WH1298 | Urban | Equipment Failure | 1 | 443 | 443 | 0.00049488 | 1.1171e-06
2012-09-22 03:42PM | 1556489-1 | 4353 | Rural Short | Other | 1 | 63 | 63 | 7.0379e-05 | 1.1171e-06
2013-04-04 12:50PM | 1607824-1 | 4354 | Urban | Equipment Failure | 399 | 76 | 30324 | 0.033876 | 0.00044573
2013-01-08 07:26PM | 1583374-1 | 4354 | Urban | Weather | 79 | 112 | 8848 | 0.0098843 | 8.8252e-05
2013-05-07 12:32PM | 1615401-1 | 4354 | Urban | Other | 701 | 68.5478 | 48052 | 0.05368 | 0.0007831
2012-12-19 12:11PM | 1579035-1 | 4359 | Rural Short | Animals | 3 | 312.3333 | 937 | 0.0010467 | 3.3514e-06
2012-08-30 12:09PM | 1550641-1 | 4360 | Rural Short | Third Party Impacts | 499 | 100.6513 | 50225 | 0.056107 | 0.00055744
2012-08-30 06:35PM | 1550818-1 | 4360 | Rural Short | Equipment Failure | 380 | 13.3 | 5054 | 0.0056459 | 0.00042451
2013-05-07 12:32PM | 1615401-1 | 25401 | Rural Short | Other | 471 | 68.4777 | 32253 | 0.03603 | 0.00052616
2012-09-28 09:49PM | 1557993-1 | 25401 | Rural Short | Weather | 2 | 172 | 344 | 0.00038429 | 2.2342e-06
2012-11-30 06:01PM | 1574411-1 | 25401 | Rural Short | Weather | 404 | 106.8317 | 43160 | 0.048215 | 0.00045132
2012-11-30 09:22PM | 1574503-1 | 25401 | Rural Short | Weather | 1 | 231 | 231 | 0.00025805 | 1.1171e-06
2013-02-08 06:55PM | 1592944-1 | 25403 | Rural Short | Other | 21 | 94.4762 | 1984 | 0.0022164 | 2.346e-05
2013-05-07 12:32PM | 1615401-1 | 25403 | Rural Short | Other | 638 | 68.5846 | 43757 | 0.048882 | 0.00071272
2013-02-07 09:30AM | 1592376-1 | 25403 | Rural Short | Third Party Impacts | 39 | 74.1282 | 2891 | 0.0032296 | 4.3568e-05
2013-04-11 01:54PM | 1609605-1 | 25403 | Rural Short | Third Party Impacts | 6 | 71 | 426 | 0.00047589 | 6.7027e-06
2013-06-26 02:56PM | 1631470-1 | 25403 | Rural Short | Other | 1 | 2417 | 2417 | 0.0027001 | 1.1171e-06
2012-12-27 11:17AM | 1580839-1 | WD1210 | Rural Short | Weather | 4 | 125 | 500 | 0.00055856 | 4.4685e-06
2012-12-26 06:08PM | 1580704-1 | WD1210 | Rural Short | Equipment Failure | 5 | 412 | 2060 | 0.0023013 | 5.5856e-06
2013-01-06 10:30AM | 1582702-1 | WD1210 | Rural Short | Equipment Failure | 1 | 223 | 223 | 0.00024912 | 1.1171e-06
2013-01-28 09:01PM | 1589386-1 | WD1210 | Rural Short | Equipment Failure | 281 | 51.4413 | 14455 | 0.016148 | 0.00031391
2012-12-26 07:39PM | 1583277-1 | WD1210 | Rural Short | Other | 87 | 6 | 522 | 0.00058314 | 9.7189e-05
2013-02-11 01:44PM | 1593582-1 | WD1221 | Rural Short | Other | 3 | 61 | 183 | 0.00020443 | 3.3514e-06
2012-12-12 07:34AM | 1577290-1 | WD1221 | Rural Short | Other | 9 | 122 | 1098 | 0.0012266 | 1.0054e-05
2013-01-08 10:48AM | 1583177-1 | WD1221 | Rural Short | Other | 9 | 227 | 2043 | 0.0022823 | 1.0054e-05
2012-12-05 08:14AM | 1575591-1 | WD1221 | Rural Short | Other | 1 | 205 | 205 | 0.00022901 | 1.1171e-06
2013-01-28 09:01PM | 1589386-1 | WD1221 | Rural Short | Equipment Failure | 525 | 51.539 | 27058 | 0.030227 | 0.00058649
2013-06-26 02:10PM | 1628364-1 | WD1221 | Rural Short | Other | 4 | 2433.25 | 9733 | 0.010873 | 4.4685e-06
2013-01-28 09:01PM | 1589386-1 | WD1251 | Rural Short | Equipment Failure | 583 | 51.53 | 30042 | 0.033561 | 0.00065128
2013-01-14 09:48PM | 1584955-1 | WD1251 | Rural Short | Third Party Impacts | 238 | 180.1723 | 42881 | 0.047903 | 0.00026587
2012-11-26 03:52PM | 1572790-1 | WD1251 | Rural Short | Weather | 580 | 41.05 | 23809 | 0.026598 | 0.00064793
2013-01-15 09:10AM | 1585025-1 | WD1251 | Rural Short | Equipment Failure | 236 | 170 | 40120 | 0.044819 | 0.00026364
2012-12-11 04:18PM | 1577130-1 | WD1284 | Rural Short | Animals | 1 | 211 | 211 | 0.00023571 | 1.1171e-06
2013-06-26 02:30PM | 1631463-1 | WD1284 | Rural Short | Other | 1 | 2423 | 2423 | 0.0027068 | 1.1171e-06
2013-01-28 09:01PM | 1589386-1 | WD1284 | Rural Short | Equipment Failure | 230 | 51.4435 | 11832 | 0.013218 | 0.00025694
2012-10-27 05:30PM | 1565172-1 | WD1284 | Rural Short | Equipment Failure | 6 | 135 | 810 | 0.00090487 | 6.7027e-06
2013-01-08 10:14PM | 1583436-1 | WD1284 | Rural Short | Equipment Failure | 1 | 40 | 40 | 4.4685e-05 | 1.1171e-06
2013-01-28 09:01PM | 1589386-1 | WD1288 | Rural Short | Equipment Failure | 94 | 51.4468 | 4836 | 0.0054024 | 0.00010501
2012-11-30 06:10PM | 1577093-1 | 35418 | Rural Short | Weather | 331 | 455.6586 | 150823 | 0.16849 | 0.00036977
2013-03-04 06:45PM | 1600735-1 | 35418 | Rural Short | Equipment Failure | 2 | 248.5 | 497 | 0.00055521 | 2.2342e-06
2013-03-12 05:13PM | 1602958-1 | 35418 | Rural Short | Other | 2 | 232 | 464 | 0.00051834 | 2.2342e-06
2012-12-01 11:21AM | 1574627-1 | 35418 | Rural Short | Weather | 69 | 412 | 28428 | 0.031757 | 7.7081e-05
2012-12-03 05:47PM | 1575103-1 | 35418 | Rural Short | Vegetation | 69 | 377.8841 | 26074 | 0.029128 | 7.7081e-05
2013-05-18 11:53PM | 1618560-1 | 35418 | Rural Short | Other | 70 | 123 | 8610 | 0.0096184 | 7.8198e-05
2012-08-21 02:07PM | 1547769-1 | 35418 | Rural Short | Equipment Failure | 606 | 152.7277 | 92553 | 0.10339 | 0.00067697
2012-12-01 04:14PM | 1574683-1 | 35418 | Rural Short | Other | 99 | 115 | 11385 | 0.012718 | 0.00011059
2013-06-02 01:12PM | 1622327-1 | 35418 | Rural Short | Vegetation | 334 | 130.9311 | 43731 | 0.048853 | 0.00037312
2013-06-03 09:11AM | 1622439-1 | 35418 | Rural Short | Vegetation | 2 | 240.5 | 481 | 0.00053733 | 2.2342e-06
2012-11-30 06:10PM | 1577093-1 | D810 | Rural Short | Weather | 201 | 456.5473 | 91766 | 0.10251 | 0.00022454
2012-12-03 02:33PM | 1575054-1 | D810 | Rural Short | Other | 1 | 137 | 137 | 0.00015305 | 1.1171e-06
2012-09-19 12:35PM | 1555714-1 | D810 | Rural Short | Other | 2 | 139 | 278 | 0.00031056 | 2.2342e-06
2012-07-27 02:00PM | 1540911-1 | D810 | Rural Short | Vegetation | 3 | 164 | 492 | 0.00054962 | 3.3514e-06
2012-09-18 05:29PM | 1555504-1 | D810 | Rural Short | Weather | 19 | 542.2105 | 10302 | 0.011509 | 2.1225e-05
2012-11-30 06:10PM | 1577093-1 | D813 | Rural Short | Weather | 305 | 455.7738 | 139011 | 0.15529 | 0.00034072
2012-12-25 10:13AM | 1580446-1 | D813 | Rural Short | Weather | 6 | 30 | 180 | 0.00020108 | 6.7027e-06
2012-09-07 02:34PM | 1552821-1 | D813 | Rural Short | Weather | 25 | 54 | 1350 | 0.0015081 | 2.7928e-05
2013-04-19 03:08PM | 1611594-1 | D813 | Rural Short | Vegetation | 159 | 162.3711 | 25817 | 0.028841 | 0.00017762
2013-06-02 11:06AM | 1622303-1 | D813 | Rural Short | Vegetation | 159 | 133.6289 | 21247 | 0.023735 | 0.00017762
2012-12-26 04:53PM | 1580699-1 | D813 | Rural Short | Weather | 1 | 122 | 122 | 0.00013629 | 1.1171e-06
2012-08-09 05:07PM | 1544227-1 | D813 | Rural Short | Weather | 300 | 120.5833 | 36175 | 0.040412 | 0.00033514
2012-09-29 08:16AM | 1558029-1 | D813 | Rural Short | Equipment Failure | 11 | 185.6364 | 2042 | 0.0022812 | 1.2288e-05
2012-11-30 06:10PM | 1577093-1 | D814 | Rural Short | Weather | 377 | 456.695 | 172174 | 0.19234 | 0.00042115
2012-10-20 12:25PM | 1563297-1 | D814 | Rural Short | Equipment Failure | 27 | 199 | 5373 | 0.0060023 | 3.0162e-05
2013-01-08 12:31PM | 1583179-1 | D814 | Rural Short | Equipment Failure | 1 | 156 | 156 | 0.00017427 | 1.1171e-06
2013-01-18 12:44PM | 1586003-1 | D814 | Rural Short | Other | 3 | 98 | 294 | 0.00032843 | 3.3514e-06
2013-01-20 08:22AM | 1586701-1 | D814 | Rural Short | Weather | 3 | 198.6667 | 596 | 0.0006658 | 3.3514e-06
2012-12-17 08:38AM | 1578386-1 | D814 | Rural Short | Equipment Failure | 2 | 274 | 548 | 0.00061218 | 2.2342e-06
2012-07-09 10:31AM | 1536582-1 | D814 | Rural Short | Equipment Failure | 2 | 244 | 488 | 0.00054515 | 2.2342e-06
2013-01-18 05:56PM | 1586279-1 | D814 | Rural Short | Vegetation | 211 | 1171.6682 | 247222 | 0.27618 | 0.00023571
2013-05-08 07:25AM | 1615672-1 | D814 | Rural Short | Vegetation | 15 | 223 | 3345 | 0.0037368 | 1.6757e-05
2013-06-02 11:43AM | 1622314-1 | D814 | Rural Short | Vegetation | 542 | 169.2214 | 91718 | 0.10246 | 0.00060548
2012-12-01 11:24AM | 1574626-1 | D814 | Rural Short | Other | 105 | 407 | 42735 | 0.04774 | 0.0001173
2013-01-19 05:41PM | 1586651-1 | D814 | Rural Short | Vegetation | 2 | 112 | 224 | 0.00025023 | 2.2342e-06
2012-10-15 02:24AM | 1561633-1 | WBB2 | Urban | Animals | 34 | 103 | 3502 | 0.0039122 | 3.7982e-05
2012-11-14 06:00AM | 1569682-1 | WBB2 | Urban | Equipment Failure | 75 | 1.96 | 147 | 0.00016422 | 8.3784e-05
2013-03-15 03:47AM | 1603624-1 | WBB2 | Urban | Other | 34 | 279.4412 | 9501 | 0.010614 | 3.7982e-05
2012-09-28 10:15PM | 1557998-1 | WBB2 | Urban | Equipment Failure | 77 | 15.039 | 1158 | 0.0012936 | 8.6018e-05
2013-02-08 03:22AM | 1592651-1 | WBB2 | Urban | Animals | 34 | 95.6176 | 3251 | 0.0036318 | 3.7982e-05
2013-01-27 12:55PM | 1589125-1 | WBB2 | Urban | Equipment Failure | 51 | 317 | 16167 | 0.01806 | 5.6973e-05
2013-01-27 01:37PM | 1589131-1 | WBB2 | Urban | Equipment Failure | 76 | 3 | 228 | 0.0002547 | 8.4901e-05
2013-05-22 06:55AM | 1619210-1 | WBC2 | Rural Short | Equipment Failure | 10 | 246 | 2460 | 0.0027481 | 1.1171e-05
2013-01-16 12:40PM | 1585383-1 | WBC2 | Rural Short | Vegetation | 10 | 124.9 | 1249 | 0.0013953 | 1.1171e-05
2012-07-11 11:55AM | 1537073-1 | WBC2 | Rural Short | Vegetation | 933 | 1.7663 | 1648 | 0.001841 | 0.0010423
2012-07-21 05:00PM | 1539487-1 | WBC2 | Rural Short | Other | 33 | 14.3333 | 473 | 0.0005284 | 3.6865e-05
2012-09-10 07:03AM | 1553335-1 | WBC2 | Rural Short | Equipment Failure | 967 | 102.8418 | 99448 | 0.1111 | 0.0010803
2012-09-10 02:24PM | 1553504-1 | WBC2 | Rural Short | Equipment Failure | 383 | 69 | 26427 | 0.029522 | 0.00042786
2013-01-17 03:26AM | 1585556-1 | WBC2 | Rural Short | Vegetation | 964 | 84.3994 | 81361 | 0.09089 | 0.0010769
2013-01-13 03:38PM | 1584376-1 | WBC2 | Rural Short | Vegetation | 964 | 51.7915 | 49927 | 0.055774 | 0.0010769
2013-03-07 12:39PM | 1601729-1 | WBC2 | Rural Short | Other | 1 | 323 | 323 | 0.00036083 | 1.1171e-06
2012-08-26 08:17AM | 1549516-1 | WBD2 | Rural Short | Equipment Failure | 33 | 68.7879 | 2270 | 0.0025359 | 3.6865e-05
2013-02-19 06:56AM | 1595290-1 | WBD2 | Rural Short | Equipment Failure | 58 | 480 | 27840 | 0.031101 | 6.4793e-05
2013-02-19 06:32PM | 1595618-1 | WBD2 | Rural Short | Equipment Failure | 92 | 159 | 14628 | 0.016341 | 0.00010278
2013-02-19 03:57PM | 1595523-1 | WBD2 | Rural Short | Equipment Failure | 12 | 75 | 900 | 0.0010054 | 1.3405e-05
2012-08-20 11:03AM | 1547418-1 | WBD2 | Rural Short | Vegetation | 60 | 44.9 | 2694 | 0.0030095 | 6.7027e-05
2012-07-01 10:54PM | 1534694-1 | WBD2 | Rural Short | Equipment Failure | 151 | 472.649 | 71370 | 0.079729 | 0.00016869
2013-01-25 12:21PM | 1588198-1 | WBD2 | Rural Short | Vegetation | 729 | 78.6708 | 57351 | 0.064068 | 0.00081438
2012-12-17 05:18PM | 1578583-1 | WBD2 | Rural Short | Vegetation | 7 | 85 | 595 | 0.00066469 | 7.8198e-06
2013-03-07 05:19AM | 1601556-1 | WBD2 | Rural Short | Vegetation | 30 | 249.6 | 7488 | 0.008365 | 3.3514e-05
2012-09-15 05:53PM | 1554833-1 | WBD2 | Rural Short | Equipment Failure | 1 | 129 | 129 | 0.00014411 | 1.1171e-06
2012-12-27 06:33PM | 1580952-1 | WBE2 | Rural Short | Third Party Impacts | 2 | 41.5 | 83 | 9.2721e-05 | 2.2342e-06
2012-11-20 01:44AM | 1571078-1 | WBE2 | Rural Short | Other | 39 | 96.4615 | 3762 | 0.0042026 | 4.3568e-05
2013-05-28 06:42PM | 1621172-1 | M159 | Urban | Other | 8 | 313.125 | 2505 | 0.0027984 | 8.937e-06
2012-09-07 02:06PM | 1552801-1 | M159 | Urban | Equipment Failure | 1 | 259 | 259 | 0.00028933 | 1.1171e-06
2013-04-21 02:29PM | 1611825-1 | M160 | Urban | Third Party Impacts | 7 | 21 | 147 | 0.00016422 | 7.8198e-06
2012-09-28 09:48PM | 1557992-1 | M160 | Urban | Equipment Failure | 49 | 139.4082 | 6831 | 0.007631 | 5.4739e-05
2013-03-15 09:36AM | 1603661-1 | M166 | Urban | Third Party Impacts | 7 | 112 | 784 | 0.00087582 | 7.8198e-06
2012-10-11 09:39PM | 1563976-1 | YYA2 | Rural Short | Weather | 1401 | 90.2256 | 126406 | 0.14121 | 0.0015651
2013-04-14 07:27AM | 1610176-1 | YYA2 | Rural Short | Other | 2 | 107 | 214 | 0.00023906 | 2.2342e-06
2012-08-26 04:55PM | 1549563-1 | YYA2 | Rural Short | Equipment Failure | 2 | 49.5 | 99 | 0.00011059 | 2.2342e-06
2012-10-01 08:52AM | 1558207-1 | YYA2 | Rural Short | Equipment Failure | 3 | 73.6667 | 221 | 0.00024688 | 3.3514e-06
2012-12-10 10:00PM | 1576960-1 | YYA2 | Rural Short | Equipment Failure | 372 | 145.9651 | 54299 | 0.060658 | 0.00041557
2012-11-14 11:13AM | 1569777-1 | YYA2 | Rural Short | Other | 1 | 174 | 174 | 0.00019438 | 1.1171e-06
2012-07-15 07:32PM | 1537920-1 | YYA2 | Rural Short | Equipment Failure | 38 | 107.2105 | 4074 | 0.0045511 | 4.2451e-05
2013-06-08 01:18PM | 1623954-1 | YYA2 | Rural Short | Third Party Impacts | 1408 | 73.5376 | 103541 | 0.11567 | 0.0015729
2012-10-11 09:39PM | 1563976-1 | YYB2 | Rural Short | Weather | 722 | 90.162 | 65097 | 0.072721 | 0.00080656
2012-08-21 07:30PM | 1547916-1 | YYB2 | Rural Short | Other | 18 | 101 | 1818 | 0.0020309 | 2.0108e-05
2013-06-21 09:52PM | 1627075-1 | YYB2 | Rural Short | Vegetation | 424 | 53 | 22472 | 0.025104 | 0.00047366
2013-02-25 07:29AM | 1597830-1 | YYB2 | Rural Short | Weather | 2 | 461 | 922 | 0.00103 | 2.2342e-06
2013-06-25 05:46AM | 1627675-1 | YYB2 | Rural Short | Weather | 13 | 74 | 962 | 0.0010747 | 1.4523e-05
2013-06-25 03:21PM | 1627979-1 | YYB2 | Rural Short | Weather | 16 | 136 | 2176 | 0.0024309 | 1.7874e-05
2013-06-25 06:27PM | 1628045-1 | YYB2 | Rural Short | Weather | 13 | 39 | 507 | 0.00056638 | 1.4523e-05
2013-06-25 07:23PM | 1628064-1 | YYB2 | Rural Short | Weather | 16 | 472 | 7552 | 0.0084365 | 1.7874e-05
2012-11-03 05:23AM | 1566814-1 | YYB2 | Rural Short | Animals | 15 | 206.7333 | 3101 | 0.0034642 | 1.6757e-05
2013-04-20 11:06AM | 1611746-1 | YYB2 | Rural Short | Weather | 1 | 121 | 121 | 0.00013517 | 1.1171e-06
2013-04-20 11:25AM | 1611728-1 | YYB2 | Rural Short | Vegetation | 721 | 73 | 52633 | 0.058797 | 0.00080544
2013-01-28 05:23PM | 1589328-1 | 4857 | Urban | Equipment Failure | 1 | 105 | 105 | 0.0001173 | 1.1171e-06
2013-05-18 10:52AM | 1618452-1 | 4860 | Urban | Equipment Failure | 116 | 25.5172 | 2960 | 0.0033067 | 0.00012959
2013-06-12 10:30AM | 1624573-1 | 4866 | Urban | Equipment Failure | 58 | 208.5345 | 12095 | 0.013512 | 6.4793e-05
2012-08-30 02:33PM | 1550733-1 | 4866 | Urban | Third Party Impacts | 18 | 179.5556 | 3232 | 0.0036105 | 2.0108e-05
2012-09-04 06:36PM | 1551830-1 | 4866 | Urban | Other | 22 | 29.4091 | 647 | 0.00072278 | 2.4577e-05
2012-12-25 07:11PM | 1580574-1 | 4866 | Urban | Other | 1 | 179 | 179 | 0.00019996 | 1.1171e-06
2012-12-03 01:14PM | 1575037-1 | 4866 | Urban | Other | 16 | 124.0625 | 1985 | 0.0022175 | 1.7874e-05
2012-08-16 09:47AM | 1546228-1 | 4866 | Urban | Equipment Failure | 1 | 130 | 130 | 0.00014523 | 1.1171e-06
2013-04-29 08:22AM | 1613549-1 | 4866 | Urban | Other | 1 | 112 | 112 | 0.00012512 | 1.1171e-06
2013-05-08 09:20AM | 1615694-1 | 4866 | Urban | Equipment Failure | 1 | 32 | 32 | 3.5748e-05 | 1.1171e-06
2012-08-25 05:21PM | 1549487-1 | 4869 | Urban | Third Party Impacts | 125 | 171 | 21375 | 0.023878 | 0.00013964
2013-03-25 04:14PM | 1606178-1 | 4873 | Urban | Third Party Impacts | 39 | 195 | 7605 | 0.0084957 | 4.3568e-05
2012-12-05 11:37AM | 1575699-1 | 4873 | Urban | Weather | 18 | 619 | 11142 | 0.012447 | 2.0108e-05
2013-05-22 12:46PM | 1619344-1 | 4873 | Urban | Third Party Impacts | 25 | 7 | 175 | 0.0001955 | 2.7928e-05
2013-01-25 02:18PM | 1588246-1 | 4873 | Urban | Equipment Failure | 25 | 134 | 3350 | 0.0037424 | 2.7928e-05
2013-02-15 11:49AM | 1594684-1 | 4873 | Urban | Other | 35 | 75 | 2625 | 0.0029324 | 3.9099e-05
2012-08-23 02:40AM | 1548233-1 | DP1210 | Rural Short | Weather | 1551 | 75.3179 | 116818 | 0.1305 | 0.0017327
2012-08-23 07:24AM | 1548244-1 | A095 | Rural Short | Weather | 6 | 326 | 1956 | 0.0021851 | 6.7027e-06
2012-08-23 07:38AM | 1548247-1 | J493 | Urban | Other | 11 | 148.8182 | 1637 | 0.0018287 | 1.2288e-05
2012-08-23 09:25AM | 1548276-1 | 27191 | Urban | Weather | 1 | 139 | 139 | 0.00015528 | 1.1171e-06
2012-08-23 11:51AM | 1548318-1 | 55874 | Urban | Weather | 1786 | 115.0146 | 205416 | 0.22947 | 0.0019952
2012-08-23 12:56PM | 1548367-1 | 35701 | Urban | Weather | 175 | 504.9314 | 88363 | 0.098712 | 0.0001955
2012-08-23 01:14PM | 1548393-1 | 8637 | Rural Short | Weather | 409 | 137.2127 | 56120 | 0.062693 | 0.0004569
2012-08-23 01:15PM | 1548395-1 | 35696 | Urban | Weather | 37 | 539.2162 | 19951 | 0.022288 | 4.1333e-05
2012-08-23 01:16PM | 1548399-1 | S790 | Rural Short | Weather | 186 | 108 | 20088 | 0.022441 | 0.00020778
2012-08-23 01:21PM | 1548403-1 | S741 | Rural Short | Weather | 700 | 156 | 109200 | 0.12199 | 0.00078198
2012-08-23 01:23PM | 1548405-1 | D814 | Rural Short | Other | 199 | 185.4121 | 36897 | 0.041218 | 0.00022231
2012-08-23 01:25PM | 1548408-1 | W118 | Urban | Weather | 732 | 75.123 | 54990 | 0.06143 | 0.00081773
2012-08-23 02:04PM | 1548514-1 | 2807 | Urban | Weather | 27 | 167 | 4509 | 0.0050371 | 3.0162e-05
2012-08-23 02:07PM | 1548521-1 | AZ1272 | Urban | Weather | 22 | 70.5 | 1551 | 0.0017327 | 2.4577e-05
2012-08-23 02:14PM | 1548540-1 | S790 | Rural Short | Other | 7 | 219 | 1533 | 0.0017125 | 7.8198e-06
2012-08-23 02:16PM | 1548542-1 | R256 | Urban | Weather | 549 | 131.7322 | 72321 | 0.080791 | 0.0006133
2012-08-23 02:17PM | 1548544-1 | 41535 | Urban | Other | 1816 | 222.2401 | 403588 | 0.45086 | 0.0020287
2012-08-23 02:17PM | 1548545-1 | 55356 | Urban | Weather | 627 | 1374.4641 | 861789 | 0.96272 | 0.00070043
2012-08-23 02:18PM | 1548546-1 | R251 | Urban | Weather | 927 | 49.2298 | 45636 | 0.050981 | 0.0010356
2012-08-23 02:45PM | 1548601-1 | 8798 | Rural Short | Other | 587 | 326.6712 | 191756 | 0.21421 | 0.00065575
2012-08-23 03:05PM | 1548641-1 | C891 | Urban | Equipment Failure | 807 | 40.3086 | 32529 | 0.036339 | 0.00090152
2012-08-23 03:27PM | 1548670-1 | 8637 | Rural Short | Weather | 7 | 383.8571 | 2687 | 0.0030017 | 7.8198e-06
2012-08-23 03:50PM | 1548699-1 | 19857 | Urban | Weather | 119 | 225.9496 | 26888 | 0.030037 | 0.00013294
2012-08-23 04:08PM | 1548723-1 | A051 | Rural Short | Weather | 1 | 138 | 138 | 0.00015416 | 1.1171e-06
2012-08-23 04:20PM | 1548740-1 | W163 | Rural Short | Weather | 1 | 67 | 67 | 7.4847e-05 | 1.1171e-06
2012-08-23 04:30PM | 1548744-1 | W163 | Rural Short | Weather | 7 | 90.8571 | 636 | 0.00071049 | 7.8198e-06
2012-08-23 02:13PM | 1548765-1 | L941 | Rural Short | Weather | 463 | 89.1317 | 41268 | 0.046101 | 0.00051723
2012-08-23 04:59PM | 1548780-1 | 35696 | Urban | Weather | 655 | 125.1924 | 82001 | 0.091605 | 0.00073171
2012-08-23 05:06PM | 1548794-1 | 8737 | Urban | Weather | 708 | 107.4647 | 76085 | 0.084996 | 0.00079092
2012-08-23 04:27PM | 1548815-1 | W163 | Rural Short | Weather | 1 | 121 | 121 | 0.00013517 | 1.1171e-06
2012-08-23 05:49PM | 1548842-1 | 19856 | Urban | Weather | 1327 | 67.2087 | 89186 | 0.099631 | 0.0014824
2012-08-23 05:56PM | 1548849-1 | 19857 | Urban | Weather | 1 | 161 | 161 | 0.00017986 | 1.1171e-06
2012-08-23 04:46PM | 1548870-1 | 5872 | Urban | Weather | 19 | 224.9474 | 4274 | 0.0047746 | 2.1225e-05
2012-08-23 05:22PM | 1548929-1 | 49357 | Urban | Weather | 49 | 194 | 9506 | 0.010619 | 5.4739e-05
2012-08-23 06:44PM | 1548937-1 | S590 | Urban | Weather | 1 | 178 | 178 | 0.00019885 | 1.1171e-06
2012-08-23 05:04PM | 1548967-1 | W163 | Rural Short | Weather | 2 | 259 | 518 | 0.00057867 | 2.2342e-06
2012-08-23 08:44PM | 1548971-1 | 35988 | Rural Short | Weather | 5 | 105.2 | 526 | 0.00058761 | 5.5856e-06
2012-10-12 07:04AM | 1560834-1 | SXD2 | Rural Short | Vegetation | 121 | 137.281 | 16611 | 0.018556 | 0.00013517
2012-10-12 07:11AM | 1560835-1 | CLC2 | Rural Short | Equipment Failure | 137 | 123.3942 | 16905 | 0.018885 | 0.00015305
2012-10-12 07:37AM | 1560839-1 | ULF2 | Urban | Vegetation | 1703 | 32.0164 | 54524 | 0.06091 | 0.0019025
2012-10-12 08:18AM | 1560851-1 | KVA2 | Rural Short | Weather | 346 | 170.1908 | 58886 | 0.065783 | 0.00038652
2012-10-12 08:25AM | 1560853-1 | BDG2 | Rural Short | Weather | 1661 | 103.233 | 171470 | 0.19155 | 0.0018555
2012-10-12 08:37AM | 1560860-1 | C832 | Urban | Vegetation | 1521 | 76.5391 | 116416 | 0.13005 | 0.0016991
2012-10-12 08:54AM | 1560868-1 | RBB2 | Rural Short | Weather | 2 | 254 | 508 | 0.0005675 | 2.2342e-06
2012-10-12 09:07AM | 1560877-1 | ULH2 | Urban | Weather | 41 | 96.561 | 3959 | 0.0044227 | 4.5802e-05
2012-10-12 09:16AM | 1560883-1 | BK1288 | Rural Short | Weather | 819 | 496.5556 | 406679 | 0.45431 | 0.00091492
2012-10-12 09:23AM | 1560889-1 | KYB2 | Urban | Other | 26 | 189.0769 | 4916 | 0.0054918 | 2.9045e-05
2012-10-12 09:48AM | 1560900-1 | DP1284 | Rural Short | Equipment Failure | 66 | 413.8939 | 27317 | 0.030516 | 7.373e-05
2012-10-12 09:50AM | 1560903-1 | DP1210 | Rural Short | Equipment Failure | 1 | 135 | 135 | 0.00015081 | 1.1171e-06
2012-10-12 10:16AM | 1560924-1 | 8743 | Urban | Animals | 44 | 99.6136 | 4383 | 0.0048963 | 4.9153e-05
2012-10-12 10:26AM | 1560934-1 | ULB2 | Urban | Weather | 1374 | 37.1827 | 51089 | 0.057073 | 0.0015349
2012-10-12 10:08AM | 1560946-1 | SN1230 | Rural Short | Vegetation | 151 | 74.6821 | 11277 | 0.012598 | 0.00016869
2012-10-12 10:43AM | 1560947-1 | BK1288 | Rural Short | Weather | 132 | 285.3182 | 37662 | 0.042073 | 0.00014746
2012-10-12 10:27AM | 1560950-1 | BK1288 | Rural Short | Weather | 38 | 2052.7895 | 78006 | 0.087142 | 4.2451e-05
2012-10-12 10:51AM | 1560955-1 | BK1251 | Rural Short | Weather | 68 | 457.2206 | 31091 | 0.034732 | 7.5964e-05
2012-10-12 10:51AM | 1560956-1 | HKB2 | Urban | Weather | 2107 | 168.2278 | 354456 | 0.39597 | 0.0023538
2012-10-12 10:57AM | 1560969-1 | BK1251 | Rural Short | Weather | 861 | 397.0801 | 341886 | 0.38193 | 0.00096184
2012-10-12 11:00AM | 1560973-1 | BYC2 | Rural Short | Weather | 32 | 26.6875 | 854 | 0.00095402 | 3.5748e-05
2012-10-12 10:43AM | 1560983-1 | 10244 | Rural Short | Weather | 218 | 1372.3991 | 299183 | 0.33422 | 0.00024353
2012-10-12 11:12AM | 1560984-1 | 19893 | Urban | Other | 1 | 51 | 51 | 5.6973e-05 | 1.1171e-06
2012-10-12 11:20AM | 1560995-1 | 10244 | Rural Short | Weather | 40 | 105.125 | 4205 | 0.0046975 | 4.4685e-05
2012-10-12 11:47AM | 1561035-1 | MYC2 | Urban | Equipment Failure | 67 | 59.8806 | 4012 | 0.0044819 | 7.4847e-05
2012-10-12 11:50AM | 1561041-1 | BK1288 | Rural Short | Weather | 407 | 263.8821 | 107400 | 0.11998 | 0.00045467
2012-10-12 11:51AM | 1561045-1 | 8801 | Rural Short | Weather | 29 | 209.0345 | 6062 | 0.006772 | 3.2396e-05
2012-10-12 11:43AM | 1561048-1 | BK1236 | Urban | Weather | 442 | 520.9163 | 230245 | 0.25721 | 0.00049377
2012-10-12 12:00PM | 1561063-1 | SZ1242 | Urban | Weather | 205 | 189.5268 | 38853 | 0.043403 | 0.00022901
2012-10-12 12:41PM | 1561104-1 | 35001 | Urban | Weather | 1 | 14 | 14 | 1.564e-05 | 1.1171e-06
2012-10-12 12:47PM | 1561107-1 | R211 | Rural Short | Weather | 180 | 278.8111 | 50186 | 0.056064 | 0.00020108
2012-10-12 12:55PM | 1561111-1 | YYB2 | Rural Short | Weather | 720 | 48.95 | 35244 | 0.039372 | 0.00080433
2012-10-12 12:57PM | 1561114-1 | BK1299 | Rural Short | Weather | 718 | 128.5655 | 92310 | 0.10312 | 0.00080209
2012-10-12 02:05PM | 1561163-1 | W188 | Rural Short | Other | 1 | 311 | 311 | 0.00034742 | 1.1171e-06
2012-10-12 02:08PM | 1561167-1 | CRA2 | Urban | Equipment Failure | 64 | 53.9375 | 3452 | 0.0038563 | 7.1496e-05
2012-10-12 03:00PM | 1561246-1 | SXB2 | Rural Short | Weather | 1 | 93 | 93 | 0.00010389 | 1.1171e-06
2012-10-12 11:38AM | 1561259-1 | BK1299 | Rural Short | Weather | 62 | 1396.6452 | 86592 | 0.096734 | 6.9261e-05
2012-10-12 04:30PM | 1561294-1 | S738 | Rural Short | Other | 2 | 95 | 190 | 0.00021225 | 2.2342e-06
2012-10-12 04:42PM | 1561304-1 | SHD2 | Urban | Equipment Failure | 1 | 105 | 105 | 0.0001173 | 1.1171e-06
2012-10-12 05:04PM | 1561342-1 | WL1217 | Urban | Other | 31 | 174.2903 | 5403 | 0.0060358 | 3.4631e-05
2012-10-12 06:43PM | 1561364-1 | KMD2 | Urban | Equipment Failure | 80 | 40.2375 | 3219 | 0.003596 | 8.937e-05
2012-10-12 06:38PM | 1561368-1 | BK1251 | Rural Short | Weather | 12 | 335.3333 | 4024 | 0.0044953 | 1.3405e-05
2012-10-12 07:11PM | 1561369-1 | 10241 | Urban | Vegetation | 108 | 103.6759 | 11197 | 0.012508 | 0.00012065
2012-10-12 08:09PM | 1561384-1 | BYC2 | Rural Short | Equipment Failure | 56 | 928.9286 | 52020 | 0.058113 | 6.2559e-05
2012-10-12 09:45PM | 1561397-1 | WBC2 | Rural Short | Equipment Failure | 964 | 71.8174 | 69232 | 0.07734 | 0.0010769
2012-10-12 07:20PM | 1561445-1 | BK1236 | Urban | Weather | 10 | 937.9 | 9379 | 0.010477 | 1.1171e-05
2012-10-12 12:51PM | 1564866-1 | 10241 | Urban | Weather | 1141 | 38.6459 | 44095 | 0.049259 | 0.0012746
2012-10-12 12:51PM | 1564866-1 | 10242 | Urban | Weather | 1291 | 38.6383 | 49882 | 0.055724 | 0.0014422
2012-10-12 12:51PM | 1564866-1 | 10244 | Rural Short | Weather | 908 | 38.6211 | 35068 | 0.039175 | 0.0010143
2012-10-12 12:51PM | 1564866-1 | 10245 | Rural Short | Weather | 877 | 38.6226 | 33872 | 0.037839 | 0.00097971
2012-10-12 12:51PM | 1564866-1 | 10247 | Urban | Weather | 455 | 38.6615 | 17591 | 0.019651 | 0.00050829
2012-10-12 12:51PM | 1564866-1 | 10248 | Urban | Weather | 1121 | 38.6467 | 43323 | 0.048397 | 0.0012523
2012-10-12 12:51PM | 1564866-1 | 10250 | Urban | Weather | 957 | 38.6186 | 36958 | 0.041287 | 0.0010691
2012-10-12 12:51PM | 1564866-1 | 10251 | Urban | Weather | 1382 | 38.6346 | 53393 | 0.059646 | 0.0015439
2012-10-12 12:51PM | 1564866-1 | BK1236 | Urban | Weather | 938 | 38.6194 | 36225 | 0.040468 | 0.0010479
2012-10-12 12:51PM | 1564866-1 | BK1251 | Rural Short | Weather | 924 | 38.6201 | 35685 | 0.039864 | 0.0010322
2012-10-12 12:51PM | 1564866-1 | BK1288 | Rural Short | Weather | 1362 | 38.6351 | 52621 | 0.058784 | 0.0015215
2012-10-12 12:51PM | 1564866-1 | BK1299 | Rural Short | Weather | 718 | 38.6323 | 27738 | 0.030987 | 0.00080209
2012-10-12 12:51PM | 1564866-1 | R208 | Rural Short | Weather | 1055 | 38.6152 | 40739 | 0.04551 | 0.0011786
2012-10-12 12:51PM | 1564866-1 | R210 | Rural Short | Weather | 1158 | 38.6451 | 44751 | 0.049992 | 0.0012936
2012-10-12 12:51PM | 1564866-1 | R211 | Rural Short | Weather | 1320 | 38.6371 | 51001 | 0.056974 | 0.0014746
2012-12-18 06:14AM | 1578631-1 | 54647 | Urban | Transmission failure | 23 | 223.7391 | 5146 | 0.0057487 | 2.5694e-05
2012-12-18 06:14AM | 1578631-1 | 54649 | Urban | Transmission failure | 5 | 242 | 1210 | 0.0013517 | 5.5856e-06
2012-12-18 06:14AM | 1578631-1 | 54656 | Urban | Transmission failure | 1 | 302 | 302 | 0.00033737 | 1.1171e-06
2012-12-18 06:14AM | 1578631-1 | 54658 | Urban | Transmission failure | 9 | 235.4444 | 2119 | 0.0023672 | 1.0054e-05
2012-12-18 06:14AM | 1578631-1 | 54663 | Urban | Transmission failure | 7 | 216.1429 | 1513 | 0.0016902 | 7.8198e-06
2012-12-18 06:14AM | 1578631-1 | 54665 | Urban | Transmission failure | 8 | 227 | 1816 | 0.0020287 | 8.937e-06
2012-12-18 06:14AM | 1578631-1 | 54667 | Urban | Transmission failure | 1 | 302 | 302 | 0.00033737 | 1.1171e-06
2012-12-18 06:14AM | 1578631-1 | 54679 | Urban | Transmission failure | 23 | 223.7391 | 5146 | 0.0057487 | 2.5694e-05
2012-12-18 06:14AM | 1578631-1 | 54686 | Urban | Transmission failure | 5 | 242 | 1210 | 0.0013517 | 5.5856e-06
2012-12-18 06:14AM | 1578631-1 | 54688 | Urban | Transmission failure | 15 | 221.9333 | 3329 | 0.0037189 | 1.6757e-05
2012-12-18 06:14AM | 1578631-1 | 54695 | Urban | Transmission failure | 7 | 216.1429 | 1513 | 0.0016902 | 7.8198e-06
2012-12-18 06:14AM | 1578631-1 | NE1216 | Urban | Transmission failure | 30 | 221.9667 | 6659 | 0.0074389 | 3.3514e-05
2012-12-18 06:14AM | 1578631-1 | NE1219 | Urban | Transmission failure | 1 | 302 | 302 | 0.00033737 | 1.1171e-06
2012-12-18 06:14AM | 1578631-1 | NE1249 | Urban | Transmission failure | 2 | 302.5 | 605 | 0.00067586 | 2.2342e-06
2012-12-18 06:14AM | 1578631-1 | NE1275 | Urban | Transmission failure | 2 | 302.5 | 605 | 0.00067586 | 2.2342e-06
2012-12-18 06:14AM | 1578631-1 | NE1279 | Urban | Transmission failure | 4 | 227 | 908 | 0.0010143 | 4.4685e-06
2013-02-23 12:56AM | 1596556-1 | B743 | Urban | Animals | 1075 | 231.8874 | 249279 | 0.27847 | 0.0012009
2013-02-23 04:02AM | 1596565-1 | 9019 | Urban | Other | 1 | 328 | 328 | 0.00036642 | 1.1171e-06
2013-02-23 04:55AM | 1596566-1 | BK1288 | Rural Short | Vegetation | 820 | 248 | 203360 | 0.22718 | 0.00091604
2013-02-23 06:48AM | 1596573-1 | P608 | Rural Short | Equipment Failure | 1 | 225 | 225 | 0.00025135 | 1.1171e-06
2013-02-23 06:57AM | 1596574-1 | BWA2 | Rural Short | Weather | 59 | 568.2542 | 33527 | 0.037454 | 6.591e-05
2013-02-23 06:59AM | 1596575-1 | W111 | Rural Short | Other | 281 | 67 | 18827 | 0.021032 | 0.00031391
2013-02-23 07:03AM | 1596577-1 | 16653 | Urban | Weather | 1648 | 137 | 225776 | 0.25222 | 0.001841
2013-02-23 08:12AM | 1596592-1 | J493 | Urban | Other | 11 | 678 | 7458 | 0.0083315 | 1.2288e-05
2013-02-23 08:47AM | 1596599-1 | WH1235 | Urban | Equipment Failure | 1 | 205 | 205 | 0.00022901 | 1.1171e-06
2013-02-23 09:28AM | 1596622-1 | CLD2 | Rural Short | Other | 1 | 175 | 175 | 0.0001955 | 1.1171e-06
2013-02-23 09:38AM | 1596630-1 | WQ1264 | Urban | Equipment Failure | 354 | 58.8277 | 20825 | 0.023264 | 0.00039546
2013-02-23 09:52AM | 1596635-1 | 48196 | Rural Short | Other | 30 | 86 | 2580 | 0.0028822 | 3.3514e-05
2013-02-23 11:22AM | 1596685-1 | WQ1227 | Urban | Other | 511 | 53.5969 | 27388 | 0.030596 | 0.00057085
2013-02-23 12:35PM | 1596701-1 | 10244 | Rural Short | Weather | 908 | 69.9427 | 63508 | 0.070946 | 0.0010143
2013-02-23 12:54PM | 1596712-1 | 19857 | Urban | Equipment Failure | 23 | 243 | 5589 | 0.0062436 | 2.5694e-05
2013-02-23 01:04PM | 1596720-1 | JBA2 | Rural Short | Vegetation | 10 | 256.4 | 2564 | 0.0028643 | 1.1171e-05
2013-02-23 02:04PM | 1596735-1 | BWG2 | Urban | Weather | 57 | 17 | 969 | 0.0010825 | 6.3676e-05
2013-02-23 02:44PM | 1596744-1 | HR1269 | Urban | Third Party Impacts | 1 | 392 | 392 | 0.00043791 | 1.1171e-06
2013-02-23 03:12PM | 1596753-1 | 35569 | Urban | Other | 6 | 114 | 684 | 0.00076411 | 6.7027e-06
2013-02-23 03:42PM | 1596763-1 | 16653 | Urban | Weather | 1648 | 110 | 181280 | 0.20251 | 0.001841
2013-02-23 03:46PM | 1596766-1 | 2825 | Urban | Equipment Failure | 1 | 466 | 466 | 0.00052058 | 1.1171e-06
2013-02-23 04:07PM | 1596779-1 | 55874 | Urban | Weather | 2 | 197 | 394 | 0.00044015 | 2.2342e-06
2013-02-23 04:07PM | 1596780-1 | 5501 | Rural Short | Weather | 197 | 39 | 7683 | 0.0085828 | 0.00022007
2013-02-23 04:13PM | 1596783-1 | WBE2 | Rural Short | Weather | 39 | 114.4615 | 4464 | 0.0049868 | 4.3568e-05
2013-02-23 04:30PM | 1596794-1 | J504 | Urban | Weather | 77 | 361 | 27797 | 0.031053 | 8.6018e-05
2013-02-23 04:47PM | 1596799-1 | F601 | Urban | Weather | 1445 | 91.382 | 132047 | 0.14751 | 0.0016142
2013-02-23 04:53PM | 1596802-1 | KYB2 | Urban | Other | 1 | 54 | 54 | 6.0324e-05 | 1.1171e-06
2013-02-23 05:02PM | 1596814-1 | MG1267 | Rural Short | Weather | 1176 | 119.1565 | 140128 | 0.15654 | 0.0013137
2013-02-23 05:13PM | 1596819-1 | S674 | Urban | Equipment Failure | 180 | 11 | 1980 | 0.0022119 | 0.00020108
2013-02-23 05:44PM | 1596843-1 | DFA2 | Rural Short | Operatonal Error | 68 | 1 | 68 | 7.5964e-05 | 7.5964e-05
2013-02-23 06:16PM | 1596868-1 | JBA2 | Rural Short | Other | 4 | 161 | 644 | 0.00071943 | 4.4685e-06
2013-02-23 06:44PM | 1596869-1 | BK1251 | Rural Short | Weather | 931 | 381.5639 | 355236 | 0.39684 | 0.00104
2013-02-23 07:23PM | 1596903-1 | HR1239 | Urban | Equipment Failure | 1 | 1236 | 1236 | 0.0013808 | 1.1171e-06
2013-02-23 07:55PM | 1596908-1 | S743 | Rural Short | Weather | 151 | 722 | 109022 | 0.12179 | 0.00016869
2013-02-23 07:04PM | 1596911-1 | 27201 | Urban | Weather | 258 | 88.5969 | 22858 | 0.025535 | 0.00028822
2013-02-23 08:19PM | 1596915-1 | 35696 | Urban | Weather | 656 | 82 | 53792 | 0.060092 | 0.00073283
2013-02-23 08:21PM | 1596916-1 | CRB2 | Urban | Equipment Failure | 271 | 124.7786 | 33815 | 0.037775 | 0.00030274
2013-02-23 08:25PM | 1596919-1 | R260 | Rural Short | Other | 291 | 343.6667 | 100007 | 0.11172 | 0.00032508
2013-02-23 08:28PM | 1596921-1 | 19856 | Urban | Weather | 1325 | 49.5072 | 65597 | 0.07328 | 0.0014802
2013-02-23 08:33PM | 1596924-1 | 10250 | Urban | Weather | 963 | 234.5244 | 225847 | 0.2523 | 0.0010758
2013-02-23 08:44PM | 1596933-1 | BK1299 | Rural Short | Weather | 720 | 471.2514 | 339301 | 0.37904 | 0.00080433
2013-02-23 08:55PM | 1596943-1 | L591 | Rural Short | Weather | 42 | 1507.6667 | 63322 | 0.070738 | 4.6919e-05
2013-02-23 08:56PM | 1596946-1 | RBA2 | Rural Short | Weather | 22 | 1059.8182 | 23316 | 0.026047 | 2.4577e-05
2013-02-23 09:21PM | 1596960-1 | D813 | Rural Short | Weather | 303 | 182 | 55146 | 0.061605 | 0.00033849
2013-02-23 09:29PM | 1596966-1 | BWF2 | Rural Short | Weather | 127 | 94 | 11938 | 0.013336 | 0.00014187
2013-02-23 09:33PM | 1596968-1 | 8636 | Rural Short | Weather | 504 | 467.373 | 235556 | 0.26314 | 0.00056303
2013-02-23 09:45PM | 1596979-1 | BWA2 | Rural Short | Other | 1 | 838 | 838 | 0.00093615 | 1.1171e-06
2013-02-23 09:53PM | 1596983-1 | S743 | Rural Short | Weather | 384 | 477.2161 | 183251 | 0.20471 | 0.00042897
2013-02-23 09:54PM | 1596984-1 | 8799 | Rural Short | Weather | 243 | 460 | 111780 | 0.12487 | 0.00027146
2013-02-23 10:09PM | 1596993-1 | 10248 | Urban | Weather | 20 | 813 | 16260 | 0.018164 | 2.2342e-05
2013-02-23 10:17PM | 1596998-1 | D814 | Rural Short | Weather | 378 | 187 | 70686 | 0.078965 | 0.00042227
2013-02-23 10:26PM | 1597000-1 | S743 | Rural Short | Weather | 302 | 386.0728 | 116594 | 0.13025 | 0.00033737
2013-02-23 10:54PM | 1597015-1 | S738 | Rural Short | Other | 4 | 1104 | 4416 | 0.0049332 | 4.4685e-06
2013-02-23 11:01PM | 1597017-1 | 10242 | Urban | Weather | 78 | 66 | 5148 | 0.0057509 | 8.7135e-05
2013-02-23 11:06PM | 1597020-1 | RBC2 | Rural Short | Weather | 59 | 1051.1017 | 62015 | 0.069278 | 6.591e-05
2013-02-23 11:14PM | 1597025-1 | S738 | Rural Short | Weather | 710 | 94.538 | 67122 | 0.074983 | 0.00079316
2013-02-23 11:17PM | 1597028-1 | BWF2 | Rural Short | Weather | 127 | 141.9764 | 18031 | 0.020143 | 0.00014187
2013-02-23 11:20PM | 1597029-1 | W123 | Urban | Weather | 998 | 307.1503 | 306536 | 0.34244 | 0.0011149
2013-02-23 11:53PM | 1597051-1 | A051 | Rural Short | Weather | 562 | 308 | 173096 | 0.19337 | 0.00062782
2013-02-24 12:00AM | 1597057-1 | A052 | Rural Short | Weather | 620 | 162.6935 | 100870 | 0.11268 | 0.00069261
2013-02-24 12:42AM | 1597071-1 | 9052 | Urban | Weather | 1171 | 299.4432 | 350648 | 0.39172 | 0.0013081
2013-02-24 12:44AM | 1597072-1 | SC1204 | Urban | Third Party Impacts | 711 | 51.1688 | 36381 | 0.040642 | 0.00079427
2013-02-24 12:58AM | 1597077-1 | WL1251 | Urban | Weather | 860 | 413.3116 | 355448 | 0.39708 | 0.00096072
2013-02-24 01:06AM | 1597081-1 | WL1217 | Urban | Vegetation | 65 | 130.0462 | 8453 | 0.009443 | 7.2613e-05
2013-02-24 12:57AM | 1597084-1 | 6419 | Urban | Weather | 23 | 152.1304 | 3499 | 0.0039088 | 2.5694e-05
2013-02-24 01:17AM | 1597086-1 | RBA2 | Rural Short | Weather | 10 | 834.7 | 8347 | 0.0093246 | 1.1171e-05
2013-02-24 01:25AM | 1597088-1 | CT1262 | Rural Short | Weather | 611 | 535.4632 | 327168 | 0.36549 | 0.00068256
2013-02-24 01:54AM | 1597100-1 | RBD2 | Rural Short | Weather | 67 | 47.9403 | 3212 | 0.0035882 | 7.4847e-05
2013-02-24 02:24AM | 1597107-1 | WWE2 | Urban | Weather | 506 | 136.6561 | 69148 | 0.077247 | 0.00056526
2013-02-24 02:50AM | 1597112-1 | M396 | Urban | Weather | 1 | 406 | 406 | 0.00045355 | 1.1171e-06
2013-02-24 02:55AM | 1597115-1 | KVB2 | Rural Short | Weather | 23 | 537.3913 | 12360 | 0.013808 | 2.5694e-05
2013-02-23 09:03PM | 1597116-1 | L591 | Rural Short | Weather | 138 | 590.6957 | 81516 | 0.091063 | 0.00015416
2013-02-24 02:58AM | 1597117-1 | KMD2 | Urban | Weather | 1395 | 684.4939 | 954869 | 1.0667 | 0.0015584
2013-02-24 04:13AM | 1597147-1 | NA1207 | Rural Short | Weather | 118 | 1432.5339 | 169039 | 0.18884 | 0.00013182
2013-02-24 04:51AM | 1597159-1 | A052 | Rural Short | Equipment Failure | 14 | 486 | 6804 | 0.0076009 | 1.564e-05
2013-02-24 04:56AM | 1597162-1 | BK1299 | Rural Short | Weather | 62 | 719.1129 | 44585 | 0.049807 | 6.9261e-05
2013-02-24 05:29AM | 1597171-1 | ULL2 | Rural Short | Weather | 468 | 387.7073 | 181447 | 0.2027 | 0.00052281
2013-02-24 05:48AM | 1597176-1 | YYA2 | Rural Short | Weather | 1328 | 32.6755 | 43393 | 0.048475 | 0.0014835
2013-02-24 06:50AM | 1597205-1 | M394 | Urban | Other | 1315 | 5.6783 | 7467 | 0.0083415 | 0.001469
2013-02-24 07:21AM | 1597222-1 | GG1295 | Rural Short | Weather | 58 | 309.5862 | 17956 | 0.020059 | 6.4793e-05
2013-02-24 07:53AM | 1597247-1 | BGA2 | Rural Short | Weather | 2 | 1967 | 3934 | 0.0043947 | 2.2342e-06
2013-02-24 08:00AM | 1597249-1 | S738 | Rural Short | Weather | 6 | 130 | 780 | 0.00087135 | 6.7027e-06
2013-02-24 12:47AM | 1597257-1 | WQ1249 | Urban | Equipment Failure | 169 | 560.2722 | 94686 | 0.10578 | 0.00018879
2013-02-24 08:18AM | 1597259-1 | BK1299 | Rural Short | Weather | 97 | 516.732 | 50123 | 0.055993 | 0.00010836
2013-02-24 09:00AM | 1597280-1 | MG1286 | Rural Short | Weather | 1 | 573 | 573 | 0.00064011 | 1.1171e-06
2013-02-24 12:01AM | 1597282-1 | A314 | Urban | Vegetation | 15 | 696 | 10440 | 0.011663 | 1.6757e-05
2013-02-24 09:10AM | 1597292-1 | 10248 | Urban | Weather | 20 | 156 | 3120 | 0.0034854 | 2.2342e-05
2013-02-24 09:13AM | 1597298-1 | S738 | Rural Short | Weather | 26 | 550.6923 | 14318 | 0.015995 | 2.9045e-05
2013-02-24 09:14AM | 1597299-1 | R215 | Urban | Weather | 2 | 528 | 1056 | 0.0011797 | 2.2342e-06
2013-02-24 09:20AM | 1597309-1 | YYA2 | Rural Short | Weather | 151 | 477.7616 | 72142 | 0.080591 | 0.00016869
2013-02-24 09:23AM | 1597313-1 | 8636 | Rural Short | Weather | 5 | 188.2 | 941 | 0.0010512 | 5.5856e-06
2013-02-24 09:59AM | 1597342-1 | BWF2 | Rural Short | Weather | 7 | 160.1429 | 1121 | 0.0012523 | 7.8198e-06
2013-02-24 06:27AM | 1597345-1 | WQ1249 | Urban | Equipment Failure | 153 | 549.3791 | 84055 | 0.0939 | 0.00017092
2013-02-24 10:02AM | 1597352-1 | BWF2 | Rural Short | Weather | 14 | 522.2143 | 7311 | 0.0081673 | 1.564e-05
2013-02-24 10:40AM | 1597385-1 | L591 | Rural Short | Weather | 9 | 331 | 2979 | 0.0033279 | 1.0054e-05
2013-02-24 10:50AM | 1597394-1 | RBB2 | Rural Short | Weather | 3 | 311.6667 | 935 | 0.0010445 | 3.3514e-06
2013-02-24 10:53AM | 1597400-1 | 87218 | Rural Short | Other | 33 | 67 | 2211 | 0.00247 | 3.6865e-05
2013-02-24 11:28AM | 1597432-1 | HKF2 | Urban | Weather | 48 | 1768.25 | 84876 | 0.094817 | 5.3622e-05
2013-02-24 12:46PM | 1597486-1 | GG1295 | Rural Short | Weather | 57 | 65.2982 | 3722 | 0.0041579 | 6.3676e-05
2013-02-24 01:32PM | 1597500-1 | B217 | Urban | Weather | 1 | 166 | 166 | 0.00018544 | 1.1171e-06
2013-02-24 01:57PM | 1597520-1 | 16653 | Urban | Weather | 1648 | 95.747 | 157791 | 0.17627 | 0.001841
2013-02-24 04:29PM | 1597577-1 | RBD2 | Rural Short | Weather | 64 | 274.1719 | 17547 | 0.019602 | 7.1496e-05
2013-02-24 05:13PM | 1597589-1 | NA1207 | Rural Short | Weather | 18 | 255.4444 | 4598 | 0.0051365 | 2.0108e-05
2013-02-24 05:40PM | 1597601-1 | 8635 | Rural Short | Other | 9 | 124 | 1116 | 0.0012467 | 1.0054e-05
2013-02-24 05:45PM | 1597603-1 | 35418 | Rural Short | Weather | 2 | 260.5 | 521 | 0.00058202 | 2.2342e-06
2013-02-24 05:48PM | 1597605-1 | M394 | Urban | Weather | 5 | 340 | 1700 | 0.0018991 | 5.5856e-06
2013-02-24 06:20PM | 1597616-1 | S743 | Rural Short | Weather | 2 | 1084 | 2168 | 0.0024219 | 2.2342e-06
2013-02-24 06:32PM | 1597625-1 | WL1217 | Urban | Weather | 2036 | 128.1046 | 260821 | 0.29137 | 0.0022745
2013-02-24 06:38PM | 1597627-1 | J509 | Urban | Equipment Failure | 1619 | 245.4046 | 397310 | 0.44384 | 0.0018086
2013-02-24 06:38PM | 1597628-1 | J512 | Urban | Other | 1386 | 487.7734 | 676054 | 0.75523 | 0.0015483
2013-02-24 06:42PM | 1597631-1 | B217 | Urban | Weather | 43 | 124 | 5332 | 0.0059565 | 4.8036e-05
2013-02-24 06:53PM | 1597641-1 | B217 | Urban | Weather | 42 | 147 | 6174 | 0.0068971 | 4.6919e-05
2013-02-24 07:55PM | 1597672-1 | RBD2 | Rural Short | Weather | 131 | 4.3817 | 574 | 0.00064123 | 0.00014634
2013-02-24 08:01PM | 1597702-1 | RBC2 | Rural Short | Weather | 30 | 131.6333 | 3949 | 0.0044115 | 3.3514e-05
2013-02-24 09:03PM | 1597731-1 | RBD2 | Rural Short | Weather | 16 | 409.25 | 6548 | 0.0073149 | 1.7874e-05
2013-02-24 09:11PM | 1597739-1 | WL1292 | Urban | Equipment Failure | 45 | 234 | 10530 | 0.011763 | 5.027e-05
2013-02-24 08:23PM | 1597740-1 | RBA2 | Rural Short | Weather | 13 | 130.3846 | 1695 | 0.0018935 | 1.4523e-05
2013-02-24 09:23AM | 1597747-1 | SHJ2 | Rural Short | Weather | 6 | 887 | 5322 | 0.0059453 | 6.7027e-06
2013-02-24 10:04PM | 1597753-1 | ULJ2 | Rural Short | Weather | 1051 | 1 | 1051 | 0.0011741 | 0.0011741
2013-02-24 10:05PM | 1597755-1 | ULH2 | Urban | Weather | 2172 | 101.7164 | 220928 | 0.2468 | 0.0024264
2013-02-24 10:36PM | 1597768-1 | 17039 | Urban | Weather | 1 | 74 | 74 | 8.2667e-05 | 1.1171e-06
2013-02-24 06:38PM | 1598190-1 | J512 | Urban | Weather | 3460 | 181 | 626260 | 0.69961 | 0.0038652
2013-02-24 06:38PM | 1598192-1 | J512 | Urban | Other | 944 | 65 | 61360 | 0.068546 | 0.0010546
2013-02-24 05:13PM | 1598316-1 | KMF2 | Urban | Weather | 27 | 56 | 1512 | 0.0016891 | 3.0162e-05
2013-03-01 01:35AM | 1599497-1 | T866 | Urban | Vegetation | 1453 | 168.8252 | 245303 | 0.27403 | 0.0016232
2013-03-01 03:36AM | 1599501-1 | HKF2 | Urban | Weather | 2323 | 242.3551 | 562991 | 0.62893 | 0.0025951
2013-03-01 04:14AM | 1599505-1 | D814 | Rural Short | Vegetation | 13 | 503 | 6539 | 0.0073048 | 1.4523e-05
2013-03-01 04:28AM | 1599513-1 | WQ1227 | Urban | Weather | 511 | 206.9648 | 105759 | 0.11815 | 0.00057085
2013-03-01 04:18AM | 1599563-1 | 2819 | Urban | Equipment Failure | 1669 | 159.4242 | 266079 | 0.29724 | 0.0018645
2013-03-01 04:18AM | 1599563-1 | 2820 | Urban | Equipment Failure | 2245 | 159.437 | 357936 | 0.39986 | 0.0025079
2013-03-01 04:18AM | 1599563-1 | 2822 | Urban | Equipment Failure | 1260 | 159.446 | 200902 | 0.22443 | 0.0014076
2013-03-01 04:18AM | 1599563-1 | 2825 | Urban | Equipment Failure | 1401 | 159.5032 | 223464 | 0.24964 | 0.0015651
2013-03-01 04:18AM | 1599563-1 | 2826 | Urban | Equipment Failure | 80 | 161.15 | 12892 | 0.014402 | 8.937e-05
2013-03-01 04:18AM | 1599563-1 | 2828 | Urban | Equipment Failure | 483 | 159.4079 | 76994 | 0.086012 | 0.00053957
2013-03-01 04:18AM | 1599563-1 | 7994 | Urban | Equipment Failure | 1564 | 159.4802 | 249427 | 0.27864 | 0.0017472
2013-03-01 04:18AM | 1599563-1 | 7995 | Urban | Equipment Failure | 242 | 159.8182 | 38676 | 0.043206 | 0.00027034
2013-03-01 04:18AM | 1599563-1 | 7996 | Urban | Equipment Failure | 101 | 159.5545 | 16115 | 0.018002 | 0.00011283
2013-03-01 05:32AM | 1599567-1 | KVC2 | Rural Short | Vegetation | 31 | 373 | 11563 | 0.012917 | 3.4631e-05
2013-03-01 06:06AM | 1599571-1 | C900 | Urban | Other | 1 | 215 | 215 | 0.00024018 | 1.1171e-06
2013-03-01 07:26AM | 1599599-1 | 8798 | Rural Short | Vegetation | 586 | 107.6348 | 63074 | 0.070461 | 0.00065463
2013-03-01 07:13AM | 1599603-1 | 17038 | Urban | Other | 18 | 148 | 2664 | 0.002976 | 2.0108e-05
2013-03-01 09:07AM | 1599644-1 | 10244 | Rural Short | Vegetation | 5 | 75 | 375 | 0.00041892 | 5.5856e-06
2013-03-01 09:33AM | 1599661-1 | L582 | Rural Short | Weather | 79 | 182.4304 | 14412 | 0.0161 | 8.8252e-05
2013-03-01 10:24AM | 1599687-1 | L946 | Rural Short | Vegetation | 447 | 34 | 15198 | 0.016978 | 0.00049935
2013-03-01 10:38AM | 1599773-1 | J502 | Urban | Equipment Failure | 1958 | 88.8708 | 174009 | 0.19439 | 0.0021873
2013-03-01 10:54AM | 1599790-1 | L591 | Rural Short | Other | 28 | 156 | 4368 | 0.0048796 | 3.1279e-05
2013-03-01 10:45AM | 1599791-1 | 10251 | Urban | Vegetation | 55 | 269.3273 | 14813 | 0.016548 | 6.1442e-05
2013-03-01 11:29AM | 1599813-1 | T831 | Rural Short | Equipment Failure | 1 | 204 | 204 | 0.00022789 | 1.1171e-06
2013-03-01 11:42AM | 1599820-1 | 8634 | Rural Short | Vegetation | 644 | 206.059 | 132702 | 0.14824 | 0.00071943
2013-03-01 11:44AM | 1599822-1 | BK1236 | Urban | Weather | 1 | 114 | 114 | 0.00012735 | 1.1171e-06
2013-03-01 11:59AM | 1599826-1 | HBB2 | Urban | Other | 1 | 178 | 178 | 0.00019885 | 1.1171e-06
2013-03-01 12:21PM | 1599833-1 | 87220 | Rural Short | Equipment Failure | 1 | 495 | 495 | 0.00055297 | 1.1171e-06
2013-03-01 12:25PM | 1599836-1 | 87218 | Rural Short | Vegetation | 235 | 926.8894 | 217819 | 0.24333 | 0.00026252
2013-03-01 12:53PM | 1599855-1 | W164 | Rural Short | Weather | 1 | 92 | 92 | 0.00010278 | 1.1171e-06
2013-03-01 01:31PM | 1599876-1 | L591 | Rural Short | Vegetation | 183 | 145.7432 | 26671 | 0.029795 | 0.00020443
2013-03-01 01:48PM | 1599887-1 | 35773 | Urban | Other | 11 | 152 | 1672 | 0.0018678 | 1.2288e-05
2013-03-01 01:31PM | 1599898-1 | L591 | Rural Short | Vegetation | 28 | 326 | 9128 | 0.010197 | 3.1279e-05
2013-03-01 02:12PM | 1599899-1 | 9034 | Urban | Equipment Failure | 2 | 43 | 86 | 9.6072e-05 | 2.2342e-06
2013-03-01 02:56PM | 1599914-1 | CT1225 | Urban | Third Party Impacts | 584 | 15 | 8760 | 0.009786 | 0.0006524
2013-03-01 03:26PM | 1599960-1 | R260 | Rural Short | Vegetation | 176 | 142.3295 | 25050 | 0.027984 | 0.00019661
2013-03-01 02:22PM | 1599970-1 | 2820 | Urban | Equipment Failure | 26 | 591.8846 | 15389 | 0.017191 | 2.9045e-05
2013-03-01 04:23PM | 1600017-1 | BK1288 | Rural Short | Vegetation | 1 | 218 | 218 | 0.00024353 | 1.1171e-06
2013-03-01 04:29PM | 1600019-1 | BDC2 | Rural Short | Vegetation | 566 | 4.3039 | 2436 | 0.0027213 | 0.00063229
2013-03-01 04:12PM | 1600024-1 | W163 | Rural Short | Other | 28 | 161.25 | 4515 | 0.0050438 | 3.1279e-05
2013-03-01 05:08PM | 1600029-1 | T831 | Rural Short | Weather | 1 | 196 | 196 | 0.00021896 | 1.1171e-06
2013-03-01 05:16PM | 1600033-1 | J515 | Urban | Other | 3 | 1082 | 3246 | 0.0036262 | 3.3514e-06
2013-03-01 06:50PM | 1600067-1 | BDC2 | Rural Short | Vegetation | 21 | 9 | 189 | 0.00021114 | 2.346e-05
2013-03-01 09:09PM | 1600085-1 | J510 | Urban | Equipment Failure | 20 | 45.3 | 906 | 0.0010121 | 2.2342e-05
2013-03-01 09:23PM | 1600087-1 | 2810 | Urban | Vegetation | 1292 | 117.1455 | 151352 | 0.16908 | 0.0014433
2013-03-01 10:22PM | 1600098-1 | W164 | Rural Short | Weather | 1 | 642 | 642 | 0.00071719 | 1.1171e-06
2013-03-01 11:02PM | 1600104-1 | SC1289 | Urban | Equipment Failure | 1 | 713 | 713 | 0.00079651 | 1.1171e-06
2013-03-01 11:37PM | 1600109-1 | R256 | Urban | Other | 1 | 742 | 742 | 0.0008289 | 1.1171e-06
2013-02-23 10:48PM | 1600972-1 | KVA2 | Rural Short | Weather | 346 | 5 | 1730 | 0.0019326 | 0.00038652
2013-02-23 10:48PM | 1600972-1 | KVB2 | Rural Short | Weather | 384 | 5.0052 | 1922 | 0.0021471 | 0.00042897
2013-02-23 10:48PM | 1600972-1 | KVC2 | Rural Short | Weather | 127 | 5.0315 | 639 | 0.00071384 | 0.00014187
2013-02-23 10:48PM | 1600972-1 | KVD2 | Rural Short | Weather | 93 | 5.0215 | 467 | 0.0005217 | 0.00010389
2013-02-24 03:30PM | 1602669-1 | BK1251 | Rural Short | Weather | 8 | 65 | 520 | 0.0005809 | 8.937e-06
2013-02-24 03:37AM | 1602922-1 | 7539 | Rural Short | Weather | 1 | 2 | 2 | 2.2342e-06 | 1.1171e-06
2013-03-01 09:28AM | 1603419-1 | L582 | Rural Short | Weather | 3 | 310 | 930 | 0.0010389 | 3.3514e-06
2013-03-01 10:55AM | 1603448-1 | 7091 | Rural Short | Vegetation | 6 | 85 | 510 | 0.00056973 | 6.7027e-06
Table 2: Planned Outages
Date (DD/MM/YYYY) | Outage ID | Feeder ID / name | Feeder classification | Reason for planned outage | Number of customers interrupted | Duration of interruption (Mins) | Total planned customer minutes off supply (Mins) | Planned SAIDI impact | Planned SAIFI impact
2012-06-30 01:00AM | 208828 | 35571 | Urban | REPLACE DEFECTIVE SAFELINK S/GEAR - SUB 25084 | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2012-07-01 06:00AM | 209730 | B202 | Urban | REPLACE CONDEMNED POLE 1762. REMOVE ABS 6379 AND REPLACE LTS 19022 WITH LBS 95535 | 18 | 720 | 12960 | 0.014478 | 2.0108e-05
2012-07-01 07:00AM | 209221 | 3106 | Urban | Stand new poles. Augment Hv mains. Replace USL L723 with new LBS 90937.Install new ABS 90936. | 4 | 510 | 2040 | 0.0022789 | 4.4685e-06
2012-07-01 08:00AM | 209454 | T828 | Rural Short | MAINTAIN ABSHV DEFECTSSUB RETROFIT and INSTALL VIBRATION DAMPERS | 38 | 420 | 15960 | 0.017829 | 4.2451e-05
2012-07-01 08:00AM | 209758 | PCB2 | Urban | Replace ABSs and X arms | 10 | 450 | 4500 | 0.005027 | 1.1171e-05
2012-07-01 08:00AM | 209957 | NWE2 | Urban | REPLACE POLE AND ABS TO REPAIR PIN DEFECT | 22 | 450 | 9900 | 0.011059 | 2.4577e-05
2012-07-01 08:30AM | 209368 | WWE2 | Urban | REPLACE POLE 2X0178 and SUB POLE 2X0179 AUGMENT HV MAINS BETWEEN NEW POLES | 74 | 420 | 31080 | 0.03472 | 8.2667e-05
2012-07-01 08:30AM | 210001 | W113 | Urban | Change Pole 62 and Retro Sub 11580 | 136 | 390 | 53040 | 0.059252 | 0.00015193
2012-07-01 09:00AM | 210343 | BWD2 | Urban | Remove pole 3R0993 with ABS 50438 and erect new pole 847553 with LBS 92104 | 9 | 360 | 3240 | 0.0036195 | 1.0054e-05
2012-07-02 08:00AM | 210923 | 9020 | Urban | REPLACE RAGBOLT | 12 | 480 | 5760 | 0.0064346 | 1.3405e-05
2012-07-02 08:30AM | 209826 | 57448 | Rural Short | REPLACE CONDEMNED POLE 3 | 3 | 390 | 1170 | 0.001307 | 3.3514e-06
2012-07-02 08:30AM | 208852 | RV1280 | Urban | Replace HV crossarms and replace Poles 3G0735 and 3G0736 | 7 | 360 | 2520 | 0.0028151 | 7.8198e-06
2012-07-02 09:00AM | 210568 | 35305 | Urban | Pole change service lead in | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2012-07-02 10:00PM | 210712 | 10247 | Urban | to establish a new pillar and remove decommisioned ABC | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2012-07-03 08:00AM | 207862 | W124 | Rural Short | Replaced Condemned pole 28 with pole 860448. Replace DOF's G735 with New DOF's 95312. | 407 | 450 | 120150 | 0.13422 | 0.00045467
2012-07-03 08:00AM | 209695 | L582 | Rural Short | REPLACE POLES and AUGMENT HV MAINS | 6 | 420 | 2520 | 0.0028151 | 6.7027e-06
2012-07-03 08:00AM | 210149 | JBA2 | Rural Short | STRING EARTH WIRE BETWEEN STR 40 and 42 FDR 7050 - 11kV OUTAGE | 3 | 450 | 1350 | 0.0015081 | 3.3514e-06
2012-07-03 08:00AM | 210739 | KC1221 | Rural Short | Rearrange Low Voltage | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2012-07-03 08:00AM | 205388 | 1105 | Urban | HV Augmentation | 64 | 540 | 34560 | 0.038608 | 7.1496e-05
2012-07-03 08:00AM | 206993 | B710 | Urban | HVSWGR MAINT | 191 | 360 | 68760 | 0.076813 | 0.00021337
2012-07-03 08:00AM | 209293 | C889 | Urban | REPLACE TX + MandR HV SWITCHGEAR and COMPLETE AN EARTH TEST @ SUB # 7060 - JOHN BATMAN WERRINGTON | 89 | 480 | 42720 | 0.047723 | 9.9424e-05
2012-07-03 08:00AM | 209680 | W113 | Urban | Install ABS 90739 on 12.5/8 pole 860370 install 14/8 pole 860371. Install ABS 95102 on 14/8 pole 860372. Run 3 x 19/3.25 AAC 11kv OH aerials | 57 | 480 | 27360 | 0.030564 | 6.3676e-05
2012-07-03 08:00AM | 209782 | SWC2 | Urban | REPLACE POLE 2X1237 WITH POLE 824391 POLE 2X1236 WITH POLE 824409 AND INSTALL NEW POLE 824630. INSTALL LOAD BREAK SWITCH 87692 ON POLE 824391. | 132 | 480 | 63360 | 0.070781 | 0.00014746
2012-07-03 08:00AM | 210594 | 35701 | Urban | maintenance | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2012-07-03 08:00AM | 210724 | M397 | Urban | Change to LV circuit. | 48 | 480 | 23040 | 0.025738 | 5.3622e-05
2012-07-03 08:00AM | 211107 | 1123 | Urban | Augment road crossing | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2012-07-03 08:00AM | 211108 | 1122 | Urban | Augment road crossing | 4 | 300 | 1200 | 0.0013405 | 4.4685e-06
2012-07-03 08:30AM | 209172 | 27454 | Rural Short | Retrofit sub 4295 | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2012-07-03 08:30AM | 209483 | SHJ2 | Rural Short | REPLACE FAULTY LINE FAULT INDICATOR | 71 | 180 | 12780 | 0.014277 | 7.9316e-05
2012-07-03 08:30AM | 209662 | HBA2 | Rural Short | REPLACE POLES 3KC083 3KC082 3KC077 3KC092 ABS POLE 71031 and SUB POLE 41013 | 31 | 450 | 13950 | 0.015584 | 3.4631e-05
2012-07-03 08:30AM | 208349 | 35315 | Urban | Stand and dress new poles for future Hv augment and Pole Sub transfer | 188 | 420 | 78960 | 0.088208 | 0.00021002
2012-07-03 08:30AM | 209330 | 10287 | Urban | Retro rewire 9ft HV X-Arm links and fuses @ sub 4321 | 44 | 420 | 18480 | 0.020644 | 4.9153e-05
2012-07-03 09:00AM | 209832 | R218 | Rural Short | Augment high voltage conductors from sub 27090 to J572. | 37 | 420 | 15540 | 0.01736 | 4.1333e-05
2012-07-03 09:00AM | 209856 | X473 | Rural Short | REPLACE HV CROSSARM | 17 | 360 | 6120 | 0.0068368 | 1.8991e-05
2012-07-03 09:00AM | 210569 | 1112 | Urban | Pole change service lead in | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2012-07-03 09:00AM | 210867 | KMA2 | Urban | REPLACE LV ARM POLE 4KD198 | 7 | 240 | 1680 | 0.0018768 | 7.8198e-06
2012-07-03 09:00AM | 210892 | 49319 | Urban | Rusty Column | 27 | 180 | 4860 | 0.0054292 | 3.0162e-05
2012-07-03 09:30AM | 210060 | KVB2 | Rural Short | AUGMENT H/V CONDUCTORS | 16 | 330 | 5280 | 0.0058984 | 1.7874e-05
2012-07-04 07:30AM | 208623 | 1106 | Urban | Augment 5 bays of hv mains | 137 | 510 | 69870 | 0.078053 | 0.00015305
2012-07-04 08:00AM | 208577 | 25449 | Rural Short | NEW POLE SUB | 32 | 480 | 15360 | 0.017159 | 3.5748e-05
2012-07-04 08:00AM | 208819 | X213 | Rural Short | INSTALL DOF'S and AUGMENT HV MAINS | 8 | 450 | 3600 | 0.0040216 | 8.937e-06
2012-07-04 08:00AM | 209999 | R260 | Rural Short | Replace poles 37 and 39. Remove pole 38. Install LBS 88539. Augment HV mains from Sub 27434 to pole 40. | 31 | 450 | 13950 | 0.015584 | 3.4631e-05
2012-07-04 08:00AM | 210122 | RWE2 | Rural Short | Replace four poles install LBS and augment HV mains to 120mm CCT. Augment LV mains to 95mm ABC. | 35 | 480 | 16800 | 0.018768 | 3.9099e-05
2012-07-04 08:00AM | 208729 | WH1209 | Urban | Augment 3 bays of O/H HV mains to 3C 150mm NMSABC install 2 LBS's and remove ABS 1902. | 284 | 540 | 76680 | 0.085661 | 0.00031726
2012-07-04 08:00AM | 208970 | PKD2 | Urban | Replace Polesand xarms | 140 | 450 | 31500 | 0.035189 | 0.0001564
2012-07-04 08:00AM | 210775 | 1129 | Urban | LV Cross arms | 53 | 480 | 25440 | 0.02842 | 5.9207e-05
2012-07-04 08:30AM | 210012 | MGD2 | Rural Short | To allow staff to Augment Hv Mains between Poles 3V0754 and 818669 Wilson Dr Hilltop | 16 | 450 | 7200 | 0.0080433 | 1.7874e-05
2012-07-04 08:30AM | 209176 | B776 | Urban | REPLACE POLE 2833 WITH NEW POLE AND LBS | 13 | 420 | 5460 | 0.0060995 | 1.4523e-05
2012-07-04 09:00AM | 203873 | NA1281 | Urban | Replace pole 1YC756. | 248 | 360 | 89280 | 0.099736 | 0.00027705
2012-07-04 09:00AM | 210031 | 8734 | Urban | LV Pole change over | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2012-07-04 09:00AM | 210329 | 35315 | Urban | Augment Lv mains | 42 | 360 | 15120 | 0.016891 | 4.6919e-05
2012-07-04 09:00AM | 210982 | B709 | Urban | Rusty Column | 46 | 270 | 12420 | 0.013875 | 5.1388e-05
2012-07-04 09:00AM | 210983 | B720 | Urban | Move LV Pillar | 9 | 240 | 2160 | 0.002413 | 1.0054e-05
2012-07-04 10:00AM | 208904 | S594 | Urban | Tighten HV hardware | 209 | 240 | 50160 | 0.056035 | 0.00023348
2012-07-05 07:00AM | 208507 | M389 | Urban | Relocate and U/G section of HV. New PMS29520. | 4 | 660 | 2640 | 0.0029492 | 4.4685e-06
2012-07-05 07:30AM | 208085 | 9056 | Urban | AUGMENT 9 BAYS OF HV MAINS | 273 | 570 | 155610 | 0.17384 | 0.00030497
2012-07-05 08:00AM | 208851 | 8634 | Rural Short | ID and SPIKE HV and LV CABLES BETWEEN SUB 24716 and SUB 23274 REPOSITION CABLES | 6 | 480 | 2880 | 0.0032173 | 6.7027e-06
2012-07-05 08:00AM | 208932 | 35693 | Rural Short | augment lv mainsreplace pole and replace usl with new abs. | 115 | 540 | 62100 | 0.069373 | 0.00012847
2012-07-05 08:00AM | 209320 | L584 | Rural Short | REMOVE USL'SREPLACE POLE and AUGMENT HV MAINS | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2012-07-05 08:00AM | 210290 | R210 | Rural Short | Relocate pole 794525 1 m west | 61 | 480 | 29280 | 0.032709 | 6.8144e-05
2012-07-05 08:00AM | 211238 | R218 | Rural Short | To allow staff to replace condemned Pole #15 Burragorang Rd Mount Hunter | 11 | 420 | 4620 | 0.0051611 | 1.2288e-05
2012-07-05 08:00AM | 208031 | 8610 | Urban | HV Augmentation | 135 | 540 | 72900 | 0.081438 | 0.00015081
2012-07-05 08:00AM | 209681 | T869 | Urban | Replace Pole 276534 with 12.5/8 Pole 842358. Remove Poles 213340238 and 276536. Install G1 ground stay. | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2012-07-05 08:00AM | 209783 | SWC2 | Urban | INSTALL ONE NEW POLE AND REPLACE 4 POLES. INSTALL NEW USL 88160. AUGMENT TWO BAYS OF HV MAINS AND ERECT ONE NEW BAY OF 7/4.50AAC HV MAINS. | 259 | 480 | 124320 | 0.13888 | 0.00028933
2012-07-05 08:00AM | 210553 | UNJ2 | Urban | REPLACE UGOH | 2 | 510 | 1020 | 0.0011395 | 2.2342e-06
2012-07-05 08:00AM | 210616 | APB2 | Urban | STRING OPGW BETWEEN MOUNT TERRY TS AND STR STR 22 FDR 7050 - 11kV OUTAGE | 1 | 495 | 495 | 0.00055297 | 1.1171e-06
2012-07-05 08:00AM | 211273 | 7967 | Urban | Servie Harness | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2012-07-05 08:30AM | 208809 | 8802 | Rural Short | Replace condemned pole 106 and Replace condemned sub pole 18308 | 84 | 420 | 17640 | 0.019706 | 9.3838e-05
2012-07-05 08:30AM | 208834 | MVF2 | Rural Short | Replace Poles and Augment a section of 11KV O/H Mains to 180mm2 CCT | 65 | 420 | 27300 | 0.030497 | 7.2613e-05
2012-07-05 08:30AM | 209565 | GG1295 | Rural Short | AUGMENT HV MAINS | 16 | 420 | 6720 | 0.007507 | 1.7874e-05
2012-07-05 08:30AM | 209631 | BK1251 | Rural Short | INSTALL VIBRATION DAMPERS | 18 | 390 | 7020 | 0.0078422 | 2.0108e-05
2012-07-05 08:30AM | 211281 | MVD2 | Rural Short | Replace LV pole 3K2292 | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2012-07-05 08:30AM | 210849 | 48168 | Urban | establish new pillar | 15 | 390 | 5850 | 0.0065352 | 1.6757e-05
2012-07-05 09:00AM | 209538 | MVB2 | Rural Short | New Pole Sub 29922 | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2012-07-05 09:00AM | 210868 | 6423 | Urban | Replace Condemned Pole | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2012-07-05 09:30AM | 209794 | BYE2 | Rural Short | REPLACE POLE AND INSTALL ABS 93175 | 22 | 330 | 7260 | 0.0081103 | 2.4577e-05
2012-07-05 09:30AM | 210299 | 8741 | Urban | REMOVE ABS 288 BADEN POWELL RD NORTH ROCKS | 1 | 210 | 210 | 0.0002346 | 1.1171e-06
2012-07-06 08:00AM | 208500 | 55354 | Rural Short | Augment hv mains to hv abc and connect LBS 90634 | 172 | 540 | 92880 | 0.10376 | 0.00019214
2012-07-06 08:00AM | 208973 | A049 | Rural Short | Augment HV OH mains 19/3.25 AAC.Change over poles. | 106 | 480 | 25440 | 0.02842 | 0.00011841
2012-07-06 08:00AM | 209401 | 35980 | Rural Short | To allow staff to install USL's 91947 and USL's 91946 on replacement Pole 847417 Arina Rd Bargo | 13 | 420 | 5460 | 0.0060995 | 1.4523e-05
2012-07-06 08:00AM | 210231 | W127 | Rural Short | REPLACE POLE and ABS WITH NEW POLE and TYPE 3 LBS | 29 | 480 | 13920 | 0.01555 | 3.2396e-05
2012-07-06 08:00AM | 207782 | 5867 | Urban | RETROFIT SUB 4872 + REPLACE LV POLE 107 | 54 | 420 | 11340 | 0.012668 | 6.0324e-05
2012-07-06 08:00AM | 208086 | 1109 | Urban | POLE REPLACEMENT | 147 | 540 | 79380 | 0.088677 | 0.00016422
2012-07-06 08:00AM | 209116 | R215 | Urban | Remove ex PMS13043 install new PMS29173. | 12 | 480 | 5760 | 0.0064346 | 1.3405e-05
2012-07-06 08:30AM | 208975 | 8802 | Rural Short | Replace condemned sub 4829 + pole | 57 | 420 | 23940 | 0.026744 | 6.3676e-05
2012-07-06 09:00AM | 210772 | L584 | Rural Short | REPLACE HV POT HEAD and REPAIR ABS HANDLE | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2012-07-06 09:00AM | 211031 | BYC2 | Rural Short | Repair LV Cable | 78 | 300 | 23400 | 0.026141 | 8.7135e-05
2012-07-06 09:00AM | 211128 | C851 | Urban | maintenance | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2012-07-06 09:00AM | 211313 | 8641 | Urban | Repair Cable Fault | 14 | 90 | 1260 | 0.0014076 | 1.564e-05
2012-07-06 09:30AM | 210027 | CLB2 | Rural Short | Replace Pole 3DR100 | 8 | 240 | 1920 | 0.0021449 | 8.937e-06
2012-07-06 09:30AM | 211027 | CLD2 | Rural Short | REPLACE POLE | 11 | 270 | 2970 | 0.0033178 | 1.2288e-05
2012-07-06 10:00AM | 208912 | 4887 | Urban | Tighten HV hardware | 174 | 240 | 41760 | 0.046651 | 0.00019438
2012-07-06 10:00AM | 208913 | S674 | Urban | Repair bonding on HV crossarms | 67 | 240 | 16080 | 0.017963 | 7.4847e-05
2012-07-07 08:00AM | 210046 | M397 | Urban | Remove PMS13577 install new PMS29174 | 34 | 480 | 16320 | 0.018231 | 3.7982e-05
2012-07-07 08:00AM | 210379 | 25741 | Urban | Augment LV open wire to 150mm ABC | 136 | 480 | 45120 | 0.050404 | 0.00015193
2012-07-07 08:30AM | 209493 | WBB2 | Urban | Replace Condemned pole 3PR334 | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2012-07-08 01:30PM | 206006 | WQ1290 | Urban | To bond the earth sheaths on the 1st cable out of Wetherill Park ZS at Sub 12313. | 4 | 180 | 720 | 0.00080433 | 4.4685e-06
2012-07-08 06:00AM | 209468 | 35333 | Urban | 1) COMPLETE CONSTRUCTION OF POLE SUB 29040 AND COMMISSION AND REMOVAL OF GROUND SUB 1003 AND ASSOCISTED HV UGOH2) REPAIR ABS 9132 WELDED SHUT | 4 | 540 | 2160 | 0.002413 | 4.4685e-06
2012-07-08 06:30AM | 206591 | 27189 | Urban | HVSWGR MAINT | 6 | 420 | 2520 | 0.0028151 | 6.7027e-06
2012-07-08 07:00AM | 207651 | M170 | Urban | MandR HAZ SWITCHGEAR AT SUB 6997 | 18 | 420 | 3780 | 0.0042227 | 2.0108e-05
2012-07-08 07:00AM | 209131 | B745 | Urban | Replace existing sub 5151.Connect new HV cables at switching station 29417. Terminate 2 HV UGOH's and remove bay of O/H HV mains.Replace pole 529. | 21 | 840 | 17640 | 0.019706 | 2.346e-05
2012-07-08 07:30AM | 204368 | S602 | Urban | Replace polereplace ABS 12020 with LBS 89994.Augment HV OH mains to 120 11kv CCT. Install CLAH. | 39 | 510 | 19890 | 0.02222 | 4.3568e-05
2012-07-08 08:00AM | 207341 | WL1296 | Urban | Mand R ABS B388 MandR ABS 11999REPLACE ARRESTORS @ POLE 1543 | 127 | 480 | 60960 | 0.0681 | 0.00014187
2012-07-08 08:00AM | 209378 | PKE2 | Urban | Replace poles and augment | 19 | 420 | 7980 | 0.0089146 | 2.1225e-05
2012-07-08 10:00AM | 205952 | WQ1249 | Urban | To bondthe earth sheathson the fisrt cable out of wetherill park ZS at Substation 23496. | 1 | 180 | 180 | 0.00020108 | 1.1171e-06
2012-07-09 08:00AM | 209522 | W163 | Rural Short | RELOCATE SUB POLE | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2012-07-09 08:00AM | 210655 | JBB2 | Rural Short | LV OUTAGE TO STRING CONDUCTOR BETWEEN STR 63 AND 64 FDR 7050 | 4 | 450 | 1800 | 0.0020108 | 4.4685e-06
2012-07-09 08:00AM | 208034 | B205 | Urban | Pole change and DOF install | 53 | 540 | 28620 | 0.031972 | 5.9207e-05
2012-07-09 08:00AM | 208089 | 1106 | Urban | POLE REPLACEMENT X 3+ AUGMENT 4 BAYS OF HV MAINS | 224 | 540 | 120960 | 0.13513 | 0.00025023
2012-07-09 08:00AM | 211265 | C900 | Urban | maintenance | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2012-07-09 08:30AM | 210463 | A051 | Rural Short | REPLACE T-OFF HV X-ARM @ POLE 14. TIGHTEN HV INSULATORS @ POLES 15 16 and 17. | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2012-07-09 08:30AM | 210821 | RWE2 | Rural Short | Remove pole 3VJ054 and erect pole 815513 with LBS 83186 | 26 | 420 | 10920 | 0.012199 | 2.9045e-05
2012-07-09 08:30AM | 209931 | 19890 | Urban | REPLACE HV SW/GEAR WITH CFC SAFE LINK @ SUB 15528 REMOVE USL C635REMOVE DOFs F586 REMOVE 1 BAY HV MAINS INSTALL NEW HV UGOH | 1 | 450 | 450 | 0.0005027 | 1.1171e-06
2012-07-09 09:00AM | 211312 | A049 | Rural Short | Replace Poles | 7 | 390 | 2730 | 0.0030497 | 7.8198e-06
2012-07-09 09:00AM | 209300 | S599 | Urban | Tighten HV Hardware | 193 | 300 | 57900 | 0.064681 | 0.0002156
2012-07-10 06:30AM | 210127 | 4887 | Urban | Test Hv Cable Montrose St Feeder. Connect HV cable Sub 18615 Merrylands Rd Granville. connect HV cable CB GV1223 (Montrose Ave Feeder) New Granville Zone Elizabeth St Granville after test | 1 | 630 | 630 | 0.00070379 | 1.1171e-06
2012-07-10 07:30AM | 209868 | 4368 | Rural Short | Replace X P-137 Fdr OS/39 | 28 | 480 | 13440 | 0.015014 | 3.1279e-05
2012-07-10 08:00AM | 206846 | HKA2 | Rural Short | Install 6 new poles and string 7 bays of 180 CCT HV mains. | 6 | 480 | 2880 | 0.0032173 | 6.7027e-06
2012-07-10 08:00AM | 209707 | X877 | Rural Short | CONTRACTORS TO CUT TREES | 12 | 480 | 5760 | 0.0064346 | 1.3405e-05
2012-07-10 08:00AM | 209762 | T851 | Rural Short | REPLACE POLE 86. | 42 | 510 | 21420 | 0.023929 | 4.6919e-05
2012-07-10 08:00AM | 209774 | L584 | Rural Short | INSTALL CONDENSATION HEATERS and MAINTAIN HV SWITCHGEARS | 74 | 420 | 31080 | 0.03472 | 8.2667e-05
2012-07-10 08:00AM | 210115 | H745 | Rural Short | Install Vibration Dampers @ poles 802642 and 314697 | 1 | 210 | 210 | 0.0002346 | 1.1171e-06
2012-07-10 08:00AM | 210345 | RWB2 | Rural Short | Replace ABS 50310 with LBS 84376.Replace USL 36798 with ABS 84377.Install new DOF 84376. Replace poles and Augment OH mains to CCT as per drawing 350108 | 35 | 480 | 16800 | 0.018768 | 3.9099e-05
2012-07-10 08:00AM | 208561 | B210 | Urban | HV Augmentation | 156 | 540 | 84240 | 0.094106 | 0.00017427
2012-07-10 08:00AM | 208806 | WH1209 | Urban | Augment 4 bays of O/H HV mains to 3C 150mm NMSABC remove USL 1334 remove USL 40000. | 414 | 540 | 111780 | 0.12487 | 0.00046249
2012-07-10 08:00AM | 209292 | WWE2 | Urban | REPLACE POLES REPLACE XARMS INSTALL HV CABLE LV AUGMENT. | 53 | 480 | 25440 | 0.02842 | 5.9207e-05
2012-07-10 08:00AM | 209784 | SWC2 | Urban | REPLACE POLE 2X1233 WITH POLE 824392 POLE 2X1232 WITH POLE 824393.AUGMENT 4 BAYS OF HV MAINS TO 150 NMSHVABC FROM POLE 2X1236 TO POLE 2X1231. | 79 | 480 | 37920 | 0.042361 | 8.8252e-05
2012-07-10 08:00AM | 210927 | 9020 | Urban | REPLACE RAGBOLT | 12 | 240 | 2880 | 0.0032173 | 1.3405e-05
2012-07-10 08:00AM | 211164 | 3325 | Urban | LV Arms | 18 | 480 | 8640 | 0.0096519 | 2.0108e-05
2012-07-10 08:00AM | 211263 | C900 | Urban | maintenance | 32 | 480 | 15360 | 0.017159 | 3.5748e-05
2012-07-10 08:30AM | 209592 | 8802 | Rural Short | Retrofit sub 18645 | 13 | 330 | 4290 | 0.0047924 | 1.4523e-05
2012-07-10 08:30AM | 209731 | W164 | Rural Short | REPLACE CONDEMNED POLE 221 and REPLACE WITH NEW POLE 858194 | 14 | 300 | 4200 | 0.0046919 | 1.564e-05
2012-07-10 08:30AM | 210200 | CLA2 | Rural Short | Relocate 11kV/LV pole | 52 | 420 | 21840 | 0.024398 | 5.809e-05
2012-07-10 08:30AM | 208090 | B207 | Urban | AUGMENT 3 BAYS OF HV MAINS. | 6 | 420 | 2520 | 0.0028151 | 6.7027e-06
2012-07-10 08:30AM | 211345 | 8685 | Urban | Terminate LV cable @ Sub 7017 and terminate LV cables into new pillars | 25 | 330 | 8250 | 0.0092162 | 2.7928e-05
2012-07-10 09:00AM | 210891 | 55875 | Urban | Rusty Column | 50 | 180 | 9000 | 0.010054 | 5.5856e-05
2012-07-10 09:00AM | 211275 | B201 | Urban | Replace Condemned Pole | 26 | 240 | 6240 | 0.0069708 | 2.9045e-05
2012-07-10 10:00AM | 209302 | S590 | Urban | Tighten HV hardware | 189 | 300 | 56700 | 0.063341 | 0.00021114
2012-07-10 12:30PM | 210660 | 35982 | Rural Short | Install Vibration Dampers Between poles 772490 and 69 and Repair HV defects | 23 | 210 | 4830 | 0.0053957 | 2.5694e-05
2012-07-11 03:00PM | 209022 | WH1209 | Urban | Augment 1 bay of O/H HV mains to 150mm 3C NMSABC replace UG cable to Sub 22384. | 33 | 60 | 1980 | 0.0022119 | 3.6865e-05
2012-07-11 08:00AM | 207855 | W124 | Rural Short | Replace condemned pole 35 with pole 860445 | 120 | 450 | 27450 | 0.030665 | 0.00013405
2012-07-11 08:00AM | 207855 | W124 | Rural Short | Replace condemned pole 35 with pole 860445 | 2 | 480 | 29280 | 0.032709 | 2.2342e-06
2012-07-11 08:00AM | 209665 | R218 | Rural Short | To allow staff to replace condemned pole #26 at 370 Calf Falm Rd Mt Hunter | 38 | 420 | 15960 | 0.017829 | 4.2451e-05
2012-07-11 08:00AM | 209710 | L582 | Rural Short | STAND POLES and AUGMENT HV MAINS | 9 | 480 | 4320 | 0.004826 | 1.0054e-05
2012-07-11 08:00AM | 205408 | 1105 | Urban | HV Augmentation | 166 | 540 | 89640 | 0.10014 | 0.00018544
2012-07-11 08:00AM | 207756 | M388 | Urban | Retro Sub 10990. | 90 | 450 | 40500 | 0.045243 | 0.00010054
2012-07-11 08:00AM | 209204 | B743 | Urban | REPLACE CONDEMNED POLE 581RETRO SUB 5243 | 14 | 480 | 4800 | 0.0053622 | 1.564e-05
2012-07-11 08:00AM | 211306 | S776 | Urban | LV cable fault | 10 | 240 | 2400 | 0.0026811 | 1.1171e-05
2012-07-11 08:30AM | 209604 | MGC2 | Rural Short | Uprate ex sub 31197 to 200kva | 13 | 450 | 5850 | 0.0065352 | 1.4523e-05
2012-07-11 08:30AM | 210527 | DP1284 | Rural Short | Install Vibration Dampers poles 4BT017 and 319923 | 2 | 180 | 360 | 0.00040216 | 2.2342e-06
2012-07-11 08:30AM | 209691 | SWD2 | Urban | INSTALL POLES 820472 820473 820474 820475 | 143 | 420 | 60060 | 0.067094 | 0.00015975
2012-07-11 08:30AM | 210828 | SHK2 | Urban | REPLACE LV X ARM PL 4DR262 | 15 | 240 | 3600 | 0.0040216 | 1.6757e-05
2012-07-11 09:00AM | 210063 | 1949 | Urban | Augment 11kv OH mains to 7/4.5 AAC.Replace 11kv xarms. | 81 | 420 | 34020 | 0.038004 | 9.0487e-05
2012-07-11 09:00AM | 211172 | W113 | Urban | Install ABS 90739 on 12.5/8 pole 860370 install 14/8 pole 860371. Install ABS 95102 on 14/8 pole 860372. Run 3 x 19/3.25 AAC 11kv OH aerials | 182 | 420 | 76440 | 0.085393 | 0.00020332
2012-07-11 09:00AM | 211311 | 49319 | Urban | Rusty Columns | 36 | 300 | 10800 | 0.012065 | 4.0216e-05
2012-07-11 09:00AM | 211623 | 27202 | Urban | Repair Damaged Consac Cable | 24 | 360 | 8640 | 0.0096519 | 2.6811e-05
2012-07-11 09:30AM | 210344 | SHG2 | Urban | M and R Holec sub 21791 | 81 | 240 | 19440 | 0.021717 | 9.0487e-05
2012-07-11 11:00AM | 211307 | R247 | Urban | maintenance | 15 | 300 | 4500 | 0.005027 | 1.6757e-05
2012-07-12 08:00AM | 210034 | L591 | Rural Short | REPLACE POLESREMOVE ABSINSTALL LBS and AUGMENT HV MAINS | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2012-07-12 08:00AM | 210741 | HKD2 | Rural Short | REPLACE 6 POLES | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2012-07-12 08:00AM | 208527 | 8610 | Urban | HV Augmentation | 201 | 540 | 108540 | 0.12125 | 0.00022454
2012-07-12 08:00AM | 209257 | 7962 | Urban | REPLACE CONDEMNED POLE 1168 AND RETRO-FIT SUBS 2251 AND 2252 AND MandR ABS 2624 | 11 | 480 | 5280 | 0.0058984 | 1.2288e-05
2012-07-12 08:00AM | 209786 | SWC2 | Urban | REPLACE 3 NEW POLES AND INSTALL ONE NEW ONE. AUGMENT 7 BAYS OF HV MAINS TO 7/4.50AAC. | 299 | 480 | 143520 | 0.16033 | 0.00033402
2012-07-12 08:00AM | 209912 | 19856 | Urban | Replace pole 230 and pole 241. | 146 | 540 | 78840 | 0.088074 | 0.0001631
2012-07-12 08:00AM | 210346 | UNE2 | Urban | RETROFIT 2 SUBSTATIONS AND REPLACE 2 POLE CAPS. | 133 | 390 | 51870 | 0.057945 | 0.00014858
2012-07-12 08:00AM | 211561 | 19857 | Urban | MAINTENANCE | 7 | 240 | 1680 | 0.0018768 | 7.8198e-06
2012-07-12 08:30AM | 209286 | L948 | Rural Short | Retrofit and rewire sub 7557 and replace pole 518 | 14 | 420 | 5880 | 0.0065687 | 1.564e-05
2012-07-12 08:30AM | 209849 | GG1295 | Rural Short | AUGMENT HV MAINS BETWEEN POLES 4PK036 and 824775 INSTALL S/S 41952 ON NEW POLE | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2012-07-12 08:30AM | 210161 | WBC2 | Rural Short | RETROFIT SUB AND REPLACE MDI UNIT TRIM TREES. | 139 | 360 | 50040 | 0.055901 | 0.00015528
2012-07-12 08:30AM | 210518 | T851 | Rural Short | REPLACE HV X-ARM @ SUB 5539 REWIRE LV and REPLACE LV LINKS and FUSES | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2012-07-12 08:30AM | 210782 | RWE2 | Rural Short | Replace Poles Replace DOFs 50006 with New DOFs 91327 and Augment a section of 11KV O/H Mains. | 93 | 450 | 41850 | 0.046751 | 0.00010389
2012-07-12 08:30AM | 210960 | 35825 | Rural Short | Install Vibration Dampers @ poles 410 and 417Replace condemed Sub pole Sub 11257 | 10 | 420 | 4200 | 0.0046919 | 1.1171e-05
2012-07-12 08:30AM | 210241 | WRC2 | Urban | REPLACE POLE 1D0558 | 6 | 240 | 1440 | 0.0016087 | 6.7027e-06
2012-07-12 08:30AM | 210738 | B719 | Urban | Install HV OH mains 19/3.25 AAC.Bond in UGOH. | 12 | 330 | 3960 | 0.0044238 | 1.3405e-05
2012-07-12 08:30AM | 210899 | WRC2 | Urban | REPLACE POLE 1D0937 | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2012-07-12 09:00AM | 209218 | HBC2 | Urban | Replace Condemned pole | 22 | 300 | 6600 | 0.007373 | 2.4577e-05
2012-07-12 09:00AM | 211411 | B718 | Urban | Consac replacement | 16 | 60 | 960 | 0.0010724 | 1.7874e-05
2012-07-12 09:00AM | 211412 | B718 | Urban | Consal Replacement | 55 | 360 | 19800 | 0.022119 | 6.1442e-05
2012-07-12 09:00AM | 211541 | 3326 | Urban | LV Cable fault Locating | 11 | 360 | 3960 | 0.0044238 | 1.2288e-05
2012-07-12 09:00AM | 211640 | 7974 | Urban | Relocate LV | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2012-07-12 09:30AM | 203194 | ULF2 | Urban | Replace Condemned pole 2RR188Parson St ULLADULLA. | 167 | 330 | 55110 | 0.061564 | 0.00018656
2012-07-12 10:00AM | 211442 | CLC2 | Urban | REPLACE POLE | 84 | 270 | 22680 | 0.025336 | 9.3838e-05
2012-07-13 08:00AM | 208862 | KC1221 | Rural Short | Allow Distribution staff to augment section of HV overhead mains. | 24 | 480 | 11520 | 0.012869 | 2.6811e-05
2012-07-13 08:00AM | 209118 | 35693 | Rural Short | augment lv mains | 126 | 540 | 68040 | 0.076009 | 0.00014076
2012-07-13 08:00AM | 210195 | 35989 | Rural Short | To allow staff to install DOF's 87877 and 87878 New Pole 824546 and Remove USL's X788 and Bond Through at Janderra Rd Wilton | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2012-07-13 08:00AM | 211728 | 25747 | Rural Short | Bond in new section of LV to pillar 113882 | 16 | 120 | 1920 | 0.0021449 | 1.7874e-05
2012-07-13 08:00AM | 208382 | 35315 | Urban | Stand poles for future Hv augment. Changeover existing mains . Complete replacement of Sub 471(Use existing TX). | 163 | 450 | 73350 | 0.081941 | 0.00018209
2012-07-13 08:00AM | 208766 | 5874 | Urban | HV Augmentation | 62 | 540 | 33480 | 0.037401 | 6.9261e-05
2012-07-13 08:00AM | 210477 | C869 | Urban | Replace LV X - Arms Linksand Fuses @ Sub 2342 - Willow Tree Dr Emu Plains | 20 | 480 | 9600 | 0.010724 | 2.2342e-05
2012-07-13 08:00AM | 211308 | C855 | Urban | replace column | 32 | 480 | 15360 | 0.017159 | 3.5748e-05
2012-07-13 08:00AM | 211754 | 19857 | Urban | Replace pole | 60 | 360 | 21600 | 0.02413 | 6.7027e-05
2012-07-13 08:30AM | 209476 | 8802 | Rural Short | Retro sub 7264 and Retro sub 7252 | 17 | 360 | 6120 | 0.0068368 | 1.8991e-05
2012-07-13 08:30AM | 210232 | L940 | Rural Short | REPLACE POLE 72. | 12 | 420 | 5040 | 0.0056303 | 1.3405e-05
2012-07-13 08:30AM | 211724 | 68181 | Urban | Replace Ragbolt | 29 | 450 | 13050 | 0.014578 | 3.2396e-05
2012-07-13 09:00AM | 208385 | CLD2 | Rural Short | Replace pole 3DD175. | 97 | 360 | 34920 | 0.03901 | 0.00010836
2012-07-13 09:00AM | 209435 | MVF2 | Rural Short | Replace Condemed Poles 3XK568and 3K1912 and Replace HV Cross Arm on Pole 3XK608 | 29 | 360 | 10440 | 0.011663 | 3.2396e-05
2012-07-13 09:00AM | 211409 | 27202 | Urban | Rusty column and faulty switch | 30 | 360 | 10800 | 0.012065 | 3.3514e-05
2012-07-13 09:00AM | 211620 | 8641 | Urban | Re-connect LV Cable | 13 | 90 | 1170 | 0.001307 | 1.4523e-05
2012-07-13 09:30AM | 211582 | CLA2 | Rural Short | REPLACE L/V POLE 3DG021 | 53 | 210 | 11130 | 0.012434 | 5.9207e-05
2012-07-13 09:30AM | 210383 | WBB2 | Urban | Replace Condemned Pole 2G0320 | 4 | 210 | 840 | 0.00093838 | 4.4685e-06
2012-07-13 09:30AM | 210759 | APE2 | Urban | REPLACE POLE 222552 | 19 | 240 | 4560 | 0.0050941 | 2.1225e-05
2012-07-13 10:30AM | 211730 | 25747 | Rural Short | Bond in section of LV to pillar 110051 | 36 | 120 | 4320 | 0.004826 | 4.0216e-05
2012-07-13 12:30PM | 211732 | 25747 | Rural Short | Bond in LV to pillar 110048 | 27 | 180 | 4860 | 0.0054292 | 3.0162e-05
2012-07-14 08:00AM | 211023 | R260 | Rural Short | SUPPLY OUTAGE FOR RAILCORP TO CARRYOUT X-ARM CHANGES | 9 | 480 | 4320 | 0.004826 | 1.0054e-05
2012-07-14 08:00AM | 209871 | CT1225 | Urban | New PMS29641 and HV SW/GR U/R PMS28898 Remove sub 10581. | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2012-07-15 06:30AM | 210315 | WQ1249 | Urban | INSTALL NEW POLE AND LBS | 8 | 510 | 19380 | 0.02165 | 8.937e-06
2012-07-15 06:30AM | 210315 | WQ1249 | Urban | INSTALL NEW POLE AND LBS | 68 | 570 | 21660 | 0.024197 | 7.5964e-05
2012-07-15 07:00AM | 206045 | WQ1275 | Urban | To bond the earth sheaths on the 1st cable out of Wetherill Park ZS at Sub12558. | 2 | 150 | 300 | 0.00033514 | 2.2342e-06
2012-07-15 07:00AM | 208740 | 35571 | Urban | MandR HAZ S/GEAR SUB 17670 | 36 | 360 | 6480 | 0.0072389 | 4.0216e-05
2012-07-15 08:00AM | 206776 | HKD2 | Rural Short | REMOVE AR 24101 FROM POLE 400733 AND INSTALL LBS 89748.INSTALL NEW USL 95953. | 164 | 480 | 78720 | 0.08794 | 0.00018321
2012-07-15 08:00AM | 210117 | R260 | Rural Short | REPLACE ABS WITH TYPE 3 LBSREPLACE TXRETROFIT SUBS | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2012-07-15 08:00AM | 210175 | 10245 | Rural Short | INSTALL NEW U/G CABLETERMINATE and COMMISSION | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2012-07-15 08:00AM | 209576 | 6429 | Urban | REPLACE CONDEMNED POLE | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2012-07-15 08:00AM | 210368 | SWE2 | Urban | REPLACE UGOH AND MandR HOLEC SWITCHGEAR | 34 | 510 | 17340 | 0.019371 | 3.7982e-05
2012-07-15 08:30AM | 210634 | WRC2 | Urban | REPLACE POLE 1D1022 REPLACE HV FUSES SUBS 26275 and 43042 STRAIGHTEN POLES 1D1020 1D1028 1D1029 and 1D1030 . REPLACE POLE CAPS POLES 1D1026 and 1D1027. | 39 | 390 | 15210 | 0.016991 | 4.3568e-05
2012-07-15 10:00AM | 206050 | WQ1271 | Urban | To bond the earth sheaths the 1st cable out of Wetherill Park ZS at Sub 18790. | 1 | 180 | 180 | 0.00020108 | 1.1171e-06
2012-07-15 10:00PM | 206614 | 27187 | Urban | HVSWGR MAINT | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2012-07-16 08:00AM | 210292 | X877 | Rural Short | Allow staff to replace pole and erect ABS 91331 | 30 | 480 | 14400 | 0.016087 | 3.3514e-05
2012-07-16 08:00AM | 210554 | 46475 | Rural Short | CONNECT TO THE EXISTING NETWORK 2 X NEW BAYS OF 80mm CCT 11kV | 30 | 480 | 14400 | 0.016087 | 3.3514e-05
2012-07-16 08:00AM | 210661 | 35989 | Rural Short | To allow staff to Retrofit Sub and chanbge TX at Sub 10485 Picton Rd and install new DOF's 87875 and 87876 new pole 824548 and install 1 bay 3x 7/4.50 AAC at Emma Lane Wilton | 11 | 480 | 5280 | 0.0058984 | 1.2288e-05
2012-07-16 08:00AM | 209311 | 4883 | Urban | Tighten HV hardware | 35 | 360 | 12600 | 0.014076 | 3.9099e-05
2012-07-16 08:00AM | 209312 | S594 | Urban | Tighten HV hardware | 277 | 300 | 83100 | 0.092833 | 0.00030944
2012-07-16 08:00AM | 209354 | R215 | Urban | Remove sub 10579 and section HV OH. New PMS29644. | 20 | 480 | 9600 | 0.010724 | 2.2342e-05
2012-07-16 08:00AM | 211405 | APB2 | Urban | STRING OPGW BETWEEN MOUNT TERRY TS AND STR STR 22 FDR 7050 - 11kV OUTAGE | 1 | 495 | 495 | 0.00055297 | 1.1171e-06
2012-07-16 08:30AM | 210112 | 27454 | Rural Short | Replace HV crossarm poles 230233234235236. Replace pole cap pole 235. | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2012-07-16 09:00AM | 211647 | MGF2 | Rural Short | Replace x-pole #3T1268 | 6 | 300 | 1800 | 0.0020108 | 6.7027e-06
2012-07-16 09:00AM | 208126 | NA1266 | Urban | MandR HV Switchgear @ S/S 20895. | 137 | 240 | 32880 | 0.036731 | 0.00015305
2012-07-17 01:00PM | 208447 | BDF2 | Rural Short | REPLACE L/A's and DOF's @ SUB 19768 | 25 | 180 | 4500 | 0.005027 | 2.7928e-05
2012-07-17 08:00AM | 208976 | A049 | Rural Short | Augment HV OH mains 19/3.25 AAC.Change over poles. | 73 | 480 | 35040 | 0.039144 | 8.155e-05
2012-07-17 08:00AM | 209676 | 27446 | Rural Short | Remove ABS 64213 from pole 782963 remove pole 98 and Install new Auto LBS 95586 + pole | 15 | 480 | 7200 | 0.0080433 | 1.6757e-05
2012-07-17 08:00AM | 210257 | W163 | Rural Short | STAND POLESREMOVE USL'S REMOVE HV MAINS FOR TREE TRIMMING. | 9 | 480 | 4320 | 0.004826 | 1.0054e-05
2012-07-17 08:00AM | 210752 | HKA2 | Rural Short | REPLACE 5 POLES and INSTALL 2 NEW POLES also AUGMENT 3 BAYS of HV MAINS and INSTALL NEW LBS 88579 | 32 | 480 | 15360 | 0.017159 | 3.5748e-05
2012-07-17 08:00AM | 211032 | 35989 | Rural Short | String new conductor for 66kV Feeder 869 between Pole 1 -15. Stand new poles 12 and 13. Run ropes for OPGW poles 1-15 (Not Connected) | 79 | 480 | 37920 | 0.042361 | 8.8252e-05
2012-07-17 08:00AM | 208545 | B210 | Urban | HV Augmentation | 131 | 540 | 70740 | 0.079025 | 0.00014634
2012-07-17 08:00AM | 209134 | WH1209 | Urban | Augment 3 bays of O/H HV mains to 3C 150mm NMSABC. | 850 | 540 | 142020 | 0.15865 | 0.00094955
2012-07-17 08:00AM | 209787 | SWC2 | Urban | REPLACE POLE 2X1188 WITH POLE 824410 REPLACE POLE 2X1185 WITH POLE 824411 AND REFURBISH SUB 40512.AUGMENT 2 BAYS OF HV MAINS TO 150 NMSHVABC FROM POLE 824410 TO POLE 2X1184. | 97 | 480 | 46560 | 0.052013 | 0.00010836
2012-07-17 08:00AM | 211729 | 3325 | Urban | Replace LV arms | 42 | 480 | 20160 | 0.022521 | 4.6919e-05
2012-07-17 08:00AM | 211772 | 19857 | Urban | maintenance | 33 | 240 | 7920 | 0.0088476 | 3.6865e-05
2012-07-17 08:30AM | 209959 | DFA2 | Rural Short | REPLACE HV CROSSARMS as per BUSHFIRE DEFECTS | 5 | 270 | 1350 | 0.0015081 | 5.5856e-06
2012-07-17 08:30AM | 209588 | UNC2 | Urban | AUGMENT HV MAINS and INSTALL LBS 94762 and REMOVE SUB 23728 | 56 | 420 | 23520 | 0.026275 | 6.2559e-05
2012-07-17 09:00AM | 203495 | SXC2 | Rural Short | REPLACE ABS 30305 with LBS REPLACE X POLE | 125 | 330 | 41250 | 0.046081 | 0.00013964
2012-07-17 09:00AM | 208441 | BDF2 | Rural Short | REPLACE L/A's and DOF's @ SUB 51653 | 1 | 180 | 180 | 0.00020108 | 1.1171e-06
2012-07-17 09:00AM | 211950 | B799 | Urban | Replace Column | 2 | 180 | 360 | 0.00040216 | 2.2342e-06
2012-07-17 09:30AM | 211038 | BYE2 | Rural Short | AUGMENT H/V CONDUCTORS | 12 | 330 | 3960 | 0.0044238 | 1.3405e-05
2012-07-18 06:30AM | 210966 | WL1251 | Urban | Attach cable earths to earth bar at Hzy SW 37772 in Pad Sub 17692. | 30 | 840 | 25200 | 0.028151 | 3.3514e-05
2012-07-18 08:00AM | 209535 | KC1221 | Rural Short | Augment Section of 11KV Overehead mains to 7/4.5aac | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2012-07-18 08:00AM | 210731 | A049 | Rural Short | Replace pole 480.Augment HV OH mains to 19/3.25 AAC.Change over poles. | 24 | 480 | 5760 | 0.0064346 | 2.6811e-05
2012-07-18 08:00AM | 210125 | W123 | Urban | Uprate pole sub 9207 from 200kVA to 300kVA. Replace pole 430 with 11m/8kN. Augment LV mains from 95mm LV ABC to 150mm LV ABC | 10 | 600 | 6000 | 0.0067027 | 1.1171e-05
2012-07-18 08:00AM | 210276 | C891 | Urban | install new LBS and change pole | 19 | 480 | 9120 | 0.010188 | 2.1225e-05
2012-07-18 08:00AM | 211126 | PKE2 | Urban | REPLACE UGOH AND RETRO FIT SUB | 93 | 480 | 44640 | 0.049868 | 0.00010389
2012-07-18 08:00AM | 211870 | 8686 | Urban | replace column | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2012-07-18 08:30AM | 210007 | KME2 | Rural Short | AUGMENT HV MAINS | 8 | 420 | 3360 | 0.0037535 | 8.937e-06
2012-07-18 08:30AM | 210024 | BLA2 | Rural Short | Replace ABS pole 73188 and retrofit sub 40025 | 200 | 420 | 44100 | 0.049265 | 0.00022342
2012-07-18 08:30AM | 210903 | RWE2 | Rural Short | Replace Pole and Augment a section of 11KV O/H Mains. | 37 | 450 | 16650 | 0.0186 | 4.1333e-05
2012-07-18 08:30AM | 211183 | APD2 | Rural Short | Install Vibration Dampers poles 4CY053 319926 227588 and 227584 | 8 | 240 | 1920 | 0.0021449 | 8.937e-06
2012-07-18 08:30AM | 211703 | CRF2 | Urban | Replace Condemned Pole 3RD185 | 7 | 270 | 1890 | 0.0021114 | 7.8198e-06
2012-07-18 08:30AM | 211707 | 35696 | Urban | Maintenance | 30 | 480 | 14400 | 0.016087 | 3.3514e-05
2012-07-18 09:00AM | 206868 | ULC2 | Rural Short | REPLACE TXR in PAD SUB 72010 | 97 | 300 | 29100 | 0.032508 | 0.00010836
2012-07-18 09:00AM | 210093 | KVA2 | Rural Short | 11kV OH mains extension | 6 | 270 | 1620 | 0.0018097 | 6.7027e-06
2012-07-18 09:00AM | 211833 | 3347 | Urban | LV Arm change | 3 | 180 | 540 | 0.00060324 | 3.3514e-06
2012-07-18 09:00AM | 211836 | 3347 | Urban | LV Arm change | 4 | 180 | 720 | 0.00080433 | 4.4685e-06
2012-07-18 09:00AM | 211949 | B718 | Urban | Consac Replacement | 16 | 360 | 5760 | 0.0064346 | 1.7874e-05
2012-07-18 10:00AM | 210744 | 25449 | Rural Short | Replace TX Sub 40706 and replace polecap pole 4AA005 | 3 | 300 | 900 | 0.0010054 | 3.3514e-06
2012-07-19 06:00AM | 208868 | 4361 | Urban | Installation of hardware and rollers for the replacement of HARDEX with OPGW. | 10 | 720 | 7200 | 0.0080433 | 1.1171e-05
2012-07-19 07:00AM | 210566 | 54679 | Urban | Install PMS 29865 | 1 | 240 | 240 | 0.00026811 | 1.1171e-06
2012-07-19 08:00AM | 206763 | HKD2 | Rural Short | INSTALL 3 NEW POLES AND REPLACE 2 EXISTING ONES. AUGMENT 3 BAYS OF HV MAINS TO 7/4.50AAC | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2012-07-19 08:00AM | 209527 | 8801 | Rural Short | Retro links fuses and replace leaky 100 kVA Tx @ sub 9763 | 10 | 420 | 4200 | 0.0046919 | 1.1171e-05
2012-07-19 08:00AM | 210304 | W163 | Rural Short | AUGMENT HV MAINS | 12 | 480 | 5760 | 0.0064346 | 1.3405e-05
2012-07-19 08:00AM | 211101 | A049 | Rural Short | Replace pole 197.Install new poles. | 24 | 480 | 11520 | 0.012869 | 2.6811e-05
2012-07-19 08:00AM | 211336 | RBB2 | Rural Short | Repair PBI damaged Cable and out of tension | 18 | 360 | 6480 | 0.0072389 | 2.0108e-05
2012-07-19 08:00AM | 208531 | 8610 | Urban | HV Augmentation | 163 | 540 | 88020 | 0.098329 | 0.00018209
2012-07-19 08:00AM | 209157 | 3335 | Urban | Allow staff to remove ABS 11381(PL 1) and erect LBS 91693 on pole 2 | 26 | 480 | 12480 | 0.013942 | 2.9045e-05
2012-07-19 08:00AM | 209789 | SWC2 | Urban | REPLACE 3 POLES. Remove existing ABS 89371.INSTALL NEW ABS 74415 ON POLE 825189. AUGMENT 3 BAYS OF HV MAINS TO 7/4.50AAC. | 270 | 480 | 129600 | 0.14478 | 0.00030162
2012-07-19 08:00AM | 210096 | 19856 | Urban | Replace pole 230 with pole 857105 replace pole 270 with pole 857113 replace pole 271 with pole 859700 Install LBS 93207 augment 2 bays of O/H HV mains to 3 x 120mm 22kv CCT and augment 2 bays of O/H LV mains. | 108 | 540 | 58320 | 0.06515 | 0.00012065
2012-07-19 08:00AM | 211624 | 55870 | Urban | Change over LV and Run ABC | 34 | 480 | 16320 | 0.018231 | 3.7982e-05
2012-07-19 08:00AM | 211773 | 35696 | Urban | MAINTENANCE | 21 | 480 | 10080 | 0.011261 | 2.346e-05
2012-07-19 08:30AM | 209927 | 4360 | Rural Short | Retro Rewire LV arms Links and Fuses @ sub 5445 | 10 | 420 | 4200 | 0.0046919 | 1.1171e-05
2012-07-19 08:30AM | 210385 | WRA2 | Urban | REPLACE POLE 1D0902 REPLACE HV ARM POLE 1D0892 REPLACE HV FUSES SUB 41318 REPLACE HV ARM and RETRO SUB 41804 REPLACE LV ARM POLE 4CK482. | 116 | 330 | 38280 | 0.042763 | 0.00012959
2012-07-19 08:30AM | 210839 | 3105 | Urban | REPLACE CONDEMNED POLE 773 | 26 | 360 | 9360 | 0.010456 | 2.9045e-05
2012-07-19 09:00AM | 210666 | SXC2 | Rural Short | Augment HV Conductors ( 8 - 14 )Princes Hwy WANDANDIAN. | 33 | 360 | 11880 | 0.013271 | 3.6865e-05
2012-07-19 09:00AM | 211041 | BYE2 | Rural Short | AUGMENT H/V CONDUCTORS REPLACE POLE and REMOVE USL 30757 INSTALL USL 93174 AT POLE 326699 | 32 | 360 | 11520 | 0.012869 | 3.5748e-05
2012-07-19 09:00AM | 211957 | W111 | Rural Short | Change low voltage pole 20 and pole 14. | 37 | 360 | 13320 | 0.01488 | 4.1333e-05
2012-07-19 09:00AM | 211284 | BK1236 | Urban | STAND NEW POLE | 96 | 360 | 34560 | 0.038608 | 0.00010724
2012-07-19 09:00AM | 211572 | 3360 | Urban | Change over | 23 | 360 | 8280 | 0.0092498 | 2.5694e-05
2012-07-19 09:00AM | 212030 | 3326 | Urban | LV Cable Fault | 10 | 180 | 1800 | 0.0020108 | 1.1171e-05
2012-07-20 01:00PM | 212074 | 27202 | Urban | Replace Rusty Column | 20 | 120 | 2400 | 0.0026811 | 2.2342e-05
2012-07-20 08:00AM | 206777 | HKA2 | Rural Short | REPLACE ONE POLE AND INSTALL TWO SETS OF 40A DOFs | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2012-07-20 08:00AM | 209521 | 35816 | Rural Short | New sub 29873 | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2012-07-20 08:00AM | 209795 | 8635 | Rural Short | Remove ABS 5036 + pole and Install new Auto LBS + pole | 57 | 480 | 27360 | 0.030564 | 6.3676e-05
2012-07-20 08:00AM | 210306 | 25401 | Rural Short | Retro rewire links and fuses @ sub 3481 | 36 | 390 | 14040 | 0.015684 | 4.0216e-05
2012-07-20 08:00AM | 205173 | M390 | Urban | Erect 1 span new 11kV OH mains. | 1 | 300 | 300 | 0.00033514 | 1.1171e-06
2012-07-20 08:00AM | 208908 | 55874 | Urban | REPLACE TX + POLE SUB 3545 | 58 | 480 | 27840 | 0.031101 | 6.4793e-05
2012-07-20 08:00AM | 209316 | A054 | Urban | HV Augmentation | 99 | 540 | 53460 | 0.059721 | 0.00011059
2012-07-20 08:00AM | 210856 | 10242 | Urban | REPLACE ABS WITH LBS and AUGMENT HV MAINS | 28 | 450 | 28800 | 0.032173 | 3.1279e-05
2012-07-20 08:30AM | 210081 | SWD2 | Urban | AUGMENT HV MAINS COMMISSION LBS 85031 | 142 | 420 | 59640 | 0.066625 | 0.00015863
2012-07-20 09:00AM | 211203 | R218 | Rural Short | Straighten Pole 825628 and augment LV Mains from pole 825627 and 305987 Mayfarm Rd Brownlow Hill. | 9 | 390 | 3510 | 0.0039211 | 1.0054e-05
2012-07-20 09:00AM | 211962 | A049 | Rural Short | Replace poles | 8 | 390 | 3120 | 0.0034854 | 8.937e-06
2012-07-20 09:00AM | 211946 | B718 | Urban | Consac Replacement | 26 | 360 | 9360 | 0.010456 | 2.9045e-05
2012-07-20 09:00AM | 212072 | B799 | Urban | Replace Rusty Column | 24 | 240 | 5760 | 0.0064346 | 2.6811e-05
2012-07-21 06:30AM | 211423 | 6430 | Urban | install a new pole and relocate HV open wire | 1 | 570 | 570 | 0.00063676 | 1.1171e-06
2012-07-21 07:00AM | 210641 | MGA2 | Rural Short | LV SW/Gr U/R PMS23777 | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2012-07-21 08:00AM | 210832 | S788 | Rural Short | STAND NEW POLE and DRESS POLE ADJACENT SUB # 5864 - CRANEBROOK RD CRANEBROOK | 67 | 480 | 32160 | 0.035927 | 7.4847e-05
2012-07-22 06:30AM | 207910 | 1960 | Urban | HVSWGR MAINT | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2012-07-22 07:00AM | 205970 | WQ1260 | Urban | To bond the earth sheaths on the 1st cable out of Wetherill park ZS at Substation 2386. | 4 | 180 | 720 | 0.00080433 | 4.4685e-06
2012-07-22 08:00AM | 207778 | 4857 | Urban | Allow staff to replace 2 poles. | 1 | 540 | 540 | 0.00060324 | 1.1171e-06
2012-07-22 08:00AM | 209494 | CRB2 | Urban | REPLACE POLE and RETRO-FIT SUB 40230 | 184 | 450 | 82800 | 0.092498 | 0.00020555
2012-07-22 08:00AM | 209690 | NG1262 | Urban | To allow staff to replace Condemned pole #308 with New Pole 868566 at Econo Pl Silverdale | 10 | 420 | 4200 | 0.0046919 | 1.1171e-05
2012-07-22 08:00AM | 210302 | 1962 | Urban | Augment 11kv OH mains to 7/4.5 AAC.Replace HV xarm Sub 4116.Fit TX safety chain Sub 4116. (District switch) | 77 | 300 | 23100 | 0.025805 | 8.6018e-05
2012-07-22 08:00AM | 211053 | T854 | Urban | Clearance to allow stringing of OPGW FDR 447. | 22 | 480 | 10560 | 0.011797 | 2.4577e-05
2012-07-22 09:00AM | 211427 | MVD2 | Rural Short | Replace Condemned Pole 3K1546 | 16 | 390 | 3120 | 0.0034854 | 1.7874e-05
2012-07-22 09:00AM | 205987 | WQ1227 | Urban | To bond the earth sheaths on the 1st cable out of Wetherill Park ZS at Sub 16251. | 28 | 180 | 5040 | 0.0056303 | 3.1279e-05
2012-07-23 08:00AM | 208773 | 4354 | Urban | HV Augmentation | 6 | 540 | 3780 | 0.0042227 | 6.7027e-06
2012-07-23 08:00AM | 209743 | 1106 | Urban | POLE REPLACEMENT X 2 | 96 | 570 | 54720 | 0.061129 | 0.00010724
2012-07-23 08:00AM | 210033 | T884 | Urban | REMOVE POLES and AERIALS INSTALL NEW ABS 90646 NEW POLES and AERIALS | 149 | 540 | 80460 | 0.089883 | 0.00016645
2012-07-23 08:00AM | 211461 | ULF2 | Urban | Upgrade existing pole Substation 72011 from 250 kVA to 315 kVA on new pole | 10 | 480 | 25920 | 0.028956 | 1.1171e-05
2012-07-23 08:30AM | 211280 | MVH2 | Rural Short | Replace condemned poles 3K0155 and 3K0329 Retrofit Dofs at Subs 30108 and 30097 | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2012-07-23 08:30AM | 211461 | ULF2 | Urban | Upgrade existing pole Substation 72011 from 250 kVA to 315 kVA on new pole | 98 | 420 | 22680 | 0.025336 | 0.00010948
2012-07-23 11:30AM | 212394 | 20725 | Urban | maintenance | 2 | 270 | 540 | 0.00060324 | 2.2342e-06
2012-07-23 12:45PM | 211370 | MGD2 | Rural Short | Install a set of LV fuses at Sub 30382 | 3 | 165 | 495 | 0.00055297 | 3.3514e-06
2012-07-24 06:00AM | 211082 | 4889 | Urban | Terminate HV feeder Merrylands Mall No1 CB GV 1267. Granville Zone.Turn down existing HV cable pole 799264. STJ to new feeder from CB GV1267 | 138 | 540 | 74520 | 0.083248 | 0.00015416
2012-07-24 08:00AM | 210769 | W163 | Rural Short | RUN NEW HV MAINS | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2012-07-24 08:00AM | 210835 | S788 | Rural Short | REPLACE CONDEMNED SUB POLE # 5864 - CRANEBROOK RD CRANEBROOK | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2012-07-24 08:00AM | 211135 | A049 | Rural Short | Replace pole | 11 | 480 | 5280 | 0.0058984 | 1.2288e-05
2012-07-24 08:00AM | 211972 | A098 | Rural Short | Condemned Pole | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2012-07-24 08:00AM | 208774 | 5506 | Urban | HV Augmentation | 108 | 540 | 58320 | 0.06515 | 0.00012065
2012-07-24 08:00AM | 209768 | 8685 | Urban | REPLACE TX + CUBICLE + LV SW GR SUB 6664 | 9 | 480 | 4320 | 0.004826 | 1.0054e-05
2012-07-24 08:00AM | 210659 | RVC2 | Urban | Replace pole | 106 | 450 | 24300 | 0.027146 | 0.00011841
2012-07-24 08:30AM | 210147 | BYC2 | Rural Short | CHANGE POLE 2VR055 INSTALL NEW POLE 841979 | 40 | 420 | 16800 | 0.018768 | 4.4685e-05
2012-07-24 08:30AM | 210381 | 8636 | Rural Short | Remove ABS 350 and install new LBS | 22 | 420 | 9240 | 0.010322 | 2.4577e-05
2012-07-24 08:30AM | 211347 | 35982 | Rural Short | Install vibration dampers between poles 79 and 81. | 4 | 180 | 720 | 0.00080433 | 4.4685e-06
2012-07-24 08:30AM | 211430 | MVF2 | Rural Short | Replace Poles Install New pole Install LBS 91941 and Augment a section of 11KV O/H Mains | 18 | 450 | 8100 | 0.0090487 | 2.0108e-05
2012-07-24 08:30AM | 210296 | WBB2 | Urban | REPLACE SUB POLE AND TRANSFORMER | 58 | 420 | 24360 | 0.027213 | 6.4793e-05
2012-07-24 08:30AM | 210622 | KMF2 | Urban | M and R Holec Sub 42378 | 93 | 240 | 22320 | 0.024934 | 0.00010389
2012-07-24 08:30AM | 211907 | DP1236 | Urban | RETENSION LV MAINS POLE 4AT063 | 46 | 240 | 11040 | 0.012333 | 5.1388e-05
2012-07-24 09:00AM | 209169 | 35693 | Rural Short | augment hv mains to 120mm ct and rehash sub 9130 | 124 | 420 | 52080 | 0.05818 | 0.00013852
2012-07-24 09:00AM | 211991 | MGD2 | Rural Short | Install LV Fuses at Sub 30349 | 9 | 180 | 1620 | 0.0018097 | 1.0054e-05
2012-07-24 09:00AM | 212181 | HBB2 | Urban | Tap change and load balance | 73 | 300 | 21900 | 0.024465 | 8.155e-05
2012-07-24 09:30AM | 212163 | W123 | Urban | Extend LV Cable pillar 83190 | 20 | 270 | 5400 | 0.0060324 | 2.2342e-05
2012-07-24 12:45PM | 211395 | MGD2 | Rural Short | Install LV Fuses at Sub 31792 | 2 | 165 | 330 | 0.00036865 | 2.2342e-06
2012-07-25 01:00PM | 212174 | 49319 | Urban | Replace Rusty Column | 11 | 120 | 1320 | 0.0014746 | 1.2288e-05
2012-07-25 07:00AM | 209438 | R214 | Urban | Remove sub12544 ABS55318 and ABS55319 and U/G section of fdr R214. | 8 | 660 | 5280 | 0.0058984 | 8.937e-06
2012-07-25 07:30AM | 210305 | E898 | Urban | INSTALL AND TERMINATE NEW HV 240 CU XLPE CABLE FROM SW 77292 SUB 25257 TO CB RS 1262 ROSEHILL ZONE SUB. | 90 | 510 | 45900 | 0.051276 | 0.00010054
2012-07-25 07:30AM | 210656 | 8770 | Urban | RELACE CONDEMNED POLE RETRO SUB 1750 | 9 | 570 | 5130 | 0.0057308 | 1.0054e-05
2012-07-25 08:00AM | 207888 | W188 | Rural Short | Rectify Pin defect D255 @ Sub 10786 and Replace Tx. | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2012-07-25 08:00AM | 210852 | W163 | Rural Short | STAND POLES | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2012-07-25 08:00AM | 211060 | 27446 | Rural Short | change poles and install ABS and augment 1 bay | 60 | 480 | 28800 | 0.032173 | 6.7027e-05
2012-07-25 08:00AM | 211725 | R260 | Rural Short | Augment HV mains from pole 826230 to pole 2. | 45 | 450 | 20250 | 0.022622 | 5.027e-05
2012-07-25 08:00AM | 199046 | 35773 | Urban | REPLACE CONDEMNED POLE # 188 - WARATAH RD ST MARYS | 23 | 480 | 11040 | 0.012333 | 2.5694e-05
2012-07-25 08:00AM | 210324 | CRB2 | Urban | Replace poles and augment | 98 | 450 | 44100 | 0.049265 | 0.00010948
2012-07-25 08:00AM | 211220 | CT1225 | Urban | Retro Sub 11657. | 10 | 420 | 4200 | 0.0046919 | 1.1171e-05
2012-07-25 08:15AM | 211569 | BDG2 | Rural Short | Install and commission new Pad Sub 29606. Install new 11 kV Cabling to Pad Sub 32176 and UGOH termination associated with works. | 77 | 465 | 35805 | 0.039998 | 8.6018e-05
2012-07-25 08:30AM | 210320 | 8637 | Rural Short | Retro 9ft HV arm safety chain and mdi @ sub 5359 | 14 | 420 | 5880 | 0.0065687 | 1.564e-05
2012-07-25 08:30AM | 210791 | 8634 | Rural Short | Install HV vibration dampeners | 28 | 450 | 12600 | 0.014076 | 3.1279e-05
2012-07-25 08:30AM | 211465 | GG1295 | Rural Short | Change Tx pole and remove LV pole | 15 | 420 | 6300 | 0.0070379 | 1.6757e-05
2012-07-25 08:30AM | 211626 | 35981 | Rural Short | Install vibration dampers and repair HV defects | 31 | 270 | 8370 | 0.0093503 | 3.4631e-05
2012-07-25 08:30AM | 209744 | 35315 | Urban | Stand poles for future Hv augment. Changeover existing mains. | 114 | 420 | 23940 | 0.026744 | 0.00012735
2012-07-25 08:30AM | 212156 | 3102 | Urban | Change XARMS | 17 | 390 | 6630 | 0.0074065 | 1.8991e-05
2012-07-25 09:00AM | 210287 | 35980 | Rural Short | Uprate Sub 12160 to 50KVA single phase. | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2012-07-25 09:00AM | 210436 | HKE2 | Rural Short | Replace Condemned pole 1K0156 - Install New 20A DOFs 95183Clarendon Cres ST GEORGES BASIN | 58 | 270 | 15660 | 0.017494 | 6.4793e-05
2012-07-25 09:00AM | 210386 | 1123 | Urban | STAND POLE ADJ POLE2602 | 76 | 360 | 27360 | 0.030564 | 8.4901e-05
2012-07-25 09:00AM | 212173 | 49319 | Urban | Replace Rusty Column | 19 | 180 | 3420 | 0.0038206 | 2.1225e-05
2012-07-25 09:00AM | 212329 | 3347 | Urban | LV pole change | 5 | 300 | 1500 | 0.0016757 | 5.5856e-06
2012-07-25 09:00AM | 212512 | 3358 | Urban | LV Cross arms | 5 | 180 | 900 | 0.0010054 | 5.5856e-06
2012-07-25 09:30AM | 211348 | 35989 | Rural Short | Install vibration dampers and repair defects. | 48 | 270 | 6480 | 0.0072389 | 5.3622e-05
2012-07-25 09:30AM | 211348 | 35989 | Rural Short | Install vibration dampers and repair defects. | 48 | 330 | 7920 | 0.0088476 | 5.3622e-05
2012-07-25 12:30PM | 211639 | H745 | Rural Short | Install Vibration Dampers @ poles 802642 and 16 | 1 | 195 | 195 | 0.00021784 | 1.1171e-06
2012-07-26 06:00PM | 212347 | M390 | Urban | To replace Existing Defective H/V Safelink S/Gear @ Sub 23904 Queen St Narellan With New (CFC) Safelink S/Gear (As Per PIN Defect # D237) | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2012-07-26 07:30AM | 211769 | JBA2 | Rural Short | 11KV Isolation for HVC 25468 Jamberoo Rec. Park to carry out HV MandR to own equipment. | 3 | 510 | 1530 | 0.0017092 | 3.3514e-06
2012-07-26 08:00AM | 207149 | HKD2 | Rural Short | AUGMENT 12 BAYS OF HV MAINS TO 7/4.50AAC. | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2012-07-26 08:00AM | 210124 | KC1221 | Rural Short | Allow staff to augment a section of 11 KV O/H mains. | 24 | 480 | 11520 | 0.012869 | 2.6811e-05
2012-07-26 08:00AM | 211618 | MGC2 | Rural Short | Uprate ex sub 31197 to 200kva | 33 | 480 | 15840 | 0.017695 | 3.6865e-05
2012-07-26 08:00AM | 208538 | 8610 | Urban | HV Augmentation | 183 | 540 | 98820 | 0.11039 | 0.00020443
2012-07-26 08:00AM | 210502 | 19856 | Urban | Replace poles 268 and 239 with pole 857116 and 857115 and augment 3 bays of LV mains under HV mains. | 134 | 540 | 72360 | 0.080835 | 0.00014969
2012-07-26 08:00AM | 210871 | 7972 | Urban | REPLACE CONDEMNED POLE 2601 | 16 | 450 | 7200 | 0.0080433 | 1.7874e-05
2012-07-26 08:00AM | 212507 | 4880 | Urban | INSTALL NEW L.V. 3 WAY SW and RE-DIRECT EXISTING L.V. CABLE and INSTALL NEW L.V.CABLE . | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2012-07-26 08:30AM | 210777 | T851 | Rural Short | RETRO SUB 1803 and REPLACE Tx REPLACE LV FUSE | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2012-07-26 08:30AM | 211213 | WWE2 | Urban | RETRO S/S 40512 REPLACE ABS'S 70585 70522 74417 INSTALL DOF'S 85032 INSTALL TX CHAINS S/S 41420 and 40471 REPLACE POLE 2X0133 AUGMENT HV MAINS BETWEEN POLE 2X0136 and 825320. | 582 | 420 | 147420 | 0.16469 | 0.00065016
2012-07-26 09:00AM | 208347 | HKE2 | Rural Short | Replace Condemned pole 2DR009 and Defect RepairsHarriss Ave BASIN VIEW | 42 | 270 | 11340 | 0.012668 | 4.6919e-05
2012-07-26 09:00AM | 210680 | SXC2 | Rural Short | Replace poles ( 3 4 and 6 ) Install New ABS 91060 LBS 91061 and Remove USL 30206Princes Hwy WANDANDIAN. | 55 | 360 | 19800 | 0.022119 | 6.1442e-05
2012-07-26 09:00AM | 210755 | 10244 | Rural Short | Replace flased over insulators | 10 | 330 | 3300 | 0.0036865 | 1.1171e-05
2012-07-26 09:00AM | 212356 | MVH2 | Rural Short | Replace condemed pole 302858 | 17 | 300 | 5100 | 0.0056973 | 1.8991e-05
2012-07-26 09:00AM | 212289 | B718 | Urban | Consac Replacement | 29 | 360 | 10440 | 0.011663 | 3.2396e-05
2012-07-26 09:00AM | 212328 | 1962 | Urban | LV Pole changeover | 4 | 300 | 1200 | 0.0013405 | 4.4685e-06
2012-07-26 09:00AM | 212479 | B799 | Urban | Replace Rusty Column | 10 | 120 | 1200 | 0.0013405 | 1.1171e-05
2012-07-27 08:00AM | 210118 | 35825 | Rural Short | Change condemed pole 229 | 14 | 420 | 5880 | 0.0065687 | 1.564e-05
2012-07-27 08:00AM | 210621 | 48185 | Rural Short | Commission new 315kVA Padmount Sub No. 29706 | 26 | 540 | 7560 | 0.0084454 | 2.9045e-05
2012-07-27 08:00AM | 210874 | W124 | Rural Short | Replace defective HV crossarms + Replace USL's G756 + retrofit sub 9274 | 73 | 450 | 32850 | 0.036697 | 8.155e-05
2012-07-27 08:00AM | 211103 | 27454 | Rural Short | erect dofs change pole and augment 1 bay | 3 | 540 | 1620 | 0.0018097 | 3.3514e-06
2012-07-27 08:00AM | 211201 | L582 | Rural Short | INSTALL NEW SECTION O/H MAINS AND NEW 63KVA POLE SUB 29343 | 9 | 480 | 4320 | 0.004826 | 1.0054e-05
2012-07-27 08:00AM | 208778 | 35307 | Urban | HV Augmentation | 66 | 480 | 31680 | 0.03539 | 7.373e-05
2012-07-27 08:00AM | 209861 | 46395 | Urban | Augment HV OH mains 7/4.5 AAC. Change over poles. | 63 | 480 | 30240 | 0.033782 | 7.0379e-05
2012-07-27 08:00AM | 210308 | B747 | Urban | replace condemned pole and retro sub 4427 | 29 | 480 | 13920 | 0.01555 | 3.2396e-05
2012-07-27 08:30AM | 210483 | T851 | Rural Short | REPLACE SUB POLE 474. TIGHTEN POLE 126. | 23 | 450 | 10350 | 0.011562 | 2.5694e-05
2012-07-27 08:30AM | 211124 | 25451 | Rural Short | REPLACE USL'S 46536 WITH DOF'S 93246 AUGMENT HV MAINS BETWEEN POLES 2RX127 and 294396 | 10 | 420 | 4200 | 0.0046919 | 1.1171e-05
2012-07-27 08:30AM | 210547 | S776 | Urban | Uprate TX to 500kva and replace LV SWGR @ Sub 15584 | 35 | 390 | 13650 | 0.015249 | 3.9099e-05
2012-07-27 08:30AM | 210947 | WRC2 | Urban | REPLACE POLE 1D0328 REPLACE HV ARM and RETRO SUB 41877 . | 54 | 360 | 19440 | 0.021717 | 6.0324e-05
2012-07-27 08:30AM | 211601 | MG1208 | Urban | Replace Pole Install DOFs 92628 and Augment a Section of 11KV O/H Mains | 123 | 390 | 47970 | 0.053588 | 0.00013741
2012-07-27 09:00AM | 210352 | ULE2 | Rural Short | Install New DOFs 95129 ( replace pole 1DR030 ) and Remove DOFs 41820Kingaman Rd MILTON. | 9 | 330 | 2970 | 0.0033178 | 1.0054e-05
2012-07-27 09:00AM | 210963 | HBA2 | Rural Short | Replace Condemned pole 3KA360 | 59 | 330 | 19470 | 0.02175 | 6.591e-05
2012-07-27 09:00AM | 212327 | 8610 | Urban | LV pole change | 5 | 300 | 1500 | 0.0016757 | 5.5856e-06
2012-07-27 09:30AM | 210183 | CLA2 | Rural Short | Replace pole 3DG062. | 76 | 300 | 22800 | 0.02547 | 8.4901e-05
2012-07-28 07:00AM | 211418 | B202 | Urban | REPLACE CONDEMNED POLE 1749 | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2012-07-28 08:00AM | 211168 | BDE2 | Urban | INSTALL 2 x NEW 11KV POLES | 30 | 450 | 13500 | 0.015081 | 3.3514e-05
2012-07-28 08:00AM | 211921 | B207 | Urban | Augment 7 bays of hv mains | 22 | 600 | 13200 | 0.014746 | 2.4577e-05
2012-07-29 06:30AM | 207908 | 46748 | Urban | HVSWGR MAINT | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2012-07-29 07:00AM | 209757 | 17061 | Urban | RETROFIT + TX CHANGE SUB 8078 and RETROFIT SUB 370 | 6 | 480 | 2880 | 0.0032173 | 6.7027e-06
2012-07-29 07:00AM | 209908 | 3106 | Urban | Augment Hv mains. Replace ABS D154 with new ABS 90935.Remove ABS 1813.Transfer existing Hv UGOH to new pole. | 14 | 570 | 7980 | 0.0089146 | 1.564e-05
2012-07-29 07:00AM | 212189 | J469 | Urban | To allow staff to replace condemned Pole 223 Pembroke rd Minto | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2012-07-29 08:00AM | 211592 | W163 | Rural Short | STAND NEW POLE.AUGMENT HV MAINS and REMOVE HV MAINS.INSTALL NEW ABS | 9 | 480 | 4320 | 0.004826 | 1.0054e-05
2012-07-29 08:00AM | 211768 | MYP2 | Urban | REPLACE ABS PIN POLE and X- ARMS | 35 | 450 | 15750 | 0.017595 | 3.9099e-05
2012-07-29 08:00AM | 212325 | 3347 | Urban | Lv Changeover pole 713 | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2012-07-30 08:00AM | 207657 | NG1210 | Rural Short | Replace condemed Pole 140 Retro fit Sub 10315 and HV defects | 33 | 480 | 15840 | 0.017695 | 3.6865e-05
2012-07-30 08:00AM | 209682 | 35989 | Rural Short | Install 25KVA single phase pole sub 29777 on 12.5/12 pole 857024. | 1 | 540 | 540 | 0.00060324 | 1.1171e-06
2012-07-30 08:00AM | 211073 | 8802 | Rural Short | Retro sub 18544 | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2012-07-30 08:00AM | 211231 | 5898 | Rural Short | Connect to the network new Pole Sub 29081 replace pole 90 with new pole 824656 | 1 | 510 | 510 | 0.00056973 | 1.1171e-06
2012-07-30 08:00AM | 211880 | A049 | Rural Short | Replace pole 29 and install DOFs 90455 (20A boric acid type).Augment HV OH mains 19/3.25 AAC.(District Switcher) | 34 | 480 | 16320 | 0.018231 | 3.7982e-05
2012-07-30 08:00AM | 212050 | BK1251 | Rural Short | Replace pole 5 with new pole 853175.Install new 25kVA pole sub 29686. | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2012-07-30 08:00AM | 208028 | B210 | Urban | HV Augmentation | 262 | 540 | 71820 | 0.080232 | 0.00029269
2012-07-30 08:00AM | 212008 | 1106 | Urban | POLE REPLACEMENT + AUGMENT HV MAINS X 8 BAYS | 362 | 600 | 217200 | 0.24264 | 0.0004044
2012-07-30 08:30AM | 212354 | MVH2 | Rural Short | Replace condemned poles 3K0155 and 3K0329 Retrofit Dofs at Subs 30108 and 30097 | 10 | 420 | 4200 | 0.0046919 | 1.1171e-05
2012-07-30 08:30AM | 212376 | 27142 | Urban | Relocate SL column | 12 | 420 | 5040 | 0.0056303 | 1.3405e-05
2012-07-30 09:00AM | 211285 | BYG2 | Rural Short | Install DOF 96366 and Replace HV mains. | 12 | 240 | 2880 | 0.0032173 | 1.3405e-05
2012-07-30 09:00AM | 212710 | 41533 | Rural Short | Change S/L Column | 2 | 270 | 540 | 0.00060324 | 2.2342e-06
2012-07-30 09:00AM | 212510 | 8610 | Urban | Pole changeover | 2 | 300 | 600 | 0.00067027 | 2.2342e-06
2012-07-30 11:00AM | 212136 | L947 | Rural Short | Commission to SCADA LBS 90536 Kentucky Dr Glossodia. | 36 | 300 | 10800 | 0.012065 | 4.0216e-05
2012-07-31 06:30AM | 210673 | M391 | Rural Short | Augment 11kV OH mains install new LBS and pole. Remove 2 x USL.Remove pole. Transmission Mains works. | 3 | 690 | 2070 | 0.0023124 | 3.3514e-06
2012-07-31 08:00AM | 209436 | 35693 | Rural Short | augment hv mainschange pole and augment 2 bays of lv | 109 | 540 | 58860 | 0.065754 | 0.00012177
2012-07-31 08:00AM | 210711 | 10289 | Rural Short | Remove ABS 77275 and install auto recloser 29561. Remove DOF's 29829 and bond through | 44 | 480 | 21120 | 0.023594 | 4.9153e-05
2012-07-31 08:00AM | 208380 | B204 | Urban | HVSWGR MAINT | 101 | 360 | 36360 | 0.040618 | 0.00011283
2012-07-31 08:00AM | 209318 | 5875 | Urban | New DOF install | 214 | 480 | 51840 | 0.057911 | 0.00023906
2012-07-31 08:00AM | 212036 | 1109 | Urban | 1 AUGMENT HV MAINS TO 7/4.50AAC.2 AUGMENT HV MAINS TO 19/3.25AAC. | 200 | 585 | 117000 | 0.1307 | 0.00022342
2012-07-31 08:00AM | 212046 | 10250 | Urban | Repair/Replace HV Hardware pole 338 Replace HV tie pole334 Replace HV Arms Sub 9374 | 100 | 450 | 45000 | 0.05027 | 0.00011171
2012-07-31 08:00AM | 212495 | 8620 | Urban | Isolate 2 LV distributors Remove cables. | 26 | 270 | 7020 | 0.0078422 | 2.9045e-05
2012-07-31 08:00AM | 212581 | B713 | Urban | Remove LV cable from Pillar Relocate into Sub 27446. Install LV fuse strip | 4 | 300 | 1200 | 0.0013405 | 4.4685e-06
2012-07-31 08:00AM | 212596 | D852 | Urban | Replace Condemned Pole | 6 | 480 | 2880 | 0.0032173 | 6.7027e-06
2012-07-31 08:30AM | 210595 | HBA2 | Rural Short | Replace Condemned Pole 3KA1533KA154 3KA149 and 3KA150 | 6 | 420 | 2100 | 0.002346 | 6.7027e-06
2012-07-31 08:30AM | 211077 | GG1232 | Rural Short | REPLACE POLE 4KX039 REPLACE HV ARMS and RETRO SUB 40944 REPLACE HV and LV ARMS POLE 4KX048 REPLACE HV HARDWARE POLES 4PA212 and 4PA215 STRAIGHTEN POLE 4PA211 . | 9 | 360 | 3240 | 0.0036195 | 1.0054e-05
2012-07-31 08:30AM | 211341 | MGD2 | Rural Short | Augment Hv Mains between Poles 3V0754 and 830320 Wilson Dr Hilltop | 16 | 450 | 7200 | 0.0080433 | 1.7874e-05
2012-07-31 09:00AM | 210687 | SXC2 | Rural Short | Replace pole Install New pole ( 1 and 2 ) and Aug HV to CCTPrinces Hwy WANDANDIAN. | 55 | 360 | 19800 | 0.022119 | 6.1442e-05
2012-07-31 09:00AM | 212290 | B718 | Urban | Consac Replacement | 24 | 360 | 8640 | 0.0096519 | 2.6811e-05
2012-07-31 09:00AM | 212773 | 8610 | Urban | LV Pole change | 15 | 360 | 5400 | 0.0060324 | 1.6757e-05
2012-07-31 09:00AM | 212919 | B709 | Urban | Replace LV Switchboard in Column 8598 | 38 | 240 | 9120 | 0.010188 | 4.2451e-05
2012-08-01 08:00AM | 210271 | DP1284 | Rural Short | NEW PAD SUBSTATIONS and RECLOSER | 10 | 510 | 5100 | 0.0056973 | 1.1171e-05
2012-08-01 08:00AM | 210662 | W188 | Rural Short | Remove existing Pole Sub No.10859 and associated mains Leichardt Rd Bardia. Install new 63kVA Pole Sub No.29843 Zouch Rd Bardia. | 5 | 540 | 2700 | 0.0030162 | 5.5856e-06
2012-08-01 08:00AM | 212011 | R210 | Rural Short | Retofit Sub 9191 Sub 11019 Sub 20369 Sub10976 and replace TX | 167 | 450 | 75150 | 0.083952 | 0.00018656
2012-08-01 08:00AM | 212291 | W163 | Rural Short | AUGMENT HV MAINSINSTALL LBS and DOF'S REMOVE HV MAINS and ABS | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2012-08-01 08:00AM | 208776 | 5506 | Urban | HV Augmentation | 108 | 540 | 58320 | 0.06515 | 0.00012065
2012-08-01 08:00AM | 209887 | AZ1227 | Urban | REPLACE CONDEMNED POLE | 51 | 480 | 24480 | 0.027347 | 5.6973e-05
2012-08-01 08:00AM | 210092 | 9025 | Urban | REPLACE CONDEMNED POLE # 196 - RACECOURSE RD PENRITH | 53 | 480 | 25440 | 0.02842 | 5.9207e-05
2012-08-01 08:00AM | 210165 | 35315 | Urban | Replace Sub 12 with new Sub 32159 pole 833144. Install new LBS 95225 on pole 833139. Install new ABS 90932 on new pole 833142. Install new HV 180mm CCT mains from pole 833137 to pole 833145. Augment HV mains to 180mm CCT from pole 833145 to pole 833147. | 49 | 480 | 23520 | 0.026275 | 5.4739e-05
2012-08-01 08:00AM | 211016 | CRF2 | Urban | Replace poles and retrofit | 245 | 450 | 110250 | 0.12316 | 0.00027369
2012-08-01 08:00AM | 212342 | R215 | Urban | New LV circuits. | 18 | 420 | 7560 | 0.0084454 | 2.0108e-05
2012-08-01 08:00AM | 212917 | 35696 | Urban | repair UG cable | 26 | 480 | 12480 | 0.013942 | 2.9045e-05
2012-08-01 08:30AM | 210310 | 8636 | Rural Short | 1) RETENSION RIVER CROSSING 76 and INSTALL VIBRATION DAMPERS ON SPAN.2) RETRO SUB 15257 and REPLACE HV X-ARM. | 17 | 420 | 7140 | 0.0079762 | 1.8991e-05
2012-08-01 08:30AM | 211460 | DP1284 | Rural Short | Restrain HV Mains 4AD002 and 4AG179 Retro sub 43123 Replace polecaps poles 4AG179 and 4AG180 Install vibration dampers poles 4AD007 4AD006 and 4AD005 | 5 | 300 | 1500 | 0.0016757 | 5.5856e-06
2012-08-01 08:30AM | 211876 | MVF2 | Rural Short | Replace Poles Install New poles Install DOFs 91481 and Augment a section of 11KV O/H Mains | 12 | 450 | 5400 | 0.0060324 | 1.3405e-05
2012-08-01 08:30AM | 211086 | KMA2 | Urban | REPLACE ABS 71913 WITH LBS 93269 and ABS 71909 WITH LBS 93270 | 363 | 420 | 152460 | 0.17032 | 0.00040551
2012-08-01 08:30AM | 212309 | 7962 | Urban | Condemned Pole | 8 | 390 | 3120 | 0.0034854 | 8.937e-06
2012-08-01 09:30AM | 211700 | ULJ2 | Rural Short | Install New LBS 95490Tuckerman Rd ULLADULLA. | 24 | 270 | 6480 | 0.0072389 | 2.6811e-05
2012-08-01 09:30AM | 212025 | KVB2 | Rural Short | REPLACE POLE 1RJ017 AT SUB 50168 | 50 | 300 | 15000 | 0.016757 | 5.5856e-05
2012-08-01 11:00AM | 212511 | 3358 | Urban | LV Crossarm change | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2012-08-02 08:00AM | 210011 | S786 | Rural Short | Remove ABS 52117 and bond through @ pole 771899 Install mid span pole with auto LBS and retro sub 1493 | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2012-08-02 08:00AM | 210870 | 77674 | Rural Short | Isolate 11kV O/H Mains below Fdr 828/4 to allow the replacement of 66kV ABS 35091 | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2012-08-02 08:00AM | 211300 | MGE2 | Rural Short | Replace pole 3R1324 and install new Dof's 91902 (20amp)and Augment Mains to 3X7/4.50 | 13 | 480 | 6240 | 0.0069708 | 1.4523e-05
2012-08-02 08:00AM | 211594 | GG1295 | Rural Short | REPLACE UGOH RETROFIT SUBS REPLACE POLE CAP | 7 | 510 | 3570 | 0.0039881 | 7.8198e-06
2012-08-02 08:00AM | 212287 | W163 | Rural Short | AUGMENT HV MAINS | 16 | 480 | 7680 | 0.0085795 | 1.7874e-05
2012-08-02 08:00AM | 208539 | 8610 | Urban | HV Augmentation | 240 | 540 | 65880 | 0.073596 | 0.00026811
2012-08-02 08:00AM | 210380 | B720 | Urban | REPLACE LV SW GR + REPUMP SW 12761 + HV SW GR MAINT SUB 1831 | 74 | 420 | 31080 | 0.03472 | 8.2667e-05
2012-08-02 08:00AM | 210503 | 19856 | Urban | Augment 6 bays of O/H LV mains under HV mains. | 63 | 540 | 34020 | 0.038004 | 7.0379e-05
2012-08-02 08:00AM | 211925 | RV1280 | Urban | Replace pole and retrofit | 174 | 420 | 73080 | 0.081639 | 0.00019438
2012-08-02 08:00AM | 212092 | 9056 | Urban | POLE REPLACEMENT X 2 + AUGMENT HV MAINS X 4 BAYS | 513 | 570 | 292410 | 0.32666 | 0.00057308
2012-08-02 08:00AM | 212665 | 41367 | Urban | Spike and ID cable Install 1 new Pillar relocate 2 pillars and Column | 6 | 420 | 2520 | 0.0028151 | 6.7027e-06
2012-08-02 08:30AM | 211227 | GG1295 | Rural Short | AUGMENT HV MAINS BETWEEN POLES 824775 and 212620 | 12 | 420 | 5040 | 0.0056303 | 1.3405e-05
2012-08-02 08:30AM | 211436 | JBA2 | Rural Short | Install Vibration Dampers pole 4JT008 | 12 | 180 | 2160 | 0.002413 | 1.3405e-05
2012-08-02 08:30AM | 212439 | A049 | Rural Short | To replace poles | 11 | 390 | 4290 | 0.0047924 | 1.2288e-05
2012-08-02 09:00AM | 212513 | 35333 | Urban | Lv changeover | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2012-08-02 09:00AM | 212645 | UNB2 | Urban | Connect new URD to Padmount Sub 41289 | 17 | 300 | 5100 | 0.0056973 | 1.8991e-05
2012-08-02 09:00AM | 212998 | 19870 | Urban | Underground Project | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2012-08-02 09:30AM | 211248 | T836 | Rural Short | Uprate PS 15180 to 63KVA | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2012-08-02 09:30AM | 211778 | 35982 | Rural Short | Install Vibration Dampers and repair HV defects | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2012-08-02 09:45AM | 211746 | 35982 | Rural Short | Install Vibration Dampers Between poles 772490 and 69 and Repair HV defects | 23 | 255 | 5865 | 0.0065519 | 2.5694e-05
2012-08-03 08:00AM | 210619 | 8633 | Rural Short | LIVE LINE RETRO SUB 7974 | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2012-08-03 08:00AM | 211087 | 27446 | Rural Short | augment hv mains | 57 | 540 | 30780 | 0.034385 | 6.3676e-05
2012-08-03 08:00AM | 211394 | MGD2 | Rural Short | Augment HV mains and Redirect existing line plus install new Dof's 92640 | 58 | 480 | 27840 | 0.031101 | 6.4793e-05
2012-08-03 08:00AM | 212128 | 10245 | Rural Short | Retrofit Sub 9449 | 62 | 450 | 27900 | 0.031168 | 6.9261e-05
2012-08-03 08:00AM | 208789 | L544 | Urban | HV Augmentation | 68 | 480 | 32640 | 0.036463 | 7.5964e-05
2012-08-03 08:00AM | 210564 | 8620 | Urban | Uprate Sub 5011 Uprate 2 bays LV to ABC | 24 | 420 | 10080 | 0.011261 | 2.6811e-05
2012-08-03 08:00AM | 211581 | 1132 | Urban | Replace Pole 1. Erect D.O.F. 91900 on pole 2.Augment 11KV O.H. mains to 7/4.50 AAC from pole 1. to pole 2. | 88 | 420 | 36960 | 0.041289 | 9.8307e-05
2012-08-03 08:00AM | 212523 | CT1225 | Urban | Retro Sub 11657. | 10 | 420 | 4200 | 0.0046919 | 1.1171e-05
2012-08-03 08:30AM | 212442 | A049 | Rural Short | To replace poles | 14 | 390 | 5460 | 0.0060995 | 1.564e-05
2012-08-03 08:30AM | 212775 | X479 | Rural Short | REPLACE HV CROSSARMS.BUSHFIRE DEFECTS | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2012-08-03 08:30AM | 210106 | J516 | Urban | Repair USL P219. | 85 | 300 | 25500 | 0.028487 | 9.4955e-05
2012-08-03 08:30AM | 211331 | WWF2 | Urban | AUGMENT HV MAINS REPLACE 71547 and POLES 2P0390 2P0386 2P0385 2P0384 2P0383 | 289 | 420 | 121380 | 0.1356 | 0.00032285
2012-08-03 08:30AM | 212003 | WBB2 | Urban | Tap Change on Sub 40108 | 18 | 240 | 4320 | 0.004826 | 2.0108e-05
2012-08-03 08:30AM | 213120 | S776 | Urban | LV Interruption - Lilac St South Penrith | 23 | 330 | 7590 | 0.0084789 | 2.5694e-05
2012-08-03 09:00AM | 211722 | R218 | Rural Short | Install DOFs @ pole 825558. and Augment HV conductors from pole 784661 to J572 change over stay wire at J572 and remove pole | 38 | 420 | 15960 | 0.017829 | 4.2451e-05
2012-08-03 09:00AM | 212698 | RBD2 | Rural Short | Limited district switchingReplace L/A's and install LV fuses @ sub 30760 | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2012-08-03 09:00AM | 212516 | 3351 | Urban | Lv Changeover | 4 | 180 | 720 | 0.00080433 | 4.4685e-06
2012-08-03 09:30AM | 212280 | CLA2 | Rural Short | REPLACE POLE No 3DG272 | 34 | 330 | 11220 | 0.012534 | 3.7982e-05
2012-08-04 07:00AM | 212292 | J481 | Urban | Uprate HV switchgear in PM 13638 to 3 feeder safelink and terminate new cable. Remove SS 15460 and STJ cables to maintain circuitry. Install new 500KVA PM's 29275 and 29276. Terminate new cable to PM 13131. | 1 | 600 | 600 | 0.00067027 | 1.1171e-06
2012-08-04 07:00AM | 213000 | 35767 | Urban | HOLD POLE 1498 HARRIS ST ST MARYS WHILE SYDNEY WATER EXCAVATE AROUND BASE OF POLE | 4 | 600 | 2400 | 0.0026811 | 4.4685e-06
2012-08-04 07:30AM | 212179 | 1112 | Urban | AUGMENT HV MAINS X 11 BAYS | 94 | 630 | 59220 | 0.066156 | 0.00010501
2012-08-05 07:00AM | 210467 | 3106 | Urban | Augment Hv mains to 7/4.5 AAC Sub 146 to pole 789433. Replace ABS 5111 with new ABS 90934. | 173 | 600 | 103800 | 0.11596 | 0.00019326
2012-08-05 07:00AM | 211999 | 8617 | Urban | MandR HVSWGR @ SUB 17894 | 28 | 300 | 4200 | 0.0046919 | 3.1279e-05
2012-08-05 08:00AM | 212242 | X879 | Rural Short | To allow staff to Replace Condemned Pole # 209 and TX at Sub 10969 at Heath Rd Leppington | 21 | 480 | 10080 | 0.011261 | 2.346e-05
2012-08-05 08:00AM | 208788 | 4857 | Urban | AUGMENT SECTION OF O/H HV MAINS TO 7/4.50 AAC | 10 | 540 | 5400 | 0.0060324 | 1.1171e-05
2012-08-05 08:00AM | 209995 | CRB2 | Urban | REPLACE POLES and AUGMENT | 73 | 450 | 32850 | 0.036697 | 8.155e-05
2012-08-05 08:00AM | 212938 | 9056 | Urban | LV Changeover | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2012-08-05 09:00AM | 212814 | MVD2 | Rural Short | Replace Condemned Pole 3K1546 | 16 | 390 | 3120 | 0.0034854 | 1.7874e-05
2012-08-05 11:00PM | 208067 | 1960 | Urban | HVSWGR MAINT | 23 | 360 | 8280 | 0.0092498 | 2.5694e-05
2012-08-06 06:30PM | 203560 | BDE2 | Urban | MandR HV Switchgear @ S/S 51630. | 5 | 270 | 1350 | 0.0015081 | 5.5856e-06
2012-08-06 07:30AM | 211272 | 41535 | Urban | REPLACE CONDEMNED POLE # 1674 and USL # A179 - OFF DEBRINCAT AVE NORTH ST MARYS | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2012-08-06 08:00AM | 187656 | X877 | Rural Short | Retro Sub 15363 and Replace Tx . | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2012-08-06 08:00AM | 212444 | 35816 | Rural Short | Rectify defect D920 on Sub 29873 | 9 | 300 | 2700 | 0.0030162 | 1.0054e-05
2012-08-06 08:00AM | 210618 | 25783 | Urban | Remove:1 x pole HV OH mainsInstall:1 x new pole 1 x HV UGOH HV UG cable new PS 29626 | 28 | 540 | 8100 | 0.0090487 | 3.1279e-05
2012-08-06 08:00AM | 210979 | 1106 | Urban | Augment 9 bays of hv mains + replace 1 pole + ABS.Upgrade 2 x abs guildford rd. | 328 | 600 | 196800 | 0.21985 | 0.00036642
2012-08-06 08:30AM | 213062 | X492 | Rural Long | REPAIR HV DEFECT(PSBI) | 20 | 180 | 2880 | 0.0032173 | 2.2342e-05
2012-08-06 08:30AM | 212221 | ULJ2 | Rural Short | Install new 25 kVA Sub on replacement pole | 9 | 450 | 4050 | 0.0045243 | 1.0054e-05
2012-08-06 08:30AM | 212993 | JBA2 | Rural Short | REPLACE POLE 4HV044 | 1 | 300 | 300 | 0.00033514 | 1.1171e-06
2012-08-06 08:45AM | 212183 | BYF2 | Rural Short | Install LV UGOH to existing Transformer Pole 789835 | 23 | 330 | 7590 | 0.0084789 | 2.5694e-05
2012-08-06 09:30AM | 212920 | HBA2 | Rural Short | Replace street light | 20 | 180 | 3600 | 0.0040216 | 2.2342e-05
2012-08-07 01:00PM | 212995 | S335 | Urban | Replace Rusty Column | 11 | 120 | 1320 | 0.0014746 | 1.2288e-05
2012-08-07 03:00PM | 212192 | T866 | Urban | Replace LV switchgear in PM 12477 | 20 | 30 | 600 | 0.00067027 | 2.2342e-05
2012-08-07 08:00AM | 211123 | L946 | Rural Short | Replace condemned pole 206 | 8 | 390 | 3120 | 0.0034854 | 8.937e-06
2012-08-07 08:00AM | 212408 | X879 | Rural Short | To allow staff to Retrofit Subs 10628 and 11935 Eastwood Rd Leppington. | 24 | 480 | 6720 | 0.007507 | 2.6811e-05
2012-08-07 08:00AM | 212800 | HKA2 | Rural Short | REPLACE POLE 2DX033 WITH POLE 829504 AND POLE 2DX037 WITH POLE 829505.AUGMENT 5 BAYS OF HV MAINS TO 19/3.25AAC FROM POLE 829504 TO POLE 767233. | 154 | 480 | 73920 | 0.082578 | 0.00017204
2012-08-07 08:00AM | 209329 | R250 | Urban | Install new DOF | 47 | 480 | 22560 | 0.025202 | 5.2505e-05
2012-08-07 08:00AM | 210509 | CRB2 | Urban | Replace poles and augment | 98 | 450 | 22500 | 0.025135 | 0.00010948
2012-08-07 08:00AM | 211608 | 4374 | Urban | Replace poles 406 with 814704 and 409 with 814703. ABS 82790 to be installed on pole 814703 | 52 | 480 | 24960 | 0.027883 | 5.809e-05
2012-08-07 08:00AM | 212192 | T866 | Urban | Replace LV switchgear in PM 12477 | 20 | 30 | 600 | 0.00067027 | 2.2342e-05
2012-08-07 08:00AM | 212821 | 3185 | Urban | LV ABC - Remove O/W | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2012-08-07 08:00AM | 213400 | 35702 | Urban | REPLACE POLE | 21 | 480 | 10080 | 0.011261 | 2.346e-05
2012-08-07 08:30AM | 212310 | MVF2 | Rural Short | Replace Poles and Augment a section of 11KV O/H Mains | 14 | 450 | 6300 | 0.0070379 | 1.564e-05
2012-08-07 08:30AM | 212903 | A049 | Rural Short | To replace poles | 13 | 420 | 5460 | 0.0060995 | 1.4523e-05
2012-08-07 09:00AM | 213013 | X217 | Rural Short | REPAIR PSBI'S and INSTALL VIBRATION DAMPERS | 11 | 360 | 3960 | 0.0044238 | 1.2288e-05
2012-08-07 09:00AM | 212996 | S326 | Urban | Replace Rusty Column | 27 | 240 | 6480 | 0.0072389 | 3.0162e-05
2012-08-07 09:00AM | 213111 | 27188 | Urban | Replace Rust Column | 19 | 240 | 4560 | 0.0050941 | 2.1225e-05
2012-08-07 09:00PM | 211637 | WRC2 | Urban | REPLACE POLE 1D0712 and ABS 72829 REPLACE POLE 1D0728 RETRO SUB 42083 REPLACE HV ARM POLE 1D0732 RETRO SUB 41844 . REMOVE LIVE LINKS POLE 1D0282 . | 124 | 540 | 66960 | 0.074802 | 0.00013852
2012-08-08 08:00AM | 209447 | 35693 | Rural Short | augment hv mains | 113 | 540 | 61020 | 0.068167 | 0.00012623
2012-08-08 08:00AM | 211287 | X879 | Rural Short | Retro Subs 10841 10894 and 11985. | 40 | 480 | 19200 | 0.021449 | 4.4685e-05
2012-08-08 08:00AM | 211566 | X802 | Rural Short | INSTAL NEW USL'S and BYPASS DOFS.REPAIR HV DEFECTS and INSTALL VIBRATION DAMPERS (VARIOUS LOCATIONS) | 29 | 420 | 12180 | 0.013607 | 3.2396e-05
2012-08-08 08:00AM | 211935 | P608 | Rural Short | Install vibartion dampers Replace DOF's @ Subs 10524 and11037 And replace MDI @ Sub 10079 | 11 | 510 | 5610 | 0.006267 | 1.2288e-05
2012-08-08 08:00AM | 211938 | 35989 | Rural Short | Pull in new OPGW line from Pole 1 Peel St. to Pole 25 near Douglas Park Drive Wilton for 66kV Feeder 869/2. This outage is for clearance purposes. | 86 | 480 | 41280 | 0.046115 | 9.6072e-05
2012-08-08 08:00AM | 208790 | 17038 | Urban | HV Augmentation | 222 | 540 | 119880 | 0.13392 | 0.000248
2012-08-08 08:00AM | 211364 | 1125 | Urban | Allow staff to augment section of HV overhead and maintenance on poles | 157 | 480 | 75360 | 0.084186 | 0.00017539
2012-08-08 08:00AM | 211390 | 7966 | Urban | REPLACE CONDEMNED POLE 248 AND MandR ABS 8365 | 28 | 480 | 13440 | 0.015014 | 3.1279e-05
2012-08-08 08:00AM | 211472 | 46477 | Urban | Replace condemned pole 184 replace HV X-arm @ pole 189 and replace condemned LV pole 205 | 6 | 420 | 2520 | 0.0028151 | 6.7027e-06
2012-08-08 08:00AM | 211609 | BLD2 | Urban | RETENSION MAINS AND CONTRACTOR TREE TRIMMING | 62 | 360 | 22320 | 0.024934 | 6.9261e-05
2012-08-08 08:00AM | 212828 | R253 | Urban | Replace Pole | 34 | 300 | 10200 | 0.011395 | 3.7982e-05
2012-08-08 08:00AM | 213115 | 4880 | Urban | INSTALL NEW L.V. 3 WAY SW and RE-DIRECT EXISTING L.V. CABLE and INSTALL NEW L.V.CABLE . | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2012-08-08 08:30AM | 210585 | 35315 | Urban | Stand/Replace poles for future Hv augment. Changeover existing mains. Replace existing USL 193 with new LBS 90933 | 250 | 420 | 52500 | 0.058649 | 0.00027928
2012-08-08 08:30AM | 211974 | WBB2 | Urban | Replace Condemned Poles 3PR356 and 3PR325 | 36 | 420 | 15120 | 0.016891 | 4.0216e-05
2012-08-08 08:30AM | 212317 | HBB2 | Urban | REPLACE UGOH | 1 | 450 | 450 | 0.0005027 | 1.1171e-06
2012-08-08 09:00AM | 211813 | CLD2 | Rural Short | To change L/V condemned pole 3HP243 | 17 | 240 | 4080 | 0.0045578 | 1.8991e-05
2012-08-08 09:00AM | 213365 | B748 | Urban | Replace poles 1694 and 1695 | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2012-08-08 09:30AM | 210672 | A347 | Urban | Install new DOF | 70 | 450 | 31500 | 0.035189 | 7.8198e-05
2012-08-08 10:00PM | 212200 | MYE2 | Rural Short | CLEARANCE ISOLATION TO ALLOW RMS TO INSTALL NEW SIGNAGE ON MOUNT OUSLEY | 3 | 330 | 990 | 0.0011059 | 3.3514e-06
2012-08-08 11:00AM | 212831 | 19857 | Urban | Replace Pole | 11 | 300 | 3300 | 0.0036865 | 1.2288e-05
2012-08-09 08:00AM | 207819 | HKD2 | Rural Short | AUGMENT 6 BAYS OF HV MAINS TO 120 CCT. | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2012-08-09 08:00AM | 211646 | NA1207 | Rural Short | REPLACE 2 POLES No's 2XR030 and 228654 also INSTALL 3 STAY POLES No's 847474 847475 847476 and REQUIRED AERIAL STAYS | 49 | 480 | 23520 | 0.026275 | 5.4739e-05
2012-08-09 08:00AM | 212286 | R211 | Rural Short | Retro And Replace TX at Sub 1098 | 1 | 390 | 390 | 0.00043568 | 1.1171e-06
2012-08-09 08:00AM | 208541 | 1957 | Urban | HV Augmentation | 44 | 540 | 17820 | 0.019907 | 4.9153e-05
2012-08-09 08:00AM | 210504 | 19856 | Urban | Augment 6 bays of O/H LV mains under HV mains. | 56 | 540 | 30240 | 0.033782 | 6.2559e-05
2012-08-09 08:00AM | 211017 | CRF2 | Urban | Replace poles and augment | 94 | 450 | 42300 | 0.047254 | 0.00010501
2012-08-09 08:00AM | 211113 | 4857 | Urban | AUGMENT SECTION OF 11 KV TO 7/4.50 AAC REPLACE LEAKING TX SUB 658 | 5 | 480 | 2400 | 0.0026811 | 5.5856e-06
2012-08-09 08:00AM | 211954 | T888 | Urban | CHANGE 2 POLES and AUGMENT LV MAINS | 23 | 540 | 12420 | 0.013875 | 2.5694e-05
2012-08-09 08:00AM | 213148 | S785 | Urban | repair defects | 124 | 480 | 59520 | 0.066491 | 0.00013852
2012-08-09 08:00AM | 213310 | 8620 | Urban | Isolate 2 LV distributors Remove cables. | 26 | 270 | 7020 | 0.0078422 | 2.9045e-05
2012-08-09 08:00AM | 213539 | AZ1227 | Urban | 48Hr Pole Replacement | 27 | 480 | 12960 | 0.014478 | 3.0162e-05
2012-08-09 08:30AM | 211026 | 8802 | Rural Short | Retro rewire HV and LV arms links and fuses @ sub 2857.Retro rewire fuses and replace Tx @ sub 11619 | 26 | 420 | 10920 | 0.012199 | 2.9045e-05
2012-08-09 08:30AM | 211919 | 57448 | Rural Short | REPLACE CONDEMNED POLE 3 | 3 | 390 | 1170 | 0.001307 | 3.3514e-06
2012-08-09 08:30AM | 211932 | KME2 | Rural Short | AUGMENT HV MAINS | 8 | 300 | 2400 | 0.0026811 | 8.937e-06
2012-08-09 08:30AM | 212905 | A049 | Rural Short | Augment LV mains/change over poles | 16 | 420 | 6720 | 0.007507 | 1.7874e-05
2012-08-09 08:30AM | 212301 | KMD2 | Urban | M and R Holec Sub 41119 | 54 | 240 | 12960 | 0.014478 | 6.0324e-05
2012-08-09 08:30AM | 212490 | 7974 | Urban | 3 x changeover poles | 11 | 420 | 4620 | 0.0051611 | 1.2288e-05
2012-08-09 08:30AM | 213529 | B713 | Urban | TO install LV links in pillar 51226 | 45 | 270 | 12150 | 0.013573 | 5.027e-05
2012-08-09 09:00AM | 211359 | MGD2 | Rural Short | Install LV fuses at Sub 31753 | 4 | 180 | 720 | 0.00080433 | 4.4685e-06
2012-08-09 09:00AM | 211576 | H745 | Rural Short | Change Pole 135 | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2012-08-09 09:00AM | 212463 | RBA2 | Rural Short | Full retro and fit LV fuses Sub 30475 | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2012-08-09 09:00AM | 213165 | 35333 | Urban | LV pole change over | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2012-08-09 09:00AM | 213224 | L508 | Urban | Install a new LV cable into Pillar 3743 | 103 | 300 | 30900 | 0.034519 | 0.00011506
2012-08-09 09:30AM | 209657 | ULJ2 | Rural Short | Replace Condemned pole 2KA013 - S/S 72602Princes Hwy MILTON | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2012-08-09 10:30AM | 212668 | APE2 | Urban | MandR HOLIC S/S 42483 | 196 | 240 | 47040 | 0.052549 | 0.00021896
2012-08-10 07:30AM | 210372 | 16666 | Urban | REPLACE LV S/GEAR SUB 17232. BETTS RD PARRAMATTA | 59 | 510 | 30090 | 0.033614 | 6.591e-05
2012-08-10 08:00AM | 210665 | 8711 | Rural Short | Augment O/H mains replace USL 666 | 86 | 540 | 46440 | 0.051879 | 9.6072e-05
2012-08-10 08:00AM | 211256 | X879 | Rural Short | Retro Sub 10670 and Replace Tx. | 17 | 360 | 6120 | 0.0068368 | 1.8991e-05
2012-08-10 08:00AM | 212492 | 57448 | Rural Short | COMMISSION RECLOSERINSTALL VIBRATION DAMPERSREPLACE HV CROSSARMS and RETROFIT SUB | 40 | 420 | 16800 | 0.018768 | 4.4685e-05
2012-08-10 08:00AM | 212783 | W111 | Rural Short | Pull in new OPGW line from Pole 25 to Pole 27 and string new 66kV 61/3.25 AAC Conductor from Pole 15 to Pole 27 for new Fdr 869/2. This outage is for clearance purposes. | 102 | 480 | 48960 | 0.054694 | 0.00011395
2012-08-10 08:00AM | 210679 | B205 | Urban | REPLACE POLE 184 | 33 | 480 | 15840 | 0.017695 | 3.6865e-05
2012-08-10 08:00AM | 211690 | 4370 | Urban | Replace pole 420 with pole 814699 and replace pole 354 with pole 814702. | 89 | 480 | 42720 | 0.047723 | 9.9424e-05
2012-08-10 08:00AM | 212080 | MR2298 | Urban | HV TEST TO FAULT FIND HV CABLE FAULT BETWEEN SW 80951 SUB 28272 and SW 39055 SUB 23001 | 35 | 420 | 14700 | 0.016422 | 3.9099e-05
2012-08-10 08:30AM | 210732 | D814 | Rural Short | Install HV Vibration Dampeners Adj Pole 42 Pole 762678 Pole 762679 Pole 77 Pole 764764 Pole 764839 Pole 74 USL 52969 and SUB 4988 | 13 | 420 | 5460 | 0.0060995 | 1.4523e-05
2012-08-10 08:30AM | 212002 | H745 | Rural Short | Install new ABS 86798 augmment mains from sub 17066 to pole 822268 | 29 | 450 | 13050 | 0.014578 | 3.2396e-05
2012-08-10 08:30AM | 212604 | DFA2 | Rural Short | REPLACE HV CROSSARMS as per BUSHFIRE DEFECTS | 5 | 270 | 1350 | 0.0015081 | 5.5856e-06
2012-08-10 08:30AM | 213268 | A049 | Rural Short | Augment LV OH mains 150 ABC | 8 | 390 | 3120 | 0.0034854 | 8.937e-06
2012-08-10 08:30AM | 211549 | BLE2 | Urban | REPLACE POLES RETROFIT SUB VARIOUS DEFECTS IN AREA | 155 | 420 | 65100 | 0.072725 | 0.00017315
2012-08-10 08:30AM | 212680 | SHB2 | Urban | REPLACE LV ARMS POLES 1D0480 1D0481 1D0482 1D0485 1D0487 1D0489 1D0526 and 1D0530 . | 92 | 390 | 35880 | 0.040082 | 0.00010278
2012-08-10 08:30AM | 213480 | S776 | Urban | construction | 27 | 210 | 5670 | 0.0063341 | 3.0162e-05
2012-08-10 09:00AM | 208433 | CLD2 | Rural Short | REPLACE POLE 3HP148 - ABS 30796 WITH NEW LBS 95262 | 11 | 300 | 3300 | 0.0036865 | 1.2288e-05
2012-08-10 09:00AM | 213162 | 16649 | Urban | Change pole over | 8 | 420 | 3360 | 0.0037535 | 8.937e-06
2012-08-10 09:00AM | 213453 | 49362 | Urban | Consac Replacement | 77 | 360 | 27720 | 0.030967 | 8.6018e-05
2012-08-10 09:30AM | 213368 | CLA2 | Rural Short | REPAIR STREET LIGHT COLUMN | 104 | 150 | 15600 | 0.017427 | 0.00011618
2012-08-10 10:00AM | 213375 | 8718 | Urban | REMOVE CONDEMNED POLE 58 | 12 | 240 | 2880 | 0.0032173 | 1.3405e-05
2012-08-10 10:30PM | 212502 | 1106 | Urban | AUGMENT 1 BAY OF HV MAINS | 37 | 300 | 11100 | 0.0124 | 4.1333e-05
2012-08-11 05:00PM | 211267 | A317 | Urban | establish new pad sub 29693 | 192 | 30 | 5760 | 0.0064346 | 0.00021449
2012-08-11 06:30AM | 211267 | A317 | Urban | establish new pad sub 29693 | 192 | 30 | 5760 | 0.0064346 | 0.00021449
2012-08-11 08:00AM | 212010 | 55885 | Urban | Replace poles.Replace USL L737 with LBS 93268 | 79 | 420 | 33180 | 0.037066 | 8.8252e-05
2012-08-12 08:00AM | 212566 | R260 | Rural Short | RETROFIT SUBS and REPAIR USL'S | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2012-08-12 08:00AM | 209321 | T889 | Urban | HV Augmentation | 142 | 540 | 76680 | 0.085661 | 0.00015863
2012-08-12 08:00AM | 209323 | T889 | Urban | Upgrade HV cross arm | 68 | 300 | 20400 | 0.022789 | 7.5964e-05
2012-08-12 08:30AM | 212345 | 35989 | Rural Short | retrofit substation 10485 | 4 | 450 | 1800 | 0.0020108 | 4.4685e-06
2012-08-12 08:30AM | 210807 | B743 | Urban | REPLACE TRANSFORMER SUB 9955 AND DOF POLE 1652 | 4 | 330 | 660 | 0.0007373 | 4.4685e-06
2012-08-13 08:00AM | 208786 | 8635 | Rural Short | HV Augmentation | 26 | 480 | 12480 | 0.013942 | 2.9045e-05
2012-08-13 08:00AM | 211878 | L948 | Rural Short | remove usl and install new auto recloser | 40 | 480 | 19200 | 0.021449 | 4.4685e-05
2012-08-13 08:00AM | 212902 | HKA2 | Rural Short | REPLACE POLE 2DK030 WITH POLE 829590 POLE 2DK034 WITH POLE 829593. INSTALL NEW POLE 829591 AND POLE 829592. REMOVE POLE 2DK033. INSTALL NEW HVUSL No ON POLE 829591.AUGMENT 7 BAYS OF HV MAINS TO 7/4.50AAC. | 30 | 480 | 14400 | 0.016087 | 3.3514e-05
2012-08-13 09:00AM | 212064 | W111 | Rural Short | Change pole substation 10725 | 61 | 420 | 25620 | 0.028621 | 6.8144e-05
2012-08-13 09:00AM | 213243 | MGD2 | Rural Short | Replace Condemed LV pole 3V0039 | 11 | 300 | 3300 | 0.0036865 | 1.2288e-05
2012-08-13 09:00AM | 212661 | J500 | Urban | To MandR H/V SW/Gear @ Sub 11311 Bangala Ave Bradbury. | 77 | 300 | 23100 | 0.025805 | 8.6018e-05
2012-08-13 09:00AM | 213408 | 8610 | Urban | LV Pole changeover | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2012-08-13 09:00AM | 213543 | 52238 | Urban | Replace Streetlight Column | 15 | 210 | 3150 | 0.0035189 | 1.6757e-05
2012-08-13 10:00AM | 213620 | CLC2 | Urban | REPLACE POLE 3GA167 | 105 | 240 | 25200 | 0.028151 | 0.0001173
2012-08-14 05:00PM | 213545 | 1123 | Urban | REMOVE SUB 5255 GILBERT ST CABRAMATTA AND INSTALL NEW PAD SUB 28850 REPLAVE CAST IRON POT HEAD AND HV UNDERGROUND CABLE FROM O/H 11 KV MAIN IN GILBERT ST | 2020 | 30 | 15150 | 0.016924 | 0.0022566
2012-08-14 07:30AM | 209040 | 27202 | Urban | HV SW GR MAINT | 65 | 360 | 23400 | 0.026141 | 7.2613e-05
2012-08-14 07:30AM | 213545 | 1123 | Urban | REMOVE SUB 5255 GILBERT ST CABRAMATTA AND INSTALL NEW PAD SUB 28850 REPLAVE CAST IRON POT HEAD AND HV UNDERGROUND CABLE FROM O/H 11 KV MAIN IN GILBERT ST | 2020 | 30 | 15150 | 0.016924 | 0.0022566
2012-08-14 08:00AM | 206712 | HKA2 | Rural Short | INSTALL 3 NEW POLES AND AUGMENT 5 BAYS OF HV MAINS TO 7/4.50AAC. | 5 | 480 | 2400 | 0.0026811 | 5.5856e-06
2012-08-14 08:00AM | 211323 | L948 | Rural Short | Replace ABS 5266 with Auto Recloser | 36 | 480 | 17280 | 0.019304 | 4.0216e-05
2012-08-14 08:00AM | 211892 | L948 | Rural Short | install load break switch | 2 | 510 | 1020 | 0.0011395 | 2.2342e-06
2012-08-14 08:00AM | 211764 | J469 | Urban | Retro Sub 10343 Replace Tx and Retension OH Mains. | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2012-08-14 08:00AM | 213830 | 8776 | Urban | Street light Replacement | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2012-08-14 08:00AM | 213831 | 8776 | Urban | Street light replacement | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2012-08-14 08:30AM | 212599 | 35981 | Rural Short | Install vibration dampers | 31 | 270 | 8370 | 0.0093503 | 3.4631e-05
2012-08-14 08:30AM | 212787 | MVF2 | Rural Short | Replace Poles Install New poles Install DOFs 91479 and 91480 and Augment a section of 11KV O/H Mains | 12 | 450 | 5400 | 0.0060324 | 1.3405e-05
2012-08-14 08:30AM | 213421 | A049 | Rural Short | To augment and change over LV mains | 14 | 390 | 5460 | 0.0060995 | 1.564e-05
2012-08-14 08:30AM | 211403 | WRA2 | Urban | REPLACE POLE 1D0258 REPLACE LV ARM and HV FUSES SUB 42805 REPLACE LV ARMS POLES 1D0278 and 1D0279 . | 105 | 390 | 40950 | 0.045746 | 0.0001173
2012-08-14 08:30AM | 212441 | PKD2 | Urban | AUGMENT HV MAINS | 14 | 420 | 5880 | 0.0065687 | 1.564e-05
2012-08-14 09:00AM | 142880 | ULE2 | Rural Short | Replace Condemned polesOld Princes Hwy TERMEIL | 22 | 270 | 5940 | 0.0066357 | 2.4577e-05
2012-08-14 09:00AM | 213410 | 3353 | Urban | LV Crossarm changeover | 2 | 180 | 360 | 0.00040216 | 2.2342e-06
2012-08-14 11:30AM | 210587 | BK1236 | Urban | MAINTAIN HV SWITCHGEAR | 24 | 240 | 5760 | 0.0064346 | 2.6811e-05
2012-08-15 06:00AM | 213701 | M400 | Urban | Install new Pillar 121466 and change pillar 15335 | 19 | 540 | 10260 | 0.011462 | 2.1225e-05
2012-08-15 08:00AM | 213686 | X492 | Rural Long | REPAIR BROKEN HV TIES(PSBI'S)INSTALL VIBRATION DAMPERS | 13 | 420 | 5460 | 0.0060995 | 1.4523e-05
2012-08-15 08:00AM | 210197 | 2 | Rural Short | Final connection testing and commissioning of new Feeder KVD2 along with establishment of new distribution open points. | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2012-08-15 08:00AM | 211303 | X879 | Rural Short | Retro Subs 10764 and 11376. | 28 | 420 | 11760 | 0.013137 | 3.1279e-05
2012-08-15 08:00AM | 211547 | L584 | Rural Short | REPLACE HV POT HEADREPAIR ABS HANDLE and MAINTAIN HV SWITCHGEAR | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2012-08-15 08:00AM | 212188 | 8634 | Rural Short | install 5 poles adjacent existing | 19 | 480 | 9120 | 0.010188 | 2.1225e-05
2012-08-15 08:00AM | 212915 | BK1299 | Rural Short | Augment LV mains from Pole J28 to Sub 14165 with 1 x 150mm LVABC. | 22 | 450 | 9900 | 0.011059 | 2.4577e-05
2012-08-15 08:00AM | 210197 | 2 | Urban | Final connection testing and commissioning of new Feeder KVD2 along with establishment of new distribution open points. | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2012-08-15 08:00AM | 210254 | 9032 | Urban | iNSTALL TWO NEW PADMOUNT SUBSTATIONS 28617 AND 28618 AND SECTION OF HIGH VOLTAGE CABLE. | 19 | 540 | 10260 | 0.011462 | 2.1225e-05
2012-08-15 08:00AM | 212979 | CRF2 | Urban | REPLACE UGOH AND CHANGEOVER POLE REPLACE POLE | 61 | 510 | 31110 | 0.034754 | 6.8144e-05
2012-08-15 08:00AM | 213767 | 8620 | Urban | Isolate 2 LV distributors Remove cables. | 26 | 270 | 7020 | 0.0078422 | 2.9045e-05
2012-08-15 08:00AM | 213919 | 8772 | Urban | Street Light Replacement | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2012-08-15 08:30AM | 211708 | T851 | Rural Short | REPLACE HV X-ARM @ SUB 5539 REWIRE LV and REPLACE LV LINKS and FUSES | 5 | 405 | 2025 | 0.0022622 | 5.5856e-06
2012-08-15 08:30AM | 211743 | GG1295 | Rural Short | AUGMENT HV MAINS BETWEEN POLES 4PK036 and 212620 INSTALL S/S 41952 ON NEW POLE | 12 | 420 | 5040 | 0.0056303 | 1.3405e-05
2012-08-15 08:30AM | 211757 | L948 | Rural Short | Retro links fuses MDI @ sub 3739 | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2012-08-15 08:30AM | 212107 | JBA2 | Rural Short | REPLACE POLE 210421 | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2012-08-15 08:30AM | 213699 | W163 | Rural Short | replace condemned lv pole | 2 | 450 | 900 | 0.0010054 | 2.2342e-06
2012-08-15 08:30AM | 212093 | 1133 | Urban | REPLACE POLES 1081 AND 1554 AND AUGMENT 1 X BAY OF 11KV O/H MAINS | 37 | 390 | 14430 | 0.01612 | 4.1333e-05
2012-08-15 09:00AM | 211117 | CRB2 | Urban | Replace pole 3RK459 | 33 | 300 | 9900 | 0.011059 | 3.6865e-05
2012-08-15 10:00AM | 213798 | A049 | Rural Short | Change over LV to new pole | 1 | 180 | 180 | 0.00020108 | 1.1171e-06
2012-08-16 08:00AM | 211240 | HKA2 | Rural Short | INSTALL NEW POLE 830068.AUGMENT HV MAINS TO 3x7/4.50AAC FROM POLE 813633 TO POLE 2DY003 | 72 | 480 | 34560 | 0.038608 | 8.0433e-05
2012-08-16 08:00AM | 212446 | L591 | Rural Short | REPLACE POLESREMOVE ABSINSTALL LBS and AUGMENT HV MAINS | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2012-08-16 08:00AM | 210505 | 19856 | Urban | Augment 5 bays of O/H LV mains under HV mains. | 40 | 540 | 21600 | 0.02413 | 4.4685e-05
2012-08-16 08:00AM | 212455 | 35765 | Urban | Retro / Rewire of Sub # 5752 - WATTLE AVE ST MARYS | 29 | 480 | 13920 | 0.01555 | 3.2396e-05
2012-08-16 08:00AM | 212601 | 7967 | Urban | REPLACE CONDEMNED SUB POLE 3972 | 63 | 510 | 32130 | 0.035893 | 7.0379e-05
2012-08-16 08:00AM | 213199 | NWA2 | Urban | Replace UGOH + new pole and HV jointing | 57 | 480 | 27360 | 0.030564 | 6.3676e-05
2012-08-16 08:00AM | 213274 | R215 | Urban | Replace pole and install ABS | 75 | 420 | 31500 | 0.035189 | 8.3784e-05
2012-08-16 08:00AM | 213757 | 9020 | Urban | Lv Interruption - Charkers St Penrith | 24 | 480 | 11520 | 0.012869 | 2.6811e-05
2012-08-16 08:30AM | 210549 | 10289 | Rural Short | Replace LBS 90478 for Automated LBS | 2 | 390 | 780 | 0.00087135 | 2.2342e-06
2012-08-16 08:30AM | 211652 | 8801 | Rural Short | Replace pole 91 | 26 | 420 | 10920 | 0.012199 | 2.9045e-05
2012-08-16 08:30AM | 212781 | 35989 | Rural Short | Install vibration dampers between poles 11 and 12 | 1 | 180 | 180 | 0.00020108 | 1.1171e-06
2012-08-16 08:30AM | 213427 | A049 | Rural Short | To augment/change over LV mains. | 6 | 390 | 2340 | 0.0026141 | 6.7027e-06
2012-08-16 08:30AM | 211111 | WWF2 | Urban | Replace Condemned Sub pole 40558 | 53 | 390 | 20670 | 0.023091 | 5.9207e-05
2012-08-16 08:30AM | 211731 | BLD2 | Urban | Trim Trees clear of HV mains and stand new pole. | 65 | 420 | 27300 | 0.030497 | 7.2613e-05
2012-08-16 08:30AM | 212977 | SWD2 | Urban | AUGMENT HV MAINS RETRO S/S 40437 | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2012-08-16 09:00AM | 212999 | MGD2 | Rural Short | Replace Condemned Poles 3V0012 and 3V0013 Replace ABS 50533 with new ABS 96825 | 195 | 360 | 70200 | 0.078422 | 0.00021784
2012-08-16 09:00AM | 213016 | DP1210 | Rural Short | REPLACE STREETLIGHT 4AV520 | 31 | 180 | 5580 | 0.0062335 | 3.4631e-05
2012-08-16 09:00AM | 212763 | 35335 | Urban | Augment Fdr 471 pole13 to 15 | 15 | 420 | 6300 | 0.0070379 | 1.6757e-05
2012-08-16 09:00AM | 212957 | W123 | Urban | RETROFIT SUB | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2012-08-16 09:00AM | 213474 | S598 | Urban | X Arm change | 5 | 300 | 1500 | 0.0016757 | 5.5856e-06
2012-08-16 09:30AM | 212533 | BYE2 | Rural Short | AUGMENT H/V CONDUCTORS BETWEEN POLE 1XH042 and POLE 326699 [USL 93174] | 34 | 330 | 11220 | 0.012534 | 3.7982e-05
2012-08-16 09:30AM | 203183 | ULF2 | Urban | Replace Condemned pole 2RP060Deering St ULLADULLA. | 285 | 300 | 85500 | 0.095514 | 0.00031838
2012-08-16 10:00AM | 212782 | 35989 | Rural Short | Install Vibration Dampers | 11 | 360 | 3960 | 0.0044238 | 1.2288e-05
2012-08-17 08:00AM | 211326 | W188 | Rural Short | Retro Sub 10407 and Replace Tx. | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2012-08-17 08:00AM | 212900 | NA1207 | Rural Short | AUGMENT O/H MAINS with 6/4.75 between POLES 847472 and 847573 | 51 | 480 | 24480 | 0.027347 | 5.6973e-05
2012-08-17 08:00AM | 210681 | W113 | Urban | HV Augmentation | 54 | 540 | 29160 | 0.032575 | 6.0324e-05
2012-08-17 08:00AM | 211660 | 1129 | Urban | AUGMENT SECTION OF 11 KV O/H TO 7/4.50 AAC | 77 | 480 | 36960 | 0.041289 | 8.6018e-05
2012-08-17 08:00AM | 211671 | WRE2 | Urban | POLE REPLACEMENT X 1INSTALL 1X LBS | 127 | 510 | 64770 | 0.072356 | 0.00014187
2012-08-17 08:00AM | 211718 | 4370 | Urban | Install 2 bays of LV mains replace pole 423 with pole 814697 and pole 422 with 814698. | 124 | 480 | 29760 | 0.033245 | 0.00013852
2012-08-17 08:00AM | 213449 | 46752 | Urban | Pole Change | 23 | 420 | 9660 | 0.010791 | 2.5694e-05
2012-08-17 08:30AM | 211655 | 25449 | Rural Short | SRAIGHTEN POLES 4AG008 and 4AG009 REPLACE HV FUSES SUB 41743 REPLACE LV POLE 4AG012 INSTALL LV MID SPAN POLE BETWEEN POLES 4AG010 and 4AG011 REPLACE LV ARMS POLES 4AG010 and 4AG011. | 2 | 390 | 780 | 0.00087135 | 2.2342e-06
2012-08-17 08:30AM | 212313 | L941 | Rural Short | Replace ABS 5670 with new LBS + pole | 44 | 420 | 18480 | 0.020644 | 4.9153e-05
2012-08-17 09:00AM | 213412 | 16660 | Urban | Pole change over | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2012-08-17 09:00AM | 213783 | 25779 | Urban | INSTALL NEW LV CABLE INTO EXISTING PILLAR 109765 and INSTALL NEW LV CABLE INTO PAD SUB 27651 FUSE STRIP R . | 16 | 360 | 5760 | 0.0064346 | 1.7874e-05
2012-08-17 09:00AM | 213936 | 8676 | Urban | Replace Rusty Column | 2 | 180 | 360 | 0.00040216 | 2.2342e-06
2012-08-17 09:00AM | 214120 | 27191 | Urban | Repair LV Termination | 6 | 240 | 1440 | 0.0016087 | 6.7027e-06
2012-08-17 09:30AM | 213796 | 25779 | Urban | INSTALL NEW LV CABLE INTO EXISTING PILLAR S91425 | 51 | 270 | 13770 | 0.015383 | 5.6973e-05
2012-08-17 09:30AM | 213923 | 48203 | Urban | Repair Pillar | 38 | 150 | 5700 | 0.0063676 | 4.2451e-05
2012-08-18 01:00PM | 212412 | 7979 | Urban | REPLACE TRF SUB 19409 and DOF POLE 1464 | 1 | 390 | 390 | 0.00043568 | 1.1171e-06
2012-08-18 08:00AM | 212649 | CRA2 | Urban | REMOVE PL769283 AND RUN 2 BAYS OF LV ABC - 11kV OUTAGE FOR CLEARANCE ONLY | 53 | 450 | 23850 | 0.026643 | 5.9207e-05
2012-08-18 08:30AM | 213249 | W126 | Rural Short | Railcorp - Essential maintenance at Railcorp pole 526 | 79 | 300 | 23700 | 0.026476 | 8.8252e-05
2012-08-19 08:00AM | 212306 | WBC2 | Rural Short | Replace Condemned Pole 3PP015 and replace LV Crossarms | 23 | 330 | 7590 | 0.0084789 | 2.5694e-05
2012-08-19 08:00AM | 208151 | 27447 | Urban | Remove pole 413 and install LBS 69394 + pole. Remove ABS 5022 and install auto recloser 92825 + pole | 48 | 480 | 23040 | 0.025738 | 5.3622e-05
2012-08-19 08:00AM | 210734 | 35315 | Urban | Augment HV OH mains to 7/4.5 AAC. Pole 901 to pole 910. Change over poles. | 163 | 480 | 78240 | 0.087403 | 0.00018209
2012-08-19 08:00AM | 212090 | MYK2 | Urban | Replace pole and retrofit sub | 29 | 390 | 11310 | 0.012635 | 3.2396e-05
2012-08-19 09:00AM | 212105 | SHJ2 | Rural Short | REMOVE ABS 74037 INSTALL LBS 95501 MandR ABS 62333 | 30 | 360 | 10800 | 0.012065 | 3.3514e-05
2012-08-19 09:00AM | 213124 | 35989 | Rural Short | Install Vibration Dampers between poles 101 and 100 | 2 | 330 | 660 | 0.0007373 | 2.2342e-06
2012-08-19 09:00PM | 213950 | NA1266 | Urban | MandR HV Switchgear @ S/S 50853 - TX no 1 | 28 | 179 | 5012 | 0.005599 | 3.1279e-05
2012-08-20 08:00AM | 211343 | M391 | Rural Short | Retro Sub 10916 and Replace Tx. | 30 | 360 | 10800 | 0.012065 | 3.3514e-05
2012-08-20 08:00AM | 213005 | R216 | Rural Short | To allow staff to replace Pole 378 Mooresfield Rd Ellis Lane | 47 | 480 | 22560 | 0.025202 | 5.2505e-05
2012-08-20 08:00AM | 213466 | W163 | Rural Short | AUGMENT HV MAINS | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2012-08-20 08:00AM | 209113 | MR2232 | Urban | HV Augmentation | 233 | 540 | 125820 | 0.14056 | 0.00026029
2012-08-20 08:00AM | 211059 | R215 | Urban | New PMS29646 remove sub 11824. | 6 | 480 | 2880 | 0.0032173 | 6.7027e-06
2012-08-20 08:00AM | 213238 | W120 | Urban | Replace pole 392 with new 12.5M/Sub pole. Install new 100kVA pole sub | 68 | 540 | 36720 | 0.041021 | 7.5964e-05
2012-08-20 08:30AM | 213536 | ULJ2 | Rural Short | Install new 11kV pole and mains | 15 | 390 | 5850 | 0.0065352 | 1.6757e-05
2012-08-20 09:30AM | 211737 | ULE2 | Rural Short | INSTALL NEW DOF's RETRO-FIT SUB 72084 and DEFECT REPAIRS | 17 | 300 | 5100 | 0.0056973 | 1.8991e-05
2012-08-20 10:00AM | 214094 | 35010 | Urban | Bond in new cable at pillar100276 | 13 | 120 | 1560 | 0.0017427 | 1.4523e-05
2012-08-20 11:30AM | 213791 | 17035 | Urban | Lv Interrpution - Marsden Rd St Marys | 11 | 270 | 2970 | 0.0033178 | 1.2288e-05
2012-08-20 12:30AM | 213948 | NA1266 | Urban | MandR HV Switchgear @ S/S 50853 - TX no 2 | 28 | 180 | 5040 | 0.0056303 | 3.1279e-05
2012-08-21 08:00AM | 206761 | HKA2 | Rural Short | Install 7 new poles. Replace one set of USLs and install new 25kVA substation. | 25 | 480 | 12000 | 0.013405 | 2.7928e-05
2012-08-21 08:00AM | 209088 | 27454 | Rural Short | HV Augmentation | 7 | 540 | 3780 | 0.0042227 | 7.8198e-06
2012-08-21 08:00AM | 212101 | 8798 | Rural Short | change 3 poles and augment 2 bays of lv | 30 | 480 | 14400 | 0.016087 | 3.3514e-05
2012-08-21 08:00AM | 213335 | P608 | Rural Short | Replace poles and install new poles. | 6 | 420 | 2520 | 0.0028151 | 6.7027e-06
2012-08-21 08:00AM | 213803 | 8634 | Rural Short | Remove ABS 14431 and bonds from pole 132. Install new LBS + pole re bond and run short bay of 120mm CCT | 4 | 450 | 1800 | 0.0020108 | 4.4685e-06
2012-08-21 08:00AM | 210742 | SWC2 | Urban | Change poles and augment mains | 119 | 480 | 57120 | 0.06381 | 0.00013294
2012-08-21 08:00AM | 211546 | 48161 | Urban | Underground 2 sections of existing LV OH mains. | 47 | 540 | 25380 | 0.028353 | 5.2505e-05
2012-08-21 08:00AM | 212024 | 55885 | Urban | Augment LV mains to 150 ABC.(district switcher) | 38 | 480 | 9120 | 0.010188 | 4.2451e-05
2012-08-21 08:00AM | 212784 | CRD2 | Urban | Stand poles | 63 | 420 | 26460 | 0.029559 | 7.0379e-05
2012-08-21 08:00AM | 212861 | C893 | Urban | REPLACE POLE # 1096 - WORCESTER RD CAMBRIDGE PARK | 50 | 480 | 24000 | 0.026811 | 5.5856e-05
2012-08-21 08:00AM | 214232 | 35702 | Urban | maintenance | 35 | 480 | 16800 | 0.018768 | 3.9099e-05
2012-08-21 08:30AM | 210684 | MVC2 | Rural Short | Pole changes | 42 | 540 | 22680 | 0.025336 | 4.6919e-05
2012-08-21 08:30AM | 212103 | JBA2 | Rural Short | Replace poles 4JJ107 and 4JJ035 replace HV hardware pole 4JJ254 retro sub 43248 Install vibration dampers poles 4JX064 280188 296538 296539 296540 and replace HV arm pole 4JK021 | 65 | 360 | 23400 | 0.026141 | 7.2613e-05
2012-08-21 08:30AM | 212489 | L948 | Rural Short | Retro sub 2801 replace HV arm @ pole116 and replace polecap @ pole 173 | 4 | 390 | 1560 | 0.0017427 | 4.4685e-06
2012-08-21 08:30AM | 213154 | H745 | Rural Short | Install Vibration Dampers @ poles 802642 and 6 | 1 | 180 | 180 | 0.00020108 | 1.1171e-06
2012-08-21 08:30AM | 213491 | R218 | Rural Short | Install new pole 825629 and augment conductors from pole 825629 to pole 825626 | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2012-08-21 08:30AM | 213503 | BK1251 | Rural Short | Retrofit Sub 17389 | 1 | 300 | 300 | 0.00033514 | 1.1171e-06
2012-08-21 09:00AM | 212688 | ULE2 | Rural Short | 1. Install Additional pole 858954 2. Retro S/S 728973. Replace X pole 1HR025 ( ABS 41651 ) with new pole and LBS 96653Pretty Beach Rd PRETTY BEACH. | 70 | 360 | 25200 | 0.028151 | 7.8198e-05
2012-08-21 09:00AM | 213260 | RBA2 | Rural Short | Replace Condemned Poles 3XX750 and 3XX755 and Retro DOFs at Sub 30706 | 11 | 390 | 4290 | 0.0047924 | 1.2288e-05
2012-08-21 09:00AM | 213578 | 16653 | Urban | LV Pole change over | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2012-08-21 09:00AM | 214092 | 49362 | Urban | Consac Replacement | 30 | 360 | 10800 | 0.012065 | 3.3514e-05
2012-08-21 09:30PM | 211186 | WL1295 | Urban | Connect cable earths in Sub 26959 | 1 | 120 | 120 | 0.00013405 | 1.1171e-06
2012-08-21 12:30PM | 213746 | BK1251 | Rural Short | Limited District Switching Replace pole cap pole 308 | 1 | 150 | 150 | 0.00016757 | 1.1171e-06
2012-08-22 01:00PM | 213568 | S591 | Urban | LV Crossarm change | 4 | 150 | 600 | 0.00067027 | 4.4685e-06
2012-08-22 08:00AM | 211373 | R216 | Rural Short | Retro Sub's 10957 12221and Replace Tx @ 10957. | 17 | 420 | 7140 | 0.0079762 | 1.8991e-05
2012-08-22 08:00AM | 212194 | 8634 | Rural Short | augment 5 bays of hv mains to 150mm hv abc and install sectionaliser. | 19 | 480 | 9120 | 0.010188 | 2.1225e-05
2012-08-22 08:00AM | 212758 | W163 | Rural Short | STAND POLES and AUGMENT HV MAINS | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2012-08-22 08:00AM | 212904 | NA1270 | Rural Short | Augment one bay of HV mains to 6/1/2.5 ACSR. | 19 | 480 | 9120 | 0.010188 | 2.1225e-05
2012-08-22 08:00AM | 214235 | 35693 | Rural Short | maintenance | 64 | 300 | 19200 | 0.021449 | 7.1496e-05
2012-08-22 08:00AM | 211596 | 3184 | Urban | Allow staff to remove USL 83053 and replace with ABS 92355 retro fit pole sub 4139. | 66 | 480 | 31680 | 0.03539 | 7.373e-05
2012-08-22 08:00AM | 214288 | 25773 | Urban | Install new Pillar | 52 | 420 | 21840 | 0.024398 | 5.809e-05
2012-08-22 08:30AM | 213256 | 35989 | Rural Short | To allow staff to install DOF's 87877 and 87878 New Poles 824546 and 824547 and Remove USL's X788 Janderra Rd Wilton | 14 | 450 | 6300 | 0.0070379 | 1.564e-05
2012-08-22 08:30AM | 213423 | A049 | Rural Short | To install HV OH mains and change over poles. | 11 | 390 | 4290 | 0.0047924 | 1.2288e-05
2012-08-22 08:30PM | 211604 | PKC2 | Urban | REMOVE ABS 74418 and 70622 INSTALL ABS 95376ABS 95377 LBS 88359 REPLACE POLE 3TC303 AUGMENT BETWEEN POLE 3TC303 and S/S 41689 | 555 | 540 | 299700 | 0.3348 | 0.00062
2012-08-22 09:00AM | 212217 | L942 | Rural Short | Retro rewire links and fuses @ sub 8703 | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2012-08-22 09:00AM | 213579 | S594 | Urban | LV Crossarm change | 6 | 240 | 1440 | 0.0016087 | 6.7027e-06
2012-08-22 09:30AM | 212150 | 3184 | Urban | AUGMENT ONE BAY 11KV O/H MAINS AND INSTALL DOF AT BOLD ST CABRAMATTA | 40 | 300 | 6900 | 0.0077081 | 4.4685e-05
2012-08-23 08:00AM | 183903 | W114 | Rural Short | To allow staff to Retrofit Sub 10164 Brooks Point Rd Appin | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2012-08-23 08:00AM | 206698 | HKA2 | Rural Short | Replace 3 poles and install one new one. Refit existing 50kVA sub. Augment 7 bays of HV mains. | 23 | 480 | 11040 | 0.012333 | 2.5694e-05
2012-08-23 08:00AM | 210686 | W111 | Rural Short | HV Augmentation | 6 | 480 | 2880 | 0.0032173 | 6.7027e-06
2012-08-23 08:00AM | 213030 | X879 | Rural Short | To allow staff to replace Condemned Pole 343 Gregory Rd Leppington | 31 | 480 | 14880 | 0.016623 | 3.4631e-05
2012-08-23 08:00AM | 213077 | L582 | Rural Short | REPLACE POLEAUGMENT MAINS and TREE TRIMMING. | 9 | 480 | 4320 | 0.004826 | 1.0054e-05
2012-08-23 08:00AM | 213117 | W127 | Rural Short | RETROFIT SUB | 48 | 420 | 20160 | 0.022521 | 5.3622e-05
2012-08-23 08:00AM | 206772 | SWC2 | Urban | AUGMENT 10 BAYS OF HV MAINS TO 7/4.50AAC. REPLACE 4 POLES. | 128 | 480 | 61440 | 0.068636 | 0.00014299
2012-08-23 08:00AM | 209111 | MR2232 | Urban | HV Augmentation | 63 | 540 | 34020 | 0.038004 | 7.0379e-05
2012-08-23 08:00AM | 212543 | 1125 | Urban | AUGMENT 1 BAY 11KV O/H MAINS AND REPLACE DEFECTIVE HV X-ARMS | 20 | 480 | 7200 | 0.0080433 | 2.2342e-05
2012-08-23 08:00AM | 213302 | NWE2 | Urban | Replace pole and UGOH | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2012-08-23 08:00AM | 214122 | WL1251 | Urban | Replace Condemned Pole | 22 | 480 | 10560 | 0.011797 | 2.4577e-05
2012-08-23 08:00AM | 214415 | 3188 | Urban | Replace LV Arms | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2012-08-23 08:30AM | 212518 | MVB2 | Rural Short | Install vibration dampers @ 5 locations | 211 | 420 | 88620 | 0.098999 | 0.00023571
2012-08-23 08:30AM | 212745 | A051 | Rural Short | REPLACE HV X-ARMS AT POLES 136 and 137. REPLACE POLE CAP @ 134 | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2012-08-23 08:30AM | 212543 | 1125 | Urban | AUGMENT 1 BAY 11KV O/H MAINS AND REPLACE DEFECTIVE HV X-ARMS | 10 | 360 | 5400 | 0.0060324 | 1.1171e-05
2012-08-23 08:30AM | 214072 | UNB2 | Urban | Connect new URD to Padmount Sub 41289 | 17 | 360 | 6120 | 0.0068368 | 1.8991e-05
2012-08-23 09:00AM | 213002 | BDF2 | Rural Short | Replace pole 1YA107. | 34 | 390 | 13260 | 0.014813 | 3.7982e-05
2012-08-23 09:00AM | 214161 | GV1278 | Urban | LV crossarm change | 5 | 240 | 1200 | 0.0013405 | 5.5856e-06
2012-08-23 10:00AM | 214376 | 9020 | Urban | maintenance | 17 | 240 | 4080 | 0.0045578 | 1.8991e-05
2012-08-23 12:00PM | 214374 | 9020 | Urban | maintenance | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2012-08-24 07:30AM | 213269 | KC1288 | Rural Short | REPLACE LV CROSSARMS @ SUB 1235 OFF MAMRE RD KEMPS CREEK | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2012-08-24 08:00AM | 210669 | 8711 | Rural Short | Replace ABS 5977 with new ABS 91813 and HV Pole changes | 36 | 540 | 19440 | 0.021717 | 4.0216e-05
2012-08-24 08:00AM | 211415 | A049 | Rural Short | Install/augment HV OH mains 19/3.25 AAC.Change over poles.(Creates cross zone tie) | 21 | 480 | 10080 | 0.011261 | 2.346e-05
2012-08-24 08:00AM | 212259 | 8634 | Rural Short | RETENSION RIVER X-INGS AND INSTALL SUPPORT STAYS AT POLES 782285 and 782287. | 5 | 480 | 2400 | 0.0026811 | 5.5856e-06
2012-08-24 08:00AM | 211475 | J497 | Urban | M/R HV Switchgear in Substation 13082. | 84 | 360 | 30240 | 0.033782 | 9.3838e-05
2012-08-24 08:00AM | 214440 | 8762 | Urban | Replace condemned Pole and defects | 24 | 480 | 11520 | 0.012869 | 2.6811e-05
2012-08-24 08:30AM | 211689 | L948 | Rural Short | Remove USL E574. Replace pole 159 with Auto LBS 90891 + pole | 19 | 420 | 7980 | 0.0089146 | 2.1225e-05
2012-08-24 08:30AM | 212211 | JBA2 | Rural Short | REPLACE POLE 4HY055 RETRO SUBS 42216 and 42294 . | 8 | 420 | 3360 | 0.0037535 | 8.937e-06
2012-08-24 08:30AM | 214200 | L582 | Rural Short | REPLACE CROSSARM AT POLE 141 | 8 | 240 | 1920 | 0.0021449 | 8.937e-06
2012-08-24 09:00AM | 213433 | RBA2 | Rural Short | Relocate substation install 2 x LBS and 11kV mains extension | 15 | 375 | 5625 | 0.0062838 | 1.6757e-05
2012-08-24 09:00AM | 214117 | 10244 | Rural Short | REPAIR BROKEN HV TIE(PSBI) | 6 | 180 | 1080 | 0.0012065 | 6.7027e-06
2012-08-24 09:00AM | 214257 | X802 | Rural Short | REPAIR HV TIE POLE 55 (PL469520)LIMITED SWITCHING REQUEST | 17 | 300 | 5100 | 0.0056973 | 1.8991e-05
2012-08-24 09:00AM | 214263 | X802 | Rural Short | REPAIR HV TIE POLE 36 -PL469455REPLACE HV XARM POLE 18 -PL469464LIMITED SWITCHING REQUEST | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2012-08-24 09:00AM | 214164 | 16649 | Urban | LV pole change over | 1 | 300 | 300 | 0.00033514 | 1.1171e-06
2012-08-24 09:30AM | 213040 | CLB2 | Rural Short | Replace surge diverters adjacent to CLB1 | 3 | 330 | 990 | 0.0011059 | 3.3514e-06
2012-08-25 08:00AM | 212324 | CT1225 | Urban | New PMS29641 and HV SW/GR U/R PMS28898 Remove sub 10581. | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2012-08-25 08:30AM | 212097 | W113 | Urban | Change Pole 62 | 136 | 390 | 53040 | 0.059252 | 0.00015193
2012-08-25 09:00AM | 212576 | BDB2 | Urban | Install New ABS poles and Augment HV Conductors.Scenic Dr and Hyam St NOWRA. | 109 | 420 | 45780 | 0.051142 | 0.00012177
2012-08-26 08:00AM | 211837 | 8633 | Rural Short | RETROFIT SUB 8014 + SUB 309 | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2012-08-26 08:00AM | 211573 | WL1296 | Urban | REPLACE ABS B388 WITH NEW ABS 96497 | 127 | 480 | 60960 | 0.0681 | 0.00014187
2012-08-26 08:00AM | 212786 | CRD2 | Urban | Replace poles | 279 | 420 | 117180 | 0.1309 | 0.00031168
2012-08-26 08:30AM | 212629 | RWE2 | Rural Short | Install vibration dampers @ pole 3VD045 and 3VD044 | 3 | 210 | 630 | 0.00070379 | 3.3514e-06
2012-08-26 08:30AM | 212631 | RWE2 | Rural Short | Install vibration dampers @ pole 3VJ285 and 3VJ286 | 16 | 210 | 3360 | 0.0037535 | 1.7874e-05
2012-08-26 08:30AM | 214224 | W163 | Rural Short | RUN 3 BAYS LV ABC OFF SUB 15145 | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2012-08-26 08:30AM | 213235 | 35001 | Urban | REPLACE CONDEMNED POLE 375 (USL 9952) | 18 | 390 | 7020 | 0.0078422 | 2.0108e-05
2012-08-26 08:30AM | 213248 | 3106 | Urban | Augment HV OH mains 7/4.5 AAC USL P106 to ABS 90935. | 18 | 390 | 7020 | 0.0078422 | 2.0108e-05
2012-08-26 11:59PM | 212177 | R214 | Urban | Install new LBS | 12 | 241 | 2892 | 0.0032307 | 1.3405e-05
2012-08-26 12:30PM | 212960 | RWE2 | Rural Short | Install vibration dampers @ pole 3VJ393 and 3VJ392 | 10 | 180 | 1800 | 0.0020108 | 1.1171e-05
2012-08-27 07:00AM | 210959 | 19871 3112 | Urban | Install new sub 28609. Install new 240 al xlpe cable to existing cable from sps19202 sub 12881to sub sps 83187 28609. Install new safelink s/gear sub 5991. Install new cable from sps 83193 sub 5991 to sps 83189 sub 28609. Park Pde Parramatta | 2 | 540 | 1080 | 0.0012065 | 2.2342e-06
2012-08-27 08:00AM | 211553 | A049 | Rural Short | Install HV OH mains (150 NMS ABC and 7/4.5 AAC).Install LBS 90111. | 20 | 480 | 9600 | 0.010724 | 2.2342e-05
2012-08-27 08:00AM | 213241 | MVC2 | Rural Short | Install vibration 5 dampers @ 2 job sites | 61 | 240 | 14640 | 0.016355 | 6.8144e-05
2012-08-27 08:00AM | 213618 | 35988 | Rural Short | Install Vibration Dampers between poles 43and42.Replace TX and HV Retro @ Sub 10201 | 16 | 480 | 7680 | 0.0085795 | 1.7874e-05
2012-08-27 08:00AM | 213829 | YYA2 | Rural Short | Augment one bay of HV Mains to 3x19/3.25AAAC replace and install poles. | 143 | 480 | 68640 | 0.076679 | 0.00015975
2012-08-27 08:00AM | 214417 | WBD2 | Rural Short | Augment LV Mains | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2012-08-27 08:00AM | 211321 | 25783 | Urban | Remove:2 x poles | 28 | 540 | 7560 | 0.0084454 | 3.1279e-05
2012-08-27 08:00AM | 214234 | 35702 | Urban | maintenance | 34 | 240 | 8160 | 0.0091157 | 3.7982e-05
2012-08-27 08:00AM | 214625 | 35702 | Urban | maintenance | 34 | 240 | 8160 | 0.0091157 | 3.7982e-05
2012-08-27 08:30AM | 213035 | MVC2 | Rural Short | Install vibration damper @ pole 3XA200 and 3XA204 | 10 | 210 | 2100 | 0.002346 | 1.1171e-05
2012-08-27 09:00AM | 213419 | B776 | Urban | COMMISSIONING CHECK FOR LBS 86829 | 1 | 300 | 300 | 0.00033514 | 1.1171e-06
2012-08-27 09:00AM | 214163 | 1962 | Urban | LV pole change over | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2012-08-27 09:00AM | 214448 | 1129 | Urban | Repalce LV arms | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2012-08-27 09:00AM | 214455 | X858 | Urban | Install new pillar | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2012-08-27 10:00AM | 214256 | X473 | Rural Short | REPLACE HV DISC INSULATOR and RETRO SUB | 2 | 300 | 600 | 0.00067027 | 2.2342e-06
2012-08-27 12:30PM | 213029 | MGE2 | Rural Short | Install vibration damper @ pole 320523 | 10 | 180 | 1800 | 0.0020108 | 1.1171e-05
2012-08-27 12:30PM | 213063 | MG1219 | Rural Short | Install vibration damper @ pole 770617 | 8 | 180 | 1440 | 0.0016087 | 8.937e-06
2012-08-27 12:30PM | 213106 | BWE2 | Rural Short | Install vibration dampers @ pole 3X0990 and sub 31300 | 4 | 180 | 720 | 0.00080433 | 4.4685e-06
2012-08-28 01:00PM | 213716 | RWC2 | Rural Short | Replace HV X Arm at Pole 201332 | 11 | 150 | 1650 | 0.0018432 | 1.2288e-05
2012-08-28 01:00PM | 214740 | 8610 | Urban | Replacing Connections | 31 | 120 | 3720 | 0.0041557 | 3.4631e-05
2012-08-28 08:00AM | 209091 | 27454 | Rural Short | Pole Changes | 8 | 540 | 4320 | 0.004826 | 8.937e-06
2012-08-28 08:00AM | 211283 | HKA2 | Rural Short | INSTALL NEW POLE 830070 AND REPLACE POLE 2DY005 WITH POLE 830069.AUGMENT HV MAINS TO 3x7/4.50AAC FROM 2DY003 TO POLE 773994.INSTALL 40A DOFs 90666 ON POLE 200152. | 97 | 480 | 46560 | 0.052013 | 0.00010836
2012-08-28 08:00AM | 211723 | X877 | Rural Short | Retro Subs 11374 and 12322. | 17 | 360 | 6120 | 0.0068368 | 1.8991e-05
2012-08-28 08:00AM | 214450 | X877 | Rural Short | Replace LV Arms | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2012-08-28 08:00AM | 209830 | BLC2 | Urban | REPLACE HV POLES | 65 | 480 | 31200 | 0.034854 | 7.2613e-05
2012-08-28 08:00AM | 211324 | A048 | Urban | C0REPLACE POLE 130 REPLACE HV X-ARM @ POLE 132 RE-INSTALL LA's @ POLE 134. | 9 | 480 | 4320 | 0.004826 | 1.0054e-05
2012-08-28 08:00AM | 213286 | SWC2 | Urban | AUGMENT 4 BAYS OF HV MAINS TO 150 NMSHVABC. | 79 | 480 | 37920 | 0.042361 | 8.8252e-05
2012-08-28 08:00AM | 213644 | C855 | Urban | REPLACE HV X-ARMS AT POLE # 69 - TRAFALGAR RD EMU PLAINS | 22 | 480 | 10560 | 0.011797 | 2.4577e-05
2012-08-28 08:30AM | 213054 | SHJ2 | Rural Short | REPLACE POLE 4GX035 RETRO SUBS 40862 and 40865 REPLACE HV ARMS POLES 4GX034 and 4GX033 . | 11 | 420 | 4620 | 0.0051611 | 1.2288e-05
2012-08-28 08:30AM | 213730 | H745 | Rural Short | Change HV pole 36 and LV pole 37. | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2012-08-28 08:30AM | 213629 | WBB2 | Urban | 11kV OUTAGE TO REPLACE STR 68 FDR 7025 | 28 | 450 | 12600 | 0.014076 | 3.1279e-05
2012-08-28 08:30AM | 214566 | 48166 | Urban | Connect New Pillar S118608 to existing Column 213233. | 3 | 240 | 720 | 0.00080433 | 3.3514e-06
2012-08-28 09:00AM | 213007 | BDC2 | Rural Short | REPLACE POLE 1YA104 [ SUB 51690 ] | 15 | 390 | 5850 | 0.0065352 | 1.6757e-05
2012-08-28 09:00AM | 214402 | A049 | Rural Short | Change over LV services | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2012-08-28 09:00AM | 214167 | 16649 | Urban | LV pole change over | 6 | 240 | 1440 | 0.0016087 | 6.7027e-06
2012-08-28 10:30AM | 213713 | BWC2 | Urban | Repair HV Tie and Retension HV mains at Pole 3R0198 | 7 | 150 | 1050 | 0.001173 | 7.8198e-06
2012-08-29 08:00AM | 211167 | 10244 | Rural Short | REPLACE ABS WITH SCADA CONTROLLED LOAD BREAK SWITCH | 60 | 450 | 27000 | 0.030162 | 6.7027e-05
2012-08-29 08:00AM | 209154 | 7970 | Urban | HV Augmentation | 192 | 540 | 53460 | 0.059721 | 0.00021449
2012-08-29 08:00AM | 210815 | 35315 | Urban | Augment HV OH mains 7/4.5 AAC.Change over poles.Pole 901 to 833147. | 172 | 540 | 46440 | 0.051879 | 0.00019214
2012-08-29 08:00AM | 211751 | 4374 | Urban | Augment 3 bays of LV mains replace pole 285492 with pole 814700 and install new pole 814701. | 220 | 480 | 52800 | 0.058984 | 0.00024577
2012-08-29 08:00AM | 211755 | 1131 | Urban | Replace pole 1. Augment 2 x bays of HVand install D.O.F. 91524 | 82 | 480 | 39360 | 0.04397 | 9.1604e-05
2012-08-29 08:00AM | 212424 | 49319 | Urban | REPLACE LV SW GR + HV SW GR MAINT SUB 17117 | 52 | 480 | 24960 | 0.027883 | 5.809e-05
2012-08-29 08:00AM | 213476 | NA1225 | Urban | RETENSION ONE BAY of HV MAINS | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2012-08-29 08:00AM | 213736 | WRE2 | Urban | Replace UGOH and pole + joint new section of cable | 38 | 480 | 18240 | 0.020376 | 4.2451e-05
2012-08-29 08:30AM | 212961 | RWE2 | Rural Short | Install 10 vibration dampers @ 5 worksites | 38 | 420 | 15960 | 0.017829 | 4.2451e-05
2012-08-29 08:30AM | 213924 | 57444 | Rural Short | REPLACE CONDEMNED POLE 314(410424) ALSO REPLACE SHROUD ON SUB 14938 REPLACE 2 HV XRAMS.REPAIR A STAY | 4 | 390 | 1560 | 0.0017427 | 4.4685e-06
2012-08-29 08:30AM | 213980 | W163 | Rural Short | REWIRE IMPORT/EXPORT LINKS AT AUTO RECLOSER | 3 | 390 | 1170 | 0.001307 | 3.3514e-06
2012-08-29 08:30AM | 213020 | WWE2 | Urban | AUGMENT HV MAINS and INSTALL DOF'S REPLACE POLE 2X0137 | 160 | 420 | 35280 | 0.039412 | 0.00017874
2012-08-29 08:30AM | 213280 | SHE2 | Urban | REPLACE POLE 1C0369 . | 7 | 300 | 2100 | 0.002346 | 7.8198e-06
2012-08-29 09:00AM | 214170 | 16653 | Urban | LV pole change over | 9 | 240 | 2160 | 0.002413 | 1.0054e-05
2012-08-29 09:00AM | 214390 | NG1247 | Urban | Change low voltage cross arm at pole E164. | 20 | 240 | 4800 | 0.0053622 | 2.2342e-05
2012-08-29 09:00AM | 214506 | 49362 | Urban | Consac Replacement | 23 | 360 | 8280 | 0.0092498 | 2.5694e-05
2012-08-30 03:00AM | 209560 | WL1214 | Urban | INSTALL NEW 11KV FEEDER. (WL 1214 BERNERA RD) | 3 | 60 | 180 | 0.00020108 | 3.3514e-06
2012-08-30 08:00AM | 199267 | HKA2 | Rural Short | AUGMENT 6 BAYS OF HV MAINS. REPLACE 2 POLES AND INSTALL NEW LBS 87959. | 56 | 480 | 26880 | 0.030028 | 6.2559e-05
2012-08-30 08:00AM | 210689 | KC1284 | Rural Short | Pole changes | 42 | 540 | 22680 | 0.025336 | 4.6919e-05
2012-08-30 08:00AM | 212199 | 8634 | Rural Short | augment 4 bays of hv mains to 150mm hv abc | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2012-08-30 08:00AM | 212471 | 41533 | Rural Short | RETRO / RE WIRE OF SUB # 787 - STONEY CREEK RD SHANES PARK | 13 | 480 | 6240 | 0.0069708 | 1.4523e-05
2012-08-30 08:00AM | 213212 | L582 | Rural Short | STAND POLE and AUGMENT HV MAINS | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2012-08-30 08:00AM | 206774 | SWC2 | Urban | AUGMENT 6 BAYS OF HV MAINS TO 7/4.50AAC. REPLACE 4 POLES. REPLACE TX. INSTALL NEW ABS 88159 | 197 | 480 | 94560 | 0.10563 | 0.00022007
2012-08-30 08:00AM | 209117 | MR2232 | Urban | HV Augmentation | 37 | 540 | 19980 | 0.02232 | 4.1333e-05
2012-08-30 08:00AM | 210796 | D828 | Urban | Allow staff to remove ABS A816 and pole.erect new pole with LBS 90848. | 25 | 480 | 12000 | 0.013405 | 2.7928e-05
2012-08-30 08:00AM | 210811 | 35315 | Urban | Replace pole 915.Augment HV OH mains 7/4.5 AAC pole 910 to pole 789433.Change over poles. | 80 | 540 | 43200 | 0.04826 | 8.937e-05
2012-08-30 08:00AM | 211800 | 7972 | Urban | REPLACE CONDEMNED SUB POLE 530 | 27 | 450 | 12150 | 0.013573 | 3.0162e-05
2012-08-30 08:00AM | 212425 | B799 | Urban | REPLACE LV SW GR SUB 8792 | 74 | 480 | 35520 | 0.03968 | 8.2667e-05
2012-08-30 08:00AM | 212946 | CRD2 | Urban | Replace poles and augment | 147 | 450 | 66150 | 0.073897 | 0.00016422
2012-08-30 08:00AM | 214727 | 5878 | Urban | Pole Replacement | 36 | 420 | 15120 | 0.016891 | 4.0216e-05
2012-08-30 08:30AM | 212517 | T851 | Rural Short | REPLACE POLE 77 USL 978 WITH NEW POLE and SCADA LBS. REPLACE HV X-ARM @ POLE 215. REPLACE POLE 79. | 63 | 420 | 26460 | 0.029559 | 7.0379e-05
2012-08-30 08:30AM | 212605 | APC2 | Rural Short | REMOVE ABS 73275 and INSTALL LBS 95857 | 12 | 360 | 4320 | 0.004826 | 1.3405e-05
2012-08-30 08:30AM | 213173 | BK1251 | Rural Short | RETROFIT SUB | 48 | 390 | 18720 | 0.020912 | 5.3622e-05
2012-08-30 08:30AM | 213763 | MGD2 | Rural Short | Augment high voltage mains from pole 3V0160 to pole 3V0037 and install new ABS 90840 at pole 3v0163. | 98 | 450 | 44100 | 0.049265 | 0.00010948
2012-08-30 09:00AM | 214010 | BWA2 | Rural Short | Install LLLs and Temp LV Links | 70 | 225 | 15750 | 0.017595 | 7.8198e-05
2012-08-30 09:00AM | 212766 | J497 | Urban | To MandR H/V S/Gear @ Sub 13190 Kanimbla Ave Bradbury. | 105 | 300 | 31500 | 0.035189 | 0.0001173
2012-08-30 09:00AM | 214247 | 8744 | Urban | LV arm change | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2012-08-30 09:00AM | 214504 | 49362 | Urban | Consac Replacement | 22 | 360 | 7920 | 0.0088476 | 2.4577e-05
2012-08-30 09:30AM | 212684 | ULE2 | Rural Short | Replace Condemned polesKurrawa Dr MERRY BEACH. | 52 | 300 | 15600 | 0.017427 | 5.809e-05
2012-08-31 07:00PM | 209560 | WL1214 | Urban | INSTALL NEW 11KV FEEDER. (WL 1214 BERNERA RD) | 3 | 60 | 180 | 0.00020108 | 3.3514e-06
2012-08-31 08:00AM | 210696 | CT1262 | Rural Short | HV Augmentation | 5 | 540 | 2700 | 0.0030162 | 5.5856e-06
2012-08-31 08:00AM | 212416 | SN1230 | Rural Short | INSTALL AUTORECLOSER 89017 ON POLE 814889 COMPLETE WITH USL SETS. KEEP EXISTING ABS 82890 ON POLE. | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2012-08-31 08:00AM | 212443 | 8798 | Rural Short | tree trimimg adjacent hv mains and change pole | 135 | 480 | 64800 | 0.072389 | 0.00015081
2012-08-31 08:00AM | 212755 | MYK2 | Urban | AUGMENT ONE BAY OF HV MAINS TO 3x7/4.50AAC FROM POLE 3A0443 TO POLE 824483 | 26 | 480 | 12480 | 0.013942 | 2.9045e-05
2012-08-31 08:00AM | 213761 | 55885 | Urban | Augment LV mains to 150 ABC. Alter Sub 6421 for LV ABC.(district switcher) | 48 | 480 | 11520 | 0.012869 | 5.3622e-05
2012-08-31 08:00AM | 214627 | 9020 | Urban | maintenance | 25 | 480 | 12000 | 0.013405 | 2.7928e-05
2012-08-31 08:30AM | 211666 | L940 | Rural Short | MAINTAIN ABS 58327 and 58346. | 72 | 420 | 30240 | 0.033782 | 8.0433e-05
2012-08-31 08:30AM | 211742 | 8634 | Rural Short | RETRO SUB 9794 and INSTALL NEW Tx HANGING BRACKET. REPLAC POLE CAP @ 62. | 2 | 330 | 660 | 0.0007373 | 2.2342e-06
2012-08-31 08:30AM | 213337 | 25403 | Rural Short | RETRO SUB 6862 REPLACE MDI and LV BOX ARMS. | 10 | 360 | 3600 | 0.0040216 | 1.1171e-05
2012-08-31 08:30AM | 213608 | 57448 | Rural Short | REPLACE CONDEMNED POLE 3 | 3 | 390 | 1170 | 0.001307 | 3.3514e-06
2012-08-31 08:30AM | 214066 | MVF2 | Rural Short | Trim Trees Near Hv Conductor | 5 | 450 | 2250 | 0.0025135 | 5.5856e-06
2012-08-31 08:30AM | 212761 | DP1258 | Urban | REPLACE POLES 4AJ626 4AJ625 and RETRO SUB 41767. | 77 | 390 | 30030 | 0.033547 | 8.6018e-05
2012-08-31 08:30AM | 212882 | PKF2 | Urban | Replace poles and retension LV mains | 17 | 330 | 5610 | 0.006267 | 1.8991e-05
2012-08-31 09:00AM | 214310 | 8610 | Urban | HV L/V pole change gear | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2012-08-31 09:00AM | 214678 | CRB2 | Urban | REPLACE LV CROSSARMS | 32 | 240 | 7680 | 0.0085795 | 3.5748e-05
2012-08-31 09:00AM | 214731 | 19815 | Urban | Reconnect LV Cable | 14 | 240 | 3360 | 0.0037535 | 1.564e-05
2012-08-31 10:00AM | 212939 | S674 | Urban | Repair bonding on HV crossarms | 144 | 240 | 34560 | 0.038608 | 0.00016087
2012-08-31 10:00AM | 214680 | 49918 | Urban | Replace street light column | 33 | 180 | 5940 | 0.0066357 | 3.6865e-05
2012-08-31 10:00AM | 214840 | 68181 | Urban | Replace Column | 25 | 180 | 4500 | 0.005027 | 2.7928e-05
2012-09-01 05:00PM | 213943 | A317 | Urban | establish new pad sub 29693 | 192 | 30 | 5760 | 0.0064346 | 0.00021449
2012-09-01 06:30AM | 213104 | 35523 | Urban | id and spike out of service HV cable from Sw 59097 @ Sub 25611and STJ. | 2 | 570 | 1140 | 0.0012735 | 2.2342e-06
2012-09-01 06:30AM | 213943 | A317 | Urban | establish new pad sub 29693 | 192 | 30 | 5760 | 0.0064346 | 0.00021449
2012-09-01 08:00AM | 213324 | A049 | Rural Short | Replace pole 802 and install LBS 91649 | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2012-09-01 08:30AM | 214100 | 35989 | Rural Short | Retrofit substation 10485 and change TX. | 4 | 390 | 1560 | 0.0017427 | 4.4685e-06
2012-09-01 08:30AM | 214252 | 61617 | Rural Short | Install new pole 874731 And replace DOF's @ Sub's 11261 and 12281 | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2012-09-02 07:30AM | 212852 | 46477 | Urban | ESTABLISH NEW 1000KVA P/MOUNT SUB 29936 WITH SAFELINK CF HV S/GEAR INSTALL NEW 11KV SAFELINK CFC S/G IN EXISTING SUB 16022 REMOVE EX DOFs X122 | 1 | 570 | 570 | 0.00063676 | 1.1171e-06
2012-09-02 07:30AM | 213331 | 8622 | Urban | Install new Cable in Sub 23852 and New Pole and HUGOH. Remove 1 bay HV mains | 19 | 510 | 9690 | 0.010825 | 2.1225e-05
2012-09-02 08:00AM | 213161 | 6421 | Urban | repair burnt off bond and mand r abs 11969REPLACE ARRESTORS @ POLE 466 | 39 | 480 | 18720 | 0.020912 | 4.3568e-05
2012-09-02 08:30AM | 213886 | RBB2 | Rural Short | Job 1:-Install vibration dampers @ pole 3YH3593YH358 and replace FP 50190Job 2:-Install vibration dampers @ pole 3YA0983X1074 and 3X1073Job 3:-Install vibration dampers @ pole 3YH372 and 3YH316 | 60 | 270 | 16200 | 0.018097 | 6.7027e-05
2012-09-02 09:00AM | 212023 | BDG2 | Rural Short | REPLACE POLES 2XK015 and 2XK016 | 15 | 360 | 5400 | 0.0060324 | 1.6757e-05
2012-09-02 09:00AM | 213214 | UNC2 | Urban | STAND POLES 869901 869900 869899 871276 871274 RETRO SUBS 41300 and 41715 | 21 | 360 | 7560 | 0.0084454 | 2.346e-05
2012-09-02 12:30PM | 213166 | RBC2 | Rural Short | Install vibration dampers @ pole 3XY581 and 3XY579 | 6 | 180 | 1080 | 0.0012065 | 6.7027e-06
2012-09-03 07:30AM | 213581 | 48185 | Rural Short | Install new section of U/G mains and new Pad Subs 295102951129512. Remove Section of O/H mains and ABS's 5240752408. | 9 | 660 | 5940 | 0.0066357 | 1.0054e-05
2012-09-03 08:00AM | 213787 | R218 | Rural Short | Install vibration dampers and defect rectification. | 6 | 420 | 2520 | 0.0028151 | 6.7027e-06
2012-09-03 08:00AM | 213747 | 1112 | Urban | Augment 7bays of hv mains Replace 2 poles + Install new pole. | 289 | 600 | 173400 | 0.19371 | 0.00032285
2012-09-03 08:00AM | 215180 | R250 | Urban | low voltage work | 4 | 300 | 1200 | 0.0013405 | 4.4685e-06
2012-09-03 08:30AM | 213122 | BWF2 | Rural Short | Install vibration dampers @ poles 3YA017and 331157 | 23 | 210 | 4830 | 0.0053957 | 2.5694e-05
2012-09-03 08:30AM | 213395 | BWF2 | Rural Short | Install vibration dampers @ pole 793661 and 3R1701 | 1 | 210 | 210 | 0.0002346 | 1.1171e-06
2012-09-03 08:30AM | 213403 | MVF2 | Rural Short | Install 4 dampers @ 2 worksites | 18 | 420 | 7560 | 0.0084454 | 2.0108e-05
2012-09-03 08:30AM | 213823 | 10286 | Rural Short | REPLACE HV X-ARM @ POLE 15 | 1 | 240 | 240 | 0.00026811 | 1.1171e-06
2012-09-03 08:30AM | 214828 | X217 | Rural Short | LIMITED SWITCHINGREPAIR BROKEN TIE AT POLE 196 AND INSTALL VIBRATION DAMPENERS | 9 | 390 | 3510 | 0.0039211 | 1.0054e-05
2012-09-03 08:30AM | 213399 | MYP2 | Urban | REPLACE SWITCHING STATION 43199 | 1 | 510 | 510 | 0.00056973 | 1.1171e-06
2012-09-03 09:00AM | 212873 | J497 | Urban | To MandR H/V S/Gear @ Sub 13189 Georges River Rd Kentlyn. | 68 | 300 | 20400 | 0.022789 | 7.5964e-05
2012-09-03 09:00AM | 214955 | 8676 | Urban | Replace LV Links | 2 | 180 | 360 | 0.00040216 | 2.2342e-06
2012-09-03 12:00AM | 209324 | T899 | Urban | Install new DOF | 82 | 360 | 29520 | 0.032977 | 9.1604e-05
2012-09-03 12:00PM | 215181 | 9022 | Urban | low voltage | 1 | 240 | 240 | 0.00026811 | 1.1171e-06
2012-09-04 08:00AM | 206762 | HKA2 | Rural Short | AUGMENT 11 BAYS OF HV MAINS TO 7/4.50AAC FROM POLE 773994 TO POLE 2DY086. | 25 | 480 | 12000 | 0.013405 | 2.7928e-05
2012-09-04 08:00AM | 210699 | W111 | Rural Short | HV Augmentation | 1 | 540 | 540 | 0.00060324 | 1.1171e-06
2012-09-04 08:00AM | 212108 | 8798 | Rural Short | Augment hv mains 3 bays | 50 | 480 | 24000 | 0.026811 | 5.5856e-05
2012-09-04 08:00AM | 213797 | MC1252 | Rural Short | Install vibration dampers. Retro Sub. Defect rectification. Remove redundant 11kV OH mains and poles. | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2012-09-04 08:00AM | 214289 | P608 | Rural Short | Install Vibration Dampers between poles 1415 and 17 | 40 | 480 | 19200 | 0.021449 | 4.4685e-05
2012-09-04 08:00AM | 214292 | L591 | Rural Short | CONTRACTOR TREE TRIMMING | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2012-09-04 08:00AM | 214361 | 27454 | Rural Short | HV Augmentation | 7 | 540 | 3780 | 0.0042227 | 7.8198e-06
2012-09-04 08:00AM | 214725 | R293 | Rural Short | REPAIR BROKEN HV TIE(PSBI) | 2 | 120 | 240 | 0.00026811 | 2.2342e-06
2012-09-04 08:00AM | 212426 | 49319 | Urban | REPLACE LV SW GR SUB 16141 | 63 | 480 | 30240 | 0.033782 | 7.0379e-05
2012-09-04 08:00AM | 214673 | 9029 | Urban | maintenance | 33 | 480 | 15840 | 0.017695 | 3.6865e-05
2012-09-04 08:00AM | 214839 | 8762 | Urban | L.V. Arms | 24 | 480 | 11520 | 0.012869 | 2.6811e-05
2012-09-04 08:15AM | 213844 | NA1207 | Rural Short | Install PM Sub Replace pole and install new pole | 15 | 465 | 6975 | 0.0077919 | 1.6757e-05
2012-09-04 08:30AM | 212323 | 25449 | Rural Short | Install vibration dampers poles 3YR030 271766 3YR014 and 3YR007 retro subs 41398 and 42074 and replace polecap pole 310835 | 11 | 240 | 2640 | 0.0029492 | 1.2288e-05
2012-09-04 08:30AM | 212560 | L941 | Rural Short | Install Auto LBS 91383 + pole and Install new mid span pole | 29 | 420 | 12180 | 0.013607 | 3.2396e-05
2012-09-04 08:30AM | 214244 | MVF2 | Rural Short | Replace Condemned Poles 3XX154 and 3K2590 Contract Tree Trimming and Retrofit DOFs at Sub 30806 | 18 | 420 | 7560 | 0.0084454 | 2.0108e-05
2012-09-04 08:30AM | 214665 | 76225 | Rural Short | LIMITED SWITCHING REPAIR BROKEN TIES AT POLES 28 AND 22 | 9 | 120 | 1080 | 0.0012065 | 1.0054e-05
2012-09-04 08:30AM | 213096 | UNC2 | Urban | Tree trimming using climbers and retrofit subs 42458 and 42122 and remove HV mains and Sub 41316 | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2012-09-04 09:00AM | 214265 | 25747 | Rural Short | Install new poles to relocate HV. Remove redundant poles | 1 | 600 | 600 | 0.00067027 | 1.1171e-06
2012-09-04 09:00AM | 212940 | J504 | Urban | To MandR H/V S/Gear @ Sub 13085 Karri Pl Bradbury. | 100 | 300 | 30000 | 0.033514 | 0.00011171
2012-09-04 09:00AM | 214841 | 8770 | Urban | Replace Service | 1 | 300 | 300 | 0.00033514 | 1.1171e-06
2012-09-04 09:00AM | 214975 | 5878 | Urban | H/V L/V pole change over | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2012-09-04 09:00AM | 214976 | S591 | Urban | L/V pole change over | 4 | 180 | 720 | 0.00080433 | 4.4685e-06
2012-09-04 09:30AM | 213888 | KVA2 | Rural Short | REPLACE POLES 1AJ014 and 1AJ012 | 18 | 300 | 5400 | 0.0060324 | 2.0108e-05
2012-09-04 10:00AM | 214672 | 8679 | Urban | replace column | 83 | 360 | 29880 | 0.03338 | 9.2721e-05
2012-09-04 10:30PM | 212630 | T868 | Rural Short | To MandR H/V SW/Gear and Re-dress HV cables @ Sub 13608 Thomas Rose Dv Rosemeadow. | 18 | 450 | 8100 | 0.0090487 | 2.0108e-05
2012-09-04 11:00AM | 214695 | 76225 | Rural Short | REPLACE HV CROSSARM and REPLACE SHROUD ON SUB | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2012-09-04 11:00AM | 214733 | R293 | Rural Short | REPLACE HV CROSSARM(PSBI) | 6 | 270 | 1620 | 0.0018097 | 6.7027e-06
2012-09-05 08:00AM | 209159 | 8711 | Rural Short | HV Augmentation | 35 | 540 | 18900 | 0.021114 | 3.9099e-05
2012-09-05 08:00AM | 211555 | A049 | Rural Short | To install HV OH mains 7/4.5 AAC.Replace HV xarm Sub 9851. | 13 | 480 | 6240 | 0.0069708 | 1.4523e-05
2012-09-05 08:00AM | 213319 | 1 | Rural Short | Commence commisisoning of new 11kV Generator and associated Transformer. | 127 | 540 | 68580 | 0.076612 | 0.00014187
2012-09-05 08:00AM | 213875 | T828 | Rural Short | INSTALL NEW POLE 863331 | 11 | 540 | 5940 | 0.0066357 | 1.2288e-05
2012-09-05 08:00AM | 213959 | T828 | Rural Short | Replace X Arms Fdr 811 P-9A | 16 | 540 | 8640 | 0.0096519 | 1.7874e-05
2012-09-05 08:00AM | 214047 | X877 | Rural Short | Allow staff to MandR poles and hardware. | 16 | 480 | 7680 | 0.0085795 | 1.7874e-05
2012-09-05 08:00AM | 214069 | BK1299 | Rural Short | Augment LV mains from Pole J28 to Sub 14165 with 1 x 150mm LVABC. | 22 | 450 | 9900 | 0.011059 | 2.4577e-05
2012-09-05 08:00AM | 214971 | L591 | Rural Short | **LIMITED DIST SWITCHING**REPLACE HV CROSSARM and INSTALL VIBRATION DAMPERS | 25 | 420 | 10500 | 0.01173 | 2.7928e-05
2012-09-05 08:00AM | 214996 | R293 | Rural Short | **LIMITED DISTRICT SWITCHING**REPAIR BROKEN HV TIES and RETROFIT SUB | 17 | 420 | 7140 | 0.0079762 | 1.8991e-05
2012-09-05 08:00AM | 211474 | MR2224 | Urban | Install:HV OH mains 1 x new pole 1 x HV UGOH HV UG cable new PS 29799 | 10 | 540 | 5400 | 0.0060324 | 1.1171e-05
2012-09-05 08:00AM | 211856 | 4370 | Urban | Augment 3 bays of O/H HV mains to 3 x 19/3.25 AAC. | 180 | 480 | 43200 | 0.04826 | 0.00020108
2012-09-05 08:00AM | 213123 | WRE2 | Urban | POLE REPLACEMENT x 2 + INSTALL 1 LBS + DOF'S 40a | 237 | 540 | 127980 | 0.14297 | 0.00026476
2012-09-05 08:00AM | 213128 | CRA2 | Urban | Replace pole and augment | 248 | 450 | 111600 | 0.12467 | 0.00027705
2012-09-05 08:00AM | 214062 | KYA2 | Urban | NEW PADSUB | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2012-09-05 08:00AM | 214165 | 7962 | Urban | REPLACE CONDEMNED POLE SUB 2259 | 46 | 480 | 22080 | 0.024666 | 5.1388e-05
2012-09-05 08:30AM | 213563 | RWD2 | Rural Short | Install 20 dampers @ 5 worksites and replace HV x-arm @ sub 30830 | 98 | 420 | 41160 | 0.045981 | 0.00010948
2012-09-05 08:30AM | 214314 | 35981 | Rural Short | Install vibration dampers | 36 | 300 | 10800 | 0.012065 | 4.0216e-05
2012-09-05 09:00AM | 212967 | T869 | Urban | To MandR H/V S/Gear @ Sub 11439 Kaylan Ave Bradbury. | 92 | 300 | 27600 | 0.030833 | 0.00010278
2012-09-05 09:00AM | 214553 | 5496 | Urban | L/V cross arm change | 3 | 180 | 540 | 0.00060324 | 3.3514e-06
2012-09-06 01:00PM | 215226 | S326 | Urban | Replace Rusty Column | 6 | 120 | 720 | 0.00080433 | 6.7027e-06
2012-09-06 08:00AM | 211299 | HKA2 | Rural Short | AUGMENT 7 BAYS . INSTLALL 5 NEW POLES. INSTALL NEW ABS 87961 ON POLE 824679. | 16 | 480 | 7680 | 0.0085795 | 1.7874e-05
2012-09-06 08:00AM | 211523 | J477 | Rural Short | Retro Subs 10398 and 11672 Replace Tx @ Sub 10398. | 23 | 420 | 9660 | 0.010791 | 2.5694e-05
2012-09-06 08:00AM | 212201 | 8634 | Rural Short | augment 4 bays of lv mains | 20 | 480 | 9600 | 0.010724 | 2.2342e-05
2012-09-06 08:00AM | 213259 | L582 | Rural Short | STAND POLE and AUGMENT HV MAINS | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2012-09-06 08:00AM | 213902 | T842 | Rural Short | Connect to the network via new section of O/H mains new pole sub 29760 | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2012-09-06 08:00AM | 214124 | 35989 | Rural Short | String new conductor for 66kV Feeder 869/2 between new Poles 1 -15. | 79 | 480 | 37920 | 0.042361 | 8.8252e-05
2012-09-06 08:00AM | 214825 | WBD2 | Rural Short | String HV insulated mains | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2012-09-06 08:00AM | 209158 | 7970 | Urban | Augment 7 bays of HV mains and replace 4 poles. | 198 | 540 | 106920 | 0.11944 | 0.00022119
2012-09-06 08:00AM | 213966 | A352 | Urban | RE-INSTATE LEANING POLE and EXTEND O/H HV and RE-STRING LV MAINS. | 98 | 480 | 47040 | 0.052549 | 0.00010948
2012-09-06 08:00AM | 215044 | L534 | Urban | Replace Pole | 39 | 480 | 18720 | 0.020912 | 4.3568e-05
2012-09-06 08:00AM | 215116 | NWD2 | Urban | REPLACE UGOH and POLE TEST CABLE AND COMMISION | 170 | 480 | 81600 | 0.091157 | 0.00018991
2012-09-06 08:30AM | 210685 | MVC2 | Rural Short | HV Augmentation | 42 | 540 | 22680 | 0.025336 | 4.6919e-05
2012-09-06 08:30AM | 212747 | L941 | Rural Short | Remove ABS C190 Replace pole 103 with Auto LBS 91315 + pole | 23 | 450 | 10350 | 0.011562 | 2.5694e-05
2012-09-06 08:30AM | 213640 | RBB2 | Rural Short | Install vibration dampers @ pole 3YG097 and 3YG096 | 21 | 210 | 4410 | 0.0049265 | 2.346e-05
2012-09-06 08:30AM | 213649 | RBC2 | Rural Short | Install 6 vibration dampers @ 2 worksites | 35 | 210 | 7350 | 0.0082108 | 3.9099e-05
2012-09-06 08:30AM | 213819 | PKD2 | Urban | Retension HV and Lv mains | 64 | 240 | 15360 | 0.017159 | 7.1496e-05
2012-09-06 09:00AM | 214160 | 1 | Rural Short | Replace faulty Surge Diverters between JBB1 and JBB2.Replace 33kV Surge diverers #1 TX | 5 | 300 | 1500 | 0.0016757 | 5.5856e-06
2012-09-06 09:00AM | 214866 | W111 | Rural Short | Augment low voltage mains and remove open wire. | 57 | 360 | 20520 | 0.022923 | 6.3676e-05
2012-09-06 09:00AM | 213352 | MYK2 | Urban | Install servive poles and replace services | 11 | 300 | 3300 | 0.0036865 | 1.2288e-05
2012-09-06 09:00AM | 215028 | D831 | Urban | Change LV X-arms | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2012-09-06 09:00AM | 215231 | C824 | Urban | Replace Rusty Column | 13 | 180 | 2340 | 0.0026141 | 1.4523e-05
2012-09-06 12:30PM | 213652 | RBE2 | Rural Short | Install vibration dampers @ pole 3X0736 and 3X0694 | 14 | 180 | 2520 | 0.0028151 | 1.564e-05
2012-09-07 08:00AM | 210670 | 8711 | Rural Short | HV Pole Changes | 28 | 540 | 15120 | 0.016891 | 3.1279e-05
2012-09-07 08:00AM | 211635 | 48196 | Rural Short | Allow staff to De-commission and remove pole sub 22592. | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2012-09-07 08:00AM | 212989 | A049 | Rural Short | Augment HV OH mains 7/4.5 AAC and install ABS 90340. | 13 | 480 | 6240 | 0.0069708 | 1.4523e-05
2012-09-07 08:00AM | 214541 | KC1288 | Rural Short | REPLACE LV CROSSARMS @ SUB 1235 OFF MAMRE RD KEMPS CREEK | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2012-09-07 08:00AM | 215376 | KC1288 | Rural Short | Maintenance | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2012-09-07 08:30AM | 212664 | T852 | Rural Short | REPLACE Tx @ SUB 4823 | 8 | 210 | 1680 | 0.0018768 | 8.937e-06
2012-09-07 08:30AM | 213416 | 4353 | Rural Short | REPLACE POLE 8 USL 2300. | 6 | 420 | 2520 | 0.0028151 | 6.7027e-06
2012-09-07 08:30AM | 213916 | WBD2 | Rural Short | REPLACE 2 MONTH CONDEMNED POLE | 90 | 420 | 37800 | 0.042227 | 0.00010054
2012-09-07 08:30AM | 214108 | GG1295 | Rural Short | AUGMENT HV MAINS BETWEEN POLES 212620 and 824775 | 12 | 420 | 5040 | 0.0056303 | 1.3405e-05
2012-09-07 08:30AM | 213332 | APE2 | Urban | REPLACE POLE 4DP050 REPLACE LV ARMS POLES 4DP041 and 4DP024. | 80 | 360 | 28800 | 0.032173 | 8.937e-05
2012-09-07 08:30AM | 215325 | C896 | Urban | LV Interruption | 40 | 330 | 13200 | 0.014746 | 4.4685e-05
2012-09-07 09:00AM | 214659 | SXD2 | Rural Short | Replace TX @ S/S 50295. | 13 | 240 | 3120 | 0.0034854 | 1.4523e-05
2012-09-07 09:00AM | 215227 | B799 | Urban | Replace Rusty Column | 29 | 120 | 3480 | 0.0038876 | 3.2396e-05
2012-09-07 09:00AM | 215303 | 27202 | Urban | Replace 40hr rusty column | 7 | 120 | 840 | 0.00093838 | 7.8198e-06
2012-09-07 10:00AM | 214643 | 8679 | Urban | maintenance | 31 | 360 | 11160 | 0.012467 | 3.4631e-05
2012-09-07 11:00AM | 214139 | A098 | Rural Short | RETRO SUB # 1895 | 2 | 330 | 660 | 0.0007373 | 2.2342e-06
2012-09-07 11:00AM | 215225 | 27202 | Urban | Replace Rusty Column | 26 | 120 | 3120 | 0.0034854 | 2.9045e-05
2012-09-07 11:00AM | 215228 | S326 | Urban | Replace Rusty Column | 20 | 120 | 2400 | 0.0026811 | 2.2342e-05
2012-09-08 07:00AM | 214395 | 35312 | Urban | Remove OH mains and Sw/Gr install new HV cable and Sw/Gr Sub 2392 STJ | 11 | 570 | 6270 | 0.0070043 | 1.2288e-05
2012-09-08 08:00AM | 214963 | S735 | Rural Short | Replace pole and install ABS 94497 for future works | 8 | 420 | 1680 | 0.0018768 | 8.937e-06
2012-09-08 08:30AM | 212912 | A052 | Rural Short | REPLACE ABS 17158 WITH NEW SCADA LBS 91725. REPLACE HV X-ARMS AND INSULATORS. | 1 | 390 | 390 | 0.00043568 | 1.1171e-06
2012-09-08 09:00AM | 215113 | S334 | Urban | Replace switchboard in column | 3 | 240 | 720 | 0.00080433 | 3.3514e-06
2012-09-09 08:00AM | 209771 | D828 | Urban | Allow staff to replace pole and erect new LBS 86575. | 25 | 480 | 12000 | 0.013405 | 2.7928e-05
2012-09-09 08:00AM | 214413 | UNC2 | Urban | REPLACE HV RGB12 SWITCHGEAR | 1 | 390 | 390 | 0.00043568 | 1.1171e-06
2012-09-09 08:30AM | 214097 | RWC2 | Rural Short | Install 4 vibration dampers @ 2 worksites | 15 | 210 | 3150 | 0.0035189 | 1.6757e-05
2012-09-09 08:30AM | 214392 | 35816 | Rural Short | Change condemed pole 311 and repair HV Hardware | 38 | 420 | 12600 | 0.014076 | 4.2451e-05
2012-09-09 08:30AM | 214105 | MG1204 | Urban | 1/ Break HV bonds at pole 3T04082/ Replace pole 3T0396 and install new Dof's 92618 on new pole 8531503/ Remake bonds at pole 3T0408 | 2 | 450 | 900 | 0.0010054 | 2.2342e-06
2012-09-09 08:30AM | 215099 | 35005 | Urban | Chang over poles | 19 | 390 | 7410 | 0.0082779 | 2.1225e-05
2012-09-09 09:00AM | 205968 | BDA2 | Urban | REPLACE POLE 1XR105 | 88 | 360 | 31680 | 0.03539 | 9.8307e-05
2012-09-09 12:30PM | 214058 | BWH2 | Rural Short | Install 6 dampers @ 2 worksites | 9 | 180 | 1620 | 0.0018097 | 1.0054e-05
2012-09-10 08:00AM | 208161 | 9056 | Urban | AUGMENT 6 BAYS OF HV MAINS | 722 | 600 | 433200 | 0.48394 | 0.00080656
2012-09-10 08:00AM | 214096 | MR2292 | Urban | ESTABLISH NEW 22KV 315 KVA P/M SUB 28658 INSTALL AREVA 2FDR HV S/GEAR INSTALL 22KV 3 CORE Al XLPE CABLE | 15 | 540 | 8100 | 0.0090487 | 1.6757e-05
2012-09-10 08:00AM | 214343 | 35530 | Urban | replace column | 104 | 480 | 49920 | 0.055767 | 0.00011618
2012-09-10 08:30AM | 214286 | R218 | Rural Short | Install new pole 825629 and augment conductors from pole 825629 to pole 825626 | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2012-09-10 08:30AM | 214412 | RWD2 | Rural Short | Install 6 dampers @ 3 worksites | 56 | 420 | 23520 | 0.026275 | 6.2559e-05
2012-09-10 08:30AM | 214282 | RVC2 | Urban | Tree removal by Contractors near Sub 40140 | 23 | 330 | 7590 | 0.0084789 | 2.5694e-05
2012-09-10 08:30AM | 214682 | BLD2 | Urban | REPLACE LEAKING TRANSFORMER | 113 | 240 | 27120 | 0.030296 | 0.00012623
2012-09-10 09:00AM | 214007 | J514 | Urban | To MandR H/V S/Gear @ Sub 11400 Rosewood Dv Macquarie Fields. | 88 | 300 | 26400 | 0.029492 | 9.8307e-05
2012-09-11 08:00AM | 211330 | HKA2 | Rural Short | REPLACE 4 POLES AND INSTALL ONE NEW. REMOVE ONE POLE.REPLACE USL 30481 WITH 87972 USL 30350 WITH 87971 AND REMOVE ABS 30368. | 9 | 480 | 4320 | 0.004826 | 1.0054e-05
2012-09-11 08:00AM | 211885 | A049 | Rural Short | Replace pole and re install LBS 80132 | 58 | 480 | 13920 | 0.01555 | 6.4793e-05
2012-09-11 08:00AM | 212467 | 8798 | Rural Short | change 2 poles and augment 2 bays of lv | 160 | 480 | 76800 | 0.085795 | 0.00017874
2012-09-11 08:00AM | 214296 | L591 | Rural Short | REMOVE ABSINSTALL LBS and AUGMENT HV MAINS | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2012-09-11 08:00AM | 214339 | 25744 | Rural Short | Hv Pole Replacement | 42 | 540 | 22680 | 0.025336 | 4.6919e-05
2012-09-11 08:00AM | 214640 | R218 | Rural Short | Stand new and replace poles. | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2012-09-11 08:00AM | 209163 | AZ1272 | Urban | HV Augmentation | 140 | 570 | 79800 | 0.089146 | 0.0001564
2012-09-11 08:00AM | 211847 | 1125 | Urban | Allow staff to augment section Of HV mains and replace pole. | 84 | 480 | 40320 | 0.045042 | 9.3838e-05
2012-09-11 08:00AM | 213170 | CRD2 | Urban | Replace poles | 29 | 450 | 13050 | 0.014578 | 3.2396e-05
2012-09-11 08:00AM | 215377 | 35702 | Urban | maintenance | 37 | 480 | 17760 | 0.01984 | 4.1333e-05
2012-09-11 08:00AM | 215541 | J481 | Urban | Connect new pillars to existing network | 25 | 480 | 12000 | 0.013405 | 2.7928e-05
2012-09-11 08:30AM | 214368 | BGB2 | Rural Short | Replace 11kV Pole and install a new 11kV pole | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2012-09-11 08:30AM | 214886 | 35981 | Rural Short | Install vibration dampers | 31 | 300 | 9300 | 0.010389 | 3.4631e-05
2012-09-11 08:30AM | 213956 | KMD2 | Urban | REPLACE POLE 4KG309 | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2012-09-11 09:00AM | 215161 | S598 | Urban | LV Pole change | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2012-09-11 09:00AM | 215166 | S598 | Urban | LV pole change | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2012-09-11 09:30AM | 215457 | ULE2 | Rural Short | Replace LV x pole | 72 | 270 | 19440 | 0.021717 | 8.0433e-05
2012-09-11 09:30AM | 215169 | 3114 | Urban | Changeover Pole | 2 | 270 | 540 | 0.00060324 | 2.2342e-06
2012-09-12 08:00AM | 213632 | 57448 | Rural Short | INSTALL VIBRATION DAMPERSREPLACE HV CROSSARMS | 40 | 420 | 16800 | 0.018768 | 4.4685e-05
2012-09-12 08:00AM | 213671 | L941 | Rural Short | Retro rewire and replace all arms with ABC fuse box @ sub 19617 | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2012-09-12 08:00AM | 214185 | 35988 | Rural Short | Install Vibration Dampers between poles 1415179 and178 | 157 | 450 | 70650 | 0.078925 | 0.00017539
2012-09-12 08:00AM | 214363 | 27454 | Rural Short | HV Augmentation | 7 | 570 | 3990 | 0.0044573 | 7.8198e-06
2012-09-12 08:00AM | 214405 | 27446 | Rural Short | Uprate pole sub 22787 to 100kVA Install G1 ground stay on pole 284284 | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2012-09-12 08:00AM | 215305 | R293 | Rural Short | **LIMITED DISTRICT SWITCHING**REPAIR BROKEN HV TIE(PSBI) | 2 | 120 | 240 | 0.00026811 | 2.2342e-06
2012-09-12 08:00AM | 212197 | 4374 | Urban | 1. Install LBS 82789 and augment 3 bays of O/H HV mains to 150mm HV NMSABC.2. To replace Arrestors Sub 1706 Moray St 3. To Repair ABS 2453 March St | 12 | 480 | 2880 | 0.0032173 | 1.3405e-05
2012-09-12 08:00AM | 215256 | 9030 | Urban | Telstra - maintenance | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2012-09-12 08:30AM | 214371 | WBC2 | Rural Short | Allow trimming and removal of tree | 42 | 330 | 13860 | 0.015483 | 4.6919e-05
2012-09-12 08:30AM | 214044 | MYG2 | Urban | REPLACE LEAKING TRANSFORMER | 81 | 300 | 24300 | 0.027146 | 9.0487e-05
2012-09-12 08:30AM | 214776 | PKE2 | Urban | RETROFIT SUBSTATION REPLACE MDI UNIT REPLACE HV FUSE ARM REPLACE POLE CAP. | 96 | 360 | 34560 | 0.038608 | 0.00010724
2012-09-12 08:30PM | 212851 | PKC2 | Urban | REPLACE POLES MERRETT AVE and LAKE AVE AUGMENT HV MAINS MERRETT AVE INSTALL LBS 88360 | 69 | 540 | 37260 | 0.041624 | 7.7081e-05
2012-09-12 09:00AM | 214555 | 9046 | Urban | REPLACE POLE J1904 AND INSTALL LBS | 10 | 360 | 3600 | 0.0040216 | 1.1171e-05
2012-09-12 09:00AM | 215513 | 35388 | Urban | remove redundant HV OH mains | 50 | 360 | 18000 | 0.020108 | 5.5856e-05
2012-09-12 09:30AM | 213019 | ULE2 | Rural Short | Replace Condemned pole 1HP 030Northaven Ave BAWLEY POINT. | 151 | 300 | 45300 | 0.050606 | 0.00016869
2012-09-12 09:30AM | 215062 | BDG2 | Rural Short | REPLACE POLE 328118 | 39 | 210 | 8190 | 0.0091492 | 4.3568e-05
2012-09-12 12:00PM | 215257 | 35695 | Rural Short | Telstra - maintenance | 1 | 240 | 240 | 0.00026811 | 1.1171e-06
2012-09-13 08:00AM | 209162 | 8711 | Rural Short | HV Augmentation | 35 | 570 | 19950 | 0.022287 | 3.9099e-05
2012-09-13 08:00AM | 210701 | CT1262 | Rural Short | HV Augmentation | 10 | 540 | 5400 | 0.0060324 | 1.1171e-05
2012-09-13 08:00AM | 212997 | 8802 | Rural Short | Remove Sub # 2876 Install new Sub # 29977and install new LBS 95025 | 8 | 510 | 4080 | 0.0045578 | 8.937e-06
2012-09-13 08:00AM | 213445 | L582 | Rural Short | REPLACE POLE and USL'SAUGMENT HV MAINS | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2012-09-13 08:00AM | 214237 | MC1252 | Rural Short | Replace pole and install LBS. Remove ABS. | 38 | 420 | 15960 | 0.017829 | 4.2451e-05
2012-09-13 08:00AM | 214280 | 35989 | Rural Short | Pull in OPGW for new 66kV Feeder 869/2 from Pole 1 -25. Clip in 66kV Uranus conductor from new poles 1 -15 | 47 | 480 | 22560 | 0.025202 | 5.2505e-05
2012-09-13 08:00AM | 214746 | DP1210 | Rural Short | Reconnect HV jumpers | 59 | 270 | 15930 | 0.017796 | 6.591e-05
2012-09-13 08:00AM | 214781 | X802 | Rural Short | REPLACE HV CROSSARM and RETROFIT SUB | 11 | 450 | 4950 | 0.0055297 | 1.2288e-05
2012-09-13 08:00AM | 211859 | 55885 | Urban | Augment LV OH mains to 150 ABC | 48 | 510 | 12240 | 0.013674 | 5.3622e-05
2012-09-13 08:00AM | 214189 | UNJ2 | Urban | REPLACE POLE AND TRANSFORMER | 82 | 450 | 36900 | 0.041222 | 9.1604e-05
2012-09-13 08:00AM | 214346 | 8679 | Urban | REPLACE COLUMNS | 51 | 300 | 15300 | 0.017092 | 5.6973e-05
2012-09-13 08:00AM | 214790 | 35503 | Urban | Replace ABS's 47404 and 47405 with 90887 and 90886. Also replace 6 poles and OH 11KV mains. | 7 | 540 | 3780 | 0.0042227 | 7.8198e-06
2012-09-13 08:00AM | 215378 | 27191 | Urban | Remove:1 x minor pillar and UG cable | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2012-09-13 08:30AM | 214483 | MVC2 | Rural Short | New Substation and OH Mains | 5 | 390 | 1950 | 0.0021784 | 5.5856e-06
2012-09-13 08:30AM | 214615 | WWF2 | Urban | Trim Tree overhangs | 3 | 300 | 900 | 0.0010054 | 3.3514e-06
2012-09-13 09:00AM | 210909 | KVA2 | Rural Short | Install Vibration Dampers @ poles 1JY008 and 1JY007. | 6 | 180 | 1080 | 0.0012065 | 6.7027e-06
2012-09-13 09:00AM | 214370 | 35989 | Rural Short | Install Vibration Dampers between poles 101 and 100 | 2 | 330 | 660 | 0.0007373 | 2.2342e-06
2012-09-13 09:00AM | 213001 | J502 | Urban | To MandR H/V S/Gear @ Sub 13005 Creigan Rd Bradbury. | 48 | 300 | 14400 | 0.016087 | 5.3622e-05
2012-09-13 09:00AM | 215159 | S598 | Urban | LV Pole change | 2 | 180 | 360 | 0.00040216 | 2.2342e-06
2012-09-13 09:00AM | 215587 | X858 | Urban | LV cable fault | 76 | 330 | 25080 | 0.028017 | 8.4901e-05
2012-09-13 10:00AM | 214348 | 8679 | Urban | REPLACE COLUMNS | 39 | 360 | 14040 | 0.015684 | 4.3568e-05
2012-09-14 01:00PM | 215643 | 48203 | Urban | Connect LV Network within new subdivision to existing LV Network via 6 Pillar bond-ins. | 6 | 60 | 480 | 0.00053622 | 6.7027e-06
2012-09-14 06:00AM | 214848 | A322 | Urban | Replace ace SW gear at TRF 2 sub 5231 and uprate transformer.Establish new feeder from CB 35440 Homepride zone to sw 91240 | 2 | 720 | 1440 | 0.0016087 | 2.2342e-06
2012-09-14 08:00AM | 214300 | W112 | Rural Short | To allow staff to Retro Sub 12263 and Sub 11263 Cataract Dam Appin | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2012-09-14 08:00AM | 214345 | A049 | Rural Short | Install HV OH mains 150 ABC and 19/3.25 AAC.Install LBS 90341.Augment LV OH mains 150 ABC. | 28 | 480 | 13440 | 0.015014 | 3.1279e-05
2012-09-14 08:00AM | 214365 | 35988 | Rural Short | Install Vibration Dampers and repair HV defects | 29 | 510 | 14790 | 0.016522 | 3.2396e-05
2012-09-14 08:00AM | 213717 | R256 | Urban | Replace 342 with pole 866126 and stand 5 new poles. | 52 | 480 | 24960 | 0.027883 | 5.809e-05
2012-09-14 08:00AM | 214601 | UNB2 | Urban | REPLACE CONDEMNED POLES REPLACE ABS RETROFIT SUB AND REPAIR DEFECTS | 300 | 450 | 76050 | 0.084957 | 0.00033514
2012-09-14 08:00AM | 215381 | 9020 | Urban | maintenance | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2012-09-14 08:30AM | 214824 | X217 | Rural Short | REPAIR BROKEN HV TIES(PSBI'S) | 10 | 240 | 2400 | 0.0026811 | 1.1171e-05
2012-09-14 08:30AM | 215050 | 57448 | Rural Short | REPLACE CONDEMNED POLE 3 | 3 | 390 | 1170 | 0.001307 | 3.3514e-06
2012-09-14 09:00AM | 215399 | L537 | Urban | Two pole replacements | 18 | 360 | 6480 | 0.0072389 | 2.0108e-05
2012-09-14 09:00AM | 215446 | M166 | Urban | Changeover Pole | 25 | 360 | 9000 | 0.010054 | 2.7928e-05
2012-09-14 09:00AM | 215451 | AZ1205 | Urban | Relocate services | 14 | 420 | 5880 | 0.0065687 | 1.564e-05
2012-09-14 09:00AM | 215684 | 16666 | Urban | LV Oh Change over | 9 | 360 | 3240 | 0.0036195 | 1.0054e-05
2012-09-14 09:00AM | 215844 | F601 | Urban | LV Changeover | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2012-09-14 09:30AM | 213799 | HKC2 | Rural Short | Replace pole 3HC137. | 171 | 330 | 56430 | 0.063039 | 0.00019103
2012-09-14 10:30AM | 215643 | 48203 | Urban | Connect LV Network within new subdivision to existing LV Network via 6 Pillar bond-ins. | 10 | 120 | 960 | 0.0010724 | 1.1171e-05
2012-09-15 06:00AM | 212124 | 6419 | Urban | REPLACE RGB 12 WITH SAFE LINK HV SWITCH GEAR REPLACE TX1SUB 5230 SCRIVENER ST WARWICK FARM | 1 | 1020 | 1020 | 0.0011395 | 1.1171e-06
2012-09-15 08:00AM | 214982 | 4860 | Urban | Establish new pad sub 29600 | 2 | 600 | 1200 | 0.0013405 | 2.2342e-06
2012-09-15 08:30AM | 214471 | 35989 | Rural Short | Repair defects at poles 148 154 and 155. | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2012-09-15 09:00AM | 212587 | 25451 | Rural Short | AUGMENT ONE BAY OF HV MAINS TO 3x7/4.50AAC FROM POLE 221326 TO POLE 3YY210 | 21 | 360 | 7560 | 0.0084454 | 2.346e-05
2012-09-16 07:00AM | 212774 | S743 | Rural Short | REPLACE USL POLE 76 | 6 | 540 | 1620 | 0.0018097 | 6.7027e-06
2012-09-16 07:00AM | 212405 | 35769 | Urban | Job 1 Re Configure HV Network. Remove ABS 28551 USL 10942 and 1 Bay OH Mains between ABS 28551 and usl 10942. Remove and abandon HV cable between Sw 80248 and HV UGOH pole 271108. Install new UGOH on pole J271111. Terminate new cable to Sw 80249. Job 2 in | 14 | 540 | 7560 | 0.0084454 | 1.564e-05
2012-09-16 08:00AM | 215407 | X492 | Rural Long | *LIMITED DISTRICT SWITCHING* REPAIR BROKEN HV TIE and INSTALL VIBRATION DAMPERS | 19 | 420 | 7980 | 0.0089146 | 2.1225e-05
2012-09-16 08:00AM | 209252 | 4857 | Urban | AUGMENT SECTION OF O/H MAINS TO 7/4.50 AAC REPLACE USL 4984 WITH NEW LBS 91483 ON REPLACEMENT POLE 839389 | 18 | 540 | 9720 | 0.010858 | 2.0108e-05
2012-09-16 08:00AM | 212404 | S602 | Urban | Augment LV mains to 150 ABC.Replace OH SL mains. | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2012-09-16 08:00AM | 213407 | CRD2 | Urban | Replace poles and Tx and augment | 42 | 450 | 18900 | 0.021114 | 4.6919e-05
2012-09-16 08:00AM | 215019 | UNG2 | Urban | REPLACE HV SWITCHGEAR MAINTAIN SWITCHGEAR | 4 | 510 | 2040 | 0.0022789 | 4.4685e-06
2012-09-16 08:30AM | 214701 | BWH2 | Rural Short | Install 6 vibration dampers @ poles 3XH0153XR0063XR0073XR010 and 3XR011 | 18 | 210 | 3780 | 0.0042227 | 2.0108e-05
2012-09-16 12:30PM | 212962 | RWA2 | Rural Short | Install 4 vibration dampers @ 2 worksites | 13 | 180 | 2340 | 0.0026141 | 1.4523e-05
2012-09-16 12:30PM | 213150 | MGD2 | Rural Short | Install vibration dampers @ pole 3TX010 and pole 3TY010 | 6 | 180 | 1080 | 0.0012065 | 6.7027e-06
2012-09-17 08:00AM | 213342 | P608 | Rural Short | Install new pole and Auto LBS. Remove pole. Remove USL. | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2012-09-17 08:00AM | 214259 | 5898 | Rural Short | Connect New Sub 29081 replace pole 90 with new pole 824656 | 1 | 510 | 510 | 0.00056973 | 1.1171e-06
2012-09-17 08:00AM | 212769 | WRE2 | Urban | REPLACE POLE 4CK747 WITH POLE 847922 AND POLE 4CK748 WITH POLE 847923.INSTALL 40A DOFs ON POLE 847922.AUGMENT ONE BAY OF HV MAINS TO 3x7/4.50AAC FROM POLE 847922 TO POLE 847923. | 260 | 480 | 124800 | 0.13942 | 0.00029045
2012-09-17 08:00AM | 214217 | S785 | Urban | Install new DOFs | 14 | 520 | 7280 | 0.0081326 | 1.564e-05
2012-09-17 08:00AM | 214815 | 27334 | Urban | To Re-Pump Hazymeyer Cable Box Termination @ SW-M979 In Sub 13210 Hoping Rd Ingleburn. | 95 | 300 | 28500 | 0.031838 | 0.00010613
2012-09-17 08:30AM | 214279 | BDF2 | Rural Short | Uprate substation | 13 | 420 | 5460 | 0.0060995 | 1.4523e-05
2012-09-17 08:30AM | 215750 | L588 | Rural Short | **LIMITED DISTRICT SWITCHING**REPLACE CROSSARM ON POLE 3 AND INSTALL VIBRATION DAMPENERS ON POLES 2 34 AND 5 | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2012-09-17 09:30AM | 208378 | BDB2 | Urban | Replace TX and Retrofit S/S 50114Fairway Dr NORTH NOWRA. | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2012-09-17 09:30AM | 214712 | 5869 | Urban | Replace road crossing service mains to pole 2583. | 2 | 270 | 540 | 0.00060324 | 2.2342e-06
2012-09-17 09:30AM | 215449 | CRD2 | Urban | Stand new LV poles | 27 | 120 | 3240 | 0.0036195 | 3.0162e-05
2012-09-17 12:30PM | 215168 | RWD2 | Rural Short | Install vibration dampers at POLE 3VP267 and 3VP266 | 5 | 180 | 900 | 0.0010054 | 5.5856e-06
2012-09-18 01:00PM | 216057 | BDG2 | Rural Short | REPLACE STREET LIGHT COLUMNS | 137 | 120 | 16440 | 0.018365 | 0.00015305
2012-09-18 01:00PM | 215884 | 19816 | Urban | Blue Point Link in Column | 8 | 90 | 720 | 0.00080433 | 8.937e-06
2012-09-18 08:00AM | 212530 | 8798 | Rural Short | Install ABS and Augment 4 bays of lv mains | 153 | 510 | 78030 | 0.087169 | 0.00017092
2012-09-18 08:00AM | 213172 | W185 | Rural Short | Replace Castiron UGOH | 10 | 420 | 4200 | 0.0046919 | 1.1171e-05
2012-09-18 08:00AM | 214347 | A049 | Rural Short | Install HV OH mains 19/3.25 AAC | 13 | 420 | 5460 | 0.0060995 | 1.4523e-05
2012-09-18 08:00AM | 215763 | A096 | Rural Short | Maintenance - replace pole | 7 | 180 | 1260 | 0.0014076 | 7.8198e-06
2012-09-18 08:00AM | 215694 | 1131 | Urban | Erect ABS | 21 | 480 | 10080 | 0.011261 | 2.346e-05
2012-09-18 08:00AM | 216085 | 9027 | Urban | MAINTENANCE | 11 | 210 | 2310 | 0.0025805 | 1.2288e-05
2012-09-18 08:30AM | 212204 | DP1210 | Rural Short | REPLACE ABSs 71222 and 71200 REPLACE UG/OH'S POLE 200305 and 775197 REPLACE POLES 222607 4CT008 4CR200 RETRO S/S 41292 DEFECT REPAIRS POLE 4CT132 4CT123 4CT118 4CT135 | 12 | 420 | 5040 | 0.0056303 | 1.3405e-05
2012-09-18 08:30AM | 214049 | 10286 | Rural Short | Replace pole 203 retro sub 2800 and replace leaky Tx at sub 16044 | 16 | 420 | 6720 | 0.007507 | 1.7874e-05
2012-09-18 08:30AM | 215875 | 3334 | Urban | Change LV arms | 5 | 450 | 2250 | 0.0025135 | 5.5856e-06
2012-09-18 08:30AM | 215965 | BWD2 | Urban | Relocate LV Service pole PL351289 | 2 | 300 | 600 | 0.00067027 | 2.2342e-06
2012-09-18 08:45AM | 214883 | BWB2 | Urban | Install 2 new 11kV poles and 1 LV Pole | 24 | 360 | 8640 | 0.0096519 | 2.6811e-05
2012-09-18 09:00AM | 214862 | W111 | Rural Short | Change pole substation 10725 and low voltage pole 64. | 61 | 420 | 25620 | 0.028621 | 6.8144e-05
2012-09-18 09:00AM | 215883 | 27202 | Urban | Replace Rusty Column | 2 | 180 | 360 | 0.00040216 | 2.2342e-06
2012-09-18 11:00AM | 215764 | A098 | Rural Short | maintenance | 10 | 300 | 3000 | 0.0033514 | 1.1171e-05
2012-09-18 11:00PM | 212033 | 48168 | Urban | REPLACE HV SWGR AT S/S 12642 | 185 | 59 | 10915 | 0.012193 | 0.00020667
2012-09-19 07:30AM | 215561 | 5869 | Urban | Isolate Tx below DOFs for work.Change LV fuses (West Dist) and Erect LV UGOH on Sub Install Pillar | 22 | 450 | 9900 | 0.011059 | 2.4577e-05
2012-09-19 08:00AM | 212263 | L584 | Rural Short | REMOVE USL'SREPLACE POLE and AUGMENT HV MAINS | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2012-09-19 08:00AM | 212777 | D810 | Rural Short | INSTALL STAYS TO POLES 102 103 401181 INSTALL VIBRATION DAMPERS ON RIVER CROSSING BAY 401181 TO POLE 166. INSTALL VIBRATION DAMPERS ADJ USL E561. INSTALL VIBRATION DAMPERS ON RIVER CROSSING BAY 774388 TO 110. | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2012-09-19 08:00AM | 215103 | BK1251 | Rural Short | REPAIR HVABC CABLE TERMINATION and STRAIGHTEN POLE | 19 | 420 | 7980 | 0.0089146 | 2.1225e-05
2012-09-19 08:00AM | 215755 | R293 | Rural Short | **LIMITED DISTRICT SWITCHING**REPAIR BROKEN HV TIE(PSBI) | 2 | 120 | 240 | 0.00026811 | 2.2342e-06
2012-09-19 08:00AM | 212593 | 5877 | Urban | REPLACE POLE 1005 | 100 | 420 | 21000 | 0.02346 | 0.00011171
2012-09-19 08:00AM | 212732 | WRC2 | Urban | AUGMENT 2 BAYS OF HV MAINS TO 3x7/4.50AAC FROM POLE 289046 TO POLE 4CK073.REPLACE POLE 4CK070 WITH POLE 847832 AND INSTALL LBS 92307. | 107 | 480 | 51360 | 0.057375 | 0.00011953
2012-09-19 08:00AM | 213635 | R251 | Urban | Replace pole 353 with pole 865082 stand 5 poles re wire and replace links and fuses at Sub 14004 and augment 1 bay of LV mains. | 39 | 480 | 18720 | 0.020912 | 4.3568e-05
2012-09-19 08:00AM | 215092 | WRC2 | Urban | Replace UGOH pole | 61 | 480 | 29280 | 0.032709 | 6.8144e-05
2012-09-19 08:00AM | 215739 | 35702 | Urban | maintenance | 50 | 480 | 24000 | 0.026811 | 5.5856e-05
2012-09-19 08:30AM | 214391 | X877 | Rural Short | Replace X-pole USL J049 | 3 | 450 | 1350 | 0.0015081 | 3.3514e-06
2012-09-19 08:30AM | 215186 | MVF2 | Rural Short | Replace Condemed Poles 3XK568and 3K1912 and Replace HV Cross Arm on Pole 3XK608 and fit vibration dampers | 32 | 420 | 13440 | 0.015014 | 3.5748e-05
2012-09-19 08:30AM | 213661 | WRC2 | Urban | REPLACE POLE 1D0564REPLACE TX SUB 41821RETRO SUB 42182 and REPLACE LV ARM POLE 1D0559. | 105 | 420 | 44100 | 0.049265 | 0.0001173
2012-09-19 08:30AM | 214201 | BLE2 | Urban | Replace poles Retrofit subs and replace crossarms | 151 | 420 | 63420 | 0.070848 | 0.00016869
2012-09-19 09:00AM | 216089 | 3351 | Urban | LV Arm change | 6 | 180 | 1080 | 0.0012065 | 6.7027e-06
2012-09-19 09:30AM | 213920 | ULE2 | Rural Short | Replace Condemned pole 1GD010 Monkey Mountain Rd TERMEIL | 12 | 270 | 3240 | 0.0036195 | 1.3405e-05
2012-09-19 09:30AM | 215913 | SXD2 | Rural Short | Replace TX @ S/S 50869. | 75 | 360 | 27000 | 0.030162 | 8.3784e-05
2012-09-19 12:00AM | 214681 | 9057 | Urban | Change LV switch gear | 17 | 270 | 4590 | 0.0051276 | 1.8991e-05
2012-09-20 07:30AM | 215979 | MR2224 | Urban | Replace sub 4338 and pole 87 . Withers Rd Kellyville | 19 | 510 | 9690 | 0.010825 | 2.1225e-05
2012-09-20 08:00AM | 209092 | 27454 | Rural Short | HV Augmentation | 8 | 540 | 4320 | 0.004826 | 8.937e-06
2012-09-20 08:00AM | 214530 | T868 | Rural Short | To allow staff to Retrofit Subs 11937 and 10454 also Replace Tx at Sub 10454 Meadowvale Appin Rd Campbelltown | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2012-09-20 08:00AM | 214898 | L582 | Rural Short | Install new pole 854205 and augment section of Lv mains off pole sub 14726 | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2012-09-20 08:00AM | 215076 | R260 | Rural Short | ABS MAINTENANCES and HV DEFCTS | 172 | 420 | 72240 | 0.080701 | 0.00019214
2012-09-20 08:00AM | 215839 | X802 | Rural Short | REPLACE HV CROSSARM and RETROFIT SUB | 11 | 450 | 4950 | 0.0055297 | 1.2288e-05
2012-09-20 08:00AM | 215897 | AZ1227 | Urban | Condemned Pole | 52 | 480 | 24960 | 0.027883 | 5.809e-05
2012-09-20 08:30AM | 214614 | 35989 | Rural Short | To allow staff to install DOF's 87877 and 87878 New Poles 824546 and 824547 and Remove USL's X788 Janderra Rd Wilton | 14 | 450 | 6300 | 0.0070379 | 1.564e-05
2012-09-20 08:30AM | 215000 | GG1232 | Rural Short | M and R Holec sub 43352 | 7 | 240 | 1680 | 0.0018768 | 7.8198e-06
2012-09-20 08:30AM | 214661 | PCD2 | Urban | Replace rusty transformer and retro fit substation and replace pole caps | 52 | 360 | 18720 | 0.020912 | 5.809e-05
2012-09-20 08:30AM | 215455 | CRD2 | Urban | Change over poles and install LV ABC | 27 | 360 | 9720 | 0.010858 | 3.0162e-05
2012-09-20 09:00AM | 216079 | 8711 | Rural Short | Changeover Pole | 2 | 390 | 780 | 0.00087135 | 2.2342e-06
2012-09-20 09:00AM | 214404 | T894 | Urban | Replace pole 168 | 38 | 420 | 15960 | 0.017829 | 4.2451e-05
2012-09-20 09:30AM | 216054 | BDG2 | Rural Short | REPLACE STREET LIGHT COLUMNS | 59 | 90 | 5310 | 0.0059319 | 6.591e-05
2012-09-20 10:30AM | 216056 | BDG2 | Rural Short | REPLACE STREET LIGHT COLUMNS | 137 | 90 | 12330 | 0.013774 | 0.00015305
2012-09-21 08:00AM | 215490 | X492 | Rural Long | REPLACE HV CROSSARMSINSTALL VIBRATION DAMPERS and REPAIR BROKEN HV TIES | 275 | 480 | 132000 | 0.14746 | 0.00030721
2012-09-21 08:00AM | 210671 | 8711 | Rural Short | HV Augmentation | 50 | 600 | 30000 | 0.033514 | 5.5856e-05
2012-09-21 08:00AM | 211485 | HKA2 | Rural Short | AUGMENT 6 BAYS OF HV MAINS TO 3x180CCT FROM POLE 2GH036 TO POLE 826836. | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2012-09-21 08:00AM | 212611 | S738 | Rural Short | REPLACE POLE 286 + 287 + 288 + RETRO SUB 995 | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2012-09-21 08:00AM | 214220 | 41535 | Urban | install two reclosers remove lbs and replace usl with dofs | 38 | 540 | 20520 | 0.022923 | 4.2451e-05
2012-09-21 08:00AM | 215142 | AZ1227 | Urban | REPLACE COND POLE 367 | 22 | 390 | 8580 | 0.0095849 | 2.4577e-05
2012-09-21 08:00AM | 215382 | 9020 | Urban | maintenance | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2012-09-21 08:30AM | 214332 | APC2 | Rural Short | INSTALL LBS 95198 | 28 | 360 | 10080 | 0.011261 | 3.1279e-05
2012-09-21 08:30AM | 215032 | RWC2 | Rural Short | Replace Poles 201331 and 201332 | 11 | 420 | 4620 | 0.0051611 | 1.2288e-05
2012-09-21 08:30AM | 215403 | RBE2 | Rural Short | Uprate existing Sub 32125. Connect new LV UG mains | 27 | 420 | 11340 | 0.012668 | 3.0162e-05
2012-09-21 09:00AM | 208830 | CLD2 | Rural Short | Replace pole 3HP272 and Replace TX @ S/S 50928. | 61 | 330 | 20130 | 0.022488 | 6.8144e-05
2012-09-21 09:00AM | 215029 | A049 | Rural Short | Replace/install poles for future works.Install LBS 90507. | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2012-09-21 09:00AM | 214679 | PKA2 | Urban | Replace HV X arm and retro fit substation and replace MDI unit | 45 | 420 | 18900 | 0.021114 | 5.027e-05
2012-09-21 09:00AM | 216101 | 8680 | Urban | Replace Switch in Pillar | 59 | 180 | 10620 | 0.011864 | 6.591e-05
2012-09-21 09:00AM | 216102 | 25775 | Urban | Replace Switch in Pillar | 37 | 180 | 6660 | 0.00744 | 4.1333e-05
2012-09-21 10:00AM | 216086 | 48203 | Urban | Replacing LV Switch | 36 | 240 | 8640 | 0.0096519 | 4.0216e-05
2012-09-21 10:00AM | 216136 | 35530 | Urban | maintenance | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2012-09-21 10:00AM | 216137 | 35508 | Urban | maintenance | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2012-09-22 02:00PM | 216227 | 5500 | Urban | maintenance | 25 | 120 | 3000 | 0.0033514 | 2.7928e-05
2012-09-22 06:30AM | 213058 | 35773 | Urban | UPRATE LOW VOLTAGE SWITCH GEAR IN SUB 5924 | 11 | 690 | 7590 | 0.0084789 | 1.2288e-05
2012-09-22 07:00AM | 214743 | 35767 | Urban | Run new 240mm XLPE HV cable and terminate at SW 18175 SUB 1629 and replace existing HV UG/OH at pole 1498. | 5 | 540 | 2700 | 0.0030162 | 5.5856e-06
2012-09-22 07:30AM | 214245 | 1112 | Urban | Augment HV mains below 33kV mains | 678 | 630 | 427140 | 0.47717 | 0.00075741
2012-09-22 08:00AM | 215406 | 19856 | Urban | Augment HV mains and strip out s/l conductor | 160 | 480 | 76800 | 0.085795 | 0.00017874
2012-09-22 11:00AM | 216082 | 9027 | Urban | MAINTENANCE | 10 | 270 | 2700 | 0.0030162 | 1.1171e-05
2012-09-22 11:30AM | 214268 | WQ1260 | Urban | REPLACE DEFECTIVE LAs POLE 152 (GIPPS RD SMITHFIELD) | 5 | 330 | 1650 | 0.0018432 | 5.5856e-06
2012-09-23 06:00AM | 213540 | AZ1205 | Urban | Replace cond pole 589 and remove sub 1302 as per project. Replace ABS 9601 with replacement ABS 96850. Replace cond pole 591 | 34 | 90 | 3060 | 0.0034184 | 3.7982e-05
2012-09-23 08:00AM | 216091 | L582 | Rural Short | LIMITED SWITCHING Fit vibration dampers to 11kV O/H mains | 10 | 450 | 4500 | 0.005027 | 1.1171e-05
2012-09-23 08:00AM | 208815 | B214 | Urban | HV Augmentation | 26 | 540 | 14040 | 0.015684 | 2.9045e-05
2012-09-23 08:00AM | 209327 | WH1261 | Urban | Install new DOF and augment 1 bay of HV mains | 27 | 420 | 11340 | 0.012668 | 3.0162e-05
2012-09-23 08:00AM | 212936 | S602 | Urban | Augment LV mains to 150 ABC.Replace OH SL mains.Change over LV UGOH. | 34 | 510 | 17340 | 0.019371 | 3.7982e-05
2012-09-23 08:00AM | 213441 | UNC2 | Urban | REPLACE UGOH's AUGMENT HV MAINS REMOVE S/S 20211 INSTALL S/S 32220 and LBS's 96452 95805.REMOVE HV MAINS and REPLACE POLES | 174 | 450 | 78300 | 0.08747 | 0.00019438
2012-09-23 08:00AM | 213729 | CRD2 | Urban | Replace poles and augment | 72 | 420 | 30240 | 0.033782 | 8.0433e-05
2012-09-23 08:30AM | 212981 | T851 | Rural Short | 1) INSTALL LIVE LINE LINKS ADJ POLE 4.2) REPLACE ABS R792 WITH NEW SCADA LBS 92200.3) REMOVE LIVE LINE LINKS ADJ POLE 4 | 10 | 360 | 3600 | 0.0040216 | 1.1171e-05
2012-09-23 08:30AM | 215527 | 35990 | Rural Short | Repair HV defects @ Sub 10567 | 14 | 360 | 5040 | 0.0056303 | 1.564e-05
2012-09-23 08:30AM | 216152 | L582 | Rural Short | LIMITED SWITCHING INSTALL VIBRATION DAMPENERS | 21 | 180 | 3780 | 0.0042227 | 2.346e-05
2012-09-23 09:00AM | 202321 | BDA2 | Urban | Replace pole 1XR152. Replace TX @ S/S 50145. | 166 | 360 | 59760 | 0.066759 | 0.00018544
2012-09-23 10:00PM | 213540 | AZ1205 | Urban | Replace cond pole 589 and remove sub 1302 as per project. Replace ABS 9601 with replacement ABS 96850. Replace cond pole 591 | 34 | 90 | 3060 | 0.0034184 | 3.7982e-05
2012-09-23 11:30AM | 216151 | L582 | Rural Short | LIMITED SWITCHING INSTALL VIBRATION DAMPENERS | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2012-09-24 08:00AM | 214241 | 4359 | Rural Short | Replace DOF 1883. Replace polecap at poles 21 and 25. Desap poles 40 43 and 44 | 9 | 390 | 3510 | 0.0039211 | 1.0054e-05
2012-09-24 08:00AM | 215315 | NG1210 | Rural Short | REMOVE POLE 170 INSTALL NEW POLE 858193 1M ADJ . EXTEND EXISTING MAINS AS NEEDED | 16 | 510 | 12240 | 0.013674 | 1.7874e-05
2012-09-24 08:00AM | 215315 | NG1210 | Rural Short | REMOVE POLE 170 INSTALL NEW POLE 858193 1M ADJ . EXTEND EXISTING MAINS AS NEEDED | 32 | 540 | 12960 | 0.014478 | 3.5748e-05
2012-09-24 08:00AM | 215318 | ULL2 | Rural Short | Reconfigure the DOF's on pole 826493 | 117 | 420 | 49140 | 0.054895 | 0.0001307
2012-09-24 08:00AM | 209319 | 5875 | Urban | New DOF installation | 27 | 540 | 14580 | 0.016288 | 3.0162e-05
2012-09-24 08:00AM | 212767 | KMC2 | Urban | AUGMENT ONE BAY OF HV MAINS TO 3x7/4.50AAC FROM POLE 4JD021 TO POLE 847733.REPLACE POLE 4JD019 TO POLE 847733. | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2012-09-24 08:00AM | 216318 | 35696 | Urban | MAINTENANCE | 26 | 480 | 12480 | 0.013942 | 2.9045e-05
2012-09-24 08:30AM | 214264 | 8802 | Rural Short | Replace HV insulators at pole 7. Replace DOF carriers at sub 23530 | 65 | 210 | 13650 | 0.015249 | 7.2613e-05
2012-09-24 08:30AM | 214822 | BWH2 | Rural Short | Replace Hv Pole's andHV Augmentation | 255 | 480 | 104160 | 0.11636 | 0.00028487
2012-09-24 08:30AM | 215639 | P608 | Rural Short | Retro Sub 11961Retro and replace tx at Sub 11037 | 3 | 390 | 1170 | 0.001307 | 3.3514e-06
2012-09-24 08:30AM | 215993 | BK1251 | Rural Short | INSTALL VIBRATION DAMPERS | 13 | 390 | 5070 | 0.0056638 | 1.4523e-05
2012-09-24 09:00AM | 216081 | 5494 | Urban | LV Pole changeover | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2012-09-25 08:00AM | 212583 | 8798 | Rural Short | Augment 4 bays of hv mains to hv abc | 162 | 510 | 82620 | 0.092296 | 0.00018097
2012-09-25 08:00AM | 213188 | S735 | Rural Short | Install AR 94495 with USL's 94494 and 94496.Remove ABS 14366. | 18 | 480 | 6720 | 0.007507 | 2.0108e-05
2012-09-25 08:00AM | 215082 | HKA2 | Rural Short | Replace one pole and install 4 new poles remove 3 poles. Augment 4 bays of HV mains. | 28 | 480 | 13440 | 0.015014 | 3.1279e-05
2012-09-25 08:00AM | 215518 | HKE2 | Rural Short | Install / Replace poles and Augment mains | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2012-09-25 08:00AM | 208791 | 17038 | Urban | HV Augmentation | 377 | 600 | 226200 | 0.25269 | 0.00042115
2012-09-25 08:00AM | 211842 | 55874 | Urban | HVSWGR MAINT | 46 | 360 | 16560 | 0.0185 | 5.1388e-05
2012-09-25 08:00AM | 214724 | PCA2 | Urban | 2 NEW PADMOUNT SUBSTATIONS | 1 | 450 | 450 | 0.0005027 | 1.1171e-06
2012-09-25 08:00AM | 215836 | 19871 | Urban | Install a new LV pillar | 2 | 390 | 780 | 0.00087135 | 2.2342e-06
2012-09-25 08:00AM | 216139 | 41535 | Urban | maintenance | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2012-09-25 08:00AM | 216285 | 25781 | Urban | TO bond in new cable and Pillar to existing network | 72 | 150 | 10800 | 0.012065 | 8.0433e-05
2012-09-25 08:30AM | 214273 | KME2 | Rural Short | REPLACE POLE 4KD648 | 44 | 360 | 15840 | 0.017695 | 4.9153e-05
2012-09-25 08:30AM | 214687 | 35418 | Rural Short | Replace HV arm at pole 32 | 9 | 300 | 2700 | 0.0030162 | 1.0054e-05
2012-09-25 08:30AM | 214918 | BK1251 | Rural Short | RETROFIT SUB 12528 | 60 | 390 | 23400 | 0.026141 | 6.7027e-05
2012-09-25 08:30AM | 215617 | L947 | Rural Short | Replace pole 467 | 48 | 390 | 9360 | 0.010456 | 5.3622e-05
2012-09-25 08:30AM | 215693 | 8802 | Rural Short | To replace HV cross arms | 27 | 450 | 12150 | 0.013573 | 3.0162e-05
2012-09-25 08:30AM | 216144 | L591 | Rural Short | LIMITED SWITCHING REPLACE CONDEMNED POLE 49 | 11 | 300 | 3300 | 0.0036865 | 1.2288e-05
2012-09-25 08:30AM | 214499 | BLD2 | Urban | Replace Condemned Pole 2C0992 | 117 | 330 | 38610 | 0.043132 | 0.0001307
2012-09-25 08:30AM | 216321 | C896 | Urban | LV Interruption - Pasturegate Cambridge Gardens | 32 | 330 | 10560 | 0.011797 | 3.5748e-05
2012-09-25 09:00AM | 214457 | BYC2 | Rural Short | Replace poles ( 3 5 and 7 )Bong Bong Rd BERRY. | 9 | 360 | 3240 | 0.0036195 | 1.0054e-05
2012-09-25 09:00AM | 214988 | BYC2 | Rural Short | STAND POLES | 64 | 360 | 23040 | 0.025738 | 7.1496e-05
2012-09-25 09:00AM | 216272 | 1112 | Urban | Service Lead in pole (additional) | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2012-09-25 09:00AM | 216273 | 1112 | Urban | LV pole change | 7 | 360 | 2520 | 0.0028151 | 7.8198e-06
2012-09-25 09:30AM | 215607 | S743 | Rural Short | To fit Vibration Dampeners to gully crossing between poles 10 and 287827 | 2 | 390 | 780 | 0.00087135 | 2.2342e-06
2012-09-26 07:30AM | 215313 | S790 | Rural Short | Replace existing Pole-27 and install new midpole 33kV ABS Fdr 451 | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2012-09-26 08:00AM | 208506 | X877 | Rural Short | RETROFIT SUB 8447 GREENDALE ROAD BRINGELLY | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2012-09-26 08:00AM | 214425 | CLD2 | Rural Short | Replacement of surge diverters adjacent to CLD1 | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2012-09-26 08:00AM | 215653 | H745 | Rural Short | Replace pole remove USL and install LBS. Rectify defects. | 55 | 420 | 23100 | 0.025805 | 6.1442e-05
2012-09-26 08:00AM | 211278 | HKB2 | Urban | POLE REPLACEMENT X 2 INSTALL LBS 92344 VOST DR INSTALL 240SQ AL XLPE 3 CORE HV CABLE POLE SUB 51564 TO PAD SUB 22433. | 244 | 540 | 131760 | 0.14719 | 0.00027258
2012-09-26 08:00AM | 211388 | 5867 | Urban | RETROFIT SUB 4872 + REPLACE LV POLE 107 | 56 | 420 | 11760 | 0.013137 | 6.2559e-05
2012-09-26 08:00AM | 213814 | R251 | Urban | Augment 7 bays of LV mains and remove SL conductor near O/H HV mains. | 44 | 480 | 21120 | 0.023594 | 4.9153e-05
2012-09-26 08:00AM | 214594 | UNJ2 | Urban | Replace poles and Transformer | 140 | 450 | 63000 | 0.070379 | 0.0001564
2012-09-26 08:15AM | 215571 | BWB2 | Urban | Relocate 2 x 11kV UGOHs and remove 2 poles | 25 | 465 | 11625 | 0.012987 | 2.7928e-05
2012-09-26 08:30AM | 215308 | W124 | Rural Short | Replace HV Crossarms. Maintain sub + replace poles. | 41 | 420 | 17220 | 0.019237 | 4.5802e-05
2012-09-26 08:30AM | 215555 | APC2 | Rural Short | RETRO SUB 43347. INSTALL DAMPERS POLES 4GR041 and 4GR043.MandR ABS 75052 and 75875. REPLACE POLE CAP POLE 227577. | 11 | 390 | 4290 | 0.0047924 | 1.2288e-05
2012-09-26 08:30AM | 215784 | X473 | Rural Short | REPLACE CROSSARM AT POLE 3 AND RETROFIT SUB 16981 | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2012-09-26 08:30AM | 216277 | 35980 | Rural Short | Repair HV Defects at pole 156158159 and 160 | 11 | 270 | 2970 | 0.0033178 | 1.2288e-05
2012-09-26 08:30AM | 216074 | B201 | Urban | Changeover Pole | 23 | 420 | 9660 | 0.010791 | 2.5694e-05
2012-09-26 09:00AM | 216247 | BYC2 | Rural Short | High Priority Bushfire defect.Replace pole 2VH032. | 41 | 300 | 12300 | 0.013741 | 4.5802e-05
2012-09-26 09:00AM | 216356 | 8689 | Urban | Replace Column | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2012-09-26 09:30AM | 213772 | YYA2 | Rural Short | Replace USLs with DOFs and Install Span of HV conductorBloodwood Rd YATTE YATTAH. | 6 | 270 | 1620 | 0.0018097 | 6.7027e-06
2012-09-27 03:00PM | 216312 | APA2 | Urban | REPAIR HV TERMINATION @ PL 209633 BUSH FIRE DEFECT | 376 | 15 | 2850 | 0.0031838 | 0.00042004
2012-09-27 08:00AM | 211351 | HKA2 | Rural Short | REPLACE 2 POLES AND INSTALL 2 NEW ONES. AUGMENT 4 BAYS OF HV MAINS TO 3x19/3.25AAC FROM POLE 826909 TO POLE 826906.REMOVE ABS 30271 AND POLE 228210.INSTALL LBS 88972 | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2012-09-27 08:00AM | 214318 | 35989 | Rural Short | Augment 11kV Conductor 35989 from Pole 10 Ashwood Rd. to new Pole 12 in the Sydney Catchment Authority corridor Wilton as part of new 66kV Feeder 869/2 works | 56 | 480 | 26880 | 0.030028 | 6.2559e-05
2012-09-27 08:00AM | 214892 | X879 | Rural Short | To allow staff to replace condemned pole # 138 McCann Rd Rossmore SUB 10761 | 20 | 480 | 9600 | 0.010724 | 2.2342e-05
2012-09-27 08:00AM | 215493 | T829 | Rural Short | Run new O/H Earth Wire from Str 50 to Str 57 66kV Fdr 831 | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2012-09-27 08:00AM | 215493 | T829 | Rural Short | Run new O/H Earth Wire from Str 50 to Str 57 66kV Fdr 831 | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2012-09-27 08:00AM | 215800 | W111 | Rural Short | To allow staff to Retrofit Sub 11408 Macquariedale Rd Appin | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2012-09-27 08:00AM | 211396 | B743 | Urban | REPLACE CONDEMNED POLE and REPLACE USL 9537 WITH USL 96280RETRO SUB 5245 | 8 | 540 | 4320 | 0.004826 | 8.937e-06
2012-09-27 08:00AM | 212039 | 5877 | Urban | HVSWGR MAINT | 122 | 360 | 43920 | 0.049064 | 0.00013629
2012-09-27 08:00AM | 214052 | WRF2 | Urban | Stand new Poles | 33 | 480 | 15840 | 0.017695 | 3.6865e-05
2012-09-27 08:00AM | 216352 | MR2224 | Urban | Install:LV UG cable LV pillars Streetlights | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2012-09-27 08:30AM | 214668 | WBC2 | Rural Short | Replace Condemned Pole 3PR102 | 51 | 390 | 19890 | 0.02222 | 5.6973e-05
2012-09-27 08:30AM | 216251 | RWC2 | Rural Short | Replace Poles 201331 and 201332 | 11 | 420 | 4620 | 0.0051611 | 1.2288e-05
2012-09-27 08:30AM | 213143 | J512 | Urban | To Replace Existing Kiosk Sub (11432) With New Padmount Sub 32210. | 64 | 480 | 15360 | 0.017159 | 7.1496e-05
2012-09-27 08:30AM | 213979 | APE2 | Urban | REMOVE ABS 72838 and INSTALL LBS 95506 INSTALL ABS 95509 REPLACE CONDEMNED POLE 208556 REMOVE LIVE LINE LNKS. | 280 | 420 | 117600 | 0.13137 | 0.00031279
2012-09-27 08:30AM | 215701 | PCB2 | Urban | Replace Rusty Transformer | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2012-09-27 08:30AM | 215855 | 19856 | Urban | Replace service pole. | 2 | 150 | 300 | 0.00033514 | 2.2342e-06
2012-09-27 08:30AM | 216312 | APA2 | Urban | REPAIR HV TERMINATION @ PL 209633 BUSH FIRE DEFECT | 4 | 405 | 76950 | 0.085962 | 4.4685e-06
2012-09-27 09:00AM | 215627 | H745 | Rural Short | Repair HV Stay on pole J22Replace DOFs at sub 11775 | 3 | 180 | 540 | 0.00060324 | 3.3514e-06
2012-09-27 09:00AM | 216284 | L591 | Rural Short | *LIMITED DISTRICT SWITCHING*INSTALL VIBRATION DAMPERS | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2012-09-27 09:00AM | 216289 | L591 | Rural Short | *LIMITED DISTRICT SWITCHING*INSTALL VIBRATION DAMPERS | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2012-09-27 09:00AM | 216292 | L591 | Rural Short | *LIMITED DISTICT SWITCHING*INSTALL VIBRATION DAMPERS | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2012-09-27 09:00AM | 214308 | SXA2 | Urban | Install New LBS 94267 ( replaces ABS 30146 )River Rd SUSSEX INLET. | 87 | 330 | 28710 | 0.032073 | 9.7189e-05
2012-09-27 09:00AM | 216346 | MR2299 | Urban | Quality of Supply | 63 | 360 | 22680 | 0.025336 | 7.0379e-05
2012-09-28 08:00AM | 215562 | R260 | Rural Short | Stand new HV poles | 16 | 420 | 6720 | 0.007507 | 1.7874e-05
2012-09-28 08:00AM | 210853 | 55874 | Urban | REPLACE POLE 893 | 58 | 480 | 13920 | 0.01555 | 6.4793e-05
2012-09-28 08:00AM | 213047 | J491 | Urban | To MandR H/V S/Gear @ Sub 11357 Conjola Cr Leumeah. | 50 | 300 | 15000 | 0.016757 | 5.5856e-05
2012-09-28 08:00AM | 213322 | A054 | Urban | Install ABS 91669 and LV links pole 988.Replace USL 2688 with LBS 91676. Replace pole 996 for future SPS. | 94 | 480 | 45120 | 0.050404 | 0.00010501
2012-09-28 08:30AM | 214128 | MVH2 | Rural Short | Replace Pole's and Augment 3 Bay's of Hv Oh Mains | 84 | 480 | 40320 | 0.045042 | 9.3838e-05
2012-09-28 08:30AM | 215939 | D814 | Rural Short | To replace HV Crossarms | 77 | 450 | 34650 | 0.038708 | 8.6018e-05
2012-09-28 08:30AM | 216274 | 35825 | Rural Short | Urgent repair of bush fire defects | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2012-09-28 08:30AM | 216406 | L588 | Rural Short | CONTRACTOR TREE TRIMMING | 2 | 390 | 780 | 0.00087135 | 2.2342e-06
2012-09-28 08:30AM | 214610 | KMF2 | Urban | REPLACE POLE 4KD769 | 36 | 300 | 10800 | 0.012065 | 4.0216e-05
2012-09-28 08:30AM | 215105 | CRB2 | Urban | Replace ABS 73240 and Transformer 40323 | 181 | 420 | 76020 | 0.084923 | 0.0002022
2012-09-28 08:30AM | 216424 | AZ1205 | Urban | Relocate Services | 10 | 450 | 4500 | 0.005027 | 1.1171e-05
2012-09-28 09:00AM | 214178 | CLD2 | Rural Short | To replace L/V pole 3HP103 Pole is L/V open point between s/s 50408 and 50409 | 18 | 300 | 5400 | 0.0060324 | 2.0108e-05
2012-09-28 09:00AM | 215771 | WBC2 | Rural Short | Install LV ABC and remove crossarms | 5 | 300 | 1500 | 0.0016757 | 5.5856e-06
2012-09-28 09:00AM | 216469 | P608 | Rural Short | Isolate high voltage conductors for contractors to undertake tree trimming as an urgent bush fire defect. | 23 | 360 | 8280 | 0.0092498 | 2.5694e-05
2012-09-28 09:00AM | 216646 | BWH2 | Rural Short | Replace LV cross arm on pole 3P0315 | 2 | 300 | 600 | 0.00067027 | 2.2342e-06
2012-09-28 09:00AM | 216077 | HR1210 | Urban | Changeover Corner Pole | 25 | 360 | 9000 | 0.010054 | 2.7928e-05
2012-09-28 09:00AM | 216344 | MR2299 | Urban | Quality of Supply | 22 | 360 | 7920 | 0.0088476 | 2.4577e-05
2012-09-28 09:30AM | 213768 | CLA2 | Rural Short | Replace pole 2YP066 - S/S 50384 | 12 | 270 | 3240 | 0.0036195 | 1.3405e-05
2012-09-28 09:30AM | 216327 | APE2 | Urban | REPLACE LV CABLE TO PILLAR 73671 | 29 | 300 | 8700 | 0.0097189 | 3.2396e-05
2012-09-28 11:00AM | 216657 | L540 | Urban | lv job | 32 | 300 | 9600 | 0.010724 | 3.5748e-05
2012-09-29 07:00AM | 214303 | 2819 | Urban | 11KV CUT OUT BETWEEN POLE 459 and ABS 66069 FOR RAIL CORP POLE REPLACEMENT. PLEASE ISSUE OPERATING AGREEMENT | 32 | 540 | 8640 | 0.0096519 | 3.5748e-05
2012-09-29 08:00AM | 216286 | 35825 | Rural Short | Urgent bush fire defect to cut trees within close proximity to HV. | 10 | 300 | 3000 | 0.0033514 | 1.1171e-05
2012-09-29 08:00AM | 216479 | 35702 | Urban | rectify bushfire defects - install spreaders | 128 | 300 | 38400 | 0.042897 | 0.00014299
2012-09-29 09:00AM | 216739 | FF1217 | Urban | 48Hr Pole | 20 | 300 | 6000 | 0.0067027 | 2.2342e-05
2012-09-30 08:00AM | 213849 | 27031 | Urban | Sub 25292 Dunn Rd Smeaton Grange.To Install WF73-MDI Unit | 1 | 210 | 210 | 0.0002346 | 1.1171e-06
2012-09-30 10:30AM | 213861 | 27029 | Urban | Sub 27244 Topham Rd Smeaton Grange.To Install WF73-MDI Unit | 1 | 210 | 210 | 0.0002346 | 1.1171e-06
2012-10-02 07:30AM | 215554 | BWA2 | Rural Short | Replace and relocate 2 HV/LV poles | 52 | 480 | 23040 | 0.025738 | 5.809e-05
2012-10-02 08:00AM | 213546 | 35983 | Rural Short | New PMS29652 remove sub 11595. | 58 | 540 | 31320 | 0.034988 | 6.4793e-05
2012-10-02 08:00AM | 210676 | B776 | Urban | HV Augmentation | 139 | 570 | 79230 | 0.088509 | 0.00015528
2012-10-02 08:00AM | 214631 | B776 | Urban | Replace pole 1350 with pole 842074 pole 942 with pole 842075 and pole 941 with pole 842324 | 144 | 570 | 82080 | 0.091693 | 0.00016087
2012-10-02 08:00AM | 215130 | 9029 | Urban | ISOLATE HV AT SUB # 5876 TO MAINTAIN CLEARANCES TO REPLACE LV X-ARM AT POLE # 134 - GILDA AVE PENRITH | 35 | 180 | 6300 | 0.0070379 | 3.9099e-05
2012-10-02 08:30AM | 215554 | BWA2 | Rural Short | Replace and relocate 2 HV/LV poles | 44 | 420 | 20160 | 0.022521 | 4.9153e-05
2012-10-02 08:30AM | 215854 | D813 | Rural Short | Replace rusty Tx @ sub 1967.Replace weathered HV arm @ sub 1966 | 63 | 330 | 20790 | 0.023225 | 7.0379e-05
2012-10-02 08:30AM | 215724 | PKD2 | Urban | Replace condemned pole 3TC191 | 23 | 360 | 8280 | 0.0092498 | 2.5694e-05
2012-10-02 09:00AM | 214713 | X802 | Rural Short | RETRO FIT SUB 15679 (NOT A SWER SUB) | 19 | 360 | 6840 | 0.0076411 | 2.1225e-05
2012-10-02 09:30AM | 216690 | BDA2 | Urban | REPLACE STREET LIGHT COLUMNS | 60 | 180 | 10800 | 0.012065 | 6.7027e-05
2012-10-03 06:00AM | 216813 | B202 | Urban | Project Job | 19 | 750 | 14250 | 0.015919 | 2.1225e-05
2012-10-03 08:00AM | 214723 | BWH2 | Rural Short | Replace Pole and Install a new LBS 91646 | 24 | 420 | 10080 | 0.011261 | 2.6811e-05
2012-10-03 08:00AM | 215741 | W163 | Rural Short | AUGMENT HV MAINS AND STAND POLE | 4 | 330 | 1320 | 0.0014746 | 4.4685e-06
2012-10-03 08:00AM | 215867 | MGE2 | Rural Short | ABS and USL upgrades | 366 | 540 | 197640 | 0.22079 | 0.00040887
2012-10-03 08:00AM | 216192 | WBD2 | Rural Short | Install new substation and 5 bays OH mains | 1 | 555 | 555 | 0.00062 | 1.1171e-06
2012-10-03 08:00AM | 214325 | 1962 | Urban | Install DOF'S | 115 | 450 | 51750 | 0.057811 | 0.00012847
2012-10-03 08:00AM | 215781 | 8620 | Urban | Augment 3 bays of HV mains and replace 1 pole | 161 | 600 | 96600 | 0.10791 | 0.00017986
2012-10-03 08:00AM | 216470 | 8620 | Urban | Isolation of LV mains for HV mains augmentation to 7/4.50 AAC between pole 1323 (853657) and pole 1344. | 68 | 540 | 36720 | 0.041021 | 7.5964e-05
2012-10-03 08:00AM | 216505 | R251 | Urban | Augment 7 bays of LV mains and remove SL conductor near O/H HV mains. | 63 | 560 | 35280 | 0.039412 | 7.0379e-05
2012-10-03 08:30AM | 212475 | HKE2 | Rural Short | INSTALL NEW POLE 830477 AND REPLACE POLE 2DP045 WITH POLE 830478.INSTALL LBS 90812 ON POLE 830477 ERECT 2 BAYS OF HV MAINS FROM POLE 314134 TO POLE 830478. | 387 | 270 | 104490 | 0.11673 | 0.00043233
2012-10-03 08:30AM | 215799 | H745 | Rural Short | Change low voltage pole 364 and hang LBS at pole 822269. | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2012-10-03 08:30AM | 214755 | CRB2 | Urban | REPLACE POLES 657 656 and 655 INSTALL LBS 96637 and AUGMENT 11KV MAINS from SUB 40357 to POLE 656 | 77 | 390 | 30030 | 0.033547 | 8.6018e-05
2012-10-03 08:30AM | 216638 | 1125 | Urban | Defect - LV Arms | 16 | 360 | 5760 | 0.0064346 | 1.7874e-05
2012-10-03 08:30AM | 216814 | 27142 | Urban | LV Job | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2012-10-03 09:00AM | 216433 | 1106 | Urban | LV Crossarm change | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2012-10-03 09:30AM | 214879 | J506 | Urban | To Re-Pump Hazymeyer Cable Box Termination @ SW-P288-P289-P290-P291-In SW/ST 15441 Currawong St Ingleburn.(As Per PIN-D204) | 51 | 360 | 18360 | 0.02051 | 5.6973e-05
2012-10-03 09:30AM | 215588 | GV1282 | Urban | REPLACE DEFECTIVE SAFELINK UNIT FAILED TEST POINTS @ SUB 26698 WORKS REQUEST 93055 Defect D010 | 31 | 440 | 13640 | 0.015238 | 3.4631e-05
2012-10-03 09:30AM | 216693 | BDA2 | Urban | REPLACE STREET LIGHT COLUMNS | 62 | 120 | 7440 | 0.0083114 | 6.9261e-05
2012-10-03 10:00AM | 216340 | HKE2 | Rural Short | Replace DOF 95184 | 7 | 60 | 420 | 0.00046919 | 7.8198e-06
2012-10-04 08:00AM | 211367 | HKA2 | Rural Short | INSTALL NEW POLE 826904 AND POLE 826905 AND REMOVE POLE 228713.AUGMENT 3 BAYS OF HV MAINS TO 3 x 180 CCT FROM POLE 826906 TO POLE 826839. | 3 | 315 | 945 | 0.0010557 | 3.3514e-06
2012-10-04 08:00AM | 215808 | W163 | Rural Short | REPLACE POLE and REDRESS SUB POLE | 9 | 370 | 3330 | 0.00372 | 1.0054e-05
2012-10-04 08:00AM | 213556 | 25773 | Urban | REPLACE HV SW GR AREVA FOR AREVA SUB 18906 | 1 | 500 | 500 | 0.00055856 | 1.1171e-06
2012-10-04 08:00AM | 214635 | 41535 | Urban | Augment HV conductor + Replace pole | 93 | 495 | 46035 | 0.051427 | 0.00010389
2012-10-04 08:00AM | 214829 | AZ1205 | Urban | REPLACE COND POLE 577 REPLACE ABS 9581 WITH NEW ABS 97210 | 30 | 480 | 8160 | 0.0091157 | 3.3514e-05
2012-10-04 08:00AM | 215811 | J496 | Urban | To allow staff to Retrofit Sub 10431 High st Campbelltown | 62 | 180 | 11160 | 0.012467 | 6.9261e-05
2012-10-04 08:00AM | 215881 | SWF2 | Urban | REPLACE CAST IRON POTHEAD and POLE | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2012-10-04 08:30AM | 212795 | S738 | Rural Short | To isolate HV and LV to allow tree lopper to cut trees | 6 | 420 | 2520 | 0.0028151 | 6.7027e-06
2012-10-04 08:30AM | 214978 | 46475 | Rural Short | Replace pole 292 and Retro sub 7613 | 1 | 270 | 270 | 0.00030162 | 1.1171e-06
2012-10-04 08:30AM | 212994 | 8615 | Urban | To Isolate HV to allow contractor to remove treeTo MandR Holec Swg Sub 23140 | 249 | 420 | 34860 | 0.038943 | 0.00027816
2012-10-04 09:00AM | 215833 | BDC2 | Rural Short | Install New Sectionaliser 95528Moss Vale Rd BEAUMONT. | 7 | 150 | 1050 | 0.001173 | 7.8198e-06
2012-10-04 09:00AM | 216622 | 2822 | Urban | Street Light Improvement | 21 | 360 | 7560 | 0.0084454 | 2.346e-05
2012-10-05 08:00AM | 216258 | R210 | Rural Short | Replace Pole 264 | 38 | 520 | 19760 | 0.022074 | 4.2451e-05
2012-10-05 08:00AM | 216689 | T831 | Rural Short | REPLACE LV CROSSARMSRETROFIT SUBREPLACE TRANSFORMERCONNECT HV EARTH and INSTALL VIBRATION DAMPERS | 15 | 385 | 5775 | 0.0064514 | 1.6757e-05
2012-10-05 08:00AM | 216697 | T828 | Rural Short | REPLACE LV CROSSARMS and RETROFIT SUB | 10 | 420 | 4200 | 0.0046919 | 1.1171e-05
2012-10-05 08:00AM | 215361 | AZ1272 | Urban | REPLACE COND POLE 177 | 18 | 450 | 8100 | 0.0090487 | 2.0108e-05
2012-10-05 08:00AM | 216676 | GV1223 | Urban | LV Changeover | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2012-10-05 08:30AM | 211557 | A049 | Rural Short | Augment HV OH mains 7/4.5 AAC.Install OH stay. | 2 | 450 | 900 | 0.0010054 | 2.2342e-06
2012-10-05 08:30AM | 215823 | DFA2 | Rural Short | REPLACE POLE 3PA013 | 5 | 275 | 1375 | 0.001536 | 5.5856e-06
2012-10-05 08:30AM | 216629 | R260 | Rural Short | REPLACE HV CROSSARM and POLE CAP | 1 | 390 | 390 | 0.00043568 | 1.1171e-06
2012-10-05 08:30AM | 216700 | 1957 | Urban | Pole Replacement | 5 | 390 | 1950 | 0.0021784 | 5.5856e-06
2012-10-05 09:00AM | 215828 | BDC2 | Rural Short | Install New Sectionaliser 95276Leebold Hill Rd CAMBEWARRA | 9 | 180 | 1620 | 0.0018097 | 1.0054e-05
2012-10-05 09:00AM | 216618 | 2822 | Urban | Street Light Improvement | 16 | 360 | 5760 | 0.0064346 | 1.7874e-05
2012-10-05 10:30AM | 216849 | 9026 | Urban | LV JOB | 11 | 330 | 3630 | 0.0040551 | 1.2288e-05
2012-10-06 06:00PM | 214572 | WX1270 | Urban | INSTALL NEW HV SW/GR AND INSTALL NEW 11KV CABLE. | 6 | 600 | 2400 | 0.0026811 | 6.7027e-06
2012-10-06 08:00AM | 214922 | L942 | Rural Short | INSTALL NEW CONCRETE POLES and RUN 150 Sq HV ABC O/H MAINS FROM SUB 5425 | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2012-10-07 06:30AM | 213438 | S597 | Urban | MandR HVSWGR @ SUB 22172 | 160 | 185 | 14800 | 0.016533 | 0.00017874
2012-10-07 08:00AM | 213868 | L534 | Urban | To install new HV UG cable Sw 79817 Sub 16192 to UGOH pole 815437.To disco/abandon HV UG cable Sw 79817 Sub 16192 to UGOH pole 497.Remove HV OH mains pole 815437 to pole 489. | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2012-10-07 08:00AM | 215311 | BLB2 | Urban | Replace Condemned Pole 3PC0686 | 4 | 270 | 1080 | 0.0012065 | 4.4685e-06
2012-10-07 09:00AM | 214787 | M166 | Urban | MandR HAZ S/GEAR AND REPLACE LV BRAIDS @ SUB 14430 (TX 2) | 4 | 435 | 1740 | 0.0019438 | 4.4685e-06
2012-10-07 09:00PM | 216704 | 10247 | Urban | Remove LV UGOH turn in to pillar | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2012-10-07 10:00AM | 215435 | RS1203 | Urban | JOB 1 - CUT IN NEW ABS 76856 LIVE LINEJOB 2 - INSTALL NEW LBS 76855 AND ERECT NEW HV O/H CONDUCTORS | 12 | 300 | 3600 | 0.0040216 | 1.3405e-05
2012-10-08 08:00AM | 209703 | 35983 | Rural Short | LIMITED SWITCHING- to allow staff to repl ace condemned pole #12 with new pole # 857613 at 65 Mullholland Rd Picton | 4 | 295 | 1180 | 0.0013182 | 4.4685e-06
2012-10-08 08:00AM | 215328 | 8802 | Rural Short | NEW 315 KVA 11 KV P/MOUNT SUB 28120 WITH SAFELINK CFC HV S/GEAR STAND NEW POLE REMOVE 2 BAYS HV MAINS | 36 | 540 | 19440 | 0.021717 | 4.0216e-05
2012-10-08 08:00AM | 216055 | X877 | Rural Short | UPRATE EXISTING POLE SUB 5182 TO 100KVA | 5 | 165 | 825 | 0.00092162 | 5.5856e-06
2012-10-08 08:00AM | 216225 | YYA2 | Rural Short | Augment one bay of HV Mains to 7/4.50AAC and install new poles. | 19 | 375 | 7125 | 0.0079595 | 2.1225e-05
2012-10-08 08:00AM | 213535 | 5509 | Urban | REPLACE LOW VOLTAGE SWITCHGEAR AND MandR HV SWITCHGEAR @ SUB 8211 LINDRIDGE PL ST CLAIR | 82 | 480 | 39360 | 0.04397 | 9.1604e-05
2012-10-08 08:00AM | 217024 | AZ1272 | Urban | Condemned Pole | 13 | 480 | 6240 | 0.0069708 | 1.4523e-05
2012-10-08 08:00AM | 217082 | 5509 | Urban | maintenance | 77 | 480 | 36960 | 0.041289 | 8.6018e-05
2012-10-08 08:30AM | 215887 | 8802 | Rural Short | Install 9ft HV arm Replace twin LV arms linksrewire and earth @ sub 4627 | 29 | 225 | 6525 | 0.0072892 | 3.2396e-05
2012-10-08 09:00AM | 216342 | MVF2 | Rural Short | Replace Poles Install New poleand Augment a section of 11KV O/H Mains | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2012-10-08 09:00AM | 216371 | BK1251 | Rural Short | INSTALL VIBRATION DAMPERS | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2012-10-09 04:00PM | 216035 | UNB2 | Urban | REPLACE HV SWITCHGEAR | 4 | 60 | 1740 | 0.0019438 | 4.4685e-06
2012-10-09 08:00AM | 211333 | HKA2 | Rural Short | AUGMENT 6 BAYS OF HV MAINS TO 7/4.50AAC FROM POLE 824680 TO POLE 824685.REPLACE POLE 2DK067 AND USL30350 WITH NEW POLE 824685 AND INSTALL NEW USL 87971. | 32 | 415 | 13280 | 0.014835 | 3.5748e-05
2012-10-09 08:00AM | 212607 | 8798 | Rural Short | augment 4 bays of hv mains to abc | 104 | 500 | 52000 | 0.05809 | 0.00011618
2012-10-09 08:00AM | 215013 | A051 | Rural Short | Replace ABS 3877 + pole with LBS 97368 + pole | 30 | 375 | 11250 | 0.012568 | 3.3514e-05
2012-10-09 08:00AM | 216248 | W163 | Rural Short | REPLACE CONDEMNED POLES and INSTALL SECTIONALISER | 51 | 400 | 20400 | 0.022789 | 5.6973e-05
2012-10-09 08:00AM | 214187 | J512 | Urban | To Remove Existing Kiosk Sub 13077 and DOF's P510 and H/V Cable Install New PM Sub 29237 and Associated H/V Cable and Terminate. | 92 | 560 | 25760 | 0.028777 | 0.00010278
2012-10-09 08:00AM | 216035 | UNB2 | Urban | REPLACE HV SWITCHGEAR | 54 | 540 | 15660 | 0.017494 | 6.0324e-05
2012-10-09 08:00AM | 216319 | CT1225 | Urban | Retrofit Sub 11505 and 11506 - Springfield Rd Catherine Fields | 2 | 340 | 8160 | 0.0091157 | 2.2342e-06
2012-10-09 08:00AM | 216850 | C899 | Urban | LV job | 45 | 240 | 10800 | 0.012065 | 5.027e-05
2012-10-09 08:30AM | 212992 | A049 | Rural Short | Augment HV OH mains 7/4.5 AAC. | 1 | 390 | 390 | 0.00043568 | 1.1171e-06
2012-10-09 08:30AM | 215363 | W124 | Rural Short | Transformer change and replace HV crossarm | 50 | 360 | 18000 | 0.020108 | 5.5856e-05
2012-10-09 08:30AM | 215713 | SN1230 | Rural Short | NEW SINGLE PHASE 25KVA POLE SUB 32189 | 42 | 270 | 11340 | 0.012668 | 4.6919e-05
2012-10-09 08:30AM | 216072 | BWE2 | Rural Short | Replace poles x 4 | 2 | 440 | 880 | 0.00098307 | 2.2342e-06
2012-10-09 08:30AM | 216373 | BWA2 | Rural Short | Relocate 2 x 11kV/LV poles | 52 | 560 | 29120 | 0.032531 | 5.809e-05
2012-10-09 08:30AM | 214212 | KMF2 | Urban | REPLACE POLES 4KG196 and 4KG197. STRAIGHTEN POLE 4KG096. RETRO SUBS 41324 and 41933.REPLACE LV ARMS POLES 4KG2044KG2064KG210 4KG198 and 4KG200. | 91 | 320 | 29120 | 0.032531 | 0.00010166
2012-10-09 08:30AM | 215570 | CRB2 | Urban | Replace ABS Pole 70365 | 222 | 355 | 55025 | 0.06147 | 0.000248
2012-10-09 08:30AM | 215674 | HR1217 | Urban | REPLACE CONDEMNED POLE 639 | 14 | 330 | 4620 | 0.0051611 | 1.564e-05
2012-10-09 08:30AM | 215899 | 10287 | Urban | Retro LV arms rewire links fuses and MDI @ sub 5481 | 76 | 375 | 15375 | 0.017176 | 8.4901e-05
2012-10-09 08:30AM | 217128 | MYG2 | Urban | LV Job | 23 | 390 | 8970 | 0.010021 | 2.5694e-05
2012-10-09 09:00AM | 216800 | MVF2 | Rural Short | Replace Condemed Poles 3XK568and 3K1912 | 29 | 360 | 10440 | 0.011663 | 3.2396e-05
2012-10-09 09:00AM | 216617 | 7994 | Urban | Street Light Improvement | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2012-10-09 09:00AM | 216938 | S599 | Urban | Tighten HV Hardware | 193 | 375 | 72375 | 0.080852 | 0.0002156
2012-10-10 08:00AM | 212335 | S743 | Rural Short | REPLACE POLE 41 | 5 | 450 | 2250 | 0.0025135 | 5.5856e-06
2012-10-10 08:00AM | 213496 | HKA2 | Rural Short | AUGMENT 2 BAYS OF HV MAINS AND REPLACE ONE POLE | 73 | 375 | 27375 | 0.030581 | 8.155e-05
2012-10-10 08:00AM | 215356 | R260 | Rural Short | REPLACE POLE and USL'S WITH NEW POLE and DOF'S | 93 | 375 | 34875 | 0.03896 | 0.00010389
2012-10-10 08:00AM | 215955 | KC1284 | Rural Short | Replace p35 with p871858. Remove ABS 3430. Install LBS 96558. Remove ABS 3162 @ p31. Install LBS 96556 @ p860806. Replace HV crossarm @ p31. | 26 | 420 | 10920 | 0.012199 | 2.9045e-05
2012-10-10 08:00AM | 216084 | W163 | Rural Short | AUGMENT HV MAINS | 13 | 450 | 5850 | 0.0065352 | 1.4523e-05
2012-10-10 08:00AM | 216197 | R260 | Rural Short | REMOVE USL'S and INSTALL NEW SECTIOALISER | 87 | 370 | 32190 | 0.03596 | 9.7189e-05
2012-10-10 08:00AM | 211781 | 1129 | Urban | AUGMENT SECTION OF O/H 11 KV TO 7/4.50 AAC RECTIFY DEFECTS WITHIN ISOLATION | 11 | 510 | 5610 | 0.006267 | 1.2288e-05
2012-10-10 08:00AM | 213553 | R256 | Urban | Augment 6 bays of LV mains and SL near O/H HV mains. | 48 | 120 | 5760 | 0.0064346 | 5.3622e-05
2012-10-10 08:00AM | 214633 | SWC2 | Urban | Replace USL 88160 with LBS-R 96869 on pole 825182.Augment 10 bays of HV mains to 7/4.50 AAC between poles 3DO332 and pole 825186 | 317 | 465 | 147405 | 0.16467 | 0.00035413
2012-10-10 08:00AM | 215849 | 35315 | Urban | To augment LV mains OH mains 150 ABC and remove old poles.(district switcher) | 118 | 365 | 21535 | 0.024057 | 0.00013182
2012-10-10 08:00AM | 217084 | 35519 | Urban | maintenance | 29 | 480 | 13920 | 0.01555 | 3.2396e-05
2012-10-10 08:00AM | 217131 | 1125 | Urban | Defects | 12 | 360 | 4320 | 0.004826 | 1.3405e-05
2012-10-10 08:30AM | 215938 | D813 | Rural Short | Replace twin LV arms fuse mdi bare earths and 1 phase service @ sub 1963 | 1 | 285 | 285 | 0.00031838 | 1.1171e-06
2012-10-10 08:30AM | 215987 | H745 | Rural Short | Chang pole 311756 with new pole 873288 and install ABS 86798. | 29 | 270 | 7830 | 0.008747 | 3.2396e-05
2012-10-10 08:30AM | 216702 | RBD2 | Rural Short | Replace Condemned Poles 3XY390 and 3XY375 | 19 | 390 | 7410 | 0.0082779 | 2.1225e-05
2012-10-10 08:30AM | 216305 | HBB2 | Urban | 11kV O/H augment | 16 | 240 | 3840 | 0.0042897 | 1.7874e-05
2012-10-10 09:00AM | 216793 | 3353 | Urban | LV Arm change | 6 | 240 | 1440 | 0.0016087 | 6.7027e-06
2012-10-11 08:00AM | 216783 | X492 | Rural Long | REPLACE CONDEMNED POLESINSTALL VIBRATION DAMPERS(NUMEROUS SPANS) *LIMITED DISTRICT SWITCHING* | 50 | 450 | 22500 | 0.025135 | 5.5856e-05
2012-10-11 08:00AM | 215074 | MGD2 | Rural Short | Repair Defects on a section of OH Mains plus repair phasing on sub 30231 | 58 | 450 | 26100 | 0.029157 | 6.4793e-05
2012-10-11 08:00AM | 216543 | MG1267 | Rural Short | HV Augmentation | 127 | 510 | 64770 | 0.072356 | 0.00014187
2012-10-11 08:00AM | 212619 | X863 | Urban | MandR HVSWGR @ SUB 7754 | 75 | 210 | 15750 | 0.017595 | 8.3784e-05
2012-10-11 08:00AM | 214637 | B776 | Urban | Augment Mains | 144 | 432 | 62208 | 0.069494 | 0.00016087
2012-10-11 08:00AM | 214778 | R251 | Urban | Install new package sub 14154 and terminate new HV cable + Install new HV UG/OH @ pole J461 Olivet st Glenbrook. | 22 | 480 | 10560 | 0.011797 | 2.4577e-05
2012-10-11 08:00AM | 216324 | CT1225 | Urban | Retrofit Sub 11642 - Springfield Rd Catherine Fields | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2012-10-11 08:00AM | 216957 | 2825 | Urban | IV Pole Change Over | 35 | 420 | 14700 | 0.016422 | 3.9099e-05
2012-10-11 08:00AM | 217028 | AZ1272 | Urban | LV Job | 9 | 480 | 4320 | 0.004826 | 1.0054e-05
2012-10-11 08:00AM | 217146 | 25746 | Urban | Replace Column | 28 | 480 | 13440 | 0.015014 | 3.1279e-05
2012-10-11 08:30AM | 215442 | 4360 | Rural Short | Replace USL 8088 + pole | 1 | 390 | 390 | 0.00043568 | 1.1171e-06
2012-10-11 08:30AM | 215928 | DFA2 | Rural Short | Replace poles and transformers retrofit subs | 36 | 420 | 15120 | 0.016891 | 4.0216e-05
2012-10-11 08:30AM | 215956 | L947 | Rural Short | Replace HV and LV arms @ sub 6851 | 40 | 360 | 14400 | 0.016087 | 4.4685e-05
2012-10-11 08:30AM | 216457 | 35990 | Rural Short | Change pole 216436 and retrofit pole substation10189 maintain ABS 25885 and change insulators at pole 439. | 30 | 450 | 13500 | 0.015081 | 3.3514e-05
2012-10-11 08:30AM | 214719 | APB2 | Urban | M and R Holec Sub 42463 and Retro Sub 41105 | 90 | 240 | 21600 | 0.02413 | 0.00010054
2012-10-11 08:30AM | 216031 | 7962 | Urban | REPLACE CONDEMNED POLE 1379 | 15 | 360 | 5400 | 0.0060324 | 1.6757e-05
2012-10-11 09:00AM | 215429 | DP1210 | Rural Short | REPLACING ABS 73011 WITH LBS 96735 | 208 | 375 | 78000 | 0.087135 | 0.00023236
2012-10-11 09:30AM | 215282 | ULE2 | Rural Short | Retrofit S/S 72519 and Repair DefectsWollombi Way MERRY BEACH. | 52 | 300 | 15600 | 0.017427 | 5.809e-05
2012-10-11 10:30AM | 216905 | W127 | Rural Short | TREE TRIMMING BY CONTRACT TREE CLIMBERS | 8 | 235 | 11045 | 0.012339 | 8.937e-06
2012-10-11 11:00PM | 216045 | 48168 | Urban | REPLACE HV SWGR AT S/S 12642 | 185 | 59 | 10915 | 0.012193 | 0.00020667
2012-10-12 01:00PM | 217057 | UNB2 | Urban | Stand new street light | 19 | 150 | 2850 | 0.0031838 | 2.1225e-05
2012-10-12 08:00AM | 214545 | 8634 | Rural Short | RETENSION RIVER X-INGS AND INSTALL SUPPORT STAYS AT POLES 782285 and 782287. | 5 | 480 | 2400 | 0.0026811 | 5.5856e-06
2012-10-12 08:00AM | 214605 | R218 | Rural Short | Install new 11kV OH mains. Remove redundant 11kV OH mains. Relocate Sub. | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2012-10-12 08:00AM | 214639 | A098 | Rural Short | Augment HV conductor + Replace poles + Install ABS + Install DOFs | 14 | 540 | 7560 | 0.0084454 | 1.564e-05
2012-10-12 08:00AM | 215427 | X877 | Rural Short | Allow staff to MandR poles and hardware. | 34 | 480 | 11040 | 0.012333 | 3.7982e-05
2012-10-12 08:00AM | 217151 | T828 | Rural Short | LIMITED SWITCHING REPLACE LV CROSSARMS and RETROFIT SUB | 10 | 420 | 4200 | 0.0046919 | 1.1171e-05
2012-10-12 08:00AM | 212752 | L534 | Urban | REPLACE POLE 967 SUB 467 and LV POLE 978 | 54 | 480 | 25920 | 0.028956 | 6.0324e-05
2012-10-12 08:00AM | 214384 | 8774 | Urban | Upgrade existing Padmount Sub 17680 to 1000kVA Tx and Augment LV Mains to facilitate the installation of a 1250A CB. | 35 | 540 | 18900 | 0.021114 | 3.9099e-05
2012-10-12 08:00AM | 215846 | 35315 | Urban | To change over LV mains and remove old poles.(district switcher) | 156 | 480 | 37440 | 0.041825 | 0.00017427
2012-10-12 08:00AM | 217085 | 35503 | Urban | maintenance | 62 | 480 | 29760 | 0.033245 | 6.9261e-05
2012-10-12 08:30AM | 214157 | 10290 | Rural Short | Replace pole 101 retro sub 4801 replace HV X-ams 91 and 96 | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2012-10-12 08:30AM | 215715 | BWH2 | Rural Short | Replace Hv Poles and Augment Hv Oh Mains | 65 | 480 | 31200 | 0.034854 | 7.2613e-05
2012-10-12 08:30AM | 215975 | RVD2 | Urban | Tree Trimming by Climbers | 1 | 330 | 330 | 0.00036865 | 1.1171e-06
2012-10-12 09:00AM | 215427 | X877 | Rural Short | Allow staff to MandR poles and hardware. | 12 | 360 | 8280 | 0.0092498 | 1.3405e-05
2012-10-12 09:00AM | 216193 | W111 | Rural Short | Change over low voltage and remove poles. | 37 | 390 | 14430 | 0.01612 | 4.1333e-05
2012-10-12 09:00AM | 216766 | T831 | Rural Short | REPLACE LV CROSSARM | 45 | 360 | 16200 | 0.018097 | 5.027e-05
2012-10-12 09:00AM | 213559 | T869 | Urban | To MandR H/V S/Gear @ Sub 13096 Dickens Rd Ambarvale. | 81 | 360 | 29160 | 0.032575 | 9.0487e-05
2012-10-12 09:00AM | 216080 | KMB2 | Urban | REPLACE X POLE 4JC232 | 6 | 240 | 1440 | 0.0016087 | 6.7027e-06
2012-10-12 09:00AM | 216796 | 16653 | Urban | LV Pole change | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2012-10-12 09:00AM | 216797 | 16653 | Urban | LV Pole change | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2012-10-12 09:00AM | 217053 | UNB2 | Urban | Stand New Street Light | 23 | 150 | 3450 | 0.0038541 | 2.5694e-05
2012-10-12 09:00AM | 217145 | 2822 | Urban | Street Light Improvement | 7 | 180 | 1260 | 0.0014076 | 7.8198e-06
2012-10-13 08:00AM | 216616 | W127 | Rural Short | Install New 12.5M/12kN pole Remove existing stay pole S791 | 48 | 330 | 15840 | 0.017695 | 5.3622e-05
2012-10-13 08:30AM | 216628 | L584 | Rural Short | ISOLATE FOR RAILCORP TO CHANGE CONDEMNED POLE and RETRO FIT SUBS | 2 | 400 | 800 | 0.0008937 | 2.2342e-06
2012-10-13 09:00AM | 216730 | X879 | Rural Short | Relocate LV OH Mains to facilitate the construction of a new vehicular bridge over the proposed new train line. | 29 | 480 | 13920 | 0.01555 | 3.2396e-05
2012-10-13 09:00AM | 215320 | ULF2 | Urban | REPLACE CONDEMNED POLE 2RR048 and RETROFIT S/S 72951SOUTH PACIFIC CRES ULLADULLA | 66 | 265 | 17490 | 0.019538 | 7.373e-05
2012-10-14 06:30AM | 213432 | 35307 | Urban | MandR HVSWGR @ SUB18422 | 116 | 330 | 19140 | 0.021382 | 0.00012959
2012-10-14 08:00AM | 212017 | NG1262 | Urban | Remove existing Kiosk 13009 and associated OH mains. Install New 1000kVA Padmount 28675 and relocate HV USL U624 to new Pole | 7 | 500 | 3500 | 0.0039099 | 7.8198e-06
2012-10-14 08:00AM | 213009 | 4857 | Urban | AUGMENT SECTION OF O/H 11 KV TO 7/4.50AAC | 11 | 480 | 5280 | 0.0058984 | 1.2288e-05
2012-10-14 08:00AM | 217390 | M160 | Urban | REPAIRS TO ABS U145 | 8 | 290 | 2320 | 0.0025917 | 8.937e-06
2012-10-14 08:30AM | 215145 | CRB2 | Urban | Replace poles and augment mains | 188 | 450 | 84600 | 0.094508 | 0.00021002
2012-10-14 09:30AM | 215245 | 6420 | Urban | Replace X Stay Pole PU834489( Fdr 504 P-92 ) | 12 | 109 | 1308 | 0.0014612 | 1.3405e-05
2012-10-14 10:00AM | 215591 | C835 | Urban | REPAIR / REPLACE DEFECTIVE SAFELINK UNIT TRANSPOSSED TEST POINTS @ SUB 27072WORKS REQUEST 110499 | 310 | 420 | 65100 | 0.072725 | 0.00034631
2012-10-14 10:00PM | 212041 | S328 | Urban | HVSWGR MAINT | 71 | 420 | 29820 | 0.033313 | 7.9316e-05
2012-10-15 08:00AM | 215445 | 8798 | Rural Short | tree trimimg adjacent hv mains and change pole | 154 | 500 | 77000 | 0.086018 | 0.00017204
2012-10-15 08:00AM | 216728 | X213 | Rural Short | INSTALL NEW POLES REMOVE USL'S and AUGMENT HV MAINS | 8 | 450 | 3600 | 0.0040216 | 8.937e-06
2012-10-15 08:00AM | 213691 | J493 | Urban | To MandR H/V S/Gear @ Sub 11427 Paroo St Ruse. | 81 | 315 | 25515 | 0.028503 | 9.0487e-05
2012-10-15 08:00AM | 216762 | 3325 | Urban | Augment 1 bay of overhead mains. | 164 | 480 | 78720 | 0.08794 | 0.00018321
2012-10-15 09:00AM | 216972 | 55890 | Urban | Replace LV xarms | 22 | 360 | 7920 | 0.0088476 | 2.4577e-05
2012-10-15 10:00PM | 216575 | A325 | Urban | Replace 2 poles and augment 2 bays of HV mains. | 249 | 480 | 119520 | 0.13352 | 0.00027816
2012-10-16 08:00AM | 213267 | W124 | Rural Short | REPLACE USL'S WITH ABS and AUGMENT HV MAINS | 203 | 510 | 103530 | 0.11566 | 0.00022678
2012-10-16 08:00AM | 216431 | RWB2 | Rural Short | AUGMENT 7 BAYS OF HV MAINS TO 120mm CCT | 65 | 452 | 29380 | 0.032821 | 7.2613e-05
2012-10-16 08:00AM | 213114 | C826 | Urban | To Isolate HV and LV to allow Tree Loppers to remove a tree | 31 | 100 | 3100 | 0.0034631 | 3.4631e-05
2012-10-16 08:00AM | 214451 | R251 | Urban | run1bay of hv and install new abs | 116 | 560 | 34160 | 0.038161 | 0.00012959
2012-10-16 08:00AM | 215700 | 2819 | Urban | 11KV CUT OUT BETWEEN POLE 459 and ABS 66069 TO CHANGE OVER ASSETS TO NEW RAIL CORP POLE | 48 | 460 | 11040 | 0.012333 | 5.3622e-05
2012-10-16 08:00AM | 217086 | 35519 | Urban | maintenance | 46 | 480 | 22080 | 0.024666 | 5.1388e-05
2012-10-16 08:30AM | 215959 | S786 | Rural Short | Replace Twin LV arms service arm links fuses mdi and rewire @ sub 2628 | 5 | 330 | 1650 | 0.0018432 | 5.5856e-06
2012-10-16 08:30AM | 216112 | 35989 | Rural Short | Retrofit substation 10485 and change TX. | 4 | 345 | 1380 | 0.0015416 | 4.4685e-06
2012-10-16 08:30AM | 216386 | 8802 | Rural Short | Replace HV X-Arms LV X-Arms LV Links LV Fuses at Sub 6826. Repair Broken HV Tie @ Pole 31 and Pole 27. | 7 | 465 | 3255 | 0.0036362 | 7.8198e-06
2012-10-16 08:30AM | 216239 | B217 | Urban | REPLACE CONDEMNED POLE 214 (USL 14566) | 51 | 390 | 19890 | 0.02222 | 5.6973e-05
2012-10-16 08:45AM | 215810 | MYG2 | Urban | INSTALL NEW LV PILARS | 45 | 435 | 19575 | 0.021868 | 5.027e-05
2012-10-16 09:00AM | 215219 | ULE2 | Rural Short | Replace Condemned poles and Retro SubVoyager Cres BAWLEY POINT | 37 | 245 | 9065 | 0.010127 | 4.1333e-05
2012-10-16 09:00AM | 216767 | RBE2 | Rural Short | Replace Condemned Pole 3X0954 Retrofit DOFs at Sub 30564 and Sub 30210 | 11 | 405 | 4455 | 0.0049768 | 1.2288e-05
2012-10-16 09:00AM | 216983 | A049 | Rural Short | Replace LV Xarms | 20 | 300 | 6000 | 0.0067027 | 2.2342e-05
2012-10-16 09:00AM | 213678 | J495 | Urban | To MandR H/V S/Gear @ Sub 13001 Goulburn St Ruse. | 88 | 195 | 17160 | 0.01917 | 9.8307e-05
2012-10-16 09:00AM | 214912 | UNE2 | Urban | REPLACE POLES and AUGMENT HV MAINS BETWEEN POLES 871357 871358 and REMOVE ABS 70757 and COMMISSION ABS 96509 | 216 | 345 | 37260 | 0.041624 | 0.0002413
2012-10-16 09:00AM | 216799 | 35388 | Urban | LV Pole change | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2012-10-17 03:30PM | 215170 | UNJ2 | Urban | REPLACE SWITCHING STATION 43170 | 118 | 0 | 0 | 0 | 0.00013182
2012-10-17 08:00AM | 216133 | W163 | Rural Short | AUGMENT HV MAINS and REMOVE/TRIM TREES | 20 | 340 | 6800 | 0.0075964 | 2.2342e-05
2012-10-17 08:00AM | 216613 | HKA2 | Rural Short | Install new poles and HV mains.Remove redundant HV mains and poles | 8 | 370 | 2960 | 0.0033067 | 8.937e-06
2012-10-17 08:00AM | 213771 | 55885 | Urban | Augment HV OH mains 150 NMS.Alter Sub 6421 for HV ABC. | 116 | 490 | 28420 | 0.031749 | 0.00012959
2012-10-17 08:00AM | 214575 | 49357 | Urban | HV SW GR MAINT SUB 16101 | 222 | 310 | 35030 | 0.039133 | 0.000248
2012-10-17 08:00AM | 216067 | AZ1272 | Urban | RETRO SUB 4006 REPLACE TX and REPLACE HV ARMS | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2012-10-17 08:00AM | 216906 | A324 | Urban | Pole replacements augmentation of HV mains and installation ABS. | 170 | 510 | 86700 | 0.096854 | 0.00018991
2012-10-17 08:30AM | 216198 | 4368 | Rural Short | Retro sub 10494 | 12 | 210 | 2520 | 0.0028151 | 1.3405e-05
2012-10-17 08:30AM | 216478 | 10290 | Rural Short | Replace LV X-Arms LV Links LV Fuses Rewire to 1x120 MDI and Earth at Sub 3733 | 16 | 390 | 6240 | 0.0069708 | 1.7874e-05
2012-10-17 08:30AM | 215170 | UNJ2 | Urban | REPLACE SWITCHING STATION 43170 | 90 | 420 | 43680 | 0.048796 | 0.00010054
2012-10-17 08:30AM | 216601 | KMB2 | Urban | INSTALL ADDITIONAL POLE | 32 | 205 | 6560 | 0.0073283 | 3.5748e-05
2012-10-17 08:30AM | 217565 | 52238 | Urban | Replace Column | 31 | 360 | 11160 | 0.012467 | 3.4631e-05
2012-10-17 09:00AM | 216446 | R218 | Rural Short | Undertake repairs to ABS 66302 and 66303. | 37 | 210 | 7770 | 0.00868 | 4.1333e-05
2012-10-17 09:00AM | 217331 | 5867 | Urban | Consac Replacement | 10 | 360 | 3600 | 0.0040216 | 1.1171e-05
2012-10-17 09:00AM | 217337 | 5867 | Urban | Consac Replacement | 27 | 360 | 9720 | 0.010858 | 3.0162e-05
2012-10-17 09:00AM | 217359 | 17067 | Urban | Locate LV cable fault with test sector | 24 | 240 | 5760 | 0.0064346 | 2.6811e-05
2012-10-17 09:30AM | 215610 | BYD2 | Rural Short | INSTALL ADDITIONAL POLES and new LBS 95571 | 9 | 225 | 2025 | 0.0022622 | 1.0054e-05
2012-10-17 09:30AM | 217272 | C808 | Urban | TEST HV CABLE BETWEEN SW # E196 (SUB # 8435 SEATON GR) and SW # 92681 (SUB # 12999 STILT AVE) AFTER CABLE STRIKE - PIN DEFECT # D323 | 43 | 390 | 16770 | 0.018734 | 4.8036e-05
2012-10-17 10:00AM | 217543 | 8777 | Urban | Replace Street Light Column | 10 | 300 | 3000 | 0.0033514 | 1.1171e-05
2012-10-17 11:00AM | 217347 | 9025 | Urban | Maintenance | 1 | 300 | 300 | 0.00033514 | 1.1171e-06
2012-10-18 07:00AM | 216573 | 20725 | Urban | Remove section of mains and pole sub 8182 USL C714Install new ABS 93018 Install new Poles x2 new pad Sub 29449 and New Sections of U/G cable | 33 | 540 | 17820 | 0.019907 | 3.6865e-05
2012-10-18 08:00AM | 216786 | MVF2 | Rural Short | Replace 5 poles install one new pole. | 130 | 490 | 63700 | 0.071161 | 0.00014523
2012-10-18 08:00AM | 216928 | BWF2 | Rural Short | Trim Trees In Clearances | 1 | 475 | 475 | 0.00053063 | 1.1171e-06
2012-10-18 08:00AM | 214800 | B205 | Urban | Augment 3 bays of HV Mains. Replace 3 poles. | 61 | 540 | 32940 | 0.036798 | 6.8144e-05
2012-10-18 08:00AM | 217007 | 49917 | Urban | Augment HV conductor and Replace poles | 153 | 600 | 91800 | 0.10255 | 0.00017092
2012-10-18 08:00AM | 217667 | 35304 | Urban | Isolation for tree lopper to cut tree | 7 | 390 | 2730 | 0.0030497 | 7.8198e-06
2012-10-18 08:30AM | 216123 | 35988 | Rural Short | Replace Pole 30 ABS U470 and Install ground stay at pole 34 | 6 | 391 | 2346 | 0.0026208 | 6.7027e-06
2012-10-18 08:30AM | 216242 | B217 | Urban | REPLACE CONDEMNED POLE 482 | 36 | 615 | 22140 | 0.024733 | 4.0216e-05
2012-10-18 09:00AM | 211202 | A049 | Rural Short | To test new 11kv Alex Ave UG feeder.To connect and bond in new 11kv Alex Ave UG feeder.Remove 1 bay HV OH mains.(job to run from 16/10/12 to 18/10/12) | 6 | 180 | 1080 | 0.0012065 | 6.7027e-06
2012-10-18 09:00AM | 216769 | T831 | Rural Short | REPLACE LV CROSSARMS | 45 | 360 | 16200 | 0.018097 | 5.027e-05
2012-10-18 09:00AM | 217523 | RWB2 | Rural Short | Replace Condemned LV Pole 3J0463 | 35 | 360 | 12600 | 0.014076 | 3.9099e-05
2012-10-18 09:00AM | 217101 | 5877 | Urban | Pole Changeover | 28 | 360 | 10080 | 0.011261 | 3.1279e-05
2012-10-18 09:00AM | 217600 | B799 | Urban | Repair Switch and replace SL Column | 5 | 240 | 1200 | 0.0013405 | 5.5856e-06
2012-10-18 10:00AM | 217296 | APF2 | Urban | (LIMITED SWITCHING) Tap change sub 41338 | 60 | 25 | 1500 | 0.0016757 | 6.7027e-05
2012-10-19 08:00AM | 216502 | 10290 | Rural Short | Replace LV X-Arms MDI and Outrigger at Sub 5377 | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2012-10-19 08:00AM | 216872 | R260 | Rural Short | Run and connect LV ABC + remove open wire | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2012-10-19 08:00AM | 217491 | R218 | Rural Short | Install new 11kV OH mains. Remove redundant 11kV OH mains. Relocate Sub. | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2012-10-19 08:00AM | 216473 | R248 | Urban | PERFORM ABS MAINTENANCE ON ABS H317 GREAT WESTERN HIGHWAY WARRIMOO | 60 | 120 | 7560 | 0.0084454 | 6.7027e-05
2012-10-19 08:00AM | 217023 | A322 | Urban | Augment HV Conductor and Replace pole | 119 | 455 | 54145 | 0.060486 | 0.00013294
2012-10-19 08:00AM | 217660 | 35530 | Urban | Maintenance | 24 | 240 | 5760 | 0.0064346 | 2.6811e-05
2012-10-19 08:00AM | 217810 | J478 | Urban | Bond new section of LV to existing network | 46 | 480 | 22080 | 0.024666 | 5.1388e-05
2012-10-19 08:30AM | 215084 | DP1210 | Rural Short | REPLACE POLES 4CA037 and 4CA038 . RETRO SUBS 40722 41635 and 40700.REPLACE LV ARMS POLES 4AY292 and 4CA023.REPLACE HV ARM POLE 4CA022. | 37 | 390 | 14430 | 0.01612 | 4.1333e-05
2012-10-19 08:30AM | 216489 | D814 | Rural Short | Retro Replace LV X-Arms HV X-Arm MDI LV Fuses Rewire 1x 120 Bare Earth at Sub 2023 | 11 | 360 | 3960 | 0.0044238 | 1.2288e-05
2012-10-19 08:30AM | 216852 | 35990 | Rural Short | Change Condemed Pole 454 | 12 | 285 | 3420 | 0.0038206 | 1.3405e-05
2012-10-19 09:00AM | 217339 | 5867 | Urban | Consac Replacement | 29 | 360 | 10440 | 0.011663 | 3.2396e-05
2012-10-19 09:00AM | 217342 | 5867 | Urban | Consac Replacement | 9 | 360 | 3240 | 0.0036195 | 1.0054e-05
2012-10-19 09:00AM | 217547 | RVD2 | Urban | Tree Trimming by Climbers | 1 | 330 | 330 | 0.00036865 | 1.1171e-06
2012-10-19 09:00AM | 217557 | 16660 | Urban | Pole change HV/LV | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2012-10-19 09:30AM | 213790 | YYB2 | Rural Short | Replace USLs with DOFsPorters Creek Rd YATTE YATTAH. | 18 | 125 | 2250 | 0.0025135 | 2.0108e-05
2012-10-19 11:00AM | 217661 | 8679 | Urban | maintenance | 45 | 300 | 13500 | 0.015081 | 5.027e-05
2012-10-20 08:00AM | 215576 | MR2292 | Urban | NEW 315 KVA 22KV P/MOUNT SUB 28658 AREVER 2 FDR HV S/GEAR INSTALL 240 Sq Al XLPE CABLE INSTALL 2 STJs | 14 | 90 | 1260 | 0.0014076 | 1.564e-05
2012-10-20 08:30AM | 216913 | KMA2 | Urban | TEST HV CABLE TO LOCATE CABLE FAULT | 33 | 270 | 8910 | 0.0099535 | 3.6865e-05
2012-10-20 12:00PM | 216643 | SWD2 | Urban | REFURB SUBSTATION 40570 | 15 | 1370 | 20550 | 0.022957 | 1.6757e-05
2012-10-21 06:30AM | 214599 | 35443 | Urban | REPLACE HV and LV SW/GR CUBICLE + TX and PERFORM 2 STJ'S. | 6 | 925 | 2775 | 0.0031 | 6.7027e-06
2012-10-21 06:30AM | 216774 | T898 | Urban | 1 I D and SPIKE existing cable2. Bond new section of cable onto sw 73338 in sub 27432 and cut existing cable and carry out HV STJ | 12 | 578 | 6936 | 0.0077483 | 1.3405e-05
2012-10-21 07:00AM | 214228 | 55874 | Urban | REPLACE POLE 2833 | 8 | 500 | 2000 | 0.0022342 | 8.937e-06
2012-10-21 07:00AM | 217203 | 17035 | Urban | Run 33kv conductor and OPGW Pole 396 - new UGOH pole west of ABS 53211 Replace ABS 53211 with LBS 89464. Install 33kV UG0H. | 246 | 215 | 52890 | 0.059084 | 0.00027481
2012-10-21 08:00AM | 216506 | PCB2 | Urban | REPLACE UGOH and POLE Mandr HOLEC SWITCHGEAR | 23 | 420 | 9660 | 0.010791 | 2.5694e-05
2012-10-21 08:30AM | 216755 | 35990 | Rural Short | Repair HV defects @ Sub 10567 | 14 | 360 | 5040 | 0.0056303 | 1.564e-05
2012-10-21 08:30AM | 214014 | L543 | Urban | Remove HV OH mains and ABS's 42685 and 37570. | 39 | 270 | 10530 | 0.011763 | 4.3568e-05
2012-10-21 09:00AM | 216310 | W188 | Rural Short | Relocate 2 poles (184 and 185 Zouch Rd Bardia) and transfer associated HV and LV mains to suit. | 2 | 410 | 820 | 0.00091604 | 2.2342e-06
2012-10-21 09:00AM | 216022 | NA1281 | Urban | Replace pole 1YC756. | 248 | 300 | 74400 | 0.083114 | 0.00027705
2012-10-21 09:00PM | 214599 | 35443 | Urban | REPLACE HV and LV SW/GR CUBICLE + TX and PERFORM 2 STJ'S. | 6 | 55 | 165 | 0.00018432 | 6.7027e-06
2012-10-22 03:00PM | 217434 | R251 | Urban | Install 11 bays of O/H HV mains to 150mm HV NMSABC install ABS 94880 and stand 3 new poles and commssion ABS 95487 | 180 | 30 | 1800 | 0.0020108 | 0.00020108
2012-10-22 08:00AM | 215738 | L940 | Rural Short | REPLACE EXISTING POLE and INSTALL NEW 3 PH 100 KVA POLE SUB 32179 INSTALL NEW POLE 867904 | 14 | 470 | 6580 | 0.0073506 | 1.564e-05
2012-10-22 08:00AM | 212418 | WRB2 | Urban | AUGMENT 3 BAYS OF HV MAINS + REPLACE HARDWARE.INSTALL USL 93289. | 144 | 495 | 71280 | 0.079628 | 0.00016087
2012-10-22 08:00AM | 217096 | 3325 | Urban | Replace 1 pole and augment 1 bay of HV mains. | 220 | 510 | 112200 | 0.12534 | 0.00024577
2012-10-22 08:00AM | 217434 | R251 | Urban | Install 11 bays of O/H HV mains to 150mm HV NMSABC install ABS 94880 and stand 3 new poles and commssion ABS 95487 | 180 | 450 | 27000 | 0.030162 | 0.00020108
2012-10-22 08:30AM | 217052 | MVH2 | Rural Short | Install New Sub 29454 Remove Sub 30416 and Augment a Section of 11KV O/H Mains | 1 | 405 | 405 | 0.00045243 | 1.1171e-06
2012-10-22 08:30AM | 217779 | L582 | Rural Short | DOUBLE ARM LV AT POLE 87 | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2012-10-22 08:30AM | 217865 | L582 | Rural Short | LOCAL SWITCHING REQUEST REPLACE LV CROSSARM OFF SUB 17461 | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2012-10-22 08:30AM | 216299 | RVD2 | Urban | NEW POLE SUBSTATION | 24 | 300 | 7200 | 0.0080433 | 2.6811e-05
2012-10-22 08:30AM | 216771 | 17061 | Urban | Install HV cable between subs 10487 and 18459 | 172 | 525 | 90300 | 0.10088 | 0.00019214
2012-10-22 09:00AM | 217554 | 2815 | Urban | Pole Change LV | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2012-10-22 09:00AM | 217879 | S326 | Urban | Install LV Cables | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2012-10-22 09:30AM | 217563 | HKE2 | Rural Short | Replace pole 2GK064. | 63 | 240 | 15120 | 0.016891 | 7.0379e-05
2012-10-23 03:30PM | 215496 | DP1269 | Urban | REPLACE SWITCHGEAR IN SWITCHING STATION 23059 | 19 | 30 | 570 | 0.00063676 | 2.1225e-05
2012-10-23 08:00AM | 216438 | C814 | Rural Short | RETRO SUB # 799 | 10 | 315 | 3150 | 0.0035189 | 1.1171e-05
2012-10-23 08:00AM | 216933 | W124 | Rural Short | AUGMENT LV MAINS and REDRESS SUB POLE | 54 | 440 | 23760 | 0.026543 | 6.0324e-05
2012-10-23 08:00AM | 217054 | X802 | Rural Short | INSTALL USL'SREPLACE POLESINSTALL NEW SUBAUGMENT and REMOVE HV MAINS | 29 | 360 | 10440 | 0.011663 | 3.2396e-05
2012-10-23 08:00AM | 217972 | HKA2 | Rural Short | Install /replace poles install new LBS and augment mains. | 95 | 510 | 48450 | 0.054124 | 0.00010613
2012-10-23 08:00AM | 213494 | B764 | Urban | MandR HVSWGR @ SUB 7799 AND FIX DEFECTS DO64 ON SWITCHGEAR AND CABLES | 88 | 200 | 17600 | 0.019661 | 9.8307e-05
2012-10-23 08:00AM | 215632 | A350 | Urban | REPLACE HV ARMS | 32 | 450 | 14400 | 0.016087 | 3.5748e-05
2012-10-23 08:30AM | 216644 | D813 | Rural Short | MandR ABS 2446 and Repair Pole Cap at Pole 8 | 19 | 365 | 6935 | 0.0077472 | 2.1225e-05
2012-10-23 08:30AM | 216687 | RWC2 | Rural Short | Install new padmount substation and Assoc UG mains | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2012-10-23 08:30AM | 215819 | 49918 | Urban | REPLACE POLE 284 AND ABS U103 | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2012-10-23 08:30AM | 216414 | WRB2 | Urban | REPLACE X PLs 1G0333 1G0330 1G0329 RETRO FIT SUB 41841 | 84 | 330 | 27720 | 0.030967 | 9.3838e-05
2012-10-23 08:30AM | 216458 | NWB2 | Urban | Replace ABS pole 70483 and Install LBS | 48 | 360 | 17280 | 0.019304 | 5.3622e-05
2012-10-23 09:00AM | 217345 | 5867 | Urban | Consac Replacement | 28 | 360 | 10080 | 0.011261 | 3.1279e-05
2012-10-23 09:00AM | 217548 | 1105 | Urban | LV Arm change | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2012-10-23 09:00AM | 217549 | 1105 | Urban | Cross arm change | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2012-10-23 09:00AM | 217550 | 1105 | Urban | Cross arm change | 2 | 180 | 360 | 0.00040216 | 2.2342e-06
2012-10-23 09:00AM | 217662 | 8652 | Urban | Rusty Column | 10 | 240 | 2400 | 0.0026811 | 1.1171e-05
2012-10-23 09:00AM | 217663 | 19816 | Urban | Rusty Column | 41 | 180 | 7380 | 0.0082443 | 4.5802e-05
2012-10-24 08:00AM | 215710 | KC1288 | Rural Short | replace abs pole with new recloser | 15 | 530 | 7950 | 0.0088811 | 1.6757e-05
2012-10-24 08:00AM | 212413 | WWB2 | Urban | INSTALL LBS + AUGMENT 1 BAY OF HV MAINS REPLACE 2 POLES. | 158 | 420 | 66360 | 0.074132 | 0.0001765
2012-10-24 08:00AM | 213870 | J493 | Urban | To MandR H/V S/Gear @ Sub 13000 Peel St Ruse. | 82 | 240 | 19680 | 0.021985 | 9.1604e-05
2012-10-24 08:00AM | 216880 | C896 | Urban | PERFORM HV SWITCHGEAR MandR / EARTH TEST and REPLACE PLASTIC COVER ON SWITCHGEAR FRAME @ SUB # 5937 - NEWHAM DR CAMBRIDGE PARK | 1 | 470 | 470 | 0.00052505 | 1.1171e-06
2012-10-24 08:00AM | 217903 | 8762 | Urban | Condemned Pole and Defects | 47 | 480 | 22560 | 0.025202 | 5.2505e-05
2012-10-24 08:00AM | 217946 | 19871 | Urban | Install a new pillar | 6 | 480 | 2880 | 0.0032173 | 6.7027e-06
2012-10-24 08:00AM | 217953 | 19894 | Urban | Maintenance | 35 | 420 | 14700 | 0.016422 | 3.9099e-05
2012-10-24 08:00AM | 217955 | 19894 | Urban | Maintenance | 28 | 480 | 13440 | 0.015014 | 3.1279e-05
2012-10-24 08:00AM | 217979 | J481 | Urban | Cut in LV pillars | 26 | 480 | 12480 | 0.013942 | 2.9045e-05
2012-10-24 08:30AM | 214737 | T851 | Rural Short | Replace USL 17129 with Auto LBS 92212 | 3 | 385 | 1155 | 0.0012903 | 3.3514e-06
2012-10-24 08:30AM | 216210 | 46487 | Rural Short | Retro sub 16054 and sub 15892 | 15 | 285 | 4275 | 0.0047757 | 1.6757e-05
2012-10-24 08:30AM | 216765 | GG1232 | Rural Short | REPLACE X POLE 4KX039 | 9 | 305 | 2745 | 0.0030665 | 1.0054e-05
2012-10-24 08:30AM | 217860 | W163 | Rural Short | LOCAL SWITCHING REQUEST ISOLATE SUB 28862 TO ALLOW LV ABC TO BE RUN | 2 | 285 | 570 | 0.00063676 | 2.2342e-06
2012-10-24 08:30AM | 216726 | SHC2 | Urban | NEW LV PILLARS | 38 | 450 | 17100 | 0.019103 | 4.2451e-05
2012-10-24 08:30AM | 217032 | WRF2 | Urban | MandR HOLIC SWITCHGEAR | 72 | 240 | 17280 | 0.019304 | 8.0433e-05
2012-10-24 09:00AM | 216365 | CLD2 | Rural Short | Change L/V poles 3TT139 and 3TT142 Gerringong Street Currarong | 14 | 390 | 5460 | 0.0060995 | 1.564e-05
2012-10-24 09:30AM | 217100 | ULE2 | Rural Short | Replace 2 ABS's with 2 Type 3 LBSsMurramarang Rd KIOLOA. | 305 | 350 | 106750 | 0.11925 | 0.00034072
2012-10-24 09:30AM | 218002 | BDG2 | Rural Short | 48hr pole. Limited switching.Replace pole 1XJ043. | 10 | 260 | 2600 | 0.0029045 | 1.1171e-05
2012-10-25 05:00PM | 215529 | APA2 | Urban | REPLACE S/S 43196 | 42 | 3 | 126 | 0.00014076 | 4.6919e-05
2012-10-25 08:00AM | 215267 | L588 | Rural Short | CONTRACTOR TREE TRIMMING | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2012-10-25 08:00AM | 216609 | 55354 | Rural Short | RETRO and RE-WIRE SUB # 9489 | 70 | 300 | 21000 | 0.02346 | 7.8198e-05
2012-10-25 08:00AM | 216803 | T831 | Rural Short | RETROFIT SUB REPLACE LV CROSSARMS | 59 | 255 | 15045 | 0.016807 | 6.591e-05
2012-10-25 08:00AM | 217150 | R260 | Rural Short | Augment Existing Bare Overhead HV mains to 3 x 120mm AL CCT. Replace USL's W008 with DOF's 95050 ( 16A ). | 88 | 450 | 39600 | 0.044238 | 9.8307e-05
2012-10-25 08:00AM | 217392 | 8798 | Rural Short | Change over underground service to new pole. | 1 | 300 | 300 | 0.00033514 | 1.1171e-06
2012-10-25 08:00AM | 217558 | ULE2 | Rural Short | Augment one bay of HV mains to 19/3.25AAAC and one bay of HV mains to 7/4.50AAAC | 4 | 400 | 1600 | 0.0017874 | 4.4685e-06
2012-10-25 08:00AM | 213898 | J495 | Urban | To MandR H/V S/Gear @ Sub 11391 Sirius St Ruse | 81 | 220 | 17820 | 0.019907 | 9.0487e-05
2012-10-25 08:00AM | 215549 | 4374 | Urban | change 2 poles and run lv mains | 150 | 480 | 72000 | 0.080433 | 0.00016757
2012-10-25 08:00AM | 216140 | WWF2 | Urban | Replace ABS | 70 | 432 | 30240 | 0.033782 | 7.8198e-05
2012-10-25 08:00AM | 216565 | MR2232 | Urban | Install armour rods | 46 | 120 | 5520 | 0.0061665 | 5.1388e-05
2012-10-25 08:00AM | 217126 | SWE2 | Urban | MandR HOLEC SWITCHGEAR | 1 | 205 | 205 | 0.00022901 | 1.1171e-06
2012-10-25 08:00AM | 217971 | 27334 | Urban | Cut in new LV pillar | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2012-10-25 08:30AM | 217092 | H745 | Rural Short | Augment high voltage mains from sub 17066 to sub 12035 and install ABS 86798 and LBS 86799 | 29 | 435 | 12615 | 0.014092 | 3.2396e-05
2012-10-25 08:30AM | 217414 | MGC2 | Rural Short | HV Augmentation | 13 | 495 | 6435 | 0.0071887 | 1.4523e-05
2012-10-25 08:30AM | 217654 | RBA2 | Rural Short | Install New Poles Replace Poles Remove Poles and Augment a Section of 11KV O/H Mains to 3 x 7/4.50 AAAC | 26 | 375 | 9750 | 0.010892 | 2.9045e-05
2012-10-25 08:30AM | 215762 | BLD2 | Urban | Replace Condemned Sub pole 41043 | 35 | 349 | 12215 | 0.013646 | 3.9099e-05
2012-10-25 08:30AM | 216673 | 46477 | Urban | Replace LV X-Arms at Sub 5432 | 2 | 180 | 360 | 0.00040216 | 2.2342e-06
2012-10-25 09:00AM | 211908 | A049 | Rural Short | To remove 2 bays HV OH mains for future Advance St 11kv UG feeder. | 52 | 420 | 21840 | 0.024398 | 5.809e-05
2012-10-25 09:00AM | 214973 | BYC2 | Rural Short | Replace poles ( 15 16 and 19 )Bong Bong Rd BERRY. | 9 | 300 | 2700 | 0.0030162 | 1.0054e-05
2012-10-25 09:00AM | 217777 | UNC2 | Urban | Augment LV Mains and replace two Poles | 20 | 360 | 7200 | 0.0080433 | 2.2342e-05
2012-10-25 09:00AM | 218085 | 52238 | Urban | Replace Rusted column | 3 | 180 | 540 | 0.00060324 | 3.3514e-06
2012-10-25 12:00PM | 216561 | S735 | Rural Short | Install Armour rods | 10 | 240 | 2400 | 0.0026811 | 1.1171e-05
2012-10-26 05:00AM | 218050 | L509 | Urban | Move service around | 1 | 90 | 90 | 0.00010054 | 1.1171e-06
2012-10-26 06:00AM | 217174 | 27191 | Urban | Install sub 28741 and remove pole sub 233. | 36 | 680 | 24480 | 0.027347 | 4.0216e-05
2012-10-26 08:00AM | 217080 | W111 | Rural Short | To allow staff to retrofit Sub 10165 Macquariedale Rd Appin | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2012-10-26 08:00AM | 217121 | C814 | Rural Short | REPLACE POLE # 139 - BARNES RD LLANDILO | 21 | 310 | 6510 | 0.0072725 | 2.346e-05
2012-10-26 08:00AM | 217437 | T828 | Rural Short | LIMITED SWITCHING REPLACE LV CROSSARMS and RETROFIT SUB | 10 | 390 | 3900 | 0.0043568 | 1.1171e-05
2012-10-26 08:00AM | 217920 | 8634 | Rural Short | augment hv mains and replace usl with new abs | 220 | 465 | 102300 | 0.11428 | 0.00024577
2012-10-26 08:00AM | 215006 | W120 | Urban | Replace pole 392 with new 12.5M/Sub pole. Install new 100kVA pole sub | 68 | 300 | 20400 | 0.022789 | 7.5964e-05
2012-10-26 08:00AM | 216456 | 4375 | Urban | UPRATE SUB 16083 TO 500 KVA CHANGE LV SW GEAR | 2 | 340 | 680 | 0.00075964 | 2.2342e-06
2012-10-26 08:00AM | 216559 | T889 | Urban | Upgrade HV cross arm | 68 | 180 | 12240 | 0.013674 | 7.5964e-05
2012-10-26 08:00AM | 217366 | RVC2 | Urban | Replace 2 poles + Augment 1 bay of conductor + Install DOFs | 165 | 520 | 85800 | 0.095849 | 0.00018432
2012-10-26 08:30AM | 216875 | P608 | Rural Short | Remove USL 12478 and replace it with ABS 86796 and repair defects at poles 36 37 and 38. | 28 | 430 | 12040 | 0.01345 | 3.1279e-05
2012-10-26 08:30AM | 216886 | 8634 | Rural Short | Install Vibration Dampeners at Pole 86 and Pole 130-131. | 3 | 180 | 540 | 0.00060324 | 3.3514e-06
2012-10-26 08:30AM | 215773 | DP1258 | Urban | REPLACE ABS 75154 RETRO S/S 42684 41643 41787 41234 + AREA DEFECTS | 165 | 411 | 67815 | 0.075757 | 0.00018432
2012-10-26 08:30AM | 217402 | MYG2 | Urban | Replace ABS pole 70212 | 72 | 360 | 15480 | 0.017293 | 8.0433e-05
2012-10-26 08:30AM | 217987 | UNG2 | Urban | REPLACE STREET LIGHT COLUMNS | 52 | 180 | 9360 | 0.010456 | 5.809e-05
2012-10-26 09:00AM | 214509 | CLD2 | Rural Short | Replace pole 3HG115 and 3HD013 Myola Rd MYOLA. | 85 | 360 | 30600 | 0.034184 | 9.4955e-05
2012-10-26 09:00AM | 217090 | BYD2 | Rural Short | Stand new poles. | 9 | 205 | 1845 | 0.0020611 | 1.0054e-05
2012-10-26 09:00AM | 217556 | F601 | Urban | Pole change LV | 4 | 180 | 720 | 0.00080433 | 4.4685e-06
2012-10-26 09:00AM | 217996 | 8685 | Urban | Cable Fault | 24 | 360 | 8640 | 0.0096519 | 2.6811e-05
2012-10-26 09:30AM | 213857 | ULE2 | Rural Short | Replace Condemned poles 1GR025 and 1GR028Monkey Mountain Rd TERMEIL | 2 | 150 | 300 | 0.00033514 | 2.2342e-06
2012-10-26 10:00AM | 218088 | 1125 | Urban | Low voltage interruption | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2012-10-27 07:00AM | 217220 | FF1239 | Urban | establish new pad sub 29994 | 184 | 30 | 5520 | 0.0061665 | 0.00020555
2012-10-27 07:00AM | 218056 | 7974 | Urban | Changeover Pole | 2 | 600 | 1200 | 0.0013405 | 2.2342e-06
2012-10-27 08:00AM | 216465 | PKF2 | Urban | 11kV OUTAGE ON FDR PKF2 TO REPLACE STR 74 75 76 FDR 7381 | 13 | 440 | 5720 | 0.0063899 | 1.4523e-05
2012-10-27 08:30AM | 218207 | H745 | Rural Short | Change condemned 48hour pole 160.48 hour pole | 5 | 290 | 1450 | 0.0016198 | 5.5856e-06
2012-10-28 07:00AM | 205734 | 4869 | Urban | AUGMENT SECTION OF O/H HV TO 7/4.50 AAC | 10 | 600 | 6000 | 0.0067027 | 1.1171e-05
2012-10-28 07:00AM | 217220 | FF1239 | Urban | establish new pad sub 29994 | 184 | 30 | 5520 | 0.0061665 | 0.00020555
2012-10-28 08:00AM | 217120 | 8617 | Urban | Replace 3 poles. Augment 3 bays of HV mains. | 141 | 525 | 74025 | 0.082695 | 0.00015751
2012-10-28 08:30AM | 216781 | 46479 | Urban | Retro Sub 4724 Remove Arms and make Rural Sub Replace Service with 95mm LVABC. MandR ABS C153. | 37 | 405 | 14985 | 0.01674 | 4.1333e-05
2012-10-28 08:30AM | 217114 | NWE2 | Urban | Replace ABS 74161 with LBS 97124Retrofit Subs 22386 41448 43329 and 43082 Install Pole Caps | 85 | 390 | 33150 | 0.037033 | 9.4955e-05
2012-10-28 08:30AM | 218051 | 19894 | Urban | replace UGOH | 18 | 540 | 9720 | 0.010858 | 2.0108e-05
2012-10-28 09:00AM | 216668 | NA1225 | Urban | Replace pole 1XT013. | 15 | 250 | 3750 | 0.0041892 | 1.6757e-05
2012-10-28 10:00PM | 212741 | 27188 | Urban | HVSWGR MAINT | 56 | 370 | 20720 | 0.023147 | 6.2559e-05
2012-10-29 01:00PM | 217951 | 19857 | Urban | maintenance | 1 | 180 | 180 | 0.00020108 | 1.1171e-06
2012-10-29 08:00AM | 217541 | R208 | Rural Short | Replace 2 poles and Augment HV Mains to 150mm HVABC | 6 | 550 | 3300 | 0.0036865 | 6.7027e-06
2012-10-29 08:00AM | 214275 | UNJ2 | Urban | NEW PAD SUBSTATION | 76 | 510 | 38760 | 0.0433 | 8.4901e-05
2012-10-29 08:00AM | 215150 | 25783 | Urban | Remove:1 x HV UGOH 2 x poles HV OH mainsInstall:1 x HV STJ 2 x poles 1 x HV UGOH HV UG cable | 18 | 420 | 3780 | 0.0042227 | 2.0108e-05
2012-10-29 08:00AM | 217477 | GV1223 | Urban | Hv hardware rectification | 179 | 220 | 39380 | 0.043992 | 0.00019996
2012-10-29 08:00AM | 217950 | 9022 | Urban | Maintenance | 21 | 360 | 7560 | 0.0084454 | 2.346e-05
2012-10-29 08:30AM | 216759 | D810 | Rural Short | MandR ABS 11213 | 8 | 230 | 1840 | 0.0020555 | 8.937e-06
2012-10-29 08:30AM | 217361 | GG1295 | Rural Short | New pole Substation and Overhead Mains | 4 | 330 | 1320 | 0.0014746 | 4.4685e-06
2012-10-29 08:30AM | 217511 | MVC2 | Rural Short | HV Augmentation | 81 | 475 | 38475 | 0.042981 | 9.0487e-05
2012-10-29 09:00AM | 217658 | RBE2 | Rural Short | Replace Condemned Pole 3X0582 | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2012-10-30 08:00AM | 214993 | L941 | Rural Short | Replace USL 9725 + pole with LBS 95510 Augment 4 bays of 150mm LVABC from ABS 95510 to SUB 3723 Tie in HV and Replace twin LV arms rewire links and fuses @ sub 3723 | 22 | 480 | 10560 | 0.011797 | 2.4577e-05
2012-10-30 08:00AM | 214632 | R251 | Urban | augment hv mains | 49 | 380 | 18620 | 0.020801 | 5.4739e-05
2012-10-30 08:00AM | 217406 | PKA2 | Urban | Replace pole | 224 | 430 | 49020 | 0.054761 | 0.00025023
2012-10-30 08:00AM | 217621 | 20717 | Urban | PEPLACE 2 X POLES # 120 and 121 CNR OF FITCH and LADBURY AV | 32 | 460 | 14720 | 0.016444 | 3.5748e-05
2012-10-30 08:30AM | 216474 | BWH2 | Rural Short | Replace Hv Pole's and HV Augmentation | 240 | 530 | 107060 | 0.1196 | 0.00026811
2012-10-30 08:30AM | 217876 | W163 | Rural Short | REPLACE 2 CONDEMNED POLES and INSTALL SECTIONALISER and NEW USLs | 41 | 314 | 11618 | 0.012979 | 4.5802e-05
2012-10-30 08:30AM | 215505 | PKF2 | Urban | Replace Poles and Install LV ABC mains | 27 | 390 | 10530 | 0.011763 | 3.0162e-05
2012-10-30 08:30AM | 216915 | A054 | Urban | To install new 300kva SPS 29588(district switcher) | 17 | 420 | 7140 | 0.0079762 | 1.8991e-05
2012-10-30 09:00AM | 217560 | 16649 | Urban | pole change sub | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2012-10-30 09:00AM | 217835 | 16660 | Urban | Pole change ABS and LV Pin | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2012-10-30 09:00AM | 218283 | 55867 | Urban | Improving S/L | 31 | 360 | 11160 | 0.012467 | 3.4631e-05
2012-10-30 09:30AM | 217760 | KVA2 | Rural Short | ****LIMITED SWITCHING**** Replace pole 1HX022 ( S/S 50584 )Carters Rd BARRENGARY. | 3 | 300 | 900 | 0.0010054 | 3.3514e-06
2012-10-31 08:00AM | 216187 | D810 | Rural Short | INSTALL STAYS TO POLES 102 103 401181 INSTALL VIBRATION DAMPERS ON RIVER CROSSING BAY 401181 TO POLE 166. INSTALL VIBRATION DAMPERS ADJ USL E561. INSTALL VIBRATION DAMPERS ON RIVER CROSSING BAY 774388 TO 110. | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2012-10-31 08:00AM | 216482 | GG1295 | Rural Short | Augment one bay of HV Mains to 7/4.50AAAC. Replace two existing poles. | 5 | 460 | 2300 | 0.0025694 | 5.5856e-06
2012-10-31 08:00AM | 216560 | 27454 | Rural Short | HV Augmentation | 2 | 465 | 930 | 0.0010389 | 2.2342e-06
2012-10-31 08:00AM | 216652 | BYB2 | Rural Short | restring existing mains to new poles /install new mains and new poles / install new pole sub | 19 | 390 | 7410 | 0.0082779 | 2.1225e-05
2012-10-31 08:00AM | 212037 | 5877 | Urban | HVSWGR MAINT | 46 | 255 | 11730 | 0.013104 | 5.1388e-05
2012-10-31 08:00AM | 214362 | 3184 | Urban | Allow staff to remove USL 83053 and replace with ABS 92355 | 68 | 440 | 29920 | 0.033424 | 7.5964e-05
2012-10-31 08:00AM | 214716 | MR2232 | Urban | Install 1 x new poleUpgrade polesub 24412 from 63KVA to 200KVA | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2012-10-31 08:00AM | 217257 | 8773 | Urban | Connect New LV Subdivision to Existing Network. | 2 | 240 | 4080 | 0.0045578 | 2.2342e-06
2012-10-31 08:00AM | 218058 | 7970 | Urban | AUGMENT LV MAINS BETWEEN POLES 847460 and 2211 | 20 | 360 | 7200 | 0.0080433 | 2.2342e-05
2012-10-31 08:00AM | 218345 | RS1262 | Urban | Install a new pole | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2012-10-31 08:00AM | 218445 | 9026 | Urban | maintenance (replace x arms) | 86 | 240 | 20640 | 0.023057 | 9.6072e-05
2012-10-31 08:30AM | 217010 | 76225 | Rural Short | RETROFIT SUBREPAIR HV TIE and REPLACE LV CROSSARM | 4 | 230 | 920 | 0.0010278 | 4.4685e-06
2012-10-31 08:30AM | 217034 | 76225 | Rural Short | HV DEFECTS and INSTALL VIBRATION DAMPERS | 13 | 235 | 3055 | 0.0034128 | 1.4523e-05
2012-10-31 08:30AM | 217573 | H745 | Rural Short | Install new poles 862800 862801 and 632286 | 13 | 333 | 4329 | 0.004836 | 1.4523e-05
2012-10-31 08:30AM | 217021 | PCE2 | Urban | Replace ABS 70683 with LBS 97151Retrofit Subs 4172642043 and 41632 | 110 | 220 | 24200 | 0.027034 | 0.00012288
2012-10-31 09:00AM | 214584 | ULC2 | Rural Short | Install New Recloser 96682Princes Hwy MILTON. | 1 | 235 | 235 | 0.00026252 | 1.1171e-06
2012-10-31 09:00AM | 216295 | A049 | Rural Short | To augment LV mains replace HV/LV xarms and install street lighting. | 67 | 317 | 21239 | 0.023727 | 7.4847e-05
2012-10-31 09:00AM | 217094 | BYD2 | Rural Short | Augment HV mains. | 9 | 215 | 1935 | 0.0021616 | 1.0054e-05
2012-10-31 09:00AM | 216823 | 8781 | Urban | REPLACE TRFCUBICLE and LV SWITCHGEAR IN SUB 16367 | 8 | 510 | 4080 | 0.0045578 | 8.937e-06
2012-10-31 09:00AM | 218354 | B799 | Urban | Replace Rusty Column | 6 | 240 | 1440 | 0.0016087 | 6.7027e-06
2012-10-31 09:30AM | 217463 | SXD2 | Rural Short | Replace TX @ S/S 50869. | 75 | 285 | 21375 | 0.023878 | 8.3784e-05
2012-10-31 10:00AM | 217257 | 8773 | Urban | Connect New LV Subdivision to Existing Network. | 32 | 360 | 6120 | 0.0068368 | 3.5748e-05
2012-10-31 11:00AM | 218441 | 17038 | Urban | maintenance | 30 | 300 | 9000 | 0.010054 | 3.3514e-05
2012-11-01 01:00PM | 218352 | 19816 | Urban | Replace Rusty Column | 15 | 180 | 2700 | 0.0030162 | 1.6757e-05
2012-11-01 07:00AM | 216490 | R214 | Urban | Uprate Tx at SUB 12088 | 6 | 546 | 3276 | 0.0036597 | 6.7027e-06
2012-11-01 07:00AM | 217473 | 3166 | Urban | Stand P-12 P-13 Fdr 474 and re locate bonds UGOH @ P-13 | 76 | 90 | 3420 | 0.0038206 | 8.4901e-05
2012-11-01 08:00AM | 215589 | 4368 | Rural Short | augment lv mains and change poles | 51 | 510 | 26010 | 0.029056 | 5.6973e-05
2012-11-01 08:00AM | 217631 | SN1230 | Rural Short | INSTALL LIGHTNING ARRESTOR BRACKET ON AUTORECLOSER 89017 ON POLE 814889. | 14 | 240 | 3360 | 0.0037535 | 1.564e-05
2012-11-01 08:00AM | 218478 | M391 | Rural Short | LIMITED DISTRICT SWITCHINGTo alow staff to Retro fit Sub 11927 and 11504 Cawdor Rd Cawdor | 15 | 200 | 3000 | 0.0033514 | 1.6757e-05
2012-11-01 08:00AM | 217418 | 8693 | Urban | pole replacement x 4spike + id cable/ upgrade hv ugoh + sttj. | 57 | 560 | 31920 | 0.035658 | 6.3676e-05
2012-11-01 08:00AM | 217454 | UNC2 | Urban | 11kV OUTAGE TO REPLACE STR 37 38 39 FDR 7091 - 11kV OUT FOR CLEARANCE ONLY | 3 | 450 | 1350 | 0.0015081 | 3.3514e-06
2012-11-01 08:30AM | 215590 | L948 | Rural Short | Remove USL E574. Replace pole 159 with Auto LBS 90891 + pole | 19 | 390 | 7410 | 0.0082779 | 2.1225e-05
2012-11-01 08:30AM | 217721 | R218 | Rural Short | Replace X-pole 182 | 28 | 390 | 10920 | 0.012199 | 3.1279e-05
2012-11-01 08:30AM | 217890 | RBA2 | Rural Short | Replace Poles and Augment a Section of 11KV O/H Mains to 3 x 7/4.50 AAAC | 16 | 450 | 7200 | 0.0080433 | 1.7874e-05
2012-11-01 08:30AM | 217159 | APA2 | Urban | MandR HOLIC | 181 | 370 | 66970 | 0.074814 | 0.0002022
2012-11-01 08:30AM | 218446 | APB2 | Urban | REPLACE STREETLIGHT 4AG176 | 31 | 210 | 6510 | 0.0072725 | 3.4631e-05
2012-11-01 09:00AM | 216353 | WBC2 | Rural Short | Replace poles 3KC188 and 3KC190 | 16 | 360 | 5760 | 0.0064346 | 1.7874e-05
2012-11-01 09:00AM | 208590 | NA1266 | Urban | Replace TX and Retrofit S/S 50786Wallace St NOWRA. | 72 | 270 | 19440 | 0.021717 | 8.0433e-05
2012-11-01 09:00AM | 215641 | UNE2 | Urban | REMOVE ABS 88902 COMMISSION lbs 96483 AUGMENT HV MAINS FROM POLE 2R0301 TO 2R0289 | 113 | 216 | 24408 | 0.027267 | 0.00012623
2012-11-01 09:00AM | 218349 | 19815 | Urban | Rusty Column | 20 | 240 | 4800 | 0.0053622 | 2.2342e-05
2012-11-01 09:00AM | 218357 | 2822 | Urban | Quality of supply | 67 | 360 | 24120 | 0.026945 | 7.4847e-05
2012-11-02 01:00PM | 218376 | 19816 | Urban | Repair LV switchboard in column and Replace switch cover | 13 | 120 | 1560 | 0.0017427 | 1.4523e-05
2012-11-02 06:30AM | 217133 | S790 | Rural Short | RETRO SUB # 16474 | 4 | 340 | 1360 | 0.0015193 | 4.4685e-06
2012-11-02 08:00AM | 215397 | 27446 | Rural Short | Replace pole 21. HV and LV arms @ sub 5455. Replace all LV arms @ sub 2874 | 49 | 495 | 24255 | 0.027096 | 5.4739e-05
2012-11-02 08:00AM | 218604 | X877 | Rural Short | 48 Hr Pole | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2012-11-02 08:00AM | 215215 | 35530 | Urban | REPLACE TX AND RETERMINATE HV CABLE TO SWITCH F559 @ SUB 15514 ILLAWARRA DR ST CLAIR | 54 | 450 | 24300 | 0.027146 | 6.0324e-05
2012-11-02 08:00AM | 215310 | 4372 | Urban | Replace pole 666 with new pole 818307. | 86 | 460 | 39560 | 0.044193 | 9.6072e-05
2012-11-02 08:00AM | 215462 | S326 | Urban | Disco Existing UG cable at Sub 24179 sw 48062 and at OH mains between ABS73913 and ABS 46565. Terminate HV s/c and e cable at Sub 24179 from Sub 22277 sw 37168 | 38 | 305 | 11590 | 0.012947 | 4.2451e-05
2012-11-02 08:00AM | 217490 | 35315 | Urban | To change over LV mains/streetlights and remove old poles.(district switcher) | 294 | 390 | 57330 | 0.064044 | 0.00032843
2012-11-02 08:00AM | 217508 | R251 | Urban | Install new package sub 14154 and terminate new HV cable + Install new HV UG/OH @ pole J461 Olivet st Glenbrook. | 23 | 570 | 13110 | 0.014645 | 2.5694e-05
2012-11-02 08:00AM | 218138 | 5494 | Urban | LV ID Spike | 28 | 420 | 11760 | 0.013137 | 3.1279e-05
2012-11-02 08:00AM | 218669 | 8769 | Urban | Augment LV Circuit to facilitate the installation of pillars feeding new subdivision | 74 | 480 | 35520 | 0.03968 | 8.2667e-05
2012-11-02 08:30AM | 216804 | D813 | Rural Short | Break 11KV bonds @ Pole E100 Replace HV X-Arm @ Sub 1966 Remake 11KV Bonds @ Pole E100. | 1 | 390 | 390 | 0.00043568 | 1.1171e-06
2012-11-02 08:30AM | 217581 | MG1267 | Rural Short | HV Augmentation | 127 | 510 | 64770 | 0.072356 | 0.00014187
2012-11-02 08:30AM | 217882 | 57444 | Rural Short | REPLACE CONDEMNED POLE 291 WITH NEW POLE 841724 AND REPLACE CROSSARMS ON POLES 292 AND 293 | 17 | 235 | 3995 | 0.0044629 | 1.8991e-05
2012-11-02 08:30AM | 217921 | BK1288 | Rural Short | Retention LV conductors | 6 | 270 | 1620 | 0.0018097 | 6.7027e-06
2012-11-02 08:30AM | 218406 | L591 | Rural Short | REPLACE DAMAGED LV PILLAR 23397 | 20 | 390 | 7800 | 0.0087135 | 2.2342e-05
2012-11-02 08:30AM | 218430 | L591 | Rural Short | REPLACE CONDEMENED POLE 1 (PL408571)LIMITED SWITCHING REQUEST | 3 | 226 | 678 | 0.00075741 | 3.3514e-06
2012-11-02 08:30AM | 214980 | PKC2 | Urban | Replace Condemned Pole | 1 | 270 | 270 | 0.00030162 | 1.1171e-06
2012-11-02 08:30AM | 216143 | DP1206 | Urban | REMOVE ABS 71256 and INSTALL LBS 96214 RETRO SUB 40641 and REPLACE ABS 72899 | 241 | 330 | 79530 | 0.088845 | 0.00026923
2012-11-02 08:30AM | 217473 | 3166 | Urban | Stand P-12 P-13 Fdr 474 and re locate bonds UGOH @ P-13 | 76 | 450 | 17100 | 0.019103 | 8.4901e-05
2012-11-02 09:00AM | 215004 | NA1270 | Rural Short | Replace Steel HV MainsBurrier Rd BURRIER | 14 | 210 | 2940 | 0.0032843 | 1.564e-05
2012-11-02 09:00AM | 217238 | BDF2 | Rural Short | Replace poles.Install HV USL. | 25 | 360 | 9000 | 0.010054 | 2.7928e-05
2012-11-02 09:00AM | 217421 | X802 | Rural Short | RETRO FIT SUB 15679 (NOT A SWER SUB) | 19 | 269 | 5111 | 0.0057096 | 2.1225e-05
2012-11-02 09:00AM | 216400 | HBB2 | Urban | Replace pole 3JY479 | 1 | 180 | 180 | 0.00020108 | 1.1171e-06
2012-11-02 09:00AM | 218371 | 8685 | Urban | Repair LV cable fault in column | 16 | 240 | 3840 | 0.0042897 | 1.7874e-05
2012-11-02 09:00AM | 218374 | 19816 | Urban | Repair LV switch board in column | 10 | 180 | 1800 | 0.0020108 | 1.1171e-05
2012-11-02 09:00AM | 218636 | DP1206 | Urban | REPLACE LEAKING TX @ DS 41761 | 58 | 315 | 18270 | 0.02041 | 6.4793e-05
2012-11-02 09:30AM | 218427 | D823 | Urban | Replace rusted column | 4 | 150 | 600 | 0.00067027 | 4.4685e-06
2012-11-02 11:00AM | 217567 | GV1223 | Urban | Reconfigure jib arm and droppers at sub 3269 and augment one bay of LV mains. | 5 | 180 | 900 | 0.0010054 | 5.5856e-06
2012-11-02 12:00AM | 209984 | BDD2 | Urban | MandR Holec switchgear @ S/S 50515. | 45 | 235 | 10575 | 0.011814 | 5.027e-05
2012-11-03 08:00AM | 215346 | R215 | Urban | To Replace Existing HV S/Gear with CFC Safelink @ Sub11591Install new HV cable and Terminate @ Sub11591 and Pole 145. | 164 | 420 | 68880 | 0.076947 | 0.00018321
2012-11-03 08:30AM | 217968 | C896 | Urban | Replace LV S/G in sub 7000 | 15 | 315 | 4725 | 0.0052784 | 1.6757e-05
2012-11-03 09:00AM | 215073 | HKE2 | Rural Short | Replace Regulator tanks @ 29005 | 81 | 207 | 16767 | 0.018731 | 9.0487e-05
2012-11-03 09:30AM | 217626 | CLA2 | Rural Short | Replace HV mains @ CX412 | 16 | 360 | 5760 | 0.0064346 | 1.7874e-05
2012-11-03 10:00AM | 206489 | B205 | Urban | Install hv pin for hv bonding purposes.+ replace bond. | 284 | 210 | 59640 | 0.066625 | 0.00031726
2012-11-03 11:00PM | 214087 | 49006 | Urban | HVSWGR MAINT | 24 | 325 | 3900 | 0.0043568 | 2.6811e-05
2012-11-04 06:00AM | 216667 | 35763 | Urban | (11kv) Fdr 497 Replace X P-81 and X P-83 | 6 | 660 | 3960 | 0.0044238 | 6.7027e-06
2012-11-04 07:00AM | 214520 | 8622 | Urban | HV SWGR MandR @ SUB 22376 | 1 | 195 | 195 | 0.00021784 | 1.1171e-06
2012-11-04 07:00AM | 215307 | 17061 | Urban | RETROFIT + TX CHANGE SUB 8078 | 3 | 230 | 690 | 0.00077081 | 3.3514e-06
2012-11-04 07:00AM | 217800 | 17038 | Urban | Change poles 385 J387 391 change cast iron pothead pole 391. Remove 1 span11kV OH Pole 30075 - 299. Augment 11kV from LB89473 - pole 385 | 153 | 20 | 3060 | 0.0034184 | 0.00017092
2012-11-04 08:00AM | 216419 | 25783 | Urban | Remove 1 x poleInstall:1 x pole and HV UGOH HV UG cable | 1 | 450 | 450 | 0.0005027 | 1.1171e-06
2012-11-04 08:00AM | 217512 | L537 | Urban | Remove redundant OH mains and equipment | 30 | 360 | 10800 | 0.012065 | 3.3514e-05
2012-11-04 09:30AM | 217029 | B212 | Urban | EXCERCISE HV C/BREAKER @ SUB 22429 | 4 | 0 | 0 | 0 | 4.4685e-06
2012-11-05 08:00AM | 218152 | 8634 | Rural Short | Augment HV mains to 80mm CCT and install new LBS 79863. | 220 | 510 | 112200 | 0.12534 | 0.00024577
2012-11-05 08:00AM | 218817 | 8634 | Rural Short | Augment HV mains to 80mm CCT and install new LBS 79863. | 220 | 631 | 138820 | 0.15508 | 0.00024577
2012-11-05 08:00AM | 215573 | D828 | Urban | Allow staff to remove ABS A816 and pole.erect new pole with LBS 90848. | 26 | 510 | 13260 | 0.014813 | 2.9045e-05
2012-11-05 08:00AM | 217522 | 8767 | Urban | Augment 3 Bays of O/H conductor | 153 | 635 | 97155 | 0.10853 | 0.00017092
2012-11-05 08:00AM | 217850 | J496 | Urban | Replace poles | 154 | 525 | 80850 | 0.090319 | 0.00017204
2012-11-05 08:00AM | 217858 | WH1235 | Urban | REMOVE ABS + USL AND INSTALL LBS X 2 POL REPLACEMENT X 2 AUGMENT HV MAINS X 2 BAYS. | 286 | 505 | 144430 | 0.16135 | 0.0003195
2012-11-05 08:30AM | 216363 | 8801 | Rural Short | MandR ABS 57427 ABS 57428 ABS 57429 ABS 59500 | 23 | 425 | 9775 | 0.01092 | 2.5694e-05
2012-11-05 08:30AM | 217881 | MGE2 | Rural Short | Replace pole 3R1499 with new pole 847554. Augment OH mains. Retrofit substations 30201 and 32019 | 3 | 445 | 1335 | 0.0014914 | 3.3514e-06
2012-11-05 08:30AM | 217142 | 8680 | Urban | Replace road crossing service mains for street light install | 2 | 270 | 540 | 0.00060324 | 2.2342e-06
2012-11-05 10:00AM | 218661 | 35503 | Urban | maintenance | 17 | 240 | 4080 | 0.0045578 | 1.8991e-05
2012-11-05 12:00PM | 218658 | 20717 | Urban | maintenance | 15 | 240 | 3600 | 0.0040216 | 1.6757e-05
2012-11-05 12:30PM | 218652 | L544 | Urban | To Augment 3 bays OH to 150mm ABC | 24 | 210 | 5040 | 0.0056303 | 2.6811e-05
2012-11-06 08:00AM | 217420 | X877 | Rural Short | Allow staff to MandR poles and hardware. | 33 | 440 | 14520 | 0.016221 | 3.6865e-05
2012-11-06 08:00AM | 217792 | DP1284 | Rural Short | NEW PADS SUBSTATIONS | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2012-11-06 08:00AM | 217923 | NA1207 | Rural Short | RETENSION OH MAINS | 51 | 180 | 9180 | 0.010255 | 5.6973e-05
2012-11-06 08:00AM | 217941 | MGE2 | Rural Short | Replace 1 Pole Install 2 new Poles andAugment 4 Bays of 120mm CCT. | 26 | 410 | 10660 | 0.011908 | 2.9045e-05
2012-11-06 08:00AM | 217945 | 55354 | Rural Short | FIT SAFETY CHAIN TO SUB # 9009 | 4 | 165 | 660 | 0.0007373 | 4.4685e-06
2012-11-06 08:00AM | 218660 | 35693 | Rural Short | maintenance | 25 | 480 | 12000 | 0.013405 | 2.7928e-05
2012-11-06 08:00AM | 213955 | J495 | Urban | To MandR H/V S/Gear @ Sub 11390 Bennelong St Ruse. | 91 | 300 | 27300 | 0.030497 | 0.00010166
2012-11-06 08:00AM | 214686 | R251 | Urban | augment hv mains and remove dofs | 42 | 515 | 21630 | 0.024163 | 4.6919e-05
2012-11-06 08:00AM | 216364 | CT1225 | Urban | To allow staff to Retrofit Sub 12227 Badgally Rd Campbelltown | 5 | 215 | 1075 | 0.0012009 | 5.5856e-06
2012-11-06 08:00AM | 217963 | B205 | Urban | Augment 5 Bays of HV Mains and Replace Existing ABS. | 121 | 480 | 58080 | 0.064882 | 0.00013517
2012-11-06 08:00AM | 218437 | CT1225 | Urban | LIMITED DISTRICT SWITCHING-To allow staff to Retrofit Sub 11506 Springfield Rd Catherine Field | 1 | 240 | 240 | 0.00026811 | 1.1171e-06
2012-11-06 08:30AM | 217450 | B710 | Urban | Retension OH mains.Repostion to new UGOH pole. | 51 | 390 | 19890 | 0.02222 | 5.6973e-05
2012-11-06 09:00AM | 215393 | ULE2 | Rural Short | Replace Condemned pole 1GP004Woodburn Rd TERMEIL | 17 | 240 | 4080 | 0.0045578 | 1.8991e-05
2012-11-06 09:00AM | 217796 | W111 | Rural Short | Change low voltage pole 64. | 37 | 390 | 14430 | 0.01612 | 4.1333e-05
2012-11-06 09:00AM | 218358 | 2822 | Urban | Quality of supply | 54 | 360 | 19440 | 0.021717 | 6.0324e-05
2012-11-06 09:00AM | 218808 | 46774 | Urban | Repair Cable fault | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2012-11-06 09:30AM | 218420 | ULL2 | Rural Short | Replace condemned pole 1HK 068 River rd Tabourie | 94 | 300 | 28200 | 0.031503 | 0.00010501
2012-11-07 01:00PM | 218545 | 9030 | Urban | Maintenance | 18 | 180 | 3240 | 0.0036195 | 2.0108e-05
2012-11-07 08:00AM | 218064 | W114 | Rural Short | Replace poles | 16 | 610 | 9760 | 0.010903 | 1.7874e-05
2012-11-07 08:00AM | 215266 | L537 | Urban | REPLACE POLE 613 | 424 | 480 | 101760 | 0.11368 | 0.00047366
2012-11-07 08:00AM | 216508 | 19856 | Urban | Augment 4 bays of O/H HV mains to 3 x 120mm 22kv CCT. | 102 | 450 | 22950 | 0.025638 | 0.00011395
2012-11-07 08:00AM | 217862 | 49008 | Urban | Replace 2 poles and install new DOF. | 204 | 520 | 106080 | 0.1185 | 0.00022789
2012-11-07 08:00AM | 218502 | AZ1272 | Urban | Condemned Pole | 31 | 480 | 14880 | 0.016623 | 3.4631e-05
2012-11-07 08:00AM | 218547 | 19894 | Urban | Maintenance | 52 | 240 | 12480 | 0.013942 | 5.809e-05
2012-11-07 08:00AM | 218912 | 35519 | Urban | maintenance | 42 | 360 | 15120 | 0.016891 | 4.6919e-05
2012-11-07 09:00AM | 217156 | BYD2 | Rural Short | Replace pole 3AH009 and augment 1 span HV mains. | 9 | 280 | 2520 | 0.0028151 | 1.0054e-05
2012-11-07 09:00AM | 217199 | JBB2 | Rural Short | Replace ABS 75287 to new ABS 98009 Install new LBS 95800 Replace poles 4KH058 4KH057 4KH040 4KH068. Augment HV mains to 7/4.5 AAAC between pls 4KH058 and 4KH040. | 32 | 380 | 12160 | 0.013584 | 3.5748e-05
2012-11-07 09:00AM | 218447 | T831 | Rural Short | REPLACE LV CROSSARM | 51 | 360 | 18360 | 0.02051 | 5.6973e-05
2012-11-07 09:00AM | 218382 | S674 | Urban | Pole Change LV | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2012-11-07 09:00AM | 218383 | S674 | Urban | Pole change LV | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2012-11-07 09:00AM | 218397 | WH1294 | Urban | Replace pole 337 | 119 | 240 | 28560 | 0.031905 | 0.00013294
2012-11-07 09:00AM | 218609 | J495 | Urban | To MandR H/V S/Gear @ Sub 11426 Bellinger Rd Ruse./Repump cables per defect D908 | 86 | 220 | 18920 | 0.021136 | 9.6072e-05
2012-11-07 11:00AM | 218543 | 9027 | Urban | Maintenance | 38 | 210 | 7980 | 0.0089146 | 4.2451e-05
2012-11-08 08:00AM | 217089 | MGF2 | Rural Short | Replace two poles and two ABSs. Replace DOFs on sub 30858. | 279 | 440 | 122760 | 0.13714 | 0.00031168
2012-11-08 08:00AM | 215351 | 5869 | Urban | REPLACING POLE 2062 | 164 | 480 | 39360 | 0.04397 | 0.00018321
2012-11-08 08:00AM | 215593 | 4372 | Urban | change 2 poles and augment lv mains | 50 | 360 | 18000 | 0.020108 | 5.5856e-05
2012-11-08 08:00AM | 217422 | 8774 | Urban | Upgrade existing Padmount Sub 17680 to 1000kVA Tx and Augment LV Mains to facilitate the installation of a 1250A CB. | 35 | 705 | 24675 | 0.027565 | 3.9099e-05
2012-11-08 08:00AM | 217807 | NWD2 | Urban | REPLACE POLE AND INSTALL NEW LBS | 122 | 305 | 37210 | 0.041568 | 0.00013629
2012-11-08 08:00AM | 218034 | 8615 | Urban | Replace 5 poles; Remove ABS; Install LBS; Augment 5 Bays of HV mains. | 108 | 385 | 41580 | 0.04645 | 0.00012065
2012-11-08 08:00AM | 218622 | C820 | Urban | Remove:LV OH mains 4 x poles 2 x LV UGOH's | 42 | 480 | 20160 | 0.022521 | 4.6919e-05
2012-11-08 08:00AM | 218711 | 2819 | Urban | Augment 2 bays LV Bond in LV UGOH | 37 | 370 | 13690 | 0.015293 | 4.1333e-05
2012-11-08 08:30AM | 217016 | WBD2 | Rural Short | Replace Condemned Pole and Replace Transformer | 1 | 385 | 385 | 0.00043009 | 1.1171e-06
2012-11-08 08:30AM | 217452 | MVF2 | Rural Short | Trim Trees In Clearances | 12 | 450 | 5400 | 0.0060324 | 1.3405e-05
2012-11-08 08:30AM | 216896 | APF2 | Urban | Replace LAs pole 4GA266 | 5 | 210 | 1050 | 0.001173 | 5.5856e-06
2012-11-08 08:30AM | 217620 | DP1236 | Urban | MandR HOLIC S/S 43337 and RETRO S/S 40789 | 116 | 210 | 24360 | 0.027213 | 0.00012959
2012-11-08 08:45AM | 217478 | RBA2 | Rural Short | Relocate pole substation and replace condemned pole | 12 | 390 | 4680 | 0.0052281 | 1.3405e-05
2012-11-08 09:00AM | 218471 | X492 | Rural Long | REPLACE CONDEMENED POLE 466754(SUB POLE 16838) JOB 1PUT UP VIBRATION DAMPERS JOB 2LIMITED DISTRICT SWITICHING REQUEST | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2012-11-08 09:00AM | 217451 | BYC2 | Rural Short | Replace poles ( 9 10 11 and 13 )Bong Bong Rd BERRY. | 9 | 255 | 2295 | 0.0025638 | 1.0054e-05
2012-11-08 09:00AM | 217910 | KMB2 | Urban | REPLACE X POLE 4JC232 | 6 | 240 | 1440 | 0.0016087 | 6.7027e-06
2012-11-08 09:00AM | 218380 | S590 | Urban | Pole change LV | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2012-11-09 02:00AM | 218859 | FF1213 | Urban | relocate pillar 52601 | 17 | 300 | 5100 | 0.0056973 | 1.8991e-05
2012-11-09 06:30AM | 218243 | MVH2 | Rural Short | HV Switchgear MandR at Padmount Substation 22268 | 1 | 135 | 135 | 0.00015081 | 1.1171e-06
2012-11-09 07:00AM | 216610 | 3353 | Urban | INSTALL NEW 315 KVA P/M SUB 29645 CFC SAFELINK S/G CHANGE POLE 658 | 140 | 620 | 78740 | 0.087962 | 0.0001564
2012-11-09 08:00AM | 216634 | 35818 | Rural Short | Upgrade HV Hardware | 54 | 510 | 27540 | 0.030765 | 6.0324e-05
2012-11-09 08:00AM | 217456 | RWC2 | Rural Short | Trim Trees In Clearances | 2 | 405 | 810 | 0.00090487 | 2.2342e-06
2012-11-09 08:00AM | 217909 | X881 | Rural Short | Augment one bay of HV mains and install 40A DOF. | 52 | 465 | 24180 | 0.027012 | 5.809e-05
2012-11-09 08:00AM | 218023 | 35818 | Rural Short | Augment O/H HV Conductor. Pole change. | 45 | 615 | 27675 | 0.030916 | 5.027e-05
2012-11-09 08:00AM | 215727 | 1125 | Urban | Allow staff to augment section Of HV mains. | 83 | 450 | 37350 | 0.041724 | 9.2721e-05
2012-11-09 08:00AM | 216926 | 4372 | Urban | Lower UG/OH head pole 809964 replace USL 11238 with LBS 87600 and rewire LV at Sub 5458. | 44 | 495 | 21780 | 0.024331 | 4.9153e-05
2012-11-09 08:00AM | 218914 | 35530 | Urban | replace ragbolt | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2012-11-09 08:30AM | 217564 | L584 | Rural Short | RETRO FIT SUBS | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2012-11-09 08:30AM | 218325 | 8799 | Rural Short | MandR ABS 6810.Replace Pole 216 and USL 9835.Retro Replace LV XArms MDI and install Safety Chain @ Sub 6885.Install Safety Chain @ Sub 3682 | 155 | 365 | 56575 | 0.063201 | 0.00017315
2012-11-09 08:30AM | 217251 | WRA2 | Urban | INSTALL LBS 84496 and 84497 REMOVE ABS 71827 RELOCATE UGOH FOR WRA2 REMOVE HV MAINS BETWEEN POLES 775461 and 4CK321 | 226 | 420 | 94920 | 0.10604 | 0.00025247
2012-11-09 08:30AM | 218454 | L537 | Urban | Replace poles for future works | 29 | 390 | 11310 | 0.012635 | 3.2396e-05
2012-11-09 09:00AM | 218113 | GG1295 | Rural Short | Install new pole substation | 31 | 220 | 6820 | 0.0076188 | 3.4631e-05
2012-11-09 09:00AM | 214619 | SN1219 | Urban | Replace ABS 30917. | 1 | 205 | 205 | 0.00022901 | 1.1171e-06
2012-11-09 09:00AM | 219075 | 7972 | Urban | Defects | 22 | 360 | 7920 | 0.0088476 | 2.4577e-05
2012-11-09 09:30AM | 218865 | APC2 | Rural Short | LV STJ EXISTING CABLE ONTO NEW CABLE . | 11 | 390 | 4290 | 0.0047924 | 1.2288e-05
2012-11-09 12:00PM | 217866 | A098 | Rural Short | FIT SAFETY CHAIN TO SUB # 1166 | 23 | 180 | 4140 | 0.0046249 | 2.5694e-05
2012-11-10 08:00AM | 218253 | 25451 | Rural Short | NEW PADSUB | 20 | 464 | 9280 | 0.010367 | 2.2342e-05
2012-11-10 08:00AM | 218855 | UNG2 | Urban | REPLACE STREET LIGHT COLUMNS | 105 | 300 | 31500 | 0.035189 | 0.0001173
2012-11-10 08:00PM | 217529 | 3105 | Urban | AUGMENT 3 BAYS OF 11KV MAINS | 8 | 300 | 2400 | 0.0026811 | 8.937e-06
2012-11-10 08:30AM | 219173 | MVC2 | Rural Short | Tree trimming from pole 269327 to 3P0834 | 42 | 270 | 11340 | 0.012668 | 4.6919e-05
2012-11-10 09:00AM | 219066 | RWB2 | Rural Short | Limited district switchingTree trimming from pole 3XK405 to 200844 | 17 | 295 | 5015 | 0.0056024 | 1.8991e-05
2012-11-10 09:30AM | 219098 | BDA2 | Urban | REPLACE STREET LIGHT COLUMNS | 74 | 210 | 15540 | 0.01736 | 8.2667e-05
2012-11-10 12:00PM | 219109 | RWE2 | Rural Short | Limited district switchingTree triming from pole 3VJ484 to sub 30092 | 8 | 210 | 1680 | 0.0018768 | 8.937e-06
2012-11-10 12:01AM | 217722 | 53809 | Urban | EXERCISE HV CB - SUB 22828 | 2 | 729 | 1458 | 0.0016288 | 2.2342e-06
2012-11-11 06:30AM | 214814 | 46772 | Urban | HVSWGR MAINT | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2012-11-11 07:00AM | 216614 | CT1243 | Urban | Install 25KVA 3Ph Pole sub 32183 on 14/12 pole 868492. Remove pole 789832 | 4 | 540 | 2160 | 0.002413 | 4.4685e-06
2012-11-11 07:30AM | 218163 | 35763 | Urban | FIT SAFETY CHAIN TO SUB # 20923 | 5 | 150 | 750 | 0.00083784 | 5.5856e-06
2012-11-11 08:00AM | 211362 | 4857 | Urban | AUGMENT SECTION OF O/H 11KV MAINS | 24 | 540 | 12960 | 0.014478 | 2.6811e-05
2012-11-11 08:00AM | 216522 | SWD2 | Urban | Replace Condemned Pole 3D0641 | 6 | 330 | 7260 | 0.0081103 | 6.7027e-06
2012-11-11 09:00AM | 219062 | RWD2 | Rural Short | Limited district switchingTrim trees from pole 3J1232 to 3J1226 | 12 | 180 | 2160 | 0.002413 | 1.3405e-05
2012-11-11 09:30AM | 218915 | 35763 | Urban | maintenance | 2 | 180 | 360 | 0.00040216 | 2.2342e-06
2012-11-11 10:30AM | 218888 | M158 | Urban | Replace leaking transformers. | 1 | 330 | 330 | 0.00036865 | 1.1171e-06
2012-11-12 07:00AM | 215390 | R216 | Rural Short | New PMS29896. Associated request 215863 ( 33kv isolated safety ). | 2 | 510 | 1020 | 0.0011395 | 2.2342e-06
2012-11-12 07:00AM | 218334 | 17038 | Urban | Retension 33kv Poles J393-300088 Run OPGW poles 396 - 786163. Replace ABS F400 USL 7787 ABS A130 ABS 47331ABS 7786 | 17 | 600 | 10200 | 0.011395 | 1.8991e-05
2012-11-12 08:00AM | 217058 | S735 | Rural Short | Replace USL W988 with DOFs 94358 (8A).Replace HV xarm pole 359. | 20 | 280 | 5600 | 0.0062559 | 2.2342e-05
2012-11-12 08:00AM | 218063 | KC1284 | Rural Short | Install new ABS+ Replace 2 poles | 13 | 480 | 6240 | 0.0069708 | 1.4523e-05
2012-11-12 08:00AM | 217854 | J496 | Urban | Augment HV conductor | 31 | 465 | 14415 | 0.016103 | 3.4631e-05
2012-11-12 08:00AM | 218215 | 1959 | Urban | Augment 2 bays of HV mains to 7/4.50AAC. | 268 | 300 | 80400 | 0.089816 | 0.00029939
2012-11-12 08:30AM | 217552 | S786 | Rural Short | Replace Twin LV arms service arm links fuses mdi and rewire @ sub 2628 | 5 | 345 | 1725 | 0.001927 | 5.5856e-06
2012-11-12 08:30AM | 218190 | BWE2 | Rural Short | Replace Substation fuse xarm and fuses. Augment 8 bays of HV mains to CCT. | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2012-11-12 09:00AM | 214802 | J495 | Urban | To Re-Pump Hazymeyer Cable Box Termination @ SW-M661 In Sub 11436 Sirius St Ruse. | 76 | 180 | 13680 | 0.015282 | 8.4901e-05
2012-11-12 09:00AM | 219166 | CRF2 | Urban | REPLACE STREET LIGHT COLUMNS | 41 | 150 | 6150 | 0.0068703 | 4.5802e-05
2012-11-12 09:30AM | 219072 | BDA2 | Urban | Replace LV cable | 22 | 240 | 5280 | 0.0058984 | 2.4577e-05
2012-11-13 07:30AM | 218904 | APC2 | Rural Short | AUGMENT LV MAINS / | 24 | 540 | 12960 | 0.014478 | 2.6811e-05
2012-11-13 08:00AM | 217093 | 35693 | Rural Short | Remove ABS and install Auto LBS | 59 | 510 | 30090 | 0.033614 | 6.591e-05
2012-11-13 08:00AM | 217834 | 8635 | Rural Short | NEW 3 ph 100kva pole sub 29726 STAND 5 NEW POLES RUN 7/3.75 Al O/H HV MAINS | 11 | 420 | 4620 | 0.0051611 | 1.2288e-05
2012-11-13 08:00AM | 214855 | J510 | Urban | To MandR H/V S/Gear | 86 | 195 | 16770 | 0.018734 | 9.6072e-05
2012-11-13 08:00AM | 218075 | PKF2 | Urban | RETROFIT SUBSTATIONS AND REPLACE X ARMS | 134 | 450 | 33300 | 0.0372 | 0.00014969
2012-11-13 08:00AM | 218617 | 8693 | Urban | POLE REPLACEMENT X 4 | 99 | 580 | 57420 | 0.064145 | 0.00011059
2012-11-13 08:00AM | 218878 | A350 | Urban | Replace LV X-Arm | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2012-11-13 08:00AM | 219025 | 35001 | Urban | ID and Spike LV cable. Install a new LV pillar | 18 | 390 | 7020 | 0.0078422 | 2.0108e-05
2012-11-13 08:00AM | 219162 | 8679 | Urban | maintenance | 45 | 240 | 10800 | 0.012065 | 5.027e-05
2012-11-13 08:00AM | 219235 | AZ1272 | Urban | Defects | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2012-11-13 08:00AM | 219238 | AZ1272 | Urban | Defects | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2012-11-13 08:30AM | 217300 | L947 | Rural Short | Replace HV and LV arms @ sub 6851 | 40 | 360 | 14400 | 0.016087 | 4.4685e-05
2012-11-13 08:30AM | 217462 | RWD2 | Rural Short | Trim Trees In Clearances | 6 | 300 | 1800 | 0.0020108 | 6.7027e-06
2012-11-13 08:30AM | 217892 | MVF2 | Rural Short | Replace Condemed Poles 3XK568and 3K1912 Install Recloser Bypass Fuses and USL | 32 | 420 | 13440 | 0.015014 | 3.5748e-05
2012-11-13 08:30AM | 218491 | KVB2 | Rural Short | New PM substation and associated overhead and underground mains | 37 | 315 | 11655 | 0.01302 | 4.1333e-05
2012-11-13 08:30AM | 218159 | WRB2 | Urban | Replace PL1G0316 ABS 72931 with LBS 97096 replace pole 1G0314 and retro sub 42206 | 27 | 360 | 9720 | 0.010858 | 3.0162e-05
2012-11-13 09:00AM | 218054 | ULE2 | Rural Short | 1. Augment HV Conductors ( 1 to 6 ) 2. Remove Fuses 41946. 3. Remove ABS 41732. 4. Remove Capacitors from pole 1GT 017 @ Old Regulator site Princes Hwy Termeil. | 49 | 302 | 14798 | 0.016531 | 5.4739e-05
2012-11-13 09:00AM | 219080 | 9059 | Urban | Condemned Pole | 14 | 360 | 5040 | 0.0056303 | 1.564e-05
2012-11-13 09:00AM | 219083 | 5867 | Urban | Replace 7 Board | 28 | 240 | 6720 | 0.007507 | 3.1279e-05
2012-11-13 09:00AM | 219187 | C824 | Urban | Rusty Column | 6 | 120 | 720 | 0.00080433 | 6.7027e-06
2012-11-13 10:00AM | 219042 | R251 | Urban | PIN defect | 3 | 120 | 360 | 0.00040216 | 3.3514e-06
2012-11-13 11:00AM | 219190 | C824 | Urban | Rusty Column | 4 | 120 | 480 | 0.00053622 | 4.4685e-06
2012-11-14 05:30AM | 219233 | NA1218 | Urban | ISOLATE L/V CONSAC CABLE IN STREET LIGHT COLUMN | 36 | 120 | 4320 | 0.004826 | 4.0216e-05
2012-11-14 08:00AM | 217395 | 8634 | Rural Short | RETENSION RIVER X-INGS AND INSTALL SUPPORT STAYS AT POLES 782285 and 782287. | 5 | 480 | 2400 | 0.0026811 | 5.5856e-06
2012-11-14 08:00AM | 218073 | 5898 | Rural Short | Connect New Pole Sub 29081 | 1 | 510 | 510 | 0.00056973 | 1.1171e-06
2012-11-14 08:00AM | 214893 | J483 | Urban | To MandR H/V S/Gear @ Sub 13198 Stornoway Ave St Andrews | 75 | 300 | 22500 | 0.025135 | 8.3784e-05
2012-11-14 08:00AM | 214934 | 16660 | Urban | Stand pole adjacent to condemned pole 733 and changeover ABS | 53 | 480 | 25440 | 0.02842 | 5.9207e-05
2012-11-14 08:00AM | 217907 | 49008 | Urban | Augment 3 bays of HV mains. | 204 | 480 | 97920 | 0.10939 | 0.00022789
2012-11-14 08:00AM | 218227 | J491 | Urban | Replace 2 poles | 128 | 570 | 72960 | 0.081505 | 0.00014299
2012-11-14 08:00AM | 219365 | 5494 | Urban | LV Augmentation | 55 | 450 | 24750 | 0.027649 | 6.1442e-05
2012-11-14 08:00AM | 219422 | 1122 | Urban | Lower LV Arm | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2012-11-14 08:00AM | 219474 | AZ1272 | Urban | Condemned Pole | 26 | 480 | 12480 | 0.013942 | 2.9045e-05
2012-11-14 08:30AM | 217408 | 10290 | Rural Short | Replace pole 101 retro sub 4801 replace HV X-ams 91 and 96 | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2012-11-14 08:30AM | 218015 | BWH2 | Rural Short | Replace Hv Pole's and HV Augmentation | 183 | 480 | 87840 | 0.098128 | 0.00020443
2012-11-14 08:30AM | 218587 | T831 | Rural Short | REPLACE CONDEMNED POLE 310 WITH NEW POLE 877129 AND REPLACE POLE 321 WITH NEW POLE 877130 AND RPLACE 10KVA SUB WITH NEW 25KVA SUB | 8 | 420 | 3360 | 0.0037535 | 8.937e-06
2012-11-14 08:30AM | 214127 | B764 | Urban | MandR HVSWGR @ SUB 22448 | 72 | 270 | 19440 | 0.021717 | 8.0433e-05
2012-11-14 08:30AM | 217571 | 7962 | Urban | REPLACE CONDEMNED POLE 1379 | 15 | 360 | 5400 | 0.0060324 | 1.6757e-05
2012-11-14 08:30AM | 218610 | RVF2 | Urban | AUGMENT LV MAINS | 82 | 450 | 36900 | 0.041222 | 9.1604e-05
2012-11-14 09:00AM | 218989 | S743 | Rural Short | Replace/install poles for future works | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2012-11-14 09:00AM | 218379 | 16660 | Urban | Pole Change LV | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2012-11-14 09:00AM | 218993 | 25783 | Urban | Install LV pillars and streetlights | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2012-11-14 09:00AM | 219182 | B799 | Urban | Rusty Column | 7 | 120 | 840 | 0.00093838 | 7.8198e-06
2012-11-15 08:00AM | 217723 | X492 | Rural Long | REPLACE CONDEMNED POLES and INSTALL VIBRATION DAMPERS(NUMEROUS SPANS) | 50 | 450 | 22500 | 0.025135 | 5.5856e-05
2012-11-15 08:00AM | 217048 | 4368 | Rural Short | Replace condemned sub pole 25214 | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2012-11-15 08:00AM | 214924 | J465 | Urban | To MandR H/V S/Gear | 81 | 300 | 24300 | 0.027146 | 9.0487e-05
2012-11-15 08:00AM | 215596 | 4374 | Urban | Change 2 poles and Augment LV mains | 112 | 510 | 57120 | 0.06381 | 0.00012512
2012-11-15 08:00AM | 216745 | UNH2 | Urban | NEW SUBSTATION | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2012-11-15 08:00AM | 217687 | 7972 | Urban | REPLACE X - POLE SUB 3945 | 18 | 480 | 8640 | 0.0096519 | 2.0108e-05
2012-11-15 08:00AM | 217737 | 8686 | Urban | RETRO SUB 6948 | 52 | 300 | 15600 | 0.017427 | 5.809e-05
2012-11-15 08:00AM | 219239 | AZ1272 | Urban | Condemned Pole | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2012-11-15 08:00AM | 219621 | J496 | Urban | Repair Defects SUB 11156 | 31 | 540 | 16740 | 0.018701 | 3.4631e-05
2012-11-15 08:00AM | 219647 | 1122 | Urban | Lower LV Arm | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2012-11-15 08:00AM | 219669 | 5510 | Urban | REPLACE LOW VOLTAGE SWITCHGEAR @ SUB 16405 EXPLORERS WAY ST CLAIR | 40 | 480 | 19200 | 0.021449 | 4.4685e-05
2012-11-15 08:30AM | 218680 | RBA2 | Rural Short | Replace Poles and Augment a Section of 11KV O/H Mains to 3 x 7/4.50 AAAC | 16 | 450 | 7200 | 0.0080433 | 1.7874e-05
2012-11-15 08:30AM | 217138 | WBB2 | Urban | Replace Sub pole and Transformer Sub 40036 | 28 | 360 | 10080 | 0.011261 | 3.1279e-05
2012-11-15 08:30AM | 217674 | WRF2 | Urban | Replace ABS 70877 pole 4CP006 retro sub 41523 and sub 41524 | 30 | 360 | 10800 | 0.012065 | 3.3514e-05
2012-11-15 08:30AM | 218520 | 8615 | Urban | REPLACE 3 POLES | 161 | 480 | 77280 | 0.086331 | 0.00017986
2012-11-15 08:30AM | 219090 | SXA2 | Urban | REPLACE ONE BAY OF LV OH MAINS / | 8 | 420 | 3360 | 0.0037535 | 8.937e-06
2012-11-15 09:00AM | 219084 | S743 | Rural Short | Replace Poles | 7 | 360 | 2520 | 0.0028151 | 7.8198e-06
2012-11-15 09:00AM | 215432 | HKF2 | Urban | Job 1.Replace pole 1K0149.Job 2. Replace tx and retrofit sub 50603 | 155 | 330 | 51150 | 0.057141 | 0.00017315
2012-11-15 09:00AM | 218647 | NWD2 | Urban | REPLACE POLSE AND INSTALL LBS RETROFIT SUB | 156 | 510 | 79560 | 0.088878 | 0.00017427
2012-11-15 09:00AM | 219085 | 2822 | Urban | Quality of Supply | 61 | 360 | 21960 | 0.024532 | 6.8144e-05
2012-11-16 08:00AM | 218655 | 35693 | Rural Short | maintenance | 25 | 240 | 6000 | 0.0067027 | 2.7928e-05
2012-11-16 08:00AM | 218324 | 8762 | Urban | Install new pole and augment 2 bays of HV mains. | 57 | 540 | 30780 | 0.034385 | 6.3676e-05
2012-11-16 08:00AM | 218960 | UNG2 | Urban | REPLACE STREETLUGHT COLUMNS | 83 | 360 | 29880 | 0.03338 | 9.2721e-05
2012-11-16 08:00AM | 219491 | 5494 | Urban | LV Augmentation | 24 | 450 | 10800 | 0.012065 | 2.6811e-05
2012-11-16 08:00AM | 219530 | 68195 | Urban | Replace pole | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2012-11-16 08:30AM | 218505 | 27454 | Rural Short | Replace Type 1 LBS 94705 with Type 3 Auto LBS. | 14 | 420 | 5880 | 0.0065687 | 1.564e-05
2012-11-16 08:30AM | 219711 | BWH2 | Rural Short | Limited district switchingEmergency tree trimming 2 sites | 11 | 390 | 4290 | 0.0047924 | 1.2288e-05
2012-11-16 09:00AM | 217908 | KVA2 | Rural Short | Augment HV conductors to CCTMount Scanzi Rd KANGAROO VALLEY | 15 | 360 | 5400 | 0.0060324 | 1.6757e-05
2012-11-16 09:00AM | 218695 | R251 | Urban | Replace 2 service poles. | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2012-11-16 09:00AM | 219018 | BDE2 | Urban | Install New pole and Augment HV mainsEdwards Ave BOMADERRY. | 73 | 390 | 28470 | 0.031804 | 8.155e-05
2012-11-16 09:00AM | 219527 | 35569 | Urban | Replace Service Harness | 3 | 330 | 990 | 0.0011059 | 3.3514e-06
2012-11-16 09:30AM | 219906 | J469 | Urban | lv | 27 | 110 | 2970 | 0.0033178 | 3.0162e-05
2012-11-16 10:30AM | 219189 | C893 | Urban | Maintenance | 24 | 330 | 7920 | 0.0088476 | 2.6811e-05
2012-11-16 10:30AM | 219900 | M397 | Urban | lv | 15 | 240 | 3600 | 0.0040216 | 1.6757e-05
2012-11-16 12:00PM | 219454 | 35530 | Urban | maintenance | 7 | 270 | 1890 | 0.0021114 | 7.8198e-06
2012-11-17 01:00PM | 219444 | BDA2 | Urban | Replace street light columns | 95 | 120 | 11400 | 0.012735 | 0.00010613
2012-11-17 08:00AM | 218202 | 1 | Rural Short | Commence second attempt of commisisoning of new 11kV Generator and associated Transformer. | 127 | 610 | 77470 | 0.086543 | 0.00014187
2012-11-17 08:00AM | 218645 | MVE2 | Rural Short | Install New PM Sub | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2012-11-17 08:00AM | 218843 | 25744 | Rural Short | Replace Poles 171 and 173 and install stay poles in preparation for second outage where mains will be redirected underground. | 13 | 480 | 6240 | 0.0069708 | 1.4523e-05
2012-11-17 09:00AM | 218841 | MVD2 | Rural Short | Trim Trees Near Hv Conductors | 6 | 300 | 1800 | 0.0020108 | 6.7027e-06
2012-11-17 09:00AM | 217847 | BDA2 | Urban | Replace ABS 30239 with New LBS 96755Page Ave NORTH NOWRA. | 108 | 330 | 35640 | 0.039814 | 0.00012065
2012-11-17 09:30AM | 219439 | BDA2 | Urban | Replace street light columns | 29 | 180 | 5220 | 0.0058314 | 3.2396e-05
2012-11-18 07:00AM | 214527 | S604 | Urban | MandR HVSWGR @ SUB 26549 and fix phase roll on LV | 84 | 300 | 12600 | 0.014076 | 9.3838e-05
2012-11-18 08:00AM | 216701 | 46477 | Urban | Retro Sub 5517 Replace LV X-Arms Rewire 2x120 HV X-Arms. Run 1 Bay 150mm LVABC Remove and Replace LV X-Arm's @ Pole 734. | 15 | 450 | 6750 | 0.0075406 | 1.6757e-05
2012-11-18 08:30AM | 216989 | A049 | Rural Short | Replace pole 791 and install SPS 29587 (200kva). (Job to run over 3 days) | 19 | 390 | 7410 | 0.0082779 | 2.1225e-05
2012-11-18 08:30AM | 217874 | 35980 | Rural Short | RefurbishRetro and Replace TX @ Sub 10259 | 14 | 420 | 5880 | 0.0065687 | 1.564e-05
2012-11-19 07:00AM | 218968 | 17038 | Urban | Retension 33kv Poles J393-300088 Run OPGW poles 396 - 786163. Replace ABS F400 USL 7787 ABS A130 ABS 47331ABS 7786 | 17 | 600 | 10200 | 0.011395 | 1.8991e-05
2012-11-19 08:00AM | 217227 | C814 | Rural Short | augment 1 bay of hv mains and change 2 poles and install new DOF's | 6 | 450 | 10350 | 0.011562 | 6.7027e-06
2012-11-19 08:00AM | 217227 | C814 | Rural Short | augment 1 bay of hv mains and change 2 poles and install new DOF's | 40 | 510 | 11730 | 0.013104 | 4.4685e-05
2012-11-19 08:00AM | 218400 | 3334 | Urban | Augment Hv Oh Mains and Pole to be Replaced | 48 | 480 | 23040 | 0.025738 | 5.3622e-05
2012-11-19 08:00AM | 218472 | HBB2 | Urban | AUGMENT MAINS | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2012-11-19 08:30AM | 217555 | MVC2 | Rural Short | Augment HV Mains | 71 | 480 | 34080 | 0.038071 | 7.9316e-05
2012-11-19 08:30AM | 218577 | 35816 | Rural Short | ABS Maintenance on SW 41121 | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2012-11-19 12:00PM | 219705 | 1952 | Urban | Bond in LV UGOH @Sub 2701 | 3 | 120 | 360 | 0.00040216 | 3.3514e-06
2012-11-20 08:00AM | 216041 | S738 | Rural Short | HV retro sub 4568. Muscios Lane Glenorie | 12 | 480 | 5760 | 0.0064346 | 1.3405e-05
2012-11-20 08:00AM | 217725 | 8711 | Rural Short | REPLACE COND POLE 179 | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2012-11-20 08:00AM | 217483 | R253 | Urban | Install new auto recloser and remove USL | 306 | 510 | 156060 | 0.17434 | 0.00034184
2012-11-20 08:00AM | 218524 | WH1235 | Urban | Replace 3 x Poles. Install new ABS and DOF's. Remove USL's. Augment 3 x Bays of HV Mains. | 286 | 540 | 154440 | 0.17253 | 0.0003195
2012-11-20 08:00AM | 219486 | J483 | Urban | To MandR H/V S/Gear @ Sub 13198 Stornoway Ave St Andrews | 75 | 300 | 22500 | 0.025135 | 8.3784e-05
2012-11-20 08:30AM | 217970 | BLA2 | Rural Short | Removal of a tree by council and retrofit Sub 40126 | 51 | 420 | 21420 | 0.023929 | 5.6973e-05
2012-11-20 08:30AM | 218439 | L941 | Rural Short | Replace condemned poles 138 139 and 140 | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2012-11-20 08:30AM | 219058 | L591 | Rural Short | REPLACE SUB POLE 14909 WITH NEW 25KVA SUB 29746 AND INSTALL NEW POLES 856408856410856412 AND INSTALL NEW ABS 93051 | 8 | 420 | 3360 | 0.0037535 | 8.937e-06
2012-11-20 08:30AM | 217109 | SHD2 | Urban | REPLACE ABS 71818 TO NEW LBS 96925 REPLACE X PLs 1D0458 1D0455RETRO FIT SUBS 41216 40898 42082 41825 | 183 | 360 | 65880 | 0.073596 | 0.00020443
2012-11-20 08:30AM | 217754 | WBB2 | Urban | Replace Condemned pole 2G0044 | 43 | 390 | 16770 | 0.018734 | 4.8036e-05
2012-11-20 08:30AM | 218194 | CRB2 | Urban | Replace pole augment mains | 108 | 390 | 42120 | 0.047053 | 0.00012065
2012-11-20 08:45AM | 218927 | KVB2 | Rural Short | Upgrade Substation 26469 | 14 | 390 | 5460 | 0.0060995 | 1.564e-05
2012-11-21 03:30PM | 219557 | 8634 | Rural Short | augment hv mains run lv mains and relocate sub pole install DOF's 94214. | 420 | 60 | 13260 | 0.014813 | 0.00046919
2012-11-21 08:00AM | 218994 | W164 | Rural Short | Replace 2x poles and install new pole sub 29827 and LBSw 93570 | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2012-11-21 08:00AM | 219557 | 8634 | Rural Short | augment hv mains run lv mains and relocate sub pole install DOF's 94214. | 22 | 510 | 112710 | 0.12591 | 2.4577e-05
2012-11-21 08:00AM | 215759 | AZ1272 | Urban | REPLACE COND POLE 331 | 21 | 540 | 11340 | 0.012668 | 2.346e-05
2012-11-21 08:00AM | 217677 | 25741 | Urban | RETROFIT SUB 8509 CAMDEN VALLEY WAY EDMONSON PARK | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2012-11-21 08:00AM | 218496 | J491 | Urban | Augment HV Conductor | 128 | 570 | 72960 | 0.081505 | 0.00014299
2012-11-21 08:00AM | 219367 | 25783 | Urban | Install:LV UG cable 1 x LV STJ LV pillars and SL | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2012-11-21 08:00AM | 219908 | 7972 | Urban | Defects | 22 | 420 | 9240 | 0.010322 | 2.4577e-05
2012-11-21 08:15AM | 217193 | WWF2 | Urban | Replace ABS 71453 71447 with LBS 95678 and 98018 Replace pole 2X0357 and Augment HV MainsRetrofit Sub 40544 | 12 | 420 | 42420 | 0.047388 | 1.3405e-05
2012-11-21 08:30AM | 217977 | BLA2 | Rural Short | REMOVAL of TREE by WOLLONGONG CITY COUNCIL | 52 | 420 | 21840 | 0.024398 | 5.809e-05
2012-11-21 08:30AM | 218593 | W163 | Rural Short | REPLACE 2 X17MTR CONDEMNED POLES | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2012-11-21 08:30AM | 218828 | CLD2 | Rural Short | Augment HV Conductors ( 17- 20 )Myola Rd MYOLA. | 104 | 450 | 46800 | 0.052281 | 0.00011618
2012-11-21 08:30AM | 218857 | MG1267 | Rural Short | Augment HV Mains | 149 | 480 | 71520 | 0.079896 | 0.00016645
2012-11-21 08:30AM | 217193 | WWF2 | Urban | Replace ABS 71453 71447 with LBS 95678 and 98018 Replace pole 2X0357 and Augment HV MainsRetrofit Sub 40544 | 285 | 390 | 39390 | 0.044003 | 0.00031838
2012-11-21 09:00AM | 219526 | 27187 | Urban | QOS | 35 | 360 | 12600 | 0.014076 | 3.9099e-05
2012-11-21 09:00AM | 219648 | 7976 | Urban | Replace LV XARM | 19 | 180 | 3420 | 0.0038206 | 2.1225e-05
2012-11-21 09:00AM | 219670 | B799 | Urban | REPLACE COLUMN | 7 | 120 | 840 | 0.00093838 | 7.8198e-06
2012-11-21 09:00AM | 219904 | B710 | Urban | Replace Rusty Columns | 39 | 360 | 14040 | 0.015684 | 4.3568e-05
2012-11-21 09:00AM | 220097 | 8676 | Urban | Replace S/L Column | 2 | 120 | 240 | 0.00026811 | 2.2342e-06
2012-11-21 10:00AM | 218221 | 27031 | Urban | Remove Sub 12114 and install new Sub 32310. | 1 | 240 | 240 | 0.00026811 | 1.1171e-06
2012-11-21 11:00AM | 219671 | 27202 | Urban | Replace Column | 19 | 120 | 2280 | 0.002547 | 2.1225e-05
2012-11-22 01:00PM | 219926 | RBB2 | Rural Short | REPLACE CONDEMNED POLE 3YH135 | 20 | 180 | 3600 | 0.0040216 | 2.2342e-05
2012-11-22 07:00AM | 219586 | D814 | Rural Short | Trans Mains to install new X Arms @ 13/14 and Re tension Mains across river | 36 | 660 | 23760 | 0.026543 | 4.0216e-05
2012-11-22 08:00AM | 218087 | L584 | Rural Short | Install 2 x new Poles and 1 x new LBSw 90893 and New pole Sub 29475 | 6 | 480 | 2880 | 0.0032173 | 6.7027e-06
2012-11-22 08:00AM | 218303 | A098 | Rural Short | RETRO and REPLACE HV X-ARM @ SUB # 12487 | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2012-11-22 08:00AM | 217157 | AZ1272 | Urban | REPLACE COND POLE 285 . REPLACE ABS 9525 WITH NEW ABS 97957. | 138 | 480 | 34080 | 0.038071 | 0.00015416
2012-11-22 08:00AM | 219014 | 8615 | Urban | Pole replacement + Augment 5 bays of hv mains. | 76 | 480 | 36480 | 0.040753 | 8.4901e-05
2012-11-22 08:00AM | 219789 | NWD2 | Urban | CONNECT 2 UGOHS AND REMOVE OH HV MAINS | 195 | 480 | 93600 | 0.10456 | 0.00021784
2012-11-22 08:30AM | 216436 | 8634 | Rural Short | Replace Tx - SUB 9741 | 2 | 270 | 540 | 0.00060324 | 2.2342e-06
2012-11-22 08:30AM | 218082 | 8802 | Rural Short | Replace ABS R738 with new Pole and Install new Pole and Auto LBS 91485 | 32 | 420 | 13440 | 0.015014 | 3.5748e-05
2012-11-22 08:30AM | 219154 | W163 | Rural Short | REPLACE HV CROSSARMS ON POLES 505459 AND 63 | 17 | 420 | 7140 | 0.0079762 | 1.8991e-05
2012-11-22 08:30AM | 218021 | M394 | Urban | Replace x-pole sub 11001 | 15 | 450 | 6750 | 0.0075406 | 1.6757e-05
2012-11-22 08:30AM | 218262 | CRB2 | Urban | Replace poles and augment mains | 76 | 420 | 31920 | 0.035658 | 8.4901e-05
2012-11-22 09:00AM | 218812 | RBC2 | Rural Short | Replace Condemned Pole 3YH027 and Retrofit DOFs at Sub 31402 | 47 | 330 | 15510 | 0.017327 | 5.2505e-05
2012-11-22 09:00AM | 215611 | 4374 | Urban | augment lv and change 2 poles | 115 | 390 | 44850 | 0.050103 | 0.00012847
2012-11-22 09:00AM | 219492 | 16653 | Urban | LV pole change | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2012-11-22 09:00AM | 219528 | 27187 | Urban | QOS | 67 | 360 | 24120 | 0.026945 | 7.4847e-05
2012-11-22 09:30AM | 219002 | CLA2 | Rural Short | Replace HV mains @ CX412 | 16 | 360 | 5760 | 0.0064346 | 1.7874e-05
2012-11-22 09:30AM | 217904 | J493 | Urban | To MandR HV S/Gear at Sub13002 Nattai St Ruse | 86 | 270 | 23220 | 0.02594 | 9.6072e-05
2012-11-22 09:30AM | 218743 | 27334 | Urban | To MandR H/V S/Gear and To Re- Pump Hazymeyer Cable Termination Box @ SW-K656 In Sub 13315To Re-Number H/V- S/G and SubstationFrancis St Minto. | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2012-11-22 09:30PM | 217192 | SHE2 | Urban | Replace pole 1C0057 and remove ABS 72819 replace pole 1C0338 and install new ABS 97307 replace pole 1C0061 and ABS 71837 replace pole 1C0058 install new pole and ABS 97306 and retro sub 40877 | 186 | 450 | 83700 | 0.093503 | 0.00020778
2012-11-23 08:00AM | 219743 | A096 | Rural Short | REPLACE HV X-ARM and TX and RE-WIRE @ SUB # 4674 | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2012-11-23 08:00AM | 213775 | 55885 | Urban | Augment HV OH mains 150 NMS | 258 | 510 | 65790 | 0.073495 | 0.00028822
2012-11-23 08:00AM | 216947 | 4372 | Urban | augment lv mains and carry out s/l work | 44 | 510 | 22440 | 0.025068 | 4.9153e-05
2012-11-23 08:00AM | 219024 | CRA2 | Urban | Augment 2 bays of LV OH Mains from open wire to 150mm ABC | 63 | 480 | 30240 | 0.033782 | 7.0379e-05
2012-11-23 08:00AM | 219117 | 8675 | Urban | Augment 1 bay of conductor + Install DOFs | 121 | 480 | 58080 | 0.064882 | 0.00013517
2012-11-23 08:00AM | 219898 | 35528 | Urban | Maintenance | 15 | 480 | 7200 | 0.0080433 | 1.6757e-05
2012-11-23 08:30AM | 216350 | 8633 | Rural Short | Replace ABS 344 with LBS 123159 | 6 | 420 | 2520 | 0.0028151 | 6.7027e-06
2012-11-23 08:30AM | 218326 | MGD2 | Rural Short | Augment high voltage mains from pole 3V0261 to ABS 50800 and install new DOFs at pole 3VO224. | 170 | 450 | 76500 | 0.08546 | 0.00018991
2012-11-23 08:30AM | 218911 | D813 | Rural Short | Replace pole 12 | 25 | 360 | 9000 | 0.010054 | 2.7928e-05
2012-11-23 08:30AM | 219231 | W163 | Rural Short | SWITCH FOR CONTRATORS TO ALLOW TREE TRIMMING | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2012-11-23 08:30AM | 217948 | HBB2 | Urban | 11kV O/H augment | 108 | 420 | 30240 | 0.033782 | 0.00012065
2012-11-23 08:30AM | 219322 | PKF2 | Urban | Replace Pole 3TG157 | 121 | 330 | 39930 | 0.044607 | 0.00013517
2012-11-24 07:00AM | 219436 | KYE2 | Urban | CHANGE OUT LV SUB END. | 1 | 450 | 450 | 0.0005027 | 1.1171e-06
2012-11-24 08:00AM | 219271 | 25744 | Rural Short | Redirect 2 Spans OH Mains UG to facilitate the construction of a new Rail overpass for the Leppington Railway Line. | 13 | 480 | 6240 | 0.0069708 | 1.4523e-05
2012-11-24 08:00AM | 219913 | 17037 | Urban | REPLACE POLE # 1682 / ABS # R126 - BASS ST COLYTON (PIN DEFECT # D313) | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2012-11-25 06:30AM | 216494 | 16662 | Urban | MandR HVSWGR @ SUB 6230 | 160 | 270 | 21600 | 0.02413 | 0.00017874
2012-11-25 07:30AM | 217250 | WL1296 | Urban | MandR HAZ SWITCHGEAR AT SUB 16305 AND SUB 16306 LYN PARADE PRESTONS | 47 | 540 | 25380 | 0.028353 | 5.2505e-05
2012-11-25 08:00AM | 219441 | X877 | Rural Short | Replace condemned p12 and associated defects | 31 | 420 | 13020 | 0.014545 | 3.4631e-05
2012-11-25 08:00AM | 217664 | 35307 | Urban | Outage to permit installation of fibre between poles A1611 and A2068 underneath Fdr 479. NOTE: Isolation points have been relocated as ABB Switchgear is 2005 Nameplate at sub 23290. | 2 | 540 | 44280 | 0.049466 | 2.2342e-06
2012-11-25 08:00AM | 218493 | B215 | Urban | Replace one pole. Upgrade UG cable and remove OH mains. | 8 | 540 | 4320 | 0.004826 | 8.937e-06
2012-11-25 08:30AM | 218563 | 35333 | Urban | CONNECT SCandE CABLE TO SW 69082 SUB 27114 BALLANDELLA RD PENDLE HILL | 2 | 390 | 780 | 0.00087135 | 2.2342e-06
2012-11-26 07:30AM | 218153 | 5867 | Urban | Change LV sw gear Sub 3094 Grove Pl Prospect | 86 | 510 | 43860 | 0.048997 | 9.6072e-05
2012-11-26 08:00AM | 216633 | W114 | Rural Short | HV Augmentation | 16 | 480 | 7680 | 0.0085795 | 1.7874e-05
2012-11-26 08:00AM | 216757 | W188 | Rural Short | Install new 12.5/8 poles 854922854923 and 854924. Install new 315KVA PM 28900 and 500KVA PM's 289012890228903 and 28904. | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2012-11-26 08:00AM | 218584 | X877 | Rural Short | To allow staff to Retro Sub 12204 Replace Pole Cap Pole 57 and Replace pole 55 at Sub 11052 Cut Hill Rd Cobbitty | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2012-11-26 08:00AM | 219273 | YYA2 | Rural Short | INSTALL NEW POLE SUBSTATION ON REPLACEMENT POLE | 5 | 480 | 2400 | 0.0026811 | 5.5856e-06
2012-11-26 08:30AM | 219381 | MVB2 | Rural Short | Install 2 New Poles Remove a Pole and Augment LV Mains | 74 | 420 | 31080 | 0.03472 | 8.2667e-05
2012-11-26 09:00AM | 219275 | T831 | Rural Short | REPLACE LV CROSSARM | 14 | 360 | 5040 | 0.0056303 | 1.564e-05
2012-11-26 12:30PM | 220169 | L582 | Rural Short | LIMITED DISTRICT SWITCHING REPAIR BROKEN TIE ON POLE 782796 | 7 | 120 | 840 | 0.00093838 | 7.8198e-06
2012-11-27 08:00AM | 219405 | GG1269 | Rural Short | Install New 4 feeder Switching Station. Install New HV UGOH cables. Install New Pole. | 24 | 480 | 11520 | 0.012869 | 2.6811e-05
2012-11-27 08:00AM | 219475 | HKD2 | Rural Short | REPLACE EXISTING ABS with NEW ABS 123208 on POLE 3HG095 | 14 | 420 | 5880 | 0.0065687 | 1.564e-05
2012-11-27 08:00AM | 216155 | 9032 | Urban | To install 2 New Padmount Substations 29857 and 29858 and also install section of high voltage cable and connect to the existing network | 41 | 540 | 22140 | 0.024733 | 4.5802e-05
2012-11-27 08:00AM | 218579 | T869 | Urban | To allow staff to Replace Condemned Pole #15 Sub 11044 Wedderburn Rd St Helens Park | 11 | 480 | 5280 | 0.0058984 | 1.2288e-05
2012-11-27 08:00AM | 219899 | 9032 | Urban | maintenance | 12 | 240 | 2880 | 0.0032173 | 1.3405e-05
2012-11-27 08:00AM | 220309 | 1112 | Urban | LV pole change over | 7 | 240 | 1680 | 0.0018768 | 7.8198e-06
2012-11-27 08:30AM | 217425 | BLA2 | Rural Short | Replace Condemned Pole 3PC114 | 59 | 270 | 15930 | 0.017796 | 6.591e-05
2012-11-27 08:30AM | 217668 | BYC2 | Rural Short | AUGMENT HV MAINS | 37 | 420 | 15540 | 0.01736 | 4.1333e-05
2012-11-27 08:30AM | 217954 | 35983 | Rural Short | Change USL pole J735 install new poles 848073 848074 852689 852690 and Augment high voltage mains from USL J735 to pole 91. Install new USL pole and by pass fuses at pole 852689 and remove USL 18605.ASP to install new pole substation 264910. | 18 | 450 | 4500 | 0.005027 | 2.0108e-05
2012-11-27 08:30AM | 218682 | 27446 | Rural Short | Replace ABS 5059 with Auto LBS 92936 and replace Pole 99. | 23 | 420 | 9660 | 0.010791 | 2.5694e-05
2012-11-27 08:30AM | 219076 | L591 | Rural Short | AUGMENT 5 BAYS 3 X 120MM CCT FROM POLE 367 TO ABS 93051 | 8 | 420 | 3360 | 0.0037535 | 8.937e-06
2012-11-27 08:30AM | 219401 | RBA2 | Rural Short | Replace Poles and Augment a Section of 11KV O/H Mains to 3 x 7/4.50 AAAC | 29 | 450 | 13050 | 0.014578 | 3.2396e-05
2012-11-27 08:30AM | 219955 | A346 | Urban | Condemned Pole | 2 | 390 | 780 | 0.00087135 | 2.2342e-06
2012-11-27 09:00AM | 209417 | BYE2 | Rural Short | Replace Condemned pole 2XV036 - S/S 50022Strongs Rd JASPERS BRUSH | 54 | 360 | 19440 | 0.021717 | 6.0324e-05
2012-11-27 09:00AM | 217954 | 35983 | Rural Short | Change USL pole J735 install new poles 848073 848074 852689 852690 and Augment high voltage mains from USL J735 to pole 91. Install new USL pole and by pass fuses at pole 852689 and remove USL 18605.ASP to install new pole substation 264910. | 2 | 420 | 4200 | 0.0046919 | 2.2342e-06
2012-11-27 09:00AM | 219673 | BDF2 | Rural Short | REPLACE POLE 1TY026 REPLACE POLE 1TY038 and INSTALL NEW SUB 32303 REMOVE SUB 50201 | 38 | 360 | 9000 | 0.010054 | 4.2451e-05
2012-11-27 09:00AM | 219495 | S598 | Urban | LV pole change | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2012-11-27 09:30AM | 213925 | ULE2 | Rural Short | REPLACE CONDEMNED POLES 1GD005 and 1GD007 TERMEIL | 12 | 270 | 3240 | 0.0036195 | 1.3405e-05
2012-11-27 09:30AM | 219673 | BDF2 | Rural Short | REPLACE POLE 1TY026 REPLACE POLE 1TY038 and INSTALL NEW SUB 32303 REMOVE SUB 50201 | 12 | 330 | 8250 | 0.0092162 | 1.3405e-05
2012-11-27 12:00PM | 220290 | 5498 | Urban | LV Change over | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2012-11-28 08:00AM | 217542 | S743 | Rural Short | Replace Pole and install LBS 92894 Replace USL 6743 with ABS 92895 Remove C242 and Rebond | 27 | 480 | 12960 | 0.014478 | 3.0162e-05
2012-11-28 08:00AM | 219535 | HKA2 | Rural Short | REPLACE 2 POLES REPLACE DOF's 30121 with DOFs 88578 also AUGMENT 8 BAYS of HV MAINS | 32 | 540 | 17280 | 0.019304 | 3.5748e-05
2012-11-28 08:00AM | 219674 | MGC2 | Rural Short | Errect new sub 29703 and pole remove old sub 30801 and augment OH Mains to 80mm CCT | 61 | 480 | 29280 | 0.032709 | 6.8144e-05
2012-11-28 08:00AM | 220195 | L582 | Rural Short | REPLACE HV CROSSARM | 16 | 420 | 6720 | 0.007507 | 1.7874e-05
2012-11-28 08:00AM | 216169 | AZ1272 | Urban | REPLACE COND POLE 225 | 28 | 540 | 15120 | 0.016891 | 3.1279e-05
2012-11-28 08:00AM | 219266 | D845 | Urban | REPLACE CONDEMNED POLE SUB 4931 | 13 | 480 | 6240 | 0.0069708 | 1.4523e-05
2012-11-28 08:00AM | 219956 | 9030 | Urban | Maintenance | 19 | 240 | 4560 | 0.0050941 | 2.1225e-05
2012-11-28 08:00AM | 220069 | 35528 | Urban | replace column | 24 | 480 | 11520 | 0.012869 | 2.6811e-05
2012-11-28 08:00AM | 220111 | WWF2 | Urban | Install ABS Augment HV Mains Change poles 2X0386 2X0375 2X0374 and 2X0373 and Augment HV MainsRetrofit Subs 40532 40413 and 41453 | 292 | 420 | 122640 | 0.137 | 0.0003262
2012-11-28 08:30AM | 218118 | H745 | Rural Short | Augment High voltage mains from USL K790 to sub 12312. | 6 | 450 | 2700 | 0.0030162 | 6.7027e-06
2012-11-28 08:30AM | 218176 | L942 | Rural Short | Replace ABS 6559 with LBS 123026 | 27 | 420 | 11340 | 0.012668 | 3.0162e-05
2012-11-28 08:30AM | 219620 | RWB2 | Rural Short | Augment LV mains | 8 | 450 | 3600 | 0.0040216 | 8.937e-06
2012-11-28 08:30AM | 219736 | 46487 | Rural Short | Remove redundant stay wire @ sub 3665 | 11 | 150 | 1650 | 0.0018432 | 1.2288e-05
2012-11-28 08:30AM | 218833 | WRF2 | Urban | REPLACE HV ARM and RETRO SUB 41849 REPLACE LV ARM POLE 1C0486. | 89 | 330 | 29370 | 0.03281 | 9.9424e-05
2012-11-28 08:30AM | 218886 | C900 | Urban | Replace poles 229 and 874 Parkes ave Remove 1 bay of O/H HV MainsInstall new HV UG/OH on new pole 847833 and terminate new HV Cable @ Sw 81218 Sub28306. | 522 | 480 | 125280 | 0.13995 | 0.00058314
2012-11-28 09:00AM | 215426 | ULE2 | Rural Short | 1. Replace Condemned pole 1HJ099 2. Replace Condemned pole 1HJ085both at Murramurang Rd BAWLEY POINT | 12 | 330 | 3960 | 0.0044238 | 1.3405e-05
2012-11-28 10:00AM | 219036 | KMA2 | Urban | REMOVE ABS 71924 and INSTALL LBS 97932 | 146 | 270 | 39420 | 0.044037 | 0.0001631
2012-11-28 11:00AM | 219976 | C893 | Urban | maintenance | 42 | 300 | 12600 | 0.014076 | 4.6919e-05
2012-11-28 12:00PM | 219390 | A098 | Rural Short | FIT SAFETY CHAIN TO SUB # 1166 | 23 | 180 | 4140 | 0.0046249 | 2.5694e-05
2012-11-28 12:00PM | 220070 | A098 | Rural Short | maintenance | 21 | 180 | 3780 | 0.0042227 | 2.346e-05
2012-11-29 01:00PM | 219591 | BLC2 | Urban | Replace Condemned Pole 3PD705 | 73 | 120 | 8760 | 0.009786 | 8.155e-05
2012-11-29 08:00AM | 218105 | 35982 | Rural Short | Replace x-pole 77 | 6 | 420 | 2520 | 0.0028151 | 6.7027e-06
2012-11-29 08:00AM | 219943 | P608 | Rural Short | Tree lopping and defect rectification. | 6 | 450 | 2700 | 0.0030162 | 6.7027e-06
2012-11-29 08:00AM | 218842 | C897 | Urban | Augment 4 bays of HV mains and replace 1 pole | 146 | 540 | 78840 | 0.088074 | 0.0001631
2012-11-29 08:00AM | 219959 | 35571 | Urban | Condemned Pole | 6 | 420 | 2520 | 0.0028151 | 6.7027e-06
2012-11-29 08:00AM | 220163 | UNB2 | Urban | REMOVE CONDEMNED STREET LIGHT COLUMNS | 103 | 240 | 24720 | 0.027615 | 0.00011506
2012-11-29 08:00AM | 220343 | MR2206 | Urban | Spike/ ID LV cable | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2012-11-29 08:00AM | 220582 | 20717 | Urban | Maintenance | 15 | 480 | 7200 | 0.0080433 | 1.6757e-05
2012-11-29 08:30AM | 218839 | BWH2 | Rural Short | Replace Hv Pole's and HV Augmentation | 183 | 480 | 87840 | 0.098128 | 0.00020443
2012-11-29 08:30AM | 219320 | APC2 | Rural Short | PRE STAND POLE FOR REPLACEMENT | 11 | 360 | 3960 | 0.0044238 | 1.2288e-05
2012-11-29 08:30AM | 218438 | WRA2 | Urban | REPLACE S/S 41807 REMOVE ABS 68848 AUGMENT HV MAINS | 96 | 420 | 40320 | 0.045042 | 0.00010724
2012-11-29 08:30AM | 219962 | 7964 | Urban | Defects | 43 | 450 | 19350 | 0.021616 | 4.8036e-05
2012-11-29 09:00AM | 219687 | BDF2 | Rural Short | AUGMENT H/V CONDUCTORS FROM Pole 1VA023 TO Pole 1TY026 | 38 | 360 | 9000 | 0.010054 | 4.2451e-05
2012-11-29 09:00AM | 220100 | 19816 | Urban | Rusty Column | 17 | 180 | 3060 | 0.0034184 | 1.8991e-05
2012-11-29 09:00AM | 220312 | 16653 | Urban | LV pole change over | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2012-11-29 09:30AM | 219687 | BDF2 | Rural Short | AUGMENT H/V CONDUCTORS FROM Pole 1VA023 TO Pole 1TY026 | 12 | 330 | 8250 | 0.0092162 | 1.3405e-05
2012-11-29 09:30AM | 219967 | 35569 | Urban | Replace Service Harness | 3 | 300 | 900 | 0.0010054 | 3.3514e-06
2012-11-30 08:00AM | 216636 | 35818 | Rural Short | HV Augmentation | 70 | 480 | 33600 | 0.037535 | 7.8198e-05
2012-11-30 08:00AM | 218701 | 10286 | Rural Short | Replace USL 3654 with Recloser 95414 + pole Replace Poles 270 and 325634. | 35 | 480 | 16800 | 0.018768 | 3.9099e-05
2012-11-30 08:00AM | 216952 | 4372 | Urban | augment lv mains | 17 | 510 | 8670 | 0.0096854 | 1.8991e-05
2012-11-30 08:00AM | 219768 | 8615 | Urban | Replace one pole and install DOFs | 99 | 480 | 47520 | 0.053086 | 0.00011059
2012-11-30 08:00AM | 220404 | A314 | Urban | Rectify Defects | 67 | 420 | 28140 | 0.031436 | 7.4847e-05
2012-11-30 08:15AM | 218218 | 25782 | Urban | To install new poles.Retension OH HV/LV mains.Remove OH HV/LV mains | 10 | 465 | 4650 | 0.0051946 | 1.1171e-05
2012-11-30 08:30AM | 218677 | P608 | Rural Short | Change poles 22 23 remove USL pole P005 and install LBS 86795.. | 28 | 450 | 12600 | 0.014076 | 3.1279e-05
2012-11-30 08:30AM | 219290 | WBD2 | Rural Short | Replace Condemned Pole 2D0292 | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2012-11-30 08:30AM | 219762 | L582 | Rural Short | REPLACE CONEMNED POLE 175(PL408855) SUNSHINE VALLEYRETRO FIT SUB 14673 HALF WAY HOUSE | 8 | 390 | 3120 | 0.0034854 | 8.937e-06
2012-11-30 09:00AM | 219094 | HKD2 | Rural Short | Isolate HV Conductors to allow removal of tree.Edendale St WOOLLAMIA. | 84 | 330 | 27720 | 0.030967 | 9.3838e-05
2012-11-30 09:00AM | 219228 | HKA2 | Rural Short | Replace Pole 2DX081 | 5 | 240 | 1200 | 0.0013405 | 5.5856e-06
2012-11-30 09:00AM | 218200 | UNE2 | Urban | REPLACE POLES and AUGMENT HV MAINS BETWEEN POLES 871357 871358 and REMOVE ABS 70757 and COMMISSION ABS 96509 | 114 | 360 | 39240 | 0.043836 | 0.00012735
2012-11-30 09:30AM | 220561 | BWH2 | Rural Short | Install new POA pole adjacent to pole 3P0343 | 36 | 210 | 7560 | 0.0084454 | 4.0216e-05
2012-11-30 10:00AM | 220721 | APB2 | Urban | REMOVE RUSTED STREET LIGHT | 29 | 60 | 1740 | 0.0019438 | 3.2396e-05
2012-11-30 11:00AM | 220583 | 8679 | Urban | Maintenance | 45 | 300 | 13500 | 0.015081 | 5.027e-05
2012-12-01 04:30PM | 219691 | 20725 | Urban | CONNECT TO THE NETWORK NEW PAD SUBS 2982029833REMOVE ABS 93018 INSTALL NEW ABS 94567 | 72 | 60 | 4320 | 0.004826 | 8.0433e-05
2012-12-01 06:30AM | 219691 | 20725 | Urban | CONNECT TO THE NETWORK NEW PAD SUBS 2982029833REMOVE ABS 93018 INSTALL NEW ABS 94567 | 72 | 60 | 4320 | 0.004826 | 8.0433e-05
2012-12-01 07:00AM | 219435 | 19857 | Urban | Remove existing Pole Sub and asociated pole then replace pole 2 and connect new 22kV pad sub Via HV UGOH | 4 | 600 | 2400 | 0.0026811 | 4.4685e-06
2012-12-01 08:00AM | 219349 | UNH2 | Urban | Replace poles + Augment HV conductor.Install new LBS | 147 | 530 | 77910 | 0.087035 | 0.00016422
2012-12-01 09:30AM | 219143 | BYD2 | Rural Short | Augment HV ConductorsBryces Rd FAR MEADOW. | 9 | 360 | 3240 | 0.0036195 | 1.0054e-05
2012-12-02 06:00AM | 217353 | RS1236 | Urban | SEE ATTACHED DESCRIPTION | 33 | 600 | 19800 | 0.022119 | 3.6865e-05
2012-12-02 06:00AM | 218919 | 6421 | Urban | REPLACE CAST IRON POT HEAD POLE 2043 AND REPLACE TWO 2004 SAFELINK H/V SWITCH GEAR SUB 7430 AND EARTH BOND CABLES CONNECTED TO CIRCUIT BREAKER 6421 MOOREBNK ZONENEWBRIDGE RD LIVERPOOLPOLE 2043 | 16 | 840 | 6720 | 0.007507 | 1.7874e-05
2012-12-02 06:00AM | 220117 | RS1203 | Urban | LV Augment | 13 | 600 | 7800 | 0.0087135 | 1.4523e-05
2012-12-02 06:30AM | 217844 | 49008 | Urban | HVSWGR MAINT | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2012-12-02 07:30AM | 217738 | 7977 | Urban | REPAIRS TO ABS 6394 and REPLACE SURGE DIVERTORS AT UG/OH POLE 2277 WOODPARK RD | 35 | 390 | 13650 | 0.015249 | 3.9099e-05
2012-12-02 08:00AM | 219616 | 35765 | Urban | x | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2012-12-02 08:00AM | 219726 | SWG2 | Urban | REPLACE UGOH POLE TEST AND COMMISION | 4 | 510 | 2040 | 0.0022789 | 4.4685e-06
2012-12-02 08:30AM | 218188 | UNC2 | Urban | Replace Sub pole 41692 | 27 | 390 | 10530 | 0.011763 | 3.0162e-05
2012-12-02 09:30AM | 217714 | A341 | Urban | EXERCISE HV CB'S @ SUB 22699 | 1 | 60 | 60 | 6.7027e-05 | 1.1171e-06
2012-12-03 08:00AM | 218083 | 27446 | Rural Short | stand poles | 4 | 510 | 2040 | 0.0022789 | 4.4685e-06
2012-12-03 08:00AM | 219095 | WH1235 | Urban | Replace 2 poles augment 2 bays of HV mains. | 98 | 480 | 47040 | 0.052549 | 0.00010948
2012-12-03 08:30AM | 219826 | MVB2 | Rural Short | Replace Poles Install New DOFs 89728 Augment 11KV O/H Mains and Retrofit DOFs at Sub 30215 | 214 | 450 | 96300 | 0.10758 | 0.00023906
2012-12-03 08:30AM | 220751 | 27446 | Rural Short | Replace ABS 5059 with Auto LBS 92936 and replace Pole 99. | 23 | 420 | 9660 | 0.010791 | 2.5694e-05
2012-12-03 08:30AM | 219730 | RVC2 | Urban | Replace ABS pole 70009 | 114 | 360 | 41040 | 0.045847 | 0.00012735
2012-12-03 09:00AM | 218020 | L941 | Rural Short | Commissioning to SCADA LBS89887. | 11 | 240 | 2640 | 0.0029492 | 1.2288e-05
2012-12-03 09:00AM | 220554 | SHD2 | Urban | REPLACE X POLE 1G0092 | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2012-12-03 10:00AM | 219921 | NN1233 | Urban | Correct HV cross defect D915 | 5 | 240 | 1200 | 0.0013405 | 5.5856e-06
2012-12-04 08:00AM | 218129 | KC1284 | Rural Short | Augment HV conductor | 44 | 570 | 25080 | 0.028017 | 4.9153e-05
2012-12-04 08:00AM | 218226 | S743 | Rural Short | To install/replace poles for future works.Replace pole 83 and USL A583 with ABS 91967 | 40 | 480 | 19200 | 0.021449 | 4.4685e-05
2012-12-04 08:00AM | 220569 | 25744 | Rural Short | Replace Condemned Pole | 10 | 420 | 4200 | 0.0046919 | 1.1171e-05
2012-12-04 08:00AM | 216798 | 5500 | Urban | PERFORM MandR ON HV SWITCHGEAR @ SUB # 21230 | 57 | 300 | 17100 | 0.019103 | 6.3676e-05
2012-12-04 08:00AM | 218507 | WL1236 | Urban | RETRO SUB 2938 MandR HV and LV ARMS | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2012-12-04 08:00AM | 219954 | 25783 | Urban | Install:LV UG cable LV pillars | 140 | 300 | 21000 | 0.02346 | 0.0001564
2012-12-04 08:00AM | 220811 | 1122 | Urban | Erect UG cable | 3 | 240 | 720 | 0.00080433 | 3.3514e-06
2012-12-04 08:30AM | 216637 | 35818 | Rural Short | HV Augmentation | 8 | 420 | 3360 | 0.0037535 | 8.937e-06
2012-12-04 08:30AM | 219384 | 8636 | Rural Short | Replace pole 74 and retention mains. | 17 | 420 | 7140 | 0.0079762 | 1.8991e-05
2012-12-04 08:30AM | 219580 | 35418 | Rural Short | Replace all HV and LV arms @ pole 34.Replace HV arm @ pole 26 | 22 | 390 | 8580 | 0.0095849 | 2.4577e-05
2012-12-04 08:30AM | 219998 | MGD2 | Rural Short | Repair Defects on a section of OH Mains plus repair phasing on sub 30231 | 59 | 420 | 24780 | 0.027682 | 6.591e-05
2012-12-04 08:30AM | 220755 | GG1269 | Rural Short | Change Pillar 112390 to 3 way type and connect new cable and pillars 122577 and 122578 to pillar 112390 | 40 | 165 | 6600 | 0.007373 | 4.4685e-05
2012-12-04 08:30AM | 217868 | UNC2 | Urban | Replace poles and augment H.V mains | 54 | 420 | 22680 | 0.025336 | 6.0324e-05
2012-12-04 08:30AM | 219596 | SHE2 | Urban | REPLACE ABS 71876 | 153 | 360 | 55080 | 0.061531 | 0.00017092
2012-12-04 08:30AM | 220126 | BDB2 | Urban | The installation of OPGW for 33kV Feeder 7505 from Pole 1 to Pole 24. | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2012-12-04 09:00AM | 219476 | ULE2 | Rural Short | Augment HV Conductors ( 31 to 26 )Off Princes Hwy TERMEIL. | 49 | 330 | 16170 | 0.018064 | 5.4739e-05
2012-12-04 09:00AM | 219533 | CLD2 | Rural Short | Replace pole 3TT126 | 63 | 360 | 22680 | 0.025336 | 7.0379e-05
2012-12-04 09:00AM | 219784 | BK1251 | Rural Short | INSTALL VIBRATION DAMPERS | 11 | 360 | 3960 | 0.0044238 | 1.2288e-05
2012-12-04 09:00AM | 219809 | WBD2 | Rural Short | TAP CHANGE ON TX | 21 | 45 | 945 | 0.0010557 | 2.346e-05
2012-12-04 09:00AM | 220473 | 5496 | Urban | LV Pole Change | 3 | 180 | 540 | 0.00060324 | 3.3514e-06
2012-12-04 09:00AM | 220553 | 27187 | Urban | Quality of supply | 27 | 360 | 9720 | 0.010858 | 3.0162e-05
2012-12-04 09:30AM | 219901 | BDF2 | Rural Short | REPLACE POLES 1YT0011YT004 and 1YT005 | 13 | 330 | 4290 | 0.0047924 | 1.4523e-05
2012-12-04 11:30AM | 220817 | 77674 | Rural Short | LIMITED DISTRICT SWITCHING REPAIR STRANDED CONDUCTOR ADJ POLE 408 | 10 | 210 | 2100 | 0.002346 | 1.1171e-05
2012-12-05 08:00AM | 217540 | S738 | Rural Short | Replace pole 217 and install ABS 91973.Replace HV/LV xarms and remove USL 260 @ pole 219. | 41 | 480 | 19680 | 0.021985 | 4.5802e-05
2012-12-05 08:00AM | 219894 | R260 | Rural Short | REMOVE USL'S and INSTALL NEW SECTIOALISER Replace ABS and REPLACE POLE | 140 | 420 | 58800 | 0.065687 | 0.0001564
2012-12-05 08:00AM | 220254 | L591 | Rural Short | Connect to the network new 1ph pole sub 29976 | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2012-12-05 08:00AM | 218561 | R253 | Urban | Replace pole 321 with new pole 874492 and remove USL H043 replace pole 322 with new pole 874493 and install new Sectionaliser 96598 and remove 10 bays of SL conductor. | 126 | 480 | 60480 | 0.067563 | 0.00014076
2012-12-05 08:00AM | 219126 | WH1235 | Urban | Replace ABS with LBS. Replace one and install one new pole. | 115 | 480 | 55200 | 0.061665 | 0.00012847
2012-12-05 08:00AM | 219834 | 41537 | Urban | RE-WIRE REPLACE LV X-ARMS and BOX AND ARMS @ SUB # 7097 | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2012-12-05 08:00AM | 220754 | WL1236 | Urban | Replace Condemned Pole | 35 | 480 | 16800 | 0.018768 | 3.9099e-05
2012-12-05 08:00AM | 220832 | 46752 | Urban | Pole change | 30 | 450 | 13500 | 0.015081 | 3.3514e-05
2012-12-05 08:30AM | 218663 | MVH2 | Rural Short | Replace pole 3K0459 and ABS 50408 with a new LBS 92670 | 113 | 360 | 40680 | 0.045444 | 0.00012623
2012-12-05 08:30AM | 219837 | L941 | Rural Short | Connect LV ABC to distribution network.Pull out old open wire construction | 14 | 390 | 5460 | 0.0060995 | 1.564e-05
2012-12-05 08:30AM | 220187 | MVF2 | Rural Short | Trim Trees In Clearances | 12 | 450 | 5400 | 0.0060324 | 1.3405e-05
2012-12-05 08:30AM | 217991 | BLB2 | Urban | Replace Condemned Pole 3PJ011 and 3PD052and HV crossarms Pole 3PD049 | 122 | 420 | 51240 | 0.057241 | 0.00013629
2012-12-05 08:30AM | 220657 | SHK2 | Urban | REPLACE POLES and STAND NEW POLES | 37 | 420 | 15540 | 0.01736 | 4.1333e-05
2012-12-05 09:00AM | 213793 | NA1270 | Rural Short | Replace pole 1YP012. | 7 | 360 | 2520 | 0.0028151 | 7.8198e-06
2012-12-05 09:00AM | 219483 | W111 | Rural Short | Change low voltage pole 64 remove open wire mains between pole64 and 815971 remove open wire mains between 10725 and pole 64. | 37 | 360 | 13320 | 0.01488 | 4.1333e-05
2012-12-05 09:00AM | 219539 | M399 | Rural Short | SWITCHGEAR MAINTENANCE | 50 | 240 | 12000 | 0.013405 | 5.5856e-05
2012-12-05 09:00AM | 220107 | MVB2 | Rural Short | Isolate a Section of 11KV O/H mains to Allow for the Removal of Redundant Open Wire LV Mains | 74 | 360 | 26640 | 0.02976 | 8.2667e-05
2012-12-05 09:00AM | 220384 | 1112 | Urban | LV Pole change | 33 | 420 | 13860 | 0.015483 | 3.6865e-05
2012-12-05 09:00AM | 220815 | 68195 | Urban | Replace service harness | 3 | 300 | 900 | 0.0010054 | 3.3514e-06
2012-12-05 09:30AM | 220819 | 76225 | Rural Short | LIMITED DISTRICT SWITCHING INSTALL NEW POLE TO MAINTAIN CLEARANCES | 26 | 300 | 7800 | 0.0087135 | 2.9045e-05
2012-12-05 09:30AM | 219055 | D852 | Urban | LIMITED DISTRICT SWITCHING REQUEST RELOCATE HV MAINS TO REMOVE ENCROACHMENT | 23 | 300 | 6900 | 0.0077081 | 2.5694e-05
2012-12-05 11:00AM | 220099 | 8676 | Urban | Replace S.L Column | 2 | 180 | 360 | 0.00040216 | 2.2342e-06
2012-12-06 08:00AM | 215702 | 4368 | Rural Short | Install 7 bays of O/H HV mains to 3 x 150mm NMSABC. | 67 | 480 | 32160 | 0.035927 | 7.4847e-05
2012-12-06 08:00AM | 220202 | S788 | Rural Short | REPLACE LV X-ARM and HARDWARE @ SUB # 3394 | 27 | 480 | 12960 | 0.014478 | 3.0162e-05
2012-12-06 08:00AM | 220246 | T828 | Rural Short | INSTALL NEW POLE SUB 29913 | 11 | 480 | 5280 | 0.0058984 | 1.2288e-05
2012-12-06 08:00AM | 217639 | 17061 | Urban | HV retrofit. sub 437. Cricketers Arms Rd Prospect | 4 | 390 | 1560 | 0.0017427 | 4.4685e-06
2012-12-06 08:00AM | 219068 | A324 | Urban | Augment HV mains. | 266 | 540 | 143640 | 0.16046 | 0.00029715
2012-12-06 08:00AM | 220627 | 8769 | Urban | Augment LV Circuit to facilitate the installation of pillars feeding new subdivision | 74 | 480 | 35520 | 0.03968 | 8.2667e-05
2012-12-06 08:00AM | 220955 | CD1271 | Urban | Retro Sub 20032 and and replace associated HV hardware. TVI works. | 40 | 420 | 16800 | 0.018768 | 4.4685e-05
2012-12-06 08:30AM | 219086 | MG1219 | Rural Short | Replace Poles and Augment Hv Mains | 288 | 480 | 138240 | 0.15443 | 0.00032173
2012-12-06 08:30AM | 219642 | L946 | Rural Short | Replace USL pole 6283 | 21 | 390 | 8190 | 0.0091492 | 2.346e-05
2012-12-06 08:30AM | 219712 | DP1210 | Rural Short | NEW SUB POLE and NEW SUB No 29989 | 6 | 150 | 900 | 0.0010054 | 6.7027e-06
2012-12-06 08:30AM | 219800 | L591 | Rural Short | AUGMENT 5 BAYS 3 X 120MM CCT FROM POLE 367 TO ABS 93051 | 8 | 420 | 3360 | 0.0037535 | 8.937e-06
2012-12-06 08:30AM | 220133 | 8799 | Rural Short | Finsh off LV arms Links and fuses @ sub 6885 | 54 | 300 | 16200 | 0.018097 | 6.0324e-05
2012-12-06 08:30AM | 220217 | MGF2 | Rural Short | Augment HV Mains to 120mm CCT between Poles 3T1368 and 812014. Pole 863908 and 863904. Replace HV constructions on 4 Poles. | 448 | 480 | 215040 | 0.24023 | 0.00050047
2012-12-06 08:30AM | 220693 | MGD2 | Rural Short | Change LV crossarms at the cnr of King St Hilltop | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2012-12-06 08:30AM | 217895 | UNC2 | Urban | Replace poles augment mains and retro subs | 47 | 420 | 19740 | 0.022052 | 5.2505e-05
2012-12-06 08:30AM | 219138 | DP1206 | Urban | REPLACE POLE and ABS 72899 | 339 | 420 | 82740 | 0.092431 | 0.0003787
2012-12-06 08:30AM | 219724 | WRD2 | Urban | Replace pole 1A0416 ABS 74554 | 344 | 360 | 62280 | 0.069574 | 0.00038429
2012-12-06 08:30AM | 220038 | WRF2 | Urban | INSTALL LBS's 94766 94767 REMOVE ABS 84796 REMOVE HV BETWEEN POLES 4CK242 and 4CK240 CHANGE POLES 4CK344 and 4CK364 | 339 | 420 | 142380 | 0.15906 | 0.0003787
2012-12-06 09:00AM | 217427 | ULL2 | Rural Short | Install New LBS 97004 Replace X poles and Tree Trimming Beach st andRiver Rd TABOURIE LAKE | 233 | 330 | 76890 | 0.085895 | 0.00026029
2012-12-06 09:00AM | 220250 | BDF2 | Rural Short | REPLACE POLE 1TY025.Augment H/V conductors from pole 1TY026 to Poles 1TY018 | 38 | 360 | 9000 | 0.010054 | 4.2451e-05
2012-12-06 09:00AM | 220468 | S598 | Urban | LV Pole change | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2012-12-06 09:30AM | 220250 | BDF2 | Rural Short | REPLACE POLE 1TY025.Augment H/V conductors from pole 1TY026 to Poles 1TY018 | 12 | 330 | 8250 | 0.0092162 | 1.3405e-05
2012-12-07 06:00AM | 216789 | CJ1249 | Urban | ID and Spike HV cable between Sub 3067 sp36992 and Sub 3065 B004. Redirect cable from Sub 3065 to new cable from Sub 3066 sw73490. Terminate new cable sub 3066 sw73490. Redirect cable from sub 3067 sw 36992 to CB CJ1245 Bounty Ave Feeder. Test new feeder | 149 | 30 | 4470 | 0.0049935 | 0.00016645
2012-12-07 08:00AM | 216907 | A314 | Urban | MandR HV and LV POLES RECTIFY NETWORK DEFECTS WITHIN ISOLATION | 49 | 480 | 23520 | 0.026275 | 5.4739e-05
2012-12-07 08:00AM | 217811 | L534 | Urban | REPLACE POLE 967 SUB 467 and LV POLE 978 | 58 | 480 | 27840 | 0.031101 | 6.4793e-05
2012-12-07 08:00AM | 218815 | R253 | Urban | Install Sectionaliser 96575 remove USL H031 replace pole 156 with new pole 875823 and remove 1 bay of SL. | 220 | 480 | 104640 | 0.1169 | 0.00024577
2012-12-07 08:00AM | 221075 | B719 | Urban | Relocate 3 LV pillars for new Subdivision | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2012-12-07 08:30AM | 217568 | MVH2 | Rural Short | Replace Pole's and Augment 3 Bay's of Hv Oh Mains | 84 | 480 | 40320 | 0.045042 | 9.3838e-05
2012-12-07 08:30AM | 219683 | P608 | Rural Short | Remove poles 12 343138 311237 15 andInstall new poles 822263 822254 822255 822256 822257. ABS on pole 86794. | 9 | 450 | 4050 | 0.0045243 | 1.0054e-05
2012-12-07 08:30AM | 219787 | 4360 | Rural Short | Replace USL 8088 + pole | 6 | 390 | 2340 | 0.0026141 | 6.7027e-06
2012-12-07 08:30AM | 221127 | X473 | Rural Short | LIMITED DISTRICT SWITCHING REPAIR STRANDED CONDUCTOR ADJ POLE 47 | 3 | 180 | 540 | 0.00060324 | 3.3514e-06
2012-12-07 08:30AM | 220858 | S674 | Urban | LV Augment | 29 | 450 | 13050 | 0.014578 | 3.2396e-05
2012-12-07 09:00AM | 219951 | D814 | Rural Short | Maintain ABS | 19 | 240 | 4560 | 0.0050941 | 2.1225e-05
2012-12-07 09:00AM | 218112 | BLB2 | Urban | Replace Condemned Pole 3PD014 | 252 | 300 | 75600 | 0.084454 | 0.00028151
2012-12-07 09:00AM | 220938 | 35569 | Urban | Replace Service Harness | 3 | 330 | 990 | 0.0011059 | 3.3514e-06
2012-12-08 03:00PM | 219418 | A348 | Urban | INSTALL NEW MDI UNIT AND BLANK OFF EXISTING MDI'S AT SUB 28110 CENTRAL AVENUE CHIPPING NORTON | 1 | 150 | 150 | 0.00016757 | 1.1171e-06
2012-12-08 06:00PM | 216789 | CJ1249 | Urban | ID and Spike HV cable between Sub 3067 sp36992 and Sub 3065 B004. Redirect cable from Sub 3065 to new cable from Sub 3066 sw73490. Terminate new cable sub 3066 sw73490. Redirect cable from sub 3067 sw 36992 to CB CJ1245 Bounty Ave Feeder. Test new feeder | 149 | 30 | 4470 | 0.0049935 | 0.00016645
2012-12-08 06:30AM | 218256 | 49337 | Urban | HVSWGR MAINT | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2012-12-08 08:00AM | 220505 | X877 | Rural Short | CONNECT TO THE NETWORK NEW PAD SUB 28129 REMOVE SETION OF O/H MAINS.INSTALL NEW SECTION OF U/G MAINS. REMOVE POLE POLE SUB 1072 | 20 | 480 | 9600 | 0.010724 | 2.2342e-05
2012-12-08 08:00PM | 218978 | 7976 | Urban | REPLACE CONDEMNED POLE 1922 | 11 | 330 | 3630 | 0.0040551 | 1.2288e-05
2012-12-08 08:30AM | 220760 | APE2 | Urban | TEST CABLE FOR FAULT | 108 | 240 | 25920 | 0.028956 | 0.00012065
2012-12-08 09:00AM | 217771 | CLA2 | Rural Short | Connect and Commission New 315kVA Pad Sub 28312Greenwell Point Rd GREENWELL POINT. | 91 | 330 | 30030 | 0.033547 | 0.00010166
2012-12-09 08:00AM | 220520 | X877 | Rural Short | ROMOVE POLE SUB 7411REDIRECT SECTION OF O/H MAINS INSTALL NEW POLE 869261 NEW SECTION U/G MAINS AND PAD SUB 32203 | 7 | 390 | 2730 | 0.0030497 | 7.8198e-06
2012-12-09 08:00AM | 219694 | CRB2 | Urban | Replace poles | 395 | 370 | 146150 | 0.16327 | 0.00044126
2012-12-09 08:00AM | 219887 | WL1280 | Urban | Commission New 500kVA Padmount No. 29299. By ID/Spike and Jointing Inservice Cable between Pad Subs 25792 and 27492. | 2 | 440 | 880 | 0.00098307 | 2.2342e-06
2012-12-09 08:00AM | 220892 | ULF2 | Urban | Replace Condemned pole 2RR108 | 12 | 180 | 2160 | 0.002413 | 1.3405e-05
2012-12-09 08:30AM | 220488 | 35988 | Rural Short | Install ABS 97769 new poles 877889 877888 877893 and Remove USL 11406 | 13 | 332 | 4316 | 0.0048215 | 1.4523e-05
2012-12-09 12:30PM | 220895 | ULF2 | Urban | Replace Condemned pole 2RR101 | 1 | 150 | 150 | 0.00016757 | 1.1171e-06
2012-12-10 08:00AM | 219026 | 8798 | Rural Short | INSTALL NEW 315 KVA POLE SUB 29901 REMOVE EX SUB 2804 INSTALL NEW ABS 94515 RUN 50 mm Sq HV ABC CABLE | 62 | 450 | 27900 | 0.031168 | 6.9261e-05
2012-12-10 08:00AM | 220551 | ULE2 | Rural Short | REMOVE POLE SUB 19943 and REPLACE WITH 2X HV UGOHINSTALL NEW POLE SUB 32267 and ASSOCIATED O/H MAINS | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2012-12-10 08:00AM | 217160 | C891 | Urban | Replace one set of USLs. Augment one bay of HV mains. | 105 | 420 | 44100 | 0.049265 | 0.0001173
2012-12-10 08:00AM | 217536 | HBD2 | Urban | AUGMENT 11 KV MAINS | 2 | 810 | 1620 | 0.0018097 | 2.2342e-06
2012-12-10 08:00AM | 220336 | BDB2 | Urban | Run OPGW from Pole 26 to Pole 41 on 33kV Feeder FDR 7505 | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2012-12-10 08:00AM | 221293 | D831 | Urban | Replace Steeetlight column | 13 | 240 | 3120 | 0.0034854 | 1.4523e-05
2012-12-10 08:30AM | 220256 | MVF2 | Rural Short | Install new ABS 95303 install new section of 11KV O/H mains and remove a section of 11KV O/H Mains | 286 | 450 | 77400 | 0.086465 | 0.0003195
2012-12-10 09:00AM | 215428 | ULE2 | Rural Short | Replace Condemned poles 1HJ101Murramurang Rd BAWLEY POINT | 6 | 330 | 1980 | 0.0022119 | 6.7027e-06
2012-12-10 09:00AM | 219339 | HBB2 | Urban | Replace pole 3JY479 | 95 | 180 | 17100 | 0.019103 | 0.00010613
2012-12-10 10:00AM | 220613 | MR2232 | Urban | Install armour rods | 42 | 105 | 3045 | 0.0034016 | 4.6919e-05
2012-12-10 10:00AM | 221294 | D831 | Urban | Replace Streetlight Column | 16 | 240 | 3840 | 0.0042897 | 1.7874e-05
2012-12-11 08:00AM | 220959 | 27446 | Rural Short | Replace pole. | 4 | 510 | 2040 | 0.0022789 | 4.4685e-06
2012-12-11 08:00AM | 221131 | WL1236 | Urban | Replace Condemned Pole | 32 | 420 | 13440 | 0.015014 | 3.5748e-05
2012-12-11 08:00AM | 221268 | 6421 | Urban | establish new pillars | 15 | 480 | 7200 | 0.0080433 | 1.6757e-05
2012-12-11 08:30AM | 219802 | 8802 | Rural Short | Replace pole 155 | 26 | 360 | 9360 | 0.010456 | 2.9045e-05
2012-12-11 08:30AM | 216606 | J492 | Urban | HV Augmentation | 66 | 420 | 27720 | 0.030967 | 7.373e-05
2012-12-11 08:30AM | 219829 | SHH2 | Urban | REPLACE ABS 71842 WITH LBS 122208 | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2012-12-11 08:30AM | 220045 | SHB2 | Urban | REPLACE POLE 1D0142 ABS 71246 (PIN # D853) REPLACE TXR on SUB 41271 and REMOVE LIVE LINE LINKS ADJ to POLE 1D0139 | 95 | 360 | 34200 | 0.038206 | 0.00010613
2012-12-11 09:00AM | 218089 | 27446 | Rural Short | Replace 2 poles. | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2012-12-11 09:00AM | 221003 | NG1210 | Rural Short | Tree trimming required adj pole 841934 and K565. | 9 | 270 | 2430 | 0.0027146 | 1.0054e-05
2012-12-11 09:00AM | 219423 | BDD2 | Urban | Install New LBS 95349 ( Replaces ABS 30401 )Bunberra St BOMADERRY. | 14 | 360 | 5040 | 0.0056303 | 1.564e-05
2012-12-11 09:30AM | 219981 | ULE2 | Rural Short | RETRO-FIT SUB 72519 and REPAIR DEFECTS Wollombi Way MERRY BEACH | 52 | 300 | 15600 | 0.017427 | 5.809e-05
2012-12-12 08:00AM | 220581 | L591 | Rural Short | Connect to the network new Pad Sub 29314 via new section of U/G cable. | 9 | 480 | 4320 | 0.004826 | 1.0054e-05
2012-12-12 08:00AM | 217436 | B710 | Urban | Replace USL B131. Augment one bay of HV mains | 50 | 480 | 24000 | 0.026811 | 5.5856e-05
2012-12-12 08:00AM | 217855 | WL1292 | Urban | REPLACE COND POLE 446RETRO SUB 2944 | 35 | 480 | 16800 | 0.018768 | 3.9099e-05
2012-12-12 08:00AM | 218813 | R253 | Urban | Replace pole 334 with new pole 874759 and augment 3 bays of O/H HV mains to 3 x 150mm NMSABC. | 133 | 480 | 63840 | 0.071317 | 0.00014858
2012-12-12 08:00AM | 219814 | 7970 | Urban | REPLACE CONDEMNED POLE 1227 (USL 92197) | 112 | 450 | 50400 | 0.056303 | 0.00012512
2012-12-12 08:00AM | 220027 | SWC2 | Urban | Augment 7 Bays of HV Mains to 7/4.50AAC between Poles 3DO129 and 3DO138. Replace Poles 3DO129 [869196] 3DO130 [869209] and 3DO134[869208] Replace ABS 71481 with New ABS 95718 and DOF's on Sub 40589 | 126 | 480 | 60480 | 0.067563 | 0.00014076
2012-12-12 08:00AM | 221159 | UNG2 | Urban | REMOVE CONDEMNED STREET LIGHT COLUMNS | 69 | 240 | 16560 | 0.0185 | 7.7081e-05
2012-12-12 08:30AM | 219326 | APC2 | Rural Short | REPLACE POLE 4GR041 | 11 | 360 | 3960 | 0.0044238 | 1.2288e-05
2012-12-12 08:30AM | 219939 | R260 | Rural Short | REPLACE HV CROSSARM and POLE CAP | 1 | 390 | 390 | 0.00043568 | 1.1171e-06
2012-12-12 08:30AM | 220249 | RWA2 | Rural Short | Trim Trees Around Conductors | 9 | 450 | 4050 | 0.0045243 | 1.0054e-05
2012-12-12 08:30AM | 220294 | WBD2 | Rural Short | REPLACE CONDEMNED POLE 2G0433 | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2012-12-12 08:30AM | 220765 | PKD2 | Urban | REPLACE HV SWITCHGEAR | 38 | 420 | 15960 | 0.017829 | 4.2451e-05
2012-12-12 08:30AM | 220945 | X866 | Urban | Install new pillars | 11 | 330 | 3630 | 0.0040551 | 1.2288e-05
2012-12-12 09:00AM | 216937 | ULL2 | Rural Short | REPLACE 3 CONDEMNED POLES | 8 | 330 | 2640 | 0.0029492 | 8.937e-06
2012-12-12 09:00AM | 218463 | CLD2 | Rural Short | AUGMENT HV CONDUCTOR to CCT | 85 | 360 | 30600 | 0.034184 | 9.4955e-05
2012-12-12 09:00AM | 221118 | CJ1249 | Urban | Replace rusty column | 28 | 360 | 10080 | 0.011261 | 3.1279e-05
2012-12-12 09:00AM | 221247 | 19816 | Urban | Replace Rear Shroud | 3 | 90 | 270 | 0.00030162 | 3.3514e-06
2012-12-12 10:30AM | 221249 | 19816 | Urban | Replace switch cover | 32 | 90 | 2880 | 0.0032173 | 3.5748e-05
2012-12-13 07:30AM | 221073 | D830 | Urban | augment LV open wire to ABC | 124 | 510 | 63240 | 0.070647 | 0.00013852
2012-12-13 08:00AM | 219382 | 35695 | Rural Short | install 2 new poles | 5 | 480 | 2400 | 0.0026811 | 5.5856e-06
2012-12-13 08:00AM | 220534 | W163 | Rural Short | REPLACE CONDEMNED POLESHV CROSSARMS and REMAKE HV BONDS | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2012-12-13 08:00AM | 217377 | 35519 | Urban | REPLACE LOW VOLTAGE SWITCHGEAR AND MandR HV SWITCHGEAR @ SUB 8405 SHAKESPEAR DR ST CLAIR | 29 | 480 | 13920 | 0.01555 | 3.2396e-05
2012-12-13 08:00AM | 218110 | 49917 | Urban | Augment HV conductor | 153 | 480 | 73440 | 0.082041 | 0.00017092
2012-12-13 08:00AM | 220062 | R251 | Urban | Install new SafeLink CFC HV Sw/Gr @ Sub 17384 + Run new 240mm AL XLPE HV Cable from Sw94846 @ Sub 14154 and Terminate at Sw 94841 @ Sub 17384 and Transition Joint in HV cable. | 50 | 480 | 24000 | 0.026811 | 5.5856e-05
2012-12-13 08:00AM | 220826 | RVC2 | Urban | Replace pole and retrofit | 330 | 450 | 119250 | 0.13322 | 0.00036865
2012-12-13 08:00AM | 221090 | C900 | Urban | Repair defective Neon Indicators at sub # 26138 Albert St werrington | 142 | 180 | 25560 | 0.028554 | 0.00015863
2012-12-13 08:30AM | 218608 | BWE2 | Rural Short | HV Augmentation/ Hardware Upgrade | 36 | 480 | 17280 | 0.019304 | 4.0216e-05
2012-12-13 08:30AM | 220260 | MVD2 | Rural Short | Trim Trees Near Conductors | 20 | 450 | 9000 | 0.010054 | 2.2342e-05
2012-12-13 08:30AM | 220356 | RWB2 | Rural Short | Replace condemned poles 3J0474 and 3J0475 | 67 | 450 | 30150 | 0.033681 | 7.4847e-05
2012-12-13 08:30AM | 220444 | 8636 | Rural Short | MandR ABS 9883 | 6 | 240 | 1440 | 0.0016087 | 6.7027e-06
2012-12-13 08:30AM | 218654 | PCB2 | Urban | Replace ABS poles and Retro fit sub | 193 | 420 | 81060 | 0.090554 | 0.0002156
2012-12-13 08:30AM | 219411 | SHB2 | Urban | REPLACE X PLs 1D0363 1D0364 RETRO FIT DS 41851 | 80 | 360 | 28800 | 0.032173 | 8.937e-05
2012-12-13 08:30AM | 219985 | KMF2 | Urban | REPLACE ABS 78176 WITH LBS 97753 | 183 | 420 | 76860 | 0.085862 | 0.00020443
2012-12-13 09:00AM | 219715 | ULE2 | Rural Short | Augment HV Conductors ( 6 to 17 )Off Princes Hwy TERMEIL. | 49 | 330 | 16170 | 0.018064 | 5.4739e-05
2012-12-13 09:00AM | 220484 | BGA2 | Rural Short | Augment H/V Conductors - Roxbrough RdConnect H/V Tie and install ABS 95840 - Bryces Rd | 43 | 360 | 15480 | 0.017293 | 4.8036e-05
2012-12-13 09:00AM | 220946 | BDF2 | Rural Short | Repair U/G cable @ column 206182. | 22 | 180 | 3960 | 0.0044238 | 2.4577e-05
2012-12-13 10:00AM | 220394 | 8633 | Rural Short | Replace HV cross arm @ pole 53 | 6 | 240 | 1440 | 0.0016087 | 6.7027e-06
2012-12-14 06:30AM | 220463 | 3360 | Urban | Install 2 new PMS | 30 | 60 | 1800 | 0.0020108 | 3.3514e-05
2012-12-14 07:00AM | 219860 | T884 | Urban | STAND NEW POLES TRANSFERE EX AERIALS | 288 | 540 | 83160 | 0.0929 | 0.00032173
2012-12-14 08:00AM | 220050 | 8634 | Rural Short | augment hv mains run lv mains and relocate sub pole install DOF's 94214. | 221 | 510 | 112710 | 0.12591 | 0.00024688
2012-12-14 08:00AM | 220334 | 48196 | Rural Short | Replace 2 poles. Install DOF and agument 2 bays of HV mains. | 57 | 540 | 30780 | 0.034385 | 6.3676e-05
2012-12-14 08:00AM | 221363 | 35693 | Rural Short | maintenance | 25 | 240 | 6000 | 0.0067027 | 2.7928e-05
2012-12-14 08:00AM | 217181 | 10251 | Urban | MAINTAIN HV SWITCHGEAR and EARTH TEST | 33 | 180 | 5940 | 0.0066357 | 3.6865e-05
2012-12-14 08:00AM | 219860 | T884 | Urban | STAND NEW POLES TRANSFERE EX AERIALS | 20 | 480 | 73920 | 0.082578 | 2.2342e-05
2012-12-14 08:00AM | 221097 | 35772 | Urban | REPLACE NEUTRAL TERMINAL BLOCK | 3 | 300 | 900 | 0.0010054 | 3.3514e-06
2012-12-14 08:00AM | 221229 | C897 | Urban | REPLACE LV X-ARMS | 42 | 300 | 12600 | 0.014076 | 4.6919e-05
2012-12-14 08:00AM | 221566 | 25784 | Urban | Connect new cable to network make Pillar to Switch | 3 | 240 | 720 | 0.00080433 | 3.3514e-06
2012-12-14 08:30AM | 219060 | BWH2 | Rural Short | Replace Hv Pole's and HV Augmentation | 240 | 480 | 96960 | 0.10832 | 0.00026811
2012-12-14 08:30AM | 219748 | R218 | Rural Short | Install new pole 878535 and augment conductors from pole 825629 through 878535 to pole 825626 | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2012-12-14 08:30AM | 219798 | MGC2 | Rural Short | HV Augmentation | 13 | 300 | 3900 | 0.0043568 | 1.4523e-05
2012-12-14 08:30AM | 221042 | MVH2 | Rural Short | Replace pole 3K0459 and ABS 50408 with a new LBS 92670 | 11 | 360 | 3960 | 0.0044238 | 1.2288e-05
2012-12-14 08:30AM | 220074 | RVC2 | Urban | Replace Condemned Pole 2C0792 | 55 | 330 | 18150 | 0.020276 | 6.1442e-05
2012-12-14 08:30AM | 220502 | UNG2 | Urban | TRIM TREES NEAR POLE 2RO143 for CLEARANCES from MAINS | 41 | 240 | 9840 | 0.010992 | 4.5802e-05
2012-12-14 09:00AM | 218951 | BYC2 | Rural Short | AUGMENT HV CONDUCTORS ( REPLACE STEEL MAINS ) on POLES 2 - 13 | 9 | 360 | 3240 | 0.0036195 | 1.0054e-05
2012-12-14 09:00AM | 221391 | BGA2 | Rural Short | Replace Leaking TX @ S/S 50068. | 60 | 240 | 14400 | 0.016087 | 6.7027e-05
2012-12-14 09:00AM | 217538 | SC1204 | Urban | Create/close live line open point.Replace pole 100 and install LBS 92852.Replace pole 104 and install Sub 29717. | 14 | 360 | 5040 | 0.0056303 | 1.564e-05
2012-12-14 09:00PM | 220463 | 3360 | Urban | Install 2 new PMS | 30 | 60 | 1800 | 0.0020108 | 3.3514e-05
2012-12-14 09:30AM | 221036 | L940 | Rural Short | Removal Of Overhangs Stannix Park Rd Wilberforce | 14 | 180 | 12780 | 0.014277 | 1.564e-05
2012-12-14 09:30AM | 221036 | L940 | Rural Short | Removal Of Overhangs Stannix Park Rd Wilberforce | 128 | 240 | 17040 | 0.019036 | 0.00014299
2012-12-14 09:30AM | 221295 | 1125 | Urban | LV Changeover | 16 | 330 | 5280 | 0.0058984 | 1.7874e-05
2012-12-15 07:00AM | 219038 | 8622 | Urban | HV SWGR MandR @ SUB 9510 | 4 | 240 | 480 | 0.00053622 | 4.4685e-06
2012-12-15 08:00AM | 220576 | J514 | Urban | (1). ID and Spike HV cable between Sw P360 in PM 15445 and Sw 81746 in PM 28389.(2).Reroute HV cable through new road crossing ducts. | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2012-12-15 08:00AM | 220750 | KMA2 | Urban | SPIKE AND ID HV CABLE / 2 X HV S.T.J. / TERMINATE 2 X HV CABLE INTO NEW PM SUB | 34 | 480 | 16320 | 0.018231 | 3.7982e-05
2012-12-15 08:30AM | 220280 | MVC2 | Rural Short | Trim Trees Near Conductors | 1 | 300 | 300 | 0.00033514 | 1.1171e-06
2012-12-16 06:30AM | 209309 | 49348 | Urban | HVSWGR MAINT | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2012-12-16 08:00AM | 219905 | KYH2 | Urban | Replace pole and retrofit sub | 108 | 420 | 45360 | 0.050673 | 0.00012065
2012-12-16 08:30AM | 219742 | P608 | Rural Short | Retro fit and change high voltage arm at sub 11697 and retrofit sub 11698. | 26 | 420 | 10920 | 0.012199 | 2.9045e-05
2012-12-16 09:00AM | 219989 | YYB2 | Rural Short | REPLACE REGULATOR TANK @ REG 68909 | 18 | 360 | 6480 | 0.0072389 | 2.0108e-05
2012-12-16 09:00AM | 220586 | BGB2 | Rural Short | REPLACE POLE 2XP006 | 5 | 240 | 1200 | 0.0013405 | 5.5856e-06
2012-12-17 08:00AM | 219312 | A098 | Rural Short | Augment HV conductor + Replace poles + Install ABS + Install DOFs | 14 | 540 | 7560 | 0.0084454 | 1.564e-05
2012-12-17 08:00AM | 219692 | D813 | Rural Short | INSTALL NEW 1000KVA P/MOUNT SUB 32160 INSTALL NEW HV UGOH ON POLE 187 SAFELINK CF HV S/GEAR | 20 | 480 | 9600 | 0.010724 | 2.2342e-05
2012-12-17 08:00AM | 220051 | APC2 | Rural Short | SPIKE and ID HV CABLE . THEN 2 X HV STJ / 4 X HV SUB TERMS . COMMISSIONN NEW PM SUB . | 142 | 480 | 68160 | 0.076143 | 0.00015863
2012-12-17 08:00AM | 218816 | R253 | Urban | Replace USL H032 with Sectionaliser 96582 replace pole 207 with new pole 876459 install new pole 876615 remove 2 bays of O/H SL conductor and install new SLCP 9580. | 334 | 480 | 80160 | 0.089548 | 0.00037312
2012-12-17 08:00AM | 220780 | 46395 | Urban | Uprate Tx Sub 12554 Augment 2 bays LV | 100 | 390 | 39000 | 0.043568 | 0.00011171
2012-12-17 08:00AM | 221248 | 5506 | Urban | RESET PILLAR and COLUMN | 61 | 480 | 29280 | 0.032709 | 6.8144e-05
2012-12-17 08:00AM | 221414 | UNG2 | Urban | REPLACE STREET LIGHT COLUMNS | 79 | 270 | 21330 | 0.023828 | 8.8252e-05
2012-12-17 08:30AM | 220640 | MVB2 | Rural Short | Replace Poles Install New LBS 89727 Augment a section of 11KV O/H Mains and Retrofit DOFs at Sub 30304. | 187 | 450 | 84150 | 0.094006 | 0.0002089
2012-12-17 08:30AM | 220953 | RWB2 | Rural Short | Augment LV mains | 8 | 450 | 3600 | 0.0040216 | 8.937e-06
2012-12-17 08:30AM | 220399 | 46473 | Urban | Uprate sub 2086 to 200Kva. Replace links fuses LV arms MDI and move centre DOF away from pole | 27 | 360 | 9720 | 0.010858 | 3.0162e-05
2012-12-17 08:30AM | 220792 | RVC2 | Urban | MandR HOLEC SWITCHGEAR | 168 | 300 | 51000 | 0.056973 | 0.00018768
2012-12-17 09:00AM | 221402 | 5498 | Urban | LV pole change | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2012-12-17 10:00AM | 220958 | L941 | Rural Short | Removal Of Overhangs Adj to Sub 15894 Murrays Rd and removal of Over adj to Pole 806832 Beckman Pl Tennison | 12 | 270 | 3240 | 0.0036195 | 1.3405e-05
2012-12-17 10:00PM | 220878 | WWE2 | Urban | Replace LV fuse strip. | 44 | 180 | 7920 | 0.0088476 | 4.9153e-05
2012-12-17 12:30PM | 221425 | UNG2 | Urban | REPLACE STREET LIGHT COLUMNS | 92 | 210 | 19320 | 0.021583 | 0.00010278
2012-12-18 07:00AM | 220935 | 4869 | Urban | upgrade LV switchgear to Cat 2 | 5 | 540 | 2700 | 0.0030162 | 5.5856e-06
2012-12-18 07:30AM | 218678 | AZ1272 | Urban | REPLACE COND POLE 211 REPLACE TX @ SUB 3988 RECTIFY DEFECTS WITHIN ISOLATION | 50 | 570 | 28500 | 0.031838 | 5.5856e-05
2012-12-18 08:00AM | 218095 | 27446 | Rural Short | run 5 bays of hv mains and install new abs | 4 | 510 | 2040 | 0.0022789 | 4.4685e-06
2012-12-18 08:00AM | 221114 | P608 | Rural Short | Bush Fire defect treelopping. Cut and shackle 11kV OH mains @ p801300 and p265. Stand new poles and make safe. | 12 | 420 | 5040 | 0.0056303 | 1.3405e-05
2012-12-18 08:00AM | 216607 | J497 | Urban | HV Augmentation | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2012-12-18 08:00AM | 217476 | 35503 | Urban | REPLACE LOW VOLTAGE SWITCHGEAR @ SUB 16446 FONTANA CL ST CLAIR | 62 | 480 | 29760 | 0.033245 | 6.9261e-05
2012-12-18 08:00AM | 219485 | 1962 | Urban | HV Augmentation | 118 | 480 | 56640 | 0.063274 | 0.00013182
2012-12-18 08:00AM | 219946 | WH1235 | Urban | Replace 2 poles. Augment two bays of HV mains. | 115 | 480 | 55200 | 0.061665 | 0.00012847
2012-12-18 08:00AM | 220472 | CJ1204 | Urban | Replace poles for future augment | 100 | 480 | 48000 | 0.053622 | 0.00011171
2012-12-18 08:00AM | 221080 | 8620 | Urban | Augment 3 bays of HV mains | 26 | 480 | 12480 | 0.013942 | 2.9045e-05
2012-12-18 08:00AM | 221647 | T894 | Urban | Bond new cable into Pillar 48901 Ainsley Ave Glendenning | 11 | 300 | 3300 | 0.0036865 | 1.2288e-05
2012-12-18 08:30AM | 219346 | BLA2 | Rural Short | Replace Condemned Pole 3PC187 | 37 | 330 | 12210 | 0.01364 | 4.1333e-05
2012-12-18 08:30AM | 220526 | 27446 | Rural Short | Install new LBS 84591 + pole | 134 | 420 | 28140 | 0.031436 | 0.00014969
2012-12-18 08:30AM | 219909 | DP1206 | Urban | NEW POLE | 90 | 450 | 40500 | 0.045243 | 0.00010054
2012-12-18 08:30AM | 220485 | WRF2 | Urban | REPLACE POLES 1C0090 1C0453 INSTALL LV ADD POLE 877950 RETRO FIT SUBS 40831 41822 REPLACE HV X ARMS PLs 1C0083 1C0082 MandR DS 42715 | 222 | 390 | 86580 | 0.09672 | 0.000248
2012-12-18 08:30AM | 220545 | WWB2 | Urban | Trim overhanging Trees near sub | 207 | 240 | 49680 | 0.055499 | 0.00023124
2012-12-18 09:00AM | 219817 | ULE2 | Rural Short | Augment HV Conductors to CCT ( 17 to 26 )Off Princes Hwy TERMEIL. | 49 | 330 | 16170 | 0.018064 | 5.4739e-05
2012-12-18 09:00AM | 220524 | BDF2 | Rural Short | REPLACE POLE 1TY011Augment H/V conductors from pole 1TY011 to Pole 1TY004 | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2012-12-18 09:00AM | 221378 | 5498 | Urban | LV pole change | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2012-12-18 09:00AM | 221592 | 35010 | Urban | INSTALL NEW L/V PILLAR 115763 | 34 | 360 | 12240 | 0.013674 | 3.7982e-05
2012-12-18 10:00PM | 219448 | BWG2 | Urban | Replace one pole and ABS. Augment 3 bays of HV mains to 7/4.50AAC. | 208 | 450 | 93600 | 0.10456 | 0.00023236
2012-12-19 01:00PM | 221872 | CJ1249 | Urban | Repair Rusty Column | 19 | 120 | 2280 | 0.002547 | 2.1225e-05
2012-12-19 08:00AM | 219918 | R260 | Rural Short | AUGMENT HV MAINS | 93 | 480 | 44640 | 0.049868 | 0.00010389
2012-12-19 08:00AM | 217718 | 46752 | Urban | REPLACE POLE 825 | 7 | 243 | 1701 | 0.0019002 | 7.8198e-06
2012-12-19 08:00AM | 218615 | CV1210 | Urban | ERECT NEW TOP MOUNT LBS (92356)ON EXISTING POLE | 65 | 480 | 31200 | 0.034854 | 7.2613e-05
2012-12-19 08:00AM | 218814 | R253 | Urban | Remove 4 bays of O/H HV mains augment 3 bays of LV mains below HV and replace pole 339 wit pole 874494. | 115 | 480 | 55200 | 0.061665 | 0.00012847
2012-12-19 08:00AM | 219974 | MYM2 | Urban | Replace pole and retrofit sub | 150 | 420 | 63000 | 0.070379 | 0.00016757
2012-12-19 08:00AM | 220567 | 25782 | Urban | To install/connect new 22kv Al XLPE cable.Re tension OH mains. | 45 | 480 | 21600 | 0.02413 | 5.027e-05
2012-12-19 08:00AM | 221789 | 1952 | Urban | To augment LV and install 1 pillar for URD | 21 | 450 | 9450 | 0.010557 | 2.346e-05
2012-12-19 08:30AM | 219300 | MG1219 | Rural Short | HV Hardware Upgrade | 227 | 480 | 108960 | 0.12172 | 0.00025359
2012-12-19 08:30AM | 220244 | 8637 | Rural Short | Replace condemned sub pole 1429.Replace cast iron UGOH @ pole 33 | 21 | 450 | 9450 | 0.010557 | 2.346e-05
2012-12-19 08:30AM | 219447 | WBB2 | Urban | Replace poles and install new pole sub and decommission cottage sub | 98 | 420 | 41160 | 0.045981 | 0.00010948
2012-12-19 08:30AM | 219734 | WRF2 | Urban | AUGMENT HV MAINS and REPLACE POLES | 183 | 420 | 76860 | 0.085862 | 0.00020443
2012-12-19 09:00AM | 218957 | BYC2 | Rural Short | Augment HV Conductors ( replace steel mains ) poles 13 - 18Bong Bong Rd BERRY. | 9 | 360 | 3240 | 0.0036195 | 1.0054e-05
2012-12-19 09:00AM | 220017 | M399 | Rural Short | REPLACE TRANSFORMER(OIL LEAK) | 3 | 240 | 720 | 0.00080433 | 3.3514e-06
2012-12-19 09:00AM | 221489 | ULJ2 | Rural Short | AUGMENT LV O/H MAINS / REPLACE POLE | 33 | 360 | 11880 | 0.013271 | 3.6865e-05
2012-12-19 09:00AM | 220161 | DP1236 | Urban | REPLACE HV X ARM PL 4AT426 RETRO FIT SUBS 41353 41693 42702 REMOVE TREES NEXT TO POLE 4AT438 | 126 | 330 | 41580 | 0.04645 | 0.00014076
2012-12-19 09:00AM | 221870 | CJ1249 | Urban | Repair Rusty Column | 17 | 240 | 4080 | 0.0045578 | 1.8991e-05
2012-12-19 09:00AM | 221878 | S334 | Urban | Repair Rusty Column | 8 | 120 | 960 | 0.0010724 | 8.937e-06
2012-12-19 10:00AM | 221439 | GG1295 | Rural Short | P1 BFD TREE TRIMMING @ PL 4PJ001 FOXGROUND | 73 | 180 | 13140 | 0.014679 | 8.155e-05
2012-12-19 11:00AM | 221874 | CJ1249 | Urban | Repair Rusty Column | 30 | 120 | 3600 | 0.0040216 | 3.3514e-05
2012-12-19 11:30AM | 220941 | 10290 | Rural Short | Trim tree Adj to H/V Lines Cnr Yeomans Rd and Bells Line Of Rd Nth Richmond | 19 | 150 | 2850 | 0.0031838 | 2.1225e-05
2012-12-20 01:00PM | 221876 | C832 | Urban | Repair Rusty Column | 4 | 120 | 480 | 0.00053622 | 4.4685e-06
2012-12-20 07:00AM | 220705 | CD1271 | Urban | Network Modifications involved with Cawdor Zone Substation. | 6 | 120 | 1680 | 0.0018768 | 6.7027e-06
2012-12-20 07:00AM | 220705 | CD1271 | Urban | Network Modifications involved with Cawdor Zone Substation. | 24 | 600 | 8400 | 0.0093838 | 2.6811e-05
2012-12-20 08:00AM | 219409 | 35695 | Rural Short | run lv mains | 6 | 480 | 2880 | 0.0032173 | 6.7027e-06
2012-12-20 08:00AM | 219892 | D814 | Rural Short | UPRATE EX SUB 7739 TO 315 KVA | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2012-12-20 08:00AM | 220127 | BWH2 | Rural Short | New sub 32401 single phase. | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2012-12-20 08:00AM | 221198 | 61617 | Rural Short | MandR ABS 25883 and replace DOF's J363 | 32 | 300 | 9600 | 0.010724 | 3.5748e-05
2012-12-20 08:00AM | 221610 | 25747 | Rural Short | ID And Spike LV cable between pillar 117190 and pillar 117192. Install new LV pillars and terminate cable to Fuse strip in PM 25254. | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2012-12-20 08:00AM | 217384 | WL1296 | Urban | REPLACE COND POLE 285586 | 26 | 480 | 12480 | 0.013942 | 2.9045e-05
2012-12-20 08:00AM | 220130 | WH1235 | Urban | Augment HV OH conductor. Install new DOFs | 173 | 480 | 83040 | 0.092766 | 0.00019326
2012-12-20 08:00AM | 220262 | 8693 | Urban | Replace 4 poles. Remove ABS 8504 and install ABS 88088. Augment 4 bays of HV mains. | 109 | 480 | 52320 | 0.058448 | 0.00012177
2012-12-20 08:00AM | 220491 | CJ1204 | Urban | Replace poles for future augment | 154 | 480 | 73920 | 0.082578 | 0.00017204
2012-12-20 08:00AM | 221941 | J510 | Urban | Install new LV pillars via reconfiguration of LV circuit | 68 | 480 | 32640 | 0.036463 | 7.5964e-05
2012-12-20 08:30AM | 220733 | W163 | Rural Short | REPLACE CONDEMNED POLE AT SUB 14923 AND REPLACE CONDEMNED POLE 159 AND REPAIR LOOSE USL AT USL'S X210 | 8 | 420 | 3360 | 0.0037535 | 8.937e-06
2012-12-20 08:30AM | 220830 | RBB2 | Rural Short | Replace Condemned Pole 3YH145 and Retrofit DOFs at Sub 30688 | 35 | 390 | 13650 | 0.015249 | 3.9099e-05
2012-12-20 08:30AM | 221233 | 35990 | Rural Short | MandR ABS U757 | 8 | 210 | 1680 | 0.0018768 | 8.937e-06
2012-12-20 08:30AM | 219911 | DP1206 | Urban | NEW PAD SUBSTATION | 45 | 450 | 20250 | 0.022622 | 5.027e-05
2012-12-20 08:30AM | 220868 | SHK2 | Urban | AUGMENT HV MAINS | 37 | 420 | 15540 | 0.01736 | 4.1333e-05
2012-12-20 09:00AM | 221269 | 35530 | Urban | REPLACE COLUMN | 7 | 240 | 1680 | 0.0018768 | 7.8198e-06
2012-12-20 09:00AM | 221380 | 5498 | Urban | LV POLE CHANGE | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2012-12-20 09:00AM | 221756 | 2820 | Urban | Replace pole | 25 | 180 | 4500 | 0.005027 | 2.7928e-05
2012-12-20 09:00AM | 221879 | CJ1249 | Urban | Repair Rusty Column | 39 | 240 | 9360 | 0.010456 | 4.3568e-05
2012-12-20 09:00AM | 221881 | C824 | Urban | Repair Rusty Column | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2012-12-20 09:30AM | 219562 | ULE2 | Rural Short | Replace Condemned pole 1GD003Monkey Mountain Rd TERMEIL | 12 | 270 | 3240 | 0.0036195 | 1.3405e-05
2012-12-20 09:30AM | 221239 | 8801 | Rural Short | Removal of Branch over H/V Mains by Contractors climbers P2 DEfect | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2012-12-20 11:00AM | 221089 | CT1262 | Rural Short | Remove Spark catchers from DOF | 1 | 180 | 180 | 0.00020108 | 1.1171e-06
2012-12-20 11:00AM | 221383 | S590 | Urban | LV POLE CHANGE | 1 | 240 | 240 | 0.00026811 | 1.1171e-06
2012-12-21 01:00PM | 221938 | 19815 | Urban | Rusty Column | 28 | 120 | 3360 | 0.0037535 | 3.1279e-05
2012-12-21 01:00PM | 221951 | 19815 | Urban | Rusty Column | 10 | 120 | 1200 | 0.0013405 | 1.1171e-05
2012-12-21 08:00AM | 220351 | 8635 | Rural Short | INSTALL NEW 3 ph 63 KVA POLE SUB 29683 STAND NEW POLES CHANGE POLE 196 RUN 150 mm ABC O/H MAINS | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2012-12-21 08:00AM | 220401 | 46475 | Rural Short | Install ABS 92185 + pole | 78 | 420 | 19320 | 0.021583 | 8.7135e-05
2012-12-21 08:00AM | 222051 | T828 | Rural Short | MAINTAIN ABSREPAIR STRANDED CONDUCTOR | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2012-12-21 08:00AM | 221792 | MR2224 | Urban | Install:LV UG cable pillars Streetlights | 6 | 240 | 1440 | 0.0016087 | 6.7027e-06
2012-12-21 08:30AM | 221706 | P608 | Rural Short | Change poles 28 29 and install new pole 822265. Repair defects at poles 31323334.Retro fit pole substation 11571. | 32 | 450 | 14400 | 0.016087 | 3.5748e-05
2012-12-21 08:30AM | 221818 | UNB2 | Urban | REPLACE STREET LIGHT COLUMNS | 86 | 180 | 15480 | 0.017293 | 9.6072e-05
2012-12-21 09:00AM | 219919 | KVA2 | Rural Short | Augment HV conductors to CCTMount Scanzi Rd KANGAROO VALLEY | 15 | 360 | 5400 | 0.0060324 | 1.6757e-05
2012-12-21 09:00AM | 220950 | MVF2 | Rural Short | Holec MandR | 131 | 420 | 55020 | 0.061464 | 0.00014634
2012-12-21 09:00AM | 221386 | 5495 | Urban | LV POLE CHANGE | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2012-12-21 09:00AM | 221952 | 19815 | Urban | Rusty Column | 11 | 240 | 2640 | 0.0029492 | 1.2288e-05
2012-12-21 09:00AM | 221953 | CJ1241 | Urban | Rusty Column | 35 | 240 | 8400 | 0.0093838 | 3.9099e-05
2012-12-21 11:00AM | 221385 | 2807 | Urban | LV POLE CHANGE | 3 | 240 | 720 | 0.00080433 | 3.3514e-06
2012-12-21 12:00AM | 221955 | DP1273 | Urban | TEST HV CABLE FROM SW 61704 DS 40786 TO SW 123714 NEW DS 32564.TEST CABLE FROM SW 26783 DS 42247 TO SW 123715 NEW DS 32564 | 66 | 180 | 11880 | 0.013271 | 7.373e-05
2012-12-22 08:00AM | 221299 | R211 | Rural Short | P1 Tree trimming defect between poles 338 - 340 | 24 | 420 | 10080 | 0.011261 | 2.6811e-05
2012-12-27 01:00PM | 222068 | CJ1245 | Urban | Replace Column | 12 | 120 | 1440 | 0.0016087 | 1.3405e-05
2012-12-27 07:00AM | 217200 | B214 | Urban | REPLACE TRF AND CUBICLE - SUB 16237 | 2 | 390 | 780 | 0.00087135 | 2.2342e-06
2012-12-27 09:00AM | 222059 | CJ1245 | Urban | Replace Column | 27 | 120 | 3240 | 0.0036195 | 3.0162e-05
2012-12-27 09:00AM | 222069 | CJ1245 | Urban | Change Rusty Columns | 24 | 240 | 5760 | 0.0064346 | 2.6811e-05
2012-12-28 07:30AM | 219034 | 8611 | Urban | HV SWGR MandR @ SUB 22881 | 1 | 280 | 280 | 0.00031279 | 1.1171e-06
2012-12-28 07:30AM | 221460 | WX1210 | Urban | REPAIRS TO ABS F873 PIN DEFECT # D053 | 9 | 470 | 4230 | 0.0047254 | 1.0054e-05
2013-01-02 08:00AM | 219864 | C897 | Urban | Augment 4 bays of HV mains and replace 1 pole | 76 | 540 | 41040 | 0.045847 | 8.4901e-05
2013-01-03 06:30AM | 218921 | 5464 | Urban | MandR HVSWGR @ SUB 22965 | 1 | 210 | 210 | 0.0002346 | 1.1171e-06
2013-01-03 08:00AM | 221725 | MVB2 | Rural Short | Job 1. Augment HV Mains between Pole 3K2471 and Sub 30917 plus retro fit sub 30917Job 2. Retro fit Sub 31583 | 3 | 230 | 690 | 0.00077081 | 3.3514e-06
2013-01-03 08:30AM | 220620 | JBA2 | Rural Short | REPLACE CONDEMNED POLES 4HH041 and 4HJ037 REPLACE LV X ARM S/S 40881 | 22 | 340 | 7480 | 0.0083561 | 2.4577e-05
2013-01-03 08:30AM | 222066 | L584 | Rural Short | REPLACE S/L COLUMN and PUT IN NEW LV PILLAR | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-01-03 09:00AM | 216838 | ULL2 | Rural Short | Replace Condemned poles 1GY029 and 1GY032Princes Hwy LAKE TABOURIE | 2 | 160 | 320 | 0.00035748 | 2.2342e-06
2013-01-04 07:00AM | 221812 | J504 | Urban | To Allow staff to Replace Condemned Pole 2104 to replace UGOH and Retrofit Sub 11006 The Parkway Bradbury | 15 | 540 | 64800 | 0.072389 | 1.6757e-05
2013-01-04 08:00AM | 221812 | J504 | Urban | To Allow staff to Replace Condemned Pole 2104 to replace UGOH and Retrofit Sub 11006 The Parkway Bradbury | 87 | 480 | 57600 | 0.064346 | 9.7189e-05
2013-01-04 08:30AM | 221151 | 8801 | Rural Short | Install stay and retention HV and LV mains adj pole 290855 | 4 | 300 | 1200 | 0.0013405 | 4.4685e-06
2013-01-04 08:30AM | 221396 | WWE2 | Urban | Trim tree from HV mains | 76 | 180 | 13680 | 0.015282 | 8.4901e-05
2013-01-04 08:30AM | 221642 | KMF2 | Urban | REPLACE ABS 71994 | 162 | 420 | 68040 | 0.076009 | 0.00018097
2013-01-07 08:00AM | 222032 | WWC2 | Urban | AUGMENT LV UNDERGROUND MAINS | 22 | 360 | 7920 | 0.0088476 | 2.4577e-05
2013-01-08 08:00AM | 220942 | 17038 | Urban | uprate sub and rewire lv | 40 | 480 | 19200 | 0.021449 | 4.4685e-05
2013-01-08 09:00AM | 222240 | T831 | Rural Short | REPAIR LV UG CABLE AFTER LIGHTNING STRIKE | 7 | 120 | 840 | 0.00093838 | 7.8198e-06
2013-01-08 09:00AM | 222404 | CJ1245 | Urban | Rusty Column | 24 | 120 | 2880 | 0.0032173 | 2.6811e-05
2013-01-08 09:30AM | 220798 | KVA2 | Rural Short | REPLACE USL's 39682 with DOF's 97050 | 14 | 240 | 3360 | 0.0037535 | 1.564e-05
2013-01-08 10:00AM | 221173 | 35983 | Rural Short | Uprate LV SW/GR PMS's 23901 and 23902. | 23 | 360 | 8280 | 0.0092498 | 2.5694e-05
2013-01-09 08:00AM | 219552 | 35695 | Rural Short | run two bays of hv mains and install new sub | 34 | 519 | 17646 | 0.019713 | 3.7982e-05
2013-01-09 08:00AM | 221372 | 35824 | Rural Short | Augment 1 bay of HV mains and install 2 DOF's. | 114 | 530 | 60420 | 0.067496 | 0.00012735
2013-01-09 08:00AM | 221478 | 35695 | Rural Short | Run 2 bays of O/H HV mains 2 baysof LV mains and install a new Sub. | 16 | 510 | 8160 | 0.0091157 | 1.7874e-05
2013-01-09 08:00AM | 222083 | MVF2 | Rural Short | Replace Poles Install New LBS 92873 and Augment a Section of 11KV O/H Mains | 44 | 610 | 98210 | 0.10971 | 4.9153e-05
2013-01-09 08:00AM | 220933 | 35312 | Urban | AUGMENT HV O/H MAINS TO SUB 5100 CARMEL PL WINSTON HILLS and REPLACE POLE 958 | 41 | 320 | 13120 | 0.014657 | 4.5802e-05
2013-01-09 08:00AM | 222376 | CD1271 | Urban | Conduct TVI Works as Required at Sub 20032 | 40 | 180 | 7200 | 0.0080433 | 4.4685e-05
2013-01-09 08:30AM | 221162 | 8799 | Rural Short | Replace LV X-Arms and Links and Fuses @ Sub 7590 | 16 | 359 | 5744 | 0.0064167 | 1.7874e-05
2013-01-09 08:30AM | 221195 | 25403 | Rural Short | Replace ABS 25910 | 20 | 315 | 6300 | 0.0070379 | 2.2342e-05
2013-01-09 08:30AM | 222083 | MVF2 | Rural Short | Replace Poles Install New LBS 92873 and Augment a Section of 11KV O/H Mains | 278 | 580 | 93380 | 0.10432 | 0.00031056
2013-01-09 08:30AM | 220991 | UNC2 | Urban | REMOVE HV MAINS and CONNECT NEW FEEDER to FT1206 @ FIGTREE ZONE SUB | 74 | 300 | 22200 | 0.0248 | 8.2667e-05
2013-01-09 08:30AM | 221666 | UNE2 | Urban | AUGMENT HV MAINS and RAISE 11 KV CABLE UP POLE 871355 | 267 | 390 | 104130 | 0.11633 | 0.00029827
2013-01-09 08:30AM | 222370 | WH1257 | Urban | Pole Change Over | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-01-09 09:00AM | 222407 | 49357 | Urban | Cable Fault and Repair | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-01-09 09:00AM | 222611 | F601 | Urban | LV pole change | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2013-01-10 03:30PM | 216245 | 8634 | Rural Short | augment hv mains to 80mm cct | 194 | 60 | 5940 | 0.0066357 | 0.00021672
2013-01-10 08:00AM | 216245 | 8634 | Rural Short | augment hv mains to 80mm cct | 4 | 510 | 50490 | 0.056403 | 4.4685e-06
2013-01-10 08:00AM | 221670 | X802 | Rural Short | REPLACE CONDEMNED POLECONTRACT TREE TRIMMING and REPLACE DOF'S | 26 | 420 | 10920 | 0.012199 | 2.9045e-05
2013-01-10 08:00AM | 221793 | MGC2 | Rural Short | Remove Sub 30801 and remove one bay of HV mains Install new sub 29703. | 1 | 450 | 450 | 0.0005027 | 1.1171e-06
2013-01-10 08:00AM | 218486 | T888 | Urban | HVSWGR MAINT and LVSWGR REPLACEMENT | 77 | 420 | 32340 | 0.036128 | 8.6018e-05
2013-01-10 08:00AM | 221926 | 8764 | Urban | REPLACE COND POLE 1185 and REPLACE O/W LV MAINS BETWEEN | 31 | 480 | 14880 | 0.016623 | 3.4631e-05
2013-01-10 08:00AM | 222227 | J496 | Urban | To allow staff to replace Condemned Pole 453 Stewart St Campbelltown | 134 | 480 | 64320 | 0.071853 | 0.00014969
2013-01-10 08:00AM | 222369 | 2829 | Urban | Pole Change Over | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-01-10 08:30AM | 219681 | MG1219 | Rural Short | HV Augmentation | 258 | 480 | 123840 | 0.13834 | 0.00028822
2013-01-10 08:30AM | 221262 | A051 | Rural Short | Replace HV X-Arms @ Poles 170 and 199. | 30 | 390 | 11700 | 0.01307 | 3.3514e-05
2013-01-10 08:30AM | 221747 | BLA2 | Rural Short | Replace Condemned poles 3PC234 and 3PC232 and 3PC229 | 77 | 390 | 30030 | 0.033547 | 8.6018e-05
2013-01-10 08:30AM | 221762 | KMF2 | Urban | REPAIR ABS 71926 | 49 | 420 | 20580 | 0.02299 | 5.4739e-05
2013-01-10 08:30AM | 222503 | M400 | Urban | REPLACE DAMGED LV PILLAR | 17 | 330 | 5610 | 0.006267 | 1.8991e-05
2013-01-10 09:00AM | 207867 | BDC2 | Rural Short | Fit Vibration Dampers to poles 1PX029 and 1PX028. | 9 | 240 | 2160 | 0.002413 | 1.0054e-05
2013-01-10 09:00AM | 217830 | KVB2 | Rural Short | Install New DOFs 97094 ( Replace pole 1PH038 )Jarretts Lane KANGAROO VALLEY. | 19 | 330 | 6270 | 0.0070043 | 2.1225e-05
2013-01-10 09:00AM | 221289 | W118 | Urban | Replace HV crossarm + LV crossarms on busy poles | 79 | 330 | 26070 | 0.029123 | 8.8252e-05
2013-01-10 09:00AM | 222081 | 7973 | Urban | REPLACE SERVICE HARNESS SUB 549 | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-01-10 09:30AM | 222684 | ULB2 | Urban | Replace x poles | 126 | 270 | 34020 | 0.038004 | 0.00014076
2013-01-10 09:30PM | 221832 | APE2 | Urban | TEST CABLE FOR FAULT | 108 | 300 | 32400 | 0.036195 | 0.00012065
2013-01-10 11:00AM | 221407 | 5506 | Urban | Defect rectification | 82 | 300 | 24600 | 0.027481 | 9.1604e-05
2013-01-11 08:00AM | 220835 | 35815 | Rural Short | Replace USL with new DOFs Replace DOFs | 18 | 360 | 6480 | 0.0072389 | 2.0108e-05
2013-01-11 08:00AM | 221911 | S743 | Rural Short | Augment LV mains to 150 ABC.Alter Sub 302 for LV ABC. | 26 | 480 | 12480 | 0.013942 | 2.9045e-05
2013-01-11 08:00AM | 221904 | 8776 | Urban | REPLACE COND POLE 478 | 34 | 480 | 16320 | 0.018231 | 3.7982e-05
2013-01-11 08:30AM | 219822 | BLA2 | Rural Short | Replace Condemned pole 3PC355 | 72 | 330 | 23760 | 0.026543 | 8.0433e-05
2013-01-11 08:30AM | 220879 | MG1267 | Rural Short | HV Upgrade | 20 | 330 | 6600 | 0.007373 | 2.2342e-05
2013-01-11 08:30AM | 221324 | D814 | Rural Short | Replace River Crossing Pole 311047and Install new ground stay. Install Vibrations dampeners @ Pole 841860 and Pole 789093 | 2 | 330 | 660 | 0.0007373 | 2.2342e-06
2013-01-11 08:30AM | 222451 | L584 | Rural Short | REPLACE S/L COLUMN and PUT IN NEW LV PILLAR | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2013-01-11 08:30AM | 221776 | HBB2 | Urban | REPLACE CONDEMNED POLE AND CROSSARMS. | 185 | 450 | 83250 | 0.093 | 0.00020667
2013-01-11 08:30AM | 222817 | SWD2 | Urban | Replace LV mains | 3 | 210 | 630 | 0.00070379 | 3.3514e-06
2013-01-11 09:00AM | 222796 | L582 | Rural Short | REPLACE CONDEMNED POLE(48HR) | 10 | 360 | 3600 | 0.0040216 | 1.1171e-05
2013-01-11 09:00AM | 222415 | GV1278 | Urban | Remove redundant HV OH Mains | 15 | 360 | 5400 | 0.0060324 | 1.6757e-05
2013-01-11 09:30AM | 221712 | J462 | Urban | Uprate Tx 2 @ PM 13013 to 1000KVA and replace LV Sw/Gr with 2500A CB and Cat 2 fusestrip. | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2013-01-11 10:00PM | 218733 | 17039 | Urban | HVSWGR MAINT AND CABLE CLAMP REPLACEMENT | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-01-12 07:30AM | 221723 | 19897 | Urban | CONNNECT TO THE NETWORK NEW PAD SUB 32238 VIA NEW SECTION OF U/G TO EXISTING NETWORK RENMOVE SECTION OF MAINS | 1 | 540 | 540 | 0.00060324 | 1.1171e-06
2013-01-12 08:00AM | 220763 | 35827 | Rural Short | Replacement of 4 poles and augmentation of 6 bays of HV OH mains. | 58 | 540 | 31320 | 0.034988 | 6.4793e-05
2013-01-13 06:30AM | 221206 | 8744 | Urban | REPLACE CUBICLE and TX @SUB 6295 WITH FIRE RISK CUBICLE AND TX. INSTALL LV 1250A CB. LOYALTY RD NORTH ROCKS | 16 | 540 | 8640 | 0.0096519 | 1.7874e-05
2013-01-13 07:00AM | 219150 | T893 | Urban | Replace pole (pluck and plant) and ABS 184 with LBS 81219 | 26 | 600 | 15600 | 0.017427 | 2.9045e-05
2013-01-13 07:00AM | 220896 | 9030 | Urban | Re-align LB 89142. Repair pole cap at ABS 89143. Install pilot cable poles 367 - J374 | 6 | 720 | 4320 | 0.004826 | 6.7027e-06
2013-01-13 07:30AM | 218822 | 1953 | Urban | MandR Hazemeyer Sw/Gr @ sub 9550. Bessemer St. Blacktown | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-01-13 08:00AM | 221449 | SWD2 | Urban | Replace pole and Transformer | 55 | 450 | 24750 | 0.027649 | 6.1442e-05
2013-01-14 02:00PM | 222039 | B799 | Urban | Remove Cap Bank 1 from network | 84 | 60 | 5040 | 0.0056303 | 9.3838e-05
2013-01-14 03:30PM | 220337 | 8634 | Rural Short | augment lv mains and replace usl with new LBS | 442 | 60 | 15900 | 0.017762 | 0.00049377
2013-01-14 06:30AM | 220033 | 8694 | Urban | Replace 2 poles with new poles and also install bare low voltage mains with new 150mm low voltage ABC ConductorAlso ABS 8856 WILL BE REPLACED WITH NEW ABS 123416 | 152 | 630 | 77490 | 0.086566 | 0.0001698
2013-01-14 08:00AM | 220337 | 8634 | Rural Short | augment lv mains and replace usl with new LBS | 132 | 510 | 135150 | 0.15098 | 0.00014746
2013-01-14 08:00AM | 220033 | 8694 | Urban | Replace 2 poles with new poles and also install bare low voltage mains with new 150mm low voltage ABC ConductorAlso ABS 8856 WILL BE REPLACED WITH NEW ABS 123416 | 94 | 540 | 66420 | 0.074199 | 0.00010501
2013-01-14 08:00AM | 220910 | C830 | Urban | Isolate LV mains for removal of HV OH mains. | 169 | 540 | 91260 | 0.10195 | 0.00018879
2013-01-14 08:00AM | 221781 | 8774 | Urban | Relocate LV switchgear to correct orrienation. | 35 | 480 | 16800 | 0.018768 | 3.9099e-05
2013-01-14 08:00AM | 223032 | 55885 | Urban | Augment LV mains | 31 | 360 | 11160 | 0.012467 | 3.4631e-05
2013-01-14 08:30AM | 219850 | BWH2 | Rural Short | Replace Hv Poles and Augment Hv Oh Mains | 65 | 480 | 31200 | 0.034854 | 7.2613e-05
2013-01-14 09:00AM | 222622 | X871 | Urban | HV/LV Pole changeover | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-01-14 09:30AM | 222039 | B799 | Urban | Remove Cap Bank 1 from network | 84 | 60 | 5040 | 0.0056303 | 9.3838e-05
2013-01-14 10:00AM | 222204 | ULJ2 | Rural Short | REMOVE LV O/H MAINS / INSTALL NEW LV CABLE INTO EX PILLAR | 22 | 240 | 5280 | 0.0058984 | 2.4577e-05
2013-01-15 07:00AM | 221182 | 6430 | Urban | relocate OH mains to underground | 1 | 540 | 540 | 0.00060324 | 1.1171e-06
2013-01-15 08:00AM | 221218 | X802 | Rural Short | REPLACE CONDEMNED POLERETROFIT DOF'SSUBS and INSTALL VIBRATION DAMPERS | 8 | 450 | 3600 | 0.0040216 | 8.937e-06
2013-01-15 08:00AM | 222078 | KVB2 | Rural Short | 11kV OUTAGE to REPLACE STR 89 FDR 7513 | 10 | 450 | 4500 | 0.005027 | 1.1171e-05
2013-01-15 08:00AM | 220916 | SWC2 | Urban | Replace 3 Poles. Augment 5 Bays of 7/4.50AAC. Install LBS and replace DOF's | 141 | 480 | 67680 | 0.075607 | 0.00015751
2013-01-15 08:00AM | 221673 | 8693 | Urban | Replace 4 poles replace ABS 8502. Install DOFs. Augment 3 bays of HV mains. | 99 | 480 | 47520 | 0.053086 | 0.00011059
2013-01-15 08:00AM | 221736 | 8764 | Urban | REPLACE COND POLE 273 | 89 | 480 | 42720 | 0.047723 | 9.9424e-05
2013-01-15 08:00AM | 221739 | 35696 | Urban | Replace pole 26 replace USL 18152 with LBS 94462 and augment 3 bays of O/H HV mains to 3 x 120mm CCT. | 657 | 510 | 335070 | 0.37431 | 0.00073395
2013-01-15 08:00AM | 222569 | CT1202 | Urban | To allow staff to replace Condemned poles 1051 and 298 Moore Oxley Rd Campbelltown | 94 | 360 | 33840 | 0.037803 | 0.00010501
2013-01-15 08:00AM | 222651 | 9032 | Urban | REPLACE PILLAR | 59 | 240 | 14160 | 0.015818 | 6.591e-05
2013-01-15 08:30AM | 221443 | L947 | Rural Short | Replace condemned Pole 260. Install stay @ pole 264 | 86 | 360 | 17280 | 0.019304 | 9.6072e-05
2013-01-15 08:30AM | 220395 | UNJ2 | Urban | Replace Pole Retrofit sub and replace HV crossarms | 121 | 420 | 50820 | 0.056772 | 0.00013517
2013-01-15 08:30AM | 222587 | SC1204 | Urban | Install poles for streetlighting | 6 | 390 | 2340 | 0.0026141 | 6.7027e-06
2013-01-15 08:30AM | 222776 | 20717 | Urban | Isolate LV for contractors to perform works on adjacent sewer vent | 126 | 420 | 63840 | 0.071317 | 0.00014076
2013-01-15 09:00AM | 220859 | KMD2 | Urban | REPLACE X PL 4KG243 RETRO FIT SUB 41240 REPLACE HV X ARM PL 4KG242 LV X ARM PL 4KG253 | 57 | 330 | 18810 | 0.021013 | 6.3676e-05
2013-01-15 09:00AM | 222765 | T890 | Urban | Change LV Switchgear | 31 | 360 | 11160 | 0.012467 | 3.4631e-05
2013-01-15 09:30AM | 222079 | W124 | Rural Short | Replace HV Crossarm and USL + Replace LV cross-arm Pole J89. | 85 | 270 | 22950 | 0.025638 | 9.4955e-05
2013-01-15 09:30AM | 222922 | ULB2 | Urban | replace LV x pole Rackham Cres Burrill Lake | 19 | 270 | 5130 | 0.0057308 | 2.1225e-05
2013-01-15 11:00AM | 222618 | 2815 | Urban | LV Pole change | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2013-01-16 08:00AM | 220006 | HKE2 | Rural Short | Uprate Substation 50245 from 200 kva to 400kva | 45 | 480 | 21600 | 0.02413 | 5.027e-05
2013-01-16 08:00AM | 220674 | 25401 | Rural Short | INSTALL NEW 500 KVA PADMOUNT SUB 32423 INSTALL NEW CFCC SAFELINK HV S/GEAR CHANGE POLE 285598 NEW HV UGOH RUN 240 Sq Al UG MAINS TERMINATE NEW UG MAINS IN EX SUB 29689 | 24 | 540 | 12960 | 0.014478 | 2.6811e-05
2013-01-16 08:00AM | 220769 | X473 | Rural Short | REPLACE CONDEMNED POLEXARMSINSTALL SVDS' RETRO FIT SUBS and CONTRACT TREE TRIMMIMG | 62 | 420 | 26040 | 0.02909 | 6.9261e-05
2013-01-16 08:00AM | 221503 | 4368 | Rural Short | Install 4 bays of O/H HV mains to 3 x 150mm NMSABC. | 36 | 480 | 17280 | 0.019304 | 4.0216e-05
2013-01-16 08:00AM | 221547 | R260 | Rural Short | Replace poles 37 and 39. Remove pole 38. Install LBS 88539. Augment HV mains from Sub 27434 to pole 40. | 31 | 450 | 13950 | 0.015584 | 3.4631e-05
2013-01-16 08:00AM | 222341 | T868 | Rural Short | Uprate Tx and retrofit Sub 10473. | 35 | 420 | 14700 | 0.016422 | 3.9099e-05
2013-01-16 08:00AM | 220277 | UNC2 | Urban | Connect new UGOH to network from Figtree ZS. remove ABS + Hv mains | 176 | 480 | 82560 | 0.092229 | 0.00019661
2013-01-16 08:00AM | 221424 | 2810 | Urban | Replace 1 pole and augment 6 bays of HV OH mains. | 160 | 480 | 76800 | 0.085795 | 0.00017874
2013-01-16 08:00AM | 221768 | R245 | Urban | REPLACE POLE # 40 - ROSE CT WINMALEE | 11 | 480 | 5280 | 0.0058984 | 1.2288e-05
2013-01-16 08:00AM | 221935 | 8764 | Urban | replace cond pole 253 | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2013-01-16 08:00AM | 222347 | W113 | Urban | To allow staff to repair defect ( Works request # 116090) Retro Sub 10693 and Replace Condemned Pole 28 Macquariedale Rd Appin | 30 | 480 | 14400 | 0.016087 | 3.3514e-05
2013-01-16 08:30AM | 222442 | MGD2 | Rural Short | Augment high voltage mains from pole 3V0160 to ABS 50800 and install DOFs at pole 3V0205. | 318 | 450 | 143100 | 0.15986 | 0.00035524
2013-01-16 08:30AM | 220965 | SHK2 | Urban | REPLACE X PL 4DR334 ABS 70865 with LBS 123533 REPLACE HV X ARMS pLS 4DR3364DR340 4DR342 4DR105 4DR108 LV X ARM PL 4DR107 | 96 | 360 | 34560 | 0.038608 | 0.00010724
2013-01-16 08:30AM | 221959 | WBB2 | Urban | Replace pole and install new pole sub and decommission cottage sub andReplace Load break switch | 54 | 420 | 22680 | 0.025336 | 6.0324e-05
2013-01-17 01:00AM | 223157 | 9060 | Urban | LV Point of Attachment | 10 | 300 | 3000 | 0.0033514 | 1.1171e-05
2013-01-17 08:00AM | 219811 | A055 | Rural Short | REPLACE POLE 356 + RETROFIT SUB 7963 | 5 | 480 | 2400 | 0.0026811 | 5.5856e-06
2013-01-17 08:00AM | 220807 | R293 | Rural Short | REPLACE CONDEMNED POLES and INSTALL SVD'S | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2013-01-17 08:00AM | 221511 | 27446 | Rural Short | Install 1 bay of HV mains across river and commission new Substation. | 3 | 510 | 1530 | 0.0017092 | 3.3514e-06
2013-01-17 08:00AM | 221772 | 46487 | Rural Short | UPRATE TRANSFORMER AT SUB # 3402 - MACPHERSON RD LONDONDERRY | 11 | 480 | 5280 | 0.0058984 | 1.2288e-05
2013-01-17 08:00AM | 222597 | 8711 | Rural Short | REPLACE COLUMN | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2013-01-17 08:00AM | 223053 | 25744 | Rural Short | Relocate LV Mains to facilitate the construction of dam bank. | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2013-01-17 08:00AM | 221611 | WH1235 | Urban | Replace two poles. Reinstall TX 5048. Augment two bays of HV Mains | 34 | 480 | 16320 | 0.018231 | 3.7982e-05
2013-01-17 08:30AM | 219440 | MVF2 | Rural Short | Install DOFs. Augment 8 bays of HV mains to 120CCT. | 149 | 480 | 71520 | 0.079896 | 0.00016645
2013-01-17 08:30AM | 222060 | 27446 | Rural Short | Replace ABS 5059 with Auto LBS 92936 and replace Pole 99. | 25 | 420 | 10500 | 0.01173 | 2.7928e-05
2013-01-17 08:30AM | 222094 | MVF2 | Rural Short | Replace Poles and Augment a section of LV Mains | 22 | 480 | 10560 | 0.011797 | 2.4577e-05
2013-01-17 08:30AM | 222942 | BLA2 | Rural Short | Replace Condemned Pole 3PC345 and 3PC341 | 31 | 390 | 12090 | 0.013506 | 3.4631e-05
2013-01-17 08:30AM | 220897 | SHD2 | Urban | REPLACE ABS 71818 TO NEW LBS 96925 INSTALL EARTHING POINT AT ABS 37074RETRO FIT SUBS 41216 41825 | 167 | 360 | 60120 | 0.067161 | 0.00018656
2013-01-17 08:30AM | 222912 | UNC2 | Urban | Terminate new LV feeds | 74 | 390 | 28860 | 0.03224 | 8.2667e-05
2013-01-17 09:00AM | 220973 | BYC2 | Rural Short | Replace TX @ S/S 50731. | 14 | 300 | 4200 | 0.0046919 | 1.564e-05
2013-01-17 09:00AM | 221753 | 8776 | Urban | REPLACE COND POLE 207 | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-01-17 09:00AM | 222809 | WH1294 | Urban | Change over pole 337 and Pull pole | 24 | 240 | 5760 | 0.0064346 | 2.6811e-05
2013-01-17 09:00AM | 223026 | 8694 | Urban | Replace Ragbolt | 22 | 360 | 7920 | 0.0088476 | 2.4577e-05
2013-01-17 11:00AM | 222614 | S599 | Urban | LV Pole change | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2013-01-18 08:00AM | 217175 | D814 | Rural Short | River Crossing No. 45 - Retention @ Pole 136 Install New Ground Stay Install Vibration Dampeners and maintain existing stay @ pole 135. River Crossing No. 44 - Replace Poles 132 and 7 Install new Stay Poles Retention and Install Vibration dampeners. | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2013-01-18 08:00AM | 220850 | 46397 | Urban | Augment O/H HV conductor | 88 | 480 | 42240 | 0.047187 | 9.8307e-05
2013-01-18 08:30AM | 221695 | MG1267 | Rural Short | HV Upgrade | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2013-01-18 08:30AM | 222779 | BK1288 | Rural Short | Replace LV king bolt + Retension mains | 36 | 330 | 11880 | 0.013271 | 4.0216e-05
2013-01-18 08:30AM | 222721 | KMF2 | Urban | REPLACE POLE 4KD769 | 10 | 300 | 3000 | 0.0033514 | 1.1171e-05
2013-01-18 09:00AM | 222325 | S743 | Rural Short | Augment LV OH mains 150 ABC | 16 | 360 | 5760 | 0.0064346 | 1.7874e-05
2013-01-18 09:00AM | 222620 | 2815 | Urban | LV Pole change | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-01-18 09:00AM | 222933 | MR2225 | Urban | Remove LV Cables | 16 | 360 | 5760 | 0.0064346 | 1.7874e-05
2013-01-19 08:00AM | 220450 | 35827 | Rural Short | Augment 10 bays of HV OH mains. | 58 | 540 | 31320 | 0.034988 | 6.4793e-05
2013-01-19 08:00AM | 222638 | 25780 | Urban | Replace existing 22 kv 315 kva TX with 500 kva TX and replace LV switch gear with CB and 2 fuse strips | 24 | 480 | 11520 | 0.012869 | 2.6811e-05
2013-01-19 08:00AM | 222961 | 5874 | Urban | REPLACE POLE 1155 | 42 | 420 | 17640 | 0.019706 | 4.6919e-05
2013-01-20 05:00AM | 220162 | 35443 | Urban | RE-ARRANGE HV NETWORK | 2 | 1080 | 2160 | 0.002413 | 2.2342e-06
2013-01-20 07:00AM | 222017 | L502 | Urban | Replace 1 pole and augment 7 bays of HV Mains | 53 | 600 | 31800 | 0.035524 | 5.9207e-05
2013-01-20 07:00AM | 222537 | WX1280 | Urban | establish new pad sub 32335 | 23 | 600 | 13800 | 0.015416 | 2.5694e-05
2013-01-20 08:00AM | 218918 | 17069 | Urban | REPLACE HV SW GR SUB 26283 | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-01-20 08:00AM | 222427 | J489 | Urban | Replace condemned pole and augment 11kV OH mains. | 35 | 420 | 14700 | 0.016422 | 3.9099e-05
2013-01-20 08:30AM | 220606 | CRD2 | Urban | Replace condemned pole and replace Hv crossarms | 50 | 390 | 19500 | 0.021784 | 5.5856e-05
2013-01-21 06:00AM | 218573 | 8689 | Urban | REPLACE DAMAGED HV UG/OH POLE 6 | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-01-21 07:00AM | 223328 | 7995 | Urban | Prepare for Stringing new conductors to upgrade 33kV FDR 455 to 132KV for future new Doonside ZS and stand new concrete poles. | 134 | 540 | 72360 | 0.080835 | 0.00014969
2013-01-21 08:00AM | 222572 | L591 | Rural Short | REPLACE CONDEMNED POLE and RETROFIT SUB | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2013-01-21 08:00AM | 222577 | L591 | Rural Short | REPLACE HV CROSSARM and REPAIR HV TIE | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2013-01-21 08:00AM | 220988 | C830 | Urban | Isolate LV mains for replacement of HV cross arms. | 92 | 540 | 49680 | 0.055499 | 0.00010278
2013-01-21 08:00AM | 222867 | J491 | Urban | To Allow Staff To Replace Condemned Pole 1352 Hargrave St Leumeah | 29 | 480 | 13920 | 0.01555 | 3.2396e-05
2013-01-21 08:00AM | 223049 | J510 | Urban | Install new LV pillars via reconfiguration of LV circuit | 84 | 480 | 40320 | 0.045042 | 9.3838e-05
2013-01-21 08:00AM | 223319 | 5875 | Urban | Replacing pole/services | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2013-01-21 08:30AM | 219994 | MG1219 | Rural Short | Replace Poles and Augment Hv Mains | 81 | 480 | 38880 | 0.043434 | 9.0487e-05
2013-01-21 09:00AM | 223066 | BWA2 | Rural Short | Replace condemned pole 3R2418 | 21 | 240 | 5040 | 0.0056303 | 2.346e-05
2013-01-22 08:00AM | 221394 | X802 | Rural Short | REPLACE POLESINSTALL NEW SUB and AUGMENT HV MAINS | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-01-22 08:00AM | 222492 | T834 | Rural Short | RETROFIT SUBSINSTALL SVDS | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2013-01-22 08:00AM | 222826 | RWA2 | Rural Short | Install New LBS 86964ABS 86965 and Poles | 31 | 480 | 14880 | 0.016623 | 3.4631e-05
2013-01-22 08:00AM | 221334 | SWC2 | Urban | Replace 3 Poles 2 ABS's and DOF's on Sub. Augment 6 Bays of HV Mains. | 190 | 480 | 91200 | 0.10188 | 0.00021225
2013-01-22 08:00AM | 221718 | 8677 | Urban | Replace 4 poles. Augment 4 bays of HV mains. | 48 | 480 | 23040 | 0.025738 | 5.3622e-05
2013-01-22 08:00AM | 221763 | 35696 | Urban | Replace poles 15 and 12 augment 1 bay of O/H HV mains to 3 x 120mm CCT augment 1 bay of O/H LV mains and remove 4 bays of O/H S/L mains. Replace USL G451 with ABS 94463 | 185 | 600 | 111000 | 0.124 | 0.00020667
2013-01-22 08:00AM | 222110 | 2829 | Urban | Erect Pole 2 x HUGOH New PM SubRem 1 bay HV OH | 93 | 450 | 41850 | 0.046751 | 0.00010389
2013-01-22 08:30AM | 222088 | W163 | Rural Short | REPLACE CONDEMNED POLE | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2013-01-22 08:30AM | 222881 | P608 | Rural Short | Limited District switchingRetro Sub 11811 Braddocks rd WerombiRepair Leaning Pole Braddocks Rd Werombi | 30 | 420 | 12600 | 0.014076 | 3.3514e-05
2013-01-22 08:30AM | 221705 | WRD2 | Urban | Replace poles 4CK602 and 4CK655 replace TX and retro sub 42818 retro subs 41858 and 41137 and replace HV arm pole 4CK656 | 132 | 360 | 47520 | 0.053086 | 0.00014746
2013-01-22 08:30AM | 221754 | WRD2 | Urban | LV isolation in worksite | 66 | 360 | 23760 | 0.026543 | 7.373e-05
2013-01-22 08:30AM | 222430 | WWB2 | Urban | Trim trees clear of mains | 1 | 240 | 240 | 0.00026811 | 1.1171e-06
2013-01-22 09:00AM | 218071 | ULB2 | Urban | Replace 2 Condemned polesHighview Dr and Dolphin Point Rd DOLPHIN POINT | 150 | 330 | 49500 | 0.055297 | 0.00016757
2013-01-22 09:00AM | 223142 | GV1278 | Urban | Remove redundant HV on mains | 14 | 360 | 5040 | 0.0056303 | 1.564e-05
2013-01-23 08:00AM | 219821 | 10245 | Rural Short | Replace two poles augment 1 bay of HV OH mains and replace two USL with 20A DOF's. | 189 | 540 | 102060 | 0.11401 | 0.00021114
2013-01-23 08:00AM | 220362 | 10245 | Rural Short | Isolate LV mains for replacement of the poles. | 64 | 540 | 34560 | 0.038608 | 7.1496e-05
2013-01-23 08:00AM | 221916 | C814 | Rural Short | uprate tx and rewire lv links and fuses | 15 | 510 | 7650 | 0.008546 | 1.6757e-05
2013-01-23 08:00AM | 222748 | L588 | Rural Short | REPLACE CONDEMNED POLE and RETROFIT SUBS | 34 | 420 | 14280 | 0.015952 | 3.7982e-05
2013-01-23 08:00AM | 222846 | R260 | Rural Short | Stand new poles 826218 826219 826220 826221 826222 and 826223 | 46 | 450 | 20700 | 0.023124 | 5.1388e-05
2013-01-23 08:00AM | 223159 | 68195 | Urban | Stand Poles | 6 | 480 | 2880 | 0.0032173 | 6.7027e-06
2013-01-23 08:00AM | 223211 | 2829 | Urban | REPLACE POLE SUB 1799 | 62 | 480 | 29760 | 0.033245 | 6.9261e-05
2013-01-23 08:30AM | 220650 | BLA2 | Rural Short | Replace Condemned poles | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2013-01-23 08:30AM | 221936 | 35988 | Rural Short | Limited District Switching Request Change Condemned Sub Pole 31 Sub 10904 and repair pole cap | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2013-01-23 08:30AM | 221068 | SHE2 | Urban | Retro sub 43124 | 12 | 240 | 2880 | 0.0032173 | 1.3405e-05
2013-01-23 08:45AM | 223170 | CJ1267 | Urban | Relace Condemned Pole | 51 | 195 | 9945 | 0.01111 | 5.6973e-05
2013-01-23 09:00AM | 218625 | ULL2 | Rural Short | Install New LBS and DOFPrinces Hwy TERMEIL. | 10 | 330 | 3300 | 0.0036865 | 1.1171e-05
2013-01-23 09:00AM | 222074 | 9056 | Urban | REMOVE ABS C419 AND INSTALL LBS 96986 | 37 | 360 | 13320 | 0.01488 | 4.1333e-05
2013-01-23 09:00AM | 222679 | 35010 | Urban | L/V U/G CABLE WORK TO RECONFIGURE 2X L/V PILLARS 100290 and 100291 | 23 | 360 | 8280 | 0.0092498 | 2.5694e-05
2013-01-23 09:00AM | 223490 | 8685 | Urban | Cable Fault | 45 | 360 | 16200 | 0.018097 | 5.027e-05
2013-01-23 09:00AM | 223734 | GV1278 | Urban | Remove HV OH redundant mains | 58 | 360 | 20880 | 0.023325 | 6.4793e-05
2013-01-23 09:30AM | 217069 | HKD2 | Rural Short | Replace pole 3GV072. | 103 | 330 | 33990 | 0.037971 | 0.00011506
2013-01-23 09:30AM | 222686 | HBC2 | Urban | REPLACE ABS 74962 with NEW ABS 123277 | 10 | 330 | 3300 | 0.0036865 | 1.1171e-05
2013-01-24 01:00PM | 223491 | C824 | Urban | Cable Fault Location | 10 | 120 | 1200 | 0.0013405 | 1.1171e-05
2013-01-24 03:30PM | 220214 | 8634 | Rural Short | augment lv mains | 2 | 60 | 840 | 0.00093838 | 2.2342e-06
2013-01-24 05:00PM | 221279 | 25741 | Urban | establish new pad sub 32225 | 272 | 30 | 6180 | 0.0069038 | 0.00030386
2013-01-24 06:30AM | 218572 | T882 | Urban | Install new sub 29910 and section of high voltage cable and connect to the existing networkAlso remove a section of over head mains | 72 | 630 | 22680 | 0.025336 | 8.0433e-05
2013-01-24 06:30AM | 221279 | 25741 | Urban | establish new pad sub 32225 | 272 | 30 | 6180 | 0.0069038 | 0.00030386
2013-01-24 08:00AM | 220214 | 8634 | Rural Short | augment lv mains | 26 | 510 | 7140 | 0.0079762 | 2.9045e-05
2013-01-24 08:00AM | 221351 | D814 | Rural Short | Replace River Crossing Poles 311057 and 311062. Install 2 new ground stays. Install Vibration Dampeners. | 3 | 450 | 1350 | 0.0015081 | 3.3514e-06
2013-01-24 08:00AM | 222824 | 8711 | Rural Short | REPLACE COLUMN | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2013-01-24 08:00AM | 222849 | W163 | Rural Short | REPLACE CONDEMNED POLESREPLACE DOF'S and RETROFIT SUB | 45 | 450 | 20250 | 0.022622 | 5.027e-05
2013-01-24 08:00AM | 218572 | T882 | Urban | Install new sub 29910 and section of high voltage cable and connect to the existing networkAlso remove a section of over head mains | 72 | 540 | 19440 | 0.021717 | 8.0433e-05
2013-01-24 08:00AM | 220507 | CJ1204 | Urban | Augment OH mains 19/3.25 AAC.Replace/change over poles.Replace HV xarm Sub 4239. | 88 | 480 | 42240 | 0.047187 | 9.8307e-05
2013-01-24 08:00AM | 221279 | 25741 | Urban | establish new pad sub 32225 | 140 | 480 | 98880 | 0.11046 | 0.0001564
2013-01-24 08:00AM | 221648 | SWC2 | Urban | Replace 2 Poles DOF's on Sub and ABS. Augment 10 Bays of HV Mains to 19/3.25 AAC and 1 Bay of HV Mains to 7/4.50 AAC | 274 | 480 | 131520 | 0.14692 | 0.00030609
2013-01-24 08:15AM | 221390 | MVB2 | Rural Short | Remove Sub 31451. Install new Sub 29653 and assoc mains | 18 | 465 | 8370 | 0.0093503 | 2.0108e-05
2013-01-24 08:30AM | 217546 | MG1267 | Rural Short | Augment HV Mains | 155 | 480 | 74400 | 0.083114 | 0.00017315
2013-01-24 08:30AM | 221418 | BLA2 | Rural Short | Replace Condemned Pole and ABS pole and retrofit sub | 370 | 420 | 94500 | 0.10557 | 0.00041333
2013-01-24 08:30AM | 222736 | KME2 | Rural Short | Install new Service Pillar 111555A and replace pillar 75363 with a new Industrial Commercial Link pillar 123182. | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2013-01-24 08:30AM | 222608 | WWE2 | Urban | Remove 1 bay HV mains. Connect new HV cable UGOH pole to switch. | 90 | 420 | 37800 | 0.042227 | 0.00010054
2013-01-24 09:00AM | 220284 | ULC2 | Rural Short | Install New Sectionaliser 97500 Remove USL 41778 Install New LBS and USLsGarrads Ln MILTON | 42 | 330 | 13860 | 0.015483 | 4.6919e-05
2013-01-24 09:00AM | 223492 | 49357 | Urban | Cable Fault | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2013-01-25 07:00AM | 223203 | 48178 | Urban | Extend LV Cables | 33 | 360 | 11880 | 0.013271 | 3.6865e-05
2013-01-25 08:00AM | 220843 | 8799 | Rural Short | Augment 3 bays of O/H HV mains to 3 x 120mm CCT and replace ABS 48258 with Sectionaliser 94275. | 5 | 510 | 2550 | 0.0028487 | 5.5856e-06
2013-01-25 08:00AM | 222900 | 57444 | Rural Short | REPAIR LEANING POLEREPLACE HV CROSSARMS and USL'S andRETROFIT SUBS | 19 | 420 | 7980 | 0.0089146 | 2.1225e-05
2013-01-25 08:00AM | 219603 | 25780 | Urban | REPLACE LV SW GR SUB 13852 | 33 | 480 | 15840 | 0.017695 | 3.6865e-05
2013-01-25 08:00AM | 220873 | 46397 | Urban | Augment O/H HV mains | 141 | 480 | 67680 | 0.075607 | 0.00015751
2013-01-25 08:00AM | 223239 | MR2225 | Urban | REPOSITION EX PILLAR 106880 and ST LIGHT COLUMN | 11 | 420 | 4620 | 0.0051611 | 1.2288e-05
2013-01-25 08:00AM | 223481 | 68195 | Urban | Replace LV Mains | 15 | 420 | 6300 | 0.0070379 | 1.6757e-05
2013-01-25 08:00AM | 223555 | GV1208 | Urban | Replace pole 330928 | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-01-25 08:30AM | 220857 | MG1267 | Rural Short | HV Upgrade | 20 | 480 | 9600 | 0.010724 | 2.2342e-05
2013-01-25 08:30AM | 221626 | 8802 | Rural Short | Replace Condemned Pole J22 | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2013-01-25 08:30AM | 222368 | 25450 | Urban | Replace burnt ABS pole Retrofit Subs and trim trees | 208 | 420 | 87360 | 0.097592 | 0.00023236
2013-01-25 08:30AM | 222717 | DP1269 | Urban | REPLACE POLE and ABS 70675 INSTALL NEW LBS 96457 RETRO SUB 40652 | 74 | 420 | 31080 | 0.03472 | 8.2667e-05
2013-01-25 09:00AM | 219767 | ULL2 | Rural Short | Install New 20A DOF 97455 ( Replace pole 1GY034 )Princes Hwy TABOURIE | 7 | 330 | 2310 | 0.0025805 | 7.8198e-06
2013-01-25 09:00AM | 222842 | RWB2 | Rural Short | Replace Condemned Pole 3J0369 and Retrofit DOFs at Sub 30271 | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2013-01-25 09:00AM | 223247 | W124 | Rural Short | Rectify LV consac defect | 70 | 360 | 25200 | 0.028151 | 7.8198e-05
2013-01-25 09:00AM | 223318 | S743 | Rural Short | Augment lv OH mains from pole 842307 to pole 842318 | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2013-01-25 09:00AM | 221590 | BDE2 | Urban | Replace Condemned pole 1XY115Edwards Ave BOMADERRY. | 104 | 330 | 34320 | 0.03834 | 0.00011618
2013-01-26 08:00AM | 221451 | UNE2 | Urban | Remove HV mains + replace pole | 220 | 360 | 64440 | 0.071987 | 0.00024577
2013-01-29 08:00AM | 221525 | 2815 | Urban | Replace pole + Augment HV mains | 129 | 480 | 61920 | 0.069172 | 0.00014411
2013-01-29 08:00AM | 221829 | 35696 | Urban | Replace poles 11 and Sub pole 9 remove 4 bays of O/H S/L mains Replace USL 12967 with LBS 94464. | 99 | 510 | 50490 | 0.056403 | 0.00011059
2013-01-29 08:30AM | 223114 | JBB2 | Rural Short | 11kV OUTAGE TO INSTALL 3 NEW POLES CONDUCTOR AND OHEW BETWEEN ABS 61691 AND ABS 73309 on 33KV FDR 7009 | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-01-29 09:00AM | 223541 | 35306 | Urban | Change over services/poles | 21 | 360 | 7560 | 0.0084454 | 2.346e-05
2013-01-29 09:00AM | 223848 | 2820 | Urban | Replace LV Switch | 25 | 240 | 6000 | 0.0067027 | 2.7928e-05
2013-01-29 10:00AM | 223019 | 48189 | Urban | DISTRIBUTION EARTH REFURBISHMENT | 48 | 240 | 11520 | 0.012869 | 5.3622e-05
2013-01-29 11:00PM | 223374 | 48168 | Urban | Replace HV Switching Station | 445 | 60 | 26700 | 0.029827 | 0.00049712
2013-01-30 08:00AM | 217438 | 35827 | Rural Short | Augment 5 bays of HV OH mains. | 9 | 540 | 4860 | 0.0054292 | 1.0054e-05
2013-01-30 08:00AM | 221519 | 35827 | Rural Short | Isolate LV mains for HV OH augmentation. | 21 | 540 | 11340 | 0.012668 | 2.346e-05
2013-01-30 08:00AM | 222985 | L579 | Rural Short | CHANGE 2 LOW VOLTAGE ARMS | 64 | 390 | 24960 | 0.027883 | 7.1496e-05
2013-01-30 08:00AM | 220631 | L544 | Urban | REPLACE POLE 778 | 16 | 420 | 6720 | 0.007507 | 1.7874e-05
2013-01-30 08:00AM | 221987 | R247 | Urban | augment lv mains and change pole and change links and fuses on sub | 113 | 510 | 57630 | 0.06438 | 0.00012623
2013-01-30 08:00AM | 222764 | 19871 | Urban | TERMINATE SCandE CABLE TO SW 7868 SUB 2298. TERMINATE NEW CABLE TO SW 70558 SUB 27287 and LEAVE OTHER END SCandE ADJ SW 19203 SUB 12881.PITT ST PARRAMATTA | 67 | 450 | 30150 | 0.033681 | 7.4847e-05
2013-01-30 08:00AM | 223669 | J489 | Urban | LIMITED DISTRICT SWITCHING-Replace Condemned Pole | 16 | 420 | 6720 | 0.007507 | 1.7874e-05
2013-01-30 08:30AM | 221787 | BLA2 | Rural Short | Replace poles. Replace HV and LV crossarms and Retrofit Sub 40185 | 112 | 420 | 47040 | 0.052549 | 0.00012512
2013-01-30 08:30AM | 222425 | W163 | Rural Short | REPAIR HV CROSSARMS.(TWIN ARM) | 7 | 330 | 2310 | 0.0025805 | 7.8198e-06
2013-01-30 08:30AM | 222875 | UNC2 | Urban | Augment HV Mains Commission LBS 96451RETRO S/S 42508 Commission FT1203 Feeder | 146 | 420 | 61320 | 0.068502 | 0.0001631
2013-01-30 08:30AM | 223096 | WWB2 | Urban | RETROFIT SUB | 41 | 420 | 17220 | 0.019237 | 4.5802e-05
2013-01-30 08:30AM | 223326 | RVF2 | Urban | INVESTIGATE FAULTY RECLOSER | 35 | 360 | 12600 | 0.014076 | 3.9099e-05
2013-01-30 09:00AM | 223893 | GV1249 | Urban | LV Pole change | 16 | 180 | 2880 | 0.0032173 | 1.7874e-05
2013-01-31 01:00PM | 223612 | BDF2 | Rural Short | REPLACE STREET LIGHT COLUMNS | 129 | 120 | 15480 | 0.017293 | 0.00014411
2013-01-31 03:30PM | 220383 | 8634 | Rural Short | augment hv mains | 2 | 60 | 180 | 0.00020108 | 2.2342e-06
2013-01-31 07:00AM | 220732 | 25775 | Urban | ID and Spike HV cable STJ and redirect to new pad sub 26563 | 103 | 600 | 61800 | 0.069038 | 0.00011506
2013-01-31 08:00AM | 220383 | 8634 | Rural Short | augment hv mains | 4 | 510 | 1530 | 0.0017092 | 4.4685e-06
2013-01-31 08:00AM | 223304 | RWA2 | Rural Short | Augment HV OH mains | 18 | 480 | 8640 | 0.0096519 | 2.0108e-05
2013-01-31 08:00AM | 220795 | T893 | Urban | REPLACE POLE 338 | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2013-01-31 08:00AM | 221766 | B205 | Urban | Replace ABS. Augment 4 bays of HV mains. | 74 | 480 | 35520 | 0.03968 | 8.2667e-05
2013-01-31 08:00AM | 223622 | GV1241 | Urban | CONNECT NEW L/V PILLAR 121359 VIA NEW LENGTH OF 240mm XLPE CABLE TO L/V PILLAR 93399 | 14 | 240 | 3360 | 0.0037535 | 1.564e-05
2013-01-31 08:00AM | 223679 | A337 | Urban | LV CABLE FAULT BETWEEN PM SUB 18243 AND COLUMN 42123. | 11 | 360 | 3960 | 0.0044238 | 1.2288e-05
2013-01-31 08:30AM | 222084 | WBD2 | Rural Short | REPLACE HV XARMS RETROFIT SUBS INSTALL NEW POLE. | 325 | 420 | 136500 | 0.15249 | 0.00036306
2013-01-31 08:30AM | 223067 | WBC2 | Rural Short | Trim Overhanging trees | 82 | 240 | 19680 | 0.021985 | 9.1604e-05
2013-01-31 08:30AM | 223119 | JBB2 | Rural Short | 11kV OUTAGE TO INSTALL 3 NEW POLES CONDUCTOR AND OHEW BETWEEN ABS 61691 AND ABS 73309 FDR 7009 | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-01-31 08:30AM | 223291 | H745 | Rural Short | LIMITED DISTRICT SWITCHINGReplace DOF's K409 Replace HV Xarms @ poles 297581 | 26 | 420 | 10920 | 0.012199 | 2.9045e-05
2013-01-31 08:30AM | 223201 | KMB2 | Urban | Replace ABS 70977 (PIN # D871) replace HV Arm poles 4JD340 and 4JD284 replace LV Fuses sub 41000 and replace LV arm pole 4JD334 | 135 | 240 | 32400 | 0.036195 | 0.00015081
2013-01-31 08:30AM | 223902 | KYC2 | Urban | NEW LV PILLAR | 86 | 450 | 38700 | 0.043233 | 9.6072e-05
2013-01-31 09:00AM | 223162 | NG1210 | Rural Short | Retrofit Sub 10315 | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2013-01-31 09:00AM | 219876 | ULB2 | Urban | Replace Condemned pole 2RH178Moore St BURRILL LAKE | 160 | 330 | 52800 | 0.058984 | 0.00017874
2013-01-31 09:00AM | 222087 | FF1202 | Urban | REPLACE ABS 4955 WITH LBS 95517 | 21 | 360 | 7560 | 0.0084454 | 2.346e-05
2013-01-31 09:00AM | 223854 | X863 | Urban | Replace LV pole | 13 | 180 | 2340 | 0.0026141 | 1.4523e-05
2013-01-31 09:00AM | 223928 | CJ1249 | Urban | Maintenance - Replace Switch | 20 | 240 | 4800 | 0.0053622 | 2.2342e-05
2013-01-31 09:30AM | 223063 | BDF2 | Rural Short | REPLACE POLES 1TY004 and 1TY001 | 13 | 330 | 4290 | 0.0047924 | 1.4523e-05
2013-01-31 09:30AM | 223412 | BYG2 | Rural Short | RETRO-FIT SUB 50696 | 3 | 270 | 810 | 0.00090487 | 3.3514e-06
2013-01-31 09:30AM | 223611 | BDF2 | Rural Short | REPLACE STREET LIGHT COLUMNS | 129 | 150 | 19350 | 0.021616 | 0.00014411
2013-02-01 01:00PM | 223619 | BDA2 | Urban | REPLACE STREET LIGHT COLUMNS | 29 | 120 | 3480 | 0.0038876 | 3.2396e-05
2013-02-01 08:00AM | 220854 | 8799 | Rural Short | Augment 3 bays of O/H HV mains to 3 x 120mm CCT and replace ABS 20877 with SCADA controlled LBS 94276. | 7 | 510 | 3570 | 0.0039881 | 7.8198e-06
2013-02-01 08:00AM | 222980 | 35816 | Rural Short | Replace USL 12404 with DOF's 96851 retrofit Sub 12166 and rectify defects | 11 | 450 | 4950 | 0.0055297 | 1.2288e-05
2013-02-01 08:00AM | 223127 | 57448 | Rural Short | INSTALL NEW DOF'S | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2013-02-01 08:00AM | 223728 | 10244 | Rural Short | HV and LV ISOLATION FOR TREE REMOVALS | 31 | 480 | 14880 | 0.016623 | 3.4631e-05
2013-02-01 08:00AM | 220796 | CJ1204 | Urban | Augment HV OH mains to 7/4.5 AAC.Change over poles.Replace HV xarm Sub 3210. | 51 | 480 | 24480 | 0.027347 | 5.6973e-05
2013-02-01 08:00AM | 220804 | 1950 | Urban | REPLACE POLE 784 | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2013-02-01 08:00AM | 221350 | 2815 | Urban | Replace poles | 218 | 480 | 104640 | 0.1169 | 0.00024353
2013-02-01 08:00AM | 223359 | 7995 | Urban | Spike/ID cable Install STJ and new Pillar Relocate Ragbolt | 3 | 390 | 1170 | 0.001307 | 3.3514e-06
2013-02-01 08:00AM | 223805 | 49918 | Urban | REPLACE RUSTY COLUMN | 34 | 180 | 6120 | 0.0068368 | 3.7982e-05
2013-02-01 08:30AM | 221741 | MG1267 | Rural Short | HV Upgrade | 55 | 480 | 26400 | 0.029492 | 6.1442e-05
2013-02-01 08:30AM | 222938 | BK1299 | Rural Short | Replace pole and USL | 3 | 390 | 1170 | 0.001307 | 3.3514e-06
2013-02-01 08:30AM | 223618 | BK1299 | Rural Short | Isolate LV so as to change pole and USL | 16 | 390 | 6240 | 0.0069708 | 1.7874e-05
2013-02-01 09:00AM | 223355 | 5877 | Urban | Change X pole 46 Fdr 445 | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2013-02-01 09:30AM | 223615 | BDA2 | Urban | REPLACE STREET LIGHT COLUMNS | 74 | 150 | 11100 | 0.0124 | 8.2667e-05
2013-02-01 10:00AM | 223799 | 49918 | Urban | REPLACE RUSTY STREET LIGHT COLUMN | 21 | 180 | 3780 | 0.0042227 | 2.346e-05
2013-02-02 08:00AM | 213387 | DP1258 | Urban | REPLACE ONE POLE AND AUGMENT ONE BAY OF HV MAINS TO 7/4.50AAC | 92 | 480 | 44160 | 0.049332 | 0.00010278
2013-02-02 08:00AM | 222639 | UNC2 | Urban | Remove HV mains terminate HV cable Run new HV mains | 312 | 450 | 100350 | 0.1121 | 0.00034854
2013-02-03 07:00AM | 218984 | 1958 | Urban | RETROFIT + TX CHANGE SUB 2903 | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2013-02-03 07:30AM | 223809 | 4870 | Urban | REMOVE DOF 7113 and EXISTING UG/OH CABLE.TERMINATE CABLE P.M SUB 4940 SW 66083 | 5 | 510 | 2550 | 0.0028487 | 5.5856e-06
2013-02-03 08:00AM | 222805 | CT1265 | Urban | To allow staff to replace Condemned Pole 2318 and ABS 16722 with New Pole 878894 and ABS 123872 Badgally Rd Campbelltown | 31 | 480 | 14880 | 0.016623 | 3.4631e-05
2013-02-03 08:00AM | 223001 | SWD2 | Urban | STRAIGHTEN POLE AND REPLACE LV MAINS | 3 | 330 | 990 | 0.0011059 | 3.3514e-06
2013-02-03 08:00AM | 223139 | W184 | Urban | (1). ID and Spike HV cable between CB W184 in Bow Bowing Zone and Sw 17260 in PM 11945. (2).Install new 315KVA PM 29426.Rebond HV earth at PM 11945. (3). Commissioning tests on new section of Ug cable. | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2013-02-03 08:30AM | 223375 | MG1282 | Rural Short | HV Switchgear MandR at Pad Sub 31833 | 13 | 300 | 3900 | 0.0043568 | 1.4523e-05
2013-02-03 08:30AM | 223158 | UNB2 | Urban | TRIM TREE OVERHANGS | 45 | 240 | 10800 | 0.012065 | 5.027e-05
2013-02-03 09:00AM | 215191 | BDE2 | Urban | Install New LBS 92799 New DOF 92798 and Augment HVMeroo Rd and Concorde Way BOMADERRY. | 46 | 330 | 15180 | 0.016958 | 5.1388e-05
2013-02-03 09:00AM | 222093 | 9052 | Urban | REPLACE ABS 8376 WITH LBS 96819 | 33 | 360 | 11880 | 0.013271 | 3.6865e-05
2013-02-04 07:00AM | 222009 | 7995 | Urban | Pull OPGW and put OH conctruction back 33kV FDR 455 to 132KV for future new Doonside ZS. | 44 | 540 | 71820 | 0.080232 | 4.9153e-05
2013-02-04 07:00AM | 222009 | 7995 | Urban | Pull OPGW and put OH conctruction back 33kV FDR 455 to 132KV for future new Doonside ZS. | 222 | 600 | 79800 | 0.089146 | 0.000248
2013-02-04 08:00AM | 222668 | A096 | Rural Short | REPLACE SERVICES FROM POLE # 131 THAT IS BEING REPLACED | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2013-02-04 08:00AM | 223086 | P608 | Rural Short | Stand new pole and prepare for augment. | 13 | 420 | 5460 | 0.0060995 | 1.4523e-05
2013-02-04 08:00AM | 223110 | MG1267 | Rural Short | Replace Pole and Augment Hv Oh MainsInstall New ABS and New LBS.Uprate DOF's 42630 | 4 | 510 | 165750 | 0.18516 | 4.4685e-06
2013-02-04 08:00AM | 221077 | C830 | Urban | Isolate LV mains for replacement of HV cross arms. | 77 | 540 | 41580 | 0.04645 | 8.6018e-05
2013-02-04 08:00AM | 222976 | 2820 | Urban | Change SW/gr Sub 16184Install cable and New PM Sub 32180 | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2013-02-04 08:00AM | 223174 | W118 | Urban | Relocate 2 X poles to new location and relocate existing conductor to new location | 6 | 540 | 3240 | 0.0036195 | 6.7027e-06
2013-02-04 08:30AM | 222675 | R260 | Rural Short | HV Isolation for Railcorp essential maintenance | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-02-04 08:30AM | 223110 | MG1267 | Rural Short | Replace Pole and Augment Hv Oh MainsInstall New ABS and New LBS.Uprate DOF's 42630 | 646 | 480 | 156000 | 0.17427 | 0.00072166
2013-02-04 08:30AM | 223627 | MG1267 | Rural Short | Replace Condemned Pole 3V0534 and Retrofit DOFs at Sub 31510 | 36 | 330 | 11880 | 0.013271 | 4.0216e-05
2013-02-04 08:30AM | 224205 | 57448 | Rural Short | REPLACE TX AND RETRO SUB 14994 AND RETRO SUB 14993 | 1 | 390 | 390 | 0.00043568 | 1.1171e-06
2013-02-04 08:30AM | 222754 | MYQ2 | Urban | Trim Trees near pole 792307 | 137 | 180 | 24660 | 0.027548 | 0.00015305
2013-02-04 09:00AM | 223424 | APE2 | Urban | RECONNECT UGOH MandR ABS 70821 | 105 | 901 | 94605 | 0.10569 | 0.0001173
2013-02-04 09:00AM | 224265 | 52237 | Urban | Repair column 16034 | 5 | 240 | 1200 | 0.0013405 | 5.5856e-06
2013-02-04 12:30AM | 220375 | WH1257 | Urban | HVSWGR MAINT AND REPUMP SPS 13884 | 28 | 420 | 5880 | 0.0065687 | 3.1279e-05
2013-02-05 08:00AM | 220833 | X877 | Rural Short | REPLACE CONDEMNED POLE 29 | 5 | 480 | 2400 | 0.0026811 | 5.5856e-06
2013-02-05 08:00AM | 223597 | A096 | Rural Short | REPLACE CONDEMNED POLE # 153 | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-02-05 08:00AM | 224071 | NG1210 | Rural Short | Repair ABS 13117 Pin Defect D380 | 27 | 360 | 9720 | 0.010858 | 3.0162e-05
2013-02-05 08:00AM | 220800 | CJ1204 | Urban | Replace pole 494.Replace USL 4568 with ABS 77340.Augment HV OH mains 19/3.25 AAC | 62 | 480 | 29760 | 0.033245 | 6.9261e-05
2013-02-05 08:00AM | 223056 | SWC2 | Urban | Replace 3 Poles. Install New DOF's on Sub. Augment 8 Bays of 7/4.50AAC | 248 | 480 | 119040 | 0.13298 | 0.00027705
2013-02-05 08:30AM | 221887 | BLA2 | Rural Short | Replace Condemned pole 3PD128 and Trim tree | 66 | 390 | 25740 | 0.028755 | 7.373e-05
2013-02-05 08:30AM | 223035 | RWE2 | Rural Short | REPLACE STEEL MAINS INSTALL DOFs 90889 REPLACE POLE 3J0904 REPLACE CONDEMNED POLE 3J1419 and RETROFIT SUB 30105 AND REPLACE TX | 5 | 450 | 2250 | 0.0025135 | 5.5856e-06
2013-02-05 08:30AM | 223175 | L948 | Rural Short | Replace condemned pole 8 | 16 | 390 | 6240 | 0.0069708 | 1.7874e-05
2013-02-05 08:30AM | 223483 | MVH2 | Rural Short | Replace X Pole 3KO219 (Structure 132).Replace Poles 3KO171 3HO218 218831 (Structures 133 131 130). | 14 | 510 | 7140 | 0.0079762 | 1.564e-05
2013-02-05 08:30AM | 224193 | L947 | Rural Short | Replace LV crossarm pole 286 | 24 | 390 | 9360 | 0.010456 | 2.6811e-05
2013-02-05 08:30AM | 223146 | M400 | Urban | REPLACE DAMGED LV PILLAR | 19 | 360 | 6840 | 0.0076411 | 2.1225e-05
2013-02-05 09:00AM | 223308 | NA1207 | Rural Short | Remove ABS 31026.Install LBS 122848. | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2013-02-05 09:00AM | 224070 | APC2 | Rural Short | REPLACE ABS 74102 | 62 | 360 | 22320 | 0.024934 | 6.9261e-05
2013-02-05 09:00AM | 218143 | ULB2 | Urban | Replace Condemned poles 2RH234 - S/S 72300 and 2PX018Wallaroy Dr BURRILL LAKE | 185 | 330 | 61050 | 0.0682 | 0.00020667
2013-02-05 09:30AM | 222650 | BLA2 | Rural Short | Tree Trimming | 119 | 180 | 21420 | 0.023929 | 0.00013294
2013-02-06 08:00AM | 222573 | KC1262 | Rural Short | REPLACE COND POLE 180 | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-02-06 08:00AM | 222772 | 8637 | Rural Short | Replace cast iron UGOHs @ poles 25 and 84 | 24 | 480 | 5760 | 0.0064346 | 2.6811e-05
2013-02-06 08:00AM | 223781 | 35818 | Rural Short | MandR ABS J304 And replace HV HardwareReplace DOF's J303 | 26 | 420 | 10920 | 0.012199 | 2.9045e-05
2013-02-06 08:00AM | 221836 | WH1209 | Urban | Replace 3 poles and one ABS. | 86 | 540 | 46440 | 0.051879 | 9.6072e-05
2013-02-06 08:00AM | 221837 | WH1209 | Urban | Isolate LV mains for replacement of 3 poles. | 216 | 540 | 116640 | 0.1303 | 0.0002413
2013-02-06 08:00AM | 221873 | 35696 | Urban | Augment 5 bays of O/H HV mains to 3 x 120mm CCT. | 219 | 510 | 111690 | 0.12477 | 0.00024465
2013-02-06 08:00AM | 222005 | 8738 | Urban | Augmemt OH Conductor | 109 | 480 | 52320 | 0.058448 | 0.00012177
2013-02-06 08:00AM | 223180 | W120 | Urban | Uprate Pole Sub | 10 | 420 | 4200 | 0.0046919 | 1.1171e-05
2013-02-06 08:00AM | 223875 | 5506 | Urban | INSTALL SERVICE POLE and 2 X SERVICES | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2013-02-06 08:00AM | 224441 | 25782 | Urban | Isolate LV to bond in 2 LV cables to existing pillars | 10 | 300 | 3900 | 0.0043568 | 1.1171e-05
2013-02-06 08:30AM | 222471 | WBC2 | Rural Short | Replace switch | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-02-06 08:30AM | 223128 | MG1267 | Rural Short | HV Upgrade | 27 | 480 | 12960 | 0.014478 | 3.0162e-05
2013-02-06 08:30AM | 223265 | MG1267 | Rural Short | Upgrade HV Network | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2013-02-06 08:30AM | 224233 | 8636 | Rural Short | To transfer LV OH mains to new pole | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2013-02-06 09:00AM | 223306 | X492 | Rural Long | INSTALL AVIATION SAFETY BALLS | 15 | 360 | 5400 | 0.0060324 | 1.6757e-05
2013-02-06 09:00AM | 223708 | BDF2 | Rural Short | Augment H/V conductors from pole 808552 to Pole 776057 | 25 | 360 | 9000 | 0.010054 | 2.7928e-05
2013-02-06 09:00AM | 223798 | CLC2 | Urban | Change Pole 3GA073 | 9 | 360 | 3240 | 0.0036195 | 1.0054e-05
2013-02-06 09:00AM | 224267 | 25775 | Urban | Quality of Supply | 2 | 120 | 240 | 0.00026811 | 2.2342e-06
2013-02-06 09:00AM | 224441 | 25782 | Urban | Isolate LV to bond in 2 LV cables to existing pillars | 16 | 240 | 3120 | 0.0034854 | 1.7874e-05
2013-02-06 09:30AM | 224466 | CV1210 | Urban | Replace O/W with ABC | 4 | 270 | 1080 | 0.0012065 | 4.4685e-06
2013-02-06 10:00PM | 223510 | DP1295 | Urban | CLEARANCE TO REPLACE STREETLIGHT 4AJ306. | 124 | 180 | 22320 | 0.024934 | 0.00013852
2013-02-07 07:30AM | 224003 | 9059 | Urban | Replace Condemned Pole | 14 | 390 | 5460 | 0.0060995 | 1.564e-05
2013-02-07 08:00AM | 220962 | X877 | Rural Short | REPLACE COND POLE 86 REPLACE USL7502 WITH NEW USL 123530 RETRO SUB 5232 MandR HV and LV ARMS | 9 | 480 | 4320 | 0.004826 | 1.0054e-05
2013-02-07 08:00AM | 221043 | S743 | Rural Short | Install/augment HV OH mains to 150 NMS ABC.Install temp HV OH mains 7/4.5 AAC. Twin arm HV Sub 6640 for future HV ABC. | 42 | 480 | 20160 | 0.022521 | 4.6919e-05
2013-02-07 08:00AM | 223255 | P608 | Rural Short | Stand Poles 822265 822261 and 822260 replacing poles 22 and 23 | 9 | 480 | 4320 | 0.004826 | 1.0054e-05
2013-02-07 08:00AM | 223350 | L948 | Rural Short | Replace lv x-arm+ 3 fuses and earth batten @ pole sub 3741 | 16 | 420 | 6720 | 0.007507 | 1.7874e-05
2013-02-07 08:00AM | 223378 | W163 | Rural Short | REPLACE HV XARMS AT POLES 410604 and410576 | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2013-02-07 08:00AM | 223877 | R248 | Urban | REPLACE ROAD CROSSING SERVICE | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2013-02-07 08:00AM | 223959 | SWC2 | Urban | Install New stay Pole. Install New DOF's on Sub. Augment 2 Bays of HV Mains to 7/4.50 AAC | 114 | 480 | 54720 | 0.061129 | 0.00012735
2013-02-07 08:00AM | 224096 | 35511 | Urban | REPLACE CONDEMNED COLUMN # 716970 | 14 | 240 | 3360 | 0.0037535 | 1.564e-05
2013-02-07 08:30AM | 222915 | 25403 | Rural Short | Install new LBS 89358 + pole | 14 | 360 | 5040 | 0.0056303 | 1.564e-05
2013-02-07 08:30AM | 223237 | MVH2 | Rural Short | Complete 11kV works including replacing ABS 50128 with Load Break Switch augmenting one span of 11 kV conductor and attaching LV O/H to Pole 3KO003. | 65 | 510 | 33150 | 0.037033 | 7.2613e-05
2013-02-07 08:30AM | 223386 | L582 | Rural Short | REPLACE CONDEMNED POLE *LIMITED DISTRICT SWITCHING* | 3 | 390 | 1170 | 0.001307 | 3.3514e-06
2013-02-07 08:30AM | 223767 | MVB2 | Rural Short | Replace Poles Install New LBS 89727 Install New DOFs 89278 and Augment a section of 11KV O/H Mains | 219 | 450 | 98550 | 0.11009 | 0.00024465
2013-02-07 08:30AM | 222480 | HBB2 | Urban | Replace Sub pole 40135 and ABS pole 71548 | 242 | 420 | 71820 | 0.080232 | 0.00027034
2013-02-07 08:30AM | 222595 | WWB2 | Urban | Tree Trimming of overhangs and Maintenance | 12 | 390 | 4680 | 0.0052281 | 1.3405e-05
2013-02-07 09:00AM | 218162 | YYA2 | Rural Short | Replace Condemned pole 2KD017Murrays Rd CONJOLA | 3 | 330 | 990 | 0.0011059 | 3.3514e-06
2013-02-07 09:00AM | 222891 | 25449 | Rural Short | REPLACE 9 POLES and AUGMENT HV MAINS BETWEEN POLES 4AA067 and 4AA009 | 29 | 360 | 10440 | 0.011663 | 3.2396e-05
2013-02-07 09:00AM | 224173 | 25403 | Rural Short | To remove bees and carry out repairs as required | 28 | 240 | 6720 | 0.007507 | 3.1279e-05
2013-02-07 09:00AM | 224393 | 8652 | Urban | Reterminate cables | 16 | 360 | 5760 | 0.0064346 | 1.7874e-05
2013-02-07 09:00AM | 224430 | 27194 | Urban | Faulty 8 Board | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2013-02-07 09:00AM | 224451 | 27194 | Urban | Replace marble bags | 6 | 240 | 1440 | 0.0016087 | 6.7027e-06
2013-02-07 09:30AM | 223723 | BDF2 | Rural Short | Augment H/V conductors from pole 776057 to Pole 1TY011 | 13 | 330 | 4290 | 0.0047924 | 1.4523e-05
2013-02-07 10:00AM | 224104 | C900 | Urban | REPLACE CONDEMNED COLUMN # 1384 | 36 | 240 | 8640 | 0.0096519 | 4.0216e-05
2013-02-08 08:00AM | 222768 | 27446 | Rural Short | change pole and augment hv and lv mains | 49 | 510 | 24990 | 0.027917 | 5.4739e-05
2013-02-08 08:00AM | 220927 | 5496 | Urban | 1) ISOLATE SECTIONS OF 11KV O/H MAINS TO ENABLE AUSGRID TO RUN FIBLE ON ADJACENT TRANSMISSION FEEDER2) REPAIR DEFECTIVE HV XARM ON POLE J890 | 50 | 570 | 28500 | 0.031838 | 5.5856e-05
2013-02-08 08:00AM | 221433 | 2815 | Urban | Augment HV conductor | 78 | 480 | 37440 | 0.041825 | 8.7135e-05
2013-02-08 08:00AM | 221634 | X871 | Urban | Install new DOF's and augment one bay of HV OH mains. | 71 | 540 | 38340 | 0.04283 | 7.9316e-05
2013-02-08 08:00AM | 222354 | WL1217 | Urban | REPLACE COND POLE 1313 | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2013-02-08 08:00AM | 224138 | 35503 | Urban | REPLACE CONDEMNED COLUMN # 25802 | 4 | 180 | 720 | 0.00080433 | 4.4685e-06
2013-02-08 08:00AM | 224467 | 25784 | Urban | Spike/ID LV cable Turn into new Pillar install STJ and connect to Pillar 122300 | 47 | 300 | 14100 | 0.015751 | 5.2505e-05
2013-02-08 08:30AM | 222893 | MG1267 | Rural Short | HV Upgrade | 27 | 480 | 12960 | 0.014478 | 3.0162e-05
2013-02-08 08:30AM | 222908 | MG1267 | Rural Short | HV Upgrade | 9 | 480 | 4320 | 0.004826 | 1.0054e-05
2013-02-08 08:30AM | 222949 | APC2 | Rural Short | REMOVE ABS 72949 and S/S 41869 INSTALL NEW S/S 32544 | 14 | 420 | 5880 | 0.0065687 | 1.564e-05
2013-02-08 08:30AM | 223077 | L948 | Rural Short | Replace LV arms @ sub 2799 | 25 | 330 | 8250 | 0.0092162 | 2.7928e-05
2013-02-08 08:30AM | 223097 | WD1251 | Rural Short | Replace condemned USL 2214 with ABS 88181 + pole | 97 | 390 | 37830 | 0.042261 | 0.00010836
2013-02-08 08:30AM | 224171 | RWB2 | Rural Short | Replace condemned poles 3J0256 and 3J0421 | 13 | 420 | 5460 | 0.0060995 | 1.4523e-05
2013-02-08 08:30AM | 224199 | W163 | Rural Short | REPLACE CONDEMNED POLE | 3 | 390 | 1170 | 0.001307 | 3.3514e-06
2013-02-08 08:30AM | 224209 | W163 | Rural Short | REPLACE CONDEMNED POLE | 1 | 390 | 390 | 0.00043568 | 1.1171e-06
2013-02-08 09:00AM | 223264 | A051 | Rural Short | Retro-fit pole sub #15841 | 2 | 300 | 600 | 0.00067027 | 2.2342e-06
2013-02-08 09:00AM | 223340 | BYB2 | Rural Short | Replace pole 2TD012 - S/S 50160 | 40 | 360 | 14400 | 0.016087 | 4.4685e-05
2013-02-08 09:00AM | 223726 | L537 | Urban | Augment LV OH mains 7/4.5 AAC. | 23 | 360 | 8280 | 0.0092498 | 2.5694e-05
2013-02-08 09:00AM | 224382 | 35403 | Urban | Repair LV Pillar | 1 | 300 | 300 | 0.00033514 | 1.1171e-06
2013-02-08 09:00AM | 224427 | 19816 | Urban | Replace Rusty Column | 10 | 240 | 2400 | 0.0026811 | 1.1171e-05
2013-02-08 09:00AM | 224429 | 19816 | Urban | Replace Rusty Column | 13 | 240 | 3120 | 0.0034854 | 1.4523e-05
2013-02-08 09:00AM | 224434 | X866 | Urban | Replace Rusty Column | 14 | 240 | 3360 | 0.0037535 | 1.564e-05
2013-02-08 09:00AM | 224436 | 27194 | Urban | Replace Rusty Column | 7 | 240 | 1680 | 0.0018768 | 7.8198e-06
2013-02-08 09:30AM | 223227 | HKA2 | Rural Short | REPLACE POLE AND TX AT SUB 50506 | 10 | 330 | 3300 | 0.0036865 | 1.1171e-05
2013-02-08 09:30AM | 224208 | ULL2 | Rural Short | replace pole 2RH 066 | 26 | 270 | 7020 | 0.0078422 | 2.9045e-05
2013-02-08 10:00AM | 224144 | 35503 | Urban | REPLACE CONDEMNED COLUMN # 23711 | 8 | 180 | 1440 | 0.0016087 | 8.937e-06
2013-02-08 11:00AM | 224266 | 8652 | Urban | Rusty Column | 16 | 240 | 3840 | 0.0042897 | 1.7874e-05
2013-02-08 11:00AM | 224407 | 27194 | Urban | Replace rusty column | 7 | 240 | 1680 | 0.0018768 | 7.8198e-06
2013-02-08 11:00AM | 224437 | CJ1245 | Urban | Replace Rusty Column | 14 | 240 | 3360 | 0.0037535 | 1.564e-05
2013-02-08 11:00AM | 224439 | 27194 | Urban | Replace Rusty Column | 25 | 240 | 6000 | 0.0067027 | 2.7928e-05
2013-02-08 12:00PM | 224151 | 41535 | Urban | REPLACE CONDEMNED COLUMN # 11754 | 25 | 180 | 4500 | 0.005027 | 2.7928e-05
2013-02-09 07:00AM | 222685 | 54649 | Urban | Replace 7 poles and OH 11kv mains. Remove USL C521. Install LBS 84682. | 4 | 600 | 2400 | 0.0026811 | 4.4685e-06
2013-02-10 06:00AM | 222241 | B202 | Urban | INSTALL NEW LBS 87422 AND INSTALL 2 NEW POLES FOR FUTURE PROJECT | 3 | 600 | 1800 | 0.0020108 | 3.3514e-06
2013-02-10 07:00AM | 220441 | T895 | Urban | REPLACE HV SW GR SUB 23710 | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-02-10 07:00AM | 222889 | B202 | Urban | Replace condemned poles | 18 | 420 | 7560 | 0.0084454 | 2.0108e-05
2013-02-10 08:00AM | 222292 | 48196 | Rural Short | Allow staff to augment section of overhead 11kv mains plus stand 2 replacement poles | 120 | 480 | 28800 | 0.032173 | 0.00013405
2013-02-10 08:00AM | 223866 | T868 | Rural Short | To allow staff to replace condemned poles 136 and 137 and Retro Sub 12105 Minerva Rd Wedderburn | 6 | 480 | 2880 | 0.0032173 | 6.7027e-06
2013-02-10 08:00AM | 222371 | PCB2 | Urban | Replace ABS Replace Pad substation Retrofit substation and maintatin USL | 30 | 510 | 15300 | 0.017092 | 3.3514e-05
2013-02-10 08:00AM | 223951 | 4870 | Urban | REMOVE DOF 7113 and EXISTING UG/OH CABLE.TERMINATE CABLE AT P.M SUB 4940 SW 66083 | 5 | 450 | 2250 | 0.0025135 | 5.5856e-06
2013-02-10 09:00AM | 222712 | 4867 | Urban | REPLACE DEFECTIVE DROP OUT FUSES 13534 WHICH FEED SUB 5902 SEVILLE STREET FAIRFIELD | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-02-11 08:00AM | 222556 | S737 | Rural Short | Upgrade LV OH mains | 32 | 480 | 7680 | 0.0085795 | 3.5748e-05
2013-02-11 08:00AM | 219915 | WH1224 | Urban | Replace 4 poles and USL. | 182 | 540 | 98280 | 0.10979 | 0.00020332
2013-02-11 08:00AM | 219945 | WH1224 | Urban | Isolation of LV mains for 4 pole replacements. | 79 | 540 | 42660 | 0.047656 | 8.8252e-05
2013-02-11 08:00AM | 223020 | 8693 | Urban | Replace 3 poles. Install one pole. Remove USL and install LBS. Augment 6 bays of HV. | 100 | 480 | 48000 | 0.053622 | 0.00011171
2013-02-11 08:00AM | 224229 | C896 | Urban | REPLACE CONDEMNED COLUMN # 1650 | 12 | 480 | 5760 | 0.0064346 | 1.3405e-05
2013-02-11 08:00AM | 224695 | 5498 | Urban | Service replacement | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-02-11 08:30AM | 223155 | MG1267 | Rural Short | Augment Hv Oh Mains | 27 | 390 | 10530 | 0.011763 | 3.0162e-05
2013-02-11 08:30AM | 223803 | 35989 | Rural Short | Limited district switching Replace condemend Sub Pole # 11Sub 11056 | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-02-11 09:00AM | 223946 | MGF2 | Rural Short | Augment 3 bays of HV mains. | 279 | 420 | 117180 | 0.1309 | 0.00031168
2013-02-11 09:00AM | 224287 | MG1267 | Rural Short | Replace Condemned LV Pole 3V0474 | 42 | 330 | 13860 | 0.015483 | 4.6919e-05
2013-02-11 09:30AM | 224223 | HBC2 | Urban | REPLACE LV LINKS IN PILLAR | 61 | 300 | 18300 | 0.020443 | 6.8144e-05
2013-02-12 07:00AM | 221392 | 35524 | Urban | Change Holec SG to Safelink | 1 | 540 | 540 | 0.00060324 | 1.1171e-06
2013-02-12 08:00AM | 214658 | CD1230 | Rural Short | Augment 11kV OH mains. | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2013-02-12 08:00AM | 223871 | P608 | Rural Short | Rplace HV X arm 2 Pole 11 and Retro subs 11441 and 11443Replace DOF's J305 | 51 | 480 | 24480 | 0.027347 | 5.6973e-05
2013-02-12 08:00AM | 220802 | CJ1204 | Urban | Augment HV OH mains 19/3.25 AAC. Install OH stay. | 156 | 480 | 37440 | 0.041825 | 0.00017427
2013-02-12 08:00AM | 222366 | 8764 | Urban | REPLACE COND LV POLES 1777 and 1779 | 38 | 480 | 18240 | 0.020376 | 4.2451e-05
2013-02-12 08:30AM | 219940 | BWH2 | Rural Short | Replace Hv Pole's and HV Augmentation | 240 | 480 | 96960 | 0.10832 | 0.00026811
2013-02-12 08:30AM | 223165 | L584 | Rural Short | REPLACE S/L COLUMN and PUT IN NEW LV PILLAR | 12 | 360 | 4320 | 0.004826 | 1.3405e-05
2013-02-12 09:00AM | 220414 | ULJ2 | Rural Short | Install New DOFs and Augment HV ConductorsTuckerman Rd ULLADULLA. | 101 | 330 | 33330 | 0.037234 | 0.00011283
2013-02-12 09:00AM | 224381 | BDF2 | Rural Short | Augment H/V conductors from pole 1TY011 to Pole 1TX003 [SUB 50673] | 13 | 390 | 5070 | 0.0056638 | 1.4523e-05
2013-02-12 09:00AM | 221292 | CJ1267 | Urban | REPAIR ABS 4905 | 155 | 360 | 55800 | 0.062335 | 0.00017315
2013-02-12 09:00AM | 224418 | 25775 | Urban | Quality Of Supply | 49 | 360 | 17640 | 0.019706 | 5.4739e-05
2013-02-12 09:00AM | 224819 | 8652 | Urban | Replace Rusty Column | 7 | 240 | 1680 | 0.0018768 | 7.8198e-06
2013-02-12 11:00AM | 224692 | AZ1227 | Urban | Service replacement | 4 | 300 | 1200 | 0.0013405 | 4.4685e-06
2013-02-13 08:00AM | 223031 | CD1230 | Rural Short | Augment 11kV OH mains. Erect new and replace poles. | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2013-02-13 08:00AM | 223828 | KC1221 | Rural Short | Augment 2 bays of LV to 150LVABC reposition insulators on Buck arm | 4 | 540 | 2160 | 0.002413 | 4.4685e-06
2013-02-13 08:00AM | 221231 | WL1292 | Urban | REPLACE COND POLE 183 | 6 | 480 | 2880 | 0.0032173 | 6.7027e-06
2013-02-13 08:00AM | 221559 | 2809 | Urban | Augment O/H Mains | 119 | 480 | 57120 | 0.06381 | 0.00013294
2013-02-13 08:00AM | 221560 | 2809 | Urban | Augment O/H Mains | 119 | 480 | 57120 | 0.06381 | 0.00013294
2013-02-13 08:00AM | 221895 | 35696 | Urban | Replace pole 799 augment 4 bays of O/H HV mains to 3 x 120mm CCT and augment 1 bay of LV mains. | 100 | 510 | 51000 | 0.056973 | 0.00011171
2013-02-13 08:00AM | 223206 | 8738 | Urban | Replace 2 poles | 153 | 480 | 73440 | 0.082041 | 0.00017092
2013-02-13 08:30AM | 223030 | JBA2 | Rural Short | STAND POLES | 12 | 420 | 5040 | 0.0056303 | 1.3405e-05
2013-02-13 08:30AM | 223274 | MG1267 | Rural Short | Augment Hv OH Mains | 27 | 480 | 12960 | 0.014478 | 3.0162e-05
2013-02-13 08:30AM | 223521 | D810 | Rural Short | Retro Sub 336 and replace LV Fuses | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2013-02-13 08:30AM | 223628 | BWH2 | Rural Short | Uprate sub 31635 | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2013-02-13 08:30AM | 224363 | 35816 | Rural Short | 1)Remove HV ABC between ABS 20936 and O/B at Sub 31013. 2) Augment 11KV OH Mains Between SUBS 30214 and 30381 | 38 | 210 | 7980 | 0.0089146 | 4.2451e-05
2013-02-13 08:30AM | 223538 | RVD2 | Urban | replace Crossarm Retension mains and retrofit Sub 40067 | 57 | 390 | 22230 | 0.024834 | 6.3676e-05
2013-02-13 08:30AM | 223626 | UNE2 | Urban | Trim overhanging tree and replace HV crossarm | 11 | 360 | 3960 | 0.0044238 | 1.2288e-05
2013-02-13 09:00AM | 224630 | 35989 | Rural Short | Change Condemned Pole # 22 | 39 | 330 | 12870 | 0.014377 | 4.3568e-05
2013-02-13 09:00AM | 223874 | DP1243 | Urban | REPLACE STREETLIGHT 4AH325 | 30 | 180 | 5400 | 0.0060324 | 3.3514e-05
2013-02-13 09:00AM | 224593 | 27191 | Urban | ISOLATED FOR TREE LOPPER | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2013-02-13 09:00AM | 224744 | A346 | Urban | Cable fault in area | 8 | 300 | 2400 | 0.0026811 | 8.937e-06
2013-02-13 09:30AM | 222294 | D852 | Urban | LIMITED DISTRICT SWITCHING REQUEST COMPLETE RELOCATION OF HV MAINS | 23 | 300 | 6900 | 0.0077081 | 2.5694e-05
2013-02-14 08:00AM | 221456 | 48196 | Rural Short | Allow staff to augment section of HV overhead mains.and stand pole | 21 | 480 | 10080 | 0.011261 | 2.346e-05
2013-02-14 08:00AM | 223300 | P608 | Rural Short | To Augment HV mains to 180mm CCT Between pole 19 and pole 5 (5 bays) | 5 | 480 | 2400 | 0.0026811 | 5.5856e-06
2013-02-14 08:00AM | 223688 | WD1210 | Rural Short | Replace condemned pole #331 (USL#1581) | 10 | 510 | 5100 | 0.0056973 | 1.1171e-05
2013-02-14 08:00AM | 224122 | R260 | Rural Short | AUGMENT HV MAINS AND REMOVE ABS 70524 | 45 | 450 | 20250 | 0.022622 | 5.027e-05
2013-02-14 08:00AM | 224336 | T828 | Rural Short | RETROFIT SUBS | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2013-02-14 08:00AM | 222604 | SWC2 | Urban | Replace 3 Poles. Install New LBS. Augment 5 Bays of HV Mains to 7/4.50 AAC | 204 | 480 | 97920 | 0.10939 | 0.00022789
2013-02-14 08:00AM | 223777 | 19871 | Urban | REPLACE LV SWITCHGEAR SUB 7863 CAMPBELL ST PARRAMATTA | 11 | 450 | 4950 | 0.0055297 | 1.2288e-05
2013-02-14 08:00AM | 223849 | 41535 | Urban | RETRO andREWIRE SUB # 4540 | 36 | 480 | 17280 | 0.019304 | 4.0216e-05
2013-02-14 08:00AM | 224764 | J504 | Urban | To allow staff to replace condemned poles 751 and 142 St Johns Rd Campbelltown | 26 | 480 | 12480 | 0.013942 | 2.9045e-05
2013-02-14 08:00AM | 224799 | J478 | Urban | Energise new LV circuitry | 22 | 420 | 9240 | 0.010322 | 2.4577e-05
2013-02-14 08:30AM | 223579 | RWD2 | Rural Short | Replace X Pole 3XK004 (Structure 204)Replace Pole 3K0132 (Structure 203)Replace X Pole 3XK163 (Structure 221)Replace Pole 3XK162 (Structure 220) | 35 | 510 | 17850 | 0.019941 | 3.9099e-05
2013-02-14 08:30AM | 224172 | MVF2 | Rural Short | Augment a section of 11KV O/H mains | 57 | 450 | 25650 | 0.028654 | 6.3676e-05
2013-02-14 08:30AM | 223658 | PKA2 | Urban | REPLACE CONDEMNED POLES | 45 | 420 | 18900 | 0.021114 | 5.027e-05
2013-02-14 08:30AM | 223687 | 7013 | Urban | REPLACE STR 36 on 33KV FDR 7013 | 56 | 420 | 23520 | 0.026275 | 6.2559e-05
2013-02-14 08:30AM | 223990 | SHH2 | Urban | REPLACE POLES 4GY001 and 4GY007. | 12 | 390 | 4680 | 0.0052281 | 1.3405e-05
2013-02-14 08:30AM | 224148 | DP1243 | Urban | MandR HOLIC IN PAD SUB's 42236 43043 | 280 | 240 | 67200 | 0.07507 | 0.00031279
2013-02-14 09:00AM | 220883 | HKD2 | Rural Short | REPLACE POLE No 3HH094 | 139 | 300 | 41700 | 0.046584 | 0.00015528
2013-02-14 09:00AM | 223317 | 48205 | Urban | DISTRIBUTION EARTH REFURBISHMENT | 2 | 120 | 240 | 0.00026811 | 2.2342e-06
2013-02-14 09:00AM | 224422 | 25775 | Urban | Quality Of Supply | 77 | 360 | 27720 | 0.030967 | 8.6018e-05
2013-02-14 09:00AM | 224716 | 48205 | Urban | CONNECT CABLE SCREEN EARTHS @ SUB 22527. | 72 | 120 | 9360 | 0.010456 | 8.0433e-05
2013-02-14 10:00AM | 223841 | WBB2 | Urban | Trim tree Overhangs | 8 | 240 | 1920 | 0.0021449 | 8.937e-06
2013-02-14 11:00AM | 224048 | C847 | Rural Short | Remove all conductors from pole 268758 to pole 307023 and all associated hardware. Remove Pole subs 22396 and 24368 and ABS 28879 and 49110 | 3 | 180 | 540 | 0.00060324 | 3.3514e-06
2013-02-15 03:00PM | 223045 | MG1267 | Rural Short | Upgrade HV Hardware | 10 | 90 | 3870 | 0.0043233 | 1.1171e-05
2013-02-15 05:00AM | 223864 | WQ1227 | Urban | DISTRIBUTION EARTH REFURBISHMENT. | 1 | 120 | 120 | 0.00013405 | 1.1171e-06
2013-02-15 08:00AM | 223332 | P608 | Rural Short | To Augment mains to 120mm CCT between Sub 12041 and Sub 11571 | 28 | 480 | 13440 | 0.015014 | 3.1279e-05
2013-02-15 08:00AM | 221504 | 2815 | Urban | Augment HV conductor | 218 | 480 | 104640 | 0.1169 | 0.00024353
2013-02-15 08:00AM | 221514 | 8764 | Urban | REPLACE COND POLE 630 | 59 | 480 | 28320 | 0.031637 | 6.591e-05
2013-02-15 08:00AM | 223275 | B716 | Urban | Replace 4 poles and USL+ABS with 2 new ABS. | 62 | 540 | 33480 | 0.037401 | 6.9261e-05
2013-02-15 08:00AM | 224474 | MR2299 | Urban | Relocate 1 x LV pillar | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2013-02-15 08:00AM | 224497 | R214 | Urban | New LV circuit. | 19 | 480 | 9120 | 0.010188 | 2.1225e-05
2013-02-15 08:00AM | 224553 | 9020 | Urban | REPLACE CONDEMNED COLUMN # 1928 | 23 | 180 | 4140 | 0.0046249 | 2.5694e-05
2013-02-15 08:00AM | 224679 | C889 | Urban | LOCATE CABLE FAULT BETWEEN COLUMN # 377 7 COLUMN # 515 | 46 | 480 | 22080 | 0.024666 | 5.1388e-05
2013-02-15 08:30AM | 223045 | MG1267 | Rural Short | Upgrade HV Hardware | 76 | 480 | 20640 | 0.023057 | 8.4901e-05
2013-02-15 08:30AM | 223699 | DP1210 | Rural Short | 11kV OUTAGE TO REPLACE STR 24 on 33KV FDR 7041 | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-02-15 08:30AM | 223913 | HBC2 | Urban | Replace pole | 82 | 390 | 31980 | 0.035725 | 9.1604e-05
2013-02-15 09:00AM | 222998 | KME2 | Rural Short | REPLACE LBS 70973 WITH LBS 122873 | 171 | 360 | 61560 | 0.06877 | 0.00019103
2013-02-15 09:00AM | 224738 | APC2 | Rural Short | RETENSION HV and LV MAINS @ PL 4GC005 | 101 | 210 | 21210 | 0.023694 | 0.00011283
2013-02-15 09:00AM | 222025 | L521 | Urban | 11kV Double up on CB L521 | 6 | 30 | 180 | 0.00020108 | 6.7027e-06
2013-02-15 09:00AM | 224713 | L537 | Urban | Change over poles. | 24 | 360 | 8640 | 0.0096519 | 2.6811e-05
2013-02-15 09:00AM | 224821 | C836 | Urban | Streetlight Improvement Project | 173 | 360 | 62280 | 0.069574 | 0.00019326
2013-02-15 09:30AM | 224018 | 48196 | Rural Short | Allow district staff to stand replacement pole | 33 | 240 | 7920 | 0.0088476 | 3.6865e-05
2013-02-15 09:30AM | 224136 | BDC2 | Rural Short | REPLACE TXR AND RETRO-FIT SUB 50795 | 9 | 300 | 2700 | 0.0030162 | 1.0054e-05
2013-02-15 09:30AM | 224592 | SXC2 | Rural Short | REPLACE CONDEMNED POLES 200218 and 200222 | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2013-02-15 10:00AM | 224561 | 9025 | Urban | REPLACE CONDEMNED COLUMN # 3915 | 17 | 180 | 3060 | 0.0034184 | 1.8991e-05
2013-02-15 12:00PM | 224577 | 9020 | Urban | REPLACE CONDEMNED COLUMN # | 4 | 180 | 720 | 0.00080433 | 4.4685e-06
2013-02-16 07:00AM | 223713 | 19890 | Urban | Replace LV Switchgear with new cat 2 webber pacific switchboard with 1250A CB and two fuse strips | 2 | 630 | 1260 | 0.0014076 | 2.2342e-06
2013-02-16 08:00AM | 222903 | B205 | Urban | Augment 7 bays of HV mains. | 175 | 480 | 84000 | 0.093838 | 0.0001955
2013-02-16 08:00AM | 224241 | MR2224 | Urban | Replace pole 264. | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2013-02-17 06:30AM | 220793 | 1958 | Urban | HVSWGR MAINT | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-02-17 07:00AM | 220443 | T892 | Urban | REPLACE HV SW GR SUB 21440 | 11 | 420 | 4620 | 0.0051611 | 1.2288e-05
2013-02-17 08:00AM | 221819 | 4873 | Urban | RELOCATE O/H MAINS TO NEW POLES | 5 | 210 | 1050 | 0.001173 | 5.5856e-06
2013-02-17 08:00AM | 222501 | NWA2 | Urban | Decommission sub 40460 and commission new padsub 29995 | 182 | 450 | 81900 | 0.091492 | 0.00020332
2013-02-17 08:00AM | 224365 | 2826 | Urban | Install LV links | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2013-02-17 08:30AM | 222726 | BLB2 | Urban | Replace LV condemned pole. | 5 | 270 | 1350 | 0.0015081 | 5.5856e-06
2013-02-17 09:00AM | 219987 | ULB2 | Urban | Replace Condemned pole 2RG078Aroo Rd ULLADULLA | 92 | 330 | 30360 | 0.033916 | 0.00010278
2013-02-17 10:30AM | 222777 | WQ1271 | Urban | DISTRIBUTION EARTH REFURBISHMENT | 1 | 270 | 270 | 0.00030162 | 1.1171e-06
2013-02-18 07:00AM | 223936 | 35509 | Urban | Install new Safelink CCFC SwGr in Sub 26826 and +Terminate new cable@ Sw 61818 in SS 26000+ Terminate new cable @ Sw 59097 in Sub 25611. | 3 | 540 | 1620 | 0.0018097 | 3.3514e-06
2013-02-18 08:00AM | 224477 | ULJ2 | Rural Short | 1 X HV UGOH / 1 X HV TERM @ NEW PM / INSTALL 1 X NEW POLE / 2 X STJ / REMOVE EXUSTING O/H MAINS | 56 | 510 | 28560 | 0.031905 | 6.2559e-05
2013-02-18 08:00AM | 220204 | WH1224 | Urban | HV OH Augmentation. | 182 | 540 | 98280 | 0.10979 | 0.00020332
2013-02-18 08:00AM | 220205 | WH1224 | Urban | Isolation of LV mains for HV OH mains augmentation. | 79 | 540 | 42660 | 0.047656 | 8.8252e-05
2013-02-18 08:00AM | 222187 | L544 | Urban | Install poles for future works. | 94 | 480 | 22560 | 0.025202 | 0.00010501
2013-02-18 08:00AM | 224244 | 7008 | Urban | REPLACE 2 X HV TRANSMISSION POLES | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-02-18 08:00AM | 224746 | SN1271 | Urban | Install 4 new LV Pillars | 61 | 480 | 29280 | 0.032709 | 6.8144e-05
2013-02-18 08:30AM | 224844 | WBB2 | Urban | Replace pole | 6 | 390 | 2340 | 0.0026141 | 6.7027e-06
2013-02-18 09:00AM | 224357 | RWB2 | Rural Short | Replace Condemned Poles 3J0659 and 3J0660 Retrofit DOFs at Subs 31330 and 30639 | 24 | 420 | 10080 | 0.011261 | 2.6811e-05
2013-02-18 09:00AM | 224558 | CLC2 | Urban | Change Pole 3GA077 ( Pole 8) | 9 | 300 | 2700 | 0.0030162 | 1.0054e-05
2013-02-19 08:00AM | 222392 | S764 | Rural Short | ISOLATE 11KV TO REPLACE EXISTING ABS # 1193 WITH NEW LBS # 123987 - NORTHERN RD ORCHARD HILLS | 6 | 480 | 2880 | 0.0032173 | 6.7027e-06
2013-02-19 08:00AM | 223671 | MG1282 | Rural Short | LV OH mains augment. | 168 | 480 | 80640 | 0.090085 | 0.00018768
2013-02-19 08:00AM | 224536 | WBD2 | Rural Short | Replace Condemned Pole | 44 | 270 | 11880 | 0.013271 | 4.9153e-05
2013-02-19 08:00AM | 224952 | 8799 | Rural Short | Augment 7 bays of HV mains to 3 x 120mm CCT and Bonding LBS 94276 | 23 | 510 | 11730 | 0.013104 | 2.5694e-05
2013-02-19 08:00AM | 221960 | 2820 | Urban | REPLACE LV SW GR + TX + CUBICLE and HV SW GR MAINT SUB 3141 | 67 | 480 | 32160 | 0.035927 | 7.4847e-05
2013-02-19 08:00AM | 223228 | 8764 | Urban | REPLACE COND POLE 1991 | 31 | 480 | 14880 | 0.016623 | 3.4631e-05
2013-02-19 08:00AM | 223249 | CD1204 | Urban | Augment 11kV OH mains. Replace pole. | 10 | 420 | 4200 | 0.0046919 | 1.1171e-05
2013-02-19 08:00AM | 223347 | 8650 | Urban | Remove:1 x pole HV OH mainsInstall:1 x pole 2 x HV UGOH HV UG cable new PS 29875 | 74 | 540 | 19980 | 0.02232 | 8.2667e-05
2013-02-19 08:00AM | 223440 | CD1204 | Urban | Augment 11kV OH mains. | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2013-02-19 08:00AM | 225142 | 5495 | Urban | Augment LV OH mains to ABC | 19 | 480 | 9120 | 0.010188 | 2.1225e-05
2013-02-19 08:30AM | 221333 | MG1267 | Rural Short | HV Upgrade | 54 | 30 | 7380 | 0.0082443 | 6.0324e-05
2013-02-19 08:30AM | 221333 | MG1267 | Rural Short | HV Upgrade | 438 | 480 | 118080 | 0.13191 | 0.0004893
2013-02-19 08:30AM | 221502 | MG1267 | Rural Short | HV Upgrade | 44 | 480 | 21120 | 0.023594 | 4.9153e-05
2013-02-19 08:30AM | 224149 | APC2 | Rural Short | M and R Holec Sub 41585 | 98 | 240 | 23520 | 0.026275 | 0.00010948
2013-02-19 08:30AM | 223588 | BLB2 | Urban | Replace Condemned Poles 3PC433 and 3PC434 | 27 | 330 | 8910 | 0.0099535 | 3.0162e-05
2013-02-19 08:30AM | 223634 | DP1236 | Urban | REPLACE ABS 71674 WITH LBS 98146 | 180 | 420 | 75600 | 0.084454 | 0.00020108
2013-02-19 08:30AM | 223880 | KMB2 | Urban | REPLACE ABS 37237 WITH LBS | 118 | 420 | 49560 | 0.055364 | 0.00013182
2013-02-19 09:00AM | 224132 | 8693 | Urban | Install poles for future works.(District Switcher) | 6 | 330 | 1980 | 0.0022119 | 6.7027e-06
2013-02-19 09:00AM | 224921 | 25775 | Urban | Quality of Supply | 15 | 360 | 5400 | 0.0060324 | 1.6757e-05
2013-02-19 09:00AM | 225074 | B778 | Urban | Connect New cable into existing pillar | 26 | 360 | 9360 | 0.010456 | 2.9045e-05
2013-02-19 09:00AM | 225100 | CJ1249 | Urban | Raise Pillar Termination | 9 | 240 | 2160 | 0.002413 | 1.0054e-05
2013-02-19 09:00AM | 225270 | B778 | Urban | Change service from OH to UG | 26 | 360 | 9360 | 0.010456 | 2.9045e-05
2013-02-19 10:00AM | 224254 | NN1277 | Urban | Change X pole 18 fdr 306 | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2013-02-19 11:00PM | 223931 | 48168 | Urban | REPLACE HV SWGR AT S/S 12642 | 161 | 59 | 9499 | 0.010612 | 0.00017986
2013-02-19 11:00PM | 225146 | 48168 | Urban | LV SWITCHING | 181 | 59 | 10679 | 0.01193 | 0.0002022
2013-02-20 08:00AM | 222373 | A096 | Rural Short | REPLACE HOUSE SERVICE INCONJUNCTION WITH POLE and ABS CHANGE | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-02-20 08:00AM | 223878 | L588 | Rural Short | INSTALL ABS 94316 and NEW POLE 861510 and INSTALL NEW LBS AND NEW POLE | 34 | 450 | 15300 | 0.017092 | 3.7982e-05
2013-02-20 08:00AM | 224754 | RBA2 | Rural Short | Job 1 : Istall new LBS 84127 and replace pole 782424.Job 2: Install new sub 28751 and 8 Bays of 11kv mains | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2013-02-20 08:00AM | 220842 | CJ1204 | Urban | Augment HV OH mains 19/3.25 AAC.Remove old poles. | 398 | 480 | 95520 | 0.10671 | 0.00044461
2013-02-20 08:00AM | 221838 | WH1209 | Urban | Replace 3 poles. | 184 | 540 | 99360 | 0.111 | 0.00020555
2013-02-20 08:00AM | 221956 | 35696 | Urban | Augment 7 bays of LV mains below O/H HV mains. | 193 | 510 | 98430 | 0.10996 | 0.0002156
2013-02-20 08:00AM | 222732 | 8738 | Urban | Augment to 7/4.50 AAC | 49 | 480 | 23520 | 0.026275 | 5.4739e-05
2013-02-20 08:00AM | 222733 | 8738 | Urban | Augment OH HV Conductor | 49 | 480 | 23520 | 0.026275 | 5.4739e-05
2013-02-20 08:00AM | 223448 | 68195 | Urban | allow staff to replace pole erect ABS 93105 augment section of overhead 11kv mainsErect new pole sub 29773 ( N.I.S.) | 30 | 480 | 14400 | 0.016087 | 3.3514e-05
2013-02-20 08:00AM | 224015 | HKB2 | Urban | Replace 6 poles. Install new LBS. Erect 4 bays of HV mains. | 59 | 480 | 28320 | 0.031637 | 6.591e-05
2013-02-20 08:30AM | 223584 | MG1267 | Rural Short | HV Upgrade | 288 | 30 | 6480 | 0.0072389 | 0.00032173
2013-02-20 08:30AM | 223584 | MG1267 | Rural Short | HV Upgrade | 144 | 480 | 103680 | 0.11582 | 0.00016087
2013-02-20 08:30AM | 224664 | W124 | Rural Short | Replace LV crossarms Poles E393 and J394 | 49 | 360 | 17640 | 0.019706 | 5.4739e-05
2013-02-20 08:30AM | 225002 | RWB2 | Rural Short | Replace Condemned Pole 3J0391 | 15 | 270 | 4050 | 0.0045243 | 1.6757e-05
2013-02-20 08:30AM | 223644 | KMA2 | Urban | CHANGE POLES COMMISSION S/S 32534 REMOVE S/S 41906 RETRO SUBS 43392 and 41189. | 488 | 420 | 121800 | 0.13607 | 0.00054515
2013-02-20 08:30AM | 224486 | MR2224 | Urban | Perform 1 x LV IDandSpike. | 10 | 360 | 3600 | 0.0040216 | 1.1171e-05
2013-02-20 08:30AM | 224626 | CRC2 | Urban | RUN NEW HV FEEDER CABLE UP POLE AND TERMINATE | 41 | 420 | 17220 | 0.019237 | 4.5802e-05
2013-02-20 09:00AM | 224918 | 25775 | Urban | Quality of Supply | 22 | 360 | 7920 | 0.0088476 | 2.4577e-05
2013-02-20 09:00AM | 225101 | CJ1249 | Urban | Install 25mm XLPE Cable | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-02-20 09:00AM | 225266 | F601 | Urban | LV Changeover | 3 | 240 | 720 | 0.00080433 | 3.3514e-06
2013-02-20 09:00AM | 225346 | 5498 | Urban | LV Pole change | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2013-02-20 11:30AM | 223995 | 35983 | Rural Short | Limited District SwitchingChange Condemned Pole #446Repair leaning pole #2 | 7 | 270 | 1890 | 0.0021114 | 7.8198e-06
2013-02-21 07:30AM | 224537 | F602 | Urban | Install a new PMS 32298 | 180 | 360 | 64800 | 0.072389 | 0.00020108
2013-02-21 08:00AM | 224484 | P608 | Rural Short | Augment HV mains between pole 822259 and 822253 and replace pole 12and stand pole 822252 | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2013-02-21 08:00AM | 225168 | L942 | Rural Short | Replace USL with LBS 95724 + pole.Replace poles 170 172 and 173.Retro 9ft HV arm @ sub 5424Install 3 Helicopter balls | 18 | 480 | 8640 | 0.0096519 | 2.0108e-05
2013-02-21 08:00AM | 222735 | 8764 | Urban | REPLACE ABS 4189 WITH NEW ABS 123861 | 28 | 480 | 13440 | 0.015014 | 3.1279e-05
2013-02-21 08:00AM | 222836 | NN1277 | Urban | To allow staff to replace Condemned Pole 328 McCrae Dr Camden South | 128 | 480 | 31680 | 0.03539 | 0.00014299
2013-02-21 08:00AM | 224373 | RVF2 | Urban | Retrofit Substation | 102 | 270 | 19980 | 0.02232 | 0.00011395
2013-02-21 08:00AM | 225046 | 49918 | Urban | RUSTY COLUMN REPLACEMENT | 34 | 300 | 10200 | 0.011395 | 3.7982e-05
2013-02-21 08:00AM | 225451 | 25780 | Urban | Isolate LV to allow new cables to be bonded. | 98 | 300 | 29400 | 0.032843 | 0.00010948
2013-02-21 08:30AM | 223123 | WBC2 | Rural Short | Replace Condemned Pole 3KC171 and 3KC176 | 101 | 420 | 42420 | 0.047388 | 0.00011283
2013-02-21 08:30AM | 224021 | KMB2 | Urban | REPLACE RECLOSER 82683 and USLS 82681 and 82680. RETRO SUB 42019. | 37 | 450 | 16650 | 0.0186 | 4.1333e-05
2013-02-21 08:30AM | 224268 | WWD2 | Urban | Replace UGOH Pole | 354 | 450 | 80550 | 0.089984 | 0.00039546
2013-02-21 08:45AM | 224036 | RBD2 | Rural Short | Augment 1 span mains to HV ABC | 25 | 390 | 9750 | 0.010892 | 2.7928e-05
2013-02-21 09:00AM | 207828 | KVB2 | Rural Short | Fit Vibration Dampers @ poles 1JC003 and 1JC002. | 4 | 300 | 1200 | 0.0013405 | 4.4685e-06
2013-02-21 09:00AM | 223420 | ULE2 | Rural Short | Replace pole 1HV013 - S/S 72205 | 99 | 360 | 35640 | 0.039814 | 0.00011059
2013-02-21 09:00AM | 224341 | KVB2 | Rural Short | Fit Vibration dampers - Various locations | 14 | 300 | 4200 | 0.0046919 | 1.564e-05
2013-02-21 09:00AM | 224455 | BDF2 | Rural Short | Job 1.Augment H/V conductors from pole 1VA013 to Pole 783071Job 2.Replace tx and retrofit sub 51521 | 4 | 360 | 53280 | 0.05952 | 4.4685e-06
2013-02-21 09:00AM | 224455 | BDF2 | Rural Short | Job 1.Augment H/V conductors from pole 1VA013 to Pole 783071Job 2.Replace tx and retrofit sub 51521 | 292 | 390 | 57720 | 0.06448 | 0.0003262
2013-02-21 09:00AM | 223168 | SC1241 | Urban | FAULT FIND + LOCATE CABLE FAULT BETWEEN SW 12782 SUB 2232 and SW 13856 SUB 7064 | 218 | 420 | 91560 | 0.10228 | 0.00024353
2013-02-21 09:00AM | 224042 | J473 | Urban | MandR HV Switchgear in PM SUB 13301 | 117 | 270 | 31590 | 0.03529 | 0.0001307
2013-02-21 09:00AM | 225287 | S674 | Urban | Lv Changeover | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2013-02-21 09:00AM | 225350 | 1112 | Urban | Replace Services | 7 | 360 | 2520 | 0.0028151 | 7.8198e-06
2013-02-21 12:00PM | 225275 | S599 | Urban | LV changeover | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2013-02-22 03:30PM | 223456 | GG1232 | Rural Short | Clearance for 33kV work | 6 | 30 | 180 | 0.00020108 | 6.7027e-06
2013-02-22 08:00AM | 222602 | 48196 | Rural Short | Allow staff to Augment section of Hv overhead mains. | 67 | 480 | 32160 | 0.035927 | 7.4847e-05
2013-02-22 08:00AM | 222742 | 27454 | Rural Short | STAND NEW LV POLE AUGMENT EX LV MAINS TO 95 mm ABC | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2013-02-22 08:00AM | 223456 | GG1232 | Rural Short | Clearance for 33kV work | 6 | 30 | 180 | 0.00020108 | 6.7027e-06
2013-02-22 08:00AM | 223852 | 27446 | Rural Short | Augment 2 bays of O/H HV mains to 7/4.5 AAC replace pole 504 and replace USL 8196 with ABS 85007. | 35 | 510 | 17850 | 0.019941 | 3.9099e-05
2013-02-22 08:00AM | 222193 | 8689 | Urban | Relocate pole and augment HV OH mains to 150 NMS ABC. | 1 | 510 | 510 | 0.00056973 | 1.1171e-06
2013-02-22 08:00AM | 223277 | 49001 | Urban | Replace 3 poles and augment 2 bays of HV OH mains. Replace ABS. | 228 | 540 | 123120 | 0.13754 | 0.0002547
2013-02-22 08:00AM | 223278 | 49001 | Urban | Isolate LV mains for replacement of 3 poles and 1 ABS and augmentation of 2 bays of HV OH mains. | 22 | 540 | 11880 | 0.013271 | 2.4577e-05
2013-02-22 08:00AM | 223771 | W120 | Urban | Tree Trimming | 201 | 480 | 96480 | 0.10778 | 0.00022454
2013-02-22 08:00AM | 223786 | W120 | Urban | TREE TRIMMING | 73 | 480 | 35040 | 0.039144 | 8.155e-05
2013-02-22 08:00AM | 224685 | 25783 | Urban | Install:LV UG cable LV pillars streetlights | 6 | 240 | 1440 | 0.0016087 | 6.7027e-06
2013-02-22 08:00AM | 225051 | 68186 | Urban | RUSTY COLUMN REPLACEMENT | 20 | 180 | 3600 | 0.0040216 | 2.2342e-05
2013-02-22 08:30AM | 222770 | MG1267 | Rural Short | Augment Hv Oh Mains | 46 | 480 | 22080 | 0.024666 | 5.1388e-05
2013-02-22 08:30AM | 223933 | DP1284 | Rural Short | REPLACE POLES and INSTALL ABS 97287 | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-02-22 08:30AM | 224621 | RWD2 | Rural Short | Replace Pole and Install New LBS 96814 | 5 | 450 | 2250 | 0.0025135 | 5.5856e-06
2013-02-22 08:30AM | 225243 | 19871 | Urban | INSTALL NEW PILLAR 121254 BY CUTTING and STJ EXISTING CABLE | 36 | 330 | 11880 | 0.013271 | 4.0216e-05
2013-02-22 08:45AM | 224328 | RWB2 | Rural Short | Uprate sub 21563 to 63kVA transformer | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2013-02-22 09:00AM | 223943 | 55169 | Urban | MandR HV Switchgear in Sub 12970 | 1 | 330 | 330 | 0.00036865 | 1.1171e-06
2013-02-22 09:00AM | 224917 | 25775 | Urban | Quality of Supply | 51 | 360 | 18360 | 0.02051 | 5.6973e-05
2013-02-22 09:00AM | 225227 | 3360 | Urban | Repair damaged pillar | 16 | 300 | 4800 | 0.0053622 | 1.7874e-05
2013-02-22 09:00AM | 225273 | B778 | Urban | Change service from OH to UG | 34 | 360 | 12240 | 0.013674 | 3.7982e-05
2013-02-22 09:00AM | 225358 | 2812 | Urban | Replace pole | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2013-02-22 09:00AM | 225359 | 2807 | Urban | Pole changeover | 3 | 240 | 720 | 0.00080433 | 3.3514e-06
2013-02-22 09:30AM | 220928 | HKA2 | Rural Short | Replace poles 3GP013 and 3GP014. | 25 | 330 | 8250 | 0.0092162 | 2.7928e-05
2013-02-22 10:00AM | 225041 | 49918 | Urban | RUSTY COLUMN REPLACEMENT | 22 | 180 | 3960 | 0.0044238 | 2.4577e-05
2013-02-23 07:00AM | 223171 | 17070 | Urban | Install new sub32281 | 2 | 540 | 1080 | 0.0012065 | 2.2342e-06
2013-02-23 09:00AM | 224916 | CLC2 | Urban | Change L/V pole 3GA078 | 52 | 300 | 15600 | 0.017427 | 5.809e-05
2013-02-23 11:00PM | 221360 | 46763 | Urban | HVSWGR MAINT | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2013-02-24 06:00AM | 221795 | 1953 | Urban | REPLACE HV SM6 SW GR SW 57935 + EARTH SW 57934 SUB 15714 | 1 | 600 | 600 | 0.00067027 | 1.1171e-06
2013-02-24 06:30AM | 221998 | T895 | Urban | install new pad sub 32336 and section of high voltage cable and connect to the existing network | 1 | 630 | 630 | 0.00070379 | 1.1171e-06
2013-02-24 07:30AM | 225305 | B745 | Urban | Remove Redundant HV | 3 | 510 | 1530 | 0.0017092 | 3.3514e-06
2013-02-24 08:00AM | 225378 | A052 | Rural Short | INSTALL NEW 1000 KVA 11KV PM SUB 29866 INSTALL NEW POLE 870571CHANGE POLE 177 LAY 240 Sq XLPE U/G HV CABLE | 8 | 540 | 4320 | 0.004826 | 8.937e-06
2013-02-24 09:00AM | 223861 | NA1266 | Urban | Replace TX @ S/S 23610. | 124 | 300 | 37200 | 0.041557 | 0.00013852
2013-02-24 11:00PM | 225313 | CD1230 | Rural Short | LV OH mains augment | 63 | 300 | 18900 | 0.021114 | 7.0379e-05
2013-02-25 07:30AM | 224029 | 55177 | Urban | New PMS's 29152 and 29153. HV SW/GR U/R to 3 fdr CFCC unit PMS's 13750 and 13751. | 170 | 510 | 86700 | 0.096854 | 0.00018991
2013-02-25 08:00AM | 223770 | 48196 | Rural Short | replace cond pole 216 | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2013-02-25 08:00AM | 222510 | 27191 | Urban | Remove:HV OH and UG mains 2 x HV UGOH 2 x polesInstall:2 x poles 2 x HV UGOH HV UG cable new PS 29881 new PS 29882 | 42 | 540 | 22680 | 0.025336 | 4.6919e-05
2013-02-25 08:00AM | 222701 | MR2292 | Urban | Change over heated LV switchgear at sub 18029 | 68 | 480 | 32640 | 0.036463 | 7.5964e-05
2013-02-25 08:00AM | 223046 | 27191 | Urban | Remove:LV OH mains 2 x poles | 16 | 540 | 8640 | 0.0096519 | 1.7874e-05
2013-02-25 08:00AM | 224067 | WL1236 | Urban | Augment 1 bay of overhead mains. | 164 | 480 | 78720 | 0.08794 | 0.00018321
2013-02-25 09:00AM | 225422 | 5498 | Urban | Pole changeover | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2013-02-25 09:00AM | 225426 | 27194 | Urban | Reterminate LV Cable | 2 | 180 | 360 | 0.00040216 | 2.2342e-06
2013-02-26 02:00PM | 223839 | 8734 | Urban | REPLACE TX AT SUB 6172 WITH 1000KVA FR3 TYPE NORTH ROCKS RD NORTH PARRAMATTA | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-02-26 08:00AM | 220823 | 8799 | Rural Short | Augment 4 bays of O/H HV mains to 3 x 120mm CCT and replace ABS 48255 with LBS 94277 | 7 | 510 | 3570 | 0.0039881 | 7.8198e-06
2013-02-26 08:00AM | 223425 | W124 | Rural Short | Repair / Replace LV Arms Replace LV Pole | 63 | 450 | 28350 | 0.03167 | 7.0379e-05
2013-02-26 08:00AM | 224047 | BWH2 | Rural Short | U/R Sub 30219 to 3 phase 100kva. | 11 | 480 | 5280 | 0.0058984 | 1.2288e-05
2013-02-26 08:00AM | 218504 | J512 | Urban | Augment 11kV OH mains. Replace pole and USL | 60 | 420 | 25200 | 0.028151 | 6.7027e-05
2013-02-26 08:00AM | 222182 | L544 | Urban | Install/change over poles.Install/augment LV mains to 150 ABC. | 100 | 480 | 24000 | 0.026811 | 0.00011171
2013-02-26 08:00AM | 222477 | MR2232 | Urban | RETROFIT SUB 4584 | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2013-02-26 08:00AM | 223881 | A314 | Urban | replace cond pole 1900 | 5 | 480 | 2400 | 0.0026811 | 5.5856e-06
2013-02-26 08:00AM | 224078 | RVC2 | Urban | REPLACE POLE AND ABS REPLACE LA'S ON LBS RETROFIT SUBSTATIONS.REMOVE ABS 74435 | 168 | 450 | 75600 | 0.084454 | 0.00018768
2013-02-26 08:00AM | 225649 | 17035 | Urban | REPLACE CONDEMNED POLE # 1045 - BROOKER ST COLYTON | 15 | 480 | 7200 | 0.0080433 | 1.6757e-05
2013-02-26 08:00AM | 225881 | 35572 | Urban | Replace impacted pole | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-02-26 08:30AM | 223887 | L940 | Rural Short | Install new capacitor pole | 10 | 450 | 4500 | 0.005027 | 1.1171e-05
2013-02-26 08:30AM | 223601 | BLD2 | Urban | Replace Condemned Pole 3PD278 and Retrofit Sub 40045 and Trim trees | 116 | 360 | 41760 | 0.046651 | 0.00012959
2013-02-26 09:00AM | 224064 | 48196 | Rural Short | Allow staff to stand make safe pole. | 34 | 360 | 12240 | 0.013674 | 3.7982e-05
2013-02-26 09:00AM | 224445 | A096 | Rural Short | Upgrade existing Lv mains from Western side of Pole Sub 1241 to 150mm ABC | 19 | 480 | 9120 | 0.010188 | 2.1225e-05
2013-02-26 09:00AM | 225371 | 2810 | Urban | Pole changeover | 6 | 240 | 1440 | 0.0016087 | 6.7027e-06
2013-02-26 09:00AM | 225427 | 19816 | Urban | Reterminate LV Cable | 4 | 180 | 720 | 0.00080433 | 4.4685e-06
2013-02-26 09:00AM | 225515 | CLC2 | Urban | Replace Pole 3DT082 | 26 | 300 | 7800 | 0.0087135 | 2.9045e-05
2013-02-26 09:30AM | 225954 | 68204 | Urban | Column change | 34 | 300 | 10200 | 0.011395 | 3.7982e-05
2013-02-27 08:00AM | 222203 | A098 | Rural Short | REPLACE SERVICES OFF COND POLE | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2013-02-27 08:00AM | 223678 | X881 | Rural Short | Allow staff to replace pole remove abs 15502 and erect abs 123388 for future auto recloser. | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2013-02-27 08:00AM | 224024 | 25449 | Rural Short | RETRO-FIT SUBS REPLACE POLE AND HV CABLE AUGMENT 11KV MAINS | 16 | 450 | 7200 | 0.0080433 | 1.7874e-05
2013-02-27 08:00AM | 224700 | KC1236 | Rural Short | Allow staff to erect line fault indicators and remove redundant fault line indicators | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-02-27 08:00AM | 217364 | NN1233 | Urban | Replace Cast Iron UGOH on pole 373 and replace Cast Iron UGOH on pole 374 | 106 | 480 | 43200 | 0.04826 | 0.00011841
2013-02-27 08:00AM | 221973 | R254 | Urban | Install Span of LV ABC conductor btwn pole 83 and pole 84. Bond HV earth to LV Neutral | 38 | 420 | 15960 | 0.017829 | 4.2451e-05
2013-02-27 08:00AM | 222773 | 8738 | Urban | Augment HV OH conductor | 53 | 480 | 25440 | 0.02842 | 5.9207e-05
2013-02-27 08:00AM | 223218 | 4372 | Urban | augment hv mains | 38 | 510 | 19380 | 0.02165 | 4.2451e-05
2013-02-27 08:00AM | 224213 | 8686 | Urban | Replace 2 poles and 1 ABS | 122 | 480 | 58560 | 0.065419 | 0.00013629
2013-02-27 08:00AM | 225111 | CT1225 | Urban | LIMITED DISTRICT SWITCHINGRetrofit Sub 11642 - Springfield Rd Catherine Fields | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-02-27 08:30AM | 223724 | MG1267 | Rural Short | Upgrade HV Hardware | 56 | 480 | 26880 | 0.030028 | 6.2559e-05
2013-02-27 08:30AM | 223740 | MG1267 | Rural Short | HV Upgrade | 56 | 480 | 26880 | 0.030028 | 6.2559e-05
2013-02-27 08:30AM | 224146 | 35990 | Rural Short | Replace X-Pole and Retro Sub - Limited district switcherChange Condemned pole 221 Sub Pole 11196Replace TX @ Sub 10212Retro Sub 10212Change X arm @ pole 224 | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2013-02-27 08:30AM | 223867 | SN1271 | Urban | 2 new padmount Subs | 79 | 420 | 33180 | 0.037066 | 8.8252e-05
2013-02-27 08:30AM | 225311 | 7962 | Urban | LV Defects | 20 | 390 | 7800 | 0.0087135 | 2.2342e-05
2013-02-27 09:00AM | 225129 | ULE2 | Rural Short | Augment HV Conductors (29 to 33 ) and Install new USL poleWoodstock Rd MILTON | 12 | 360 | 4320 | 0.004826 | 1.3405e-05
2013-02-27 09:00AM | 224591 | RS1203 | Urban | REPLACE HV U/G CABLE FROM SW 17807 SUB 12030 TO SW 17893 SUB 12875 BERRY ST GRANVILLE | 2 | 510 | 1020 | 0.0011395 | 2.2342e-06
2013-02-27 09:00AM | 225363 | 3360 | Urban | Pole change over | 9 | 360 | 3240 | 0.0036195 | 1.0054e-05
2013-02-27 09:00AM | 225730 | T894 | Urban | Install poles and streetlighting | 12 | 300 | 3600 | 0.0040216 | 1.3405e-05
2013-02-28 01:00PM | 225130 | FT1207 | Urban | REPLACE STREET LIGHT COLUMN | 28 | 150 | 4200 | 0.0046919 | 3.1279e-05
2013-02-28 07:30AM | 224160 | 1949 | Urban | Change LV sw/gear Sub 3096 Off Conway Pl King Langley | 84 | 540 | 45360 | 0.050673 | 9.3838e-05
2013-02-28 08:00AM | 222281 | W127 | Rural Short | Replace USL G625 and HV crossarms | 87 | 360 | 31320 | 0.034988 | 9.7189e-05
2013-02-28 08:00AM | 222375 | JBA2 | Rural Short | REPLACE POLE | 16 | 420 | 6720 | 0.007507 | 1.7874e-05
2013-02-28 08:00AM | 221947 | 49348 | Urban | HVSWGR MAINT | 73 | 360 | 26280 | 0.029358 | 8.155e-05
2013-02-28 08:00AM | 223785 | W120 | Urban | TREE REMOVAL NEAR HV MAINS | 1 | 450 | 450 | 0.0005027 | 1.1171e-06
2013-02-28 08:00AM | 223863 | W120 | Urban | TREE REMOVAL NEAR O/H MAINS | 5 | 450 | 2250 | 0.0025135 | 5.5856e-06
2013-02-28 08:00AM | 224666 | CD1271 | Urban | Restrain HV conductors between Pole 106 and Pole 107 Replace pole cap on Pole 107. | 20 | 360 | 7200 | 0.0080433 | 2.2342e-05
2013-02-28 08:00AM | 224725 | PKA2 | Urban | RETRO-FIT SUBS 42643 and 40796 | 98 | 270 | 26460 | 0.029559 | 0.00010948
2013-02-28 08:30AM | 223885 | L947 | Rural Short | Install Capacitor pole and mid span pole and Repair Defect # D640 | 31 | 450 | 13950 | 0.015584 | 3.4631e-05
2013-02-28 08:30AM | 224165 | DP1210 | Rural Short | MandR HOLIC S/S 41735 and RETRO S/S 41691 | 41 | 240 | 9840 | 0.010992 | 4.5802e-05
2013-02-28 08:30AM | 224895 | RWD2 | Rural Short | Augment Transmission Conductor - 11 KV Isolation for access. | 33 | 540 | 17820 | 0.019907 | 3.6865e-05
2013-02-28 08:30AM | 224310 | MYC2 | Urban | TREE TRIMMING | 80 | 180 | 14400 | 0.016087 | 8.937e-05
2013-02-28 08:30AM | 224920 | NWD2 | Urban | Repair HV Cable and ABB SwitchgearRepair 2004 ABB HV Switches. | 442 | 390 | 172380 | 0.19257 | 0.00049377
2013-02-28 09:00AM | 215544 | ULD2 | Urban | Replace TX @ S/S 72180. and Replace USL 41710 with DOFsNorth St and Princes Hwy ULLADULLA. | 186 | 330 | 61380 | 0.068569 | 0.00020778
2013-02-28 09:00AM | 225344 | 16653 | Urban | LV pole change | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2013-02-28 09:00AM | 225362 | S674 | Urban | Pole changeover | 1 | 240 | 240 | 0.00026811 | 1.1171e-06
2013-03-01 08:00AM | 223706 | 41537 | Urban | Augment OH conductor + Replace poles | 112 | 480 | 53760 | 0.060056 | 0.00012512
2013-03-01 08:00AM | 223851 | WL1217 | Urban | REPLACE SERVICE HARNESS SUB 2733 | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2013-03-01 08:00AM | 225622 | MR2224 | Urban | Remove:4 x poles LV OH mains LV UG cable | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2013-03-01 08:00AM | 225663 | 53312 | Urban | REPLACE NEUTRAL LINK TERMINAL BLOCK PILLAR # 118702 | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2013-03-01 08:00AM | 226291 | WL1236 | Urban | 48 Hour Pole | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2013-03-01 08:30AM | 225047 | SZ1352 | Urban | Replace condemned columns 8884 | 16 | 180 | 2880 | 0.0032173 | 1.7874e-05
2013-03-01 08:30AM | 225154 | UNB2 | Urban | REPLACE STREET LIGHT COLUMNS | 87 | 390 | 33930 | 0.037904 | 9.7189e-05
2013-03-01 09:00AM | 225293 | CLC2 | Urban | Change LV Poles3GA079 and 3GA114 | 51 | 360 | 18360 | 0.02051 | 5.6973e-05
2013-03-01 09:00AM | 225354 | 2806 | Urban | Pole changeover | 1 | 240 | 240 | 0.00026811 | 1.1171e-06
2013-03-01 09:00AM | 225520 | 8770 | Urban | REPAIR SERVICE TO HOUSE 343 | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-03-01 09:00AM | 225948 | C836 | Urban | Street Light Improvement | 81 | 360 | 29160 | 0.032575 | 9.0487e-05
2013-03-01 10:00AM | 224442 | 9025 | Urban | LABLE DIST FUSES @ SUB # 7102 and REPLACE CONDEMNED COLUMN # 717184 | 51 | 240 | 12240 | 0.013674 | 5.6973e-05
2013-03-01 10:30AM | 225071 | SZ1352 | Urban | Replace condemned columns 1046 | 28 | 240 | 6720 | 0.007507 | 3.1279e-05
2013-03-01 12:01AM | 224588 | S766 | Urban | Install new cat 2 fuse strip sub 20431 | 1 | 179 | 179 | 0.00019996 | 1.1171e-06
2013-03-02 08:00AM | 224355 | S737 | Rural Short | Uprate TX to 100kva.Replace earthing with seperate earthing. | 8 | 270 | 2160 | 0.002413 | 8.937e-06
2013-03-03 06:00PM | 225295 | 25747 | Rural Short | Isolate Overhead for clearance to install rail bridge | 1 | 1290 | 1290 | 0.0014411 | 1.1171e-06
2013-03-03 06:30AM | 219465 | WQ1208 | Urban | REPUMP WET BOX AT SUB 18597 CENTRE PLACE WETHERIL PARK | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-03-03 07:00AM | 223289 | WQ1286 | Urban | REPLACE CONDEMNED POLE 1349 | 8 | 540 | 4320 | 0.004826 | 8.937e-06
2013-03-03 07:30AM | 223460 | BDB2 | Urban | New Padmount Sub | 3 | 540 | 1620 | 0.0018097 | 3.3514e-06
2013-03-03 08:00AM | 224826 | T868 | Rural Short | To allow staff to replace condemned Pole #62 Wedderburn Rd Wedderburn | 13 | 480 | 6240 | 0.0069708 | 1.4523e-05
2013-03-03 08:00AM | 221840 | WH1224 | Urban | Replace 3 poles and 2 HUSL. Augment 4 bays of HV OH mains. | 166 | 480 | 79680 | 0.089012 | 0.00018544
2013-03-03 08:00AM | 225024 | WWC2 | Urban | Tree trimming and Retrofit pole Substation. | 100 | 270 | 15120 | 0.016891 | 0.00011171
2013-03-03 08:30AM | 220956 | CT1228 | Urban | Uprate PM 12865 to 1000 KVA and install new LV CB and Cat 2 Fusestrip | 10 | 450 | 4500 | 0.005027 | 1.1171e-05
2013-03-04 07:00PM | 225896 | GG1232 | Rural Short | 11KV OUTAGE CLEARANCE for 33KV WORK | 6 | 30 | 180 | 0.00020108 | 6.7027e-06
2013-03-04 08:00AM | 222470 | JBA2 | Rural Short | INSTALL NEW DROP OUT FUSES | 6 | 420 | 2520 | 0.0028151 | 6.7027e-06
2013-03-04 08:00AM | 224113 | 2810 | Urban | HV Augmentation | 128 | 540 | 69120 | 0.077215 | 0.00014299
2013-03-04 08:00AM | 224829 | 48203 | Urban | Upgrade Sub 23262 form 100kVA to 200kVA. | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2013-03-04 08:00AM | 224838 | 48203 | Urban | Bond new LV Circuit to Pillar 58381 and Make 2 way link pillar with links normally open. | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2013-03-04 08:00AM | 226031 | R214 | Urban | New LV circuit. | 19 | 480 | 9120 | 0.010188 | 2.1225e-05
2013-03-04 08:30AM | 225513 | KME2 | Rural Short | MandR HV SWITCHGEAR and CABLE S/S 42192 AS PER DEFECT PIN D09 | 46 | 240 | 11040 | 0.012333 | 5.1388e-05
2013-03-04 08:30AM | 224250 | PCD2 | Urban | Replace ABS 72536 pole with new LBS pole 124051 and replace poles. | 35 | 390 | 13650 | 0.015249 | 3.9099e-05
2013-03-04 09:00AM | 225896 | GG1232 | Rural Short | 11KV OUTAGE CLEARANCE for 33KV WORK | 6 | 30 | 180 | 0.00020108 | 6.7027e-06
2013-03-04 09:00AM | 225941 | C824 | Urban | Bond in LV Cable | 11 | 90 | 990 | 0.0011059 | 1.2288e-05
2013-03-05 08:00AM | 220824 | 8799 | Rural Short | Augment 7 bays of HV mains to 3 x 120mm CCT. | 25 | 540 | 13500 | 0.015081 | 2.7928e-05
2013-03-05 08:00AM | 223744 | BK1299 | Rural Short | Replace ABS 10347 | 105 | 330 | 34650 | 0.038708 | 0.0001173
2013-03-05 08:00AM | 224924 | W112 | Rural Short | Replace condemned Pole 165Retro Sub 11828 | 37 | 370 | 13690 | 0.015293 | 4.1333e-05
2013-03-05 08:00AM | 225127 | S743 | Rural Short | Augment HV OH mains to 150 NMS ABC. | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2013-03-05 08:00AM | 218468 | J489 | Urban | Augment 11kV OH mains. | 34 | 300 | 10200 | 0.011395 | 3.7982e-05
2013-03-05 08:00AM | 218683 | APB2 | Urban | AUGMENT MAINS | 1 | 330 | 330 | 0.00036865 | 1.1171e-06
2013-03-05 08:00AM | 221200 | B217 | Urban | INSTALL NEW SUB 32289 | 11 | 540 | 5940 | 0.0066357 | 1.2288e-05
2013-03-05 08:00AM | 221964 | MR2232 | Urban | Remove:8 x poles HV OH mains USL 6723 USL 34100Install:4 x poles 3 x HV UGOH's HV UG cable new PS 32174 new PS 32175 | 94 | 655 | 30785 | 0.034391 | 0.00010501
2013-03-05 08:00AM | 224604 | KMC2 | Urban | MandR HOLIC S/S 42193 | 273 | 200 | 39800 | 0.044461 | 0.00030497
2013-03-05 08:00AM | 226029 | J510 | Urban | Cut in LV pillar | 26 | 480 | 12480 | 0.013942 | 2.9045e-05
2013-03-05 08:00AM | 226281 | 35571 | Urban | Run new service | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2013-03-05 08:00PM | 225642 | 10251 | Urban | Remove existing pole sub 12113 and install new pad sub 32235 via a section of 240mm 11kV XLPE cable and HV UGOH | 2 | 530 | 1060 | 0.0011841 | 2.2342e-06
2013-03-05 08:30AM | 222058 | MG1267 | Rural Short | HV Upgrade | 333 | 540 | 179820 | 0.20088 | 0.000372
2013-03-05 08:30AM | 222845 | MG1267 | Rural Short | HV Upgrade | 43 | 480 | 20640 | 0.023057 | 4.8036e-05
2013-03-05 08:30AM | 224552 | HKE2 | Rural Short | Install new pole | 52 | 420 | 21840 | 0.024398 | 5.809e-05
2013-03-05 08:30AM | 225083 | L941 | Rural Short | Replace LV arms and fuses @ sub 6785 | 6 | 290 | 1740 | 0.0019438 | 6.7027e-06
2013-03-05 08:30AM | 224604 | KMC2 | Urban | MandR HOLIC S/S 42193 | 324 | 170 | 33830 | 0.037792 | 0.00036195
2013-03-05 08:30AM | 224984 | 25450 | Urban | Install New LV Pole | 21 | 150 | 3150 | 0.0035189 | 2.346e-05
2013-03-05 08:30AM | 225096 | UNB2 | Urban | REPLACE HV CROSS-ARM on SUB 40650 | 53 | 210 | 11130 | 0.012434 | 5.9207e-05
2013-03-05 08:30AM | 225447 | W123 | Urban | Replace LV crossarms on Sub 9205 | 74 | 295 | 21830 | 0.024387 | 8.2667e-05
2013-03-05 09:00AM | 222591 | 8721 | Urban | REPAIR/REPLACE HV SW GR SUB 25864 | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-03-05 09:00AM | 224045 | J506 | Urban | MandR HV Switchgear in PM SUB 13322 | 109 | 125 | 13625 | 0.015221 | 0.00012177
2013-03-05 09:00AM | 225725 | CT1266 | Urban | Determine LV Distributer cable location and configuration in SUB 10945 | 76 | 330 | 25080 | 0.028017 | 8.4901e-05
2013-03-05 09:00AM | 226074 | 68188 | Urban | 48 Hr Pole Changeover | 10 | 360 | 3600 | 0.0040216 | 1.1171e-05
2013-03-05 09:00AM | 226100 | CLC2 | Urban | Change L/V pole 3GA078 | 52 | 300 | 15600 | 0.017427 | 5.809e-05
2013-03-05 12:15PM | 224604 | KMC2 | Urban | MandR HOLIC S/S 42193 | 273 | -55 | -10945 | -0.012227 | 0.00030497
2013-03-06 07:30AM | 223907 | A314 | Urban | replace cond poles 1896 and 1897 | 44 | 470 | 10810 | 0.012076 | 4.9153e-05
2013-03-06 07:30PM | 223914 | WBB2 | Urban | Replace Condemned Pole 2G0111 Sub pole 40029 and Transformer HV crossarms Pole 2G0104 replace ABS 70118 | 30 | 420 | 12600 | 0.014076 | 3.3514e-05
2013-03-06 08:00AM | 224077 | 25403 | Rural Short | INSTALL NEW 200 KVA 11KV POLE SUB 29294 CHANGE POLE 22 | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2013-03-06 08:00AM | 225054 | L582 | Rural Short | Connect to the network new 3ph 25Kva Pole Sub 32444. | 9 | 175 | 1575 | 0.0017595 | 1.0054e-05
2013-03-06 08:00AM | 225098 | WD1284 | Rural Short | Replace condemned column 1029 | 29 | 210 | 6090 | 0.0068033 | 3.2396e-05
2013-03-06 08:00AM | 225259 | H745 | Rural Short | Stand new pole # 841779 and replace pole # 243 | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2013-03-06 08:00AM | 225742 | 8798 | Rural Short | stand new pin pole and relocate sub pole and remove hv mains | 137 | 540 | 73980 | 0.082645 | 0.00015305
2013-03-06 08:00AM | 223212 | 8738 | Urban | Replace pole + Augment OH conductor | 103 | 560 | 57680 | 0.064435 | 0.00011506
2013-03-06 08:00AM | 223907 | A314 | Urban | replace cond poles 1896 and 1897 | 2 | 440 | 10120 | 0.011305 | 2.2342e-06
2013-03-06 08:00AM | 225264 | J482 | Urban | To allow staff to make repairs and MandR ABS M781 Leumeah Rd Leumeah | 59 | 270 | 15930 | 0.017796 | 6.591e-05
2013-03-06 08:30AM | 223696 | MG1267 | Rural Short | Augment Hv Mains | 59 | 360 | 21240 | 0.023728 | 6.591e-05
2013-03-06 08:30AM | 224986 | RWC2 | Rural Short | Upgrade Sub 30583 to 63kVA | 11 | 420 | 4620 | 0.0051611 | 1.2288e-05
2013-03-06 08:30AM | 224607 | APB2 | Urban | M and R Holec Sub 42366 | 114 | 210 | 23940 | 0.026744 | 0.00012735
2013-03-06 08:30AM | 226426 | S599 | Urban | Pole change over | 4 | 270 | 1080 | 0.0012065 | 4.4685e-06
2013-03-06 09:00AM | 222831 | SC1289 | Urban | REPLACE USL 1376 POLE 420 | 28 | 375 | 6375 | 0.0071216 | 3.1279e-05
2013-03-06 09:00AM | 225985 | 35312 | Urban | Pole C/O | 3 | 180 | 540 | 0.00060324 | 3.3514e-06
2013-03-06 09:00AM | 226016 | B710 | Urban | Replace rusty columns 3156 3157 3158 | 39 | 360 | 14040 | 0.015684 | 4.3568e-05
2013-03-06 09:00AM | 226018 | B710 | Urban | Replace rusty column 3150 | 27 | 360 | 9720 | 0.010858 | 3.0162e-05
2013-03-06 09:00AM | 226309 | S591 | Urban | Pole change LV | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2013-03-06 12:30PM | 225983 | 35312 | Urban | POLE C/O | 1 | 150 | 150 | 0.00016757 | 1.1171e-06
2013-03-07 03:00PM | 224766 | APC2 | Rural Short | REPLACE PAD SUB 43278 | 702 | 10 | 4720 | 0.0052728 | 0.00078422
2013-03-07 08:00AM | 224440 | 10286 | Rural Short | INSTALL NEW 1000 KVA P/M SUB 29256 CFCC SAFELINK HV SW GEAR INSTALL NEW 500 KVA P/M SUB 32237 CFCCHV S/G LAY 240 Sq Al XLPE CABLE | 23 | 540 | 12420 | 0.013875 | 2.5694e-05
2013-03-07 08:00AM | 225383 | RWA2 | Rural Short | Job 1/ Remove ABS 50497 and Install LBS 86966 plus augment HV OH mains to 120 mm CCTJob 2/ To allow Tree loppers to trim trees aroud HV and LV Mains in Devon St | 30 | 480 | 14400 | 0.016087 | 3.3514e-05
2013-03-07 08:00AM | 225450 | APC2 | Rural Short | COMMISSION THREE NEW LV CIRCUITES | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2013-03-07 08:00AM | 225661 | R260 | Rural Short | Augment HV mains + Install LBS + Tree Trimming | 171 | 450 | 76950 | 0.085962 | 0.00019103
2013-03-07 08:00AM | 225759 | C814 | Rural Short | New ABS and LBS and Fdr re-arrange | 4 | 660 | 2640 | 0.0029492 | 4.4685e-06
2013-03-07 08:00AM | 226012 | A098 | Rural Short | REPLACE SERVICES OFF COND POLE | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2013-03-07 08:00AM | 224346 | SWC2 | Urban | Replace ABS 89371 With New LBS 124176 | 143 | 350 | 50050 | 0.055912 | 0.00015975
2013-03-07 08:00AM | 225496 | 7994 | Urban | Install poles for future works | 120 | 435 | 26100 | 0.029157 | 0.00013405
2013-03-07 08:30AM | 223662 | D810 | Rural Short | Replace pole #E58 | 5 | 320 | 1600 | 0.0017874 | 5.5856e-06
2013-03-07 08:30AM | 224766 | APC2 | Rural Short | REPLACE PAD SUB 43278 | 242 | 400 | 188800 | 0.21091 | 0.00027034
2013-03-07 08:30AM | 225418 | MVH2 | Rural Short | Change out poles 3KO236 (115) to 3KO217 (129) plus free stand new pole 816574 (114). | 21 | 530 | 11130 | 0.012434 | 2.346e-05
2013-03-07 08:30AM | 224742 | MYQ2 | Urban | Tree Trimming | 230 | 210 | 48300 | 0.053957 | 0.00025694
2013-03-07 08:30AM | 224750 | SHH2 | Urban | NEW SUBSTATION | 16 | 420 | 6720 | 0.007507 | 1.7874e-05
2013-03-07 08:30AM | 225319 | PCB2 | Urban | Replace Tx Retrofit 41355 | 55 | 216 | 11880 | 0.013271 | 6.1442e-05
2013-03-07 08:30AM | 226432 | 5496 | Urban | Pole change LV | 26 | 390 | 10140 | 0.011328 | 2.9045e-05
2013-03-07 08:30AM | 226433 | 5496 | Urban | Pole change LV | 26 | 390 | 10140 | 0.011328 | 2.9045e-05
2013-03-07 09:00AM | 222835 | A055 | Rural Short | REPLACE POLE 292 | 14 | 285 | 3990 | 0.0044573 | 1.564e-05
2013-03-07 09:00AM | 225449 | 35980 | Rural Short | Limited District SwitchingRemove lashed condemned pole #503 Adj new pole #881094 | 7 | 130 | 910 | 0.0010166 | 7.8198e-06
2013-03-07 09:00AM | 225994 | GV1249 | Urban | Pole C/O | 9 | 360 | 3240 | 0.0036195 | 1.0054e-05
2013-03-07 09:30AM | 226328 | BDA2 | Urban | Replace S/L columns. | 29 | 90 | 2610 | 0.0029157 | 3.2396e-05
2013-03-07 10:30AM | 226327 | BDG2 | Rural Short | Replace S/L columns. | 19 | 120 | 2280 | 0.002547 | 2.1225e-05
2013-03-08 08:00AM | 222921 | 27446 | Rural Short | augment lv mains | 30 | 510 | 15300 | 0.017092 | 3.3514e-05
2013-03-08 08:00AM | 223958 | J477 | Rural Short | MandR HV Switchgear in PM Sub 13294 | 71 | 300 | 21300 | 0.023795 | 7.9316e-05
2013-03-08 08:00AM | 224010 | 48196 | Rural Short | REPLACE COND POLE 232 | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2013-03-08 08:00AM | 224325 | BLA2 | Rural Short | Replace CTP 3PC289 and pole 3PC291 Install new sub pole 32575 and Decommission Kiosk sub 40020. | 111 | 480 | 53280 | 0.05952 | 0.000124
2013-03-08 08:00AM | 226333 | 35988 | Rural Short | Install New Pole 877890 and Replace Pole 43 with new pole 877894 | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2013-03-08 08:00AM | 226577 | 35989 | Rural Short | Cut in new LV pillar | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-03-08 08:00AM | 221842 | WH1209 | Urban | Replace one pole augment 7 bays of HV OH mains replace USL and install new DOF. | 184 | 480 | 88320 | 0.098664 | 0.00020555
2013-03-08 08:00AM | 222747 | 49008 | Urban | REPLACE LV SW GR + REPUMP SW A996 SUB 6739 | 81 | 480 | 38880 | 0.043434 | 9.0487e-05
2013-03-08 08:00AM | 223590 | B748 | Urban | Replace poles | 140 | 480 | 67200 | 0.07507 | 0.0001564
2013-03-08 08:00AM | 225443 | J507 | Urban | MandR ABS 61169 and Replace HV X-Arm on Pole J481Wills Rd Long Point | 55 | 480 | 26400 | 0.029492 | 6.1442e-05
2013-03-08 08:00AM | 225664 | 55875 | Urban | Replace pole 1511.Augment HV OH mains 7/4.5 AAC.Install DOFs 93104 @ pole 1512. | 107 | 480 | 51360 | 0.057375 | 0.00011953
2013-03-08 08:00AM | 226605 | 8610 | Urban | REPLACE HV ARMS POLE 1624 URGENT | 79 | 420 | 33180 | 0.037066 | 8.8252e-05
2013-03-08 08:30AM | 222967 | MG1267 | Rural Short | Replace Poles Install ABS and Augment Hv Mains | 6 | 480 | 2880 | 0.0032173 | 6.7027e-06
2013-03-08 08:30AM | 224156 | 46475 | Rural Short | Install new LBS # 92456 and pole | 9 | 450 | 4050 | 0.0045243 | 1.0054e-05
2013-03-08 08:30AM | 225655 | RWA2 | Rural Short | Replace Condemned Pole 3VJ0114 and Retrofit DOFs at Sub 31350 | 13 | 420 | 5460 | 0.0060995 | 1.4523e-05
2013-03-08 08:30AM | 225470 | W120 | Urban | Replace Crossarms | 74 | 360 | 26640 | 0.02976 | 8.2667e-05
2013-03-08 08:30AM | 226436 | S598 | Urban | Pole change 4 way tee off LV augument | 25 | 390 | 9750 | 0.010892 | 2.7928e-05
2013-03-08 09:00AM | 225284 | BYB2 | Rural Short | Replace pole 2TD012 - S/S 50160 | 40 | 360 | 14400 | 0.016087 | 4.4685e-05
2013-03-08 09:00AM | 226440 | C836 | Urban | S/L improvement project | 69 | 360 | 24840 | 0.027749 | 7.7081e-05
2013-03-09 08:00AM | 225385 | 5874 | Urban | To Spike/ID HV and LV cable Replace section of existing Cable Make 1 x TTJ Commission New Sub 32317 | 97 | 480 | 46560 | 0.052013 | 0.00010836
2013-03-09 08:00AM | 225869 | MR2225 | Urban | REPOSITION POLE 809806 INSTALL 2 HV UGOHs LAY 22kv 240 Sq Al 3c XLPE CABLE REMOVE POLE and AERIALS | 32 | 540 | 17280 | 0.019304 | 3.5748e-05
2013-03-09 09:30AM | 226656 | BDF2 | Rural Short | REPLACE RUSTY STREEL LIGHT COLUMNS | 12 | 150 | 1800 | 0.0020108 | 1.3405e-05
2013-03-09 12:30PM | 226657 | BDA2 | Urban | REPLACE RUSTY STREEL LIGHT COLUMNS | 6 | 120 | 720 | 0.00080433 | 6.7027e-06
2013-03-10 06:00AM | 224403 | 35307 | Urban | Outage to permit installation of fibre between poles A1611 and A2068 underneath Fdr 479. NOTE 1: Isolation points relocated as ABB Switchgear is 2005 Nameplate at sub 23290.NOTE 2: PM Tom Klein - 0416123493 - is primary contact on day of job. | 84 | 720 | 60480 | 0.067563 | 9.3838e-05
2013-03-10 07:00AM | 223693 | R215 | Urban | New PMS29874 | 16 | 600 | 9600 | 0.010724 | 1.7874e-05
2013-03-10 08:00AM | 223290 | WL1280 | Urban | REMOVE REDUNDANT O/H 11 KV REMOVE USL 26552REMOVE ABS 26020 | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-03-10 08:00AM | 225023 | PCE2 | Urban | Replace poles | 161 | 420 | 67620 | 0.07554 | 0.00017986
2013-03-10 09:00AM | 226687 | ULB2 | Urban | Replace Condemned pole 2PX028 | 52 | 240 | 12480 | 0.013942 | 5.809e-05
2013-03-10 10:00AM | 226431 | 5496 | Urban | Pole Changeover | 2 | 300 | 600 | 0.00067027 | 2.2342e-06
2013-03-11 08:00AM | 225854 | 48196 | Rural Short | Allow staff to replace 2 poles remove USL 2361 and erect LBS 93248. | 72 | 480 | 34560 | 0.038608 | 8.0433e-05
2013-03-11 08:00AM | 223737 | 41537 | Urban | Augment OH HV conductor + Replace poles | 219 | 480 | 105120 | 0.11743 | 0.00024465
2013-03-11 08:00AM | 226490 | S594 | Urban | Raise LV pillar | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2013-03-11 08:30AM | 225677 | RWE2 | Rural Short | Replace Pole Uprate TX at Sub 30711 to 50 KVA and Retrofit DOFs at Sub 30092 | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2013-03-11 08:30AM | 225750 | RWD2 | Rural Short | Change poles 3XK004 (205) 3XK153 (208) 3XK155 (211) 3XK157 (214) 3XK158 (215) 3XK160 (218 ) to 3XK166 (224). Stand new poles 816673 815674 815576 16488 816678 81689 816681 816682. Aug trans. cond. between poles 3XK004 (205) - 3XK153 (208). | 35 | 480 | 16800 | 0.018768 | 3.9099e-05
2013-03-11 08:30AM | 226239 | P608 | Rural Short | To Augment HV mains to 180mm CCT Between pole 19 to 23 and stand poles 822252 822248 822240 822239 and 822238. | 10 | 450 | 4500 | 0.005027 | 1.1171e-05
2013-03-11 08:30AM | 225469 | FT1207 | Urban | Replace Padmount Substation 19252 | 83 | 390 | 32370 | 0.036161 | 9.2721e-05
2013-03-11 09:00AM | 225670 | CLC2 | Urban | Replace Pole 3DV156 and 3DV157 ( poles 6 and 7) | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2013-03-11 09:00AM | 226308 | 2812 | Urban | Pole change LV | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2013-03-12 08:00AM | 225813 | R260 | Rural Short | AUGMENT HV MAINS | 45 | 450 | 20250 | 0.022622 | 5.027e-05
2013-03-12 08:00AM | 226077 | X879 | Rural Short | Remove Pole Sub 11935 and install New 100kVA Pole Sub 29886. | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2013-03-12 08:00AM | 225971 | CD1204 | Urban | To allow staff to replace Condemned Pole # 3 Fergusson Lane Grassmere | 13 | 480 | 6240 | 0.0069708 | 1.4523e-05
2013-03-12 08:00AM | 226424 | 53312 | Urban | REPLACE NEUTRAL LINK TERMINAL BLOCK PILLAR # 118702 | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2013-03-12 08:00AM | 226659 | RS1203 | Urban | Changeover service from old open wire to new bundle LV | 13 | 420 | 5460 | 0.0060995 | 1.4523e-05
2013-03-12 08:30AM | 222984 | MG1267 | Rural Short | Augment Hv Mains | 170 | 480 | 81600 | 0.091157 | 0.00018991
2013-03-12 08:30AM | 222986 | MG1267 | Rural Short | Augment Hv Mains | 98 | 480 | 47040 | 0.052549 | 0.00010948
2013-03-12 08:30AM | 224402 | 8799 | Rural Short | Replace poles 23 and 23. Stand pole 847705 adj pole 20 | 47 | 450 | 21150 | 0.023627 | 5.2505e-05
2013-03-12 09:00AM | 226063 | CLC2 | Urban | Replace pole 3DT082.Remove fuses 24522.Retrofit S/S 50109. | 170 | 300 | 51000 | 0.056973 | 0.00018991
2013-03-12 09:00AM | 226306 | RS1270 | Urban | Pole change | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-03-12 09:00AM | 226576 | 27194 | Urban | Replace 8 Board in Column | 19 | 240 | 4560 | 0.0050941 | 2.1225e-05
2013-03-12 09:00AM | 226580 | CJ1245 | Urban | Rusty Column | 19 | 150 | 2850 | 0.0031838 | 2.1225e-05
2013-03-12 09:00AM | 226581 | CJ1245 | Urban | Rusty Column | 22 | 150 | 3300 | 0.0036865 | 2.4577e-05
2013-03-12 09:00AM | 226583 | CJ1245 | Urban | Rusty Column | 18 | 150 | 2700 | 0.0030162 | 2.0108e-05
2013-03-12 09:00AM | 226740 | ULD2 | Urban | Replace Condemned pole 2RP485 | 20 | 240 | 4800 | 0.0053622 | 2.2342e-05
2013-03-12 09:30PM | 223818 | SHK2 | Urban | REMOVE ABS 68758 INSTALL LBS 92201 AUGMENT BETWEEN POLES 295927 and ABS 39086 MandR ABS 39086 INSTALL DOF'S 92202 and AUGMENT BETWEEN POLES 4DR366 and 772140 CHANGE POLES | 465 | 480 | 223200 | 0.24934 | 0.00051946
2013-03-13 08:00AM | 206079 | W185 | Rural Short | Replace pole and ABS. Retro Sub. | 50 | 420 | 21000 | 0.02346 | 5.5856e-05
2013-03-13 08:00AM | 224025 | 27446 | Rural Short | Augment 4 bays of O/H HV mains to 7/4.5 AAC. | 92 | 510 | 23460 | 0.026208 | 0.00010278
2013-03-13 08:00AM | 223279 | 49001 | Urban | Augment 8 bays of HV OH mains. | 162 | 480 | 77760 | 0.086867 | 0.00018097
2013-03-13 08:00AM | 223479 | S765 | Urban | REPLACE EXISTING ABS # 1188 WITH NEW LBS # 123848 - MULGOA RD MULGOA | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-03-13 08:00AM | 224257 | 8770 | Urban | REPLACE COND POLE 1528REPLACE ABS 7137 WITH NEW ABS 124135 | 39 | 480 | 18720 | 0.020912 | 4.3568e-05
2013-03-13 08:00AM | 225969 | 2828 | Urban | Replace poles.Install ABS 79359.Install DOFs 79361. | 97 | 480 | 46560 | 0.052013 | 0.00010836
2013-03-13 08:30AM | 224712 | JBB2 | Rural Short | 11kV OUTAGE TO INSTALL 3 NEW POLES CONDUCTOR AND OHEW BETWEEN ABS 61691 AND ABS 73309 on 33KV FDR 7009 | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-03-13 08:30AM | 225308 | L941 | Rural Short | Repalce LV arms @ pole 110 | 27 | 360 | 9720 | 0.010858 | 3.0162e-05
2013-03-13 08:30AM | 226015 | 25403 | Rural Short | Replace condemned column 7086 | 24 | 240 | 5760 | 0.0064346 | 2.6811e-05
2013-03-13 08:30AM | 225377 | PKF2 | Urban | Change Sub 40727 Retrofit Sub 41798 | 117 | 390 | 45630 | 0.050974 | 0.0001307
2013-03-13 08:30AM | 225627 | WBB2 | Urban | REPLACE CONDEMNED POLES REPLACE ABS WITH NEW LBS | 50 | 420 | 21000 | 0.02346 | 5.5856e-05
2013-03-13 08:30AM | 226427 | 2807 | Urban | Pole Change | 10 | 390 | 3900 | 0.0043568 | 1.1171e-05
2013-03-13 09:00AM | 225132 | ULE2 | Rural Short | Connect New UG cable and remove O/H conductors.Woodstock Rd MILTON | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2013-03-13 09:00AM | 226644 | S326 | Urban | Rusty Column | 11 | 150 | 1650 | 0.0018432 | 1.2288e-05
2013-03-13 09:00AM | 226645 | CJ1245 | Urban | Rusty Column | 20 | 150 | 3000 | 0.0033514 | 2.2342e-05
2013-03-13 09:30AM | 226599 | 68204 | Urban | Street light column replacement | 36 | 300 | 10800 | 0.012065 | 4.0216e-05
2013-03-13 09:30PM | 226838 | 19871 | Urban | Change from OH to UG | 1 | 390 | 390 | 0.00043568 | 1.1171e-06
2013-03-13 10:30AM | 226037 | 4354 | Urban | Replace condemned column 1087 | 30 | 300 | 9000 | 0.010054 | 3.3514e-05
2013-03-13 11:00AM | 226642 | 19816 | Urban | Rusty Column | 16 | 210 | 3360 | 0.0037535 | 1.7874e-05
2013-03-13 11:00AM | 226643 | CJ1245 | Urban | Rusty Column | 16 | 210 | 3360 | 0.0037535 | 1.7874e-05
2013-03-13 11:00AM | 226991 | S768 | Urban | Replace service blocks in Pillar 259418 | 14 | 210 | 2940 | 0.0032843 | 1.564e-05
2013-03-14 08:00AM | 224127 | 8798 | Rural Short | run 4 bays of hv abc and install abs and stand poles | 224 | 510 | 114240 | 0.12762 | 0.00025023
2013-03-14 08:00AM | 224361 | L941 | Rural Short | Install Capacitor pole and replace poles 77 and 79 | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2013-03-14 08:00AM | 225721 | 48196 | Rural Short | REPLACE COND POLE 443 | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-03-14 08:00AM | 225751 | 35988 | Rural Short | Replace poles 40 and 41 and augment high voltage mains from pole 40 through to pole 44. | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-03-14 08:00AM | 225921 | W164 | Rural Short | INSTALL LBS and POLE | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2013-03-14 08:00AM | 226330 | W124 | Rural Short | HV Earth Testing | 56 | 150 | 8400 | 0.0093838 | 6.2559e-05
2013-03-14 08:00AM | 225974 | MR2232 | Urban | REPLACE HV SW GR AUTO TRANS 25281 RM6 FOR RM6 (To repair Defect D627) + REPAIR BROKEN HV X-ARM POLE 374 | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-03-14 08:00AM | 226692 | MR2224 | Urban | Remove:4 x poles LV OH mains LV UG cable | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2013-03-14 08:30AM | 224130 | MG1267 | Rural Short | Upgrade HV Network | 20 | 480 | 9600 | 0.010724 | 2.2342e-05
2013-03-14 08:30AM | 224133 | MG1267 | Rural Short | HV Upgrade | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2013-03-14 08:30AM | 224715 | JBB2 | Rural Short | 11kV OUTAGE TO INSTALL 3 NEW POLES on 33KV FDR 7009 | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-03-14 08:30AM | 226061 | L942 | Rural Short | Replace LV arms @ pole 278 | 46 | 270 | 12420 | 0.013875 | 5.1388e-05
2013-03-14 08:30AM | 225119 | KMA2 | Urban | Replace pole 4KD497 replace ABS 71964 with LBS Retro sub 42017 | 114 | 360 | 41040 | 0.045847 | 0.00012735
2013-03-14 08:30AM | 225892 | WWD2 | Urban | Replace Cast Iron Pothead and Pole 2V0842 | 64 | 390 | 24960 | 0.027883 | 7.1496e-05
2013-03-14 08:30AM | 226355 | FT1208 | Urban | Remove Sub 42346HV Mains Between poles 2P0929 and 856522 | 67 | 360 | 24120 | 0.026945 | 7.4847e-05
2013-03-14 08:30AM | 226721 | 1112 | Urban | L/V crossarm change over | 5 | 210 | 1050 | 0.001173 | 5.5856e-06
2013-03-14 08:45AM | 226569 | CJ1267 | Urban | Replace Pole | 1 | 315 | 315 | 0.00035189 | 1.1171e-06
2013-03-14 09:00AM | 223586 | R214 | Urban | To Replace Existing L/V SW/GR With New L/V Webber SW/GR FFIFFCAT.1.@ Sub 13414 Southdown Rd Elderslie. | 85 | 390 | 33150 | 0.037033 | 9.4955e-05
2013-03-14 10:00AM | 226600 | SHH2 | Urban | Load transfer at Shell Harbour as per pinksheet. Dump sub 41990. Customers have been notified. | 19 | 120 | 2280 | 0.002547 | 2.1225e-05
2013-03-15 08:00AM | 223004 | 27446 | Rural Short | augment lv mains | 261 | 510 | 133110 | 0.1487 | 0.00029157
2013-03-15 08:00AM | 223161 | X877 | Rural Short | Allow staff to remove USL 19638 and erect DOF's 97889 | 31 | 480 | 14880 | 0.016623 | 3.4631e-05
2013-03-15 08:00AM | 224112 | BWH2 | Rural Short | Replace Poles and Augment Hv mains | 3 | 510 | 1530 | 0.0017092 | 3.3514e-06
2013-03-15 08:00AM | 225299 | 48196 | Rural Short | REPLACE COND POLES 160 and 161 | 22 | 480 | 10560 | 0.011797 | 2.4577e-05
2013-03-15 08:00AM | 226051 | 27454 | Rural Short | UPRATE EX POLE SUB 4295 TO 100KVA | 6 | 300 | 1800 | 0.0020108 | 6.7027e-06
2013-03-15 08:00AM | 223581 | L537 | Urban | REPLACE POLES 1577 + 1578 | 62 | 480 | 29760 | 0.033245 | 6.9261e-05
2013-03-15 08:00AM | 224215 | 8677 | Urban | Replace 2 poles. | 182 | 480 | 87360 | 0.097592 | 0.00020332
2013-03-15 08:00AM | 224216 | 8677 | Urban | Isolate LV mains for replacement of 2 poles. | 60 | 540 | 32400 | 0.036195 | 6.7027e-05
2013-03-15 08:00AM | 225611 | WWE2 | Urban | Trimming of overhanging tree | 223 | 270 | 60210 | 0.067262 | 0.00024912
2013-03-15 08:00AM | 226222 | 35519 | Urban | Replace column #4979 | 31 | 240 | 7440 | 0.0083114 | 3.4631e-05
2013-03-15 08:00AM | 226518 | 9027 | Urban | REPLACE CONDEMNED COLUMN # 11701 | 11 | 480 | 5280 | 0.0058984 | 1.2288e-05
2013-03-15 08:30AM | 224756 | WD1251 | Rural Short | Replace condemned USL 2214 with ABS 88181 + pole.MandR ABS 2215 | 97 | 390 | 37830 | 0.042261 | 0.00010836
2013-03-15 08:30AM | 225170 | WBE2 | Rural Short | Replace Condemned pole 2G0151 2G0154 and 2G0152 | 26 | 390 | 10140 | 0.011328 | 2.9045e-05
2013-03-15 08:30AM | 225806 | RBA2 | Rural Short | Trim trees near powerlines | 11 | 450 | 4950 | 0.0055297 | 1.2288e-05
2013-03-15 08:30AM | 226075 | L941 | Rural Short | Replace LV arms @ pole 354 | 57 | 270 | 15390 | 0.017192 | 6.3676e-05
2013-03-15 08:30AM | 226093 | L948 | Rural Short | Retention LV mains @ pole 155 | 12 | 270 | 3240 | 0.0036195 | 1.3405e-05
2013-03-15 08:30AM | 226450 | BWH2 | Rural Short | Replace Hv Pole's and HV Augmentation | 240 | 480 | 96960 | 0.10832 | 0.00026811
2013-03-15 08:30AM | 226725 | 1105 | Urban | L/V crossarm change over | 2 | 210 | 420 | 0.00046919 | 2.2342e-06
2013-03-15 09:00AM | 226386 | 25775 | Urban | Move Fire Hazzard Sub 20731 | 48 | 360 | 17280 | 0.019304 | 5.3622e-05
2013-03-15 09:00AM | 226817 | ULF2 | Urban | ****LIMITED SWITCHING****Replace pole 2RR262 - S/S 72388.Deering st Ulladulla. | 2 | 300 | 600 | 0.00067027 | 2.2342e-06
2013-03-15 10:00AM | 226223 | 35530 | Urban | Replace Coloumn # 12293 | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2013-03-15 11:00AM | 225638 | S595 | Urban | REPAIR HV END OF CUBICAL AFTER IMPACT | 3 | 150 | 450 | 0.0005027 | 3.3514e-06
2013-03-15 12:00PM | 226237 | 35519 | Urban | Replace column #7000 | 16 | 240 | 3840 | 0.0042897 | 1.7874e-05
2013-03-16 07:00AM | 225240 | HR1236 | Urban | Isolate Sub to replace LV sw/gr in Sub 17887 Connect new Service Mains | 1 | 570 | 570 | 0.00063676 | 1.1171e-06
2013-03-16 08:00AM | 226312 | 25737 | Urban | Install LV fuse strip and terminate new LV cable | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2013-03-16 08:30AM | 225330 | WD1284 | Rural Short | Replace LV arms links and fuses @ sub 1467.Replace LV arm @ pole 43 | 8 | 420 | 3360 | 0.0037535 | 8.937e-06
2013-03-17 07:00AM | 223457 | 8740 | Urban | REPLACE TX1 and TX2 WITH FR3 FIREPROOF TYPE BOND 11KV INCOMING CABLE SCREENS TO THE HV EARTH BAR SW 62967 TX3 SUB 7859 NORTH ROCKS RD NORTH ROCKS | 1 | 540 | 540 | 0.00060324 | 1.1171e-06
2013-03-17 07:30AM | 225631 | 35981 | Rural Short | Maintain ABS J333 and J353. Replace HV X-arms on Poles 373 387 and 3. | 25 | 510 | 12750 | 0.014243 | 2.7928e-05
2013-03-17 08:00AM | 225980 | S737 | Rural Short | Feeder 420 - Stand new 33kV concrete poles string 11kV centre phase and install temp USL. | 60 | 90 | 2700 | 0.0030162 | 6.7027e-05
2013-03-17 08:00AM | 226106 | CD1241 | Urban | To allow staff to replace Condemned Poles #96 and100 Little St Camden | 154 | 480 | 73920 | 0.082578 | 0.00017204
2013-03-17 09:00AM | 227198 | 5496 | Urban | Pole changeover | 14 | 240 | 3360 | 0.0037535 | 1.564e-05
2013-03-17 09:30AM | 225958 | H745 | Rural Short | Clearance to install 33kV OHEW and Riser Brackets at P. A74A73A262 and A12 | 1 | 60 | 60 | 6.7027e-05 | 1.1171e-06
2013-03-17 09:30AM | 225980 | S737 | Rural Short | Feeder 420 - Stand new 33kV concrete poles string 11kV centre phase and install temp USL. | 60 | 150 | 4500 | 0.005027 | 6.7027e-05
2013-03-18 08:00AM | 226496 | ULJ2 | Rural Short | install new single phase pole sub 32230/ install 3x new wood pole / string 3x new o/head mains | 38 | 390 | 14820 | 0.016556 | 4.2451e-05
2013-03-18 08:00AM | 222850 | J492 | Urban | To allow staff to replace condemned pole 940 McLean St Campbelltown | 73 | 480 | 35040 | 0.039144 | 8.155e-05
2013-03-18 08:00AM | 226456 | B748 | Urban | Replace poles + Augment OH HV conductor | 49 | 480 | 23520 | 0.026275 | 5.4739e-05
2013-03-18 08:30AM | 225807 | RWC2 | Rural Short | Trim trees near powerlines | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-03-18 09:00AM | 226192 | RWB2 | Rural Short | Replace Condemned Pole 3J0592 | 7 | 330 | 2310 | 0.0025805 | 7.8198e-06
2013-03-18 10:00AM | 227118 | L537 | Urban | LV Service Relocation | 3 | 300 | 900 | 0.0010054 | 3.3514e-06
2013-03-19 01:00PM | 227013 | L582 | Rural Short | LIMITED DISTRICT SWITCHING INSTALL MDI AT SUB 25994 | 1 | 120 | 120 | 0.00013405 | 1.1171e-06
2013-03-19 07:00AM | 226360 | 458/1 | Urban | Shync In and out Sub 1704 to allow for the works to be completed as per DNR 226341 | 18 | 600 | 10800 | 0.012065 | 2.0108e-05
2013-03-19 08:00AM | 222744 | C814 | Rural Short | REPLACE EXISTING ABS # 61606 WITH NEW AUTO LBS # 123865 - FOURTH AVE LLANDILO | 29 | 480 | 13920 | 0.01555 | 3.2396e-05
2013-03-19 08:00AM | 222906 | M389 | Urban | To allow staff to replace condemned pole 491 Kimbarra Ave Camden | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2013-03-19 08:00AM | 227117 | L544 | Urban | LV Service Relocation | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2013-03-19 08:00AM | 227119 | L537 | Urban | LV Service Relocation | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-03-19 08:30AM | 224128 | MG1267 | Rural Short | Replace Hv Poles and Augment Hv Mains | 55 | 480 | 26400 | 0.029492 | 6.1442e-05
2013-03-19 08:30AM | 224492 | 8799 | Rural Short | Replace poles 24 and 27. Replace 9ft HV arm and LV arms @ sub 3677. Replace LV arms @ pole 39 | 48 | 450 | 21600 | 0.02413 | 5.3622e-05
2013-03-19 08:30AM | 225805 | MVB2 | Rural Short | Trim trees near powerlines | 10 | 450 | 4500 | 0.005027 | 1.1171e-05
2013-03-19 08:30AM | 224782 | HBC2 | Urban | Replace ABS pole 71548 retrofit Sub 41458 and Trim trees | 202 | 420 | 63420 | 0.070848 | 0.00022566
2013-03-19 08:30AM | 224944 | B211 | Urban | REPLACE USL 7229 WITH LBS 97013 | 118 | 420 | 32340 | 0.036128 | 0.00013182
2013-03-19 08:30AM | 226724 | 1106 | Urban | L/V crossarm change | 6 | 390 | 2340 | 0.0026141 | 6.7027e-06
2013-03-19 09:00AM | 224841 | CLD2 | Rural Short | Install LBS Augment and Re-Route HV Conductors for Feeder CLD2Coonemia Rd CULBURRA. | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-03-19 09:00AM | 227011 | L588 | Rural Short | LIMITED DISTRICT SWITCHING INSTALL MDI AT SUB 23071 | 3 | 180 | 540 | 0.00060324 | 3.3514e-06
2013-03-19 09:00AM | 225772 | BLB2 | Urban | Replace pole and ABS with new LBS pole. | 154 | 330 | 27060 | 0.030229 | 0.00017204
2013-03-19 09:00AM | 226647 | 46772 | Urban | String mains for the upgrade of 33kv FDR 455 to 132kv FDR 23-G. | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-03-19 09:00AM | 226841 | 19871 | Urban | Change from OH to LV | 11 | 360 | 3960 | 0.0044238 | 1.2288e-05
2013-03-19 09:00AM | 227116 | 7994 | Urban | Relocate cable to new pole | 12 | 360 | 4320 | 0.004826 | 1.3405e-05
2013-03-20 05:30AM | 226451 | 20725 | Urban | Install new pad Sub 29821 via new section of U/G cable to existing subs 29820 and 29833 | 84 | 30 | 2520 | 0.0028151 | 9.3838e-05
2013-03-20 05:30PM | 226451 | 20725 | Urban | Install new pad Sub 29821 via new section of U/G cable to existing subs 29820 and 29833 | 84 | 30 | 2520 | 0.0028151 | 9.3838e-05
2013-03-20 07:30AM | 223050 | RS1270 | Urban | RETRO SUB 6191 and CHANGE TX and ASSOCIATED HARDWARE | 4 | 540 | 1080 | 0.0012065 | 4.4685e-06
2013-03-20 08:00AM | 223993 | HKE2 | Rural Short | Replace 3 poles. Install new LBS. Augment 4 bays of HV Mains. | 135 | 480 | 64800 | 0.072389 | 0.00015081
2013-03-20 08:00AM | 224085 | 27446 | Rural Short | Augment 7 bays of O/H HV mains to 7/4.5 AAC. | 104 | 510 | 53040 | 0.059252 | 0.00011618
2013-03-20 08:00AM | 226939 | W163 | Rural Short | LIMITED DISTRICT SWITCHING INSTALL MDI AT SUB 24173 | 1 | 180 | 180 | 0.00020108 | 1.1171e-06
2013-03-20 08:00AM | 223759 | 41537 | Urban | Augment OH HV conductor + Replace poles | 161 | 480 | 77280 | 0.086331 | 0.00017986
2013-03-20 08:00AM | 226266 | 35528 | Urban | Replace ragbolt #25110 | 11 | 390 | 4290 | 0.0047924 | 1.2288e-05
2013-03-20 08:30AM | 224868 | BLA2 | Rural Short | Replace Condemned pole 3PD335 and 3PD332 | 14 | 420 | 5880 | 0.0065687 | 1.564e-05
2013-03-20 08:30AM | 225811 | MVB2 | Rural Short | Trim trees near powerlines | 14 | 270 | 3780 | 0.0042227 | 1.564e-05
2013-03-20 08:30AM | 226322 | 35990 | Rural Short | Replace X-Pole - Limited district switcherChange Condemned pole 221 Sub Pole 11196Change X arm @ pole 224 | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2013-03-20 08:30AM | 226805 | KVD2 | Rural Short | INSTALL NEW 5 NEW POLES AND 11KV MAINS | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2013-03-20 09:00AM | 225165 | ULE2 | Rural Short | Augment HV O/H conductors. ( 21 to 28 )Woodstock Rd MILTON | 40 | 360 | 14400 | 0.016087 | 4.4685e-05
2013-03-20 09:00AM | 226387 | T884 | Urban | REMOVE POLES and AERIALS and ABS L450 | 159 | 240 | 38160 | 0.042629 | 0.00017762
2013-03-20 09:00AM | 227121 | S599 | Urban | LV Crossarm change over | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2013-03-20 09:00AM | 227122 | 5496 | Urban | LV crossarm change | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2013-03-20 09:00AM | 227192 | WH1272 | Urban | Replace poles for future works | 12 | 360 | 4320 | 0.004826 | 1.3405e-05
2013-03-20 11:00AM | 226944 | 19816 | Urban | Rusty Column | 15 | 210 | 3150 | 0.0035189 | 1.6757e-05
2013-03-21 01:00PM | 227139 | B715 | Urban | Rusty Column | 35 | 120 | 4200 | 0.0046919 | 3.9099e-05
2013-03-21 07:00AM | 226377 | 458/1 | Urban | Switching the LV system off to allow for the works to be completed as pe DNR 226367 | 38 | 540 | 18900 | 0.021114 | 4.2451e-05
2013-03-21 08:00AM | 224137 | 8798 | Rural Short | augment 2 bays of hv change abs pole sub pole and install LBS on existing pole | 501 | 510 | 255510 | 0.28544 | 0.00055968
2013-03-21 08:00AM | 224370 | HKA2 | Rural Short | Replace 9 poles. Replace USLs. | 175 | 480 | 84000 | 0.093838 | 0.0001955
2013-03-21 08:00AM | 224865 | R260 | Rural Short | Augment HV mains + Install LBS | 140 | 450 | 63000 | 0.070379 | 0.0001564
2013-03-21 08:00AM | 225281 | 8635 | Rural Short | INSTALL NEW 100 KVA POLE SUB 32166 INSTALL NEW POLES and RUN 7/3.75 Al HV MAINS | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2013-03-21 08:00AM | 226674 | T831 | Rural Short | Install new section of O/H Mains to new Pole Sub 29975 | 13 | 480 | 6240 | 0.0069708 | 1.4523e-05
2013-03-21 08:00AM | 223287 | MR2231 | Urban | Perform 1 x HV IDandSpikeInstall:HV UG cable 2 x HV STJ new PS 29610 | 32 | 480 | 15360 | 0.017159 | 3.5748e-05
2013-03-21 08:00AM | 223623 | 27334 | Urban | To Replace Existing L/V SW/GR With New L/V Webber SW/GR ( FFIFF ) CAT .1.in Sub 13536 | 61 | 420 | 25620 | 0.028621 | 6.8144e-05
2013-03-21 08:00AM | 223676 | L537 | Urban | REPLACE POLE 1017 | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2013-03-21 08:00AM | 226377 | 458/1 | Urban | Switching the LV system off to allow for the works to be completed as pe DNR 226367 | 32 | 480 | 16800 | 0.018768 | 3.5748e-05
2013-03-21 08:00AM | 227277 | WL1236 | Urban | Replace Condemned Pole | 11 | 480 | 5280 | 0.0058984 | 1.2288e-05
2013-03-21 08:00AM | 227392 | SHH2 | Urban | NEW LV PILLARS | 18 | 420 | 7560 | 0.0084454 | 2.0108e-05
2013-03-21 08:15AM | 226098 | 35815 | Rural Short | Limited District switching Change Condemned Pole 98 Sub 11498Change HV Xarm @ pole 99 | 40 | 450 | 18000 | 0.020108 | 4.4685e-05
2013-03-21 08:30AM | 225945 | WD1221 | Rural Short | Retro sub 3754 and 5418 | 1 | 390 | 390 | 0.00043568 | 1.1171e-06
2013-03-21 08:30AM | 226196 | BWH2 | Rural Short | Install Poles Augment a section of 11KV O/H mains and repair UGOH. | 7 | 450 | 3150 | 0.0035189 | 7.8198e-06
2013-03-21 08:30AM | 226590 | A098 | Rural Short | TREE TRIMMING @ POLE # 53 | 18 | 210 | 3780 | 0.0042227 | 2.0108e-05
2013-03-21 08:30AM | 226859 | KVD2 | Rural Short | INSTALL NEW 5 NEW POLES AND 11KV MAINS | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2013-03-21 08:30AM | 225254 | APB2 | Urban | REPLACE X PLs 313962 and 4GT074 | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2013-03-21 09:00AM | 224348 | NA1207 | Rural Short | Replace TX @ S/S 50628. | 102 | 300 | 30600 | 0.034184 | 0.00011395
2013-03-21 09:00AM | 226586 | DP1284 | Rural Short | AUGMENT HV MAINS | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2013-03-21 09:00AM | 227127 | S599 | Urban | LV crossarm changeover | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2013-03-21 09:00AM | 227141 | 49010 | Urban | Rusty Column | 36 | 180 | 6480 | 0.0072389 | 4.0216e-05
2013-03-21 09:00AM | 227172 | 1125 | Urban | Service Harness | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-03-21 09:00AM | 227447 | 8738 | Urban | Service Replacement | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2013-03-21 09:00AM | 227448 | 2815 | Urban | LV Pole change | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-03-21 09:03AM | 224628 | ULF2 | Urban | Replace Condemned pole 2PV045 - S/S 72568Kings Point Dr KINGS POINT | 100 | 327 | 31065 | 0.034703 | 0.00011171
2013-03-21 09:30AM | 227251 | NA1270 | Rural Short | ISOLATE LV TO CONNECT IN NEW LV ABC | 85 | 180 | 15300 | 0.017092 | 9.4955e-05
2013-03-21 09:30AM | 224628 | ULF2 | Urban | Replace Condemned pole 2PV045 - S/S 72568Kings Point Dr KINGS POINT | 90 | 300 | 28500 | 0.031838 | 0.00010054
2013-03-22 01:00PM | 227403 | B710 | Urban | Rusty Column | 7 | 120 | 840 | 0.00093838 | 7.8198e-06
2013-03-22 08:00AM | 222950 | A051 | Rural Short | Replace HV X-Arm @ Pole 17.Replace HV X-Arm @ Pole 276.Repair Pole Cap @ Pole 3.Replace HV X-Arm DOF's and CCT @ Sub 1431 | 45 | 390 | 17550 | 0.019605 | 5.027e-05
2013-03-22 08:00AM | 223051 | 27446 | Rural Short | isolate lv to augment hv | 269 | 510 | 137190 | 0.15326 | 0.00030051
2013-03-22 08:00AM | 223209 | S737 | Rural Short | Retrofit sub 6730. Vesperman Rd Glenorie | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-03-22 08:00AM | 225495 | P608 | Rural Short | Replace Defective Regulator 23729 | 53 | 480 | 25440 | 0.02842 | 5.9207e-05
2013-03-22 08:00AM | 225726 | 48185 | Rural Short | replace cond pole 204 | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-03-22 08:00AM | 223811 | 5878 | Urban | REPLACE POLE 2547 | 34 | 480 | 16320 | 0.018231 | 3.7982e-05
2013-03-22 08:00AM | 224161 | MR2292 | Urban | FAULT FIND + LOCATE HV CABLE FAULT BETWEEN SW 26029 SUB 20439 and SW 34130 SUB 20437 | 155 | 480 | 74400 | 0.083114 | 0.00017315
2013-03-22 08:00AM | 224217 | 8686 | Urban | Augment 6 bays of HV OH mains and upgrade hardware to 22kV. | 67 | 480 | 32160 | 0.035927 | 7.4847e-05
2013-03-22 08:00AM | 224218 | 8686 | Urban | Isolate LV mains for HV OH augmentation. | 54 | 480 | 25920 | 0.028956 | 6.0324e-05
2013-03-22 08:00AM | 226242 | WL1217 | Urban | REPLACE SERVICE HARNESS SUB 2733 | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2013-03-22 08:00AM | 226326 | CD1271 | Urban | Restrain HV conductors between Pole 106 and Pole 107 Replace pole cap on Pole 107. | 20 | 300 | 6000 | 0.0067027 | 2.2342e-05
2013-03-22 08:00AM | 226592 | S776 | Urban | REPLACE RAGBOLT COLUMN # 717542 | 36 | 480 | 17280 | 0.019304 | 4.0216e-05
2013-03-22 08:00AM | 226613 | 41537 | Urban | REPLACE SERVICE HARNESS and 3 X SERVICES @ SUB # 4541 | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2013-03-22 08:00AM | 227142 | MR2292 | Urban | HV Cable Fault Location | 143 | 480 | 68640 | 0.076679 | 0.00015975
2013-03-22 08:30AM | 222696 | MG1267 | Rural Short | Augment HV Mains | 51 | 480 | 24480 | 0.027347 | 5.6973e-05
2013-03-22 08:30AM | 225404 | MG1267 | Rural Short | Augment Hv Mains | 27 | 480 | 12960 | 0.014478 | 3.0162e-05
2013-03-22 08:30AM | 225497 | W127 | Rural Short | Replace HV and LV crossarms + tighten pins | 140 | 390 | 54600 | 0.060995 | 0.0001564
2013-03-22 08:30AM | 225565 | W127 | Rural Short | Replace LV Crossarms | 42 | 390 | 16380 | 0.018298 | 4.6919e-05
2013-03-22 08:30AM | 226363 | BWE2 | Rural Short | New Sub | 32 | 450 | 14400 | 0.016087 | 3.5748e-05
2013-03-22 08:30AM | 226438 | MG1286 | Rural Short | Trim Trees Near Powerlines | 179 | 240 | 42960 | 0.047991 | 0.00019996
2013-03-22 08:30AM | 226723 | S743 | Rural Short | Augment LV OH mains 150 ABC. Alter Sub 6640 for LV ABC. Remove old poles.(District Switcher) | 10 | 420 | 4200 | 0.0046919 | 1.1171e-05
2013-03-22 08:30AM | 226238 | SZ1352 | Urban | Replace condemned columns 8884 | 16 | 180 | 2880 | 0.0032173 | 1.7874e-05
2013-03-22 09:00AM | 226025 | GG1269 | Rural Short | Replace USLs 74616 and 74618 and M and R ABS 38952 Retro SUB 41947 | 3 | 180 | 540 | 0.00060324 | 3.3514e-06
2013-03-22 09:00AM | 226697 | CLC2 | Urban | Change LV Poles3GA079 and 3GA114 | 51 | 360 | 18360 | 0.02051 | 5.6973e-05
2013-03-22 09:00AM | 227125 | 2815 | Urban | LV Crossarm changeover | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2013-03-22 09:00AM | 227203 | 2806 | Urban | LV Pole change over | 1 | 240 | 240 | 0.00026811 | 1.1171e-06
2013-03-22 09:00AM | 227406 | 49010 | Urban | Rusty Column | 33 | 240 | 7920 | 0.0088476 | 3.6865e-05
2013-03-22 09:00AM | 227413 | M397 | Urban | LIMITED DISTRICT SWITCHINGTo allow staff to replace transformer at Sub 10776 Richardson Rd Springhill. | 2 | 180 | 360 | 0.00040216 | 2.2342e-06
2013-03-22 10:00AM | 226472 | ULL2 | Rural Short | 1. Replace Condemned pole 2PY040 2. Replace Condemned pole 2PY0233.Defect RepairsPrinces Hwy BURRILL Lake | 8 | 270 | 2160 | 0.002413 | 8.937e-06
2013-03-22 10:30AM | 225973 | 46481 | Urban | Replace service pole 512 | 3 | 300 | 900 | 0.0010054 | 3.3514e-06
2013-03-22 10:30AM | 226236 | SZ1352 | Urban | Replace condemned columns 1046 | 28 | 240 | 6720 | 0.007507 | 3.1279e-05
2013-03-23 08:00AM | 227548 | X879 | Rural Short | Redirect LV OH Mains | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-03-23 08:00AM | 226136 | 2828 | Urban | Install pole and ABS 79356.Replace poles. | 113 | 450 | 50850 | 0.056806 | 0.00012623
2013-03-24 07:00AM | 225282 | WQ1227 | Urban | DISTRIBUTION EARTH REFURBISHMENT | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-03-24 07:00AM | 226371 | GV1234 | Urban | Decommission sub7784 uprate TX and switchgear @ sub 22736. Install switching station 27730. Replace UGOH at pole 739 | 13 | 600 | 7800 | 0.0087135 | 1.4523e-05
2013-03-24 07:00AM | 227339 | WQ1227 | Urban | DISTRIBUTION EARTH REFURBISHMENT | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-03-24 07:00AM | 227468 | 1962 | Urban | Repair LV Board in Pillar | 1 | 180 | 180 | 0.00020108 | 1.1171e-06
2013-03-24 07:30AM | 224194 | PKC2 | Urban | POLE RELOCATION | 24 | 450 | 10800 | 0.012065 | 2.6811e-05
2013-03-24 07:30AM | 225413 | KMD2 | Urban | Replace pole 4KG016 intall new pole with LBS 124042 remove ABS 70520 | 158 | 420 | 66360 | 0.074132 | 0.0001765
2013-03-24 08:00AM | 225870 | UNH2 | Urban | REPLACE ABS POLE | 33 | 420 | 13860 | 0.015483 | 3.6865e-05
2013-03-24 08:00AM | 227579 | 17070 | Urban | LV Pillar Change | 3 | 180 | 540 | 0.00060324 | 3.3514e-06
2013-03-24 08:00AM | 227627 | B745 | Urban | Remove Mains | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-03-24 08:30AM | 226684 | CRE2 | Urban | Replace Pad Substation 43299 and Retrofit Sub 40311 | 118 | 390 | 46020 | 0.05141 | 0.00013182
2013-03-24 09:00AM | 226672 | BDE2 | Urban | Install New LBS 94480 and New ABS 94479Meroo Rd BOMADERRY. | 27 | 360 | 9720 | 0.010858 | 3.0162e-05
2013-03-24 09:00AM | 227024 | X863 | Urban | Change services on pole changeovers on poles 17 and 41 Fdr 825 | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2013-03-24 09:00AM | 227466 | 1962 | Urban | Repair LV Board in Pillar | 1 | 120 | 120 | 0.00013405 | 1.1171e-06
2013-03-24 10:00AM | 227577 | 46770 | Urban | LV Pillar Change | 2 | 120 | 240 | 0.00026811 | 2.2342e-06
2013-03-24 12:00PM | 225980 | S737 | Rural Short | Feeder 420 - Stand new 33kV concrete poles string 11kV centre phase and install temp USL. | 60 | 90 | 2700 | 0.0030162 | 6.7027e-05
2013-03-25 08:00AM | 221764 | 5498 | Urban | Augment 3 bays of HV OH mains. | 112 | 480 | 53760 | 0.060056 | 0.00012512
2013-03-25 08:00AM | 223295 | R214 | Urban | new PMS32283. Remove ex sub 10562. | 12 | 540 | 6480 | 0.0072389 | 1.3405e-05
2013-03-25 08:00AM | 224396 | WH1235 | Urban | Replace poles + Install USL + Install DOFs | 135 | 480 | 64800 | 0.072389 | 0.00015081
2013-03-25 08:00AM | 226623 | 2829 | Urban | Install DOFs 77495 (40A)Augment HV OH mains 7/4.5 AAC(District Switcher) | 82 | 480 | 39360 | 0.04397 | 9.1604e-05
2013-03-25 08:30AM | 226731 | RWD2 | Rural Short | Stand and/or replace poles 3XK153 (208) 816676 (209) 16488 (210) 3XK155 (211) 816678 (212) 816489 (213) 3XK157 (214) 3XK158 (215) 816681 (216) 816682 (217) 3XK160 (218) 3XK161 (219) 3XK162 (220) 3XK163 (221) 3XK168 (222) 3XK169 (223). | 35 | 480 | 16800 | 0.018768 | 3.9099e-05
2013-03-25 10:00AM | 226272 | 9025 | Urban | IDENTIFY AND LABEL DIST FUSES @ SUB # 7102 and REPLACE CONDEMNED COLUMN # 717184 | 51 | 240 | 12240 | 0.013674 | 5.6973e-05
2013-03-25 12:00PM | 226428 | 20723 | Urban | Replace coloumn # 14427 | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2013-03-26 06:30AM | 223214 | M389 | Urban | 2 new poles and ABS92436 | 4 | 660 | 2640 | 0.0029492 | 4.4685e-06
2013-03-26 07:00AM | 227437 | B718 | Urban | Rusty Column | 14 | 120 | 1680 | 0.0018768 | 1.564e-05
2013-03-26 08:00AM | 225028 | 8634 | Rural Short | change 2 poles replace usl with sectionaliser andreplace usl with dofs and augment 1 bay of hv | 28 | 510 | 14280 | 0.015952 | 3.1279e-05
2013-03-26 08:00AM | 226862 | A096 | Rural Short | REPLACELV X-ARMS and RE-WIRE @ SUB # 2165 | 13 | 480 | 6240 | 0.0069708 | 1.4523e-05
2013-03-26 08:00AM | 226916 | 35693 | Rural Short | Replace HV Cast Iron UG/OH and transition joint in cable. | 151 | 480 | 72480 | 0.080969 | 0.00016869
2013-03-26 08:00AM | 226169 | 9017 | Urban | Retension Hardex | 355 | 480 | 170400 | 0.19036 | 0.00039658
2013-03-26 08:00AM | 227859 | 48166 | Urban | Convert Column 813426 to Pillar 122164 and relocate column to new position. | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-03-26 08:30AM | 224153 | MG1267 | Rural Short | HV Upgrade | 37 | 480 | 17760 | 0.01984 | 4.1333e-05
2013-03-26 08:30AM | 226056 | DP1210 | Rural Short | Replace pole 4AX068 and Install LBS | 7 | 360 | 2520 | 0.0028151 | 7.8198e-06
2013-03-26 08:30AM | 226523 | P608 | Rural Short | Change sub pole 11821 to 28790 install new poles 822252 822250 and augment mains from ABS 86794 to pole 822246. | 2 | 450 | 900 | 0.0010054 | 2.2342e-06
2013-03-26 08:30AM | 226597 | CLA2 | Rural Short | Install LBS Augment and Re-Route HV Conductors for Feeder CLC2Coonemia Rd CULBURRA. | 6 | 450 | 2700 | 0.0030162 | 6.7027e-06
2013-03-26 08:30AM | 226688 | DP1284 | Rural Short | LOCATE CABLE FAULT and REPAIR CABLE | 147 | 420 | 61740 | 0.068971 | 0.00016422
2013-03-26 08:30AM | 225978 | BLD2 | Urban | Replace Condemned Pole 3PD278 and Retrofit Sub 40045 and Trim trees | 116 | 360 | 41760 | 0.046651 | 0.00012959
2013-03-26 08:30AM | 226617 | FT1209 | Urban | MandR HOLEC SWITCHGEAR TIGHTEN HV HARDEWARE | 2 | 330 | 660 | 0.0007373 | 2.2342e-06
2013-03-26 08:30PM | 225245 | SWJ2 | Urban | Replace ABS and cnr pole | 9 | 540 | 4860 | 0.0054292 | 1.0054e-05
2013-03-26 09:00AM | 225011 | CJ1267 | Urban | REPAIR ABS 4905 | 136 | 360 | 48960 | 0.054694 | 0.00015193
2013-03-26 09:00AM | 226250 | 8770 | Urban | REPAIR SERVICE TO HOUSE 343 | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-03-26 09:00AM | 227204 | 2806 | Urban | LV crossarm change over | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2013-03-26 09:00AM | 227440 | 48999 | Urban | Rusty Column | 25 | 120 | 3000 | 0.0033514 | 2.7928e-05
2013-03-26 09:00AM | 227441 | B713 | Urban | Rusty Column | 23 | 120 | 2760 | 0.0030833 | 2.5694e-05
2013-03-26 09:00AM | 227783 | T893 | Urban | bond in new pillar at pillar 90187 | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2013-03-26 09:30AM | 224386 | ULF2 | Urban | Replace pole 2RR177. | 92 | 270 | 24840 | 0.027749 | 0.00010278
2013-03-27 02:00PM | 227314 | P608 | Rural Short | Augment 11kV OH mains. Install poles. | 42 | 60 | 2040 | 0.0022789 | 4.6919e-05
2013-03-27 06:30AM | 224938 | T894 | Urban | To extend existing low voltage and high voltage overhead mains so that leaning pole can be straightened | 1 | 630 | 630 | 0.00070379 | 1.1171e-06
2013-03-27 07:00AM | 227295 | GG1295 | Rural Short | INSTALL ONE NEW POLE 11KV / REPLACE ONE POLE 11KV | 16 | 540 | 8640 | 0.0096519 | 1.7874e-05
2013-03-27 08:00AM | 226179 | JBA2 | Rural Short | NEW LOAD BREAK SWITCH | 15 | 480 | 7200 | 0.0080433 | 1.6757e-05
2013-03-27 08:00AM | 227028 | R260 | Rural Short | AUGMENT HV MAINS | 46 | 450 | 20700 | 0.023124 | 5.1388e-05
2013-03-27 08:00AM | 227314 | P608 | Rural Short | Augment 11kV OH mains. Install poles. | 110 | 420 | 14280 | 0.015952 | 0.00012288
2013-03-27 08:00AM | 221494 | 2806 | Urban | Replace one pole and augment two bays of HV OH mains. | 131 | 480 | 62880 | 0.070245 | 0.00014634
2013-03-27 08:00AM | 223027 | 35696 | Urban | Replace USL 12968 with ABS 94465 and augment 5 bays of O/H HV mains to 3 x 120mm CCT. | 66 | 510 | 33660 | 0.037602 | 7.373e-05
2013-03-27 08:00AM | 224091 | HKB2 | Urban | Replace 9 poles Install 3 X LBS install 11 bays of HV mains. | 364 | 480 | 174720 | 0.19518 | 0.00040663
2013-03-27 08:00AM | 224129 | 46752 | Urban | Replace 3 poles and augment 1 bay of HV OH mains. Install two new DOF's. | 312 | 540 | 168480 | 0.18821 | 0.00034854
2013-03-27 08:00AM | 226313 | A319 | Urban | establish new pad sub | 52 | 540 | 28080 | 0.031369 | 5.809e-05
2013-03-27 08:00AM | 227545 | 19815 | Urban | Perform 1 x LV IDandSpike | 9 | 450 | 4050 | 0.0045243 | 1.0054e-05
2013-03-27 08:00AM | 227589 | 2829 | Urban | Replace Pole | 27 | 480 | 12960 | 0.014478 | 3.0162e-05
2013-03-27 08:30AM | 224520 | 8799 | Rural Short | Augment 5 bays of 120mm HV CCT | 48 | 450 | 21600 | 0.02413 | 5.3622e-05
2013-03-27 08:30AM | 227224 | 5496 | Urban | LV crossarm change over | 2 | 270 | 540 | 0.00060324 | 2.2342e-06
2013-03-27 09:00AM | 223502 | HKF2 | Urban | Replace pole 3HH248. | 107 | 360 | 38520 | 0.043031 | 0.00011953
2013-03-27 09:00AM | 226671 | 35524 | Urban | Replace Condemed Coloumn PL716931 (# 42720) | 25 | 240 | 6000 | 0.0067027 | 2.7928e-05
2013-03-27 09:00AM | 227219 | 2815 | Urban | LV Crossarm change over | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2013-03-27 09:00AM | 227580 | 7994 | Urban | Replace Switch in Pillar | 32 | 240 | 7680 | 0.0085795 | 3.5748e-05
2013-03-27 09:00AM | 227582 | 8685 | Urban | Rusty Columns | 79 | 360 | 28440 | 0.031771 | 8.8252e-05
2013-03-27 09:00AM | 227584 | 8685 | Urban | Rusty Columns | 9 | 360 | 3240 | 0.0036195 | 1.0054e-05
2013-03-27 10:00PM | 225531 | 27028 | Urban | Replace existing 1000KVA Transformer with FR3 (gel) Type and Replace existing cubicle with new Steel Cubicle in PM SUB 20625 | 3 | 390 | 1170 | 0.001307 | 3.3514e-06
2013-03-27 12:00PM | 226677 | C889 | Urban | Replace Condemed coloumn PL715477 ( # 2254) | 30 | 240 | 7200 | 0.0080433 | 3.3514e-05
2013-03-28 08:00AM | 224147 | 8798 | Rural Short | augment lv mains and install new ABS | 507 | 510 | 258570 | 0.28885 | 0.00056638
2013-03-28 08:00AM | 227762 | W163 | Rural Short | LIMITED DISTRICT SWITCHING INSTALL MDI AT SUB 25585 | 2 | 270 | 540 | 0.00060324 | 2.2342e-06
2013-03-28 08:00AM | 224827 | 5875 | Urban | Replace HV crossarms and LV box arms and LV links and fuses @ SUB 3532 | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2013-03-28 08:00AM | 227704 | L537 | Urban | Replace Pole | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2013-03-28 08:30AM | 226494 | JBA2 | Rural Short | AUGMENT HV MAINS BETWEEN POLES 783325 and 877401 also TREE TRIMMING ADJ to POLE 4TJ030 in MISTY LANE JAMBEROO | 12 | 420 | 5040 | 0.0056303 | 1.3405e-05
2013-03-28 08:30AM | 226846 | RWA2 | Rural Short | Trim Trees Near Powerlines | 24 | 420 | 10080 | 0.011261 | 2.6811e-05
2013-03-28 08:30AM | 226301 | PKA2 | Urban | REPLACE CONDEMNED POLE | 154 | 420 | 60480 | 0.067563 | 0.00017204
2013-03-28 08:30AM | 227231 | S599 | Urban | LV crossarm changeover | 2 | 270 | 540 | 0.00060324 | 2.2342e-06
2013-03-28 08:30AM | 227233 | 5498 | Urban | LV crossarm changeover | 5 | 270 | 1350 | 0.0015081 | 5.5856e-06
2013-03-28 09:00AM | 227701 | CJ1241 | Urban | Rusty Column | 10 | 120 | 1200 | 0.0013405 | 1.1171e-05
2013-03-28 09:00AM | 227703 | CJ1241 | Urban | Rusty Column | 23 | 120 | 2760 | 0.0030833 | 2.5694e-05
2013-03-28 09:00AM | 227725 | C824 | Urban | Bond in LV Cable | 11 | 90 | 990 | 0.0011059 | 1.2288e-05
2013-03-28 10:00AM | 226468 | 35524 | Urban | Replace Coloumn # 42737 | 11 | 240 | 2640 | 0.0029492 | 1.2288e-05
2013-04-03 06:00AM | 227371 | 438 | Urban | Interruptiion/Isolation to allow for the scope of works as per DNR 226318 | 89 | 660 | 58740 | 0.06562 | 9.9424e-05
2013-04-03 08:00AM | 226395 | HKA2 | Rural Short | INSTALL 3 POLES ONE LBS AND AUGMENT 6 BAYS OF HV MAINS. | 106 | 480 | 50880 | 0.056839 | 0.00011841
2013-04-03 08:00AM | 224219 | 8686 | Urban | Augment 7 bays of HV OH mains to 19/3.25 AAC. | 122 | 480 | 58560 | 0.065419 | 0.00013629
2013-04-03 08:30AM | 226483 | BWH2 | Rural Short | HV Augmentation and Pole Replacement | 231 | 480 | 95520 | 0.10671 | 0.00025805
2013-04-04 08:00AM | 227790 | HKE2 | Rural Short | Replace 4 poles Install LBS remove DOFs and augment 5 bays of HV mains. | 59 | 480 | 28320 | 0.031637 | 6.591e-05
2013-04-04 08:00AM | 226221 | PKF2 | Urban | Replace Poles and Augment H/V Mains | 61 | 450 | 27450 | 0.030665 | 6.8144e-05
2013-04-04 08:00AM | 227101 | 9050 | Urban | Augment LV mains and re-arrange jib arm and HV droppers at sub 21878 | 26 | 420 | 10920 | 0.012199 | 2.9045e-05
2013-04-04 08:00AM | 227534 | 10242 | Urban | CONTRACTOR TREE TRIMMING | 50 | 420 | 21000 | 0.02346 | 5.5856e-05
2013-04-04 08:30AM | 224307 | MG1267 | Rural Short | HV Upgrade | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2013-04-04 08:30AM | 226103 | L942 | Rural Short | Install capacitor on pole 869280 | 17 | 390 | 6630 | 0.0074065 | 1.8991e-05
2013-04-04 09:00AM | 224870 | SC1238 | Urban | Augment LV OH mains 150 ABC.Alter LV circuit. | 14 | 360 | 5040 | 0.0056303 | 1.564e-05
2013-04-04 09:00AM | 227560 | S674 | Urban | LV pole changeover | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2013-04-05 08:00AM | 224722 | 35988 | Rural Short | New PMS29877 | 64 | 540 | 34560 | 0.038608 | 7.1496e-05
2013-04-05 08:00AM | 221678 | 2812 | Urban | Replace one pole and augment 2 bays of HV OH mains. | 315 | 540 | 170100 | 0.19002 | 0.00035189
2013-04-05 08:30AM | 226314 | L948 | Rural Short | Install capacitor on pole 869846. Replace LV arms @ sub 5519 | 46 | 420 | 19320 | 0.021583 | 5.1388e-05
2013-04-05 08:30AM | 226753 | MG1267 | Rural Short | Install New Poles | 64 | 480 | 30720 | 0.034318 | 7.1496e-05
2013-04-05 08:30AM | 226765 | PKA2 | Urban | Retrofit and Change TX Sub 42652 | 31 | 270 | 8370 | 0.0093503 | 3.4631e-05
2013-04-05 09:00AM | 226556 | 6421 | Urban | REPLACE SERVICE HARNESS SUB 5161 | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2013-04-05 09:00AM | 227559 | S674 | Urban | LV pole change over | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2013-04-05 12:10AM | 227799 | PKC2 | Urban | Isolate L.V. mains for high loads. | 2 | 350 | 700 | 0.00078198 | 2.2342e-06
2013-04-06 06:00AM | 226264 | 8689 | Urban | Augment HV OH mains to 150 NMS ABC.(see 33kv DandR 226265) | 1 | 30 | 30 | 3.3514e-05 | 1.1171e-06
2013-04-06 06:00PM | 225859 | 3185 | Urban | REPLACE USL 1636 WITH ABS 87014 REPLACE LTS 17582 WITH LBS 87015 AND REMOVE ABS 1646 | 148 | 600 | 52800 | 0.058984 | 0.00016533
2013-04-06 07:00AM | 226200 | MC1252 | Rural Short | New HV poles | 10 | 540 | 5400 | 0.0060324 | 1.1171e-05
2013-04-06 08:00AM | 225853 | 25451 | Rural Short | NEW PAD SUBSTAION | 20 | 480 | 9600 | 0.010724 | 2.2342e-05
2013-04-06 08:00AM | 226763 | C854 | Urban | REPLACE SRA POLE # 193 | 52 | 480 | 24960 | 0.027883 | 5.809e-05
2013-04-06 08:00AM | 227656 | 27191 | Urban | Install a new pillar and switch | 4 | 300 | 1200 | 0.0013405 | 4.4685e-06
2013-04-06 08:00AM | 227903 | WL1292 | Urban | CCommission New 315kVA Pad Sub No. 29991 via New UGOH on Replaced Pole 2450 | 12 | 480 | 5760 | 0.0064346 | 1.3405e-05
2013-04-06 08:30AM | 227612 | 8693 | Urban | Augment LV OH mains 150 ABC.(District switcher) | 20 | 330 | 6600 | 0.007373 | 2.2342e-05
2013-04-06 09:30AM | 227889 | FF1280 | Urban | TRF ISOLATION - SUB 18196 ( TO ALLOW CUSTOMER TO WORK ON LV SWITCHBOARD) | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-04-07 07:00AM | 226814 | UNE2 | Urban | NEW PAD SUBSTATION | 4 | 540 | 2160 | 0.002413 | 4.4685e-06
2013-04-07 07:30AM | 226512 | J473 | Urban | Re-dress HV Cable and MandR HV Switchgear in SUB 13237 to rectify PIN Defect D205 and Re-pump HV Cable M282 and MandR HV switchgear in SUB 13273 to rectify PIN Defect D214 | 5 | 390 | 1950 | 0.0021784 | 5.5856e-06
2013-04-07 08:00AM | 228098 | T868 | Rural Short | LIMITED DISTRICT SWITCHINGTo allow staff to replace poles #51 and #101 Appin Rd Appin | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2013-04-07 08:00AM | 221844 | WH1224 | Urban | Augment 11 bays of HV OH mains. | 97 | 480 | 46560 | 0.052013 | 0.00010836
2013-04-07 08:00AM | 221845 | WH1224 | Urban | Isolate LV mains for augmentation of 11 bays of HV OH mains. | 69 | 480 | 33120 | 0.036999 | 7.7081e-05
2013-04-08 06:00AM | 227661 | 5868 | Urban | HVSWGR MAINT | 56 | 480 | 26880 | 0.030028 | 6.2559e-05
2013-04-08 07:30AM | 227478 | NE1216 | Urban | Install switching station 29572 and sub 29573. Remove OH mains USL's 74 39883 10161 and ABS 63. | 9 | 630 | 5670 | 0.0063341 | 1.0054e-05
2013-04-08 08:00AM | 223686 | 35824 | Rural Short | LV OH mains augment U/R sub11725. | 85 | 480 | 40800 | 0.045578 | 9.4955e-05
2013-04-08 08:00AM | 225150 | 8634 | Rural Short | augment 2 bays of lv mains install 4 poles and change sub pole | 17 | 510 | 8670 | 0.0096854 | 1.8991e-05
2013-04-08 08:00AM | 223787 | 41537 | Urban | Augment OH conductor | 98 | 480 | 47040 | 0.052549 | 0.00010948
2013-04-08 08:00AM | 226408 | NWF2 | Urban | NEW PAD SUBSTATION | 79 | 540 | 42660 | 0.047656 | 8.8252e-05
2013-04-08 08:30AM | 227316 | MG1267 | Rural Short | Replace Condemned Pole 3T0887 and Run LV ABC | 30 | 420 | 12600 | 0.014076 | 3.3514e-05
2013-04-08 09:00AM | 227568 | CLD2 | Rural Short | Augment LV Mians | 43 | 240 | 10320 | 0.011529 | 4.8036e-05
2013-04-08 09:00AM | 227587 | CLD2 | Rural Short | Augment LV Mians | 86 | 240 | 20640 | 0.023057 | 9.6072e-05
2013-04-08 09:00AM | 224555 | HKB2 | Urban | Replace pole 200123. | 16 | 300 | 4800 | 0.0053622 | 1.7874e-05
2013-04-08 09:00AM | 227610 | S599 | Urban | LV pole change over | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2013-04-08 10:00AM | 225826 | 48168 | Urban | DISTRIBUTION EARTH REFURBISHMENT | 2 | 120 | 240 | 0.00026811 | 2.2342e-06
2013-04-09 02:00AM | 225559 | L545 | Urban | Perform CB Exercises and Operational Checks @ sub 22996 Alpha St. Blacktown | 1 | 240 | 240 | 0.00026811 | 1.1171e-06
2013-04-09 07:00PM | 225879 | CRB2 | Urban | Replace Condemned ABS pole 70285 and Replace HV crossarm on Sub 40268 | 55 | 480 | 26400 | 0.029492 | 6.1442e-05
2013-04-09 08:00AM | 224226 | 8798 | Rural Short | augment hv mains | 230 | 510 | 117300 | 0.13104 | 0.00025694
2013-04-09 08:00AM | 225027 | BK1299 | Rural Short | CHANGE POLES 37 + 38 redress poles 181 48 49 51 52. | 41 | 480 | 19680 | 0.021985 | 4.5802e-05
2013-04-09 08:00AM | 226798 | A098 | Rural Short | RETRO / RE-WIRE SUB # 7006REPLACE HV and LV CROSSARM | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2013-04-09 08:00AM | 227329 | L588 | Rural Short | STAND NEW POLE AND AUGEMT MAINS | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-04-09 08:00AM | 227798 | X877 | Rural Short | Replace poles install auto LBS | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2013-04-09 08:00AM | 224364 | A344 | Urban | Allow staff to remove ABS 1012 and pole. erect new LBS 97938 and pole. | 180 | 420 | 97440 | 0.10885 | 0.00020108
2013-04-09 08:00AM | 224364 | A344 | Urban | Allow staff to remove ABS 1012 and pole. erect new LBS 97938 and pole. | 284 | 480 | 111360 | 0.1244 | 0.00031726
2013-04-09 08:00AM | 226298 | 8693 | Urban | Replace pole.Replace ABS 8842 with LBS 97244.Augment LV OH mains 150 ABC. | 27 | 480 | 12960 | 0.014478 | 3.0162e-05
2013-04-09 08:00AM | 228481 | 48166 | Urban | Bond in new section of LV Network via 2 x STJ on existing Cable between Pillar 113322 and Pillar 112831 | 9 | 360 | 3240 | 0.0036195 | 1.0054e-05
2013-04-09 08:30AM | 227048 | RWD2 | Rural Short | Stand poles 3KO125 (200) 330642 ABS (201) 786246 (202) and new pole 816674 (207) plus Augment 33 kV Conductor between Poles 3KO046 (193) to 331642 (201). And tree trimming x 2 locations. | 46 | 480 | 22080 | 0.024666 | 5.1388e-05
2013-04-09 08:30AM | 227051 | JBB2 | Rural Short | 11kV OUTAGE TO INSTALL 3 NEW POLES CONDUCTOR AND OHEW BETWEEN ABS 61691 AND ABS 73309 on 33KV FDR 7009 | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-04-09 08:30AM | 227111 | L942 | Rural Short | Replace LV arms @ pole 278 | 21 | 270 | 5670 | 0.0063341 | 2.346e-05
2013-04-09 08:30AM | 226227 | SHC2 | Urban | Replace Pole 4DR067 | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-04-09 09:00AM | 227450 | F602 | Urban | Lv crossarm changeover | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2013-04-09 09:00AM | 227609 | 2815 | Urban | LV pole change over | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-04-09 09:00AM | 228467 | 8685 | Urban | Cable Fault | 23 | 360 | 8280 | 0.0092498 | 2.5694e-05
2013-04-10 08:00AM | 226214 | L591 | Rural Short | INSTALL KAON FUSE SAVERS REPLACE HV CROSSARM REPAIR LEANING POLES AND RETROFIT SUBS | 29 | 450 | 13050 | 0.014578 | 3.2396e-05
2013-04-10 08:00AM | 226614 | X877 | Rural Short | REPLACE USL 19019 WITH LBS 97728 | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2013-04-10 08:00AM | 226900 | A096 | Rural Short | REPLACE LV X-ARMS @ | 57 | 480 | 27360 | 0.030564 | 6.3676e-05
2013-04-10 08:00AM | 227191 | DP1284 | Rural Short | H/V augmentation | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2013-04-10 08:00AM | 223078 | 35696 | Urban | Replace DOF G452 with Sectionliser 93987 and augment 5 bays of O/H HV mains to 3 x 120mm CCT. | 38 | 510 | 19380 | 0.02165 | 4.2451e-05
2013-04-10 08:00AM | 224448 | 2829 | Urban | REPLACE POLE 917 | 38 | 480 | 18240 | 0.020376 | 4.2451e-05
2013-04-10 08:00AM | 224613 | 8675 | Urban | Replace poles + Augment Spans + Install HABS | 83 | 480 | 39840 | 0.044506 | 9.2721e-05
2013-04-10 08:00AM | 228008 | 8679 | Urban | REPLACE COLUMN and BURNT UP Bph TAIL AT COLUMN # 1707 - SEDGMAN CRES SHALVEY | 23 | 360 | 8280 | 0.0092498 | 2.5694e-05
2013-04-10 08:30AM | 224549 | 8799 | Rural Short | Augment 6 bay of 150mm LVABC from pole 829112 to sub 3677 | 48 | 450 | 21600 | 0.02413 | 5.3622e-05
2013-04-10 08:30AM | 227055 | JBB2 | Rural Short | 11kV OUTAGE TO INSTALL 3 NEW POLES CONDUCTOR AND OHEW BETWEEN ABS 61691 AND ABS 73309 on 33KV FDR 7009 | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-04-10 08:30AM | 226754 | NWF2 | Urban | Replace Condemned Pole 3C0287 and Transformer sub 42388 | 92 | 450 | 41400 | 0.046249 | 0.00010278
2013-04-10 08:30AM | 227391 | NWA2 | Urban | Replace one pole and remove 2 bays of HV OH mains. | 195 | 480 | 136320 | 0.15229 | 0.00021784
2013-04-10 08:30AM | 228699 | D852 | Urban | LV Project | 20 | 390 | 7800 | 0.0087135 | 2.2342e-05
2013-04-10 09:00AM | 225307 | 35989 | Rural Short | Replace Condemned Pole No 183 Replace HV DOF's on Sub 11567 | 85 | 210 | 17850 | 0.019941 | 9.4955e-05
2013-04-10 09:00AM | 228408 | MR2299 | Urban | Replace LV switch | 26 | 180 | 4680 | 0.0052281 | 2.9045e-05
2013-04-10 09:30AM | 228435 | ULH2 | Urban | replace x pole 2RP 676 | 72 | 270 | 19440 | 0.021717 | 8.0433e-05
2013-04-10 09:30AM | 228577 | HR1250 | Urban | To Isolate LV to allow cables to be relocated and to remove redundant HV mains | 240 | 300 | 72000 | 0.080433 | 0.00026811
2013-04-10 10:00AM | 227386 | MVB2 | Rural Short | Holec HV Switchgear MandR at Padmount Substation 30158 | 35 | 180 | 6300 | 0.0070379 | 3.9099e-05
2013-04-11 07:30AM | 226877 | 10248 | Urban | REPLACE LV POLE J592 WITH NEW POLE 882040 | 70 | 480 | 33600 | 0.037535 | 7.8198e-05
2013-04-11 08:00AM | 226747 | 35816 | Rural Short | Change USL R883 and install sectionaliser 97082 and repair defects. | 33 | 480 | 15840 | 0.017695 | 3.6865e-05
2013-04-11 08:00AM | 227345 | RWD2 | Rural Short | Install a new pole Top Mounted LBS 123264 | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-04-11 08:00AM | 227459 | 8634 | Rural Short | Replace condemned pole 8 Replace HV arm @ pole 49. Replace HV arm @ pole 27 Replace condemned LV pole 39. | 31 | 390 | 12090 | 0.013506 | 3.4631e-05
2013-04-11 08:00AM | 228503 | 35988 | Rural Short | LV bond in to existing LV circuit. | 10 | 420 | 4200 | 0.0046919 | 1.1171e-05
2013-04-11 08:00AM | 224349 | 17061 | Urban | HV SW GR MAINT + REPLACE TX SUB 15794 | 89 | 480 | 42720 | 0.047723 | 9.9424e-05
2013-04-11 08:00AM | 225464 | 9022 | Urban | strip out lv street light conductor | 199 | 510 | 101490 | 0.11338 | 0.00022231
2013-04-11 08:00AM | 227465 | 35508 | Urban | Remove SL Coloumn Install Pillar and New Ragbolt | 9 | 480 | 4320 | 0.004826 | 1.0054e-05
2013-04-11 08:00AM | 228499 | AZ1264 | Urban | LV Changeover | 12 | 450 | 5400 | 0.0060324 | 1.3405e-05
2013-04-11 08:30AM | 225678 | WBD2 | Rural Short | Replace Condemned pole 2G0139 and 2G0140 and replace HV crossarm 2G0142 | 56 | 390 | 21840 | 0.024398 | 6.2559e-05
2013-04-11 08:30AM | 227057 | JBB2 | Rural Short | 11kV OUTAGE TO INSTALL 3 NEW POLES on 33KV FDR 7009 | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-04-11 08:30AM | 227653 | BWE2 | Rural Short | 11 kV isolation to allow 33 kV OHEW to be strung - 33 kV Fdr 7901 | 64 | 480 | 30720 | 0.034318 | 7.1496e-05
2013-04-11 08:30AM | 227424 | WRC2 | Urban | Replace ABS 71894 | 122 | 240 | 29280 | 0.032709 | 0.00013629
2013-04-11 08:30AM | 227875 | UNB2 | Urban | REPLACE STREET LIGHT COLUMNS | 87 | 390 | 33930 | 0.037904 | 9.7189e-05
2013-04-11 08:30AM | 227923 | BWC2 | Urban | Install 11KV O/H Aerial Earthwire between poles 3R0490 and 821889 | 13 | 450 | 5850 | 0.0065352 | 1.4523e-05
2013-04-11 09:00AM | 225175 | ULE2 | Rural Short | Replace poles and Install New DOFs 123235Woodstock Rd MILTON | 32 | 360 | 11520 | 0.012869 | 3.5748e-05
2013-04-11 09:00AM | 227452 | 2812 | Urban | LV crossarm changeover | 14 | 360 | 5040 | 0.0056303 | 1.564e-05
2013-04-11 09:00AM | 227561 | 2812 | Urban | Lv Crossarm changeover | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2013-04-11 09:00AM | 228776 | KMC2 | Urban | REPLACE X POLE 4KG120 | 17 | 240 | 4080 | 0.0045578 | 1.8991e-05
2013-04-11 09:30PM | 227395 | MG1234 | Rural Short | Holec HV Switchgear MandR at Padmount Substation 31344 | 61 | 180 | 10980 | 0.012266 | 6.8144e-05
2013-04-12 08:00AM | 223068 | 27446 | Rural Short | Augment HV Mains | 251 | 510 | 128010 | 0.143 | 0.0002804
2013-04-12 08:00AM | 227044 | NG1210 | Rural Short | Limited District SwitchingChange DOF's J017 @ pole 65Change Sub Pole 79 Sub 10100Change TX 10100 | 11 | 465 | 5115 | 0.0057141 | 1.2288e-05
2013-04-12 08:00AM | 227864 | R260 | Rural Short | AUGEMENT HV MAINS | 44 | 480 | 21120 | 0.023594 | 4.9153e-05
2013-04-12 08:00AM | 228418 | 25403 | Rural Short | LV switching to allow scope of works to be completed as per DNR 228045 | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2013-04-12 08:00AM | 224221 | 8677 | Urban | Augment 6 bays of HV OH mains replace one USL with ABS and install new DOF's. | 118 | 540 | 63720 | 0.071183 | 0.00013182
2013-04-12 08:00AM | 224222 | 8677 | Urban | Isolate LV mains for HV OH augmenation USL replacement and installation of new DOF's. | 60 | 540 | 32400 | 0.036195 | 6.7027e-05
2013-04-12 08:00AM | 224656 | 2819 | Urban | REPLACE POLES 577 + 578 + 579 | 11 | 480 | 5280 | 0.0058984 | 1.2288e-05
2013-04-12 08:00AM | 227516 | 35519 | Urban | Remove coloumn # 7000 Install Pillar over over old ragbolt Install new ragbolt behind pillar | 16 | 240 | 3840 | 0.0042897 | 1.7874e-05
2013-04-12 08:00AM | 228497 | AZ1264 | Urban | LV Chaqngeover | 13 | 420 | 5460 | 0.0060995 | 1.4523e-05
2013-04-12 08:00AM | 228582 | CJ1249 | Urban | Install:LV UG cable LV pillar | 14 | 240 | 3360 | 0.0037535 | 1.564e-05
2013-04-12 08:30AM | 227095 | L946 | Rural Short | Installing Capacitor 32209 + pole. Install LBS 95723 + pole. Remove ABS X181 + pole | 7 | 450 | 3150 | 0.0035189 | 7.8198e-06
2013-04-12 09:00AM | 227930 | NA1270 | Rural Short | Install New LBS 95630 and new HV CCT conductors.Depot Rd WEST NOWRA. | 49 | 390 | 19110 | 0.021348 | 5.4739e-05
2013-04-12 09:00AM | 227451 | 2807 | Urban | LV Crossarm changeover | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2013-04-12 09:00AM | 227499 | HR1250 | Urban | Isolate LV OH for work on DandR 227470 | 198 | 300 | 59400 | 0.066357 | 0.00022119
2013-04-12 09:00AM | 228402 | 49916 | Urban | REPLACE RUSTY STREET LIGHT COLUMN 6687 | 18 | 210 | 3780 | 0.0042227 | 2.0108e-05
2013-04-12 09:00AM | 228496 | 49916 | Urban | Replace Rusty Column | 18 | 210 | 3780 | 0.0042227 | 2.0108e-05
2013-04-13 08:00AM | 227693 | W111 | Rural Short | Pull in new OPGW from Pole 41 to Pole 43 and string new 66kV 61/3.25 AAC Conductor from Pole 41 to Pole 43 for new Fdr 869/2. This outage is for clearance purposes. | 6 | 480 | 54720 | 0.061129 | 6.7027e-06
2013-04-13 08:00AM | 227693 | W111 | Rural Short | Pull in new OPGW from Pole 41 to Pole 43 and string new 66kV 61/3.25 AAC Conductor from Pole 41 to Pole 43 for new Fdr 869/2. This outage is for clearance purposes. | 222 | 510 | 58140 | 0.064949 | 0.000248
2013-04-13 08:00AM | 225153 | 8615 | Urban | Augment 5 Bays of HV mains. | 134 | 540 | 72360 | 0.080835 | 0.00014969
2013-04-14 08:00AM | 225848 | GV1208 | Urban | Replace pole 3376 and LV UGOH | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2013-04-14 08:00AM | 226356 | UNF2 | Urban | Install ABS Head | 11 | 300 | 3300 | 0.0036865 | 1.2288e-05
2013-04-14 08:00AM | 228062 | NWF2 | Urban | Replace ABS pole | 1 | 450 | 450 | 0.0005027 | 1.1171e-06
2013-04-14 08:30AM | 226997 | APE2 | Urban | Replace sw/gr in substation make a STJ and terminate HV cable | 68 | 450 | 30600 | 0.034184 | 7.5964e-05
2013-04-14 09:00AM | 225231 | YYA2 | Rural Short | Uprate TX to 300kVA @ S/S 72452York St CUNJARONG POINT. | 172 | 330 | 56760 | 0.063408 | 0.00019214
2013-04-14 09:30AM | 228199 | 46772 | Urban | Transfer 11kV construction to new concrete pole at PL B133. | 3 | 450 | 1350 | 0.0015081 | 3.3514e-06
2013-04-14 12:00PM | 228071 | J515 | Urban | Install Cat 2 LV fusestrip to existing switchgear | 16 | 240 | 3840 | 0.0042897 | 1.7874e-05
2013-04-15 08:00AM | 221846 | WH1209 | Urban | Augment 6 bays of HV OH mains. | 81 | 480 | 38880 | 0.043434 | 9.0487e-05
2013-04-15 08:00AM | 221847 | WH1209 | Urban | Isolate LV mains for HV OH augmentation. | 100 | 480 | 48000 | 0.053622 | 0.00011171
2013-04-15 08:00AM | 226622 | 25783 | Urban | Remove:1 x HV UGOH 2 x polesInstall:1 x HV UGOH 1 x HV STJ 3 x poles HV UG cable new PS 29914 re-mount USL 4210Remove:1 x poleInstall:1 x pole LBS 95088 | 4 | 540 | 2160 | 0.002413 | 4.4685e-06
2013-04-15 08:00AM | 226625 | 25783 | Urban | Remove:2 x poles | 10 | 540 | 5400 | 0.0060324 | 1.1171e-05
2013-04-15 08:00AM | 226971 | C900 | Urban | REPLACE POLE # 211 and | 30 | 480 | 14400 | 0.016087 | 3.3514e-05
2013-04-15 08:00AM | 228221 | SZ1322 | Urban | Low Voltage Outage for Conductor replacement for 33kV Feeder on Cox Street | 224 | 480 | 107520 | 0.12011 | 0.00025023
2013-04-15 08:30AM | 226668 | MVH2 | Rural Short | Stand poles Install USL 124770 and Augment mains | 54 | 480 | 25920 | 0.028956 | 6.0324e-05
2013-04-15 08:30AM | 227343 | MVB2 | Rural Short | Augment a section of 11KV O/H mains | 19 | 360 | 6840 | 0.0076411 | 2.1225e-05
2013-04-15 09:00AM | 228823 | X213 | Rural Short | *LIMITED DISTRICT SWITCHING* REPAIR STRANDED HV CONDUCTOR | 17 | 240 | 4080 | 0.0045578 | 1.8991e-05
2013-04-15 10:00PM | 228180 | MYG2 | Urban | REPLACE and UPGRADE PADMOUNT SUB 27256 | 34 | 420 | 14280 | 0.015952 | 3.7982e-05
2013-04-16 02:00AM | 225581 | 46401 | Urban | Perform CB Exercises and Operational Checks | 608 | 240 | 145920 | 0.16301 | 0.00067921
2013-04-16 08:00AM | 224239 | 8798 | Rural Short | augment 3 bays of hv and tree lopping | 414 | 510 | 211140 | 0.23587 | 0.00046249
2013-04-16 08:00AM | 224245 | 25775 | Urban | FAULT FIND + LOCATE HV CABLE FAULT BETWEEN SW 56125 SUB 25119 and SW 29138 SUB 18376 | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2013-04-16 08:00AM | 228221 | SZ1322 | Urban | Low Voltage Outage for Conductor replacement for 33kV Feeder on Cox Street | 224 | 480 | 107520 | 0.12011 | 0.00025023
2013-04-16 09:00AM | 227595 | CLC2 | Urban | Augment HV Conductors Install New LBS and USL and Remove DOF and USL Penguin Head Rd and Silvermere St CULBURRA. | 606 | 420 | 254520 | 0.28433 | 0.00067697
2013-04-16 09:00AM | 228700 | WL1251 | Urban | Raise LV Mains | 16 | 300 | 4800 | 0.0053622 | 1.7874e-05
2013-04-16 09:00AM | 228884 | M397 | Urban | LIMITED DISTRICT SWITCHINGTo allow staff to Make Repairs to Phasing at Sub 10776 Richardson Rd Springhill. | 2 | 180 | 360 | 0.00040216 | 2.2342e-06
2013-04-16 10:30AM | 228315 | 8633 | Rural Short | Stand new poles and transfer exisiting network | 6 | 60 | 180 | 0.00020108 | 6.7027e-06
2013-04-16 11:30AM | 228315 | 8633 | Rural Short | Stand new poles and transfer exisiting network | 6 | 1200 | 3600 | 0.0040216 | 6.7027e-06
2013-04-17 08:00AM | 227082 | T828 | Rural Short | REPLACE TX and RETROFIT SUB | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2013-04-17 08:00AM | 228703 | KC1284 | Rural Short | Replace Condemned Pole | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-04-17 08:00AM | 223689 | CD1267 | Urban | New sub 32246 and ABSs 96265 and 97138 | 132 | 480 | 63360 | 0.070781 | 0.00014746
2013-04-17 08:00AM | 228708 | 55890 | Urban | Replace Pole | 13 | 480 | 6240 | 0.0069708 | 1.4523e-05
2013-04-17 08:00AM | 228843 | WH1235 | Urban | Augment OH HV conductor | 218 | 480 | 104640 | 0.1169 | 0.00024353
2013-04-17 08:15AM | 227138 | 35816 | Rural Short | Limited district SwitchingChange Condemned Pole #70Change Condemned Pole #62(Sub 10236)Change HV hardware Pole #69 Change HV and LV Xarm Pole #65 | 88 | 450 | 39600 | 0.044238 | 9.8307e-05
2013-04-17 08:30AM | 226690 | MVH2 | Rural Short | Stand Poles 816606 (143) 3KO141 (144) 3KO140 (145) 3KO139 (146) 3KO138 (147) and augment 33 kV/11 kV conductor between 3KO141 (144) and 3KO138 (147). | 44 | 480 | 21120 | 0.023594 | 4.9153e-05
2013-04-17 08:30AM | 228146 | MVB2 | Rural Short | Replace PoleInstall New Pole Augment a Section of O/H 11KV Mains and Retrofit DOFs at Sub 31519 | 135 | 450 | 60750 | 0.067865 | 0.00015081
2013-04-17 08:30AM | 227975 | BLC2 | Urban | REPLACE HV SWITCHGEAR | 31 | 420 | 13020 | 0.014545 | 3.4631e-05
2013-04-17 08:30AM | 228885 | 35762 | Urban | AUGMENT EXISTING LOW VOLTAGE OVERHEAD MAINS FROM BARE WIRE TO ABC OVERHEAD MAINS | 6 | 390 | 2340 | 0.0026141 | 6.7027e-06
2013-04-17 09:00AM | 227486 | ULE2 | Rural Short | Install New Sectionaliser and New LBSCnr Princes Hwy and Bawley Point Rd TERMEIL. | 32 | 360 | 11520 | 0.012869 | 3.5748e-05
2013-04-17 09:00AM | 223267 | 35696 | Urban | Augment LV mains below O/H HV mains. | 68 | 390 | 26520 | 0.029626 | 7.5964e-05
2013-04-17 09:00AM | 226896 | KMD2 | Urban | REPLACE X PL 4KG243 RETRO FIT SUB 41240 REPLACE HV X ARM PL 4KG242 and PL 4KG257 | 57 | 330 | 18810 | 0.021013 | 6.3676e-05
2013-04-17 09:30AM | 229062 | A346 | Urban | Terminate LV cable in Column | 6 | 300 | 1800 | 0.0020108 | 6.7027e-06
2013-04-18 06:30AM | 227145 | T888 | Urban | Remove section of underground cables (2) that go to Sub 27727 so that new storm water drain can be installed and Restore Cables | 2 | 510 | 1020 | 0.0011395 | 2.2342e-06
2013-04-18 08:00AM | 228332 | X492 | Rural Long | RETROFIT SUBS | 9 | 420 | 4200 | 0.0046919 | 1.0054e-05
2013-04-18 08:00AM | 225249 | 8634 | Rural Short | job1- change 2 poles and install ABS remove USL 4384 and remove lv Job 2 : Remove ABS 14494 | 31 | 510 | 15810 | 0.017662 | 3.4631e-05
2013-04-18 08:00AM | 227805 | R260 | Rural Short | Replace ABS with Type 3 LBS. Replace USL's with sectionaliser. Augment 11kV OH mains | 25 | 480 | 12000 | 0.013405 | 2.7928e-05
2013-04-18 08:00AM | 228122 | CLB2 | Rural Short | Replace poles and augment | 304 | 480 | 145920 | 0.16301 | 0.0003396
2013-04-18 08:00AM | 228228 | 35989 | Rural Short | Install new 315KVA PM 32461 and 500KVA PM 32462 via cable termination to Sw 80931 in PM 28267. | 28 | 480 | 13440 | 0.015014 | 3.1279e-05
2013-04-18 08:00AM | 228926 | P608 | Rural Short | LIMITED DISTRICT SWITCHINGTo allow staff to isolate Tx to allow LV ABC to be installed at Sub 27893 Dietz Lane Oakdale | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2013-04-18 08:00AM | 224317 | 7994 | Urban | Replace Sub 2688.Augment HV OH mains to 7/4.5 AAC. | 66 | 480 | 31680 | 0.03539 | 7.373e-05
2013-04-18 08:00AM | 228177 | 25746 | Urban | RAISE LV CROSS ARM RETENSION LV MAINS AND RETENSION HV MAINS POLE 214666. | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-04-18 08:00AM | 228522 | 25783 | Urban | Perform 1 x LV IDandSpike. | 6 | 300 | 1800 | 0.0020108 | 6.7027e-06
2013-04-18 08:15AM | 228679 | S772 | Urban | Cut into existing ug cable and create new pillar 122685 | 17 | 435 | 7395 | 0.0082611 | 1.8991e-05
2013-04-18 08:30AM | 227572 | 35982 | Rural Short | Limited District SwitchingChange over stay at pole 38 to new pole 880921 and remove old pole Retro fit Sub 12341 and repair HV Defects at poles 15 and 19 | 14 | 360 | 5040 | 0.0056303 | 1.564e-05
2013-04-18 08:30AM | 227391 | NWA2 | Urban | Replace one pole and remove 2 bays of HV OH mains. | 89 | 480 | 136320 | 0.15229 | 9.9424e-05
2013-04-18 08:30AM | 227662 | CLC2 | Urban | Replace poles and Augment HV Conductors Penguin Head Rd CULBURRA. | 302 | 420 | 126840 | 0.1417 | 0.00033737
2013-04-18 08:30AM | 228152 | SHE2 | Urban | INSTALL ABS 82309 LBS 82280 and RETRO S/S 41339 | 37 | 420 | 9660 | 0.010791 | 4.1333e-05
2013-04-18 08:30AM | 228838 | SHK2 | Urban | REPLACE X POLE 201626 | 9 | 330 | 2970 | 0.0033178 | 1.0054e-05
2013-04-18 09:00AM | 227776 | ULE2 | Rural Short | Replace poles and Augment HV O/H conductors. ( 12 to 5 )Woodstock Rd MILTON | 37 | 360 | 13320 | 0.01488 | 4.1333e-05
2013-04-18 09:00AM | 228428 | NA1270 | Rural Short | REPLACE POLES 1XT151 AND 1XT150Remove DOF'S 93122 and install USL95629 | 50 | 360 | 18000 | 0.020108 | 5.5856e-05
2013-04-18 09:00AM | 228763 | 2 | Rural Short | Joint and terminate new 240mm into sub 6046 connect UGOH to lLV links and Terminate new LV pillars | 15 | 360 | 5400 | 0.0060324 | 1.6757e-05
2013-04-18 09:00AM | 228620 | 49319 | Urban | Rusty Column | 15 | 180 | 2700 | 0.0030162 | 1.6757e-05
2013-04-18 09:00AM | 228622 | 8680 | Urban | Rusty Column | 25 | 180 | 4500 | 0.005027 | 2.7928e-05
2013-04-18 09:00AM | 228626 | 8694 | Urban | Rusty Column | 10 | 180 | 1800 | 0.0020108 | 1.1171e-05
2013-04-18 09:00AM | 228763 | 2 | Urban | Joint and terminate new 240mm into sub 6046 connect UGOH to lLV links and Terminate new LV pillars | 15 | 360 | 5400 | 0.0060324 | 1.6757e-05
2013-04-18 09:00AM | 228936 | B762 | Urban | Lv X arm change | 14 | 360 | 5040 | 0.0056303 | 1.564e-05
2013-04-18 09:00AM | 228938 | B762 | Urban | Lv Arm Change | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2013-04-18 10:00AM | 226842 | 35989 | Rural Short | Replace Faulty Valtage Indicators on ABB Safelink Switchgear To Rectify Defect D974 | 2 | 300 | 600 | 0.00067027 | 2.2342e-06
2013-04-19 06:30AM | 228322 | L509 | Urban | establish new sub 31445 remove sub 16261. | 2 | 570 | 1140 | 0.0012735 | 2.2342e-06
2013-04-19 08:00AM | 223069 | X877 | Rural Short | Allow staff to erect DOF97889 on pole 38. retro fit pole subs 7438 and 7536 repair defects within outage. | 61 | 480 | 29280 | 0.032709 | 6.8144e-05
2013-04-19 08:00AM | 224334 | 27446 | Rural Short | Replace 2 poles and install new ABS 85009. | 106 | 510 | 54060 | 0.060392 | 0.00011841
2013-04-19 08:00AM | 224354 | 27446 | Rural Short | Replace 2 poles and install new ABS 85009. | 28 | 510 | 14280 | 0.015952 | 3.1279e-05
2013-04-19 08:00AM | 227598 | L582 | Rural Short | RETROFIT SUB 16569 AND REPLACE LV X-ARMS AT POLE 456516 | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2013-04-19 08:00AM | 227567 | W120 | Urban | Replace Crossarms | 40 | 420 | 16800 | 0.018768 | 4.4685e-05
2013-04-19 08:00AM | 227618 | 4354 | Urban | Replace condmened column 1091 | 29 | 240 | 6960 | 0.0077752 | 3.2396e-05
2013-04-19 08:00AM | 228473 | C890 | Urban | REPLACE RAGBOLT AT COLUMN # 7463 - GREENBANK DR WERRINGTON | 21 | 480 | 10080 | 0.011261 | 2.346e-05
2013-04-19 08:30AM | 226557 | L940 | Rural Short | Remove pole 405 and Install new ABS 84982 + pole | 14 | 420 | 5880 | 0.0065687 | 1.564e-05
2013-04-19 08:30AM | 226870 | DP1210 | Rural Short | Change substation LV cubicle and LV sw/gear | 3 | 330 | 990 | 0.0011059 | 3.3514e-06
2013-04-19 08:30AM | 227517 | D810 | Rural Short | Connect stay @ sub 3438 | 1 | 240 | 240 | 0.00026811 | 1.1171e-06
2013-04-19 08:30AM | 227920 | RWA2 | Rural Short | Replace Condemned Pole 3VK158 | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2013-04-19 08:30AM | 228612 | SN1271 | Urban | INSTALL NEW LV PILLAR | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-04-19 09:00AM | 228670 | HKB2 | Urban | Replace pole X pole Carmel Dr Sanctuary Point | 20 | 360 | 7200 | 0.0080433 | 2.2342e-05
2013-04-19 09:00AM | 228706 | 8680 | Urban | Repair Broken Cover | 54 | 120 | 6480 | 0.0072389 | 6.0324e-05
2013-04-19 09:00AM | 228707 | 8682 | Urban | Repair Broken Cover | 15 | 120 | 1800 | 0.0020108 | 1.6757e-05
2013-04-19 09:00AM | 228813 | 8648 | Urban | Replace Marble Bags and 1 Columns | 8 | 120 | 960 | 0.0010724 | 8.937e-06
2013-04-19 09:00AM | 228933 | 35305 | Urban | LV Arm change | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2013-04-19 09:00AM | 228935 | 35305 | Urban | Change service cross arms | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-04-19 09:00AM | 229028 | KMC2 | Urban | REPLACE X POLE 4KG120 | 18 | 240 | 4320 | 0.004826 | 2.0108e-05
2013-04-19 09:00AM | 229340 | AZ1272 | Urban | STAND POLE | 8 | 180 | 1440 | 0.0016087 | 8.937e-06
2013-04-19 12:00PM | 228705 | 8680 | Urban | Repair Broken Cover | 3 | 120 | 360 | 0.00040216 | 3.3514e-06
2013-04-19 12:00PM | 228812 | 27194 | Urban | Repair Broken Cover | 17 | 120 | 2040 | 0.0022789 | 1.8991e-05
2013-04-20 07:30AM | 228315 | 8633 | Rural Short | Stand new poles and transfer exisiting network | 6 | 60 | 180 | 0.00020108 | 6.7027e-06
2013-04-20 08:00AM | 228897 | UNE2 | Urban | Install poles .De-energise 11kV mains for clearance and leave mains isolated | 10 | 30 | 300 | 0.00033514 | 1.1171e-05
2013-04-21 04:00PM | 226904 | W184 | Urban | To Replace existing Plinth With New CulvertReplace Holec SW/GR With CCCC Safe Link SW/GRand Reterminate Existing Cables. | 12 | 90 | 450 | 0.0005027 | 1.3405e-05
2013-04-21 06:30AM | 226904 | W184 | Urban | To Replace existing Plinth With New CulvertReplace Holec SW/GR With CCCC Safe Link SW/GRand Reterminate Existing Cables. | 12 | 30 | 150 | 0.00016757 | 1.3405e-05
2013-04-21 06:30AM | 226904 | W184 | Urban | To Replace existing Plinth With New CulvertReplace Holec SW/GR With CCCC Safe Link SW/GRand Reterminate Existing Cables. | 3 | 600 | 3000 | 0.0033514 | 3.3514e-06
2013-04-21 07:00AM | 227870 | 1102 | Urban | REMOVE HV OH MAINS ABS 13489 and UGOH. INSTALL NEW HV UG CABLES AND HV SW GEAR SUB 9686 CLYDE ST SOUTH GRANVILLE | 1 | 540 | 540 | 0.00060324 | 1.1171e-06
2013-04-21 08:00AM | 227150 | 35443 | Urban | MandR HV HAZ SWITCHGEAR SUB 15312 | 32 | 360 | 11520 | 0.012869 | 3.5748e-05
2013-04-21 08:00AM | 228262 | 2828 | Urban | Install poles for future augment | 76 | 360 | 27360 | 0.030564 | 8.4901e-05
2013-04-21 08:30AM | 226519 | NWD2 | Urban | Replace poles | 104 | 360 | 18720 | 0.020912 | 0.00011618
2013-04-21 08:30PM | 226661 | 17035 | Urban | REPLACE POLE # 661 andREMOVE WISHBONE @ POLE # 660 | 20 | 480 | 9600 | 0.010724 | 2.2342e-05
2013-04-22 08:00AM | 220918 | 8799 | Rural Short | Augment 8 bays of LV mains below HV mains. | 26 | 510 | 13260 | 0.014813 | 2.9045e-05
2013-04-22 08:30AM | 226679 | MG1267 | Rural Short | Upgrade HV Network | 20 | 480 | 9600 | 0.010724 | 2.2342e-05
2013-04-22 08:30AM | 228158 | RWB2 | Rural Short | Replace Condemned Pole 3J0435 | 58 | 450 | 26100 | 0.029157 | 6.4793e-05
2013-04-22 08:30AM | 228404 | D814 | Rural Short | Re tension river crossing 44 @ pole 830491 | 4 | 180 | 720 | 0.00080433 | 4.4685e-06
2013-04-22 08:30AM | 228553 | MVH2 | Rural Short | Stand Poles and Augment mains | 44 | 480 | 21120 | 0.023594 | 4.9153e-05
2013-04-22 09:00AM | 229148 | KC1284 | Rural Short | LV Changeover | 7 | 360 | 2520 | 0.0028151 | 7.8198e-06
2013-04-22 10:00AM | 229328 | 8767 | Urban | Condemned Telstra Pole | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2013-04-23 02:00AM | 225662 | L535 | Urban | Perform CB Exercises and Operational Checks @ sub 23052 Alpha Street Blacktown | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2013-04-23 07:30AM | 225586 | AZ1272 | Urban | REPLACE COND POLE 227 | 28 | 540 | 8100 | 0.0090487 | 3.1279e-05
2013-04-23 07:30AM | 228355 | 35503 | Urban | Replace existing TX in Sub 18048 with new 500KVA FR3 TX | 28 | 360 | 10080 | 0.011261 | 3.1279e-05
2013-04-23 08:00AM | 223690 | 61617 | Rural Short | LV OH mains augment new poles. | 48 | 480 | 23040 | 0.025738 | 5.3622e-05
2013-04-23 08:00AM | 227952 | 35988 | Rural Short | Replace poles 40 and 41 and augment high voltage mains from pole 40 through to pole 44. | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2013-04-23 08:00AM | 228171 | L582 | Rural Short | REPLACE CONDEMNED POLES and RETROFIT SUB | 23 | 420 | 9660 | 0.010791 | 2.5694e-05
2013-04-23 08:00AM | 228656 | SZ1332 | Rural Short | 11kV switching to allow the scope of works to be completed as per DNR 228654 and to change over LV conductors from existing timber pole 9 feeder 458/1 to new concrete pole. | 16 | 420 | 6720 | 0.007507 | 1.7874e-05
2013-04-23 08:00AM | 228760 | 8798 | Rural Short | Augment LV mains below HV mains. | 208 | 510 | 106080 | 0.1185 | 0.00023236
2013-04-23 08:00AM | 229221 | KC1284 | Rural Short | LIMITED DISTRICT SWITCHINGTo allow staff to Replace TX and Retrofit Sub 2721 Bringelly Rd Rossmore | 24 | 480 | 11520 | 0.012869 | 2.6811e-05
2013-04-23 08:00AM | 228524 | CJ1249 | Urban | Perform 1 x LV IDandSpike | 8 | 300 | 2400 | 0.0026811 | 8.937e-06
2013-04-23 08:30AM | 229117 | MVH2 | Rural Short | Holec HV Switchgear MandR at Padmount Substation 30130 | 1 | 180 | 180 | 0.00020108 | 1.1171e-06
2013-04-23 09:00AM | 225251 | ULJ2 | Rural Short | Install / replace polesPirralea Rd ULLADULLA. | 101 | 330 | 33330 | 0.037234 | 0.00011283
2013-04-23 09:00AM | 228007 | 2806 | Urban | LV Crossarm chnageover | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2013-04-23 09:00AM | 228810 | 1949 | Urban | Consac Replacement | 38 | 360 | 13680 | 0.015282 | 4.2451e-05
2013-04-23 09:00AM | 228962 | WH1272 | Urban | Augment LV to 150 ABC poles 813770 to 813772 | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2013-04-23 09:00AM | 229006 | S674 | Urban | LV Pole change | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2013-04-23 09:00AM | 229150 | WL1292 | Urban | 3 phase upgrade | 6 | 360 | 2160 | 0.002413 | 6.7027e-06
2013-04-23 09:00AM | 229216 | M397 | Urban | LIMITED DISTRICT SWITCHINGTo allow staff to Make Repairs to Phasing at Sub 10776 Richardson Rd Springhill. | 2 | 180 | 360 | 0.00040216 | 2.2342e-06
2013-04-23 10:30AM | 229113 | 25450 | Urban | OUTAGE FOR WCC TO INSTALL CULVERT DRAIN UNDER EE O/H MAINS | 24 | 30 | 360 | 0.00040216 | 2.6811e-05
2013-04-23 11:00AM | 229113 | 25450 | Urban | OUTAGE FOR WCC TO INSTALL CULVERT DRAIN UNDER EE O/H MAINS | 24 | 300 | 3600 | 0.0040216 | 2.6811e-05
2013-04-24 04:00PM | 229113 | 25450 | Urban | OUTAGE FOR WCC TO INSTALL CULVERT DRAIN UNDER EE O/H MAINS | 24 | 30 | 360 | 0.00040216 | 2.6811e-05
2013-04-24 08:00AM | 223790 | HKA2 | Rural Short | Install 11 poles. Erect 12 and augment 6 bays of HV mains. | 100 | 480 | 48000 | 0.053622 | 0.00011171
2013-04-24 08:00AM | 227473 | BK1299 | Rural Short | Straighten pole 26. Re Dress poles 24 25 and 27 MOUNT LBS ON POLE 23 and RETRO FIT SUB 17345 | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2013-04-24 08:00AM | 227670 | H745 | Rural Short | Replace condemned pole #31 new pole #882315Install New Pole # 882909 | 26 | 420 | 10920 | 0.012199 | 2.9045e-05
2013-04-24 08:00AM | 228695 | RWB2 | Rural Short | To InstallTerminate andTest New H/V Cable Between CB-RW1292 and New Pole @ Ringwood Z/S.Replace ABS 50280 with New ABS 96980 Remove USL 50437 Remove a section of O/H 11KV Mains and Install New LBS 96979 | 10 | 540 | 5400 | 0.0060324 | 1.1171e-05
2013-04-24 08:00AM | 229453 | 87220 | Rural Short | LIMITED DISTRICT SWITCHING RETROFIT SUBS AND INSTALL MDI | 10 | 420 | 4200 | 0.0046919 | 1.1171e-05
2013-04-24 08:00AM | 224324 | 7994 | Urban | Augment HV OH mains to 7/4.5 AAC. | 68 | 480 | 32640 | 0.036463 | 7.5964e-05
2013-04-24 08:00AM | 227655 | CD1267 | Urban | Replace DOF's J642Repair HV Xarms at Pole 51 and 52 | 4 | 390 | 1560 | 0.0017427 | 4.4685e-06
2013-04-24 08:00AM | 228249 | 5506 | Urban | REPLACE EXISTING ABS # 4334 WITH NEW LBS # 123844 - WILSON ST ST MARYS | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2013-04-24 08:00AM | 229044 | L537 | Urban | Replace Pole | 27 | 480 | 12960 | 0.014478 | 3.0162e-05
2013-04-24 08:00AM | 229195 | D820 | Urban | Allow staff to replace transformer and LV switchgear PM 5148. | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2013-04-24 08:00AM | 229391 | RS1203 | Urban | LV Augment open wire to ABC | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2013-04-24 08:30AM | 228089 | JBA2 | Rural Short | REPLACE X POLES 4HJ012 4HH015 | 7 | 360 | 2520 | 0.0028151 | 7.8198e-06
2013-04-24 08:30AM | 226711 | PKD2 | Urban | Replace poles 3TD563 and 3TD564 | 51 | 420 | 21420 | 0.023929 | 5.6973e-05
2013-04-24 08:30AM | 227921 | RVF2 | Urban | MandR HOLEC SWITCHGEAR | 61 | 300 | 18300 | 0.020443 | 6.8144e-05
2013-04-24 09:00AM | 228606 | NA1270 | Rural Short | AUGMENT H/V CONDUCTORS | 50 | 360 | 18000 | 0.020108 | 5.5856e-05
2013-04-24 09:00AM | 229354 | 48196 | Rural Short | Service Changeover | 48 | 300 | 14400 | 0.016087 | 5.3622e-05
2013-04-24 09:00AM | 228579 | CLC2 | Urban | Augment LV to ABC ( poles 3 to 7 )Fairlight Way Culburra | 51 | 360 | 18360 | 0.02051 | 5.6973e-05
2013-04-24 09:00AM | 228805 | 1949 | Urban | Consac Replacement | 9 | 60 | 540 | 0.00060324 | 1.0054e-05
2013-04-24 09:00AM | 228806 | 1949 | Urban | Consac Replacement | 43 | 360 | 15480 | 0.017293 | 4.8036e-05
2013-04-24 09:00AM | 228939 | 3360 | Urban | LV Arm change | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2013-04-24 12:30PM | 228768 | SZ1322 | Urban | Repair broken tie @ pole 360 | 50 | 120 | 6000 | 0.0067027 | 5.5856e-05
2013-04-26 08:00AM | 227804 | KME2 | Rural Short | UPGRADE EXISTING PAD SUB | 44 | 360 | 15840 | 0.017695 | 4.9153e-05
2013-04-26 08:00AM | 228915 | L942 | Rural Short | UPRATE EX SUB 5424 TO 100KVA CHANGE 2 POLES AUGMENT LV MAINS IN LOCK RD TO 150 ABC REMOVE STAY POLE | 16 | 540 | 8640 | 0.0096519 | 1.7874e-05
2013-04-26 08:00AM | 222997 | HR1273 | Urban | Isolate section of LV to stand new pole. | 16 | 420 | 6720 | 0.007507 | 1.7874e-05
2013-04-26 08:00AM | 228442 | WWF2 | Urban | REPLACE UGOH POLE INSTALL NEW HV CABLES COMMISSION NEW PAD SUB | 59 | 510 | 30090 | 0.033614 | 6.591e-05
2013-04-26 08:00AM | 229374 | 35315 | Urban | AUGMENT 4 BAYS L/V MAINS | 19 | 300 | 5700 | 0.0063676 | 2.1225e-05
2013-04-26 08:30AM | 226507 | 8798 | Rural Short | MandR sub 22904 | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2013-04-26 08:30AM | 226509 | 8798 | Rural Short | MandR sub 22903 | 9 | 210 | 1890 | 0.0021114 | 1.0054e-05
2013-04-26 09:00AM | 227802 | ULE2 | Rural Short | Replace poles and Augment HV O/H conductors. ( 4 to 1 )Woodstock Rd MILTON | 18 | 360 | 6480 | 0.0072389 | 2.0108e-05
2013-04-26 09:00AM | 229322 | 2 | Rural Short | Joint and terminate new 240mm into sub 6046 connect UGOH to lLV links and Terminate new LV pillars | 15 | 360 | 5400 | 0.0060324 | 1.6757e-05
2013-04-26 09:00AM | 228866 | CLC2 | Urban | Replace poles ( 7 and 8 ) and Run LV ABC Conductor ( 6 to 9 )Penguin Head Rd CULBURRA. | 229 | 390 | 89310 | 0.09977 | 0.00025582
2013-04-26 09:00AM | 229322 | 2 | Urban | Joint and terminate new 240mm into sub 6046 connect UGOH to lLV links and Terminate new LV pillars | 15 | 360 | 5400 | 0.0060324 | 1.6757e-05
2013-04-27 06:30AM | 226364 | B748 | Urban | HVSWGR MAINT | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2013-04-27 08:00AM | 227918 | 2820 | Urban | Replace Sub 3416.Install pole for future change over. | 43 | 480 | 20640 | 0.023057 | 4.8036e-05
2013-04-27 08:15AM | 227954 | 10242 | Urban | LV ISOLATION FOR RAILCORP ESSENTIAL WORKS TREE REMOVAL | 46 | 480 | 22080 | 0.024666 | 5.1388e-05
2013-04-28 06:00AM | 229042 | F603 | Urban | Augment HV network | 209 | 720 | 150480 | 0.1681 | 0.00023348
2013-04-28 07:00AM | 225370 | 2829 | Urban | REPLACE USL 29547 POLE 724 | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-04-28 08:00AM | 229144 | S737 | Rural Short | Feeder 420 - String 33kV Conductor and clippin between Pole No.854332 to pole No.854357(J122). | 40 | 90 | 1800 | 0.0020108 | 4.4685e-05
2013-04-28 08:00AM | 226695 | PKB2 | Urban | Change Poles and Augment H/V Mains | 1 | 450 | 450 | 0.0005027 | 1.1171e-06
2013-04-28 08:00AM | 228363 | CRE2 | Urban | MandR HOLEC SWITCHGEAR REPLACE LA'S ON POTHEAD. | 25 | 270 | 6750 | 0.0075406 | 2.7928e-05
2013-04-28 09:30AM | 229144 | S737 | Rural Short | Feeder 420 - String 33kV Conductor and clippin between Pole No.854332 to pole No.854357(J122). | 40 | 150 | 3000 | 0.0033514 | 4.4685e-05
2013-04-28 12:00PM | 228383 | CRE2 | Urban | MandR HOLEC SWITCHGEAR | 27 | 210 | 5670 | 0.0063341 | 3.0162e-05
2013-04-29 07:00AM | 229129 | 25403 | Rural Short | 11kV switching to allow scope of works to be completed as per DNR 229122. | 6 | 600 | 13800 | 0.015416 | 6.7027e-06
2013-04-29 07:00AM | 225734 | R215 | Urban | LV OH mains augment | 11 | 600 | 6600 | 0.007373 | 1.2288e-05
2013-04-29 08:00AM | 229129 | 25403 | Rural Short | 11kV switching to allow scope of works to be completed as per DNR 229122. | 40 | 480 | 11040 | 0.012333 | 4.4685e-05
2013-04-29 08:00AM | 227710 | CD1204 | Urban | Install new poles and switch. Augment HV mains. Remove pole. Install USL. | 8 | 420 | 3360 | 0.0037535 | 8.937e-06
2013-04-29 08:00AM | 228179 | 2828 | Urban | Install OH aerial stay between poles 330346 and 330345 | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-04-29 08:00AM | 228445 | 1109 | Urban | Augment LV mains | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-04-29 08:30AM | 224167 | MG1267 | Rural Short | HV Upgrade | 146 | 480 | 70080 | 0.078288 | 0.0001631
2013-04-29 08:30AM | 224282 | MG1267 | Rural Short | HV Upgrade | 111 | 480 | 53280 | 0.05952 | 0.000124
2013-04-29 09:00AM | 227932 | S788 | Rural Short | Isolate LV mains for HV augmentation and replacement of hardware. | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2013-04-29 09:00AM | 228745 | RWB2 | Rural Short | Replace Condemned Sub Pole 3J0816 | 10 | 390 | 3900 | 0.0043568 | 1.1171e-05
2013-04-30 08:00AM | 224449 | 27446 | Rural Short | Augment 2 bays of O/H HV mains to 7/4.5 AAC replace pole 502 and replace ABS 8112 with ABS 85008. | 21 | 510 | 10710 | 0.011964 | 2.346e-05
2013-04-30 08:00AM | 228326 | CLB2 | Rural Short | Replace poles | 289 | 480 | 138720 | 0.15497 | 0.00032285
2013-04-30 08:00AM | 229120 | 35818 | Rural Short | Limited District Switching Retro Sub 10708Repalce DOF's @ Sub 10708 | 62 | 465 | 28830 | 0.032207 | 6.9261e-05
2013-04-30 08:00AM | 225873 | S765 | Urban | REPLACE EXISTING ABS # 1184 WITH NEW ABS # A0128 - MULGOA RD REGENTVILLE | 5 | 480 | 2400 | 0.0026811 | 5.5856e-06
2013-04-30 08:00AM | 228357 | FT1208 | Urban | LV SWITCHGEAR UPGRADE | 4 | 450 | 1800 | 0.0020108 | 4.4685e-06
2013-04-30 08:00AM | 228452 | 1109 | Urban | Install indoor sub 29487 via three new UGOH's. Remove pole 1596 and three bays HV mains. | 44 | 540 | 23760 | 0.026543 | 4.9153e-05
2013-04-30 08:00AM | 228604 | 1109 | Urban | Augment LV mains between pole 1386 and 883324 | 41 | 390 | 15990 | 0.017863 | 4.5802e-05
2013-04-30 08:00AM | 229595 | AZ1264 | Urban | Stand Pole | 23 | 480 | 11040 | 0.012333 | 2.5694e-05
2013-04-30 08:30AM | 224342 | MG1267 | Rural Short | HV Upgrade | 35 | 480 | 16800 | 0.018768 | 3.9099e-05
2013-04-30 08:30AM | 228160 | L940 | Rural Short | Install new capacitorMeet operators to discuss switching procedure | 10 | 450 | 4500 | 0.005027 | 1.1171e-05
2013-04-30 08:30AM | 228575 | APC2 | Rural Short | REPLACE ABS 74102 | 62 | 330 | 20460 | 0.022856 | 6.9261e-05
2013-04-30 08:30AM | 228739 | 8635 | Rural Short | Replace pole 273 | 26 | 390 | 10140 | 0.011328 | 2.9045e-05
2013-04-30 08:30AM | 228242 | PKD2 | Urban | MandR HOLEC SWITCHGEAR | 164 | 300 | 49200 | 0.054962 | 0.00018321
2013-04-30 08:30AM | 229298 | SHD2 | Urban | REPLACE X POLE 1G0068 | 17 | 300 | 5100 | 0.0056973 | 1.8991e-05
2013-04-30 09:00AM | 228338 | X492 | Rural Long | INSTALL KAON FUSE SAVER | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-04-30 09:00AM | 227674 | 48203 | Urban | DISTRUIBUTION EARTH REFURBISHMENT. (HINCHINBROOK ZONE SUB ). | 1 | 120 | 120 | 0.00013405 | 1.1171e-06
2013-04-30 09:00AM | 229752 | CJ1230 | Urban | Replace Crossarm | 13 | 240 | 3120 | 0.0034854 | 1.4523e-05
2013-05-01 08:00AM | 222791 | HKA2 | Rural Short | New pole sub 29851 | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2013-05-01 08:00AM | 229104 | R260 | Rural Short | Augment HV mains from pole 28 [ 826235] to pole 38 ( 826241 ). | 27 | 450 | 12150 | 0.013573 | 3.0162e-05
2013-05-01 08:00AM | 225276 | L537 | Urban | Replace poles + Augment HV Conductor | 112 | 480 | 53760 | 0.060056 | 0.00012512
2013-05-01 08:00AM | 227078 | 8770 | Urban | Allow staff to remove USL 833 an erect ABS 123886 on replacement pole. | 182 | 480 | 87360 | 0.097592 | 0.00020332
2013-05-01 08:00AM | 228580 | C890 | Urban | REPLACE RAGBOLTS FOR COLUMNS # 11794 and 11005 - PLOUGHMAN CRES WERRINGTON DOWNS | 38 | 480 | 18240 | 0.020376 | 4.2451e-05
2013-05-01 08:00AM | 228581 | S768 | Urban | Replace pillar and LV switch @ pillar # 57634 | 23 | 360 | 8280 | 0.0092498 | 2.5694e-05
2013-05-01 08:00AM | 228584 | 68179 | Urban | REPLACE CONDEMNED POLE 761 AND RETRO-FIT SUB 2210 | 48 | 480 | 23040 | 0.025738 | 5.3622e-05
2013-05-01 08:00AM | 229114 | 8737 | Urban | Augment O/H conductor + Replace pole + install DOFs | 73 | 480 | 35040 | 0.039144 | 8.155e-05
2013-05-01 08:00AM | 229118 | 8737 | Urban | Augment O/H conductor + Replace pole + install DOFs | 70 | 480 | 33600 | 0.037535 | 7.8198e-05
2013-05-01 08:00AM | 229123 | 25783 | Urban | Install:1 x new pole.Isolate polesub 2828 for LV OH mains uprate. | 15 | 480 | 7200 | 0.0080433 | 1.6757e-05
2013-05-01 08:30AM | 228489 | NG1210 | Rural Short | ABS Maintenance on switch K516 Retrofit SUB 11970 and SUB 11971 | 108 | 360 | 38880 | 0.043434 | 0.00012065
2013-05-01 08:30AM | 228835 | RWD2 | Rural Short | Augment 33 kV conductor between Pole 192 (816659) and 199 (3KO127) | 11 | 480 | 5280 | 0.0058984 | 1.2288e-05
2013-05-01 08:30AM | 229119 | RWE2 | Rural Short | Replace Condemned Sub Poles 3VA012 and 3VA021 | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2013-05-01 08:30AM | 228291 | FT1207 | Urban | MandR HOLEC SWITCHGEAR | 120 | 360 | 43200 | 0.04826 | 0.00013405
2013-05-01 08:30AM | 228548 | APE2 | Urban | MandR HOLIC SWITCHGEAR | 193 | 240 | 46320 | 0.051745 | 0.0002156
2013-05-01 09:00AM | 228349 | X492 | Rural Long | INSTALL KAON FUSE SAVER AND MAINTAIN ABS | 10 | 360 | 3600 | 0.0040216 | 1.1171e-05
2013-05-01 09:00AM | 226247 | ULE2 | Rural Short | Replace ABS 58761 with New LBS 123644Shearwater Cres BAWLEY POINT. | 201 | 330 | 66330 | 0.074099 | 0.00022454
2013-05-01 09:00AM | 229519 | 1949 | Urban | Consac Replacement | 24 | 60 | 1440 | 0.0016087 | 2.6811e-05
2013-05-02 06:30AM | 225125 | C833 | Urban | Perform 1 x HV IDandSpikeInstall:2 x HV TTJ HV UG cable new PS 30000 | 5 | 630 | 3150 | 0.0035189 | 5.5856e-06
2013-05-02 08:00AM | 228332 | X492 | Rural Long | RETROFIT SUBS | 1 | 420 | 4200 | 0.0046919 | 1.1171e-06
2013-05-02 08:00AM | 227578 | MG1267 | Rural Short | new sub 32582 | 36 | 480 | 17280 | 0.019304 | 4.0216e-05
2013-05-02 08:00AM | 228947 | RBA2 | Rural Short | Install a set of Dof's (40amp) on pole 220098 and Augment mains to 3x80 mm cctFrom pole 220098 to 829585 | 16 | 480 | 7680 | 0.0085795 | 1.7874e-05
2013-05-02 08:00AM | 229396 | 25403 | Rural Short | 11kV switching to allow the scope of works to be completed as per DNR229394. | 27 | 480 | 12960 | 0.014478 | 3.0162e-05
2013-05-02 08:00AM | 229552 | 57448 | Rural Short | LIMITED DISTRICT SWITCHING REPLACE POLES | 2 | 450 | 900 | 0.0010054 | 2.2342e-06
2013-05-02 08:00AM | 227276 | R254 | Urban | install new LBS remove abs and run 1 bay of hv abc and lv abc | 64 | 510 | 32640 | 0.036463 | 7.1496e-05
2013-05-02 08:00AM | 227630 | 4354 | Urban | Replace condmened column 7097 | 13 | 240 | 3120 | 0.0034854 | 1.4523e-05
2013-05-02 08:00AM | 228616 | NWF2 | Urban | NEW HV CABLE | 71 | 480 | 34080 | 0.038071 | 7.9316e-05
2013-05-02 08:00AM | 228878 | CLC2 | Urban | Replace poles and augment | 289 | 480 | 138720 | 0.15497 | 0.00032285
2013-05-02 08:00AM | 229133 | 1129 | Urban | replace cond pole 575 | 21 | 480 | 10080 | 0.011261 | 2.346e-05
2013-05-02 08:30AM | 228863 | MVH2 | Rural Short | Install Poles 143 142 (3KO142) 141 (3KO144) 140 139 (3KO143). Augment conductor between Poles 142 and 144 | 34 | 480 | 16320 | 0.018231 | 3.7982e-05
2013-05-02 08:30AM | 228889 | WBD2 | Rural Short | Trim overhanging trees | 24 | 420 | 10080 | 0.011261 | 2.6811e-05
2013-05-02 08:30AM | 229698 | 9059 | Urban | LV Augment | 13 | 450 | 5850 | 0.0065352 | 1.4523e-05
2013-05-02 08:30AM | 229813 | APE2 | Urban | REPAIR UG CABLES @ PILLARS 73677 and 73672 | 28 | 450 | 12600 | 0.014076 | 3.1279e-05
2013-05-02 09:00AM | 224135 | D810 | Rural Short | Replace condemned pole # 23 | 5 | 240 | 1200 | 0.0013405 | 5.5856e-06
2013-05-02 09:00AM | 229925 | ULE2 | Rural Short | Replace poles between (1DY 044 and 1DY 024) Woodstock Rd MILTON | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2013-05-02 09:00AM | 226594 | D819 | Urban | REPLACE TRANSFORMER LV SW/GR and CUBICLE @ SUB 5314. | 23 | 480 | 11040 | 0.012333 | 2.5694e-05
2013-05-02 09:00AM | 227692 | CLC2 | Urban | Replace pole and Augment HV Conductors ( 14 to 18 )Penguin Head Rd CULBURRA. | 186 | 390 | 72540 | 0.081036 | 0.00020778
2013-05-02 09:00AM | 228551 | 35524 | Urban | Raise LV service pillar and retro-fit connections | 3 | 330 | 990 | 0.0011059 | 3.3514e-06
2013-05-02 09:00AM | 229228 | 2807 | Urban | LV Arm change | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-05-02 09:00AM | 229523 | 1949 | Urban | Consac Replacement | 40 | 360 | 14400 | 0.016087 | 4.4685e-05
2013-05-02 10:00AM | 229484 | 8633 | Rural Short | Connection of bonds for temporary 11kV spans and installation of poles 854330 854331 854332 and USL A0113 | 1 | 300 | 300 | 0.00033514 | 1.1171e-06
2013-05-02 10:00AM | 227624 | 4354 | Urban | Replace condmened column 7064 | 22 | 300 | 6600 | 0.007373 | 2.4577e-05
2013-05-02 11:00AM | 228569 | 5503 | Urban | Raise UG service connections @ pillar # 15630 | 5 | 210 | 1050 | 0.001173 | 5.5856e-06
2013-05-03 08:00AM | 229098 | X877 | Rural Short | Allow staff to reomove USL 19020 and rect ABS 97759 for future recloser. | 22 | 480 | 10560 | 0.011797 | 2.4577e-05
2013-05-03 08:00AM | 229455 | SZ1332 | Rural Short | 11kV switching to allow the scope of works to be completed as per DNR229452. | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2013-05-03 08:00AM | 229803 | R293 | Rural Short | RETROFIT SUB 14531 | 3 | 450 | 1350 | 0.0015081 | 3.3514e-06
2013-05-03 08:00AM | 227445 | R254 | Urban | Change pole and replace ABS with auto LBS 95507 | 49 | 510 | 24990 | 0.027917 | 5.4739e-05
2013-05-03 08:00AM | 227719 | 8693 | Urban | Augment HV OH mains 150 NMS ABC.Twin arm HV Xarm Sub 6415. | 21 | 510 | 10710 | 0.011964 | 2.346e-05
2013-05-03 08:00AM | 228633 | C900 | Urban | Install 2 Flying Fox's. | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2013-05-03 08:00AM | 229084 | 5503 | Urban | REPLACE ACTIVE LINKS INSIDE PILLAR # 15631 - SOLANDER ST ST CLAIR | 5 | 240 | 1200 | 0.0013405 | 5.5856e-06
2013-05-03 08:30AM | 226197 | 25401 | Rural Short | Install LBS 93176 + pole. Straighten HV arm @ sub 5510 | 10 | 330 | 3300 | 0.0036865 | 1.1171e-05
2013-05-03 08:30AM | 228892 | WBD2 | Rural Short | Trim overhanging trees | 33 | 420 | 13860 | 0.015483 | 3.6865e-05
2013-05-03 08:30AM | 227519 | APB2 | Urban | MandR HOLIC SWITCHGEAR | 208 | 240 | 49920 | 0.055767 | 0.00023236
2013-05-03 08:30AM | 228640 | FT1202 | Urban | REPLACE STREETLIGHT COLUMNS | 31 | 180 | 5580 | 0.0062335 | 3.4631e-05
2013-05-03 09:00AM | 229230 | 5496 | Urban | LV pole change | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-05-03 10:00AM | 229937 | 46752 | Urban | Replace 1 pole and install new DOF's. | 194 | 480 | 93120 | 0.10403 | 0.00021672
2013-05-04 08:00AM | 229503 | 9046 | Urban | ISOLATE 11KV O/H MAINS FOR CIVIL CONTRACTOR | 41 | 480 | 19680 | 0.021985 | 4.5802e-05
2013-05-04 08:00AM | 229614 | J491 | Urban | To Reterminate Existing H/V- UG/OH Termination and Replace Existing Kiosk Sub 13317 With New Padmount Sub 29967 and Reterminate Existing H/V Cable. | 18 | 540 | 9720 | 0.010858 | 2.0108e-05
2013-05-05 01:30PM | 229731 | S737 | Rural Short | Standing new 33kV concrete poles 854359 to 854371 Transfer exsiting network over to new poles Install temp USL A0172 | 36 | 1410 | 16920 | 0.018902 | 4.0216e-05
2013-05-05 06:00AM | 229771 | 35443 | Urban | Allow staff to remove redundant 11 KV overhead mains USL 22034USL C971 ABS 2485 and USL 1719. | 22 | 540 | 49680 | 0.055499 | 2.4577e-05
2013-05-05 06:30AM | 229771 | 35443 | Urban | Allow staff to remove redundant 11 KV overhead mains USL 22034USL C971 ABS 2485 and USL 1719. | 162 | 510 | 46920 | 0.052415 | 0.00018097
2013-05-05 08:00AM | 229694 | 8633 | Rural Short | Run extra 11kV phase from pole J122 to pole 89 and connect bonds at pole 89 | 10 | 240 | 2400 | 0.0026811 | 1.1171e-05
2013-05-05 08:00AM | 230027 | 57444 | Rural Short | LIMITED DISTRICT SWITCHING STAND NEW POLE | 12 | 300 | 3600 | 0.0040216 | 1.3405e-05
2013-05-05 08:00AM | 228874 | CD1241 | Urban | To allow staff to replace Condemned Pole #96 Little Byrne St Camden | 89 | 480 | 42720 | 0.047723 | 9.9424e-05
2013-05-05 08:30AM | 227181 | WBB2 | Urban | Replace condemned poles | 55 | 390 | 21450 | 0.023962 | 6.1442e-05
2013-05-05 09:00AM | 225877 | NA1281 | Urban | Replace ABS 30737. | 26 | 300 | 7800 | 0.0087135 | 2.9045e-05
2013-05-05 09:00AM | 227146 | NA1266 | Urban | Replace TX @ S/S 23610. | 124 | 300 | 37200 | 0.041557 | 0.00013852
2013-05-05 09:00AM | 229947 | GV1234 | Urban | Pole change HV/LV | 14 | 420 | 5880 | 0.0065687 | 1.564e-05
2013-05-05 12:00PM | 229731 | S737 | Rural Short | Standing new 33kV concrete poles 854359 to 854371 Transfer exsiting network over to new poles Install temp USL A0172 | 36 | 60 | 720 | 0.00080433 | 4.0216e-05
2013-05-06 06:00AM | 229382 | B719 | Urban | To Disconnect existing HV cable and Connect new cables in Subs 29233 and 29178.comission 2 x new PM Subs | 17 | 570 | 9690 | 0.010825 | 1.8991e-05
2013-05-06 07:30AM | 228764 | 10248 | Urban | REPLACE LV POLE J592 WITH NEW POLE 882040 | 70 | 480 | 33600 | 0.037535 | 7.8198e-05
2013-05-06 08:00AM | 227581 | 35693 | Rural Short | Install new recloser 96363 and remove ABS G538 | 126 | 510 | 64260 | 0.071786 | 0.00014076
2013-05-06 08:00AM | 228487 | MG1219 | Rural Short | Bond in and Commision New LBS 90795on pole A3YC152 | 2 | 300 | 600 | 0.00067027 | 2.2342e-06
2013-05-06 08:00AM | 228749 | RWE2 | Rural Short | Instal Four poles and augment 3 bays of HV OH mains | 4 | 450 | 1800 | 0.0020108 | 4.4685e-06
2013-05-06 08:00AM | 229788 | 76225 | Rural Short | Apply working earths and install vibration dampers. | 26 | 540 | 14040 | 0.015684 | 2.9045e-05
2013-05-06 08:00AM | 227425 | 25775 | Urban | Install:LV UG cable. LV pillars streetlights | 27 | 480 | 12960 | 0.014478 | 3.0162e-05
2013-05-06 08:00AM | 228674 | C897 | Urban | Replace coloumn # 98A | 3 | 240 | 720 | 0.00080433 | 3.3514e-06
2013-05-06 08:00AM | 228689 | C890 | Urban | Replace ragbolt @ coloumn # 7457 | 47 | 480 | 22560 | 0.025202 | 5.2505e-05
2013-05-06 08:00AM | 230079 | SHG2 | Urban | CONNECT LV CABLE | 14 | 360 | 5040 | 0.0056303 | 1.564e-05
2013-05-06 08:30AM | 228662 | NG1247 | Urban | Retrofit and Replace Defective HV X-arm on Sub 10905 Retrofit Sub 18564 and Sub 11983Limited District Switching | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2013-05-06 08:30AM | 229353 | FT1210 | Urban | REPLACE PADMOUNT SUBSTATION | 78 | 480 | 37440 | 0.041825 | 8.7135e-05
2013-05-06 09:00AM | 230375 | X877 | Rural Short | Replace Service Harness | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2013-05-06 09:00AM | 229176 | 35701 | Urban | Replace existing LV mains with new 150LV ABC for one bay | 20 | 300 | 6000 | 0.0067027 | 2.2342e-05
2013-05-06 09:00AM | 229327 | GV1234 | Urban | HV SWGR MandR @ SUB 6294 | 62 | 240 | 14880 | 0.016623 | 6.9261e-05
2013-05-06 09:00AM | 229363 | CLC2 | Urban | Replace LV poles ( 4 and 7 ) | 46 | 360 | 16560 | 0.0185 | 5.1388e-05
2013-05-06 09:00AM | 229963 | B762 | Urban | LV POle change | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2013-05-06 11:00AM | 230044 | W163 | Rural Short | LIMITED DISTRICT SWITCHING INSTALL MDI AND CT'S | 1 | 180 | 180 | 0.00020108 | 1.1171e-06
2013-05-07 08:00AM | 225676 | 9032 | Urban | Install 3 new padmount substations and section of of high volatge cable and also a section of overhead mains and connect to the existing network | 10 | 540 | 5400 | 0.0060324 | 1.1171e-05
2013-05-07 08:00AM | 230451 | C891 | Urban | REPLACE 48HR CONDEMNED COLUMNS 253 and 254 - CORAL PL CAMBRIDGE PARK | 35 | 360 | 12600 | 0.014076 | 3.9099e-05
2013-05-08 07:00AM | 226515 | 8737 | Urban | REPLACE HV SW GR SAFELINK TO SAFELINK SUB 26009 | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-05-08 07:00AM | 230430 | 48187 | Urban | LV Cable Repair | 14 | 120 | 1680 | 0.0018768 | 1.564e-05
2013-05-08 08:00AM | 226664 | 8634 | Rural Short | Augment 4 bays of O/H HV mains to 2 x 80mm CCT. | 20 | 510 | 10200 | 0.011395 | 2.2342e-05
2013-05-08 08:00AM | 226717 | 48196 | Rural Short | Job 1. Live line break bonds pole 363Job 2.Allow staff to remove ABS 2360 and erect LBS 93248. replace 2 poles.Job 3. Live line re make bonds pole 363. | 33 | 480 | 15840 | 0.017695 | 3.6865e-05
2013-05-08 08:00AM | 228883 | T841 | Rural Short | REPLACE HV X-ARMS RETROFIT SUBS AND REPLACE POLE CAP | 15 | 420 | 6300 | 0.0070379 | 1.6757e-05
2013-05-08 08:00AM | 229308 | R260 | Rural Short | AUGMENT LV O/H MAINS | 4 | 450 | 1800 | 0.0020108 | 4.4685e-06
2013-05-08 08:00AM | 229705 | 8637 | Rural Short | 11kV switching to allow the scope of works to be completed as per DNR229686. | 6 | 480 | 2880 | 0.0032173 | 6.7027e-06
2013-05-08 08:00AM | 230169 | R293 | Rural Short | Apply working earths and install vibration dampers. Install kaon fuse savers and retrofit sub. | 19 | 540 | 10260 | 0.011462 | 2.1225e-05
2013-05-08 08:00AM | 225148 | 48205 | Urban | REPLACE TX AND CUBICLE AT SUB 12941 | 77 | 510 | 39270 | 0.043869 | 8.6018e-05
2013-05-08 08:00AM | 227937 | FF1239 | Urban | Replace 3 poles. Replace 1 ABS. | 146 | 480 | 70080 | 0.078288 | 0.0001631
2013-05-08 08:00AM | 227938 | FF1239 | Urban | Isolate LV mains for replacement of 3 poles and 1 ABS. | 32 | 480 | 15360 | 0.017159 | 3.5748e-05
2013-05-08 08:00AM | 228419 | R250 | Urban | REPLACE POLE FOR SUB # 25944 - STATION ST GLENBROOK | 56 | 480 | 26880 | 0.030028 | 6.2559e-05
2013-05-08 08:00AM | 228589 | C890 | Urban | REPLACE COLUMNS # 11794 and 11005 - PLOUGHMAN CRES WERRINGTON DOWNS | 39 | 480 | 18720 | 0.020912 | 4.3568e-05
2013-05-08 08:00AM | 229336 | FF1276 | Urban | Replace pole 1966 with pole 875163. Remove three bays OH HV mains install two bays HV OH mains and replace one bay OH HV. | 25 | 420 | 10500 | 0.01173 | 2.7928e-05
2013-05-08 08:00AM | 229596 | PKF2 | Urban | Replace Poles | 22 | 450 | 9900 | 0.011059 | 2.4577e-05
2013-05-08 08:00AM | 230418 | 35388 | Urban | Install a new pillar | 51 | 360 | 18360 | 0.02051 | 5.6973e-05
2013-05-08 08:30AM | 228793 | JBB2 | Rural Short | 11kV OUTAGE TO INSTALL 3 NEW POLES CONDUCTOR AND OHEW BETWEEN ABS 61691 AND ABS 73309 on 33KV FDR 7009 | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-05-08 08:30AM | 229095 | P608 | Rural Short | Change sub pole 11821 to 28790 install new poles 822252 and augment mains from 822253 to pole 822250. | 2 | 450 | 900 | 0.0010054 | 2.2342e-06
2013-05-08 08:30AM | 229677 | L940 | Rural Short | To uprate existing 63 Kva sub to 100 Kva @ sub 8721 and rewire LV | 4 | 300 | 1200 | 0.0013405 | 4.4685e-06
2013-05-08 08:30AM | 229748 | BLC2 | Urban | REPLACE 2 POWERPOLES INSTALL LV CONDUCTORS REPLACE CROSSARMS | 35 | 420 | 14700 | 0.016422 | 3.9099e-05
2013-05-08 08:45AM | 229299 | BYC2 | Rural Short | Uprate Substation 20422 to a 63kVA 3Ph Trf | 64 | 420 | 26880 | 0.030028 | 7.1496e-05
2013-05-08 09:00AM | 229370 | SN1230 | Rural Short | Replace poles and Replace TX. - 3 Jobsites | 62 | 360 | 22320 | 0.024934 | 6.9261e-05
2013-05-08 09:30AM | 230378 | D830 | Urban | L V Jointing | 5 | 330 | 1650 | 0.0018432 | 5.5856e-06
2013-05-08 10:00AM | 230432 | 8716 | Urban | LV Cable Fault | 11 | 120 | 1320 | 0.0014746 | 1.2288e-05
2013-05-08 12:30PM | 229603 | MVE2 | Rural Short | Replace Ring switch mechanism in Safelink HV switch gear at sub 24445 | 25 | 210 | 5250 | 0.0058649 | 2.7928e-05
2013-05-09 03:00PM | 229331 | DP1206 | Urban | REPLACE POLE 3RX173 and ABS 72640 RETRO SUB'S 42624 and 42623 | 222 | 30 | 8340 | 0.0093168 | 0.000248
2013-05-09 08:00AM | 226348 | 27446 | Rural Short | augment lv mains | 45 | 510 | 22950 | 0.025638 | 5.027e-05
2013-05-09 08:00AM | 226350 | 27446 | Rural Short | augment lv mains 4 bays | 125 | 510 | 63750 | 0.071216 | 0.00013964
2013-05-09 08:00AM | 229356 | RWC2 | Rural Short | To InstallTerminate andTest New H/V Cable Between CB- RW1229 and Pole 3XK315 Ringwood Z/S and to Remove a section of O/H 11KV mains between USL RWC1 and LB 96555 | 11 | 540 | 5940 | 0.0066357 | 1.2288e-05
2013-05-09 08:00AM | 229388 | RWA2 | Rural Short | Augment a section of HV OH Mains to 180 mm CCT | 12 | 480 | 5760 | 0.0064346 | 1.3405e-05
2013-05-09 08:00AM | 229681 | 8799 | Rural Short | Replace HV arm @ pole 25 | 7 | 300 | 2100 | 0.002346 | 7.8198e-06
2013-05-09 08:00AM | 226286 | B210 | Urban | REPLACE POLE 1329 | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2013-05-09 08:00AM | 226857 | 35571 | Urban | Allow staff to remove ABS46373 and erect ABS 88521 ( for future Recloser)repalce pole | 26 | 480 | 12480 | 0.013942 | 2.9045e-05
2013-05-09 08:00AM | 228451 | CRB2 | Urban | REPLACE PADMOUNT SUBSTATION REPLACE POLE CAPS | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2013-05-09 08:00AM | 229106 | CD1204 | Urban | Replace poles. | 13 | 420 | 5460 | 0.0060995 | 1.4523e-05
2013-05-09 08:30AM | 228308 | 61617 | Rural Short | Remove ABS 20924 and install new ABS 98015. | 20 | 450 | 9000 | 0.010054 | 2.2342e-05
2013-05-09 08:30AM | 228600 | BWE2 | Rural Short | 11 kV isolation to allow 33 kV OHEW to be strung - 33 kV Fdr 7902 | 16 | 480 | 7680 | 0.0085795 | 1.7874e-05
2013-05-09 08:30AM | 228795 | JBB2 | Rural Short | 11kV OUTAGE TO INSTALL 3 NEW POLES on 33KV FDR 7009 | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-05-09 08:30AM | 228364 | CRD2 | Urban | Replace Condemned Pole 2Y1147 | 153 | 360 | 55080 | 0.061531 | 0.00017092
2013-05-09 08:30AM | 229331 | DP1206 | Urban | REPLACE POLE 3RX173 and ABS 72640 RETRO SUB'S 42624 and 42623 | 222 | 15 | 4170 | 0.0046584 | 0.000248
2013-05-09 08:30AM | 229331 | DP1206 | Urban | REPLACE POLE 3RX173 and ABS 72640 RETRO SUB'S 42624 and 42623 | 612 | 420 | 116760 | 0.13043 | 0.00068368
2013-05-09 08:30AM | 229648 | R214 | Urban | New LV circuit. | 14 | 240 | 3360 | 0.0037535 | 1.564e-05
2013-05-09 09:00AM | 227707 | CLC2 | Urban | Replace pole 2GA173 ( pole 21 )Penguin Head Rd CULBURRA. | 85 | 390 | 33150 | 0.037033 | 9.4955e-05
2013-05-09 09:00AM | 229964 | 2806 | Urban | LV Pole change | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-05-09 09:30AM | 230148 | BYE2 | Rural Short | Replace poles 2VA0412VA040 and 2VA039 | 6 | 330 | 1980 | 0.0022119 | 6.7027e-06
2013-05-09 11:00AM | 229671 | C897 | Urban | Replace LV X arm and LV service x 3 | 3 | 240 | 720 | 0.00080433 | 3.3514e-06
2013-05-10 01:00PM | 229731 | S737 | Rural Short | Standing new 33kV concrete poles 854359 to 854371 Transfer exsiting network over to new poles Install temp USL A0172 | 36 | 90 | 1080 | 0.0012065 | 4.0216e-05
2013-05-10 07:30AM | 227873 | 10286 | Rural Short | INSTALL NEW 315 KVA SUB 32239 SAFELINK CFC HV S/GEARCHANGE POLE | 4 | 630 | 2520 | 0.0028151 | 4.4685e-06
2013-05-10 08:00AM | 226076 | 35693 | Rural Short | replace usl with dofs and abs switch | 62 | 480 | 29760 | 0.033245 | 6.9261e-05
2013-05-10 08:00AM | 228985 | WBD2 | Rural Short | Trim Tree overhangs | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2013-05-10 08:00AM | 229281 | R260 | Rural Short | Augment HV mains from pole 826235 to pole 826230. | 44 | 450 | 19800 | 0.022119 | 4.9153e-05
2013-05-10 08:00AM | 229918 | SZ1332 | Rural Short | 11kV switching to allow the scope of works to be completed as per DNR229900. | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2013-05-10 08:00AM | 230241 | R290 | Rural Short | Apply working earths and install vibration dampers. | 52 | 540 | 28080 | 0.031369 | 5.809e-05
2013-05-10 08:00AM | 228352 | 2828 | Urban | Replace pole.Aug HV OH mains 19/3.25 AAC. | 77 | 480 | 36960 | 0.041289 | 8.6018e-05
2013-05-10 08:00AM | 228362 | 2828 | Urban | Isolate LV OH mains for pole install DandR 228352 | 34 | 480 | 16320 | 0.018231 | 3.7982e-05
2013-05-10 08:00AM | 229398 | 20717 | Urban | ISOLATE HV and LV O/H MAINS TO ALLOW CONTRACTORS TO PERFORM WORKS ON ADJACENT SEWER VENT | 27 | 480 | 12960 | 0.014478 | 3.0162e-05
2013-05-10 08:30AM | 228791 | JBB2 | Rural Short | 11kV OUTAGE TO INSTALL 3 NEW POLES BETWEEN ABS 61691 AND ABS 73309 on 33KV FDR 7009 | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-05-10 08:30AM | 229402 | DP1284 | Rural Short | AUGMENT HV MAINS REMOVE S/S 40666 INSTALL S/S 32406 INSTALL UGOH'S POLES 804213 and 859060. REMOVE OH HV MAINS | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-05-10 08:30AM | 229468 | P608 | Rural Short | Stand poles 822259 822260 822261 and augment high voltage mains from LBS 86795 to pole 822261. | 32 | 450 | 14400 | 0.016087 | 3.5748e-05
2013-05-10 08:30AM | 230486 | D814 | Rural Short | Replace condmened pole 24 | 2 | 300 | 600 | 0.00067027 | 2.2342e-06
2013-05-10 08:30AM | 228037 | BLD2 | Urban | Replace Condemned pole 207011 | 1 | 390 | 390 | 0.00043568 | 1.1171e-06
2013-05-10 08:30AM | 229165 | CRA2 | Urban | REPLACE SUB POLE 40286 AND RETROFIT SUBSTATION 40008 | 94 | 420 | 39480 | 0.044104 | 0.00010501
2013-05-10 08:30AM | 229403 | 20717 | Urban | Isolate LV for contractors to perform works on adjacent sewer vent | 24 | 420 | 10080 | 0.011261 | 2.6811e-05
2013-05-10 08:30AM | 230808 | WH1294 | Urban | Replace pole | 29 | 390 | 11310 | 0.012635 | 3.2396e-05
2013-05-10 09:00AM | 230483 | X877 | Rural Short | Replace service | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2013-05-10 09:00AM | 229938 | 1109 | Urban | LV Pole Change | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-05-10 09:00AM | 230193 | 68188 | Urban | Condemned Pole | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2013-05-11 10:00AM | 225738 | 49353 | Urban | Perform CB Exercises and Operational Checks on HV SWGR @ sub 22072 Brookhollow Ave Baulkham Hills | 1 | 240 | 240 | 0.00026811 | 1.1171e-06
2013-05-12 01:00PM | 229946 | MG1219 | Rural Short | Replace Ring switch mechanism in Safelink HV switch gear at sub 24049 | 7 | 180 | 1260 | 0.0014076 | 7.8198e-06
2013-05-12 07:00AM | 227210 | M159 | Urban | MAINTAIN ABS F814 | 11 | 510 | 5610 | 0.006267 | 1.2288e-05
2013-05-12 07:00AM | 227337 | WQ1260 | Urban | REPAIR USL F023 | 5 | 240 | 1200 | 0.0013405 | 5.5856e-06
2013-05-12 07:30AM | 227913 | WL1251 | Urban | Replace LV Switchgear- Sub 15389 | 10 | 480 | 2400 | 0.0026811 | 1.1171e-05
2013-05-12 07:30AM | 228359 | A046 | Urban | ESTABLISH NEW 11KV 1500KVA P/M SUB 32332 RM6 S/GEAR CHANGE 3 POLES AUGMENT O/H HV MAINS REMOVE EX SUB 15787 | 45 | 630 | 28350 | 0.03167 | 5.027e-05
2013-05-12 08:30AM | 229921 | MG1219 | Rural Short | Replace Ring Switch mechanism in Safelink HV switch gear at sub 23777 | 9 | 240 | 2160 | 0.002413 | 1.0054e-05
2013-05-12 08:30AM | 228425 | SN1208 | Urban | MandR HV Switchgear @ S/S 50622 | 19 | 240 | 4560 | 0.0050941 | 2.1225e-05
2013-05-12 09:00AM | 230726 | 27454 | Rural Short | 11kV Undercrossing outage to allow stringing of ADSS (fully insulated) optic fibre along 33kV Fdr 453 route whilst energised. | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2013-05-13 08:00AM | 230934 | 87220 | Rural Short | LIMITED DISTRICT SWITCHING STAND HV POLE | 3 | 450 | 1350 | 0.0015081 | 3.3514e-06
2013-05-13 08:00AM | 227397 | S744 | Urban | Uprate polesub 15778 from 100KVA to 200KVA | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2013-05-13 08:00AM | 229912 | CD1204 | Urban | Install ABS install new poles remove pole. | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2013-05-13 08:00PM | 229672 | PKF2 | Urban | Replace poles and HV augment | 41 | 480 | 18240 | 0.020376 | 4.5802e-05
2013-05-13 08:30AM | 229909 | RBB2 | Rural Short | Replace Condemned Sub Pole 30044 (3YH110) and Replace TRF | 2 | 450 | 900 | 0.0010054 | 2.2342e-06
2013-05-13 09:00AM | 230506 | X802 | Rural Short | LIMITED DISTRICT SWITCHING ISOLATE MAINS TO ALLOW HIGH LOAD AND INSTALL VIBRATION DAMPENERS | 8 | 180 | 1440 | 0.0016087 | 8.937e-06
2013-05-13 10:00AM | 229739 | J510 | Urban | To Re-Furbish / Connect Cable Earth @ Pole 126 Pritchard Rd Macquarie Fields. | 74 | 240 | 17760 | 0.01984 | 8.2667e-05
2013-05-14 07:00AM | 226616 | 2828 | Urban | Augment HV OH mains 19/3.25 AAC. | 2 | 600 | 1200 | 0.0013405 | 2.2342e-06
2013-05-14 08:00AM | 228441 | L946 | Rural Short | INSTALL NEW1000 KVA P/MOUNT SUB 29430 REMOVE EX POLE SUB 6867 LAY 240 Sq 3c XLPE CABLE INSTALL NEW HV UGOH ON EX POLE | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2013-05-14 08:00AM | 228590 | RWC2 | Rural Short | To InstallTerminate and Test New H/V Cable Between CB-RW1281(New Switch Room) and Pole 3XK697 @ Ringwood Z/S and to Remove USL 50434 ABS 50232 and a section of O/H 11KV mains between USL RWD1 and LB 96814 | 8 | 540 | 4320 | 0.004826 | 8.937e-06
2013-05-14 08:00AM | 229205 | A096 | Rural Short | Connect to existing network new section of mains and New pole Sub 29982 | 21 | 510 | 10710 | 0.011964 | 2.346e-05
2013-05-14 08:00AM | 226369 | 9032 | Urban | Change 2 poles and augment LV mains | 6 | 510 | 3060 | 0.0034184 | 6.7027e-06
2013-05-14 08:00AM | 226373 | 9032 | Urban | isolate lv for augment | 69 | 510 | 35190 | 0.039311 | 7.7081e-05
2013-05-14 08:00AM | 229901 | C890 | Urban | REPLACE RAGBOLTS FOR COLUMNS # 8102 8103 and 8103 - GREENBANK DR WERRINGTON | 72 | 480 | 34560 | 0.038608 | 8.0433e-05
2013-05-14 08:00AM | 230136 | 27200 | Urban | INSTALL NEW L/V PILLAR 122268 | 2 | 300 | 600 | 0.00067027 | 2.2342e-06
2013-05-14 08:30AM | 229063 | OA1233 | Rural Short | Replace Leaning Pole # 35 and Replace HV X-arm on Pole 34 | 30 | 390 | 11700 | 0.01307 | 3.3514e-05
2013-05-14 08:30AM | 229568 | 27454 | Rural Short | M and R ABS 60773 | 2 | 300 | 600 | 0.00067027 | 2.2342e-06
2013-05-14 08:30AM | 230055 | PCE2 | Urban | STAND POLES | 162 | 420 | 68040 | 0.076009 | 0.00018097
2013-05-14 08:30AM | 230861 | APE2 | Urban | REPAIR LV CABLES SUB 27229 | 29 | 450 | 13050 | 0.014578 | 3.2396e-05
2013-05-14 09:00AM | 225256 | ULJ2 | Rural Short | Augment HV conductors to 180mm CCTPirralea Rd ULLADULLA. | 101 | 330 | 33330 | 0.037234 | 0.00011283
2013-05-14 09:00AM | 227676 | CLC2 | Urban | Replace pole 14 and Augment HV Conductors ( 9 to 15 )Penguin Head Rd CULBURRA. | 184 | 390 | 71760 | 0.080165 | 0.00020555
2013-05-14 09:00AM | 230920 | B745 | Urban | Pole Changeover | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2013-05-14 12:00AM | 229996 | BWG2 | Urban | Replace Ring switch mechanism in Safelink HV switch gear at sub 24395 | 1 | 180 | 180 | 0.00020108 | 1.1171e-06
2013-05-15 08:00AM | 226770 | 8634 | Rural Short | Augment 2 bays of O/H HV mains to 2 x 80mm CCT. | 36 | 510 | 18360 | 0.02051 | 4.0216e-05
2013-05-15 08:00AM | 228860 | L582 | Rural Short | REPLACE CONDMNED POLE | 24 | 420 | 10080 | 0.011261 | 2.6811e-05
2013-05-15 08:00AM | 229415 | A096 | Rural Short | Allow staff to remove ABS 15556 and erect LBS 123591 (Nulec) | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2013-05-15 08:00AM | 229458 | 10244 | Rural Short | Replace pole + Augment OH HV conductor + Install new ABS | 184 | 480 | 88320 | 0.098664 | 0.00020555
2013-05-15 08:00AM | 226844 | 27194 | Urban | REPLACE LV SW GR + REPAIR HV CAPS HITTING DOOR SUB 16174 | 40 | 480 | 19200 | 0.021449 | 4.4685e-05
2013-05-15 08:00AM | 227419 | J478 | Urban | To Replace Existing TX @ Sub 20973 With A New FR3 500KVA TX and Extend Plinth To Suit Size 5 Cubicle Durham St Minto. | 66 | 360 | 23760 | 0.026543 | 7.373e-05
2013-05-15 08:00AM | 228434 | R257 | Urban | REPLACE POLE'S #1170 and 575 - BARNET ST GLENBROOK | 24 | 480 | 11520 | 0.012869 | 2.6811e-05
2013-05-15 08:00AM | 229655 | C896 | Urban | REPLACE RAGBOLT @ COLUMN # 4095 | 23 | 480 | 11040 | 0.012333 | 2.5694e-05
2013-05-15 08:00AM | 229926 | 2812 | Urban | Replace pole | 148 | 480 | 71040 | 0.07936 | 0.00016533
2013-05-15 08:00AM | 230224 | 9059 | Urban | Replace pole 1664 and retrofit sub 7239. | 54 | 540 | 29160 | 0.032575 | 6.0324e-05
2013-05-15 08:30AM | 229358 | MVH2 | Rural Short | Stand Poles 139 (3KO143) to 136 (3KO147) then 140 (816603) to 141 (3KO144). Augment 11 and 33 kV conductor between Pole 142 (3KO142) and Pole 138 (3KO149). | 25 | 480 | 12000 | 0.013405 | 2.7928e-05
2013-05-15 08:30AM | 229583 | 8802 | Rural Short | MandR ABS 59140 | 32 | 210 | 6720 | 0.007507 | 3.5748e-05
2013-05-15 08:30AM | 230718 | P608 | Rural Short | Install new pole 822248 822252 and 1. augment mains from pole 822250 to 822246.2. augment mains from sub 822253 to 822256. | 7 | 450 | 3150 | 0.0035189 | 7.8198e-06
2013-05-15 08:30AM | 231045 | B204 | Urban | Replace LV X arms | 7 | 330 | 2310 | 0.0025805 | 7.8198e-06
2013-05-15 09:00AM | 230786 | 2828 | Urban | Replace services | 21 | 360 | 7560 | 0.0084454 | 2.346e-05
2013-05-15 09:00AM | 230999 | 8766 | Urban | Re-locate two LV pillars 118229 / 118228 | 26 | 390 | 10140 | 0.011328 | 2.9045e-05
2013-05-15 09:30AM | 229991 | D814 | Rural Short | Replace stolen earth @ sub 22564 | 2 | 120 | 240 | 0.00026811 | 2.2342e-06
2013-05-15 09:30AM | 231149 | 1109 | Urban | LV Isolation for Contractor | 52 | 360 | 18720 | 0.020912 | 5.809e-05
2013-05-16 08:00AM | 229326 | X213 | Rural Short | INSTALL NEW RECLOSER AND REPLACE POLE. REMOVE RECLOSER AND USL'S. REPLACE HV X-ARMS. RETROFIT SUB | 4 | 450 | 1800 | 0.0020108 | 4.4685e-06
2013-05-16 08:00AM | 230236 | W163 | Rural Short | UPRATE EXISTING POLE SUB 24808 TO 200kVA | 28 | 540 | 15120 | 0.016891 | 3.1279e-05
2013-05-16 08:00AM | 230415 | 8637 | Rural Short | 11kV switching to allow the scope of works to be completed as per DNR230406. | 28 | 480 | 13440 | 0.015014 | 3.1279e-05
2013-05-16 08:00AM | 230421 | 8637 | Rural Short | LV switching to allow the scope of works to be completed as per DNR230406. | 66 | 480 | 31680 | 0.03539 | 7.373e-05
2013-05-16 08:00AM | 227010 | T888 | Urban | REPLACE POLES 638 + 639 | 24 | 480 | 11520 | 0.012869 | 2.6811e-05
2013-05-16 08:30AM | 224409 | MG1267 | Rural Short | Augment Hv Oh Mains | 35 | 480 | 16800 | 0.018768 | 3.9099e-05
2013-05-16 08:30AM | 228558 | NG1299 | Rural Short | Replace Condemened Pole 76 and Retrofit SUB 1747(DN1 Switching to be undertaken) | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-05-16 08:30AM | 231258 | JBA2 | Rural Short | AUGMENT OH MAINS TO CCT | 12 | 420 | 5040 | 0.0056303 | 1.3405e-05
2013-05-16 08:30AM | 228514 | SWH2 | Urban | Replace Condemned ABS pole 70047 and Retrofit Sub 42676 | 54 | 390 | 21060 | 0.023527 | 6.0324e-05
2013-05-16 08:30AM | 230166 | FT1202 | Urban | REPLACE UGOH POLE | 66 | 450 | 29700 | 0.033178 | 7.373e-05
2013-05-16 08:30AM | 230994 | APE2 | Urban | REPLACE X CL 4DP082 | 17 | 270 | 4590 | 0.0051276 | 1.8991e-05
2013-05-16 09:00AM | 228771 | RWA2 | Rural Short | Replace Condemned Poles 3VK011 and 3VK083 | 13 | 390 | 5070 | 0.0056638 | 1.4523e-05
2013-05-16 09:00AM | 229948 | ULE2 | Rural Short | Replace poles and Augment HV O/H conductors. ( 4 to 1 )Woodstock Rd MILTON | 18 | 360 | 6480 | 0.0072389 | 2.0108e-05
2013-05-16 09:00AM | 230922 | AZ1264 | Urban | Pole Changeover | 4 | 390 | 1560 | 0.0017427 | 4.4685e-06
2013-05-17 08:00AM | 229025 | T834 | Rural Short | REPLACE ABS WITH AUTOMATED LBSW | 13 | 480 | 6240 | 0.0069708 | 1.4523e-05
2013-05-17 08:00AM | 229977 | HKA2 | Rural Short | Replace 2 poles install DOFs Install HV cable erect one bay of HV Mains. | 245 | 480 | 117600 | 0.13137 | 0.00027369
2013-05-17 08:00AM | 230365 | X217 | Rural Short | REPAIR HV TIE and STRANDED CONDUCTOR. | 13 | 420 | 5460 | 0.0060995 | 1.4523e-05
2013-05-17 08:00AM | 231084 | 25747 | Rural Short | Install new LV pillars 124494 and 124495. Remove pillars 103100 and 103103. | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2013-05-17 08:00AM | 226615 | 1950 | Urban | REPLACE POLES 790 + 792 | 37 | 420 | 15540 | 0.01736 | 4.1333e-05
2013-05-17 08:00AM | 227939 | 5871 | Urban | Replace 1 pole install 2 new DOF's and augment 2 bays of HV OH mains. | 346 | 480 | 166080 | 0.18553 | 0.00038652
2013-05-17 08:00AM | 228023 | 25783 | Urban | Perform 1 x HV IDandSpikeInstall:2 x HV STJ HV UG cable new PS 32572 | 24 | 540 | 6480 | 0.0072389 | 2.6811e-05
2013-05-17 08:00AM | 229653 | C889 | Urban | REPLACE RAGBOLT @ COLUMN # 1333 | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2013-05-17 08:00AM | 229983 | C890 | Urban | REPLACE RAGBOLT AT COLUMN # 7463 - GREENBANK DR WERRINGTON | 21 | 480 | 10080 | 0.011261 | 2.346e-05
2013-05-17 08:00AM | 230215 | B775 | Urban | AUGMENT 5 BAYS OF L/V O/H MAINS ---REPLACE POLE | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-05-17 08:00AM | 230671 | S765 | Urban | Replace hot joint service blocks | 12 | 240 | 2880 | 0.0032173 | 1.3405e-05
2013-05-17 08:30AM | 229294 | 25449 | Rural Short | Replace pole 4AC083 replace TX sub 42427 retro sub 43093 and remove L/L Links adj pole 227122 | 3 | 300 | 900 | 0.0010054 | 3.3514e-06
2013-05-17 08:30AM | 228433 | BLD2 | Urban | Replace Condemned Pole 3KY014 | 10 | 330 | 3300 | 0.0036865 | 1.1171e-05
2013-05-17 08:30AM | 230270 | PCB2 | Urban | LV isolation to replace HV crossarm Pole 3TJ292 | 11 | 240 | 2640 | 0.0029492 | 1.2288e-05
2013-05-17 09:00AM | 228808 | W114 | Rural Short | Replace Condemned Pole 89 and Retrofit Sub 12300 | 8 | 330 | 2640 | 0.0029492 | 8.937e-06
2013-05-17 09:00AM | 230073 | MVB2 | Rural Short | Replace Condemned Pole 3XD012 and Retrofit DOFs at Sub 31607 | 18 | 360 | 6480 | 0.0072389 | 2.0108e-05
2013-05-17 09:00AM | 229126 | A317 | Urban | TERMINATE HV CABLE BETWEEN SUBS 29129 and 24501 | 35 | 300 | 10500 | 0.01173 | 3.9099e-05
2013-05-17 09:00AM | 230681 | S766 | Urban | Replace U/G switch and pillar | 28 | 330 | 9240 | 0.010322 | 3.1279e-05
2013-05-17 09:30AM | 230422 | BYE2 | Rural Short | Replace pole 2VA038 | 6 | 330 | 1980 | 0.0022119 | 6.7027e-06
2013-05-18 08:00AM | 230363 | 25739 | Rural Short | Replace 2 poles stand a new pole replace 2 bays of OH Mains Erect and terminate UGOH on new pole leave unbonded short circuited and earthed for future connection. | 56 | 480 | 26880 | 0.030028 | 6.2559e-05
2013-05-18 09:00AM | 230525 | 8611 | Urban | Isolate direct connect TX1 for contractor to replace customer switchboard. | 1 | 180 | 180 | 0.00020108 | 1.1171e-06
2013-05-19 07:00AM | 229181 | 35981 | Rural Short | Maintain ABS 11480 Replace HV pins on Pole 366 replace HV pins and bonds on pole 367 and install long rods on pole 368 | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2013-05-19 08:00AM | 225967 | S744 | Urban | REPLACE POLE 88 and USL 3059 | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2013-05-19 08:00AM | 229878 | 35771 | Urban | Remove existing Sub 15538 and install new package with FR3 TX + disconnect and abandon existing HV Cable and replace with new 240ALX HV Cable from Sw96844 and terminate at new HV UG/OH + Remove DOF F911. | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-05-19 08:00AM | 230915 | B743 | Urban | Stand pole | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-05-19 08:30AM | 229496 | RVF2 | Urban | STAND NEW UGOH POLE | 12 | 390 | 4680 | 0.0052281 | 1.3405e-05
2013-05-19 08:30AM | 231277 | KMC2 | Urban | BREAK HV BONDSREPAIR HOT JOINT ON HV BUSHING REMAKE HV BONDS | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2013-05-19 09:00AM | 228293 | ULD2 | Urban | Replace TX @ S/S 72180. and Replace USL 41710 with DOFs. HV Aug 1 span to 7/4.5 aac along North st.North St and Princes Hwy ULLADULLA. | 186 | 330 | 61380 | 0.068569 | 0.00020778
2013-05-19 09:00AM | 229309 | SHE2 | Urban | 11kV OUTAGE TO REPLACE STR 62 FDR 7059 | 16 | 390 | 6240 | 0.0069708 | 1.7874e-05
2013-05-19 09:30AM | 229310 | 35767 | Urban | REPAIR THERMO VISION DEFECT @ SW 16939 | 7 | 180 | 1260 | 0.0014076 | 7.8198e-06
2013-05-20 07:30AM | 228411 | 35989 | Rural Short | (1). ID and Spike HV cable between Sw 60653 in PM 25869 and Pole Sub 28818. (2).Install new 500KVA PM 28849 via STJ's. | 2 | 510 | 1020 | 0.0011395 | 2.2342e-06
2013-05-20 08:00AM | 226982 | 8635 | Rural Short | change pole and augment mains and stand new pole and install two abs switches | 60 | 510 | 30600 | 0.034184 | 6.7027e-05
2013-05-20 08:00AM | 228124 | 48196 | Rural Short | Augment HV OH Mains from pole 10 - 17 to 3 x 7/4.45 AAC | 56 | 480 | 26880 | 0.030028 | 6.2559e-05
2013-05-20 08:00AM | 229597 | RBC2 | Rural Short | Connect in new sections of OH mains at subs 31146 and 30731 and disconect old section on OH mains at above subs | 28 | 480 | 13440 | 0.015014 | 3.1279e-05
2013-05-20 08:00AM | 229418 | R256 | Urban | RETROFIT (REPLACE) ABB SAFELINK RING MAIN and FUSE SWITCH MECH'S AT SUB # 23817 DARWIN DR and SUB # 14019 HUME RD LAPSTONE | 100 | 480 | 48000 | 0.053622 | 0.00011171
2013-05-20 08:00AM | 229976 | HKB2 | Urban | Augment 4 bays of HV mains | 375 | 480 | 180000 | 0.20108 | 0.00041892
2013-05-20 08:00AM | 230423 | C893 | Urban | REPLACE RAGBOLT AT COLUMN # 1365 - HAWDON AVE WERRINGTON DOWNS | 21 | 480 | 10080 | 0.011261 | 2.346e-05
2013-05-20 08:00AM | 230542 | MR2224 | Urban | Perform 1 x LV IDandSpike | 13 | 540 | 7020 | 0.0078422 | 1.4523e-05
2013-05-20 08:00AM | 230601 | 5872 | Urban | Augment OH HV conductor + Install DOFs | 186 | 480 | 89280 | 0.099736 | 0.00020778
2013-05-20 08:00AM | 230629 | 438 | Urban | String new conductor FDR 438 pole A817426 - pole A817431. String OPGW FDR 438 pole A169 - pole A277 | 13 | 480 | 6240 | 0.0069708 | 1.4523e-05
2013-05-20 09:00AM | 230153 | RW1218 | Urban | Replace Condemned Pole 3VC109 and Retrofit DOFs at Sub 30360 | 4 | 330 | 1320 | 0.0014746 | 4.4685e-06
2013-05-20 09:00AM | 231030 | S599 | Urban | Pole Changeover | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2013-05-20 09:00AM | 231143 | 3351 | Urban | Augment mains | 7 | 360 | 2520 | 0.0028151 | 7.8198e-06
2013-05-20 11:00PM | 229247 | 20716 | Urban | MandR AND EARTH TEST ON HV SWITCHGEAR AT SUB #14300 - UNION LN PENRITH | 37 | 330 | 12210 | 0.01364 | 4.1333e-05
2013-05-21 07:30AM | 228113 | D830 | Urban | REPLACE LV SW GEAR @ SUB16348 (SIMONE CRES CASULA) | 54 | 480 | 25920 | 0.028956 | 6.0324e-05
2013-05-21 08:00AM | 229975 | APD2 | Rural Short | Replace Safelink switch mechanism Sub 24120 | 47 | 240 | 11280 | 0.012601 | 5.2505e-05
2013-05-21 08:00AM | 230943 | W163 | Rural Short | INSTALL KAON FUSE SAVER AND REPLACE DOF | 3 | 450 | 1350 | 0.0015081 | 3.3514e-06
2013-05-21 08:00AM | 226379 | 9032 | Urban | isolate lv for augment | 65 | 510 | 33150 | 0.037033 | 7.2613e-05
2013-05-21 08:00AM | 227389 | 8744 | Urban | Pole Replacement and HV Augmentation | 148 | 480 | 71040 | 0.07936 | 0.00016533
2013-05-21 08:00AM | 228367 | 2828 | Urban | Aug HV OH mains 19/3.25 AAC.Replace USL 87101 with ABS 79360 | 150 | 480 | 72000 | 0.080433 | 0.00016757
2013-05-21 08:00AM | 229202 | 8744 | Urban | Pole Replacement and HV Augmentation | 201 | 480 | 96480 | 0.10778 | 0.00022454
2013-05-21 08:00AM | 230106 | MYK2 | Urban | NEW PAD SUBSTATION | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2013-05-21 08:00AM | 230404 | C900 | Urban | REPLACE CONDEMNED COLUMN # 1372 - HAWDON AVE CAMBRIDGE PARK | 25 | 300 | 7500 | 0.0083784 | 2.7928e-05
2013-05-21 08:00AM | 230408 | C891 | Urban | REPLACE CONDEMNED COLUMN # 512 - FRANCIS ST CAMBRIDGE PARK | 36 | 300 | 10800 | 0.012065 | 4.0216e-05
2013-05-21 08:00AM | 230742 | NWF2 | Urban | Commission New 315kVA Pad Sub No. 26251 via UGOH on replaced pole 3C0179 | 5 | 480 | 2400 | 0.0026811 | 5.5856e-06
2013-05-21 08:30AM | 227605 | WBD2 | Rural Short | Replace condemned poles | 86 | 390 | 33540 | 0.037468 | 9.6072e-05
2013-05-21 08:30AM | 229257 | BWE2 | Rural Short | 11 kV isolation to allow 33 kV OHEW to be strung - 33 kV Fdr 7901 | 18 | 480 | 8640 | 0.0096519 | 2.0108e-05
2013-05-21 08:30AM | 230607 | JBA2 | Rural Short | REPLACE X POLE 4HJ090 RETRO FIT DS 42224 | 9 | 300 | 2700 | 0.0030162 | 1.0054e-05
2013-05-21 08:30AM | 231099 | W196 | Urban | Install LV pillar 123102. | 7 | 210 | 1470 | 0.0016422 | 7.8198e-06
2013-05-21 09:00AM | 231031 | 5494 | Urban | Pole changeover | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2013-05-21 09:30AM | 229807 | 7972 | Urban | INSTALL 2 POLES FOR FUTURE PROJECT | 18 | 210 | 3780 | 0.0042227 | 2.0108e-05
2013-05-21 11:00AM | 230410 | C889 | Urban | REPLACE CONDEMNED COLUMN # 514 - FRANCIS ST CAMBRIDGE PARK | 24 | 300 | 7200 | 0.0080433 | 2.6811e-05
2013-05-21 12:00PM | 229995 | APD2 | Rural Short | Replace Safelink switch mechanism sub 24121 | 54 | 240 | 12960 | 0.014478 | 6.0324e-05
2013-05-22 08:00AM | 230613 | X492 | Rural Long | LIMITED DISTRICT SWITCHING RETROFIT SUB AND INSTALL MDI | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2013-05-22 08:00AM | 226869 | 8634 | Rural Short | Augment 4 bays of O/H HV mains to 2 x 80mm CCT | 11 | 510 | 5610 | 0.006267 | 1.2288e-05
2013-05-22 08:00AM | 226641 | WL1292 | Urban | Allow staff to stand new pole and erect ABS 123618 | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2013-05-22 08:00AM | 227935 | 5498 | Urban | Replace two poles and augment two bays of HV OH mains. | 198 | 480 | 95040 | 0.10617 | 0.00022119
2013-05-22 08:00AM | 227936 | 5498 | Urban | Isolate LV mains for replacement of 2 poles and augmentation of 2 bays of HV OH mains. | 69 | 480 | 33120 | 0.036999 | 7.7081e-05
2013-05-22 08:30AM | 228762 | JBA2 | Rural Short | AUGMENT HV MAINS BETWEEN POLES 877396 and 877401 MISTY LANE JAMBEROO | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2013-05-22 08:30AM | 229442 | RWB2 | Rural Short | Trim Trees Near Conductors | 31 | 420 | 13020 | 0.014545 | 3.4631e-05
2013-05-22 08:30AM | 231051 | 8634 | Rural Short | Replace LV arms @ pole 7 | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-05-22 08:30AM | 228619 | BLD2 | Urban | Replace Condemned Sub pole 40200 | 72 | 420 | 30240 | 0.033782 | 8.0433e-05
2013-05-22 08:30AM | 230261 | WRF2 | Urban | REPLACE X POLE 4CP007 | 22 | 360 | 7920 | 0.0088476 | 2.4577e-05
2013-05-22 09:00AM | 228477 | BDF2 | Rural Short | Install New LBS 124298 ( Replaces ABS 59747 )Gypsy Point Rd NORTH NOWRA | 20 | 360 | 7200 | 0.0080433 | 2.2342e-05
2013-05-22 09:30AM | 230546 | CLD2 | Rural Short | Replace pole 3DC015 and install additional pole | 1 | 330 | 330 | 0.00036865 | 1.1171e-06
2013-05-22 09:30AM | 231322 | ULH2 | Urban | replace pole Dickson Close Ulladulla | 16 | 270 | 4320 | 0.004826 | 1.7874e-05
2013-05-23 08:00AM | 227215 | 27446 | Rural Short | Augment 4 bays of O/H LV mains. | 35 | 510 | 17850 | 0.019941 | 3.9099e-05
2013-05-23 08:00AM | 227608 | 46752 | Urban | REPLACE POLE 864 and USL 7017 | 68 | 480 | 32640 | 0.036463 | 7.5964e-05
2013-05-23 08:00AM | 229905 | C890 | Urban | REPLACE COLUMNS # 8102 8103 and 8103 - GREENBANK DR WERRINGTON | 9 | 360 | 3240 | 0.0036195 | 1.0054e-05
2013-05-23 08:30AM | 231124 | GG1295 | Rural Short | AUGMENT LV MAINS | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2013-05-23 09:00AM | 229368 | CLC2 | Urban | Replace LV poles ( 10 and 11 ) | 30 | 360 | 10800 | 0.012065 | 3.3514e-05
2013-05-23 09:00AM | 230801 | CS1276 | Urban | Isolate section of low voltage mains so that new pole can be erected | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2013-05-23 09:30AM | 226230 | ULJ2 | Rural Short | Install New Sectionaliser 97544 ( replaces USL 41791 )Little Forest Rd MILTON. | 64 | 300 | 19200 | 0.021449 | 7.1496e-05
2013-05-24 08:00AM | 230756 | L588 | Rural Short | REPLACE LV X-ARM | 14 | 330 | 4620 | 0.0051611 | 1.564e-05
2013-05-24 08:00AM | 231212 | HKA2 | Rural Short | Remove 2 bays of HV Mains. Install 2 new poles. Install 11KV 3Core Cable. Augment 2 bays of HV Mains to 7/4.50 AAC and 2 bays of 120mm CCT. Install Clahs. | 40 | 480 | 19200 | 0.021449 | 4.4685e-05
2013-05-24 08:00AM | 227631 | 35767 | Urban | Upgrade HV Network | 69 | 480 | 33120 | 0.036999 | 7.7081e-05
2013-05-24 08:00AM | 228218 | 35767 | Urban | HV Upgrade | 74 | 480 | 35520 | 0.03968 | 8.2667e-05
2013-05-24 08:00AM | 229679 | C896 | Urban | REPLACE COLUMN # 4095 | 24 | 300 | 7200 | 0.0080433 | 2.6811e-05
2013-05-24 08:00AM | 230710 | FF1239 | Urban | AUGMENT 7 BAYS OF HV MAINS. UPGRADE HV CONSTRUCTIONS. | 330 | 480 | 116160 | 0.12976 | 0.00036865
2013-05-24 08:00AM | 231078 | C890 | Urban | REPLACE RAGBOLT @ COLUMN # 12114 | 16 | 480 | 7680 | 0.0085795 | 1.7874e-05
2013-05-24 08:00AM | 231153 | 55876 | Urban | Replace Pole | 26 | 420 | 10920 | 0.012199 | 2.9045e-05
2013-05-24 08:00AM | 231465 | SHG2 | Urban | CONNECT LV CABLE | 14 | 360 | 5040 | 0.0056303 | 1.564e-05
2013-05-24 08:00AM | 231472 | CRB2 | Urban | Change poles | 48 | 450 | 21600 | 0.02413 | 5.3622e-05
2013-05-24 08:30AM | 231130 | GG1295 | Rural Short | AUGMENT LV MAINS | 7 | 360 | 2520 | 0.0028151 | 7.8198e-06
2013-05-24 08:30AM | 229019 | 46481 | Urban | Replace condemned pole #184 and run 1bay 150mm abc from sub pole 1461 to pole 184 | 156 | 480 | 37440 | 0.041825 | 0.00017427
2013-05-24 09:00AM | 230478 | RVC2 | Urban | MandR HOLEC SWITCHGEAR RETRO SUB REPAIR DEFECTS | 259 | 360 | 93240 | 0.10416 | 0.00028933
2013-05-24 09:00AM | 231041 | 1109 | Urban | Pole changeover | 11 | 360 | 3960 | 0.0044238 | 1.2288e-05
2013-05-24 09:00AM | 231237 | CLC2 | Urban | Replace O/H conductor with LV ABC | 10 | 360 | 3600 | 0.0040216 | 1.1171e-05
2013-05-24 09:00AM | 231422 | D819 | Urban | Repair LV Pillar | 25 | 360 | 9000 | 0.010054 | 2.7928e-05
2013-05-24 09:00AM | 231425 | FF1276 | Urban | Lv Mains | 15 | 360 | 5400 | 0.0060324 | 1.6757e-05
2013-05-24 09:00AM | 231426 | 8764 | Urban | L.V. X-arm | 10 | 240 | 2400 | 0.0026811 | 1.1171e-05
2013-05-24 09:00AM | 231781 | 8779 | Urban | Streetlight columnn to be repaired | 22 | 180 | 3960 | 0.0044238 | 2.4577e-05
2013-05-24 10:30AM | 229682 | C889 | Urban | REPLACE COLUMN # 1333 | 8 | 330 | 2640 | 0.0029492 | 8.937e-06
2013-05-25 07:30AM | 223717 | 8744 | Urban | REPLACE TX AND MAKE REPAIRS TO POLE HARDWARE | 83 | 450 | 37350 | 0.041724 | 9.2721e-05
2013-05-25 08:00AM | 230937 | B748 | Urban | Augment OH HV conductor + Replace poles | 140 | 480 | 67200 | 0.07507 | 0.0001564
2013-05-25 08:00AM | 230938 | B748 | Urban | Augment OH HV conductor + Replace poles | 135 | 480 | 64800 | 0.072389 | 0.00015081
2013-05-25 08:30AM | 230401 | BWB2 | Urban | Holec HV Switchgear MandR at Padmount Substation 32052 | 1 | 210 | 210 | 0.0002346 | 1.1171e-06
2013-05-25 09:00AM | 227702 | CLC2 | Urban | Replace poles ( 19 and 20 )Penguin Head Rd CULBURRA. | 114 | 390 | 44460 | 0.049667 | 0.00012735
2013-05-25 10:00AM | 231252 | WX1254 | Urban | Isolation of 11kV and 415V to removal 11kV Span. Span to be removed to allow for the restringing of 93F and 93L by Transgrid/ BBUGL. Span to be reinstated via a separate DNR once restringing works complete. Weekend work only due to LV commercial cutomers | 20 | 240 | 4800 | 0.0053622 | 2.2342e-05
2013-05-26 06:00AM | 228463 | B202 | Urban | HV DEVELOPMENT. | 21 | 660 | 13860 | 0.015483 | 2.346e-05
2013-05-26 07:00AM | 230852 | NE1282 | Urban | Install new PMS's 32680 and 32681. | 4 | 540 | 2160 | 0.002413 | 4.4685e-06
2013-05-26 07:30AM | 228104 | 7979 | Urban | MAINTAIN ABS 7251 andMAINTAIN ABS 8342 MAINTAIN ABS 7256 REPAIR H/V HARDWARE POLE2014 | 11 | 270 | 2970 | 0.0033178 | 1.2288e-05
2013-05-26 07:30AM | 228412 | J469 | Urban | Install new 500KVA PM 32276.Uprate HV switchgear to Safelink CFC units in PM's 29614 and 22040. | 23 | 510 | 11730 | 0.013104 | 2.5694e-05
2013-05-26 08:00AM | 228131 | WX1284 | Urban | ABS MAINTENANCE @ SW 13507 NEWTON RD WETHERILL PARKABS MAINTAINCE @SW 59082 METTERS PL WETHERILL PARK | 31 | 570 | 17670 | 0.01974 | 3.4631e-05
2013-05-26 08:00AM | 230840 | SN1271 | Urban | Replace Pole | 26 | 480 | 12480 | 0.013942 | 2.9045e-05
2013-05-26 08:00AM | 231520 | C832 | Urban | REPLACE POLE | 1 | 300 | 300 | 0.00033514 | 1.1171e-06
2013-05-26 08:00AM | 231644 | CRE2 | Urban | Replace poles | 30 | 390 | 11700 | 0.01307 | 3.3514e-05
2013-05-26 08:30AM | 230191 | PCF2 | Urban | REPLACE CAST IRON UGOH | 1 | 450 | 450 | 0.0005027 | 1.1171e-06
2013-05-26 08:30AM | 230425 | PCE2 | Urban | AUGMENT HV MAINS REPLACE S/S 42113 WITH S/S 29374 INSTALL DOF's 90161 | 224 | 420 | 94080 | 0.1051 | 0.00025023
2013-05-26 08:30AM | 230747 | SWE2 | Urban | REPLACE UGOH POLE | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2013-05-26 08:30AM | 231612 | WX1284 | Urban | 20Min dump for HV switching | 4 | 60 | 240 | 0.00026811 | 4.4685e-06
2013-05-26 11:00AM | 231914 | 68181 | Urban | PVT Test 3 | 1 | 60 | 60 | 6.7027e-05 | 1.1171e-06
2013-05-26 11:00PM | 230286 | CD1241 | Urban | Retrofit Sub 11701 and rectify defects. Augment LV OH mains. | 1 | 390 | 390 | 0.00043568 | 1.1171e-06
2013-05-27 08:00AM | 231140 | W127 | Rural Short | Replace pole 496 (877366) Remove USL G619 and install ABS 97536. Install new pole 877364. | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2013-05-27 08:00AM | 231489 | X871 | Urban | Install a new Pillar | 30 | 360 | 10800 | 0.012065 | 3.3514e-05
2013-05-27 08:30AM | 230065 | ULJ2 | Rural Short | CORRECT DEFECT TO HV and LV UGOH @ POLE 857750 | 9 | 420 | 3780 | 0.0042227 | 1.0054e-05
2013-05-27 08:30AM | 231038 | MVB2 | Rural Short | Augment a Section of O/H 11KV Mains Retrofit DOFs at Sub 30157 Replace TX and Retrofit DOFs at Sub 30984 and Replace Condemned Pole 3R2788 | 71 | 450 | 31950 | 0.035692 | 7.9316e-05
2013-05-27 08:30AM | 230717 | FT1208 | Urban | Trim Overhanging tree near pole 3PX466 | 89 | 180 | 16020 | 0.017896 | 9.9424e-05
2013-05-28 07:00AM | 229999 | X877 | Rural Short | To allow staff to (1) replace ABS 51661 with New Auto LBS 123266 on replacement pole 879561 (2) Replace Condemned Pole 161 and (3) Retro Sub 10871 Coates Park Rd Cobbitty. | 11 | 480 | 5280 | 0.0058984 | 1.2288e-05
2013-05-28 08:00AM | 230806 | L582 | Rural Short | REPLACE CONDEMNED POLE and REPAIR HV EARTHS | 15 | 420 | 6300 | 0.0070379 | 1.6757e-05
2013-05-28 08:00AM | 230928 | BWA2 | Rural Short | Trim Trees Near Conductors | 107 | 480 | 51360 | 0.057375 | 0.00011953
2013-05-28 08:00AM | 231190 | GG1295 | Rural Short | Remove redundant HV conductors | 12 | 480 | 5760 | 0.0064346 | 1.3405e-05
2013-05-28 08:00AM | 231611 | X213 | Rural Short | INSTALL NEW RECLOSER AND REPLACE POLE. REMOVE RECLOSER AND USL'S. REPLACE HV X-ARMS. RETROFIT SUB | 4 | 450 | 1800 | 0.0020108 | 4.4685e-06
2013-05-28 08:00AM | 227635 | 8738 | Urban | HV Upgrade | 122 | 480 | 58560 | 0.065419 | 0.00013629
2013-05-28 08:00AM | 227636 | 55890 | Urban | HV Upgrade | 71 | 480 | 34080 | 0.038071 | 7.9316e-05
2013-05-28 08:00AM | 227868 | 2816 | Urban | Change Const's for future OPGW augment + place ex hardex in rollers. | 69 | 480 | 33120 | 0.036999 | 7.7081e-05
2013-05-28 08:00AM | 228255 | 8718 | Urban | RETROFIT SUB 2206 + REPLACE LEAKING TX | 13 | 420 | 5460 | 0.0060995 | 1.4523e-05
2013-05-28 08:00AM | 229193 | 8738 | Urban | HV Upgrade | 122 | 480 | 58560 | 0.065419 | 0.00013629
2013-05-28 08:00AM | 229627 | AZ1227 | Urban | Allow staff to erect new HV 11KV O/H mains. | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2013-05-28 08:30AM | 230436 | DP1210 | Rural Short | RETRO SUB 40737 | 67 | 240 | 16080 | 0.017963 | 7.4847e-05
2013-05-28 08:30AM | 230114 | C896 | Urban | Install new FR3 TX in Sub 7095 and replace existing LV Sw/Gr in Sub 7095 | 60 | 450 | 27000 | 0.030162 | 6.7027e-05
2013-05-28 08:30AM | 230707 | DP1258 | Urban | REPLACE X POLE 226497 RETRO FIT DS 40780 | 56 | 300 | 16800 | 0.018768 | 6.2559e-05
2013-05-28 08:30AM | 231567 | 9055 | Urban | Project | 37 | 390 | 14430 | 0.01612 | 4.1333e-05
2013-05-28 08:30PM | 230350 | KMB2 | Urban | CHANGE POLES and AUGMENT LV MAINS | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2013-05-28 09:00AM | 229642 | 55874 | Urban | REPLACE HV X-ARMS POLES 2248 + 2249 | 162 | 360 | 58320 | 0.06515 | 0.00018097
2013-05-28 09:00AM | 231035 | 2807 | Urban | LV changeover | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-05-28 09:00AM | 231039 | 1109 | Urban | LV Changeover | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-05-28 09:30AM | 231261 | BYE2 | Rural Short | Replace poles 2VA037 2VA036 and 2VA035 | 6 | 330 | 1980 | 0.0022119 | 6.7027e-06
2013-05-28 09:30AM | 231517 | ULJ2 | Rural Short | Repair ABS 41798Wilfords Ln MILTON | 25 | 240 | 6000 | 0.0067027 | 2.7928e-05
2013-05-29 08:00AM | 228246 | 48196 | Rural Short | Augment 11 KV O.H. mains between pole 7 and pole 9 to 7/4.50 AAC | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2013-05-29 08:00AM | 231026 | T841 | Rural Short | REPLACE HV X-ARMS AND RETROFIT SUB | 18 | 450 | 8100 | 0.0090487 | 2.0108e-05
2013-05-29 08:00AM | 231182 | SZ1332 | Rural Short | 11kV switching to allow the scope of works to be completed as per DNR231181. | 23 | 480 | 11040 | 0.012333 | 2.5694e-05
2013-05-29 08:00AM | 231547 | KVD2 | Rural Short | STAND NEW POLES | 5 | 450 | 2250 | 0.0025135 | 5.5856e-06
2013-05-29 08:00AM | 228546 | WH1272 | Urban | Replace LV swgr Sub 6046 | 20 | 480 | 9600 | 0.010724 | 2.2342e-05
2013-05-29 08:00AM | 231181 | 458/1 | Urban | Reconductor between poles 16 and 25 Feeder 458/1 with new Uranus (61/3.25) as per approved drawings. | 15 | 480 | 7200 | 0.0080433 | 1.6757e-05
2013-05-29 08:30AM | 230284 | KVA2 | Rural Short | Install new 25kVA sub 32538 and LV mains. Replace pole 212656 | 11 | 420 | 4620 | 0.0051611 | 1.2288e-05
2013-05-29 08:30AM | 231295 | MVH2 | Rural Short | Install Poles 142 (3KO142) and augment conductor between Poles 139 (3KO143)and 144 (3KO141) | 16 | 480 | 7680 | 0.0085795 | 1.7874e-05
2013-05-29 08:30AM | 230308 | RW1255 | Urban | Remove Voltage Regulator 13884 and Install New Voltage Regulator 32411 | 2 | 450 | 900 | 0.0010054 | 2.2342e-06
2013-05-29 08:30AM | 231459 | 25774 | Urban | Isolate Tx @ SUB 12533 for repair of LV neutral conduct and associated works. | 11 | 330 | 3630 | 0.0040551 | 1.2288e-05
2013-05-29 09:00AM | 227931 | S788 | Rural Short | HV augmentation and ABS replacement. | 69 | 480 | 33120 | 0.036999 | 7.7081e-05
2013-05-29 09:00AM | 230005 | ULE2 | Rural Short | Augment HV O/H mains to 3 x 19/3.25 from new pole 878002 to 877996. ( 4 to 21 )Woodstock Rd MILTON | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2013-05-29 09:00AM | 230951 | S788 | Rural Short | Isolate LV mains for HV augmentation and replacement of hardware. | 14 | 480 | 6720 | 0.007507 | 1.564e-05
2013-05-30 08:00AM | 230670 | KC1288 | Rural Short | REPLACE LV X-ARM @ POLE # J1 | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2013-05-30 08:00AM | 231276 | R260 | Rural Short | Replace pole remove USL W036 and Bond HV. Remove LFI's 18676/1 and 18676/2. | 115 | 450 | 51750 | 0.057811 | 0.00012847
2013-05-30 08:00AM | 227113 | B214 | Urban | REPLACE USL 2627 WITH LBS 97007 | 156 | 420 | 50400 | 0.056303 | 0.00017427
2013-05-30 08:00AM | 227915 | 35571 | Urban | REPLACE TRF (FR3 TYPE) and REPLACE LV SW/GEAR - SUB 16369 | 84 | 420 | 17640 | 0.019706 | 9.3838e-05
2013-05-30 08:00AM | 231253 | 2806 | Urban | Replace one pole and augment two bays of HV OH mains. | 131 | 480 | 62880 | 0.070245 | 0.00014634
2013-05-30 08:00AM | 231522 | 1962 | Urban | REPLACE POLE 996 | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2013-05-30 08:00AM | 231635 | T890 | Urban | INSTALL NEW LV PILLAR 123874 | 17 | 360 | 6120 | 0.0068368 | 1.8991e-05
2013-05-30 08:00AM | 231808 | C900 | Urban | REPLACE LV X-ARM @ PLOE # 69 | 14 | 90 | 1260 | 0.0014076 | 1.564e-05
2013-05-30 08:30AM | 231747 | MVB2 | Rural Short | Remove a section of 11KV O/H Mains Install new poles and a new section of 11KV O/H Mains Install New DOFs 123382 | 8 | 450 | 3600 | 0.0040216 | 8.937e-06
2013-05-30 08:30AM | 230040 | HBC2 | Urban | REPLACE ABS POLE | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-05-30 08:30AM | 230947 | RW1292 | Urban | Trim Trees Near Conductors | 230 | 450 | 103500 | 0.11562 | 0.00025694
2013-05-30 08:30AM | 232020 | 8694 | Urban | Replace LV xarm | 9 | 120 | 1080 | 0.0012065 | 1.0054e-05
2013-05-30 09:00AM | 229504 | NA1214 | Urban | Rectify PIN Defect D898.Replace ABS 30701. | 33 | 300 | 9900 | 0.011059 | 3.6865e-05
2013-05-30 09:00AM | 231995 | 2806 | Urban | LV pole change pluck and plant | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2013-05-30 09:00AM | 232018 | 7994 | Urban | Replace LV xarms | 14 | 180 | 2520 | 0.0028151 | 1.564e-05
2013-05-30 09:30AM | 229784 | HKA2 | Rural Short | REPLACE POLE 3GV099 | 183 | 300 | 54900 | 0.06133 | 0.00020443
2013-05-30 10:30AM | 230577 | C889 | Urban | REPLACE COLUMN # PL718181 | 47 | 180 | 8460 | 0.0094508 | 5.2505e-05
2013-05-30 11:00AM | 232016 | 17058 | Urban | Replace LV xarms | 9 | 240 | 2160 | 0.002413 | 1.0054e-05
2013-05-30 12:00PM | 230675 | A098 | Rural Short | REPLACE 2 X LV X-ARM @ POLE # E101 | 17 | 240 | 4080 | 0.0045578 | 1.8991e-05
2013-05-30 12:30PM | 230579 | C890 | Urban | REPLACE COLUMN # PL718419 | 13 | 210 | 2730 | 0.0030497 | 1.4523e-05
2013-05-30 12:30PM | 232021 | 17058 | Urban | Replace LV xarms | 10 | 150 | 1500 | 0.0016757 | 1.1171e-05
2013-05-31 08:00AM | 231609 | X492 | Rural Long | LIMITED DISTRICT SWITCHING RETROFIT SUB AND INSTALL MDI | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2013-05-31 08:00AM | 223635 | 35989 | Rural Short | To Replace Pole # 33 and 2 X Cast Iron UG/OH Cable Terminations @ Wilton Park Rd Wilton. | 16 | 420 | 6720 | 0.007507 | 1.7874e-05
2013-05-31 08:00AM | 227943 | 10244 | Rural Short | HV OH mains augmentation. | 169 | 480 | 81120 | 0.090621 | 0.00018879
2013-05-31 08:00AM | 227944 | 10244 | Rural Short | Isolate LV mains for HV OH mains augmentation. | 42 | 480 | 20160 | 0.022521 | 4.6919e-05
2013-05-31 08:00AM | 227970 | S788 | Rural Short | run new hv mains above lv | 21 | 510 | 10710 | 0.011964 | 2.346e-05
2013-05-31 08:00AM | 229785 | X877 | Rural Short | Job 1. Live line break H.V.Bonds pole 345Job 2.Allow staff to replace pole and abs 13356 usl 13357. erect new pole and abs 123059 for future recloser.Job 3. Live line remake HV bonds pole 345 | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2013-05-31 08:00AM | 231797 | BK1251 | Rural Short | Replace Condemned Pole | 5 | 450 | 2250 | 0.0025135 | 5.5856e-06
2013-05-31 08:00AM | 227700 | 25780 | Urban | REPLACE LV SW GR SUB 20767 | 65 | 480 | 31200 | 0.034854 | 7.2613e-05
2013-05-31 08:00AM | 229720 | CJ1267 | Urban | UPGRADE HV NETWORK | 95 | 480 | 45600 | 0.050941 | 0.00010613
2013-05-31 08:00AM | 230336 | 35762 | Urban | change service | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-05-31 08:00AM | 230409 | 2828 | Urban | Replace pole 873.Twin arm HV xarms Sub 364.Augment HV OH mains 19/3.25 AAC. | 92 | 480 | 44160 | 0.049332 | 0.00010278
2013-05-31 08:00AM | 231167 | B716 | Urban | REPLACE 2 POLES AUGMENT 3 SPANS OF L/V O/H MAINS | 35 | 540 | 18900 | 0.021114 | 3.9099e-05
2013-05-31 08:00AM | 231448 | CRB2 | Urban | Augment | 48 | 30 | 1440 | 0.0016087 | 5.3622e-05
2013-05-31 08:00AM | 231676 | 4354 | Urban | Replace column #1099 | 12 | 150 | 1800 | 0.0020108 | 1.3405e-05
2013-05-31 08:00AM | 231962 | SC1238 | Urban | Replace Pole | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2013-05-31 08:00AM | 232318 | WL1236 | Urban | Box arm | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2013-05-31 08:30AM | 228730 | X877 | Rural Short | Remove ABS J062 and install LBS 123482 and retrofit sub 10957 and 10056. | 41 | 450 | 18450 | 0.020611 | 4.5802e-05
2013-05-31 08:30AM | 230043 | MVB2 | Rural Short | Augment a Section of O/H 11KV Mains and Retrofit DOFs at Sub 30782 and 30157 | 71 | 450 | 31950 | 0.035692 | 7.9316e-05
2013-05-31 08:30AM | 229280 | BLD2 | Urban | Replace Condemned Pole 3PD276 | 3 | 270 | 810 | 0.00090487 | 3.3514e-06
2013-05-31 08:30AM | 232054 | BLD2 | Urban | ISOLATE 11KV FDR BLD2 FOR CLEARANCE ONLY | 120 | 30 | 3600 | 0.0040216 | 0.00013405
2013-05-31 09:00AM | 231298 | BYE2 | Rural Short | INSTALL NEW POLE AND ABS 88125 | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2013-05-31 09:00AM | 231774 | BWF2 | Rural Short | Replace Condemned LV Pole 3R1462 | 4 | 300 | 1200 | 0.0013405 | 4.4685e-06
2013-05-31 09:00AM | 231570 | D830 | Urban | Service Conversions | 5 | 360 | 1800 | 0.0020108 | 5.5856e-06
2013-05-31 09:00AM | 231993 | 2807 | Urban | LV pole change puck and plant | 1 | 360 | 360 | 0.00040216 | 1.1171e-06
2013-05-31 11:00AM | 230174 | SC1241 | Urban | INSTALL CLAMPS @ HV S/GEAR SUB 8941 and SUB 8940. MANORHOUSE ST Q/HILL | 137 | 240 | 32880 | 0.036731 | 0.00015305
2013-06-01 07:00AM | 230955 | 54658 | Urban | Install new subs 32463 and 32464 via two STJ's. | 4 | 540 | 2160 | 0.002413 | 4.4685e-06
2013-06-01 08:00AM | 231169 | 25747 | Rural Short | Augment / Upgrade HV Network. Upgrade section of mains to 7/4.50 AAC. Remove ABS K230 and Span Between ABS 230 and AR 47395 (Not Servicable Privately Owned) Replace USL K231 with ABS 95438 on Pole 311. | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-06-02 02:00PM | 232080 | S737 | Rural Short | Standing new 33kV concrete poles Transfer exisiting network over to new poles Replace ABS 9181 with a new one Run 33kV Ropes and OPGW RopesSite Contact Andrew Haste: 0452 266 544 | 207 | 1320 | 91080 | 0.10175 | 0.00023124
2013-06-02 07:00AM | 232132 | B743 | Urban | Stand Pole | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2013-06-02 08:00AM | 224953 | B215 | Urban | Replace 1 pole and existing USL with ABS. | 94 | 480 | 45120 | 0.050404 | 0.00010501
2013-06-02 08:30AM | 231947 | 53314 | Urban | Tie in O/H mains to new UGOH pole 40 (asset # 862736) stood on 31/5/13 | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2013-06-02 10:00AM | 232111 | ULH2 | Urban | replace LV pole Wandella cl Ulladulla | 10 | 240 | 2400 | 0.0026811 | 1.1171e-05
2013-06-02 11:00AM | 232080 | S737 | Rural Short | Standing new 33kV concrete poles Transfer exisiting network over to new poles Replace ABS 9181 with a new one Run 33kV Ropes and OPGW RopesSite Contact Andrew Haste: 0452 266 544 | 207 | 180 | 12420 | 0.013875 | 0.00023124
2013-06-03 08:00AM | 230523 | 48196 | Rural Short | allow staff to augment section of HV open wire mains | 64 | 480 | 30720 | 0.034318 | 7.1496e-05
2013-06-03 08:00AM | 231268 | W127 | Rural Short | Replace poles + Install poles | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2013-06-03 08:00AM | 231821 | X213 | Rural Short | Install vibration dampers. | 13 | 480 | 6240 | 0.0069708 | 1.4523e-05
2013-06-03 08:00AM | 231829 | X213 | Rural Short | Install vibration dampers. | 25 | 480 | 12000 | 0.013405 | 2.7928e-05
2013-06-03 08:00AM | 228002 | 53314 | Urban | run new hv mains | 18 | 510 | 9180 | 0.010255 | 2.0108e-05
2013-06-03 08:00AM | 228748 | 25783 | Urban | Remove:1 x pole | 4 | 540 | 2160 | 0.002413 | 4.4685e-06
2013-06-03 08:00AM | 231346 | D845 | Urban | Install DOFS | 181 | 480 | 86880 | 0.097055 | 0.0002022
2013-06-03 08:00AM | 231367 | WWE2 | Urban | REPLACE UGOH POLE REMOVE HV MAINS INSTALL LV LINKS | 181 | 480 | 86880 | 0.097055 | 0.0002022
2013-06-03 08:00AM | 232353 | D830 | Urban | LV Jointing | 6 | 420 | 2520 | 0.0028151 | 6.7027e-06
2013-06-03 08:00PM | 230315 | 5500 | Urban | Replace existing TX in Sub 16463 with new FR3 TX + Install new SafeLink CFC HV Sw/Gr in Sub 16463 + Remove DOF T554. | 11 | 480 | 5280 | 0.0058984 | 1.2288e-05
2013-06-03 08:30AM | 225808 | RWC2 | Rural Short | Trim trees near powerlines | 12 | 420 | 2940 | 0.0032843 | 1.3405e-05
2013-06-03 08:30AM | 225808 | RWC2 | Rural Short | Trim trees near powerlines | 2 | 450 | 3150 | 0.0035189 | 2.2342e-06
2013-06-03 08:30AM | 231224 | L947 | Rural Short | Install Capacitor Control Box on Pole 869841.Check all earthing is correct.Adjust centre phase reactor earth point | 14 | 330 | 4620 | 0.0051611 | 1.564e-05
2013-06-03 08:30AM | 230823 | CS1276 | Urban | PERFORM MandR ON HV SWITCHGEAR and EARTH TEST @ SUB # 17569 | 37 | 390 | 14430 | 0.01612 | 4.1333e-05
2013-06-03 09:00AM | 231989 | 9047 | Urban | LV Pole change | 7 | 360 | 2520 | 0.0028151 | 7.8198e-06
2013-06-03 11:00AM | 230463 | SZ1242 | Urban | Protection Checks and SCADA commissioning for Sectionaliser 92212. | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2013-06-04 08:00AM | 228156 | 4368 | Rural Short | isolate lv to change 2 poles install 2 new abs remove abs and usl | 37 | 510 | 18870 | 0.02108 | 4.1333e-05
2013-06-04 08:00AM | 228164 | 4368 | Rural Short | change 2 poles install two abs and remove abs and usl | 66 | 510 | 33660 | 0.037602 | 7.373e-05
2013-06-04 08:00AM | 231541 | GG1295 | Rural Short | REPLACE 2 HV POLES | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2013-06-04 08:00AM | 231859 | X217 | Rural Short | Install vibration dampers - See REQ# 232002 for Jobs 5 -8 and associated Earthing. | 42 | 540 | 22680 | 0.025336 | 4.6919e-05
2013-06-04 08:00AM | 231894 | X217 | Rural Short | Install vibration dampers. | 8 | 540 | 4320 | 0.004826 | 8.937e-06
2013-06-04 08:00AM | 231895 | X217 | Rural Short | Install vibration dampers | 8 | 540 | 4320 | 0.004826 | 8.937e-06
2013-06-04 08:00AM | 227924 | 17061 | Urban | Install new pole and ABS 92828 | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2013-06-04 08:00AM | 230115 | 8770 | Urban | replace cond pole 2242 | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-06-04 08:00AM | 231025 | X863 | Urban | 1/Augment ex hardex earth wire to OPGW from pole 429 Oakes Rd to pole 576 Oakes Rd.2/Replace Pole 3034792 (871785) Coral Tree Drive + Moorilla Ave and 342 (871825) Coral Tree Drve and Augment Hv Mains between poles 467 and 416. | 69 | 480 | 33120 | 0.036999 | 7.7081e-05
2013-06-04 08:00AM | 231123 | 8651 | Urban | Change LV switch gear Sub 6699 Glenwood Rd Kellyville | 74 | 480 | 35520 | 0.03968 | 8.2667e-05
2013-06-04 08:00AM | 231302 | 8610 | Urban | Augment OH HV conductor + Replace pole + Install DOFs | 298 | 480 | 143040 | 0.15979 | 0.0003329
2013-06-04 08:00AM | 231304 | J478 | Urban | Replace pole and remove ABS. Install new ABS. | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2013-06-04 08:30AM | 230253 | 35816 | Rural Short | Install new sectionaliser 97056 and remove pole 208.Repair defects at poles 212 213 217 218. | 175 | 450 | 78750 | 0.087973 | 0.0001955
2013-06-04 08:30AM | 230503 | RWD2 | Rural Short | Change out pole 816652 (185) 3KO028 (186) 328805 (187) and re-arrange S/S 30770 pole top (Site 1). Install Trunnion Clamps on 33 kV conductor at Poles 816644 to 816647 (Site 2). | 27 | 480 | 12960 | 0.014478 | 3.0162e-05
2013-06-04 08:30AM | 230647 | GG1295 | Rural Short | INSTALL NEW SUB POLE REPLACE POLE 4PG113 and INSTALL NEW ABS RUN NEW LV ABC MAINS from NEW SUB POLE to POLE 4PG107 | 18 | 360 | 6480 | 0.0072389 | 2.0108e-05
2013-06-04 08:30AM | 231162 | L941 | Rural Short | Replace Pole 126 with Pole 884424 and Replace ABS 5693 | 32 | 420 | 13440 | 0.015014 | 3.5748e-05
2013-06-04 08:30AM | 230908 | CRD2 | Urban | Replace ABS pole 70388 | 32 | 390 | 12480 | 0.013942 | 3.5748e-05
2013-06-04 08:30AM | 231238 | BWD2 | Urban | New PM Sub 29631 and associated cables. Remove pole sub 31881 | 33 | 435 | 14355 | 0.016036 | 3.6865e-05
2013-06-04 08:30AM | 232145 | C896 | Urban | Re Configure LV Network with New Cable | 39 | 330 | 12870 | 0.014377 | 4.3568e-05
2013-06-04 09:00AM | 232053 | BWH2 | Rural Short | Augment LV Mains to 150mm + S/L ABC | 80 | 420 | 33600 | 0.037535 | 8.937e-05
2013-06-04 09:00AM | 224702 | ULF2 | Urban | Replace Condemned poles 2PV015 and 2PV016Kings Point Dr KINGS POINT | 215 | 330 | 70950 | 0.07926 | 0.00024018
2013-06-04 09:00AM | 230467 | SZ1242 | Urban | Protection Checks and SCADA commissioning for Sectionaliser 92313. | 63 | 420 | 26460 | 0.029559 | 7.0379e-05
2013-06-04 09:30AM | 232162 | CLD2 | Rural Short | Reconnect repaired U/G between S/S 50397 and S/S 50267 (See defect # D823) | 30 | 240 | 7200 | 0.0080433 | 3.3514e-05
2013-06-05 07:30AM | 231557 | CD1204 | Urban | Install earthing points on CCT cable. | 5 | 90 | 450 | 0.0005027 | 5.5856e-06
2013-06-05 08:00AM | 228438 | A096 | Rural Short | REPLACE CONDEMNED SUB POLE # 9821 - DONOHOES RD MULGOA | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2013-06-05 08:00AM | 228468 | BK1299 | Rural Short | RUN 180MM CCT FROM POLE 38 TO POLE 23 | 70 | 450 | 31500 | 0.035189 | 7.8198e-05
2013-06-05 08:00AM | 231576 | GG1232 | Rural Short | Replace HV pole | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2013-06-05 08:00AM | 231681 | 57448 | Rural Short | INSTALL ABSand KAON FUSES AUGMENT HV MAINS and RETRO SUBS.APPLY WORKING EARTHS and INSTALL VIBRATION DAMPERS | 97 | 540 | 52380 | 0.058515 | 0.00010836
2013-06-05 08:00AM | 231917 | L582 | Rural Short | LIMITED DISTRICT SWITCHING STAND NEW POLES INSTALL STAYS AND INSTALL VIBRATION DAMPERS. | 5 | 450 | 2250 | 0.0025135 | 5.5856e-06
2013-06-05 08:00AM | 232390 | 57448 | Rural Short | Installation of vibration dampers at various locations. (In conjunction with REQ# 231681 - Same spur.) | 31 | 540 | 16740 | 0.018701 | 3.4631e-05
2013-06-05 08:00AM | 232409 | 57448 | Rural Short | Install vibration dampers | 103 | 540 | 55620 | 0.062134 | 0.00011506
2013-06-05 08:00AM | 229609 | 8680 | Urban | Install ABS A0278 and replace pole 46 with pole 810975. | 66 | 510 | 33660 | 0.037602 | 7.373e-05
2013-06-05 08:00AM | 230420 | 2828 | Urban | Augment HV OH mains 19/3.25 AAC.Replace ABS D119 with ABS 79357. | 49 | 480 | 23520 | 0.026275 | 5.4739e-05
2013-06-05 08:00AM | 230692 | CRE2 | Urban | Replace poles | 68 | 450 | 30600 | 0.034184 | 7.5964e-05
2013-06-05 08:00AM | 231467 | 41537 | Urban | Augment OH HV conductor | 161 | 480 | 77280 | 0.086331 | 0.00017986
2013-06-05 08:00AM | 232291 | X866 | Urban | Install 2 new pillars | 12 | 480 | 5760 | 0.0064346 | 1.3405e-05
2013-06-05 08:00AM | 232356 | D830 | Urban | LV Jointing | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-06-05 08:30AM | 221081 | RWB2 | Rural Short | Replace Hv Cross Arm and Install DOF's | 43 | 480 | 20640 | 0.023057 | 4.8036e-05
2013-06-05 08:30AM | 229047 | RWD2 | Rural Short | Augment 33 kV conductor from Pole 199 (3KO127) to Pole 205 (3XK003). Stand Poles 229 (3XK143) to 233 (3XK139). | 29 | 480 | 13920 | 0.01555 | 3.2396e-05
2013-06-05 08:30AM | 231405 | 35990 | Rural Short | Replace DOF's H795 and RepairStay on Pole 38 | 27 | 330 | 8910 | 0.0099535 | 3.0162e-05
2013-06-05 08:30AM | 229860 | KMA2 | Urban | 11kV OUTAGE ON FDR KMA2 TO REPLACE STR 8 FDR 7008 | 66 | 420 | 27720 | 0.030967 | 7.373e-05
2013-06-05 08:30AM | 231147 | SHK2 | Urban | REPLACE X PL 4DR228 RETRO FIT SUBS 41477 43064 | 121 | 300 | 36300 | 0.040551 | 0.00013517
2013-06-05 09:00AM | 230476 | L948 | Rural Short | Protection Checks and SCADA commissioning for Sectionaliser 90891. | 22 | 420 | 9240 | 0.010322 | 2.4577e-05
2013-06-05 09:00AM | 230514 | RWD2 | Rural Short | Remove Voltage Regulator Tank for Repair at VR 24602 | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2013-06-05 09:00AM | 232320 | 1125 | Urban | Replace Services | 2 | 360 | 720 | 0.00080433 | 2.2342e-06
2013-06-05 09:30AM | 230727 | ULE2 | Rural Short | Augment HV O/H conductors. ( 5 to 1 27 to 21 )Woodstock Rd MILTON | 8 | 330 | 2640 | 0.0029492 | 8.937e-06
2013-06-05 09:30AM | 229809 | 7972 | Urban | REPLACE ABS 5156 WITH ABS 124085 AND CHANGE POLE 55 (REUSE EXISTING USL) | 17 | 210 | 3570 | 0.0039881 | 1.8991e-05
2013-06-05 09:30AM | 232351 | NA1281 | Urban | L/V Jointing McKenzie St | 10 | 300 | 3000 | 0.0033514 | 1.1171e-05
2013-06-05 12:00PM | 232080 | S737 | Rural Short | Standing new 33kV concrete poles Transfer exisiting network over to new poles Replace ABS 9181 with a new one Run 33kV Ropes and OPGW RopesSite Contact Andrew Haste: 0452 266 544 | 207 | 120 | 8280 | 0.0092498 | 0.00023124
2013-06-06 01:00PM | 232223 | 49001 | Urban | Reconnect Cables in COlumns | 29 | 120 | 3480 | 0.0038876 | 3.2396e-05
2013-06-06 08:00AM | 231479 | R260 | Rural Short | Replace USL W012 with ABS 95381. Replace poles 104 105 and 175 with poles 868058868060 and 867323. | 115 | 450 | 51750 | 0.057811 | 0.00012847
2013-06-06 08:00AM | 231659 | L584 | Rural Short | INSTALL 1 X BAY OF 95MM ABC LV OFF POLE SUB 29475 | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-06-06 08:00AM | 231931 | R293 | Rural Short | Install vibration dampers. | 17 | 540 | 9180 | 0.010255 | 1.8991e-05
2013-06-06 08:00AM | 232147 | X877 | Rural Short | To allow staff to replace Existing ABS 11364 with new Auto LBS 123583 on replacement pole 883851 (Lord Ben Farm) Off Cut Hill Rd Cobbitty | 4 | 480 | 1920 | 0.0021449 | 4.4685e-06
2013-06-06 08:00AM | 227648 | 2813 | Urban | HV Augmentation | 42 | 480 | 20160 | 0.022521 | 4.6919e-05
2013-06-06 08:00AM | 228193 | X871 | Urban | Replace Poles and Augment Hv Mains | 43 | 480 | 20640 | 0.023057 | 4.8036e-05
2013-06-06 08:00AM | 228361 | 55885 | Urban | REPLACE POLE 175 | 20 | 420 | 8400 | 0.0093838 | 2.2342e-05
2013-06-06 08:00AM | 228375 | 2813 | Urban | Pole Replacement and Hv Mains Augmentation | 63 | 480 | 30240 | 0.033782 | 7.0379e-05
2013-06-06 08:00AM | 230734 | C890 | Urban | REPLACE LV LINKSand RE-TERM CABLE @ COLUMN 9596 | 15 | 480 | 7200 | 0.0080433 | 1.6757e-05
2013-06-06 08:00AM | 231431 | 7966 | Urban | RETRO SUB 5625 RECTIFY DEFECTS WITHIN ISOLATION | 59 | 480 | 28320 | 0.031637 | 6.591e-05
2013-06-06 08:00AM | 232323 | D830 | Urban | LV Service conversions | 12 | 420 | 5040 | 0.0056303 | 1.3405e-05
2013-06-06 08:30AM | 230481 | 35816 | Rural Short | Install new sectionaliser 96867 and install poles 873994 and 873995. | 114 | 450 | 51300 | 0.057308 | 0.00012735
2013-06-06 08:30AM | 231571 | L941 | Rural Short | Install new sub 32602 + pole 881046.Install new pole 881414.Install 4 bay 150mm LV ABC.Install LV links @ poles 104 839074 and 881414 | 34 | 420 | 14280 | 0.015952 | 3.7982e-05
2013-06-06 08:30AM | 230380 | KMA2 | Urban | 11kV OUTAGE ON FDR KMA2 TO REPLACE STR 8 and 9 FDR 7008 | 66 | 420 | 27720 | 0.030967 | 7.373e-05
2013-06-06 08:30AM | 231458 | BLB2 | Urban | REPLACE CONDEMNED POLES 2G0315 and 2G0346 and RETRO-FIT SUB 41009 and 40028 | 154 | 420 | 64680 | 0.072255 | 0.00017204
2013-06-06 09:00AM | 232364 | APD2 | Rural Short | Connect LV Cable into PM Sub 28988 and Pillar 115640 | 6 | 300 | 1800 | 0.0020108 | 6.7027e-06
2013-06-06 09:00AM | 229864 | KMF2 | Urban | 11kV OUTAGE ON FDR KMF2 TO REPLACE STR 8 and 9 FDR 7008 | 23 | 390 | 8970 | 0.010021 | 2.5694e-05
2013-06-06 09:00AM | 232005 | ULB2 | Urban | Retrofit SL Switchgear @ S/S 24018. | 8 | 360 | 2880 | 0.0032173 | 8.937e-06
2013-06-06 09:00AM | 232225 | 8676 | Urban | Repair LV S/B in Reln Pillar | 29 | 180 | 5220 | 0.0058314 | 3.2396e-05
2013-06-06 10:00AM | 230479 | L948 | Rural Short | Protection Checks and SCADA commissioning for Sectionaliser 92621. | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2013-06-06 10:00AM | 232500 | 2807 | Urban | Changing Services Over | 5 | 240 | 1200 | 0.0013405 | 5.5856e-06
2013-06-07 08:00AM | 227945 | S788 | Rural Short | HV OH augmentation and ABS installation. | 53 | 480 | 25440 | 0.02842 | 5.9207e-05
2013-06-07 08:00AM | 227946 | S786 | Rural Short | Isolate LV mains for HV OH augmentation and ABS installation. | 6 | 480 | 2880 | 0.0032173 | 6.7027e-06
2013-06-07 08:00AM | 232422 | S764 | Rural Short | install new auto recloser retro sub # 8183 and retro sub # 1899 | 42 | 510 | 21420 | 0.023929 | 4.6919e-05
2013-06-07 08:00AM | 227639 | 8738 | Urban | Upgrade HV Network | 152 | 480 | 72960 | 0.081505 | 0.0001698
2013-06-07 08:00AM | 228472 | C852 | Urban | Change pole 1876 | 8 | 570 | 4560 | 0.0050941 | 8.937e-06
2013-06-07 08:00AM | 228789 | 8738 | Urban | HV Upgrade | 120 | 480 | 57600 | 0.064346 | 0.00013405
2013-06-07 08:00AM | 229182 | 5496 | Urban | ISOLATE SECTIONS OF 11KV O/H MAINS TO ENABLE AUSGRID TO RUN FIBRE ON ADJACENT TRANSMISSION FEEDER | 50 | 570 | 28500 | 0.031838 | 5.5856e-05
2013-06-07 08:00AM | 231095 | 5872 | Urban | Augment OH HV conductor + install DOFs | 138 | 480 | 66240 | 0.073998 | 0.00015416
2013-06-07 08:00AM | 231581 | 2828 | Urban | Change over LV.Remove old poles. | 115 | 480 | 55200 | 0.061665 | 0.00012847
2013-06-07 08:00AM | 231613 | A324 | Urban | Replace Pole - Tension Mains | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2013-06-07 08:00AM | 232019 | WH1298 | Urban | Replace Pole | 32 | 420 | 13440 | 0.015014 | 3.5748e-05
2013-06-07 08:00AM | 232043 | CRB2 | Urban | REPLACE POLES and AUGMENT | 100 | 420 | 42000 | 0.046919 | 0.00011171
2013-06-07 08:00AM | 232327 | D830 | Urban | LV Service Conversions | 5 | 420 | 2100 | 0.002346 | 5.5856e-06
2013-06-07 08:00AM | 232538 | WL1292 | Urban | Replace service | 12 | 480 | 5760 | 0.0064346 | 1.3405e-05
2013-06-07 08:30AM | 230599 | OA1207 | Rural Short | Alter construction at pole 841781 and remove OH mains from pole 841781 to pole 242 plus retrofit pole substation 11596. | 41 | 390 | 15990 | 0.017863 | 4.5802e-05
2013-06-07 08:30AM | 231173 | L940 | Rural Short | Install 3 bays 120mm HV CCT from Sub 32354 to pole 877641.Install 63kva Tx on new sub 32354.Cut and shackle HV @ pole 13Finish off LV and connect new services. | 24 | 450 | 10800 | 0.012065 | 2.6811e-05
2013-06-07 08:30AM | 231214 | FT1208 | Urban | Trim Overhanging Trees | 8 | 240 | 1920 | 0.0021449 | 8.937e-06
2013-06-07 09:00AM | 231795 | CLC2 | Urban | Replace LV poles ( 10 and 11 ) | 30 | 360 | 10800 | 0.012065 | 3.3514e-05
2013-06-07 09:00AM | 231990 | 2812 | Urban | LV pole change | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2013-06-07 09:00AM | 232371 | C824 | Urban | Replace rear shroud in column | 14 | 180 | 2520 | 0.0028151 | 1.564e-05
2013-06-07 09:00AM | 232376 | 8680 | Urban | Install LV cable | 2 | 240 | 480 | 0.00053622 | 2.2342e-06
2013-06-08 03:30PM | 231050 | 17069 | Urban | Install new sub 32573 | 3 | 30 | 90 | 0.00010054 | 3.3514e-06
2013-06-08 08:30AM | 231125 | OA1207 | Rural Short | Change faulty LBS 86866 and retrofit pole substation 10389. | 48 | 360 | 17280 | 0.019304 | 5.3622e-05
2013-06-09 08:00AM | 231037 | BLE2 | Urban | REPLACE POLES REPLACE SUBSTATION REMOVE DOF INSTALL DOF AUGMENT HV MAINS. | 36 | 480 | 17280 | 0.019304 | 4.0216e-05
2013-06-09 08:00AM | 231485 | CRE2 | Urban | Install LBS | 25 | 390 | 9750 | 0.010892 | 2.7928e-05
2013-06-09 09:00AM | 232247 | J512 | Urban | To allow staff to install New Pole # 883861 Newton Rd Glenfield | 3 | 360 | 1080 | 0.0012065 | 3.3514e-06
2013-06-11 08:00AM | 229134 | S737 | Rural Short | Remove 1 x poleInstall:1 x new pole and new polesub 32215 | 28 | 510 | 14280 | 0.015952 | 3.1279e-05
2013-06-11 08:00AM | 231235 | L582 | Rural Short | INSTALL NEW ABS A0710 and REPLACE POLE. | 7 | 420 | 2940 | 0.0032843 | 7.8198e-06
2013-06-11 08:00AM | 231764 | W124 | Rural Short | REMOVE TREES ENDANGERING OUR HV | 59 | 325 | 19175 | 0.021421 | 6.591e-05
2013-06-11 08:00AM | 232338 | 8637 | Rural Short | 11kV switching to allow the scope of works to be completed as per DNR232336. | 6 | 480 | 2880 | 0.0032173 | 6.7027e-06
2013-06-11 08:00AM | 227633 | 55885 | Urban | Upgrade HV Network | 96 | 480 | 46080 | 0.051477 | 0.00010724
2013-06-11 08:00AM | 229706 | 55885 | Urban | Upgrade to HV | 96 | 480 | 46080 | 0.051477 | 0.00010724
2013-06-11 08:00AM | 230265 | 17038 | Urban | REPLACE POLE # 875 - TIDSWELL ST ST MARYS | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-06-11 08:00AM | 231338 | HR1210 | Urban | Replace pole and augment LV mains. | 88 | 450 | 39600 | 0.044238 | 9.8307e-05
2013-06-11 08:30AM | 231523 | RW1255 | Urban | Augment a section of 11KV O/H Mains to 180mm CCT | 37 | 450 | 16650 | 0.0186 | 4.1333e-05
2013-06-11 08:30AM | 232630 | SHK2 | Urban | REPLACE X POLE 4DR411 | 31 | 270 | 8370 | 0.0093503 | 3.4631e-05
2013-06-12 06:00AM | 229254 | 35761 | Urban | move service to other side of open point | 6 | 120 | 720 | 0.00080433 | 6.7027e-06
2013-06-12 08:00AM | 230398 | L946 | Rural Short | stand new poles adjacent existing | 6 | 510 | 3060 | 0.0034184 | 6.7027e-06
2013-06-12 08:00AM | 231476 | L942 | Rural Short | Check all earthing is correct. Adjust centre phase reactor earth point @ cap #32208 | 16 | 150 | 2400 | 0.0026811 | 1.7874e-05
2013-06-12 08:00AM | 231761 | W163 | Rural Short | Connect to the network new section of O/H mains | 4 | 540 | 2160 | 0.002413 | 4.4685e-06
2013-06-12 08:00AM | 225320 | C900 | Urban | Replace 1 pole and install ABS. | 92 | 480 | 44160 | 0.049332 | 0.00010278
2013-06-12 08:00AM | 227997 | 2816 | Urban | Augment ex hardex [earth wire] to OPGW + clip in. | 88 | 480 | 42240 | 0.047187 | 9.8307e-05
2013-06-12 08:00AM | 229169 | 25741 | Urban | STAND POLES and ERECT NEW ABS 92888 | 40 | 480 | 19200 | 0.021449 | 4.4685e-05
2013-06-12 08:00AM | 231403 | D850 | Urban | AUGMENT 11KV O/H MAINS AND RETRO-FIT SUB 4174 | 44 | 480 | 21120 | 0.023594 | 4.9153e-05
2013-06-12 08:00AM | 231851 | 25783 | Urban | Install 1 x pole. Uprate LV OH mains | 14 | 540 | 3780 | 0.0042227 | 1.564e-05
2013-06-12 08:00AM | 232095 | C890 | Urban | REPLACE RAGBOLT @ COLUMN # 7474 | 11 | 480 | 5280 | 0.0058984 | 1.2288e-05
2013-06-12 08:30AM | 231358 | 61617 | Rural Short | Replace poles 117 and 118 and retrofit substation 10577 | 14 | 450 | 6300 | 0.0070379 | 1.564e-05
2013-06-12 08:30AM | 231733 | APC2 | Rural Short | M and R ABS 80861 | 5 | 180 | 900 | 0.0010054 | 5.5856e-06
2013-06-12 08:30AM | 231780 | BWC2 | Urban | Install 11KV O/H Aerial Earthwire between poles 3R0490 and 821889 | 13 | 450 | 5850 | 0.0065352 | 1.4523e-05
2013-06-12 08:30AM | 232505 | BWD2 | Urban | Install new HV Cable between Sub 29631 and pole 3R0898. Remove ABS 50418 and 1 bay 11kV mains. | 22 | 450 | 9900 | 0.011059 | 2.4577e-05
2013-06-12 08:30AM | 232546 | L537 | Urban | Replace lv x arms | 41 | 360 | 14760 | 0.016489 | 4.5802e-05
2013-06-12 11:00AM | 231864 | L941 | Rural Short | Check all earthing is correct. Adjust centre phase reactor earth point @ cap 32218. | 5 | 270 | 1350 | 0.0015081 | 5.5856e-06
2013-06-13 02:00AM | 221419 | CT1203 | Urban | To Connect 11KV Cable Earth Screen To The HV Earth @ Indoor Sub 13615 (TX2) Coogan Ln Campbelltown | 256 | 180 | 23040 | 0.025738 | 0.00028598
2013-06-13 08:00AM | 230512 | 25744 | Rural Short | REPLACE COND POLE 153 | 5 | 480 | 2400 | 0.0026811 | 5.5856e-06
2013-06-13 08:00AM | 230973 | S788 | Rural Short | isolate lv for hv work adjacent | 10 | 510 | 5100 | 0.0056973 | 1.1171e-05
2013-06-13 08:00AM | 231128 | L941 | Rural Short | Protection Checks and SCADA commissioning for Sectionaliser 91383. | 29 | 420 | 12180 | 0.013607 | 3.2396e-05
2013-06-13 08:00AM | 232303 | R260 | Rural Short | Augment LV mains | 4 | 420 | 1680 | 0.0018768 | 4.4685e-06
2013-06-13 08:00AM | 232370 | 8637 | Rural Short | 11kV switching to allow the scope of works to be completed as per DNR232368. | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2013-06-13 08:00AM | 227640 | 16666 | Urban | HV Upgrade | 121 | 480 | 58080 | 0.064882 | 0.00013517
2013-06-13 08:00AM | 229225 | 16666 | Urban | HV Upgrade | 121 | 480 | 58080 | 0.064882 | 0.00013517
2013-06-13 08:00AM | 230966 | 53314 | Urban | install new sub pole 2 bays of hv abc new abs and length of underground hv cable | 25 | 510 | 12750 | 0.014243 | 2.7928e-05
2013-06-13 08:00AM | 231364 | X863 | Urban | Redress/ Roller 66kv const and opgwaugment. | 191 | 480 | 91680 | 0.10242 | 0.00021337
2013-06-13 08:00AM | 231632 | WRD2 | Urban | ID AND SPIKE CABLES HV AUGMENT REMOVE CAST IRON POTHEADS STJ NEW CABLES AND INSTALL NEW POTHEADS | 116 | 480 | 55680 | 0.062201 | 0.00012959
2013-06-13 08:00AM | 232166 | C890 | Urban | REPLACE RAGBOLT @ COLUMN # 9588 | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2013-06-13 08:00AM | 232458 | X863 | Urban | Install Rollers and construct to OPGW consts on earth wire [hardex] and augment to OPGW. | 267 | 480 | 128160 | 0.14317 | 0.00029827
2013-06-13 08:00AM | 232481 | CT1206 | Urban | Remove pillars 100801 and 100802. Install new switch pillar 123564. | 21 | 420 | 8820 | 0.009853 | 2.346e-05
2013-06-13 08:00AM | 232800 | D830 | Urban | Service conversions | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2013-06-13 08:30AM | 230335 | BLE2 | Urban | REPLACE CONDEMNED POLE 3PK011 2C0513 3PK013 and RETRO-FIT SUB 40125 and REPLACE CROSSARMS | 53 | 420 | 22260 | 0.024867 | 5.9207e-05
2013-06-13 08:30AM | 232549 | C896 | Urban | Replace Consac Cable with XLPE | 25 | 330 | 8250 | 0.0092162 | 2.7928e-05
2013-06-13 09:00AM | 232085 | CLD2 | Rural Short | REPLACE POLE AND UP-RATE TXR AT SUB 50411 | 136 | 360 | 48960 | 0.054694 | 0.00015193
2013-06-13 09:00AM | 231897 | FF1276 | Urban | ISOLATE BELOW DOF AT SUB 8284 TO CHANGE LV ARMS | 20 | 330 | 6600 | 0.007373 | 2.2342e-05
2013-06-13 09:00AM | 232609 | 8641 | Urban | Raise LV Pillar and Extend Cables | 13 | 360 | 4680 | 0.0052281 | 1.4523e-05
2013-06-13 09:00AM | 232610 | 49337 | Urban | Raise Pillar and Extend Cables | 9 | 360 | 3240 | 0.0036195 | 1.0054e-05
2013-06-13 09:30AM | 232599 | L579 | Rural Short | Replace column + establish new pillar | 6 | 300 | 1800 | 0.0020108 | 6.7027e-06
2013-06-14 08:00AM | 230258 | X877 | Rural Short | erect recloser 97727 and associated USL's97757 and 97758 to be commisioned @ alater date | 23 | 480 | 11040 | 0.012333 | 2.5694e-05
2013-06-14 08:00AM | 230983 | 27446 | Rural Short | change pole and install abs | 18 | 510 | 9180 | 0.010255 | 2.0108e-05
2013-06-14 08:00AM | 231572 | NG1299 | Rural Short | Replace Pole + Augment HV OH conductor + Install DOFs | 34 | 480 | 16320 | 0.018231 | 3.7982e-05
2013-06-14 08:00AM | 229174 | 35761 | Urban | change lv pole | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2013-06-14 08:00AM | 231866 | 20722 | Urban | REPAIR LEANING BOARD @ COLUMN 13212 | 4 | 240 | 960 | 0.0010724 | 4.4685e-06
2013-06-14 08:00AM | 231885 | 10241 | Urban | HV and LV DEFECT RECTIFICATION | 274 | 420 | 115080 | 0.12856 | 0.00030609
2013-06-14 08:00AM | 232175 | C889 | Urban | REPLACE RAGBOLT @ COLUMN # 1340 | 37 | 480 | 17760 | 0.01984 | 4.1333e-05
2013-06-14 08:00AM | 232369 | SZ1322 | Urban | String new conductor Feeder 453. String OPGW Feeder 453 and future feeder 425 | 23 | 480 | 11040 | 0.012333 | 2.5694e-05
2013-06-14 08:00AM | 232613 | 55876 | Urban | Replace Pole | 4 | 450 | 1800 | 0.0020108 | 4.4685e-06
2013-06-14 08:00AM | 232628 | S766 | Urban | REPAIR NEUTRAL CONNECTION @ PILLAR # 83746 | 14 | 300 | 4200 | 0.0046919 | 1.564e-05
2013-06-14 08:00AM | 232802 | D830 | Urban | Service conversions | 12 | 480 | 5760 | 0.0064346 | 1.3405e-05
2013-06-14 08:30AM | 231318 | NG1299 | Rural Short | Replace Condemened Pole 76 (DN1 Switching to be undertaken) | 4 | 360 | 1440 | 0.0016087 | 4.4685e-06
2013-06-14 08:30AM | 231760 | APC2 | Rural Short | M and R Holec Sub 41514 | 92 | 240 | 22080 | 0.024666 | 0.00010278
2013-06-14 08:30AM | 232195 | JBB2 | Rural Short | M and R ABS 70915 | 13 | 240 | 3120 | 0.0034854 | 1.4523e-05
2013-06-14 08:30AM | 231817 | SWJ2 | Urban | Replace HV tie HV fuses and HV Crossarm | 3 | 390 | 1170 | 0.001307 | 3.3514e-06
2013-06-14 09:00AM | 231888 | MVH2 | Rural Short | HV Switchgear Maintenance at Substation 31423 | 36 | 240 | 8640 | 0.0096519 | 4.0216e-05
2013-06-14 09:00AM | 231575 | 49915 | Urban | INSTALL POLE FOR FUTURE PROJECT | 19 | 240 | 4560 | 0.0050941 | 2.1225e-05
2013-06-14 09:00AM | 232705 | C824 | Urban | Replace Marble Bags | 20 | 240 | 4800 | 0.0053622 | 2.2342e-05
2013-06-14 09:30AM | 230841 | BDG2 | Rural Short | Replace pole / Install new pole String new conductor ( not connected )Meroo Rd BOMADERRY. | 158 | 330 | 52140 | 0.058247 | 0.0001765
2013-06-14 09:30AM | 232780 | ULH2 | Urban | replace LV pole Wandella close Ulladulla | 10 | 300 | 3000 | 0.0033514 | 1.1171e-05
2013-06-15 03:30PM | 230038 | J506 | Urban | To Re-Furbish / Connect Cable Earth @ Sub (11272) Fields Rd Macquarie Fields and Change L/V Switchgear. | 5 | 480 | 2400 | 0.0026811 | 5.5856e-06
2013-06-15 05:00PM | 227273 | 35443 | Urban | REPLACE EXISTING RGB12 HV SWITCHGEAR WITH ABB SAFELINK - SUB 17686 | 12 | 45 | 540 | 0.00060324 | 1.3405e-05
2013-06-15 08:30AM | 231736 | NA1266 | Urban | LV SWITCHGEAR UPGRADE | 17 | 420 | 7140 | 0.0079762 | 1.8991e-05
2013-06-16 05:00PM | 227273 | 35443 | Urban | REPLACE EXISTING RGB12 HV SWITCHGEAR WITH ABB SAFELINK - SUB 17686 | 12 | 45 | 540 | 0.00060324 | 1.3405e-05
2013-06-16 07:00AM | 229962 | 46750 | Urban | RETROFIT SUB 20013 | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2013-06-16 07:00AM | 230007 | 1962 | Urban | HV TEST TO FAULT FIND + LOCATE HV CABLE FAULT BETWEEN SW 46611 SUB 23840 and SW E694 SUB 8576 | 3 | 540 | 1620 | 0.0018097 | 3.3514e-06
2013-06-16 08:00AM | 231492 | 35990 | Rural Short | MandR ABS T341 Retrofit SUB 10210 and referb poles 482 78 and 79 | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2013-06-16 08:00AM | 232357 | R290 | Rural Short | REPLACE DOF INSTALL KAON FUSE SAVERS AND REPAIR STAY | 72 | 450 | 16650 | 0.0186 | 8.0433e-05
2013-06-16 08:00AM | 232357 | R290 | Rural Short | REPLACE DOF INSTALL KAON FUSE SAVERS AND REPAIR STAY | 2 | 540 | 19980 | 0.02232 | 2.2342e-06
2013-06-16 08:00AM | 216223 | 2828 | Urban | Augment HV OH mains 19/3.25 AAC.Change over poles. | 131 | 480 | 62880 | 0.070245 | 0.00014634
2013-06-16 08:00AM | 230290 | B201 | Urban | REPLACE CONDEMNED POLE 2073 | 25 | 360 | 9000 | 0.010054 | 2.7928e-05
2013-06-16 08:00AM | 230582 | CRE2 | Urban | REPLACE POLES and AUGMENT MAINS | 105 | 450 | 47250 | 0.052784 | 0.0001173
2013-06-16 08:00AM | 231478 | J489 | Urban | Install new poles. Install new ABS. Remove ABS. Augment 11kV OH mains. | 35 | 420 | 14700 | 0.016422 | 3.9099e-05
2013-06-16 09:00AM | 231952 | L946 | Rural Short | To remove diseased tree outside of East Kurrajong Public School | 18 | 240 | 4320 | 0.004826 | 2.0108e-05
2013-06-16 09:00AM | 232077 | B204 | Urban | RE BOND IN HV CABLE TO SUB 18341 | 5 | 180 | 900 | 0.0010054 | 5.5856e-06
2013-06-17 06:00AM | 229282 | 35761 | Urban | move service to other side of open point | 19 | 120 | 2280 | 0.002547 | 2.1225e-05
2013-06-17 07:00AM | 231923 | MC1252 | Rural Short | New HV poles | 79 | 540 | 42660 | 0.047656 | 8.8252e-05
2013-06-17 08:00AM | 232319 | A052 | Rural Short | Install DOFs (40A) A0314 and lower LV mains to suit pole 22.(District Switcher) | 18 | 420 | 7560 | 0.0084454 | 2.0108e-05
2013-06-17 08:00AM | 232467 | BWA2 | Rural Short | Trim Trees Near Conductors | 107 | 480 | 51360 | 0.057375 | 0.00011953
2013-06-17 08:00AM | 228165 | 35325 | Urban | Roller + change consts for future OPGW augment. | 59 | 480 | 28320 | 0.031637 | 6.591e-05
2013-06-17 08:00AM | 229469 | 8744 | Urban | Pole Replacement and HV Augmentation | 152 | 480 | 72960 | 0.081505 | 0.0001698
2013-06-17 08:00AM | 229482 | 8744 | Urban | Pole Replacement and HV Augmentation | 103 | 480 | 49440 | 0.05523 | 0.00011506
2013-06-17 08:00AM | 229932 | 9032 | Urban | install 2 x new ABS (A0276 and 83514) | 12 | 540 | 6480 | 0.0072389 | 1.3405e-05
2013-06-17 08:00AM | 231734 | 41537 | Urban | Augment OH HV conductor | 217 | 480 | 104160 | 0.11636 | 0.00024242
2013-06-17 08:00AM | 232313 | C900 | Urban | REPLACE RAGBOLT@ COLUMN # 1381 | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2013-06-17 09:15AM | 231782 | 1954 | Urban | Isolate Sub 21314 to uprate LV to 1250A MVCB connect new Service to Tavern | 1 | 285 | 285 | 0.00031838 | 1.1171e-06
2013-06-17 10:30AM | 232734 | S737 | Rural Short | Stand new 33kV concrete poles Transfer exisiting network over to new poles Run OPGW Rope Pull 33kV conductor and tie in Install temp USL A0850 | 114 | 90 | 5130 | 0.0057308 | 0.00012735
2013-06-17 12:00PM | 232734 | S737 | Rural Short | Stand new 33kV concrete poles Transfer exisiting network over to new poles Run OPGW Rope Pull 33kV conductor and tie in Install temp USL A0850 | 114 | 30 | 1710 | 0.0019103 | 0.00012735
2013-06-18 08:00AM | 225646 | CLA2 | Rural Short | Remove existing O/H HV Mains 2 poles and USL's. Install 1 new pole ABS and 11KV 240mm 3C cable. | 20 | 480 | 9600 | 0.010724 | 2.2342e-05
2013-06-18 08:00AM | 231705 | OA1244 | Rural Short | Replace Condemned SUB Pole @ SUB 10915 | 14 | 450 | 6300 | 0.0070379 | 1.564e-05
2013-06-18 08:00AM | 231804 | 27446 | Rural Short | Augment 4 bays of O/H LV mains. | 29 | 510 | 14790 | 0.016522 | 3.2396e-05
2013-06-18 08:00AM | 230118 | 35762 | Urban | replace abs with new LBS | 19 | 510 | 9690 | 0.010825 | 2.1225e-05
2013-06-18 08:00AM | 232290 | 9029 | Urban | REPLACE LV X-ARM @ POLE # 248 | 37 | 330 | 12210 | 0.01364 | 4.1333e-05
2013-06-18 08:00AM | 232340 | C893 | Urban | REPLACE RAGBOLT@ COLUMN # 388 | 28 | 480 | 13440 | 0.015014 | 3.1279e-05
2013-06-18 08:30AM | 231961 | 8801 | Rural Short | Install new pole 853619. Install 4 bays of 150mm HVABC from pole 212 to 767654 | 38 | 420 | 15960 | 0.017829 | 4.2451e-05
2013-06-18 08:30AM | 232477 | MVH2 | Rural Short | String in 33 kV conductor between poles 3KO028 (Pole 186) to 816659 (Pole 192) | 22 | 480 | 10560 | 0.011797 | 2.4577e-05
2013-06-18 08:30AM | 232584 | RBA2 | Rural Short | Augment a section of O/H mains to CCT | 19 | 450 | 8550 | 0.0095514 | 2.1225e-05
2013-06-18 08:30AM | 232648 | W126 | Rural Short | Replace LV crossarm | 45 | 240 | 10800 | 0.012065 | 5.027e-05
2013-06-18 08:30AM | 233041 | UNJ2 | Urban | MandR HOLEC SWITCHGEAR and RETRO SUB Change poles and augment | 232 | 360 | 83520 | 0.093302 | 0.00025917
2013-06-18 08:30AM | 233332 | APE2 | Urban | REPLACE LV U/G CABLES | 108 | 330 | 35640 | 0.039814 | 0.00012065
2013-06-18 09:00AM | 220978 | CLC2 | Urban | INSTALL NEW ABS 122822 and NEW TYPE 3 LBS 122823 also REMOVE ABS 30538 | 11 | 390 | 4290 | 0.0047924 | 1.2288e-05
2013-06-18 09:00PM | 221258 | CT1270 | Urban | To Connect 11KV Cable Earth Screen To The HV Earth @ Padmount Sub 9580 Hurley St Campbelltown.(Library) | 1 | 179 | 179 | 0.00019996 | 1.1171e-06
2013-06-18 09:00PM | 231278 | KMD2 | Urban | REPLACE POLES 4KD458 4KD762 and 4KD460 | 109 | 450 | 49050 | 0.054795 | 0.00012177
2013-06-18 09:30AM | 223701 | ULB2 | Urban | Replace poles 2RP258 ( ABS 41704 ) and 2RP255.South St ULLADULLA. | 150 | 300 | 45000 | 0.05027 | 0.00016757
2013-06-18 10:00AM | 221177 | CT1228 | Urban | To Connect 11KV Cable Earth Screen To The HV Earth @ Padmount Sub 25705 Hyde Pde Campbelltown. | 2 | 180 | 360 | 0.00040216 | 2.2342e-06
2013-06-19 08:00AM | 230407 | L947 | Rural Short | replace 3 bays of hv abc change over pole | 6 | 510 | 3060 | 0.0034184 | 6.7027e-06
2013-06-19 08:00AM | 231927 | L582 | Rural Short | REMOVE POLES AUGMENT MAINS AND INSTALL VIBRATION DAMPERS | 5 | 450 | 2250 | 0.0025135 | 5.5856e-06
2013-06-19 08:00AM | 232750 | GG1295 | Rural Short | INSTALL 7 NEW HV POLES AND ASSOCIATED CONDUCTORS. | 7 | 540 | 3780 | 0.0042227 | 7.8198e-06
2013-06-19 08:00AM | 227947 | FF1239 | Urban | HV OH augmentation and ABS installation. | 106 | 480 | 50880 | 0.056839 | 0.00011841
2013-06-19 08:00AM | 227948 | FF1239 | Urban | Isolate LV mains for HV OH mains augmentation and ABS installation. | 51 | 480 | 24480 | 0.027347 | 5.6973e-05
2013-06-19 08:00AM | 228192 | 35325 | Urban | Change ex hardex const's to opgw const's + roller up hardex for future augment. | 52 | 480 | 24960 | 0.027883 | 5.809e-05
2013-06-19 08:00AM | 230650 | 35571 | Urban | REPLACE 11KV O/H MAINS WITH 11KV UG CABLES. | 32 | 480 | 15360 | 0.017159 | 3.5748e-05
2013-06-19 08:00AM | 232074 | 5496 | Urban | HV Augmentation | 112 | 480 | 53760 | 0.060056 | 0.00012512
2013-06-19 08:00AM | 232075 | 5496 | Urban | Replace Pole and Augment Hv OH MAins | 112 | 480 | 53760 | 0.060056 | 0.00012512
2013-06-19 08:00AM | 232437 | C899 | Urban | REPLACE RAGBOLT@ COLUMN # 11071 | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2013-06-19 08:00AM | 232527 | T884 | Urban | Install new pad sub 29911 and section of high voltage cable and connect to the existing networkAlso relocate cable in sub 29912 from sw 94603 to sw 94602 | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-06-19 08:00AM | 232792 | 55890 | Urban | LV X-ARM CHANGES @ CYRIL PL BAULKHAM HILLS POLE 1736 AND PETER ST BAULKHAM HILLS POLE 1735 | 10 | 240 | 2400 | 0.0026811 | 1.1171e-05
2013-06-19 08:00AM | 232873 | 8610 | Urban | LV X-ARM CHANGE @ POLE 1586 | 7 | 150 | 1050 | 0.001173 | 7.8198e-06
2013-06-19 08:00AM | 232960 | CS1276 | Urban | Repair QOS hot joint | 15 | 420 | 6300 | 0.0070379 | 1.6757e-05
2013-06-19 08:00AM | 233099 | CD1260 | Urban | LIMITED DISTRICT SWITCHINGTo allow staff to Retrofit Sub 11749 Remove 1 bay 11kv OH Mains and replace condemned pole 509 Macquarie Ave Camden | 59 | 480 | 28320 | 0.031637 | 6.591e-05
2013-06-19 08:30AM | 221558 | BWH2 | Rural Short | Replace Hv Cross Arm and Install DOF's | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2013-06-19 08:30AM | 231972 | 61617 | Rural Short | Change pole 128 to new pole 878940. | 50 | 420 | 21000 | 0.02346 | 5.5856e-05
2013-06-19 08:30AM | 230189 | PCB2 | Urban | Replace Condenmed Poles 3TJ294 and 209432 | 58 | 420 | 24360 | 0.027213 | 6.4793e-05
2013-06-19 08:30AM | 232544 | RW1281 | Urban | Change out poles 3XK138 (234) to 3XK137 (235) and Poles 3XK168 (222) 3XK167 (223). | 35 | 480 | 16800 | 0.018768 | 3.9099e-05
2013-06-19 10:30AM | 232877 | 5872 | Urban | LV X-ARM CHANGE @ POLE | 37 | 180 | 6660 | 0.00744 | 4.1333e-05
2013-06-19 12:30PM | 232796 | 8737 | Urban | LV X-ARM CHANGE POLE 403 | 10 | 120 | 1200 | 0.0013405 | 1.1171e-05
2013-06-20 01:00AM | 232268 | CT1229 | Urban | To Connect Cable Sheath Earth To H/V Earth @ Indoor Sub 24432 (SW-49847) Macarthur Square Shopping Centre. | 1 | 210 | 210 | 0.0002346 | 1.1171e-06
2013-06-20 08:00AM | 224581 | 27446 | Rural Short | Augment 4 bays of O/H HV mains to 7/4.5 AAC. | 106 | 510 | 54060 | 0.060392 | 0.00011841
2013-06-20 08:00AM | 224601 | 27446 | Rural Short | Augment 4 bays of O/H HV mains to 7/4.5 AAC. | 28 | 510 | 14280 | 0.015952 | 3.1279e-05
2013-06-20 08:00AM | 230269 | X881 | Rural Short | Erect recloser 123391 and associated USL's 123389 and 123390 to be commissioned @ a later date | 8 | 480 | 3840 | 0.0042897 | 8.937e-06
2013-06-20 08:00AM | 231813 | 57448 | Rural Short | INSTALL ABSSTAND and REMOVE POLES | 3 | 480 | 1440 | 0.0016087 | 3.3514e-06
2013-06-20 08:00AM | 232707 | HKA2 | Rural Short | 11KV ISOLATION for POLE REPLACEMENT on 33KV FDR 7520 and AUGMENT 33KV FDR and INSTALL OPGW EARTHWIRE. | 204 | 480 | 71040 | 0.07936 | 0.00022789
2013-06-20 08:00AM | 232815 | WD1221 | Rural Short | LV switching to alow the scope of works to be completed as per DNR232790. | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2013-06-20 08:00AM | 233818 | X879 | Rural Short | LIMITED DISTRICT SWITCHINGTo allow staff to replace Poles at Phillip St Leppington | 17 | 480 | 8160 | 0.0091157 | 1.8991e-05
2013-06-20 08:00AM | 229715 | L526 | Urban | Install New Air Break Switches | 129 | 480 | 61920 | 0.069172 | 0.00014411
2013-06-20 08:00AM | 229716 | 41535 | Urban | New ABS Installation | 43 | 480 | 20640 | 0.023057 | 4.8036e-05
2013-06-20 08:00AM | 230268 | L526 | Urban | Install New Air Break Switches | 30 | 480 | 14400 | 0.016087 | 3.3514e-05
2013-06-20 08:00AM | 230544 | 8689 | Urban | Hv Upgrade | 39 | 480 | 18720 | 0.020912 | 4.3568e-05
2013-06-20 08:00AM | 232441 | C899 | Urban | REPLACE RAGBOLT@ COLUMN # 11084 | 15 | 480 | 7200 | 0.0080433 | 1.6757e-05
2013-06-20 08:00AM | 233179 | C890 | Urban | FIT NEW PILLAR @ COLUMN # 7474 | 11 | 480 | 5280 | 0.0058984 | 1.2288e-05
2013-06-20 08:00AM | 233836 | 1962 | Urban | Replace Pole | 24 | 420 | 10080 | 0.011261 | 2.6811e-05
2013-06-20 08:30AM | 220591 | MVF2 | Rural Short | Repalce Hv Cross Arms and Install DOF's | 57 | 390 | 22230 | 0.024834 | 6.3676e-05
2013-06-20 08:30AM | 232495 | SHJ2 | Rural Short | REPLACE X PLs 4DX013 4DX017 4DX020 4GX020 REPLACE HV X ARMS PLs 4DX039 4DX036 4DX040 4DX041 4DX042 RETRO FIT SUBS 40808 43479 | 7 | 360 | 2520 | 0.0028151 | 7.8198e-06
2013-06-20 08:30AM | 231577 | 49915 | Urban | AUGMENT 11KV O/H MAINS AND REPLACE USL 7109. REPLACE TRF AND RETRO-FIT SUB 4938 | 19 | 450 | 8550 | 0.0095514 | 2.1225e-05
2013-06-20 08:30AM | 231792 | BLD2 | Urban | Replace Condemned Poles 3KY083 3KY084 and ABS pole 71011 | 179 | 450 | 80550 | 0.089984 | 0.00019996
2013-06-20 08:30AM | 232121 | SZ1152 | Urban | Replace condemned pole 224 | 62 | 420 | 26040 | 0.02909 | 6.9261e-05
2013-06-20 08:30AM | 232614 | 8610 | Urban | Pole Change | 37 | 390 | 14430 | 0.01612 | 4.1333e-05
2013-06-20 08:30AM | 232854 | BWC2 | Urban | Replace Condemned Pole 3T1735 and ABS 50775 | 27 | 450 | 12150 | 0.013573 | 3.0162e-05
2013-06-20 08:30AM | 233109 | C896 | Urban | Replace Consac Cable with XLPE | 31 | 330 | 10230 | 0.011428 | 3.4631e-05
2013-06-20 09:00AM | 227525 | ULJ2 | Rural Short | Install New ABS 96559Croobyar Rd MILTON | 38 | 360 | 13680 | 0.015282 | 4.2451e-05
2013-06-20 09:00AM | 232707 | HKA2 | Rural Short | 11KV ISOLATION for POLE REPLACEMENT on 33KV FDR 7520 and AUGMENT 33KV FDR and INSTALL OPGW EARTHWIRE. | 92 | 120 | 17760 | 0.01984 | 0.00010278
2013-06-20 09:00AM | 231163 | CD1267 | Urban | Lower LV X arm | 23 | 360 | 8280 | 0.0092498 | 2.5694e-05
2013-06-20 09:00AM | 231371 | A317 | Urban | TERMINATE HV CABLE BETWEEN SUBS 29129 and 24501 | 44 | 360 | 15840 | 0.017695 | 4.9153e-05
2013-06-20 09:30AM | 230884 | BDG2 | Rural Short | Replace pole / Install New ABS / Relocate HV ConductorsMeroo Rd BOMADERRY. | 140 | 330 | 46200 | 0.051611 | 0.0001564
2013-06-21 01:00PM | 226182 | L543 | Urban | REPLACE HV SW GR SAFELINK FOR SAFELINK SUB 23558 | 79 | 30 | 2370 | 0.0026476 | 8.8252e-05
2013-06-21 08:00AM | 230516 | 25401 | Rural Short | change sub pole and augment 3 bays of hv mains and replace abs 6773 with new abs 86485 | 16 | 510 | 8160 | 0.0091157 | 1.7874e-05
2013-06-21 08:00AM | 230517 | 25401 | Rural Short | isolate lv for hv augment | 4 | 510 | 2040 | 0.0022789 | 4.4685e-06
2013-06-21 08:00AM | 232652 | R260 | Rural Short | Stand poles | 115 | 450 | 51750 | 0.057811 | 0.00012847
2013-06-21 08:00AM | 227949 | 5498 | Urban | HV OH augmentation. | 211 | 480 | 101280 | 0.11314 | 0.00023571
2013-06-21 08:00AM | 230035 | RW1255 | Urban | Replace 6 poles and HV constructions. Replace DOFs on 4 SUBs.Replace HV X-arms on non-replaced poles within HV isolation. | 29 | 480 | 13920 | 0.01555 | 3.2396e-05
2013-06-21 08:00AM | 232396 | C890 | Urban | Replace ragbolt @ coloumn # 11787 | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-06-21 08:00AM | 232447 | C899 | Urban | REPLACE RAGBOLT@ COLUMN # 11079 | 13 | 480 | 6240 | 0.0069708 | 1.4523e-05
2013-06-21 08:00AM | 232564 | 46752 | Urban | Augment OH conductor | 80 | 480 | 38400 | 0.042897 | 8.937e-05
2013-06-21 08:00AM | 233653 | 5869 | Urban | Change LV hardware to poles 2126 2125 2113 and 2110. | 40 | 390 | 15600 | 0.017427 | 4.4685e-05
2013-06-21 08:30AM | 232685 | L946 | Rural Short | Install safety chain @ sub 19609 | 3 | 120 | 360 | 0.00040216 | 3.3514e-06
2013-06-21 08:30AM | 233128 | P608 | Rural Short | Augment mains from pole 822253 to 822256 822259 to 822260 and make repairs to earthing at substation 28970. | 29 | 450 | 13050 | 0.014578 | 3.2396e-05
2013-06-21 08:30AM | 232146 | SZ1322 | Urban | Replace condemned pole 372 | 10 | 390 | 3900 | 0.0043568 | 1.1171e-05
2013-06-21 08:30AM | 232604 | HBB2 | Urban | Remove Dead tree near HV mains adjacent to pole 3JY352 | 99 | 180 | 17820 | 0.019907 | 0.00011059
2013-06-21 08:30AM | 232615 | 17067 | Urban | Pole Change | 9 | 390 | 3510 | 0.0039211 | 1.0054e-05
2013-06-21 09:00AM | 233164 | SN1271 | Urban | INSTALL 4 NEW LV PILLARS | 9 | 300 | 2700 | 0.0030162 | 1.0054e-05
2013-06-21 10:00AM | 232699 | S786 | Rural Short | Replace LV arm @ pole 55 | 7 | 270 | 1890 | 0.0021114 | 7.8198e-06
2013-06-21 10:00AM | 232096 | B764 | Urban | REPAIR SAFELINK INTERLOCK AND FAULTY TEST INDICATORS | 420 | 300 | 126000 | 0.14076 | 0.00046919
2013-06-22 08:00AM | 231563 | 27446 | Rural Short | Install new pole sub 32527 | 24 | 540 | 12960 | 0.014478 | 2.6811e-05
2013-06-22 12:30PM | 232734 | S737 | Rural Short | Stand new 33kV concrete poles Transfer exisiting network over to new poles Run OPGW Rope Pull 33kV conductor and tie in Install temp USL A0850 | 114 | 90 | 5130 | 0.0057308 | 0.00012735
2013-06-23 03:00PM | 232469 | 35703 | Urban | RESET PILLAR # 30164 - SPRINGWOOD AVE SPRINGWOOD | 56 | 240 | 13440 | 0.015014 | 6.2559e-05
2013-06-23 06:00PM | 232870 | T899 | Urban | Isolate Hv cable for State Rail project | 1 | 5 | 5 | 5.5856e-06 | 1.1171e-06
2013-06-23 07:00AM | 229690 | WQ1275 | Urban | ABS MAINTENANCE ON SW F195 DAVIES RD WETHERILL PARK | 6 | 390 | 2340 | 0.0026141 | 6.7027e-06
2013-06-23 09:00AM | 233115 | S737 | Rural Short | Stand new 33kV concrete poles Transfer exisiting network over to new poles Run OPGW rope Pull 33kV conductor and tie in | 126 | 120 | 7560 | 0.0084454 | 0.00014076
2013-06-23 09:30AM | 232689 | 4870 | Urban | Install new LV fuse strip at sub 5710 | 11 | 270 | 2970 | 0.0033178 | 1.2288e-05
2013-06-23 09:30AM | 233030 | F603 | Urban | LV Pole change | 3 | 270 | 810 | 0.00090487 | 3.3514e-06
2013-06-23 11:00AM | 233115 | S737 | Rural Short | Stand new 33kV concrete poles Transfer exisiting network over to new poles Run OPGW rope Pull 33kV conductor and tie in | 126 | 60 | 3780 | 0.0042227 | 0.00014076
2013-06-24 08:00AM | 232539 | L588 | Rural Short | Replace pole 229. Install new 63kVA pole sub 32279 on new pole 873192 | 24 | 480 | 11520 | 0.012869 | 2.6811e-05
2013-06-24 08:00AM | 225986 | 35571 | Urban | HV OH augmentation and 1 pole replacement. | 112 | 480 | 53760 | 0.060056 | 0.00012512
2013-06-24 08:00AM | 225987 | 35571 | Urban | Isolate LV mains for HV OH augmentation and pole replacement. | 27 | 480 | 12960 | 0.014478 | 3.0162e-05
2013-06-24 08:00AM | 232633 | GV1245 | Urban | Install new pole | 6 | 420 | 2520 | 0.0028151 | 6.7027e-06
2013-06-24 08:00AM | 233877 | J481 | Urban | Remove redundant LV and SL | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-06-24 08:30AM | 229870 | 35767 | Urban | Hv Augmentation with New ABS's | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2013-06-24 08:30AM | 230834 | 35767 | Urban | Hv Augmentation with New ABS's | 10 | 480 | 4800 | 0.0053622 | 1.1171e-05
2013-06-24 08:30AM | 232776 | 7972 | Urban | Project Job | 8 | 390 | 3120 | 0.0034854 | 8.937e-06
2013-06-24 12:00PM | 232151 | L588 | Rural Short | RETROFIT SUB 18675 | 12 | 210 | 2520 | 0.0028151 | 1.3405e-05
2013-06-25 07:00AM | 232525 | 53314 | Urban | Stand poles and tie in mains.Head sub pole 8203 to 11kV.Install live line links adj pole sub 8203. 11kV north side | 1 | 600 | 600 | 0.00067027 | 1.1171e-06
2013-06-25 07:00AM | 232641 | 54649 | Urban | Straighten ploes 819476 and 819478 and retension mains | 4 | 570 | 2280 | 0.002547 | 4.4685e-06
2013-06-25 08:00AM | 233079 | 25739 | Rural Short | STRING ONE BAY OF HV O/H MAINS TO COMPLETE HV CIRCUIT going to pm SUB 28904 TERMINATE HV CABLE @ SW 85269PM SUB 28904 | 87 | 540 | 46980 | 0.052482 | 9.7189e-05
2013-06-25 08:00AM | 233316 | 8637 | Rural Short | 11kV switching to allow the scope of works to be completed as per DNR 233314. | 94 | 480 | 45120 | 0.050404 | 0.00010501
2013-06-25 08:00AM | 233655 | 87222 | Rural Short | RETROFIT SUB 16728 | 2 | 450 | 900 | 0.0010054 | 2.2342e-06
2013-06-25 08:00AM | 233657 | 87222 | Rural Short | RETROFIT SUB 16866 | 1 | 450 | 450 | 0.0005027 | 1.1171e-06
2013-06-25 08:00AM | 233672 | 25739 | Rural Short | 1Augment TWO BAYS OF HV O/H MAINSand INSTALL NEW ABS122815 | 12 | 540 | 6480 | 0.0072389 | 1.3405e-05
2013-06-25 08:00AM | 227238 | 5464 | Urban | REMOVE U/G CABLE FROM SW 38768 SUB 22897 TO UGOH POLE 19. INSTALL NEW U/G CABLE FROM SW L239 SUB 4737 TO UGOH POLE 19 | 16 | 450 | 7200 | 0.0080433 | 1.7874e-05
2013-06-25 08:00AM | 229589 | MR2292 | Urban | FAULT FIND + LOCATE HV CABLE FAULT BETWEEN SW 26029 SUB 20439 and SW 34130 SUB 20437 | 144 | 480 | 69120 | 0.077215 | 0.00016087
2013-06-25 08:00AM | 231530 | 9032 | Urban | Install new pole 860368+ Replace pole 413 with new pole 879304+ Install 2x new ABS+ Install new 63A DOF's+ Augment 1 bay of HV mains between pole 417 and pole 437 Ulm rd to 7.45 AAC. | 34 | 510 | 17340 | 0.019371 | 3.7982e-05
2013-06-25 08:00AM | 232337 | C900 | Urban | REPLACE COLUMN # 1381 | 17 | 240 | 4080 | 0.0045578 | 1.8991e-05
2013-06-25 08:00AM | 233093 | 49341 | Urban | Replace LV x-arm | 11 | 180 | 1980 | 0.0022119 | 1.2288e-05
2013-06-25 08:00AM | 233650 | 55888 | Urban | LV x-arm replacements | 18 | 360 | 6480 | 0.0072389 | 2.0108e-05
2013-06-25 08:30AM | 232723 | S786 | Rural Short | Replace LV arms and box in arm @ sub 4676 | 10 | 420 | 4200 | 0.0046919 | 1.1171e-05
2013-06-25 08:30AM | 233646 | 87222 | Rural Short | RETROFIT SUB 16865 | 1 | 420 | 420 | 0.00046919 | 1.1171e-06
2013-06-25 08:30AM | 233275 | WRG2 | Urban | REPLACE POLES 1G0314 1G0315 | 20 | 270 | 5400 | 0.0060324 | 2.2342e-05
2013-06-25 09:00AM | 233580 | 35405 | Urban | INSTALL NEW L/V PILLLAR 123027 | 83 | 360 | 29880 | 0.03338 | 9.2721e-05
2013-06-25 09:00AM | 233775 | FF1206 | Urban | Cross Arm Change | 10 | 360 | 1800 | 0.0020108 | 1.1171e-05
2013-06-25 10:30AM | 232620 | 8634 | Rural Short | LV Interuptions to allow 30 hour Test | 208 | 60 | 12480 | 0.013942 | 0.00023236
2013-06-25 10:30AM | 232341 | C893 | Urban | REPLACE COLUMN # 388 | 28 | 240 | 6720 | 0.007507 | 3.1279e-05
2013-06-25 11:30AM | 233098 | 55866 | Urban | Change LV link arm | 32 | 180 | 5760 | 0.0064346 | 3.5748e-05
2013-06-25 12:30PM | 233065 | 55880 | Urban | Change LV X-arm | 11 | 150 | 1650 | 0.0018432 | 1.2288e-05
2013-06-26 06:00AM | 232947 | 35523 | Urban | Install new sub 32667 via 2 x STJ's | 1 | 720 | 720 | 0.00080433 | 1.1171e-06
2013-06-26 08:00AM | 230541 | 8637 | Rural Short | change 2 poles and install 2 new ABS | 15 | 510 | 7650 | 0.008546 | 1.6757e-05
2013-06-26 08:00AM | 230552 | 8637 | Rural Short | isolate lv for hv pole changes | 7 | 510 | 3570 | 0.0039881 | 7.8198e-06
2013-06-26 08:00AM | 232207 | X802 | Rural Short | RETROFIT SUB 16789 | 1 | 450 | 450 | 0.0005027 | 1.1171e-06
2013-06-26 08:00AM | 233350 | 57448 | Rural Short | REPAIR STRANDED CONDUCTOR INSTALL KAON FUSE SAVER AND RETROFIT SUBS | 31 | 450 | 13950 | 0.015584 | 3.4631e-05
2013-06-26 08:00AM | 229480 | 25741 | Urban | augment section of Hv mains to 7/4.50 aacREMOVE USL 3244 | 40 | 480 | 19200 | 0.021449 | 4.4685e-05
2013-06-26 08:00AM | 229481 | 25741 | Urban | AUGMENT SECTION OF O/H HV TO 7/4.50 AAC REMOVE USL 3244 | 22 | 480 | 10560 | 0.011797 | 2.4577e-05
2013-06-26 08:00AM | 231631 | C900 | Urban | REPAIR CABLE FAULT and REPLACE COLUMN # 1372 | 44 | 480 | 21120 | 0.023594 | 4.9153e-05
2013-06-26 08:00AM | 232502 | S785 | Urban | REPLACE LV X-ARMS @ POLE # 403 | 7 | 480 | 3360 | 0.0037535 | 7.8198e-06
2013-06-26 08:00AM | 233136 | W123 | Urban | Replace Poles + Install DOFs + Augment HV conductor | 78 | 480 | 37440 | 0.041825 | 8.7135e-05
2013-06-26 08:00AM | 233236 | 5878 | Urban | Replace LV link pole 1984 and change LV arm pole 1980 | 58 | 390 | 22620 | 0.025269 | 6.4793e-05
2013-06-26 09:00AM | 232001 | D841 | Urban | REPLACE CONDEMNED POLE 1736 | 22 | 360 | 7920 | 0.0088476 | 2.4577e-05
2013-06-26 09:00AM | 233618 | RW1281 | Urban | Rectify service Encroachment at Number 20 | 1 | 240 | 240 | 0.00026811 | 1.1171e-06
2013-06-26 09:30AM | 232760 | J512 | Urban | To Replace Rusted S/L Column 30740 Newtown Rd Glenfield. | 19 | 120 | 2280 | 0.002547 | 2.1225e-05
2013-06-26 09:30AM | 233993 | 1133 | Urban | Repair cable in Streetlight Column | 3 | 390 | 1170 | 0.001307 | 3.3514e-06
2013-06-27 07:00AM | 233325 | 8637 | Rural Short | 11kV switching to allow the scope of works to be completed as per DNR233323. | 21 | 600 | 12600 | 0.014076 | 2.346e-05
2013-06-27 08:00AM | 229512 | X881 | Rural Short | REPLACE ABS 2296 WITH AUTO LBS 122993 (PROTECTION TO COMMISSION @A LATER DATE) | 83 | 480 | 39840 | 0.044506 | 9.2721e-05
2013-06-27 08:00AM | 230411 | L946 | Rural Short | replace 4 bays of hv abc beyond sub 26947 | 6 | 510 | 3060 | 0.0034184 | 6.7027e-06
2013-06-27 08:00AM | 232372 | C890 | Urban | Remove condemed coloumn and install new pillar @ coloumn's # 9502 and 9503 | 2 | 480 | 960 | 0.0010724 | 2.2342e-06
2013-06-27 08:00AM | 233645 | D830 | Urban | REPLACE L/V SW GEAR PM SUB 5331 | 93 | 420 | 39060 | 0.043635 | 0.00010389
2013-06-27 08:30AM | 232532 | L942 | Rural Short | Replace al HV and LV arms @ pole 149 | 3 | 420 | 1260 | 0.0014076 | 3.3514e-06
2013-06-27 09:00AM | 233905 | 52238 | Urban | LV Cable Fault | 18 | 300 | 5400 | 0.0060324 | 2.0108e-05
2013-06-27 09:30AM | 231330 | ULH2 | Urban | replace LV pole Wallace st Mollymook | 14 | 330 | 4620 | 0.0051611 | 1.564e-05
2013-06-28 01:00PM | 232707 | HKA2 | Rural Short | 11KV ISOLATION for POLE REPLACEMENT on 33KV FDR 7520 and AUGMENT 33KV FDR and INSTALL OPGW EARTHWIRE. | 296 | 120 | 17760 | 0.01984 | 0.00033067
2013-06-28 08:00AM | 233399 | X492 | Rural Long | INSTALL KAON FUSE SAVERS | 26 | 450 | 11700 | 0.01307 | 2.9045e-05
2013-06-28 08:00AM | 229890 | WD1251 | Rural Short | Job 1 - Augment 4 bays of 7/4.5 AL from pole 829724 to pole 873283. Replace poles 230 and 231.Job 2 - Install new ABS 91132 + pole. | 90 | 510 | 45900 | 0.051276 | 0.00010054
2013-06-28 08:00AM | 230580 | 25401 | Rural Short | augment lv mains at sub 3482 | 15 | 510 | 7650 | 0.008546 | 1.6757e-05
2013-06-28 08:00AM | 231857 | NG1299 | Rural Short | Augment HV OH conductor | 78 | 510 | 39780 | 0.044439 | 8.7135e-05
2013-06-28 08:00AM | 229717 | 41535 | Urban | Hv Augmentation | 110 | 480 | 52800 | 0.058984 | 0.00012288
2013-06-28 08:00AM | 230813 | 41535 | Urban | HV Upgrade | 112 | 480 | 53760 | 0.060056 | 0.00012512
2013-06-28 08:00AM | 232103 | 2810 | Urban | Replace one pole augment one bay of HV OH mains and install new DOF's. | 130 | 480 | 62400 | 0.069708 | 0.00014523
2013-06-28 08:00AM | 232440 | C899 | Urban | REPLACE COLUMN # 11071 | 3 | 180 | 540 | 0.00060324 | 3.3514e-06
2013-06-28 08:00AM | 233950 | 25784 | Urban | Isolate LV to bond in new Pillar 124869 | 15 | 210 | 3150 | 0.0035189 | 1.6757e-05
2013-06-28 08:00AM | 233992 | M389 | Urban | Change to LV circuit. | 8 | 420 | 3360 | 0.0037535 | 8.937e-06
2013-06-28 08:30AM | 231342 | BLC2 | Urban | Replace Condemned poles 3PD759 and 3PD760 | 59 | 360 | 21240 | 0.023728 | 6.591e-05
2013-06-28 08:30AM | 234017 | S674 | Urban | REPLACE POLE 800983 | 62 | 450 | 27900 | 0.031168 | 6.9261e-05
2013-06-28 09:00AM | 231279 | NA1266 | Urban | Replace pole 1YC336 - S/S 50786. | 70 | 360 | 25200 | 0.028151 | 7.8198e-05
2013-06-28 09:30AM | 232443 | C899 | Urban | REPLACE COLUMN # 11084 | 15 | 180 | 2700 | 0.0030162 | 1.6757e-05
2013-06-28 11:00AM | 232454 | C899 | Urban | REPLACE COLUMN # 11079 | 12 | 210 | 2520 | 0.0028151 | 1.3405e-05
2013-06-28 11:00AM | 233615 | S785 | Urban | REPLACE LV X-ARM @ POLE # 428 | 53 | 300 | 15900 | 0.017762 | 5.9207e-05
2013-06-29 06:30AM | 226937 | 7977 | Urban | RETROFIT ON DOF 9947 and REPLACE HV CUBICAL END @ SUB 5720 | 2 | 450 | 900 | 0.0010054 | 2.2342e-06
2013-06-29 07:00AM | 233730 | 25744 | Rural Short | Change to LV circuit. | 1 | 540 | 540 | 0.00060324 | 1.1171e-06
2013-06-29 07:00AM | 233257 | 48189 | Urban | establish new pad sub 27228 | 8 | 570 | 4560 | 0.0050941 | 8.937e-06
2013-06-29 08:00AM | 233018 | KC1288 | Rural Short | STAND NEW POLE TRANSFERE EX AERIALS | 29 | 420 | 12180 | 0.013607 | 3.2396e-05
2013-06-29 08:00AM | 233020 | J481 | Urban | (1). ID and Spike HV cable between Sw M842 in PM 13132 and Sw M845 in PM 13130. (2). Unbond HV cable from Sw M842 in PM 13132. Unbond HV cable from Sw M845 in PM 13130 and abandon. Remove PM 13130 | 1 | 480 | 480 | 0.00053622 | 1.1171e-06
2013-06-29 08:00AM | 233185 | B748 | Urban | Augment OH HV conductor | 102 | 480 | 48960 | 0.054694 | 0.00011395
2013-06-29 12:00PM | 233115 | S737 | Rural Short | Stand new 33kV concrete poles Transfer exisiting network over to new poles Run OPGW rope Pull 33kV conductor and tie in | 126 | 120 | 7560 | 0.0084454 | 0.00014076
2013-06-30 06:00AM | 229726 | A348 | Urban | DISTRIBUTION EARTH REFURB AT SUB 24030 HUNTINGDALE AVE CABRAMATTA | 50 | 210 | 10500 | 0.01173 | 5.5856e-05
2013-06-30 06:00AM | 231601 | A348 | Urban | REPLACE POT HEAD AND REPLACE DOF 6006SUB 4447 CUTLER RD LANSVALE | 1 | 540 | 540 | 0.00060324 | 1.1171e-06
2013-06-30 07:00AM | 230008 | 1962 | Urban | REPAIR HV CABLE FAULT BETWEEN SW 46611 SUB 23840 and SWE694 SUB 8576 + REPLACE HV SW GR SUB 23840 | 1 | 540 | 540 | 0.00060324 | 1.1171e-06
2013-06-30 07:00AM | 231255 | 17061 | Urban | Remove USL R638 and rebond pole.Replace HV arm. | 2 | 420 | 840 | 0.00093838 | 2.2342e-06
2013-06-30 08:00AM | 227874 | F602 | Urban | Change const's + augment ex hardex [earth wire] to opgw + clip in | 352 | 480 | 168960 | 0.18875 | 0.00039323
2013-06-30 08:30AM | 233027 | BLE2 | Urban | AUGMENT MAINS | 34 | 240 | 8160 | 0.0091157 | 3.7982e-05
2013-06-30 09:30AM | 223625 | ULF2 | Urban | Replace poles 2RP020 ( ABS 41700 ) and 2RP005Deering st ULLADULLA | 31 | 330 | 10230 | 0.011428 | 3.4631e-05
2013-07-26 09:00AM | 232054 | BLD2 | Urban | ISOLATE 11KV FDR BLD2 FOR CLEARANCE ONLY | 120 | 30 | 3600 | 0.0040216 | 0.00013405
Contents

## 5b. Network data feeder
Endeavour Energy
Network data - Feeder Reliability
2012-13
The information in templates 5a,b,c,d is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Annual Feeder Reliability Data
Feeder ID / name | Geographical description of feeder | Feeder classification | Number of distribution customers (average) | Length of distribution lines - high voltage - overhead | Length of distribution lines - high voltage - underground | Maximum demand (MW) | Energy not supplied (unplanned) (MWh) | Energy not supplied (planned) (MWh) | Number of unplanned outages | Unplanned customer minutes off-supply (including excluded events and MEDs) | Unplanned customer minutes off-supply (after removing excluded events and MED) | Unplanned interruptions (SAIFI) (including excluded events and MEDs) | Unplanned interruptions (SAIFI) (after removing excluded events and MEDs) | Number of planned outages | Planned customer minutes off-supply | Planned interruptions (SAIFI)
10241 | Mort St | Urban | 1143 | 10.1547 | 0.1988 | 174.53 |  |  | 25 | 0.72532 | 0.72532 | 0.019823 | 0.019823 | 25 | 0.0076523 | 0.0076523
10242 | Bowling Green Av | Urban | 1293 | 8.5343 | 0.80059 | 175.18 |  |  | 144 | 4.4537 | 4.4537 | 0.10679 | 0.10679 | 144 | 0.0064346 | 0.0064346
10244 | Narrow Neck Rd | Rural Short | 909 | 21.7854 | 3.1204 | 111.96 |  |  | 700 | 46.3603 | 46.3603 | 0.28269 | 0.28269 | 700 | 0.056079 | 0.056079
10245 | Barton St + Aux No 1 | Rural Short | 878 | 9.8031 | 0.50668 | 99.01 |  |  | 144 | 5.7607 | 5.7607 | 0.050378 | 0.050378 | 144 | 0.013231 | 0.013231
10247 | Parke St + Aux No 2 | Urban | 456 |  | 2.4932 | 145.91 |  |  | 18 | 0.1484 | 0.1484 | 0.0031838 | 0.0031838 | 18 | 0.00020108 | 0.00020108
10248 | Glenview St | Urban | 1123 | 6.2622 | 2.1423 | 149.19 |  |  | 12 | 0.28019 | 0.39937 | 0.0076478 | 0.0076478 | 12 | 0.00093838 | 0.00093838
10250 | Camp St | Urban | 958 | 6.8233 | 5.0227 | 172.75 |  |  | 25 | 1.8365 | 1.8365 | 0.017019 | 0.017019 | 25 | 0.0027928 | 0.0027928
10251 | Cascade St | Urban | 1384 | 8.6037 | 0.88319 | 195.34 |  |  | 128 | 8.0931 | 8.0931 | 0.086921 | 0.086921 | 128 | 0.0025023 | 0.0025023
10286 | Arthur Phillip Dr + Aux No 1 | Rural Short | 446 | 18.3731 | 3.1922 | 94.76 |  |  | 20 | 0.62384 | 0.62384 | 0.0050829 | 0.0050829 | 20 | 0.00033514 | 0.00033514
10287 | Pecks Rd | Urban | 929 | 6.6219 | 1.1118 | 225.03 | [7 empty] | 3 | 9.4955e-05 | 9.4955e-05
10289 | Tennyson Rd | Rural Short | 78 | 6.3175 | 0.22138 | 26.16 | [7 empty] | 2 | 3.7982e-05 | 3.7982e-05
10290 | Kurrajong | Rural Short | 111 | 8.44 | 0.539 | 120.83 | [7 empty] | 5 | 7.0379e-05 | 7.0379e-05
1102 | Auto Tube | Urban | 211 | 0.25873 | 1.5143 | 108.81 | [7 empty] | 1 | 1.1171e-06 | 1.1171e-06
1105 | Blaxcell St | Urban | 1138 | 4.1493 | 1.0877 | 202.55 |  |  | 54 | 2.6916 | 2.6916 | 0.028755 | 0.028755 | 54 | 0.0024733 | 0.0024733
1106 | Kirk Av + Aux No 1 | Urban | 1294 | 4.673 | 1.1638 | 179.23 |  |  | 128 | 1.1746 | 1.1746 | 0.0091157 | 0.0091157 | 128 | 0.021502 | 0.021502
1109 | Maubeuge St | Urban | 1474 | 4.4808 | 1.3455 | 199.71 |  |  | 225 | 0.86772 | 0.86772 | 0.011964 | 0.011964 | 225 | 0.014076 | 0.014076
1112 | Campbell Hill Rd | Urban | 1366 | 6.7709 | 1.4314 | 188.85 |  |  | 10 | 0.00090487 | 0.00090487 | 1.1171e-05 | 1.1171e-05 | 10 | 0.0012579 | 0.0012579
1122 | St Johns Rd East | Urban | [11 empty] | 4 | 1.4523e-05 | 1.4523e-05
1123 | Gladstone St | Urban | [11 empty] | 4 | 0.0012154 | 0.0012154
1125 | Avoca Rd | Urban | 1382 | 4.3456 | 2.2121 | 171.94 |  |  | 539 | 3.9109 | 3.9109 | 0.025375 | 0.025375 | 539 | 0.021348 | 0.021348
1129 | Joseph St | Urban | [6 empty] | 5 | 0.021259 | 0.021259 | 0.00035189 | 0.00035189 | 5 | 0.00018768 | 0.00018768
1131 | Mt Pritchard | Urban | [6 empty] | 18 | 0.43064 | 0.43064 | 0.0012601 | 0.0012601 | 18 | 0.0010356 | 0.0010356
1132 | Derby St | Urban | [11 empty] | 1 | 9.8307e-05 | 9.8307e-05
1133 | Peterlee Rd | Urban | 639 | 2.8271 | 1.5976 | 68.74 |  |  | 2 | 0.00058984 | 0.00058984 | 2.2342e-06 | 2.2342e-06 | 2 | 4.4685e-05 | 4.4685e-05
16649 | Sorrell St | Urban | 1763 | 2.4541 | 3.7694 | 159.14 |  |  | 20 | 0.118 | 0.118 | 0.00046919 | 0.00046919 | 20 | 0.00013852 | 0.00013852
16651 | Church St | Urban | 987 |  | 2.4264 | 119.22 |  |  | 1 | 9.9424e-05 | 9.9424e-05 | 1.1171e-06 | 1.1171e-06
16653 | Mason St | Urban | 1620 | 5.2732 | 1.7743 | 214.46 |  |  | 336 | 34.4228 | 30.2887 | 0.31035 | 0.31035 | 336 | 0.0045511 | 0.0045511
16660 | Buller St | Urban | 1317 | 6.161 | 1.4536 | 201.71 |  |  | 80 | 0.84854 | 0.84854 | 0.0031279 | 0.0031279 | 80 | 0.0011618 | 0.0011618
16662 | Villiers St | Urban | 365 |  | 2.2039 | 151.71 | [7 empty] | 2 | 0.00017874 | 0.00017874
16666 | Thomas St | Urban | 1478 | 2.3739 | 4.2733 | 182.24 |  |  | 4 | 0.042361 | 0.042361 | 0.0001698 | 0.0001698 | 4 | 0.00034631 | 0.00034631
17035 | Carpenter St | Urban | 1439 | 5.9427 | 0.5086 | 180.35 |  |  | 64 | 0.41777 | 0.41777 | 0.021574 | 0.021574 | 64 | 0.0052013 | 0.0052013
17037 | Chatsworth Rd | Urban | 622 | 1.2821 | 3.8695 | 132.04 |  |  | 25 | 0.034782 | 0.034782 | 0.0028151 | 0.0028151 | 25 | 0.00039099 | 0.00039099
17038 |  | Urban | 2018 |  |  | 300.85 |  |  | 144 | 1.3929 | 1.3929 | 0.14462 | 0.14462 | 144 | 0.015497 | 0.015497
17039 | Eddie Rd | Urban | 902 | 3.506 | 7.8047 | 284.19 |  |  | 20 | 0.7324 | 0.91508 | 0.014014 | 0.014014 | 20 | 2.2342e-05 | 2.2342e-05
17058 | Spruce St | Urban | 1494 | 2.5919 | 4.8789 | 263.75 |  |  | 8 | 0.67043 | 0.67043 | 0.0066848 | 0.0066848 | 8 | 8.4901e-05 | 8.4901e-05
17061 | Honeman Cl & Cap Bank 1 | Urban | 883 | 5.5037 | 5.4725 | 296.77 |  |  | 28 | 0.34493 | 0.34493 | 0.014138 | 0.014138 | 28 | 0.0012512 | 0.0012512
17067 | Taronga St | Urban | 1156 | 2.2303 | 4.9014 | 176.45 |  |  | 8 | 0.6483 | 0.6483 | 0.0067742 | 0.0067742 | 8 | 0.00014746 | 0.00014746
17068 | Peter Brock Drive | Urban | 43 | 2.2274 | 7.3824 | 199.56 |  |  | 4 | 0.0020644 | 0.0020644 | 1.7874e-05 | 1.7874e-05
17069 | Reen Rd & Cap Bank 2 | Urban | 32 | 0.75344 | 3.4006 | 288.52 | [7 empty] | 2 | 2.2342e-06 | 2.2342e-06
17070 | Hoadley Place | Urban | 19 | 0.79446 | 4.3194 | 257.82 |  |  | 18 | 0.018882 | 0.018882 | 0.00014076 | 0.00014076 | 18 | 5.027e-05 | 5.027e-05
1949 | Vardys Rd + Tattersall Rd | Urban | 751 | 1.5067 | 3.8303 | 348.77 | [7 empty] | 7 | 0.00035636 | 0.00035636
1950 | Bessemer St | Urban | 356 | 3.6069 | 2.4003 | 214.94 |  |  | 8 | 0.0045087 | 0.0045087 | 7.5964e-05 | 7.5964e-05 | 8 | 0.00017427 | 0.00017427
1952 | Lalor Rd | Urban | 342 | 1.4349 | 3.5536 | 95.65 |  |  | 8 | 0.12797 | 0.12797 | 0.0033558 | 0.0033558 | 8 | 0.00010724 | 0.00010724
1953 | Breakfast Creek | Urban | 22 | 1.5112 | 2.7703 | 16.2 |  |  | 2 | 0.0022946 | 0.0022946 | 2.6811e-05 | 2.6811e-05 | 2 | 2.2342e-06 | 2.2342e-06
1954 | Steel St + Madagascar Dr | Urban | 405 | 0.47734 | 5.0986 | 302.94 |  |  | 1 | 0.00010166 | 0.00010166 | 1.1171e-06 | 1.1171e-06 | 1 | 1.1171e-06 | 1.1171e-06
1956 | Forge St & Cap Bank 1 | Urban | 154 |  | 1.8315 | 280.35 |  |  | 1 | 0.0025705 | 0.0025705 | 3.4631e-05 | 3.4631e-05
1957 | Dalray St + Aux No 1 | Urban | 1388 | 8.892 | 0.9526 | 199.04 |  |  | 48 | 1.3109 | 1.3109 | 0.020041 | 0.020041 | 48 | 0.00067921 | 0.00067921
1958 | Tattersalls Rd + Aux No 2 | Urban | 153 | 2.3154 | 1.552 | 251.96 |  |  | 18 | 0.039928 | 0.039928 | 0.0010322 | 0.0010322 | 18 | 0.00010054 | 0.00010054
1959 | Sunnyholt Rd + Northcott Rd | Urban | 868 | 5.1803 | 1.9371 | 277.66 |  |  | 4 | 0.037998 | 0.037998 | 0.00012959 | 0.00012959 | 4 | 0.0011976 | 0.0011976
1960 | James Cook Dr + Gate Rd | Urban | 160 | 0.15451 | 3.8335 | 91 | [7 empty] | 2 | 3.2396e-05 | 3.2396e-05
1962 | Binney Rd & Jopling Cres | Urban | 1886 | 7.6621 | 3.8136 | 297.95 |  |  | 704 | 24.1355 | 24.1355 | 0.56143 | 0.56143 | 704 | 0.025524 | 0.025524
1963 | Coke 2 | Urban |  |  | 2.1046 |  |  |  | 1 | 4.4685e-06 | 4.4685e-06 | 1.1171e-06 | 1.1171e-06
19815 | Tuckwell Rd | Urban | [11 empty] | 6 | 0.00010278 | 0.00010278
19816 | Gilbert Rd | Urban | 951 | 1.7112 | 11.5583 | 268.23 | [7 empty] | 13 | 0.00022007 | 0.00022007
19856 | Silva Rd | Urban | 1324 | 14.3879 | 4.3784 | 236.93 |  |  | 1000 | 61.8032 | 61.8032 | 0.81248 | 0.81248 | 1000 | 0.085683 | 0.085683
19857 | Prince St | Urban | 2432 | 21.6857 | 3.4868 | 441.85 |  |  | 294 | 21.4414 | 21.4414 | 0.12232 | 0.12232 | 294 | 0.0063497 | 0.0063497
19870 | Cowper St | Urban | 1133 | 0.35143 | 2.6965 | 131.41 |  |  | 2 | 0.0079003 | 0.0079003 | 0.00027481 | 0.00027481 | 2 | 4.5802e-05 | 4.5802e-05
19871 | Glebe St | Urban | 1147 |  | 3.8785 | 151.22 |  |  | 252 | 4.3215 | 4.3215 | 0.060901 | 0.060901 | 252 | 0.005389 | 0.005389
19871, 3112 |  | Urban | [11 empty] | 1 | 2.2342e-06 | 2.2342e-06
19890 | Weir Rd | Urban | 142 | 1.825 | 3.1019 | 193.53 | [7 empty] | 2 | 3.3514e-06 | 3.3514e-06
19893 | Sydney Water STP 46 | Urban | 5 | 0.19399 | 1.0074 |  |  |  | 1 | 5.6973e-05 | 5.6973e-05 | 1.1171e-06 | 1.1171e-06
19894 | Caloola Av + Aux | Urban | 1061 | 7.264 | 0.82403 | 149.73 | [7 empty] | 4 | 0.00014858 | 0.00014858
19897 | Castlereagh Rd | Urban | 1 |  | 2.0287 | [8 empty] | 1 | 1.1171e-06 | 1.1171e-06
19898 | Coreen Av | Urban | 156 | 3.5484 | 1.3218 | 88.68 |  |  | 4 | 0.028826 | 0.028826 | 0.00036195 | 0.00036195
2 |  | Urban | [11 empty] | 6 | 6.9261e-05 | 6.9261e-05
20716 | Station St | Urban | 803 | 1.9216 | 4.5782 | 217.9 | [7 empty] | 1 | 4.1333e-05 | 4.1333e-05
20717 | Ladbury Ave | Urban | 830 | 6.9008 | 2.7633 | 135.63 |  |  | 28 | 0.074742 | 0.074742 | 0.00020332 | 0.00020332 | 28 | 0.0011841 | 0.0011841
20719 |  | Urban | 545 | 0.68857 | 1.8524 | 117.41 |  |  | 1 | 0.0060894 | 0.0060894 | 3.4631e-05 | 3.4631e-05
20719 | TAX Office | Urban | 545 | 0.68857 | 1.8524 | 117.41 |  |  | 1 | 0.0060894 | 0.0060894 | 3.4631e-05 | 3.4631e-05
20722 | Nepean Av | Urban | 381 | 3.0115 | 3.8303 | 209.66 |  |  | 25 | 0.64563 | 0.64563 | 0.01073 | 0.01073 | 25 | 0.00011171 | 0.00011171
20723 | Preston St | Urban | 489 | 0.14338 | 7.1344 | 178.8 | [7 empty] | 1 | 2.2342e-06 | 2.2342e-06
20725 | Glebe Pl | Urban | 1521 | 4.929 | 4.0356 | 250.55 |  |  | 144 | 11.6201 | 11.6201 | 0.087001 | 0.087001 | 144 | 0.0076813 | 0.0076813
25401 | Buckingham St & Aux No.1 | Rural Short | 443 | 7.9122 | 8.7119 | 86.4 |  |  | 96 | 2.0373 | 2.0373 | 0.02354 | 0.02354 | 96 | 0.0018768 | 0.0018768
25403 | Pitt Town Rd + Aux No 1 | Rural Short | 601 | 9.786 | 1.6572 |  |  |  | 250 | 2.8752 | 2.8752 | 0.039378 | 0.039378 | 250 | 0.0045243 | 0.0045243
25449 | West Dapto Rd | Rural Short | 140 | 20.8362 | 0.62726 | 37.2 |  |  | 252 | 1.4408 | 1.4408 | 0.026509 | 0.026509 | 252 | 0.0028151 | 0.0028151
25450 | Redalls Rd South East | Urban | 1183 | 16.9937 | 0.32349 | 169.15 |  |  | 64 | 1.9678 | 1.9678 | 0.04279 | 0.04279 | 64 | 0.0045221 | 0.0045221
25451 | Redalls Rd West | Rural Short | 25 | 3.4523 | 0.79917 | 45.5 |  |  | 16 | 0.031592 | 0.031592 | 0.00036642 | 0.00036642 | 16 | 0.00023683 | 0.00023683
25737 | Corfield Road | Urban | 580 |  | 5.4933 | 117.75 |  |  | 4 | 0.0072501 | 0.0072501 | 6.7027e-06 | 6.7027e-06 | 4 | 8.937e-06 | 8.937e-06
25738 | Yerona St | Urban | 1000 | 1.8515 | 4.7153 | 167.51 |  |  | 9 | 0.14945 | 0.14945 | 0.0038474 | 0.0038474
25739 | Croatia Ave Edmondson Park | Rural Short | 56 | 2.4406 | 0.11518 | 12.57 |  |  | 27 | 0.056494 | 0.056494 | 0.00069373 | 0.00069373 | 27 | 0.0014377 | 0.0014377
25740 | Narooma Dr | Urban | 1307 | 0.21129 | 10.3707 | 281.95 |  |  | 1 | 0.00145 | 0.00145 | 1.4523e-05 | 1.4523e-05
25741 | Camden Valley Way + Aux No 1 | Urban | 1173 | 4.1992 | 7.1552 | 259.06 |  |  | 72 | 0.13481 | 0.13481 | 0.001984 | 0.001984 | 72 | 0.0040518 | 0.0040518
25744 | Rynan Av | Rural Short | 431 | 10.4887 | 3.7492 | 99.29 |  |  | 63 | 0.26519 | 0.26519 | 0.00079762 | 0.00079762 | 63 | 0.00078422 | 0.00078422
25746 | Wroxham St | Urban | 1301 | 3.5335 | 9.108 | 290.87 |  |  | 2 | 0.00038652 | 0.00038652 | 2.2342e-06 | 2.2342e-06 | 2 | 3.2396e-05 | 3.2396e-05
25747 | Beech Rd | Rural Short | 1716 | 8.7112 | 15.673 | 222.42 |  |  | 200 | 6.3688 | 6.3688 | 0.076903 | 0.076903 | 200 | 0.0025694 | 0.0025694
25773 | Ponytail Drive | Urban | 2080 | 0.62288 | 16.8005 | 299.63 | [7 empty] | 2 | 5.9207e-05 | 5.9207e-05
25774 | Southwaite Cres | Urban | 1719 | 0.22036 | 11.9883 | 201.78 |  |  | 16 | 0.056115 | 0.056115 | 0.00043344 | 0.00043344 | 16 | 0.00019661 | 0.00019661
25775 | Gainsford Dr | Urban | 1036 | 0.55102 | 9.6347 | 30.98 |  |  | 44 | 0.59183 | 0.59183 | 0.0050628 | 0.0050628 | 44 | 0.0019438 | 0.0019438
25779 | Lakewood Dr | Urban | 712 |  | 9.6829 | 134.61 |  |  | 2 | 0.0046964 | 0.0046964 | 4.6919e-05 | 4.6919e-05 | 2 | 7.4847e-05 | 7.4847e-05
25780 | Yarrandale Dr | Urban | 1510 |  | 10.5914 | 194.63 |  |  | 4 | 0.020108 | 0.020108 | 0.00016087 | 0.00016087 | 4 | 0.00024577 | 0.00024577
25781 | Majestic Drive | Urban | 1827 | 1.385 | 14.7982 | 203.56 | [7 empty] | 1 | 8.0433e-05 | 8.0433e-05
25782 | Elizabeth Macarthur Dr | Urban | 976 | 0.15427 | 12.6697 | 215.53 | [7 empty] | 4 | 7.5964e-05 | 7.5964e-05
25783 | Burns Road | Urban | 1666 | 7.2835 | 18.355 | 217.53 |  |  | 72 | 0.06692 | 0.06692 | 0.0004826 | 0.0004826 | 72 | 0.00096966 | 0.00096966
25784 | Second Ponds Creek | Urban | 944 |  | 13.8107 | 136.23 |  |  | 12 | 0.015403 | 0.015403 | 0.00014076 | 0.00014076 | 12 | 0.00029045 | 0.00029045
27027 | Chai | Urban | 763 |  | 5.3019 | 282.8 |  |  | 1 | 0.0001698 | 0.0001698 | 1.1171e-06 | 1.1171e-06
27028 | ODea Rd | Urban | [6 empty] | 1 | 0.0028721 | 0.0028721 | 0.00061777 | 0.00061777 | 1 | 3.3514e-06 | 3.3514e-06
27029 | Sedgwick St | Urban | 576 | 1.9436 | 10.8871 | 244 | [7 empty] | 1 | 1.1171e-06 | 1.1171e-06
27031 | Turner Rd | Urban | 113 | 3.5454 | 8.092 | 89.1 |  |  | 32 | 0.0090174 | 0.0090174 | 3.5748e-05 | 3.5748e-05 | 32 | 3.5748e-05 | 3.5748e-05
27032 | Hodges Pl | Urban | 926 |  | 4.8222 | 200.79 |  |  | 1 | 0.0027269 | 0.0027269 | 3.7982e-05 | 3.7982e-05
27036 | Narellan Rd | Urban | [6 empty] | 16 | 0.17297 | 0.17297 | 0.0038027 | 0.0038027
27039 | Curran Hill Dr | Urban | 1412 |  | 9.2031 | 260.43 |  |  | 9 | 0.34785 | 0.34785 | 0.0050371 | 0.0050371
27040 | Tobruk Rd | Urban | 1074 |  | 7.1153 | 215.54 |  |  | 4 | 0.05086 | 0.05086 | 0.0024018 | 0.0024018
27142 | Gallipoli St & Cap Bank 2 | Urban | 565 | 0.04616 | 4.3242 | 187.01 |  |  | 8 | 0.0047857 | 0.0047857 | 5.3622e-05 | 5.3622e-05 | 8 | 8.937e-05 | 8.937e-05
27187 | Anella Av | Urban | 632 | 1.4945 | 7.649 | 235.39 |  |  | 16 | 0.43811 | 0.43811 | 0.005389 | 0.005389 | 16 | 0.0005809 | 0.0005809
27188 | Hoyle Av | Urban | 349 | 0.53089 | 1.4456 | 202.96 | [7 empty] | 2 | 8.3784e-05 | 8.3784e-05
27189 | Columbia Ct | Urban | 19 |  | 1.5126 | 106.11 | [7 empty] | 1 | 6.7027e-06 | 6.7027e-06
27191 | Fairway Drive | Urban | 1027 | 4.3989 | 8.31 | 303.13 |  |  | 288 | 4.8702 | 4.8702 | 0.11781 | 0.11781 | 288 | 0.0047053 | 0.0047053
27194 | Linksley Ave & Aux 2 | Urban | 637 |  | 9.6381 | 209.38 |  |  | 81 | 0.33486 | 0.33486 | 0.00093503 | 0.00093503 | 81 | 0.0012869 | 0.0012869
27200 | Kings Rd | Urban | 569 | 0.143 | 3.7803 | 220.89 | [7 empty] | 1 | 2.2342e-06 | 2.2342e-06
27201 | Packard Av | Urban | 258 | 1.2455 | 1.7505 | 68.31 |  |  | 16 | 0.24647 | 0.24647 | 0.0036552 | 0.0036552
27202 | Capacitor Bank 2B | Urban | [6 empty] | 32 | 0.14437 | 0.14437 | 0.00080433 | 0.00080433 | 32 | 0.00086242 | 0.00086242
27334 | Barff Rd | Urban | 1739 | 6.3235 | 8.3479 | 219.67 |  |  | 100 | 7.3656 | 7.3656 | 0.034765 | 0.034765 | 100 | 0.0045523 | 0.0045523
27335 | Lancaster St | Urban | 517 | 4.122 | 1.2499 | 247.4 |  |  | 16 | 0.34542 | 0.34542 | 0.0025113 | 0.0025113
27340 | Slater Rd | Urban | 608 | 0.27602 | 8.0373 | 186.91 |  |  | 16 | 0.096707 | 0.096707 | 0.00028151 | 0.00028151
27446 | Mokari St | Rural Short | 1560 | 36.576 | 3.8032 | 306.48 |  |  | 315 | 0.65722 | 0.65722 | 0.0078589 | 0.0078589 | 315 | 0.020691 | 0.020691
27447 | Terrace St | Urban | 499 | 2.6366 | 2.2452 | 202.08 |  |  | 1 | 0.018641 | 0.018641 | 0.0005742 | 0.0005742 | 1 | 5.3622e-05 | 5.3622e-05
27454 | Stephen St + Aux No 2 | Rural Short | 1039 | 43.3476 | 4.9829 | 240.98 |  |  | 1400 | 8.4723 | 8.4723 | 0.053175 | 0.053175 | 1400 | 0.0090487 | 0.0090487
2806 | Willoughby St & Capacitor Bank No 3 | Urban | 892 | 4.4492 | 3.4702 | 267.1 |  |  | 32 | 1.6696 | 1.6696 | 0.023182 | 0.023182 | 32 | 0.0012422 | 0.0012422
2807 | Mobbs Ln | Urban | 1180 | 7.5361 | 2.6561 | 169.71 |  |  | 512 | 7.6819 | 7.6819 | 0.17545 | 0.17545 | 512 | 0.0025023 | 0.0025023
2809 | Karingal + A/F Cell No 3 | Urban | 608 | 3.3553 | 1.6733 | 140.41 |  |  | 32 | 0.52228 | 0.52228 | 0.011243 | 0.011243 | 32 | 0.004254 | 0.004254
2810 | Alexander St | Urban | 1291 | 5.4648 | 1.3053 | 176.09 |  |  | 16 | 1.353 | 1.353 | 0.011555 | 0.011555 | 16 | 0.0018946 | 0.0018946
2812 | Dunlop St | Urban | 1305 | 5.1003 | 1.3981 | 172.29 |  |  | 112 | 8.1611 | 8.1611 | 0.047169 | 0.047169 | 112 | 0.0087046 | 0.0087046
2813 | Felton Rd | Urban | 833 | 6.1464 | 0.33434 | 174.79 |  |  | 18 | 0.50219 | 0.50219 | 0.0059654 | 0.0059654 | 18 | 0.0010557 | 0.0010557
2815 | Brand St + A/F Cell No 2 | Urban | 1326 | 5.1749 | 0.67122 | 162.37 |  |  | 176 | 14.8903 | 14.8903 | 0.13679 | 0.13679 | 176 | 0.011797 | 0.011797
2816 | Jenkins Rd | Urban | 784 | 5.6747 | 0.21531 | 206.11 |  |  | 32 | 0.079271 | 0.079271 | 0.0089191 | 0.0089191 | 32 | 0.0028062 | 0.0028062
2819 | Monash Rd | Urban | 1486 | 6.412 | 1.1111 | 206.45 |  |  | 288 | 23.8681 | 23.8681 | 0.21545 | 0.21545 | 288 | 0.006515 | 0.006515
2820 | Mandoo Road | Urban | 1999 | 5.8759 | 6.2922 | 280.29 |  |  | 245 | 15.8862 | 15.8862 | 0.094933 | 0.094933 | 245 | 0.0089224 | 0.0089224
2822 | Kildare Rd | Urban | 1122 |  | 6.5158 | 190.21 |  |  | 6 | 1.3466 | 1.3466 | 0.0084454 | 0.0084454 | 6 | 0.00025247 | 0.00025247
2825 | Bungarribee Rd + Aux No 2 | Urban | 1248 | 0.39298 | 5.7493 | 251.46 |  |  | 25 | 1.2734 | 1.2734 | 0.0083561 | 0.0083561 | 25 | 0.00097748 | 0.00097748
2826 | Holbeche Rd | Urban | 72 | 4.2041 | 4.3312 | 230.8 |  |  | 1 | 0.014402 | 0.014402 | 8.937e-05 | 8.937e-05 | 1 | 2.2342e-06 | 2.2342e-06
2828 | Eastern Rd | Urban | 430 | 3.4142 | 2.8816 | 106.62 |  |  | 117 | 4.292 | 4.292 | 0.040649 | 0.040649 | 117 | 0.0096318 | 0.0096318
2829 | London St | Urban | 1062 | 5.1798 | 1.0079 | 145.89 |  |  | 252 | 2.2393 | 2.2393 | 0.014826 | 0.014826 | 252 | 0.012266 | 0.012266
3100 |  | Urban | [6 empty] | 1 | 0.0074624 | 0.0074624 | 0.00018656 | 0.00018656
3102 |  | Urban | [11 empty] | 1 | 1.8991e-05 | 1.8991e-05
3105 |  | Urban | [6 empty] | 2 | 0.0032106 | 0.0032106 | 0.0010702 | 0.0010702 | 2 | 3.7982e-05 | 3.7982e-05
3106 |  | Urban | [6 empty] | 4 | 0.0077528 | 0.0077528 | 3.1279e-05 | 3.1279e-05 | 4 | 0.00023236 | 0.00023236
3114 |  | Urban | [11 empty] | 1 | 2.2342e-06 | 2.2342e-06
3166 |  | Urban | [11 empty] | 2 | 8.4901e-05 | 8.4901e-05
3184 | Harrington St | Urban | 723 | 3.4091 | 0.081159 | 90.91 |  |  | 4 | 0.015215 | 0.015215 | 0.00029939 | 0.00029939 | 4 | 0.00017539 | 0.00017539
3185 | Abercrombie St | Urban | 453 | 2.609 | 0.17583 | 59.89 |  |  | 27 | 0.78108 | 0.78108 | 0.0070077 | 0.0070077 | 27 | 0.0010557 | 0.0010557
3187 | McBurney Rd | Urban | 1208 | 0.81726 | 2.7329 | 118.82 |  |  | 9 | 0.02845 | 0.02845 | 0.00018432 | 0.00018432
3188 | Cambridge St | Urban | [6 empty] | 4 | 0.015995 | 0.015995 | 0.00027705 | 0.00027705 | 4 | 4.4685e-05 | 4.4685e-05
3325 |  | Urban | [11 empty] | 4 | 0.000496 | 0.000496
3326 |  | Urban | [6 empty] | 2 | 0.015054 | 0.015054 | 8.4901e-05 | 8.4901e-05 | 2 | 2.346e-05 | 2.346e-05
3334 |  | Urban | [11 empty] | 2 | 5.9207e-05 | 5.9207e-05
3335 |  | Urban | [11 empty] | 1 | 2.9045e-05 | 2.9045e-05
3347 | Hammers Rd East | Urban | 668 | 3.8928 | 1.4268 | 229.15 |  |  | 16 | 0.16342 | 0.16342 | 0.00067027 | 0.00067027 | 16 | 7.1496e-05 | 7.1496e-05
3351 | Old Windsor Rd | Urban | 1810 | 6.108 | 1.5234 | 349.45 |  |  | 45 | 2.7395 | 2.7395 | 0.05146 | 0.05146 | 45 | 0.0004826 | 0.0004826
3353 | Allambie Av | Urban | 1108 | 4.6504 | 1.07 | 190.84 |  |  | 100 | 3.8181 | 3.8181 | 0.08928 | 0.08928 | 100 | 0.0037703 | 0.0037703
3357 | Barnetts Rd | Urban | 1004 | 6.9526 | 0.08458 | 211.1 |  |  | 4 | 0.012556 | 0.012556 | 6.0324e-05 | 6.0324e-05
3358 | Briens Rd | Urban | 346 | 2.1708 | 1.5128 | 146.23 |  |  | 2 | 0.0043858 | 0.0043858 | 2.9045e-05 | 2.9045e-05 | 2 | 1.0054e-05 | 1.0054e-05
3360 | Glenn Av | Urban | 1192 | 4.0355 | 2.9692 | 305.94 |  |  | 80 | 1.2031 | 1.2031 | 0.0063899 | 0.0063899 | 80 | 0.0014478 | 0.0014478
35001 | Boral Quarry HVC | Urban | 874 | 3.0474 | 3.8868 | 171.03 |  |  | 32 | 0.025837 | 0.025837 | 0.010546 | 0.010546 | 32 | 0.00064346 | 0.00064346
35005 | Driftway Dr | Urban | 665 | 3.0632 | 2.8667 | 139.15 |  |  | 1 | 0.11947 | 0.11947 | 0.000496 | 0.000496 | 1 | 2.1225e-05 | 2.1225e-05
35010 | Daruga Av | Urban | 610 | 2.5084 | 5.3003 | 122.63 | [7 empty] | 3 | 7.8198e-05 | 7.8198e-05
35304 | Hillcrest Ave | Urban | 875 | 4.778 | 1.3612 | 122.53 |  |  | 4 | 0.084461 | 0.084461 | 0.0020756 | 0.0020756 | 4 | 3.1279e-05 | 3.1279e-05
35305 | Greenleaf Street | Urban | 1082 | 6.1008 | 0.29863 | 121.49 |  |  | 12 | 0.035028 | 0.035028 | 0.00042227 | 0.00042227 | 12 | 5.809e-05 | 5.809e-05
35306 | Ballandella Road | Urban | 463 | 2.4631 | 1.8083 |  |  |  | 4 | 0.035207 | 0.035207 | 0.00013629 | 0.00013629 | 4 | 9.3838e-05 | 9.3838e-05
35307 | Sirios St | Urban | 524 | 3.9536 | 0.67658 | 125.12 |  |  | 54 | 0.17794 | 0.17794 | 0.00034184 | 0.00034184 | 54 | 0.0034988 | 0.0034988
35312 | Ursula Street | Urban | 98 | 1.1552 | 0.85832 | 144.76 |  |  | 64 | 0.80113 | 0.80113 | 0.01051 | 0.01051 | 64 | 0.0010009 | 0.0010009
35314 | Oakes Road | Urban | 426 | 3.0941 | 1.448 | 178.07 |  |  | 16 | 0.17457 | 0.17457 | 0.0039546 | 0.0039546
35315 | Hurley Street | Urban | 1136 | 3.5262 | 1.8376 | 240.7 |  |  | 320 | 1.2034 | 1.2034 | 0.010367 | 0.010367 | 320 | 0.031708 | 0.031708
35325 | Goliath Avenue | Urban | 822 | 6.1896 | 2.3583 | 279.07 |  |  | 8 | 0.031905 | 0.031905 | 0.0036329 | 0.0036329 | 8 | 0.000496 | 0.000496
35326 | Carmel Place | Urban | 454 | 4.2111 | 3.077 |  |  |  | 4 | 0.067905 | 0.067905 | 0.0010568 | 0.0010568
35327 | Picasso Cres | Urban | 1372 | 6.4679 | 0.54573 | 183.32 |  |  | 9 | 0.10677 | 0.10677 | 0.0047221 | 0.0047221
35333 | Reynolds St | Urban | 968 | 4.2035 | 1.1568 | 167.04 |  |  | 4 | 0.0016801 | 0.0016801 | 0.00028598 | 0.00028598 | 4 | 1.8991e-05 | 1.8991e-05
35335 | Gideon Street | Urban | 431 | 2.8404 | 1.3026 | 137.36 |  |  | 16 | 0.018602 | 0.018602 | 0.00032173 | 0.00032173 | 16 | 0.00026811 | 0.00026811
35388 | ISABELLA ST | Urban | 1648 | 1.7476 | 4.4611 | 208.63 |  |  | 12 | 0.0099468 | 0.0099468 | 1.3405e-05 | 1.3405e-05 | 12 | 0.00050941 | 0.00050941
35403 | HAROLD ST | Urban | 1606 | 0.59093 | 5.8115 | 198.51 |  |  | 1 | 0.24185 | 0.24185 | 0.0017874 | 0.0017874 | 1 | 1.1171e-06 | 1.1171e-06
35405 | ALASKA AV | Urban | 434 |  | 1.3278 | 139.14 | [7 empty] | 1 | 9.2721e-05 | 9.2721e-05
35418 | Wisemans Ferry & Aux No.1 | Rural Short | 332 | 33.873 | 0.52543 | 74.51 |  |  | 220 | 8.123 | 8.9225 | 0.038929 | 0.038929 | 220 | 0.0018432 | 0.0018432
35442 | Northumberland St & Liverpool Hospital No.3 | Urban | 633 |  | 2.7031 | 116.45 |  |  | 1 | 0.0113 | 0.0113 | 3.7982e-05 | 3.7982e-05
35443 | Tindall Ave | Urban | 474 | 0.00178 | 3.1852 | 217.08 |  |  | 28 | 0.035064 | 0.035064 | 0.0010948 | 0.0010948 | 28 | 0.00064346 | 0.00064346
35444 | Viscount Pl + Aux No 1 | Urban | 46 | 1.0022 | 2.2179 | 167.64 |  |  | 1 | 0.0099379 | 0.0099379 | 0.00015975 | 0.00015975
35503 | Auber Glen & Aux 1A | Urban | 935 | 6.8402 | 8.5507 | 257.44 |  |  | 28 | 0.01442 | 0.01442 | 0.00051611 | 0.00051611 | 28 | 0.00084007 | 0.00084007
35508 | Endeavour Ave & St Clair Shops | Urban | 417 |  | 9.4901 | 160.43 | [7 empty] | 2 | 2.4577e-05 | 2.4577e-05
35509 | Lysaghts & Lenore Lane East | Urban | 3 |  | 3.4419 | 76.56 | [7 empty] | 1 | 3.3514e-06 | 3.3514e-06
35511 | Hawk PL & Capacitor Bank 1B | Urban | 494 |  | 6.1422 | 273.22 |  |  | 1 | 0.0055666 | 0.0055666 | 0.00055074 | 0.00055074 | 1 | 1.564e-05 | 1.564e-05
35514 | Roper Rd | Urban | 198 | 6.196 | 7.8039 | 284.28 |  |  | 36 | 0.28749 | 0.28749 | 0.0019438 | 0.0019438
35519 | Halifax Cl & Bennet Rd | Urban | 1086 |  | 10.0011 | 228.45 |  |  | 63 | 0.028832 | 0.028832 | 0.00053957 | 0.00053957 | 63 | 0.0021013 | 0.0021013
35523 | Tyrone Pl | Urban | 5 |  | 1.3866 | 31.95 | [7 empty] | 2 | 3.3514e-06 | 3.3514e-06
35524 | Chameleon Dr & Aux 2A | Urban | 691 | 0.14053 | 4.7693 | 155.57 |  |  | 64 | 0.096126 | 0.096126 | 0.012512 | 0.012512 | 64 | 0.00071496 | 0.00071496
35528 | Peppertree Drive | Urban | 657 |  | 6.4031 | 152.26 |  |  | 27 | 0.020882 | 0.020882 | 0.00016087 | 0.00016087 | 27 | 0.0005027 | 0.0005027
35530 | Illawarra Drive | Urban | 984 |  | 7.9589 | 199.54 |  |  | 32 | 0.014335 | 0.014335 | 0.00017874 | 0.00017874 | 32 | 0.00093838 | 0.00093838
35569 | Christie St & Aux No. 3 | Urban | 1443 | 4.8586 | 1.7431 | 197.67 |  |  | 192 | 11.4927 | 11.4927 | 0.079602 | 0.079602 | 192 | 0.00064346 | 0.00064346
35571 | Hume Hwy | Urban | 1736 | 6.1503 | 2.9341 | 235.41 |  |  | 90 | 0.41486 | 0.41486 | 0.0028151 | 0.0028151 | 90 | 0.0028554 | 0.0028554
35572 | Hay St | Urban | 1569 | 1.3777 | 3.7342 | 118.26 | [7 empty] | 1 | 1.1171e-06 | 1.1171e-06
35693 | Sir Henry's Pde | Rural Short | 927 | 18.2279 | 1.4946 | 196.51 |  |  | 13 | 0.0068837 | 0.0068837 | 2.9045e-05 | 2.9045e-05 | 13 | 0.0012556 | 0.0012556
35695 | Sun Valley Road | Rural Short | 360 | 9.4507 | 1.008 | 104.35 |  |  | 180 | 2.1749 | 2.1749 | 0.028688 | 0.028688 | 180 | 0.0024934 | 0.0024934
35696 | Bland Street | Urban | 1381 | 13.3205 | 1.9042 | 256.81 |  |  | 208 | 9.0818 | 9.0818 | 0.079874 | 0.079874 | 208 | 0.02808 | 0.02808
35701 | Fraser Road | Urban | 1073 | 10.3838 | 2.5585 | 173.4 |  |  | 98 | 3.6713 | 3.6713 | 0.038833 | 0.038833 | 98 | 0.0013137 | 0.0013137
35702 | Greens Pde | Urban | 856 | 7.2803 | 1.4578 | 126.44 |  |  | 63 | 5.435 | 5.435 | 0.040374 | 0.040374 | 63 | 0.0034083 | 0.0034083
35703 | Ferguson Ave | Urban | 194 | 0.25048 | 0.60055 | 48.84 | [7 empty] | 1 | 6.2559e-05 | 6.2559e-05
35761 | Dunheved Cct South | Urban | 162 | 1.753 | 2.0558 | 181.96 |  |  | 3 | 0.0018131 | 0.0018131 | 3.3514e-06 | 3.3514e-06 | 3 | 3.9099e-05 | 3.9099e-05
35762 | Maple Street | Urban | 1361 | 5.7415 | 3.8322 | 291.35 |  |  | 75 | 1.0877 | 1.0877 | 0.031436 | 0.031436 | 75 | 0.00072613 | 0.00072613
35763 | Bent Street | Urban | 253 | 5.0986 | 1.0284 | 233.75 |  |  | 48 | 2.0084 | 2.0084 | 0.010657 | 0.010657 | 48 | 0.00023236 | 0.00023236
35764 | Government Road | Urban | 42 | 3.3112 | 1.2418 | 197.57 |  |  | 9 | 0.02542 | 0.02542 | 0.00032843 | 0.00032843
35765 | Griffith Street | Urban | 1068 | 6.7085 | 0.23058 | 211.53 |  |  | 18 | 0.027079 | 0.027079 | 0.00029492 | 0.00029492 | 18 | 0.00030162 | 0.00030162
35766 | Glossop Street | Urban | 360 | 2.2669 | 0.18161 | 195.58 |  |  | 1 | 0.0089906 | 0.0089906 | 8.8252e-05 | 8.8252e-05
35767 | East Lane | Urban | 505 | 2.8081 | 2.4382 | 273.09 |  |  | 63 | 1.988 | 1.988 | 0.025031 | 0.025031 | 63 | 0.0017997 | 0.0017997
35769 | Links Road | Urban | 87 | 5.9246 | 1.0893 | 226.07 |  |  | 9 | 0.080118 | 0.080118 | 0.00034184 | 0.00034184 | 9 | 0.00014076 | 0.00014076
35771 | Dunheved East | Urban | 119 | 1.9552 | 0.81616 | 112.61 |  |  | 1 | 0.0077059 | 0.0077059 | 0.00013294 | 0.00013294 | 1 | 1.1171e-06 | 1.1171e-06
35772 | Drummond Ave | Urban | 747 |  | 11.916 | 124.99 | [7 empty] | 1 | 3.3514e-06 | 3.3514e-06
35773 | West Lane | Urban | 429 | 4.2799 | 1.9658 | 347.12 |  |  | 18 | 0.014625 | 0.014625 | 0.00012735 | 0.00012735 | 18 | 0.00034184 | 0.00034184
35815 | Bargo | Rural Short | 508 | 16.8355 | 0.23452 | 121.18 |  |  | 32 | 0.87274 | 0.87274 | 0.013682 | 0.013682 | 32 | 0.0008937 | 0.0008937
35816 | Bronzewing Street | Rural Short | 1059 | 33.6507 | 0.07116 | 142.15 |  |  | 1859 | 27.2789 | 27.2789 | 0.44698 | 0.44698 | 1859 | 0.082125 | 0.082125
35818 | Linsell Place and Aux No. 2 | Rural Short | 1340 | 25.1107 | 1.1828 | 247.78 |  |  | 486 | 11.8472 | 11.8472 | 0.20914 | 0.20914 | 486 | 0.022169 | 0.022169
35824 | Emmett Street | Rural Short | 1083 | 13.9503 | 0.38807 | 178.46 |  |  | 8 | 0.094843 | 0.094843 | 0.0050226 | 0.0050226 | 8 | 0.00070155 | 0.00070155
35825 | Stratford Rd | Rural Short | 1097 | 27.9358 | 1.1943 | 178.93 |  |  | 36 | 0.70889 | 0.70889 | 0.020349 | 0.020349 | 36 | 0.00030162 | 0.00030162
35827 | Rockford Road | Rural Short | 152 | 8.6603 | 0.34349 | 126.19 |  |  | 100 | 0.49984 | 0.49984 | 0.007306 | 0.007306 | 100 | 0.0040775 | 0.0040775
35980 | Pheasants Nest | Rural Short | 437 | 31.4475 | 0.1256 | 78.63 |  |  | 180 | 3.8997 | 3.8997 | 0.029559 | 0.029559 | 180 | 0.0019304 | 0.0019304
35981 | Haddon Place | Rural Short | 439 | 12.3469 | 1.273 | 130.77 |  |  | 54 | 2.3383 | 2.3383 | 0.017715 | 0.017715 | 54 | 0.0016087 | 0.0016087
35982 | Douglas Park | Rural Short | 404 | 46.12 | 1.4327 | 139.54 |  |  | 1176 | 12.1066 | 12.1066 | 0.11899 | 0.11899 | 1176 | 0.014232 | 0.014232
35983 | Picton | Rural Short | 982 | 24.1627 | 6.7754 | 262.92 |  |  | 600 | 24.0351 | 24.0351 | 0.17668 | 0.17668 | 600 | 0.011395 | 0.011395
35988 | Razorback | Rural Short | 597 | 52.6623 | 2.8194 | 134.59 |  |  | 1859 | 31.9445 | 31.9445 | 0.19058 | 0.19058 | 1859 | 0.041723 | 0.041723
35989 | Wilton | Rural Short | 876 | 53.7687 | 10.7733 | 190.77 |  |  | 3388 | 109.0636 | 109.0636 | 0.81442 | 0.81442 | 3388 | 0.080022 | 0.080022
35990 | Lakesland | Rural Short | 1122 | 43.8639 | 3.2805 | 202.33 |  |  | 2601 | 124.5953 | 124.5953 | 0.7729 | 0.7729 | 2601 | 0.040356 | 0.040356
35991 | Allied Mills | Rural Short |  |  | 1.3118 |  |  |  | 4 | 0.00058984 | 0.00058984 | 4.4685e-06 | 4.4685e-06
41363 | Samantha Riley Dr | Urban | 490 |  | 4.8395 | 194.5 |  |  | 4 | 0.00054962 | 0.00054962 | 4.4685e-06 | 4.4685e-06
41367 | Stanhope Parkway | Urban | 545 |  | 7.6879 | 48 | [7 empty] | 1 | 6.7027e-06 | 6.7027e-06
41533 | Palmyra Rd | Rural Short | 1207 | 20.8439 | 3.3819 | 203.82 |  |  | 72 | 0.21773 | 0.21773 | 0.0021717 | 0.0021717 | 72 | 0.00060324 | 0.00060324
41535 | Magnolia St | Urban | 1830 | 11.4223 | 1.3034 | 336.77 |  |  | 225 | 21.2282 | 21.2282 | 0.10109 | 0.10109 | 225 | 0.012931 | 0.012931
41537 | Hatherton Rd | Urban | 1206 | 6.9621 | 1.8751 | 216.95 |  |  | 200 | 4.888 | 4.888 | 0.057911 | 0.057911 | 200 | 0.020471 | 0.020471
4353 | Union St | Rural Short | [6 empty] | 1 | 7.0379e-05 | 7.0379e-05 | 1.1171e-06 | 1.1171e-06 | 1 | 6.7027e-06 | 6.7027e-06
4354 | Windsor Rd | Urban | 660 | 3.7363 | 2.6402 |  |  |  | 63 | 2.0462 | 2.0462 | 0.027659 | 0.027659 | 63 | 0.0011361 | 0.0011361
4359 | Cornwallis Rd | Rural Short | [6 empty] | 1 | 0.0010467 | 0.0010467 | 3.3514e-06 | 3.3514e-06 | 1 | 1.0054e-05 | 1.0054e-05
4360 | Freemans Reach Rd | Rural Short | [6 empty] | 12 | 0.37052 | 0.37052 | 0.0058917 | 0.0058917 | 12 | 6.2559e-05 | 6.2559e-05
4361 | Brabyn St | Urban | [11 empty] | 1 | 1.1171e-05 | 1.1171e-05
4368 | Londonderry Rd + Blacktown Rd | Rural Short | 718 | 22.8948 | 2.9462 | 281.57 |  |  | 128 | 2.9514 | 2.9514 | 0.042897 | 0.042897 | 128 | 0.004826 | 0.004826
4369 | Dight St | Urban | 1 | 2.1817 | 0.83859 |  |  |  | 1 | 4.1333e-05 | 4.1333e-05 | 1.1171e-06 | 1.1171e-06
4370 | Yarramundi Ln + Aux No 2 | Urban | 715 | 1.1763 | 2.8186 | 187.61 |  |  | 180 | 1.5614 | 1.5614 | 0.028688 | 0.028688 | 180 | 0.015805 | 0.015805
4372 | Francis St + Aux No 1 | Urban | 1049 | 7.7291 | 1.1919 | 298.16 |  |  | 96 | 5.1715 | 5.1715 | 0.056598 | 0.056598 | 96 | 0.0049868 | 0.0049868
4374 | Hereford St & Cap Bank 1 | Urban | 346 | 2.1128 | 0.143 | 289.55 |  |  | 8 | 0.11455 | 0.11455 | 0.0030922 | 0.0030922 | 8 | 0.00073842 | 0.00073842
4375 | West Market St | Urban | 409 | 0.79802 | 1.6191 | 213.49 |  |  | 4 | 0.036061 | 0.036061 | 0.0018365 | 0.0018365 | 4 | 8.937e-06 | 8.937e-06
438 |  | Urban | [11 empty] | 2 | 0.00011395 | 0.00011395
458/1 |  | Urban | [11 empty] | 5 | 7.9316e-05 | 7.9316e-05
46395 | Balmoral St | Urban | 1280 | 6.0529 | 2.2994 | 210.22 |  |  | 18 | 0.027602 | 0.027602 | 0.0084387 | 0.0084387 | 18 | 0.0016388 | 0.0016388
46397 | Main St | Urban | 852 | 2.5585 | 3.5579 | 111.45 | [7 empty] | 2 | 0.00025582 | 0.00025582
46401 | Westpoint No.2 | Urban | 22 |  | 1.1801 | 125.28 | [7 empty] | 1 | 0.00067921 | 0.00067921
46473 |  | Urban | [6 empty] | 1 | 0.00032061 | 0.00032061 | 1.1171e-06 | 1.1171e-06 | 1 | 3.0162e-05 | 3.0162e-05
46475 |  | Rural Short | [6 empty] | 45 | 2.1911 | 2.1911 | 0.051695 | 0.051695 | 45 | 0.00072389 | 0.00072389
46477 |  | Urban | [6 empty] | 16 | 0.03111 | 0.03111 | 0.00031279 | 0.00031279 | 16 | 0.00010724 | 0.00010724
46479 |  | Urban | [11 empty] | 1 | 4.1333e-05 | 4.1333e-05
46481 |  | Urban | [6 empty] | 8 | 0.044613 | 0.044613 | 0.00021449 | 0.00021449 | 8 | 0.00036195 | 0.00036195
46485 |  | Urban | [6 empty] | 1 | 0.00017762 | 0.00017762 | 1.1171e-06 | 1.1171e-06
46487 |  | Rural Short | [6 empty] | 27 | 0.059148 | 0.059148 | 0.00042227 | 0.00042227 | 27 | 0.000372 | 0.000372
46748 | Huntingwood Drive | Urban | 12 |  | 1.8225 | 272.97 |  |  | 1 | 0.0005809 | 0.0005809 | 2.2342e-06 | 2.2342e-06 | 1 | 2.2342e-06 | 2.2342e-06
46750 | Lidco St | Urban | 99 | 0.97099 | 2.5042 | 146.33 |  |  | 1 | 0.0018231 | 0.0018231 | 1.7874e-05 | 1.7874e-05 | 1 | 3.3514e-06 | 3.3514e-06
46752 | Julie St | Urban | 1647 | 7.2791 | 1.4677 | 259.13 | [7 empty] | 7 | 0.00079762 | 0.00079762
46763 | Auto Place | Urban | 43 | 1.9826 | 7.7293 | 224.66 |  |  | 1 | 0.00064905 | 0.00064905 | 3.3514e-06 | 3.3514e-06 | 1 | 3.3514e-06 | 3.3514e-06
46768 | Squill Pl | Urban | 124 | 0.77859 | 0.82496 | 170.16 |  |  | 1 | 0.014674 | 0.014674 | 0.00020667 | 0.00020667
46770 | Brabham Dr | Urban | 323 |  | 4.3006 | 360 | [7 empty] | 1 | 2.2342e-06 | 2.2342e-06
46772 | Desmond Drive | Urban | 12 | 1.0273 | 2.0459 | 180.37 |  |  | 3 | 0.00065016 | 0.00065016 | 6.7027e-06 | 6.7027e-06 | 3 | 5.5856e-06 | 5.5856e-06
46774 | Penny Pl | Urban | 544 | 0.88517 | 6.0946 | 175.64 |  |  | 4 | 0.22054 | 0.22054 | 0.0013696 | 0.0013696 | 4 | 3.5748e-05 | 3.5748e-05
48161 | Glen Innes Rd | Urban | 1066 | 0.86576 | 8.2908 | 206.38 |  |  | 25 | 0.46606 | 0.46606 | 0.006429 | 0.006429 | 25 | 0.0013126 | 0.0013126
48166 | Merchant Way | Urban | 186 | 0.82112 | 4.2496 | 129.97 | [7 empty] | 3 | 1.7874e-05 | 1.7874e-05
48168 | Keppel CCT | Urban | 1259 | 0.01741 | 17.2862 | 343.8 |  |  | 28 | 0.053879 | 0.053879 | 0.0010791 | 0.0010791 | 28 | 0.005246 | 0.005246
48178 | Dominico CL | Urban | 1003 | 0.05791 | 8.1839 | 223.15 |  |  | 4 | 0.0013607 | 0.0013607 | 1.7874e-05 | 1.7874e-05 | 4 | 0.00014746 | 0.00014746
48180 | Cowpasture Rd South | Urban | 519 | 0.2273 | 5.5038 | 242.69 |  |  | 1 | 0.00026252 | 0.00026252 | 2.2342e-06 | 2.2342e-06
48185 | Second Ave | Rural Short | 469 | 5.368 | 5.9413 | 82.66 |  |  | 4 | 0.18474 | 0.18474 | 0.0021717 | 0.0021717 | 4 | 2.6811e-05 | 2.6811e-05
48187 | Parer Ave | Urban | 583 | 0.32646 | 8.0185 | 101.25 |  |  | 1 | 0.00030162 | 0.00030162 | 1.1171e-06 | 1.1171e-06 | 1 | 1.564e-05 | 1.564e-05
48189 | Rottnest Ave | Urban | 1731 |  | 10.3112 | 381.72 |  |  | 18 | 0.87304 | 0.87304 | 0.032388 | 0.032388 | 18 | 0.00056303 | 0.00056303
48196 | Fifteenth Ave | Rural Short | 704 | 16.5874 | 1.3496 | 173.43 |  |  | 833 | 53.4299 | 53.4299 | 0.20658 | 0.20658 | 833 | 0.032953 | 0.032953
48203 | Seventeenth Ave | Urban | 518 | 0.76833 | 8.7996 | 89.2 |  |  | 63 | 4.3935 | 4.3935 | 0.011988 | 0.011988 | 63 | 0.0010155 | 0.0010155
48205 | Armidale Ave | Urban | 1014 | 0.32488 | 6.2158 | 171.62 |  |  | 16 | 0.026945 | 0.026945 | 0.00031279 | 0.00031279 | 16 | 0.00070155 | 0.00070155
4857 | Malta St | Urban | 535 | 3.745 | 0.48678 | 141.93 |  |  | 6 | 0.00070379 | 0.00070379 | 6.7027e-06 | 6.7027e-06 | 6 | 7.7081e-05 | 7.7081e-05
4860 | Whitaker St + Aux No 1 | Urban | 221 | 2.1782 | 1.1799 | 131.92 |  |  | 1 | 0.0033067 | 0.0033067 | 0.00012959 | 0.00012959 | 1 | 2.2342e-06 | 2.2342e-06
4866 | Matthes St & Aux No.2 | Urban | 998 | 5.1825 | 0.92965 | 168.45 |  |  | 64 | 0.16455 | 0.16455 | 0.0010546 | 0.0010546
4867 | Seville St | Urban | 81 | 0.3515 | 0.28615 | 66.67 | [7 empty] | 1 | 1.1171e-06 | 1.1171e-06
4869 | Normanby St | Urban | 1165 | 4.2231 | 1.8226 | 134.63 |  |  | 2 | 0.047757 | 0.047757 | 0.00027928 | 0.00027928 | 2 | 1.6757e-05 | 1.6757e-05
4870 | Lisbon St | Urban | 272 | 3.238 | 1.5439 | 166.1 | [7 empty] | 3 | 2.346e-05 | 2.346e-05
4873 | Loftus St | Urban | 1389 | 7.5994 | 1.3827 | 200.84 |  |  | 50 | 0.27813 | 0.27813 | 0.0015863 | 0.0015863 | 50 | 0.001173 | 0.001173
4880 |  | Urban | [11 empty] | 2 | 2.0108e-05 | 2.0108e-05
4883 | Carlton St | Urban | [6 empty] | 1 | 0.009204 | 0.009204 | 7.7081e-05 | 7.7081e-05 | 1 | 3.9099e-05 | 3.9099e-05
4887 | Woodville Rd | Urban | [6 empty] | 2 | 0.010577 | 0.010577 | 6.0324e-05 | 6.0324e-05 | 2 | 0.0001955 | 0.0001955
4889 |  | Urban | [11 empty] | 1 | 0.00015416 | 0.00015416
48999 | Petro Pump & Aux No 2 | Urban | 516 | 0.82203 | 6.8796 | 96.77 |  |  | 1 | 0.00036418 | 0.00036418 | 1.1171e-06 | 1.1171e-06 | 1 | 2.7928e-05 | 2.7928e-05
49001 | Barnier Dr | Urban | 816 | 1.6389 | 5.0169 | 190.89 |  |  | 36 | 0.91311 | 0.91311 | 0.011127 | 0.011127 | 36 | 0.0044338 | 0.0044338
49006 | Rickard Rd | Urban | 1039 |  | 8.233 | 241.01 | [7 empty] | 1 | 1.3405e-05 | 1.3405e-05
49008 | Warrimoo Rd | Urban | 898 | 3.0178 | 5.9785 | 186.12 |  |  | 100 | 4.0414 | 4.0414 | 0.0042674 | 0.0042674 | 100 | 0.013685 | 0.013685
49010 | Narrabri Street | Urban | 878 | 3.8369 | 3.5033 | 327.25 |  |  | 2 | 0.00083561 | 0.00083561 | 2.2342e-06 | 2.2342e-06 | 2 | 7.7081e-05 | 7.7081e-05
49319 | Saxonvale Road | Urban | 1222 |  | 8.9878 | 245.11 |  |  | 112 | 0.15718 | 0.15718 | 0.0017829 | 0.0017829 | 112 | 0.0039859 | 0.0039859
49328 | Depford Ave | Urban | 702 |  | 6.2382 | 186.78 |  |  | 25 | 0.12961 | 0.12961 | 0.00056415 | 0.00056415
49337 | Burbank Place | Urban | 783 | 0.15989 | 12.1781 | 297.86 |  |  | 2 | 0.01301 | 0.01301 | 0.0017583 | 0.0017583 | 2 | 1.564e-05 | 1.564e-05
49341 | Warooga Drive | Urban | 1371 | 4.7352 | 8.9242 | 342.33 |  |  | 4 | 0.010767 | 0.010767 | 0.0035502 | 0.0035502 | 4 | 4.9153e-05 | 4.9153e-05
49348 | Bella Vista Drive | Urban | 723 | 0.12969 | 6.4692 | 225.32 |  |  | 2 | 0.00076411 | 0.00076411 | 2.2342e-06 | 2.2342e-06 | 2 | 8.2667e-05 | 8.2667e-05
49353 | Enterprise Data | Urban | 72 |  | 5.2081 | 163.41 | [7 empty] | 1 | 1.1171e-06 | 1.1171e-06
49357 | Prestige Ave | Urban | 958 | 2.1731 | 7.3 | 392.13 |  |  | 36 | 0.17398 | 0.17398 | 0.00084454 | 0.00084454 | 36 | 0.0012065 | 0.0012065
49362 | Greenhill Drive | Urban | 980 |  | 8.0968 | 203.97 |  |  | 36 | 0.33502 | 0.33502 | 0.010899 | 0.010899 | 36 | 0.0015282 | 0.0015282
49366 | Inglewood Place | Urban | 354 |  | 4.7831 | 196.45 |  |  | 1 | 0.094325 | 0.094325 | 0.0015696 | 0.0015696
49382 | Norwest Marketown | Urban | 255 |  | 3.4608 | 188.76 |  |  | 1 | 0.016244 | 0.016244 | 0.00014634 | 0.00014634
49391 | Whitby Road | Urban | 694 |  | 5.0774 | 153.16 |  |  | 1 | 0.00014858 | 0.00014858 | 1.1171e-06 | 1.1171e-06
49914 | Dublin Street | Urban | 640 | 4.0572 | 0.62901 | 125.77 |  |  | 16 | 0.34502 | 0.34502 | 0.0065061 | 0.0065061
49915 | Charles Street | Urban | 945 | 4.9026 | 0.2605 | 150.5 |  |  | 8 | 0.0055543 | 0.0055543 | 2.2342e-05 | 2.2342e-05 | 8 | 0.0001698 | 0.0001698
49916 | Hamilton Rd | Urban | 892 | 2.1479 | 4.3374 | 164.7 |  |  | 8 | 0.029867 | 0.029867 | 6.7027e-05 | 6.7027e-05 | 8 | 0.00016087 | 0.00016087
49917 | Victoria Street | Urban | 288 | 2.8801 | 1.1771 | 176.43 | [7 empty] | 2 | 0.00034184 | 0.00034184
49918 | Hamersley St + Aux No 1 | Urban | 1152 | 1.6651 | 6.231 | 216.7 |  |  | 6 | 0.0112 | 0.0112 | 0.00026811 | 0.00026811 | 6 | 0.00017539 | 0.00017539
52237 | Bonnyrigg Ave | Urban | 572 |  | 6.9999 | 192.39 |  |  | 1 | 0.000744 | 0.000744 | 2.0108e-05 | 2.0108e-05 | 1 | 5.5856e-06 | 5.5856e-06
52238 | Kinghorne Rd & Aux No. 3 | Urban | 1394 | 0.21478 | 8.4941 | 277.61 |  |  | 100 | 0.45677 | 0.45677 | 0.0022342 | 0.0022342 | 100 | 0.0018712 | 0.0018712
53312 | Spare & Ninth Ave | Urban | 1156 |  | 11.4757 |  |  |  | 2 | 0.00014969 | 0.00014969 | 2.2342e-06 | 2.2342e-06 | 2 | 8.937e-06 | 8.937e-06
53314 | Crimson St & Spare | Urban | 611 | 22.9494 | 8.3738 |  |  |  | 4 | 0.018875 | 0.018875 | 9.8307e-05 | 9.8307e-05 | 4 | 5.3622e-05 | 5.3622e-05
53801 | Rosella St & Aux No.3 | Urban | 629 |  | 3.8588 | 103.16 |  |  | 1 | 0.00017315 | 0.00017315 | 1.1171e-06 | 1.1171e-06
53803 | Joshua Moore Drive | Urban | 814 | 0.06855 | 5.4914 | 220.71 |  |  | 9 | 0.0086465 | 0.0086465 | 0.00017092 | 0.00017092
53809 | Parkers Farm Pl | Urban | 46 |  | 3.186 | 98.82 | [7 empty] | 1 | 2.2342e-06 | 2.2342e-06
5464 | Charles St | Urban | 921 | 0.30926 | 2.4011 | 177.79 |  |  | 50 | 1.0423 | 1.0423 | 0.010222 | 0.010222 | 50 | 0.00047478 | 0.00047478
54647 | Shale Place & Aux No.1 | Urban | 17 |  | 2.5062 | 33.55 |  |  | 1 | 0.0057487 | 0 | 0 | 0
54649 | Mirvac Estate | Urban | 4 | 2.0644 | 0.52486 | 6.41 |  |  | 2 | 0.0027034 | 0 | 0 | 0 | 2 | 8.937e-06 | 8.937e-06
54656 | CML Shared | Urban | 1 |  | 0.90873 | 49.59 |  |  | 2 | 0.0004435 | 0.00021225 | 2.2342e-06 | 2.2342e-06
54658 | Eastern Creek Dr | Urban | 7 |  | 1.9952 | 30.58 |  |  | 1 | 0.0023672 | 0 | 0 | 0 | 1 | 4.4685e-06 | 4.4685e-06
54663 | CML Cold Storage | Urban | 5 |  | 0.30413 | 113.29 |  |  | 1 | 0.0016902 | 0 | 0 | 0
54665 | Old Wallgrove Rd West | Urban | 6 | 1.8747 | 1.9927 | 202.42 |  |  | 1 | 0.0020287 | 0 | 0 | 0
54667 | Hewlett Packard No.2 | Urban | 1 |  | 0.45011 |  |  |  | 1 | 0.00033737 | 0 | 0 | 0
5467 | Horwood Pl | Urban | 84 |  | 0.58928 | 49.32 |  |  | 1 | 0.0018734 | 0.0018734 | 2.346e-05 | 2.346e-05
54679 | Southridge St West | Urban | 17 |  | 1.8057 | 25.74 |  |  | 1 | 0.0057487 | 0 | 0 | 0 | 1 | 1.1171e-06 | 1.1171e-06
54686 | CML NDC | Urban | 4 |  | 0.71788 | 70.34 |  |  | 1 | 0.0013517 | 0 | 0 | 0
54688 | Shale Pl & Aux No.2 | Urban | 11 |  | 2.4884 | 37.29 |  |  | 1 | 0.0037189 | 0 | 0 | 0
54695 | Southridge Street East | Urban | 5 | 1.2395 | 1.2595 | 220.48 |  |  | 2 | 0.0017282 | 7.5964e-05 | 2.2342e-06 | 2.2342e-06
5472 | Phillip + Valentine St | Urban | 456 |  | 1.8355 | 240.95 |  |  | 1 | 0.0071049 | 0.0071049 | 4.4685e-05 | 4.4685e-05
5475 | Council Chambers | Urban | 298 |  | 2.2017 | 234.25 |  |  | 1 | 0.0094452 | 0.0094452 | 1.1171e-05 | 1.1171e-05
5494 | Pennant Hills Rd & Cap Bank 1 | Urban | 826 | 1.6319 | 4.3556 | 184.81 |  |  | 20 | 0.085125 | 0.085125 | 0.00026811 | 0.00026811 | 20 | 0.000496 | 0.000496
5495 | Epping Rd | Urban | 1584 | 4.2578 | 2.372 | 261.04 |  |  | 18 | 2.1013 | 2.1013 | 0.029257 | 0.029257 | 18 | 0.0002413 | 0.0002413
5496 | Warwick Rd + A/F Cell No 1 | Urban | 969 | 7.7205 | 1.1776 | 187.1 |  |  | 1053 | 31.1758 | 31.1758 | 0.28742 | 0.28742 | 1053 | 0.027146 | 0.027146
5498 | Dundas Valley | Urban | 2356 | 6.2841 | 1.5348 | 261.85 |  |  | 48 | 0.010403 | 0.010403 | 5.3622e-05 | 5.3622e-05 | 48 | 0.0028017 | 0.0028017
5499 | Sargents Rd | Urban | 2 |  | 4.0929 | 175.81 |  |  | 1 | 1.8991e-05 | 1.8991e-05 | 2.2342e-06 | 2.2342e-06
5500 | Hewitt St | Urban | 739 | 2.7 | 3.135 | 154.12 |  |  | 48 | 0.22544 | 0.22544 | 0.0094106 | 0.0094106 | 48 | 0.0016623 | 0.0016623
5501 | Rebecca St | Rural Short | 993 | 9.4303 | 13.3994 | 217.4 |  |  | 49 | 0.8509 | 0.8509 | 0.015671 | 0.015671
5503 | St Clair Ave | Urban | 807 |  | 6.1871 | 149.79 |  |  | 18 | 0.049332 | 0.049332 | 0.0044171 | 0.0044171 | 18 | 0.00010054 | 0.00010054
5504 | Woodlands Rd + Aux No 1 | Urban | 114 | 0.38765 | 0.60053 | 34.3 |  |  | 1 | 0.0010881 | 0.0010881 | 0.00010278 | 0.00010278
5506 | Desborough St + Aux No 2 | Urban | 1288 | 6.7211 | 1.9329 | 266.28 |  |  | 150 | 5.8418 | 5.8418 | 0.077953 | 0.077953 | 150 | 0.010473 | 0.010473
5507 | Tanderra St | Urban | 153 | 0.65394 | 0.03174 | 24.59 |  |  | 4 | 0.018645 | 0.018645 | 0.00061665 | 0.00061665
5509 | Melville Rd | Urban | 1093 | 3.4417 | 4.2679 | 223.49 |  |  | 50 | 0.13557 | 0.13557 | 0.010009 | 0.010009 | 50 | 0.0044406 | 0.0044406
5510 | No 2 Tie | Urban | 812 |  | 5.7199 | 172.27 |  |  | 16 | 0.045914 | 0.045914 | 0.0030698 | 0.0030698 | 16 | 0.00071496 | 0.00071496
55167 | Queen St | Urban | 601 | 2.9173 | 6.7903 | 197.64 |  |  | 4 | 0.014129 | 0.014129 | 5.809e-05 | 5.809e-05
55169 | Pearson Cres | Urban | 912 | 0.11612 | 9.292 | 263.61 | [7 empty] | 1 | 1.1171e-06 | 1.1171e-06
55175 | Harrison Ave | Urban | 664 |  | 8.3169 | 226.53 |  |  | 4 | 0.0035212 | 0.0035212 | 7.373e-05 | 7.373e-05
55177 | AUXILLARY NUMBER 1 & Pains Pl | Urban | 780 |  | 5.3908 | 147.44 |  |  | 1 | 0.0054337 | 0.0054337 | 3.5748e-05 | 3.5748e-05 | 1 | 0.00018991 | 0.00018991
55354 | Palomino Rd & Auxiliary No 1 | Rural Short | 1063 | 16.5153 | 2.2301 | 261.02 |  |  | 108 | 1.5781 | 1.5781 | 0.038185 | 0.038185 | 108 | 0.0098932 | 0.0098932
55356 | Bunyan Rd | Urban | 609 | 5.363 | 2.6004 | 149.94 |  |  | 1 | 0.96272 | 0.96272 | 0.00070043 | 0.00070043
55361 | Troy St | Urban | 631 | 3.8512 | 2.1045 | 156.79 |  |  | 4 | 0.0093637 | 0.0093637 | 6.7027e-05 | 6.7027e-05
55864 | Stockland Mall | Urban | 181 |  | 2.0516 | 160.93 |  |  | 1 | 0.018411 | 0.018411 | 0.00019773 | 0.00019773
55866 | Glanmire Road | Urban | 447 | 3.1211 | 0.05536 | 96.64 |  |  | 9 | 0.18993 | 0.18993 | 0.0018265 | 0.0018265 | 9 | 0.00032173 | 0.00032173
55867 | Cropley Drive | Urban | 866 | 2.181 | 4.1108 | 209.66 |  |  | 25 | 0.54 | 0.54 | 0.0051723 | 0.0051723 | 25 | 0.00086577 | 0.00086577
55870 | Vanessa Avenue | Urban | 824 | 5.1741 | 1.0929 | 301.71 |  |  | 16 | 0.36785 | 0.36785 | 0.0039591 | 0.0039591 | 16 | 0.00060771 | 0.00060771
55874 | Sarah Crescent | Urban | 1331 | 5.4879 | 0.64995 | 369.91 |  |  | 343 | 18.7503 | 18.7503 | 0.24966 | 0.24966 | 343 | 0.018173 | 0.018173
55875 | Hilda Road | Urban | 919 | 6.2344 | 1.3815 | 177.37 |  |  | 72 | 1.2825 | 1.2825 | 0.014411 | 0.014411 | 72 | 0.006314 | 0.006314
55876 | Burrell Cres | Urban | 1494 | 4.71 | 1.8856 | 244 |  |  | 8 | 0.6405 | 0.6405 | 0.0067608 | 0.0067608 | 8 | 0.00013405 | 0.00013405
55879 | Gooden Crescent | Urban | 642 | 4.6795 | 1.0293 | 136.68 |  |  | 9 | 0.2051 | 0.2051 | 0.0021784 | 0.0021784
55880 | Palace Road | Urban | 254 | 3.026 | 0.08655 | 56 |  |  | 4 | 0.060988 | 0.060988 | 0.00060324 | 0.00060324 | 4 | 4.9153e-05 | 4.9153e-05
55885 | Lindsay Street | Urban | 1895 | 9.0059 | 2.7071 | 324.27 |  |  | 540 | 17.6098 | 17.6098 | 0.3904 | 0.3904 | 540 | 0.027789 | 0.027789
55888 | Turon Avenue | Urban | 229 | 2.4793 | 0.72449 |  |  |  | 1 | 0.023294 | 0.023294 | 0.00025023 | 0.00025023 | 1 | 2.0108e-05 | 2.0108e-05
55890 | Kentwell Street | Urban | 1551 | 7.1583 | 1.5936 | 243.75 |  |  | 144 | 11.4658 | 11.4658 | 0.14824 | 0.14824 | 144 | 0.0046651 | 0.0046651
55891 | Suttor Place | Urban | 181 | 1.0809 | 3.0601 | 51.07 |  |  | 9 | 0.092038 | 0.092038 | 0.00084789 | 0.00084789
57040 | O'Connell St | Urban | 335 |  | 3.4779 | 219.02 |  |  | 1 | 0.0027358 | 0.0027358 | 4.5802e-05 | 4.5802e-05
57444 | Kirkconnell | Rural Short | 50 | 16.5214 |  | 1.44 |  |  | 64 | 1.1945 | 1.1945 | 0.0025202 | 0.0025202 | 64 | 0.00064346 | 0.00064346
57448 | Mount Lambie | Rural Short | 127 | 62.1244 |  | 13.78 |  |  | 3150 | 10.2861 | 10.2861 | 0.054661 | 0.054661 | 3150 | 0.031168 | 0.031168
5867 | Pendant Av | Urban | 996 | 3.6875 | 2.4892 | 263.27 |  |  | 11 | 0.062609 | 0.062609 | 0.00043009 | 0.00043009 | 11 | 0.0003653 | 0.0003653
5868 | Locke St & Cap Bank 1 | Urban | 74 |  | 1.5149 | 280.66 | [7 empty] | 1 | 6.2559e-05 | 6.2559e-05
5869 | James St | Urban | 876 | 3.6179 | 1.2365 | 122.69 | [7 empty] | 5 | 0.0002547 | 0.0002547
5871 | Panorama Pde | Urban | 692 | 2.7465 | 2.7299 | 143.65 | [7 empty] | 1 | 0.00038652 | 0.00038652
5872 | Lucretia Rd + Aux No 1 | Urban | 733 | 4.3021 | 0.14088 | 168.24 |  |  | 48 | 1.9554 | 1.9554 | 0.025604 | 0.025604 | 48 | 0.0064525 | 0.0064525
5874 | Federal Rd + Aux No 2 | Urban | 1419 | 1.3773 | 2.8279 | 123.64 |  |  | 3 | 0.4951 | 0.4951 | 0.0047589 | 0.0047589 | 3 | 0.00022454 | 0.00022454
5875 | Beaufort St ß& Cap Bank 2 | Urban | 1075 | 6.828 | 0.06627 | 273.21 |  |  | 5 | 0.013685 | 0.013685 | 0.00013964 | 0.00013964 | 5 | 0.00016422 | 0.00016422
5877 | St Martins Cres | Urban | 429 | 1.2163 | 1.5354 | 109.5 |  |  | 6 | 0.001488 | 0.001488 | 0.001488 | 0.001488 | 6 | 0.0003329 | 0.0003329
5878 | Orana Av | Urban | 475 | 2.009 | 0.53211 | 188.16 | [7 empty] | 4 | 0.00014634 | 0.00014634
5898 |  | Rural Short | [11 empty] | 3 | 3.3514e-06 | 3.3514e-06
61617 | Tahmoor | Rural Short | 449 | 16.5642 | 0.40614 | 120.85 |  |  | 216 | 9.0879 | 9.0879 | 0.073596 | 0.073596 | 216 | 0.0067563 | 0.0067563
6419 | Scrivener St | Urban | 501 | 3.65 | 2.0448 | 176.71 |  |  | 2 | 0.14661 | 0.2854 | 0.0039859 | 0.0039859 | 2 | 2.2342e-06 | 2.2342e-06
6420 | Seton St & Cap Bank1 | Urban | 270 | 2.5968 | 1.4211 | 283.19 |  |  | 9 | 0.041309 | 0.041309 | 0.0010523 | 0.0010523 | 9 | 0.00012065 | 0.00012065
6421 | Longstaff + CMA Standby | Urban | 572 | 5.702 | 5.6566 | 242.11 |  |  | 720 | 14.4373 | 14.4373 | 0.16851 | 0.16851 | 720 | 0.012065 | 0.012065
6423 | Maddecks Av | Urban | 944 | 3.1524 | 3.2669 | 197.55 |  |  | 1 | 0.014765 | 0.014765 | 6.9261e-05 | 6.9261e-05 | 1 | 2.2342e-06 | 2.2342e-06
6424 | Metal Recyclers + Aux No 1 | Urban | 776 | 5.0256 | 3.369 | 258.11 |  |  | 9 | 0.19378 | 0.19378 | 0.0028822 | 0.0028822
6429 | Regent Cres | Urban | 95 | 1.3721 | 0.89091 | 101.87 | [7 empty] | 1 | 1.8991e-05 | 1.8991e-05
6430 | Nuwarra Rd | Urban | 728 | 5.4358 | 1.0136 | 146.1 |  |  | 18 | 1.0162 | 1.0162 | 0.0052951 | 0.0052951 | 18 | 2.0108e-05 | 2.0108e-05
68179 | Maud St | Urban | 849 | 3.2778 | 0.16958 | 122.6 |  |  | 4 | 0.2429 | 0.2429 | 0.0037937 | 0.0037937 | 4 | 0.00021449 | 0.00021449
68181 | Gipps St | Urban | 996 | 2.8631 | 3.2913 | 197.14 |  |  | 243 | 1.5558 | 1.5558 | 0.1062 | 0.1062 | 243 | 0.0049768 | 0.0049768
68186 | Polding St | Urban | 495 | 1.798 | 1.119 | 183.74 | [7 empty] | 1 | 2.2342e-05 | 2.2342e-05
68188 | Tasman Pde | Urban | 892 | 4.4497 | 0.29626 | 165.73 |  |  | 18 | 0.2919 | 0.2919 | 0.0017427 | 0.0017427 | 18 | 0.00017092 | 0.00017092
68190 | O'Connell St | Urban | 359 | 2.2527 | 1.6606 | 162.47 |  |  | 1 | 0.0012333 | 0.0012333 | 4.2451e-05 | 4.2451e-05
68195 | Rawson Rd | Urban | 989 | 4.0279 | 0.31055 | 143.91 |  |  | 125 | 3.9687 | 3.9687 | 0.033709 | 0.033709 | 125 | 0.0016478 | 0.0016478
68197 | Thorney Rd | Urban | 728 | 5.1865 | 0.58801 | 119.96 |  |  | 1 | 0.008842 | 0.008842 | 6.591e-05 | 6.591e-05
68204 | Smithfield Rd | Urban | 1049 | 2.0276 | 6.9786 | 217.23 |  |  | 50 | 0.030442 | 0.030442 | 0.00067027 | 0.00067027 | 50 | 0.001955 | 0.001955
7008 |  | Urban | [11 empty] | 1 | 1.1171e-06 | 1.1171e-06
7013 |  | Urban | [11 empty] | 1 | 6.2559e-05 | 6.2559e-05
7091 |  | Rural Short | [6 empty] | 4 | 0.0062737 | 0.0062737 | 4.0216e-05 | 4.0216e-05
7507 |  | Urban | [6 empty] | 1 | 2.2342e-05 | 2.2342e-05 | 2.2342e-06 | 2.2342e-06
7530 |  | Rural Short | [6 empty] | 1 | 0.0050851 | 0.0050851 | 2.2342e-06 | 2.2342e-06
7532 |  | Rural Short | [6 empty] | 1 | 0.00018097 | 0.00018097 | 1.1171e-06 | 1.1171e-06
7539 |  | Rural Short | [6 empty] | 1 | 2.2342e-06
76225 | Bylong North | Rural Short |  | 18.5128 |  |  |  |  | 216 | 0.9405 | 0.9405 | 0.0049868 | 0.0049868 | 216 | 0.0015282 | 0.0015282
77674 | Ilford Hall Rd | Rural Short | 22 | 23.0557 | 0.14204 | 27.33 |  |  | 98 | 0.85973 | 0.85973 | 0.010385 | 0.010385 | 98 | 0.00049265 | 0.00049265
7908 |  | Rural Short | [6 empty] | 1 | 0.00060101 | 0.00060101 | 1.1171e-06 | 1.1171e-06
7910 |  | Rural Short | [6 empty] | 9 | 0.0025571 | 0.0025571 | 1.0054e-05 | 1.0054e-05
796 |  | Rural Short | [6 empty] | 1 | 0.00028151 | 0.00028151 | 1.1171e-06 | 1.1171e-06
7962 | Braeside Rd | Urban | 851 | 5.114 | 0.32468 | 158.41 |  |  | 294 | 18.2389 | 18.2389 | 0.21311 | 0.21311 | 294 | 0.006295 | 0.006295
7964 | Daffodil St | Urban | 288 | 2.1481 | 0.07137 | 153.53 |  |  | 9 | 0.24188 | 0.24188 | 0.0032374 | 0.0032374 | 9 | 0.00043233 | 0.00043233
7966 | Bolaro Av | Urban | 518 | 4.2927 | 0.07845 | 104.3 |  |  | 32 | 1.3816 | 1.3816 | 0.019867 | 0.019867 | 32 | 0.001555 | 0.001555
7967 | Cumberland Rd + Aux No 1 | Urban | 97 | 0.36701 | 0.28293 | 91.05 |  |  | 36 | 0.32586 | 0.32586 | 0.0043568 | 0.0043568 | 36 | 0.00080433 | 0.00080433
7970 | Betts Rd + Aux No 1 | Urban | 731 | 5.5054 | 1.3476 | 219.58 |  |  | 405 | 16.602 | 16.602 | 0.21063 | 0.21063 | 405 | 0.038819 | 0.038819
7972 | Rosewall St | Urban | 597 | 4.5851 | 1.0727 | 137.44 |  |  | 128 | 6.4431 | 6.4431 | 0.092873 | 0.092873 | 128 | 0.0026453 | 0.0026453
7973 | Merrylands Rd West | Urban | 311 | 2.0572 | 0.18088 | 67.16 |  |  | 9 | 0.2612 | 0.2612 | 0.0034988 | 0.0034988 | 9 | 4.0216e-05 | 4.0216e-05
7974 | Terry St | Urban | 928 | 4.978 | 0.44637 | 252.14 |  |  | 64 | 4.1709 | 4.1709 | 0.05616 | 0.05616 | 64 | 0.00071496 | 0.00071496
7976 | Eldridge Rd | Urban | 1218 | 5.7803 | 0.76742 | 246.35 |  |  | 128 | 6.2918 | 6.2918 | 0.098485 | 0.098485 | 128 | 0.0021449 | 0.0021449
7977 | Fox Industries | Urban | 143 | 2.8484 | 0.52636 | 191.83 |  |  | 98 | 0.69822 | 0.69822 | 0.0081639 | 0.0081639 | 98 | 0.0020253 | 0.0020253
7979 | Warren Rd | Urban | 303 | 6.2874 | 0.80848 | 154.66 |  |  | 18 | 0.50896 | 0.50896 | 0.0068167 | 0.0068167 | 18 | 0.00011059 | 0.00011059
7994 | Milson Rd | Urban | 1393 | 1.6317 | 8.0582 | 215.83 |  |  | 288 | 14.0683 | 14.0683 | 0.090031 | 0.090031 | 288 | 0.012869 | 0.012869
7995 | OTC | Urban | 216 | 0.89579 | 5.4966 | 50.27 |  |  | 4 | 0.17282 | 0.17282 | 0.0010814 | 0.0010814 | 4 | 0.00030162 | 0.00030162
7996 | Rankin Pl | Urban | 90 |  | 0.84179 | 10.61 |  |  | 1 | 0.018002 | 0.018002 | 0.00011283 | 0.00011283
845 |  | Rural Short | [6 empty] | 1 | 6.0324e-05 | 6.0324e-05 | 1.1171e-06 | 1.1171e-06
8610 | Rowley St | Urban | 1556 | 8.4002 | 0.74865 | 234.93 |  |  | 153 | 14.534 | 14.534 | 0.098165 | 0.098165 | 153 | 0.012487 | 0.012487
8611 | Abbott Rd | Urban | 161 | 1.208 | 1.516 | 99.71 | [7 empty] | 2 | 2.2342e-06 | 2.2342e-06
8614 | Drum Reconditioners & Cap Bank 1 | Urban | 24 |  | 1.2657 | 282.94 |  |  | 1 | 0.0047053 | 0.0047053 | 1.4523e-05 | 1.4523e-05
8615 | Park Rd + Aux No 1 | Urban | 621 | 4.0777 | 0.64548 | 112.68 |  |  | 54 | 1.3866 | 1.3866 | 0.01299 | 0.01299 | 54 | 0.0066457 | 0.0066457
8617 | Lowana Cres | Urban | 384 | 2.6051 | 1.628 | 278.83 |  |  | 3 | 0.0015986 | 0.0015986 | 3.3514e-06 | 3.3514e-06 | 3 | 0.00018879 | 0.00018879
8620 | Barangaroo Rd | Urban | 1016 | 3.4692 | 2.7185 | 155.83 |  |  | 392 | 14.202 | 14.202 | 0.11567 | 0.11567 | 392 | 0.020801 | 0.020801
8622 | Powers Rd + Aux No 2 | Urban | 139 | 1.5725 | 0.98104 | 98.39 | [7 empty] | 4 | 2.6811e-05 | 2.6811e-05
8633 | Halcrows Rd | Rural Short | 216 | 20.5285 | 0.18506 | 62.56 |  |  | 128 | 0.47859 | 0.47859 | 0.0092944 | 0.0092944 | 128 | 0.00073283 | 0.00073283
8634 | Sackville | Rural Short | 630 | 98.3945 | 1.9684 | 116.85 |  |  | 15876 | 359.8554 | 359.8554 | 3.6138 | 3.6138 | 15876 | 0.35668 | 0.35668
8635 | Ebenezer | Rural Short | 726 | 56.3677 | 0.1842 | 194.68 |  |  | 2660 | 41.0924 | 43.0806 | 0.22099 | 0.22099 | 2660 | 0.077685 | 0.077685
8636 | Maroota | Rural Short | 532 | 52.0462 | 3.4146 | 129.93 |  |  | 1050 | 67.1699 | 71.8889 | 0.29685 | 0.29685 | 1050 | 0.014779 | 0.014779
8637 | Mitchell Park | Rural Short | 638 | 35.605 | 0.53322 | 173.18 |  |  | 832 | 14.5166 | 14.5166 | 0.10758 | 0.10758 | 832 | 0.019661 | 0.019661
8641 | Roseberry Rd | Urban | 797 | 0.17957 | 6.9565 | 252.38 | [7 empty] | 3 | 4.4685e-05 | 4.4685e-05
8647 | James Mileham Dr & Aux No 3 | Urban | 598 |  | 3.6589 | 200.25 |  |  | 1 | 0.010111 | 0.010111 | 0.00067362 | 0.00067362
8648 | Glenhaven Rd | Urban | 787 | 9.937 | 5.0436 | 281.48 |  |  | 16 | 0.32807 | 0.32807 | 0.0081192 | 0.0081192 | 16 | 0.00014299 | 0.00014299
8650 | Stringers Rd & A/T 5 | Urban | 75 | 1.7865 | 0.37964 | 73.26 |  |  | 8 | 0.0074534 | 0.0074534 | 0.00034407 | 0.00034407 | 8 | 0.00028151 | 0.00028151
8651 | Malonga Av | Urban | 579 | 1.9453 | 2.41 | 127.87 |  |  | 9 | 0.030631 | 0.030631 | 0.0019639 | 0.0019639 | 9 | 0.000744 | 0.000744
8652 | Craigmore Drive & Cap Bank 3 | Urban | 713 | 0.6397 | 8.8157 | 217.65 |  |  | 4 | 0.048224 | 0.048224 | 0.0032128 | 0.0032128 | 4 | 5.4739e-05 | 5.4739e-05
8675 | Stuart Rd | Urban | 846 | 4.8677 | 0.65675 | 138.5 |  |  | 8 | 0.01644 | 0.01644 | 0.00027705 | 0.00027705 | 8 | 0.00091157 | 0.00091157
8676 | Kilbride Av | Urban | 1089 | 3.4903 | 1.9032 | 134.83 |  |  | 5 | 0.002089 | 0.002089 | 5.5856e-06 | 5.5856e-06 | 5 | 4.1333e-05 | 4.1333e-05
8677 | Bunsen Av | Urban | 439 | 3.1516 | 0.72984 | 85.53 |  |  | 5 | 0.0011674 | 0.0011674 | 5.5856e-06 | 5.5856e-06 | 5 | 0.00052281 | 0.00052281
8679 | Hardy St | Urban | 1144 | 2.9852 | 5.7219 | 179.25 |  |  | 648 | 3.2918 | 3.2918 | 0.016087 | 0.016087 | 648 | 0.032756 | 0.032756
8680 | Keesing Cres + Aux No.1 | Urban | 1392 | 2.9412 | 4.2322 | 204.71 |  |  | 63 | 0.18191 | 0.18191 | 0.00051611 | 0.00051611 | 63 | 0.0021214 | 0.0021214
8682 | Stevenage Rd | Urban | 825 | 3.4404 | 4.6151 | 156.37 | [7 empty] | 1 | 1.6757e-05 | 1.6757e-05
8683 | Pringle Rd | Urban | 1121 | 2.6698 | 4.4737 | 187.87 |  |  | 1 | 0.0017081 | 0.0017081 | 4.6919e-05 | 4.6919e-05
8685 | Popondetta Rd | Urban | 1593 | 1.8451 | 6.309 | 190.54 |  |  | 968 | 6.2302 | 6.2302 | 0.027133 | 0.027133 | 968 | 0.031089 | 0.031089
8686 | Bougainville Rd | Urban | 755 | 5.1226 | 1.8773 | 131.49 |  |  | 6 | 0.024271 | 0.024271 | 0.00022119 | 0.00022119 | 6 | 0.00046807 | 0.00046807
8689 | Emert Pde + Aux No 3 | Urban | 635 | 3.2876 | 0.70464 | 106.75 |  |  | 20 | 0.57767 | 0.57767 | 0.0075517 | 0.0075517 | 20 | 0.00021002 | 0.00021002
8690 | Cooma St | Urban | 800 | 4.2024 | 0.56412 | 113.76 |  |  | 1 | 0.010416 | 0.010416 | 0.00089146 | 0.00089146
8693 | Mariana Cres | Urban | 393 | 3.0031 | 0.41951 | 161.17 |  |  | 36 | 1.27 | 1.27 | 0.028433 | 0.028433 | 36 | 0.002404 | 0.002404
8694 | Boldrewood Rd | Urban | 1389 | 3.208 | 6.8669 | 193.98 |  |  | 125 | 0.53641 | 0.53641 | 0.0019829 | 0.0019829 | 125 | 0.0045802 | 0.0045802
8711 | Delaware Rd + Aux No 2 | Rural Short | 673 | 20.3602 | 5.691 | 229.91 |  |  | 40 | 0.46202 | 0.46202 | 0.0014076 | 0.0014076 | 40 | 0.0011841 | 0.0011841
8716 | Saxony Rd | Urban | 817 | 9.9805 | 4.3639 | 259.87 |  |  | 1 | 0.16412 | 0.16412 | 0.0024923 | 0.0024923 | 1 | 1.2288e-05 | 1.2288e-05
8718 | Burley Rd + Aux No 3 | Urban | 198 | 6.3691 | 0.15203 | 176.63 |  |  | 2 | 0.067027 | 0.067027 | 0.00043568 | 0.00043568 | 2 | 2.7928e-05 | 2.7928e-05
8721 | Wonderland | Urban | 15 | 3.7617 | 2.2864 | 136.04 |  |  | 1 | 0.0017114 | 0.0017114 | 1.6757e-05 | 1.6757e-05 | 1 | 1.1171e-06 | 1.1171e-06
87218 | Charbon Clandulla | Rural Short | 235 | 49.1273 | 0.39051 |  |  |  | 30 | 1.3264 | 1.5768 | 0.0056437 | 0.0056437
87220 | Rylstone | Rural Short | 711 | 184.0855 | 0.17365 |  |  |  | 72 | 0.62346 | 0.62346 | 0.024009 | 0.024009 | 72 | 0.00052281 | 0.00052281
87222 |  | Rural Short | [6 empty] | 27 | 1.51 | 1.51 | 0.0048863 | 0.0048863 | 27 | 4.0216e-05 | 4.0216e-05
87223 | APC Works | Rural Short | 428 | 5.0797 | 0.11421 |  |  |  | 1 | 0.002909 | 0.002909 | 2.346e-05 | 2.346e-05
8734 | Denistone Rd | Urban | 587 | 4.6765 | 1.0902 | 135.88 |  |  | 18 | 0.082182 | 0.082182 | 0.00070379 | 0.00070379 | 18 | 6.0324e-05 | 6.0324e-05
8735 | Yalding Av | Urban | 556 | 4.3096 | 1.1482 | 158.38 |  |  | 4 | 0.20812 | 0.20812 | 0.0024845 | 0.0024845
8737 | Barclay Rd | Urban | 709 | 2.6986 | 4.325 | 173.48 |  |  | 100 | 2.122 | 2.122 | 0.019617 | 0.019617 | 100 | 0.0043009 | 0.0043009
8738 | Caprera Rd + Aux No 1 | Urban | 1298 | 5.9002 | 1.1311 | 209.11 |  |  | 275 | 5.3283 | 5.3283 | 0.16319 | 0.16319 | 275 | 0.028933 | 0.028933
8740 | North Rocks Rd | Urban | 2 |  | 0.60291 | 117.4 | [7 empty] | 1 | 1.1171e-06 | 1.1171e-06
8741 | Stirling Av | Urban | 405 | 2.8772 | 1.2838 | 178.28 |  |  | 1 | 0.13648 | 0.13648 | 0.0004502 | 0.0004502 | 1 | 1.1171e-06 | 1.1171e-06
8743 | Becky Av + Aux No 2 | Urban | 742 | 4.7662 | 0.53388 | 151.99 |  |  | 25 | 0.86168 | 0.86168 | 0.012791 | 0.012791
8744 | Rifle Range Rd | Urban | 571 | 3.3618 | 1.649 | 151.22 | [7 empty] | 7 | 0.00079986 | 0.00079986
8762 | Hemphill Ave & Cap. Bank 1 | Urban | 1553 | 7.5057 | 1.1492 | 302.26 |  |  | 80 | 4.581 | 4.581 | 0.039434 | 0.039434 | 80 | 0.0028062 | 0.0028062
8764 | Wearne Rd | Urban | 1359 | 4.2836 | 2.6213 | 187.68 | [7 empty] | 8 | 0.00033849 | 0.00033849
8766 | Madson Pl | Urban | 1074 | 0.06867 | 7.6844 | 160.53 |  |  | 50 | 0.098351 | 0.098351 | 0.00061442 | 0.00061442 | 50 | 0.002709 | 0.002709
8767 | Humphries Rd + Aux No 1 | Urban | 487 | 3.3095 | 0.85799 | 234.63 |  |  | 32 | 0.27861 | 0.27861 | 0.0016623 | 0.0016623 | 32 | 0.0027883 | 0.0027883
8769 | Montgomery Rd + Aux No 2 | Urban | 434 |  | 3.3628 | 66.4 |  |  | 2 | 0.00013405 | 0.00013405 | 2.2342e-06 | 2.2342e-06 | 2 | 0.00016533 | 0.00016533
8770 | Edna Av | Urban | 932 | 4.8406 | 0.7474 | 165.58 |  |  | 252 | 2.3997 | 2.3997 | 0.0093369 | 0.0093369 | 252 | 0.0094106 | 0.0094106
8772 | Bradfield Cres | Urban | 376 |  | 2.8863 | 132.64 |  |  | 4 | 0.0081706 | 0.0081706 | 0.00014523 | 0.00014523 | 4 | 4.4685e-06 | 4.4685e-06
8773 | Kalang Rd | Urban | 1392 |  | 10.4496 | 319.88 |  |  | 50 | 3.3458 | 3.3458 | 0.016701 | 0.016701 | 50 | 0.00047478 | 0.00047478
8774 | Homestead Rd | Urban | 1376 |  | 10.2935 | 281.79 |  |  | 48 | 0.22325 | 0.22325 | 0.00061665 | 0.00061665 | 48 | 0.0018768 | 0.0018768
8776 | Holdin St | Urban | 490 |  | 2.3425 | 166.88 |  |  | 196 | 0.62133 | 0.62133 | 0.0038161 | 0.0038161 | 196 | 0.002518 | 0.002518
8777 | Bishop Cr | Urban | 674 |  | 4.0975 | 127.37 |  |  | 9 | 0.021207 | 0.021207 | 6.7027e-05 | 6.7027e-05 | 9 | 0.00010054 | 0.00010054
8779 | Bulls Rd | Urban | 1005 | 0.27082 | 5.9373 | 216.59 |  |  | 36 | 0.17337 | 0.17337 | 0.001173 | 0.001173 | 36 | 0.00088476 | 0.00088476
8780 | Kemp St & Cap. Bank 3 | Urban | 692 |  | 4.5656 | 271.36 |  |  | 9 | 0.3897 | 0.3897 | 0.0025068 | 0.0025068
8781 | Porteous Street | Urban | 977 |  | 7.4807 | 193.37 |  |  | 1 | 4.3568e-05 | 4.3568e-05 | 1.1171e-06 | 1.1171e-06 | 1 | 8.937e-06 | 8.937e-06
8798 | Greggs Rd | Rural Short | 1078 | 31.8373 | 1.3302 | 184.58 |  |  | 1216 | 70.5538 | 70.5538 | 0.42332 | 0.42332 | 1216 | 0.21763 | 0.21763
8799 | Bilpin + Aux No 1 | Rural Short | 1089 | 56.3033 | 0.15202 | 163.89 |  |  | 3150 | 105.3241 | 105.3241 | 0.68783 | 0.68783 | 3150 | 0.1297 | 0.1297
8801 | Grose Vale Rd + Aux No 2 | Rural Short | 685 | 76.9117 | 2.4063 | 104.44 |  |  | 864 | 29.3565 | 29.3565 | 0.23438 | 0.23438 | 864 | 0.015443 | 0.015443
8802 | Comleroy Rd | Rural Short | 1037 | 47.559 | 0.92981 | 240.14 |  |  | 3332 | 133.1782 | 133.1782 | 0.87978 | 0.87978 | 3332 | 0.077948 | 0.077948
9016 | Stafford St | Urban | 661 | 1.4001 | 2.5104 | 275.74 |  |  | 1 | 0.017888 | 0.017888 | 0.00012177 | 0.00012177
9017 | Parker St | Urban | 329 | 1.6895 | 0.26298 | 196.18 |  |  | 1 | 0.005809 | 0.005809 | 5.809e-05 | 5.809e-05 | 1 | 0.00039658 | 0.00039658
9019 | Treetops Av | Urban | 1051 | 3.6279 | 2.725 | 203.91 |  |  | 49 | 1.8944 | 1.8944 | 0.01578 | 0.01578
9020 | Fragar Rd | Urban | 1073 | 1.3038 | 5.4259 | 220.76 |  |  | 250 | 0.81399 | 0.81399 | 0.0037424 | 0.0037424 | 250 | 0.0034351 | 0.0034351
9022 | Penrose Cres + Aux No 2 | Urban | 1011 | 4.2361 | 1.2619 | 223.41 |  |  | 3 | 0.2152 | 0.2152 | 0.0033715 | 0.0033715 | 3 | 0.00024688 | 0.00024688
9025 | Westmont Dr & Evan St | Urban | 2392 | 6.9707 | 8.2812 | 403.25 |  |  | 720 | 5.1524 | 5.1524 | 0.039613 | 0.039613 | 720 | 0.02783 | 0.02783
9026 |  | Urban | 2074 |  |  | 371.79 |  |  | 2 | 0.004283 | 0.004283 | 0.00031726 | 0.00031726 | 2 | 0.00010836 | 0.00010836
9027 | Hilliger Rd | Urban | 813 | 7.7528 | 3.483 | 223.7 |  |  | 4 | 0.0053309 | 0.0053309 | 2.6811e-05 | 2.6811e-05 | 4 | 7.8198e-05 | 7.8198e-05
9029 | Evans St + Aux No 3 | Urban | 810 | 4.0765 | 2.506 | 209.55 |  |  | 3 | 0.006877 | 0.006877 | 0.00012065 | 0.00012065 | 3 | 0.0001173 | 0.0001173
9030 |  | Urban | 1471 |  |  | 347.93 |  |  | 16 | 0.11423 | 0.11423 | 0.0074713 | 0.0074713 | 16 | 0.00021002 | 0.00021002
9032 | Angophora Av | Urban | 1453 | 6.1565 | 7.5835 | 287.35 |  |  | 160 | 11.5802 | 11.5802 | 0.11824 | 0.11824 | 160 | 0.0057911 | 0.0057911
9033 | Colless St | Urban | 1103 | 2.3553 | 1.4869 | 179.65 |  |  | 4 | 0.18175 | 0.18175 | 0.0045556 | 0.0045556
9034 | Lethbridge St | Urban | 524 | 1.2708 | 2.6949 | 359.24 |  |  | 25 | 0.12146 | 0.12146 | 0.00042451 | 0.00042451
9046 | Albert St | Urban | 1113 | 5.9361 | 0.2885 | 215.8 |  |  | 2 | 0.0069105 | 0.0069105 | 4.4685e-05 | 4.4685e-05 | 2 | 5.6973e-05 | 5.6973e-05
9047 | Myall St | Urban | 1112 | 3.9006 | 1.3077 | 148.7 |  |  | 36 | 0.32409 | 0.32409 | 0.0031101 | 0.0031101 | 36 | 0.00028151 | 0.00028151
9049 | Chetwynd Rd | Urban | 837 | 2.6081 | 0.75479 | 189.13 |  |  | 36 | 1.2472 | 1.2472 | 0.016589 | 0.016589
9050 | Amherst + Aux No 1 | Urban | 1580 | 4.6991 | 1.6658 | 196.31 |  |  | 16 | 1.3327 | 1.3327 | 0.0082175 | 0.0082175 | 16 | 0.00046472 | 0.00046472
9052 | Fowler Rd + Aux No 2 | Urban | 1168 | 4.3107 | 0.71177 | 158.43 |  |  | 6 | 1.184 | 0.60085 | 0.0039345 | 0.0039345 | 6 | 0.00022119 | 0.00022119
9055 | Harris St | Urban | 1596 | 2.6956 | 2.1067 | 144.98 |  |  | 4 | 0.057688 | 0.057688 | 0.00044015 | 0.00044015 | 4 | 0.00016533 | 0.00016533
9056 | Charlotte St | Urban | 1459 | 4.9205 | 1.5542 | 290.55 |  |  | 54 | 0.16967 | 0.16967 | 0.0015081 | 0.0015081 | 54 | 0.015584 | 0.015584
9057 | Mathews St | Urban | 671 | 1.2082 | 2.087 | 104.92 |  |  | 1 | 0.001345 | 0.001345 | 3.0162e-05 | 3.0162e-05 | 1 | 1.8991e-05 | 1.8991e-05
9059 | Bristol St | Urban | 974 | 4.8689 | 0.57246 | 147.88 |  |  | 100 | 4.8263 | 4.8263 | 0.036105 | 0.036105 | 100 | 0.0026532 | 0.0026532
9060 | Grace Cres | Urban | 1381 | 1.7053 | 3.5639 | 211.13 |  |  | 16 | 0.80884 | 0.80884 | 0.0073685 | 0.0073685 | 16 | 0.00017874 | 0.00017874
9062 | Gloucester Av | Urban | 687 | 3.0975 | 1.0158 | 12 |  |  | 4 | 0.042549 | 0.042549 | 0.00039769 | 0.00039769
A046 | Norwood Rd & Cap Bank 2 | Urban | 379 | 6.4094 | 1.2832 | 188.03 |  |  | 16 | 0.042692 | 0.042692 | 0.00056303 | 0.00056303 | 16 | 0.00080433 | 0.00080433
A048 | Hamilton St | Urban | 306 | 8.9822 | 1.5898 | 240.16 |  |  | 36 | 0.079032 | 0.079032 | 0.00046919 | 0.00046919 | 36 | 0.00036195 | 0.00036195
A049 | Garfield Rd | Rural Short | [6 empty] | 592 | 70.5507 | 70.5507 | 0.47765 | 0.47765 | 592 | 0.011457 | 0.011457
A051 | Nelson Rd + Aux No 3 | Rural Short | 1043 | 38.9426 | 2.4307 | 250.95 |  |  | 486 | 21.3247 | 21.3247 | 0.17705 | 0.17705 | 486 | 0.0093201 | 0.0093201
A052 | Richmond Rd | Rural Short | 758 | 26.466 | 1.6935 | 149.21 |  |  | 429 | 23.4249 | 22.9929 | 0.058076 | 0.058076 | 429 | 0.0041535 | 0.0041535
A053 | McCulloch St & Riverstone Meat Co No 4 | Rural Short |  | 9.431 | 2.8023 | 150.12 |  |  | 1 | 0.0018466 | 0.0018466 | 2.1225e-05 | 2.1225e-05
A054 | Railway Tce | Urban | [6 empty] | 3 | 0.092856 | 0.092856 | 0.00021114 | 0.00021114 | 3 | 0.0002346 | 0.0002346
A055 | Dingle St & Cap Bank 3 | Rural Short | 728 | 18.2449 | 3.2645 | 196.81 |  |  | 128 | 1.9173 | 1.9173 | 0.014263 | 0.014263 | 128 | 0.0013584 | 0.0013584
A095 | RAAF/RAN Central Reserve | Rural Short | 186 | 20.4949 | 0.05576 | 134.45 |  |  | 36 | 0.087819 | 0.087819 | 0.0013607 | 0.0013607
A096 | Littlefields Rd + Aux No 1 | Rural Short | 1019 | 36.0725 | 3.2501 | 278.13 |  |  | 891 | 9.4712 | 9.4712 | 0.10385 | 0.10385 | 891 | 0.013663 | 0.013663
A098 | Luddenham + Aux No 2 | Rural Short | 487 | 30.3616 | 1.0677 | 136.91 |  |  | 896 | 1.7941 | 1.7941 | 0.0066312 | 0.0066312 | 896 | 0.011153 | 0.011153
A314 | Orange Grove Rd | Urban | 430 | 3.0313 | 0.4404 | 75.17 |  |  | 10 | 0.070183 | 0.023739 | 0.00014523 | 0.00014523 | 10 | 0.00032173 | 0.00032173
A315 | El Toro Industrial | Urban | 835 | 0.47061 | 2.8175 | 107.74 |  |  | 4 | 0.001021 | 0.001021 | 4.4685e-06 | 4.4685e-06
A317 | A Bathurst St + B Lachlan St | Urban | 845 | 1.5232 | 4.1513 | 106.46 |  |  | 4 | 0.018236 | 0.018236 | 0.00034407 | 0.00034407 | 4 | 0.00051723 | 0.00051723
A319 | Liverpool Shoppingtown & Cap No .2 | Urban | 403 |  | 1.6805 | 274.56 | [7 empty] | 1 | 5.809e-05 | 5.809e-05
A322 | Gallop St | Urban | 1405 | 3.117 | 1.5562 | 199.89 |  |  | 2 | 0.015785 | 0.015785 | 0.00018321 | 0.00018321 | 2 | 0.00013517 | 0.00013517
A324 | Grimson Cres | Urban | 1360 | 6.4784 | 1.1056 | 288.59 |  |  | 27 | 0.11124 | 0.11124 | 0.0013372 | 0.0013372 | 27 | 0.004464 | 0.004464
A325 | Copeland St | Urban | 938 | 3.3253 | 1.2747 | 122.71 |  |  | 9 | 0.13796 | 0.13796 | 0.00058649 | 0.00058649 | 9 | 0.0025035 | 0.0025035
A337 | Cherrybrook Rd | Urban | 516 |  | 4.906 | 134.64 |  |  | 9 | 0.03288 | 0.03288 | 0.00015081 | 0.00015081 | 9 | 0.00011059 | 0.00011059
A339 | Fairview Rd | Urban | 782 | 0.39556 | 2.1763 | 109.8 |  |  | 1 | 0.1076 | 0.1076 | 0.00084119 | 0.00084119
A341 | Hume Hwy | Urban | 154 | 1.4302 | 0.47143 | 141 |  |  | 9 | 0.10502 | 0.10502 | 0.00069038 | 0.00069038 | 9 | 1.0054e-05 | 1.0054e-05
A343 | Roebuck St | Urban | 421 | 2.4651 | 0.81751 | 108.86 |  |  | 4 | 0.016578 | 0.016578 | 0.00016757 | 0.00016757
A344 | Vale St | Urban | 603 | 3.4447 | 0.14832 | 88.9 | [7 empty] | 2 | 0.00025917 | 0.00025917
A346 | Liverpool St | Urban | 524 | 4.612 | 3.1241 | 235.98 |  |  | 27 | 0.10628 | 0.10628 | 0.0055398 | 0.0055398 | 27 | 0.00016087 | 0.00016087
A347 | Boundary Ln | Urban | 1353 | 6.0793 | 0.73315 | 193.66 |  |  | 9 | 0.048655 | 0.048655 | 0.00028151 | 0.00028151 | 9 | 0.00070379 | 0.00070379
A348 | Huntingdale Av + Aux No 2 | Urban | 909 | 6.733 | 1.3934 | 193.39 |  |  | 75 | 2.0368 | 2.0368 | 0.031536 | 0.031536 | 75 | 0.0014523 | 0.0014523
A350 | Lasa St+Aux No 3 | Urban | 650 | 2.8912 | 0.78231 | 175.02 |  |  | 2 | 0.01467 | 0.01467 | 3.1279e-05 | 3.1279e-05 | 2 | 4.5802e-05 | 4.5802e-05
A352 | Cabramatta Rd | Urban | 664 | 0.30146 | 2.1174 | 110.61 | [7 empty] | 1 | 0.00010948 | 0.00010948
A354 | Charlton Av | Urban | 702 | 1.5388 | 5.6778 | 167.68 |  |  | 1 | 0.0074255 | 0.0074255 | 2.7928e-05 | 2.7928e-05
APA2 | Centenary West | Urban | 1460 | 1.5822 | 7.6656 | 173.75 |  |  | 64 | 0.52966 | 0.52966 | 0.03766 | 0.03766 | 64 | 0.0073819 | 0.0073819
APB2 | Centenary East | Urban | 1760 | 7.1499 | 6.5626 | 180.64 |  |  | 324 | 23.9205 | 23.9205 | 0.35199 | 0.35199 | 324 | 0.019626 | 0.019626
APC2 | Regal Heights | Rural Short | 1145 | 42.3969 | 7.9533 | 128.79 |  |  | 5202 | 248.5236 | 248.5236 | 2.9487 | 2.9487 | 5202 | 0.34964 | 0.34964
APD2 | Albion Park Rail | Rural Short | 1457 | 29.3678 | 7.1313 | 293.18 |  |  | 64 | 2.2929 | 2.2929 | 0.062005 | 0.062005 | 64 | 0.0020198 | 0.0020198
APE2 | Green Meadows | Urban | 2093 | 6.3868 | 5.7041 | 256.88 |  |  | 3150 | 73.1055 | 73.1055 | 1.2445 | 1.2445 | 3150 | 0.31922 | 0.31922
APF2 | Oak Flats | Urban | 874 | 14.263 | 1.5478 | 224.98 |  |  | 32 | 0.49127 | 0.49127 | 0.018276 | 0.018276 | 32 | 0.0011618 | 0.0011618
AZ1205 | Heathcote Rd | Urban | 1045 | 6.725 | 2.8003 | 193.3 |  |  | 180 | 21.6976 | 21.6976 | 0.14877 | 0.14877 | 180 | 0.0030162 | 0.0030162
AZ1227 | Brallos Ave | Urban | 796 | 9.9388 | 4.1097 | 189.06 |  |  | 96 | 1.8165 | 1.8165 | 0.016274 | 0.016274 | 96 | 0.0030922 | 0.0030922
AZ1257 | Arrowfield Dr | Urban | 1223 |  | 7.3295 | 222.25 |  |  | 4 | 0.02467 | 0.02467 | 0.00032396 | 0.00032396
AZ1264 | Moorebank Ave | Urban | 126 | 1.5794 | 1.4063 | 111.4 |  |  | 4 | 0.004826 | 0.004826 | 8.0433e-05 | 8.0433e-05 | 4 | 5.809e-05 | 5.809e-05
AZ1272 | Wattlegrove Dr & Aux No.1 | Urban | 1338 | 5.4213 | 4.6605 | 155.34 |  |  | 882 | 23.2784 | 23.2784 | 0.21874 | 0.21874 | 882 | 0.024195 | 0.024195
B201 | Pendle Way | Urban | 1558 | 6.9674 | 2.0075 | 200.74 |  |  | 192 | 5.4611 | 5.4611 | 0.047804 | 0.047804 | 192 | 0.0052907 | 0.0052907
B202 | Mandoon Rd | Urban | 56 | 1.8618 | 1.2291 | 208.79 |  |  | 96 | 0.16371 | 0.16371 | 0.0017159 | 0.0017159 | 96 | 0.0015372 | 0.0015372
B204 | Myrtle St | Urban | 267 | 2.9515 | 2.8007 | 254.78 |  |  | 48 | 0.5859 | 0.5859 | 0.0074132 | 0.0074132 | 48 | 0.0020198 | 0.0020198
B205 | Metella Rd + Aux No 3 | Urban | 611 | 2.9135 | 1.4824 | 121.76 |  |  | 7 | 0.44876 | 0.44876 | 0.0046919 | 0.0046919 | 7 | 0.00089481 | 0.00089481
B207 | Church Ln + Aux No 2 | Urban | 52 | 3.5265 | 0.97091 | 87.11 |  |  | 2 | 0.010912 | 0.010912 | 0.00011395 | 0.00011395 | 2 | 3.1279e-05 | 3.1279e-05
B210 | Ottawa St | Urban | 877 | 5.3016 | 0.93516 | 170.6 |  |  | 45 | 0.18548 | 0.18548 | 0.0025135 | 0.0025135 | 45 | 0.0043635 | 0.0043635
B211 | Magowar Rd | Urban | 957 | 6.9656 | 0.98845 | 215.69 |  |  | 2 | 0.001707 | 0.001707 | 1.3405e-05 | 1.3405e-05 | 2 | 8.6018e-05 | 8.6018e-05
B212 | Great Western Hway | Urban | 185 | 2.1192 | 0.75014 | 78.05 | [7 empty] | 1 | 4.4685e-06 | 4.4685e-06
B214 | Amax Av | Urban | 1335 | 5.0019 | 1.5723 | 218.6 |  |  | 64 | 4.1582 | 4.1582 | 0.040842 | 0.040842 | 64 | 0.0026453 | 0.0026453
B215 | Buffalo Pl | Urban | 666 | 3.4498 | 1.0872 | 214.93 |  |  | 2 | 0.0065106 | 0.0065106 | 0.00010501 | 0.00010501 | 2 | 0.00011395 | 0.00011395
B217 | Rowood Rd | Urban | 1701 | 8.3317 | 1.6826 | 263.69 |  |  | 120 | 2.6716 | 3.9616 | 0.037991 | 0.037991 | 120 | 0.0043791 | 0.0043791
B709 | Chaplin Cres | Urban | 367 | 0.47328 | 2.5927 | 209.95 |  |  | 2 | 0.00029939 | 0.00029939 | 2.2342e-06 | 2.2342e-06 | 2 | 9.3838e-05 | 9.3838e-05
B710 | Picton St | Urban | 1114 | 0.32414 | 5.3994 | 188.45 |  |  | 28 | 0.013481 | 0.013481 | 0.00010948 | 0.00010948 | 28 | 0.0018053 | 0.0018053
B712 | Rowntree St | Urban | [6 empty] | 4 | 0.0011797 | 0.0011797 | 6.7027e-06 | 6.7027e-06
B713 | Pye Rd + Aux No 4 | Urban | 1583 |  | 7.0992 | 233.68 | [7 empty] | 3 | 8.0433e-05 | 8.0433e-05
B715 | Mallee Cres + Aux No 3 | Urban | 1201 | 2.6842 | 4.5585 | 162.46 |  |  | 9 | 0.52147 | 0.52147 | 0.0040283 | 0.0040283 | 9 | 0.00035189 | 0.00035189
B716 | Lovegrove Dr | Urban | 1058 | 2.0642 | 4.4776 | 159.11 | [7 empty] | 2 | 0.00010836 | 0.00010836
B718 | Quakers Rd | Urban | 891 |  | 8.3198 | 214.57 |  |  | 28 | 0.012793 | 0.012793 | 0.00020332 | 0.00020332 | 28 | 0.00080433 | 0.00080433
B719 | Nirimba & Stonecutters Ridge | Urban | 206 | 0.23462 | 7.9974 | 237.85 | [7 empty] | 3 | 3.5748e-05 | 3.5748e-05
B720 | Sherridon Cr & Cap Bank 3 | Urban | 932 | 0.04069 | 6.0392 | 289.5 |  |  | 2 | 0.011772 | 0.011772 | 2.4577e-05 | 2.4577e-05 | 2 | 9.2721e-05 | 9.2721e-05
B743 | Newbridge Rd + Wattle Grove | Urban | 1032 | 6.9597 | 2.6174 | 357.68 |  |  | 448 | 31.4324 | 31.4324 | 0.20795 | 0.20795 | 448 | 0.0018589 | 0.0018589
B745 | Market St | Urban | 343 | 2.2762 | 1.8466 | 240.03 |  |  | 4 | 0.1272 | 0.1272 | 0.00028151 | 0.00028151 | 4 | 3.6865e-05 | 3.6865e-05
B746 | Blamey Rd & Cap Bank 3 | Urban | 52 | 1.4102 | 1.4519 | 279.07 |  |  | 1 | 0.0080745 | 0.0080745 | 5.809e-05 | 5.809e-05
B747 | Edgecombe Av | Urban | 804 | 9.7718 | 1.9531 | 220.63 |  |  | 16 | 0.079986 | 0.079986 | 0.00063899 | 0.00063899 | 16 | 0.00051834 | 0.00051834
B748 | Lucas Rd | Urban | 1022 | 5.3586 | 1.5104 | 211.18 |  |  | 63 | 2.6893 | 2.6893 | 0.023694 | 0.023694 | 63 | 0.0058012 | 0.0058012
B762 | Barden St + Aux No 2 | Urban | 374 | 0.8123 | 0.88991 | 107.88 |  |  | 3 | 0.0024063 | 0.0024063 | 3.3514e-06 | 3.3514e-06 | 3 | 2.4577e-05 | 2.4577e-05
B764 | Helen St & Aux No 1 | Urban | 2090 | 0.58064 | 5.3811 | 195.48 | [7 empty] | 3 | 0.00064793 | 0.00064793
B773 | Marion St | Urban | 1014 | 1.2382 | 2.9015 | 145.66 |  |  | 4 | 0.0067899 | 0.0067899 | 6.7027e-05 | 6.7027e-05
B775 | High St | Urban | 222 |  | 2.2253 | 168.56 | [7 empty] | 1 | 1.1171e-06 | 1.1171e-06
B776 | Crimea St + Aux No 1 | Urban | 2398 | 4.8463 | 2.5129 | 198.7 |  |  | 80 | 8.3682 | 8.3682 | 0.05532 | 0.05532 | 80 | 0.0053086 | 0.0053086
B778 | Bobart St + Aux No 2 | Urban | 1498 |  | 3.5868 | 264.53 |  |  | 3 | 0.016908 | 0.016908 | 0.00017427 | 0.00017427 | 3 | 9.6072e-05 | 9.6072e-05
B799 | West Castle Hill & Capacitor Bank No.1 | Urban | [11 empty] | 10 | 0.00027705 | 0.00027705
B799 |  | Urban |  |  |  | 183.34 | [7 empty] | 10 | 0.00027705 | 0.00027705
BDA2 | McMahons Rd | Urban | 1819 | 12.9767 | 3.2767 | 206.71 |  |  | 468 | 14.431 | 14.431 | 0.4552 | 0.4552 | 468 | 0.033862 | 0.033862
BDB2 | Scenic Dr | Urban | 145 | 3.8384 | 0.44255 | 65.2 |  |  | 30 | 0.43884 | 0.038189 | 0.0044573 | 0.0044573 | 30 | 0.00079762 | 0.00079762
BDC2 | North Bomaderry | Rural Short | 928 | 39.4655 | 0.57145 | 170.63 |  |  | 980 | 8.0417 | 8.0417 | 0.2439 | 0.2439 | 980 | 0.0081014 | 0.0081014
BDD2 | Bolong Rd | Urban | 716 | 3.0204 | 2.9059 | 171.46 |  |  | 8 | 0.050288 | 0.050288 | 0.0058582 | 0.0058582 | 8 | 0.00026364 | 0.00026364
BDE2 | Bomaderry | Urban | 1151 | 8.9164 | 0.97972 | 188.56 |  |  | 726 | 13.7797 | 13.7797 | 0.34594 | 0.34594 | 726 | 0.034739 | 0.034739
BDF2 | Cambewarra | Rural Short | 1231 | 44.7123 | 2.7564 | 196.67 |  |  | 4704 | 206.5095 | 206.5095 | 2.0956 | 2.0956 | 4704 | 0.11035 | 0.11035
BDG2 | Meroo Meadow & Aux Transf No1 | Rural Short | 1663 | 29.9355 | 5.617 | 181.27 |  |  | 1440 | 27.3061 | 27.3061 | 0.6507 | 0.6507 | 1440 | 0.1266 | 0.1266
BGA2 | Shoalhaven Heads | Rural Short | 718 | 33.792 | 0.23353 | 79.15 |  |  | 160 | 8.1315 | 1.3529 | 0.026342 | 0.026342 | 160 | 0.0092051 | 0.0092051
BGB2 | Bomaderry | Rural Short | 25 | 4.7752 | 0.091653 | 72.27 | [7 empty] | 2 | 8.937e-06 | 8.937e-06
BK1236 | Wentworth St | Urban | 939 | 8.5566 | 0.46503 | 109.11 |  |  | 450 | 9.8345 | 9.8345 | 0.096787 | 0.096787 | 450 | 0.030162 | 0.030162
BK1251 | Future | Rural Short | 925 | 78.7692 | 0.077088 | 123.51 |  |  | 2640 | 160.1416 | 170.7154 | 1.0055 | 1.0055 | 2640 | 0.044774 | 0.044774
BK1288 | Cleopatra St | Rural Short | 1364 | 12.4941 | 0.27406 | 112.21 |  |  | 392 | 31.2391 | 31.2391 | 0.15618 | 0.15618 | 392 | 0.0091961 | 0.0091961
BK1299 | Sunbeam Ave & Aux Bus No2 | Rural Short | 719 | 14.012 | 0.23075 | 73.98 |  |  | 2432 | 98.9227 | 95.4878 | 0.5488 | 0.5488 | 2432 | 0.097127 | 0.097127
BLA2 | Haigh Street | Rural Short | 1481 | 19.2515 | 1.8736 | 164.03 |  |  | 612 | 10.967 | 10.967 | 0.17605 | 0.17605 | 612 | 0.045726 | 0.045726
BLB2 | Hobart Street North | Urban | 1468 | 5.8439 | 2.8901 | 149.41 |  |  | 32 | 2.0445 | 2.0445 | 0.024273 | 0.024273 | 32 | 0.0028866 | 0.0028866
BLC2 | Hobart Street South | Urban | 622 | 3.3257 | 1.8764 | 63.75 |  |  | 5 | 0.0012288 | 0.0012288 | 5.5856e-06 | 5.5856e-06 | 5 | 0.0002938 | 0.0002938
BLD2 | Hobart Street West | Urban | 1393 | 8.9288 | 0.19476 | 117.22 |  |  | 325 | 4.8274 | 4.8274 | 0.11182 | 0.11182 | 325 | 0.031531 | 0.031531
BLE2 | Slacky Flat | Urban | 662 | 3.8535 | 1.5582 | 146.47 |  |  | 45 | 1.301 | 1.301 | 0.022354 | 0.022354 | 45 | 0.0043132 | 0.0043132
BWA2 | Burradoo | Rural Short | 1262 | 13.8405 | 1.7927 | 128.27 |  |  | 448 | 2.712 | 2.712 | 0.016641 | 0.016641 | 448 | 0.028956 | 0.028956
BWB2 | Bowral St | Urban | 1343 | 9.0845 | 1.14 | 175.75 |  |  | 48 | 5.2787 | 5.2787 | 0.054171 | 0.054171 | 48 | 0.0008937 | 0.0008937
BWC2 | Mt Gibraltar | Urban | 435 | 7.0157 | 0.04921 | 186.09 |  |  | 144 | 2.5276 | 2.5276 | 0.013834 | 0.013834 | 144 | 0.002413 | 0.002413
BWD2 | Merrigang St | Urban | 900 | 6.066 | 0.70799 | 200.04 |  |  | 36 | 0.19443 | 0.19443 | 0.0017159 | 0.0017159 | 36 | 0.00066357 | 0.00066357
BWE2 | Kangaloon | Rural Short | 1617 | 60.3341 | 16.763 | 216.06 |  |  | 648 | 2.3046 | 2.3046 | 0.016489 | 0.016489 | 648 | 0.014749 | 0.014749
BWF2 | Old South Rd | Rural Short | 127 | 30.2448 | 2.6156 | 31.97 |  |  | 96 | 0.75662 | 0.90886 | 0.0075339 | 0.0075339 | 96 | 0.0007507 | 0.0007507
BWG2 | Shepherd St | Urban | 542 | 3.7883 | 1.3907 | 185.34 |  |  | 8 | 0.010027 | 0.010027 | 0.00030833 | 0.00030833 | 8 | 0.00093391 | 0.00093391
BWH2 | Centennial Rd | Rural Short | 1090 | 142.339 | 1.3585 | 141.29 |  |  | 38663 | 648.8047 | 648.8047 | 6.149 | 6.149 | 38663 | 0.97274 | 0.97274
BYB2 | Berry Mountain | Rural Short | 692 | 38.0314 | 1.4025 |  |  |  | 675 | 13.3216 | 13.3216 | 0.08375 | 0.08375 | 675 | 0.011562 | 0.011562
BYC2 | Woodhill | Rural Short | 394 | 51.756 | 0.06659 | 131.67 |  |  | 5292 | 67.4764 | 67.4764 | 0.43325 | 0.43325 | 5292 | 0.12907 | 0.12907
BYD2 | Shoalhaven Heads Central | Rural Short | 986 | 18.4163 | 1.3447 | 153.29 |  |  | 660 | 56.054 | 14.4047 | 0.14471 | 0.14471 | 660 | 0.0066357 | 0.0066357
BYE2 | Jaspers Brush | Rural Short | 225 | 27.5469 | 0.47967 | 113.38 |  |  | 36 | 0.84816 | 0.84816 | 0.008365 | 0.008365 | 36 | 0.00051388 | 0.00051388
BYF2 | Berry | Rural Short | 478 | 3.407 | 1.0023 |  |  |  | 4 | 0.0052304 | 0.0052304 | 0.0009004 | 0.0009004 | 4 | 0.00010278 | 0.00010278
BYG2 | Shoalhaven Heads Nth | Rural Short | 622 | 27.6996 | 1.7974 | 73.84 |  |  | 144 | 6.7955 | 1.4168 | 0.056243 | 0.056243 | 144 | 0.0012065 | 0.0012065
C808 | Bottlebrush Dr & Cap Bank 3 | Urban | [11 empty] | 1 | 4.8036e-05 | 4.8036e-05
C811 | Scenic Cct + Aux No 2 | Urban | 1049 |  | 8.2283 | 223.01 |  |  | 1 | 0.0043579 | 0.0043579 | 2.0108e-05 | 2.0108e-05
C812 | Andrews Rd | Urban | 1159 | 2.8886 | 11.6107 | 225.76 |  |  | 25 | 0.18277 | 0.18277 | 0.0015975 | 0.0015975
C814 | Llandilo | Rural Short | 599 | 32.8238 | 1.028 | 237.41 |  |  | 252 | 0.42654 | 0.42654 | 0.0083985 | 0.0083985 | 252 | 0.0041021 | 0.0041021
C820 | Brisbane Rd | Urban | 537 | 0.1874 | 1.424 | 187.85 | [7 empty] | 1 | 4.6919e-05 | 4.6919e-05
C824 | Darcey Rd | Urban | 771 | 0.27908 | 5.3987 | 200.9 |  |  | 36 | 0.30504 | 0.30504 | 0.00086465 | 0.00086465 | 36 | 0.00041557 | 0.00041557
C826 | Cecil Av | Urban | [11 empty] | 2 | 6.0324e-05 | 6.0324e-05
C826 |  | Urban |  |  |  | 48.4 | [7 empty] | 2 | 6.0324e-05 | 6.0324e-05
C830 | Castle Pl | Urban | 3 | 0.60942 | 0.91148 | 240.21 | [7 empty] | 3 | 0.00037759 | 0.00037759
C832 | Telfer Rd | Urban | 584 | 4.2077 | 3.3858 | 187.52 |  |  | 50 | 2.7947 | 2.7947 | 0.03272 | 0.03272 | 50 | 0.00013964 | 0.00013964
C833 | Rogans Hill + Aux No 2 | Urban | 1120 | 2.709 | 3.0085 | 173.37 | [7 empty] | 1 | 5.5856e-06 | 5.5856e-06
C835 | Mons Rd & Cap Bank 2 | Urban | 440 | 0.54412 | 2.2178 | 277.02 | [7 empty] | 2 | 0.00034631 | 0.00034631
C836 | Hainsworth St | Urban | 1232 | 0.62959 | 3.7031 | 123.38 | [7 empty] | 3 | 0.00036083 | 0.00036083
C847 | Sheens Ln | Rural Short | 5 | 3.5757 | 0.3286 | 21.31 | [7 empty] | 1 | 3.3514e-06 | 3.3514e-06
C851 | Leonay Pde | Urban | 889 | 5.3705 | 1.3192 | 213.26 |  |  | 4 | 0.039834 | 0.039834 | 0.002022 | 0.002022 | 4 | 2.2342e-05 | 2.2342e-05
C852 | Pyramid + Aux No 3 | Urban | 371 | 3.2877 | 0.36698 | 111.7 | [7 empty] | 1 | 8.937e-06 | 8.937e-06
C854 | Bromley Rd | Urban | 940 | 4.7691 | 1.2798 | 222.02 |  |  | 1 | 0.0048595 | 0.0048595 | 6.4793e-05 | 6.4793e-05 | 1 | 5.809e-05 | 5.809e-05
C855 | Wedmore Rd | Urban | 462 | 4.912 | 0.25299 | 115.56 | [7 empty] | 2 | 6.0324e-05 | 6.0324e-05
C869 | Ithaca St | Urban | 661 | 3.7462 | 2.4096 | 181.49 | [7 empty] | 1 | 2.2342e-05 | 2.2342e-05
C889 | Henry Lawson Av | Urban | 761 | 0.18588 | 4.001 | 189.9 |  |  | 648 | 2.7833 | 2.7833 | 0.010537 | 0.010537 | 648 | 0.026151 | 0.026151
C890 | Greenbank Dr | Urban | 917 |  | 5.5778 | 196.93 |  |  | 135 | 0.31831 | 0.31831 | 0.0022119 | 0.0022119 | 135 | 0.003348 | 0.003348
C891 | Rugby St | Urban | 819 | 6.612 | 0.84304 | 324.88 |  |  | 64 | 3.8223 | 3.8223 | 0.029599 | 0.029599 | 64 | 0.0034854 | 0.0034854
C893 | Glencoe Av | Urban | 1080 | 4.2889 | 2.6329 | 202.75 |  |  | 150 | 2.7879 | 2.7879 | 0.042395 | 0.042395 | 150 | 0.0053901 | 0.0053901
C896 | Trinity Drive + Aux No 2 | Urban | 697 | 1.7803 | 4.9816 | 149.34 |  |  | 539 | 0.65804 | 0.65804 | 0.0022365 | 0.0022365 | 539 | 0.016531 | 0.016531
C897 | Harrow Rd | Urban | 1142 | 7.1994 | 0.92927 | 229.88 |  |  | 5 | 0.00066469 | 0.00066469 | 5.5856e-06 | 5.5856e-06 | 5 | 0.00030162 | 0.00030162
C899 | Leslie Ct | Urban | 561 |  | 4.8242 | 158.7 |  |  | 175 | 1.4406 | 1.4406 | 0.0048483 | 0.0048483 | 175 | 0.0029604 | 0.0029604
C900 | Burton St | Urban | 1822 | 3.5955 | 6.9854 | 263.8 |  |  | 1400 | 18.2578 | 18.2578 | 0.11214 | 0.11214 | 1400 | 0.087024 | 0.087024
CD1204 | Sheathers Ln | Urban | 564 | 23.4566 | 8.3827 |  |  |  | 63 | 1.3769 | 1.3769 | 0.026838 | 0.026838 | 63 | 0.00059319 | 0.00059319
CD1230 | Mayfarm Rd | Rural Short | 18 | 4.396 | 0.15889 |  |  |  | 3 | 0.47627 | 0.47627 | 0.0026811 | 0.0026811 | 3 | 8.0433e-05 | 8.0433e-05
CD1234 | West Brook Rd | Urban | 455 | 52.0852 | 1.0618 |  |  |  | 25 | 0.053141 | 0.053141 | 0.00069261 | 0.00069261
CD1241 | Barsden St | Urban | 771 | 2.3614 | 4.536 | [8 empty] | 3 | 0.00027258 | 0.00027258
CD1260 | Ironbark Av | Urban | 683 | 4.7513 | 0.93624 | [8 empty] | 1 | 6.591e-05 | 6.591e-05
CD1267 | McCrae Dr 1 | Urban | 1080 | 11.4751 | 7.9056 |  |  |  | 3 | 0.00056303 | 0.00056303 | 1.0054e-05 | 1.0054e-05 | 3 | 0.00017762 | 0.00017762
CD1271 | The Old Oaks Rd | Urban | 419 | 21.0744 | 4.0178 |  |  |  | 63 | 0.26249 | 0.26249 | 0.0099703 | 0.0099703 | 63 | 0.001307 | 0.001307
CD1297 | Old Hume Hwy | Urban | 769 | 3.4678 | 3.2616 |  |  |  | 4 | 0.032345 | 0.032345 | 0.00014299 | 0.00014299
CJ1204 | Warwick Pd | Urban | 659 | 3.2094 | 3.5089 |  |  |  | 225 | 0.56891 | 0.56891 | 0.0036697 | 0.0036697 | 225 | 0.023543 | 0.023543
CJ1230 |  | Urban | [11 empty] | 1 | 1.4523e-05 | 1.4523e-05
CJ1241 | Kentwell Av | Urban | 1163 | 4.1693 | 6.63 |  |  |  | 27 | 0.1324 | 0.1324 | 0.012809 | 0.012809 | 27 | 0.00068368 | 0.00068368
CJ1245 | Bounty Av | Urban | 1200 | 0.035066 | 12.5593 |  |  |  | 360 | 1.2251 | 1.2251 | 0.0066357 | 0.0066357 | 360 | 0.0073998 | 0.0073998
CJ1249 | Castle St | Urban | 1027 | 0.94988 | 8.1391 |  |  |  | 99 | 1.317 | 1.317 | 0.0031335 | 0.0031335 | 99 | 0.0033581 | 0.0033581
CJ1267 | Sherwin Av | Urban | 2134 | 7.0575 | 4.8113 |  |  |  | 20 | 0.13332 | 0.13332 | 0.00046919 | 0.00046919 | 20 | 0.0019572 | 0.0019572
CJ1286 | Showground Rd | Urban | 308 |  | 0.77031 |  |  |  | 1 | 0.0018432 | 0.0018432 | 2.4577e-05 | 2.4577e-05
CLA2 | Greenwell Point | Rural Short | 1327 | 48.6435 | 1.7644 | 158.52 |  |  | 792 | 5.785 | 3.3807 | 0.13282 | 0.13282 | 792 | 0.037803 | 0.037803
CLB2 | Culburra | Rural Short | 2326 | 18.5706 | 0.54793 |  |  |  | 64 | 0.12077 | 0.12077 | 0.037106 | 0.037106 | 64 | 0.010796 | 0.010796
CLC2 | Culburra | Rural Short | [6 empty] | 4225 | 203.363 | 203.363 | 2.0441 | 2.0441 | 4225 | 0.52768 | 0.52768
CLD2 | Callala | Rural Short | 3023 | 32.9208 | 2.7822 | 258.44 |  |  | 1458 | 34.0114 | 34.0114 | 0.86161 | 0.86161 | 1458 | 0.078181 | 0.078181
CRA2 | Keira St | Urban | 2269 | 8.1686 | 0.90495 | 216.19 |  |  | 784 | 18.2963 | 18.2963 | 0.45299 | 0.45299 | 784 | 0.10028 | 0.10028
CRB2 | Meadow St South | Urban | 2501 | 9.7454 | 0.60072 | 226.06 |  |  | 2000 | 124.2068 | 124.2068 | 1.5575 | 1.5575 | 2000 | 0.21248 | 0.21248
CRC2 | Meares St & Cap Bank 1 | Urban | 859 | 3.5966 | 0.74128 | 237.86 |  |  | 1 | 0.0031458 | 0.0031458 | 1.2288e-05 | 1.2288e-05 | 1 | 4.5802e-05 | 4.5802e-05
CRD2 | Meadow St North | Urban | 1574 | 5.0497 | 1.2351 | 279.56 |  |  | 44 | 2.1962 | 2.1962 | 0.015827 | 0.015827 | 44 | 0.0041155 | 0.0041155
CRE2 | Wallace Rd | Urban | 1210 | 6.0256 | 0.73623 | 150.24 |  |  | 28 | 0.1502 | 0.1502 | 0.0010635 | 0.0010635 | 28 | 0.0017785 | 0.0017785
CRF2 | Caldwell Av | Urban | 1663 | 6.3906 | 1.9932 | 143.32 |  |  | 45 | 1.5805 | 1.5805 | 0.028034 | 0.028034 | 45 | 0.0045042 | 0.0045042
CS1206 |  | Urban | [6 empty] | 1 | 0.0042763 | 0.0042763 | 3.6865e-05 | 3.6865e-05
CS1276 | San Diego St | Urban |  | 11.5421 | 7.1852 |  |  |  | 3 | 0.034268 | 0.034268 | 0.0068535 | 0.0068535 | 3 | 6.591e-05 | 6.591e-05
CS1280 | Caddens Rd | Urban |  | 8.115 | 11.2032 |  |  |  | 1 | 0.0098083 | 0.0098083 | 2.2342e-05 | 2.2342e-05
CT1202 | Blaxland Rd | Urban | 607 | 1.0769 | 5.0568 | 297.94 |  |  | 25 | 0.03095 | 0.03095 | 0.00027369 | 0.00027369 | 25 | 0.0026252 | 0.0026252
CT1203 | Milgate Ln | Urban | 400 |  | 3.7825 | 235.4 |  |  | 9 | 0.032421 | 0.032421 | 0.00022454 | 0.00022454 | 9 | 0.0012869 | 0.0012869
CT1206 | Woodhouse Dr | Urban | 1662 |  | 14.9249 | 308.02 |  |  | 36 | 1.0599 | 1.0599 | 0.012494 | 0.012494 | 36 | 0.00084454 | 0.00084454
CT1225 | Badgally Rd | Urban | 1889 | 24.1447 | 19.0811 | 350.82 |  |  | 1210 | 42.2778 | 42.2778 | 0.30573 | 0.30573 | 1210 | 0.011625 | 0.011625
CT1228 | Hyde Pde | Urban | 430 | 0.2372 | 4.6014 | 203.26 | [7 empty] | 2 | 1.3405e-05 | 1.3405e-05
CT1229 | Macarthur Square No.1 | Urban | 1 |  | 1.7661 | 143.22 | [7 empty] | 1 | 1.1171e-06 | 1.1171e-06
CT1233 | Spare | Urban | 729 |  | 7.6728 | 145.88 |  |  | 25 | 0.025102 | 0.025102 | 0.00020108 | 0.00020108
CT1243 | Farrow Rd | Urban | 269 | 0.57911 | 3.7003 | 133.45 | [7 empty] | 1 | 4.4685e-06 | 4.4685e-06
CT1262 | Menangle Rd | Rural Short | 609 | 27.4926 | 5.3662 | 298.01 |  |  | 168 | 11.1225 | 3.9398 | 0.034291 | 0.034291 | 168 | 0.0007507 | 0.0007507
CT1265 | Watsford Rd | Urban | 480 | 0.90323 | 4.6654 | 182.94 | [7 empty] | 1 | 3.4631e-05 | 3.4631e-05
CT1266 | Fern Ave | Urban | 201 | 2.6014 | 3.9723 | 153.07 | [7 empty] | 1 | 8.4901e-05 | 8.4901e-05
CT1270 | Spare | Urban | 2 |  | 2.1546 | 197.54 | [7 empty] | 1 | 1.1171e-06 | 1.1171e-06
CT1273 | Kialba Rd | Urban | 270 | 0.96818 | 1.537 | 142.52 |  |  | 4 | 0.032678 | 0.032678 | 0.0001698 | 0.0001698
CT1296 | Camden Road | Urban | 900 | 7.9522 | 8.4212 | 325.87 |  |  | 25 | 0.084667 | 0.084667 | 0.0010278 | 0.0010278
CV1210 | St Johns Rd East | Urban | 1699 | 1.5804 | 1.8496 |  |  |  | 2 | 0.017472 | 0.017472 | 3.7982e-05 | 3.7982e-05 | 2 | 7.7081e-05 | 7.7081e-05
CV1236 | Joseph St | Urban | 1614 | 5.2912 | 1.8359 |  |  |  | 4 | 0.0033603 | 0.0033603 | 4.4685e-06 | 4.4685e-06
CV1239 | Mt Pritchard | Urban | 1237 | 6.3793 | 0.33864 |  |  |  | 1 | 0.0020957 | 0.0020957 | 3.1279e-05 | 3.1279e-05
CV1247 | Derby St | Urban | 1715 | 4.031 | 2.1958 |  |  |  | 1 | 0.0086566 | 0.0086566 | 0.00013741 | 0.00013741
D810 | Leets Vale | Rural Short | 202 | 28.8055 | 0.69208 | 66.62 |  |  | 175 | 4.0262 | 4.0262 | 0.0088364 | 0.0088364 | 175 | 0.00078198 | 0.00078198
D813 | Laughtondale | Rural Short | 306 | 36.2711 | 0.89466 | 226.08 |  |  | 486 | 16.9566 | 16.9566 | 0.076552 | 0.076552 | 486 | 0.0078723 | 0.0078723
D814 | MacDonald | Rural Short | 379 | 77.5777 | 0.8306 | 61.94 |  |  | 2700 | 136.5334 | 136.5334 | 0.37803 | 0.37803 | 2700 | 0.022873 | 0.022873
D819 | Speed St | Urban | 560 |  | 1.5894 | 145.65 |  |  | 8 | 0.27003 | 0.27003 | 0.0034631 | 0.0034631 | 8 | 0.00021449 | 0.00021449
D820 | Mill St & Cap Bank 1 | Urban | 1304 | 2.7033 | 2.924 | 291.04 |  |  | 16 | 1.0768 | 1.0768 | 0.0063452 | 0.0063452 | 16 | 5.3622e-05 | 5.3622e-05
D823 | McGowen Cres | Urban | 1004 | 2.7476 | 4.9138 | 303.34 |  |  | 36 | 0.06515 | 0.06515 | 0.00042897 | 0.00042897 | 36 | 0.00016087 | 0.00016087
D824 | Nagle St | Urban | 430 |  | 1.3737 | 163.72 |  |  | 1 | 0.0010054 | 0.0010054 | 1.3405e-05 | 1.3405e-05
D827 | Pirie St | Urban | 516 |  | 1.7674 | 234.46 |  |  | 1 | 0.00016645 | 0.00016645 | 1.1171e-06 | 1.1171e-06
D828 | Atkinson St & Cap Bank 2 | Urban | 1299 | 7.3159 | 1.2257 | 231.31 |  |  | 12 | 0.034398 | 0.034398 | 0.00053622 | 0.00053622 | 12 | 0.0003396 | 0.0003396
D830 | Grove St | Urban | 1486 | 5.8935 | 4.4699 | 314.89 |  |  | 539 | 13.813 | 13.813 | 0.20292 | 0.20292 | 539 | 0.017845 | 0.017845
D831 | Buckland Rd | Urban | 1880 | 4.4045 | 7.9178 | 206.03 |  |  | 75 | 8.1164 | 8.1164 | 0.09476 | 0.09476 | 75 | 0.00083784 | 0.00083784
D832 | M5 Business Park | Urban | 28 | 0.14924 | 1.1257 | 174.34 |  |  | 4 | 0.0047344 | 0.0047344 | 0.00011841 | 0.00011841
D840 | Lackey St | Urban | 710 |  | 2.1177 | 52.32 |  |  | 16 | 0.068506 | 0.068506 | 0.00046472 | 0.00046472
D841 | Wilga St | Urban | 469 | 0.79789 | 1.3925 | 88.97 |  |  | 1 | 0.0053231 | 0.0053231 | 9.1604e-05 | 9.1604e-05 | 1 | 2.4577e-05 | 2.4577e-05
D842 | McIntosh St | Urban | 233 | 0.92738 | 1.8808 | 64.32 |  |  | 1 | 0.054375 | 0.054375 | 0.0002938 | 0.0002938
D845 | Austral Pde + Aux No 1 | Urban | 1447 | 4.8641 | 0.53501 | 288.67 |  |  | 2 | 0.032164 | 0.032164 | 0.00026364 | 0.00026364 | 2 | 0.00021672 | 0.00021672
D847 | York St + Aux No 2 | Urban | 1012 |  | 3.7625 | 142.55 |  |  | 1 | 0.0015271 | 0.0015271 | 1.4523e-05 | 1.4523e-05
D850 | Delamere St | Urban | 1190 | 4.2509 | 1.4803 | 210.93 |  |  | 1 | 0.0031972 | 0.0031972 | 7.5964e-05 | 7.5964e-05 | 1 | 4.9153e-05 | 4.9153e-05
D852 | Ada St & Cap Bank 2 | Urban | 1365 | 5.7498 | 1.1591 | 285.36 |  |  | 196 | 11.1616 | 11.1616 | 0.090616 | 0.090616 | 196 | 0.0039412 | 0.0039412
DFA2 | Princes Hwy | Rural Short | 59 | 18.6953 | 0.16009 | 261.34 |  |  | 256 | 1.4451 | 1.4451 | 0.012798 | 0.012798 | 256 | 0.0028598 | 0.0028598
DFC2 | Coalcliff | Rural Short | 3 | 6.2881 | 0.04779 | 50.43 |  |  | 4 | 0.0010166 | 0.0010166 | 1.1171e-05 | 1.1171e-05
DP1206 | Cleveland Rd Sth | Urban | 1359 | 7.7561 | 3.2822 | 134.9 |  |  | 32 | 0.3556 | 0.3556 | 0.025041 | 0.025041 | 32 | 0.0043925 | 0.0043925
DP1210 | Marshall St Sth & Aux No3 | Rural Short | 1862 | 32.0671 | 3.2945 | 172.94 |  |  | 704 | 15.451 | 15.451 | 0.34201 | 0.34201 | 704 | 0.03296 | 0.03296
DP1221 | Emerson Rd | Urban | 877 | 9.6326 | 4.1823 | 114.44 |  |  | 9 | 0.6657 | 0.6657 | 0.0084722 | 0.0084722
DP1236 | Avonlea St | Urban | 1556 | 8.2038 | 0.90357 | 156.71 |  |  | 196 | 6.4991 | 6.4991 | 0.29859 | 0.29859 | 196 | 0.025618 | 0.025618
DP1243 | Bong Bong Rd | Urban | 1339 | 3.2009 | 6.3331 | 172.56 |  |  | 18 | 0.18436 | 0.18436 | 0.0094911 | 0.0094911 | 18 | 0.0031168 | 0.0031168
DP1258 | Cleveland Rd Nth | Urban | 1349 | 8.3069 | 1.0068 | 132.87 |  |  | 16 | 0.16769 | 0.16769 | 0.012092 | 0.012092 | 16 | 0.0017427 | 0.0017427
DP1269 | Princes Hwy Nth & Aux No1 | Urban | 1552 | 8.5051 | 5.3297 | 235.13 |  |  | 72 | 4.2952 | 4.2952 | 0.043273 | 0.043273 | 72 | 0.0037401 | 0.0037401
DP1273 | Marshall St East | Urban | 252 | 0.86336 | 1.039 | 138.1 |  |  | 4 | 0.056142 | 0.056142 | 0.0011216 | 0.0011216 | 4 | 0.00029492 | 0.00029492
DP1284 | Cleveland Rd West | Rural Short | 1347 | 23.1998 | 10.1691 | 181.37 |  |  | 324 | 28.9605 | 28.9605 | 0.32587 | 0.32587 | 324 | 0.0066759 | 0.0066759
DP1295 | Marshall St West & Cap Bank No2 | Urban | 801 | 6.078 | 1.2306 | 276.62 |  |  | 4 | 0.024836 | 0.024836 | 0.0017986 | 0.0017986 | 4 | 0.00055409 | 0.00055409
E898 |  | Urban | [11 empty] | 1 | 0.00010054 | 0.00010054
F601 | Telopea St | Urban | 1445 | 4.5508 | 1.506 | 190.09 |  |  | 16 | 1.3431 | 1.3431 | 0.013423 | 0.013423 | 16 | 6.2559e-05 | 6.2559e-05
F602 | Vickery Av | Urban | 664 | 2.4573 | 2.3172 | 112.71 |  |  | 12 | 0.067295 | 0.067295 | 0.000744 | 0.000744 | 12 | 0.0023906 | 0.0023906
F603 | Mulyan Av | Urban | 1022 | 0.77337 | 5.3467 | 193.65 |  |  | 8 | 0.040677 | 0.040677 | 0.00032173 | 0.00032173 | 8 | 0.00094732 | 0.00094732
FF1202 | Cunningham St | Urban | 684 | 0.34984 | 2.3254 | 75.33 | [7 empty] | 1 | 2.346e-05 | 2.346e-05
FF1206 | Sackville St | Urban | 1475 | 3.959 | 1.9081 | 254.12 | [7 empty] | 1 | 5.5856e-06 | 5.5856e-06
FF1213 |  | Urban | [11 empty] | 1 | 1.8991e-05 | 1.8991e-05
FF1217 | Tetrapak | Urban | 410 | 2.6916 | 1.7998 | 110.29 |  |  | 4 | 0.01215 | 0.01215 | 2.6811e-05 | 2.6811e-05 | 4 | 8.937e-05 | 8.937e-05
FF1239 | Myddleton Ave | Urban | 1463 | 4.9641 | 1.2259 | 215.21 | [7 empty] | 6 | 0.00085013 | 0.00085013
FF1243 | PINE RD | Urban | 80 | 1.3916 | 1.0224 | 62.31 |  |  | 1 | 0.0080947 | 0.0080947 | 8.937e-05 | 8.937e-05
FF1269 | Hedges St | Urban | 422 | 1.4082 | 1.5904 | 82.35 |  |  | 4 | 0.013441 | 0.013441 | 0.00010501 | 0.00010501
FF1276 | Dennistown Ave | Urban | 455 | 4.8118 | 1.6273 | 302.77 | [7 empty] | 3 | 6.7027e-05 | 6.7027e-05
FF1280 | Dursley Rd | Urban | 221 | 4.4549 | 1.537 | 199.9 |  |  | 4 | 0.0010121 | 0.0010121 | 6.7027e-06 | 6.7027e-06 | 4 | 4.4685e-06 | 4.4685e-06
FT1202 | Central Rd | Urban | 1592 | 5.3756 | 5.4341 | [8 empty] | 2 | 0.00010836 | 0.00010836
FT1203 | Hurt Pde | Urban | 326 | 3.3783 | 0.97228 |  |  |  | 1 | 0.00059431 | 0.00059431 | 3.1279e-05 | 3.1279e-05
FT1204 | George Fuller Dr | Urban | 708 | 3.8273 | 3.3142 |  |  |  | 1 | 0.0032888 | 0.0032888 | 7.1496e-05 | 7.1496e-05
FT1206 | Mt Kembla & Aux No1 | Urban | 434 | 12.1378 | 0.90745 |  |  |  | 25 | 0.073562 | 0.073562 | 0.0019996 | 0.0019996
FT1207 | Derribong Dr & Aux No2 | Urban | 932 |  | 5.3985 | [8 empty] | 3 | 0.00025805 | 0.00025805
FT1208 | Ridley Pde | Urban | 1541 | 8.5385 | 1.8472 |  |  |  | 16 | 0.090415 | 0.090415 | 0.00078645 | 0.00078645 | 16 | 0.0007507 | 0.0007507
FT1209 | Amaroo Av | Urban | 665 | 3.6107 | 1.3492 |  |  |  | 4 | 0.028592 | 0.028592 | 0.00041557 | 0.00041557 | 4 | 8.937e-06 | 8.937e-06
FT1210 | O'Briens Rd | Urban | 1389 | 8.2404 | 2.066 |  |  |  | 1 | 0.0024577 | 0.0024577 | 2.2342e-05 | 2.2342e-05 | 1 | 8.7135e-05 | 8.7135e-05
GG1232 | Highway Nth & Aux No3 | Rural Short | 941 | 22.0742 | 2.0178 | 121.01 |  |  | 600 | 7.7534 | 7.7534 | 0.17394 | 0.17394 | 600 | 0.0031279 | 0.0031279
GG1258 | Gerringong | Urban | 923 | 3.6814 | 1.65 | 134.42 |  |  | 9 | 1.3354 | 1.3354 | 0.011475 | 0.011475
GG1269 | Gerroa | Rural Short | 861 | 8.8939 | 2.0696 |  |  |  | 147 | 4.4858 | 4.4858 | 0.041523 | 0.041523 | 147 | 0.0035033 | 0.0035033
GG1295 | Foxground & Aux No2 | Rural Short | 227 | 44.0039 | 0.16222 | 32.71 |  |  | 2574 | 14.3344 | 11.2739 | 0.28964 | 0.28964 | 2574 | 0.026997 | 0.026997
GV1208 | Neil St | Urban | 1630 | 0.6897 | 4.9431 |  |  |  | 2 | 0.018115 | 0.018115 | 0.00012065 | 0.00012065 | 2 | 1.2288e-05 | 1.2288e-05
GV1223 | Montrose Ave | Urban | 836 | 3.2264 | 1.3409 |  |  |  | 75 | 5.1986 | 5.1986 | 0.039529 | 0.039529 | 75 | 0.0056135 | 0.0056135
GV1234 | South Street | Urban | 910 | 1.4472 | 4.3702 |  |  |  | 3 | 0.043638 | 0.043638 | 0.00036195 | 0.00036195 | 3 | 9.9424e-05 | 9.9424e-05
GV1241 | New York St | Urban | 563 | 0.73975 | 1.0609 |  |  |  | 9 | 0.17674 | 0.17674 | 0.00083449 | 0.00083449 | 9 | 0.00014076 | 0.00014076
GV1245 | Randle St | Urban | 386 | 1.1592 | 3.1894 | [8 empty] | 1 | 6.7027e-06 | 6.7027e-06
GV1249 | The Avenue | Urban | 603 | 1.5718 | 2.1348 | [8 empty] | 2 | 2.7928e-05 | 2.7928e-05
GV1278 | Granville TAFE | Urban | 216 | 0.5165 | 1.5147 |  |  |  | 4 | 0.0025738 | 0.0025738 | 0.00023236 | 0.00023236 | 4 | 0.00010278 | 0.00010278
GV1282 | Walpole St | Urban | 2208 | 2.4984 | 8.1009 |  |  |  | 16 | 0.14511 | 0.14511 | 0.00072389 | 0.00072389 | 16 | 0.00055409 | 0.00055409
H745 | Burragorang Rd | Rural Short | 553 | 44.7501 | 0.68566 | 316.75 |  |  | 3528 | 19.0484 | 19.0484 | 0.72152 | 0.72152 | 3528 | 0.052987 | 0.052987
HBA2 | Otford Rd | Rural Short | 798 | 19.3757 | 0.36002 | 161.48 |  |  | 320 | 8.2968 | 8.2968 | 0.057643 | 0.057643 | 320 | 0.008222 | 0.008222
HBB2 | Parkes St | Urban | 1338 | 11.5842 | 1.0048 | 179.64 |  |  | 300 | 1.3334 | 1.3334 | 0.020443 | 0.020443 | 300 | 0.019996 | 0.019996
HBC2 | Cemetery Rd | Urban | 809 | 11.7735 | 1.5534 | 291.68 |  |  | 343 | 11.7424 | 11.7424 | 0.10559 | 0.10559 | 343 | 0.017954 | 0.017954
HBD2 | Metropolitan Collery | Urban | 12 | 5.3251 | 0.06833 | 266.29 |  |  | 4 | 0.0084074 | 0.0084074 | 2.4577e-05 | 2.4577e-05 | 4 | 8.937e-06 | 8.937e-06
HKA2 | Tomerong | Rural Short | 838 | 78.163 | 1.9517 | 283.99 |  |  | 8960 | 70.3823 | 70.3823 | 1.8311 | 1.8311 | 8960 | 0.40095 | 0.40095
HKB2 | Santuary Point No 2 | Urban | 2251 | 17.571 | 2.7306 | 237 |  |  | 6 | 2.3758 | 2.3758 | 0.014123 | 0.014123 | 6 | 0.0011976 | 0.0011976
HKC2 | Jervis Bay | Rural Short | 803 | 13.2399 | 0.59016 | 127.03 |  |  | 25 | 2.6702 | 2.6702 | 0.013953 | 0.013953 | 25 | 0.0047757 | 0.0047757
HKD2 | Huskisson | Rural Short | 962 | 9.9532 | 1.9975 | 126.9 |  |  | 9 | 0.0077416 | 0.0077416 | 7.0379e-05 | 7.0379e-05 | 9 | 0.0005742 | 0.0005742
HKE2 | Basinview | Rural Short | 2194 | 29.564 | 3.3089 | 225.54 |  |  | 1100 | 15.9391 | 15.9391 | 0.26113 | 0.26113 | 1100 | 0.0992 | 0.0992
HKF2 | Vincentia | Urban | 2324 | 13.3663 | 0.47675 | 207.04 |  |  | 144 | 17.3527 | 17.8151 | 0.1442 | 0.1442 | 144 | 0.021073 | 0.021073
HKG2 | Sanctuary Point No 1 | Urban | 2727 | 15.436 | 0.98317 | 223.15 |  |  | 36 | 1.884 | 1.884 | 0.019565 | 0.019565
HR1206 | Centenary Rd | Urban | 1428 | 6.392 | 0.26797 | 194.9 |  |  | 1 | 0.010664 | 0.010664 | 0.000124 | 0.000124
HR1210 | Hampden St | Urban | 520 | 2.0317 | 0.6889 | 160.56 |  |  | 2 | 0.1699 | 0.1699 | 0.0032821 | 0.0032821 | 2 | 0.00012623 | 0.00012623
HR1217 | Great Western Highway | Urban | 236 | 0.87303 | 1.5377 | 104.55 | [7 empty] | 2 | 2.0108e-05 | 2.0108e-05
HR1236 | Lane St | Urban | 1301 | 3.5726 | 2.3254 | [8 empty] | 1 | 1.1171e-06 | 1.1171e-06
HR1239 | Essington St | Urban | 711 | 3.2621 | 1.2594 | 91.9 |  |  | 2 | 0.0027615 | 0.0027615 | 2.2342e-06 | 2.2342e-06 | 2 | 5.2505e-05 | 5.2505e-05
HR1243 | Chelmsford Rd | Urban | 1037 | 3.4076 | 1.4296 |  |  |  | 1 | 0.0031603 | 0.0031603 | 7.7081e-05 | 7.7081e-05
HR1247 | Fullagar Rd | Urban | 561 | 2.2325 | 1.0749 |  |  |  | 1 | 0.0024923 | 0.0024923 | 2.5694e-05 | 2.5694e-05
HR1250 | Dunmore St | Urban | 1295 | 1.7706 | 3.0284 | [8 empty] | 2 | 0.0004893 | 0.0004893
HR1269 | Westmead | Urban | 2128 | 5.3765 | 2.1649 |  |  |  | 36 | 1.5878 | 1.5878 | 0.015329 | 0.015329
HR1273 | Verlie St | Urban | 1415 | 6.0076 | 1.0373 | [8 empty] | 1 | 1.7874e-05 | 1.7874e-05
HR1276 | Boronia St | Urban | 1610 | 5.1536 | 1.7644 | 212.09 |  |  | 1 | 0.0061665 | 0.0061665 | 7.2613e-05 | 7.2613e-05
J459 | Queenscliff Dr + Aux No 1 | Urban | 1815 | 0.86856 | 16.0475 | 307.45 |  |  | 169 | 1.3921 | 1.3921 | 0.028943 | 0.028943
J460 | Pirelli | Urban | 60 |  | 3.8139 | 157.41 |  |  | 1 | 0.0032162 | 0.0032162 | 6.591e-05 | 6.591e-05
J462 | Montore Rd | Urban | 31 |  | 2.1545 | 198.41 | [7 empty] | 1 | 2.2342e-06 | 2.2342e-06
J465 | Swettenham Rd | Urban | 1588 |  | 12.1302 | 277.77 |  |  | 49 | 1.669 | 1.669 | 0.013904 | 0.013904 | 49 | 0.0044338 | 0.0044338
J467 | Reaghs Farm Rd & Capacitor bank No.1 | Urban | 21 |  | 1.8258 | 272.76 |  |  | 4 | 0.0029202 | 0.0029202 | 3.1279e-05 | 3.1279e-05
J468 | Eaglevale Rd | Urban | 800 | 1.154 | 7.3469 | 293.19 |  |  | 4 | 0.011844 | 0.011844 | 4.9153e-05 | 4.9153e-05
J469 | Pembroke Rd | Urban | 928 | 6.2415 | 2.2242 | 187.23 |  |  | 196 | 0.57923 | 0.57923 | 0.0030028 | 0.0030028 | 196 | 0.0029012 | 0.0029012
J472 | Lincoln St | Urban | 629 | 1.7609 | 4.1016 | 170.77 |  |  | 9 | 0.039295 | 0.039295 | 0.0004893 | 0.0004893
J473 | Pembury Rd | Urban | 1394 |  | 10.995 | 254.66 |  |  | 8 | 0.0088252 | 0.0088252 | 9.3838e-05 | 9.3838e-05 | 8 | 0.00054515 | 0.00054515
J474 | North Steyne Rd | Urban | 1129 | 2.0457 | 8.1306 | 264.35 |  |  | 64 | 0.15877 | 0.15877 | 0.0015372 | 0.0015372
J477 | Westmoreland Rd | Rural Short | 1304 | 10.8693 | 6.4551 | 185.84 |  |  | 98 | 1.6814 | 1.6814 | 0.021598 | 0.021598 | 98 | 0.0051455 | 0.0051455
J478 | Park Hill Rd | Urban | 1338 | 3.0106 | 9.2089 | 177.63 |  |  | 256 | 2.0374 | 2.0374 | 0.0075428 | 0.0075428 | 256 | 0.010081 | 0.010081
J480 | Airds Rd | Urban | 4 | 0.75453 | 1.2027 | 99.22 |  |  | 1 | 0.00028598 | 0.00028598 | 3.3514e-06 | 3.3514e-06
J481 | Alderney St | Urban | 1281 | 0.25427 | 9.413 | 136.78 |  |  | 5 | 0.077316 | 0.077316 | 0.00051946 | 0.00051946 | 5 | 6.0324e-05 | 6.0324e-05
J482 | Lever + Kitchen | Urban | 777 | 3.3065 | 3.4034 | 244.2 |  |  | 16 | 0.23932 | 0.23932 | 0.0072568 | 0.0072568 | 16 | 0.0010546 | 0.0010546
J483 | St Andrews Rd + Aux No 3 | Urban | 1181 | 0.18402 | 13.4775 | 248.49 |  |  | 50 | 0.1406 | 0.1406 | 0.0012065 | 0.0012065 | 50 | 0.0041892 | 0.0041892
J489 | Hoddle Av | Urban | 1929 | 9.4816 | 0.59823 | 304.55 |  |  | 80 | 1.2687 | 1.2687 | 0.0099871 | 0.0099871 | 80 | 0.0023594 | 0.0023594
J491 | Waminda Av | Urban | 1520 | 7.358 | 2.713 | 253.91 |  |  | 80 | 0.18895 | 0.18895 | 0.0019661 | 0.0019661 | 80 | 0.0063095 | 0.0063095
J492 | Manning St | Urban | 964 | 5.2276 | 0.71219 | 109.56 |  |  | 3 | 0.00066022 | 0.00066022 | 3.3514e-06 | 3.3514e-06 | 3 | 0.00016422 | 0.00016422
J493 | Junction Rd + Aux No 2 | Urban | 788 | 0.071163 | 3.833 | 178.47 |  |  | 432 | 1.2393 | 1.2393 | 0.007802 | 0.007802 | 432 | 0.040055 | 0.040055
J495 | Sirius St | Urban | 1030 | 1.2 | 5.8514 | 182.53 |  |  | 125 | 0.12735 | 0.12735 | 0.0018153 | 0.0018153 | 125 | 0.011786 | 0.011786
J496 | Stewart St | Urban | 891 | 3.1805 | 1.555 | 137.52 |  |  | 125 | 1.7625 | 1.7625 | 0.028989 | 0.028989 | 125 | 0.011506 | 0.011506
J497 | Peppin Cres | Urban | 932 | 9.7526 | 3.9903 | 63.72 |  |  | 36 | 0.01429 | 0.01429 | 0.00018768 | 0.00018768 | 36 | 0.0026543 | 0.0026543
J499 | Deans Rd | Urban | 929 |  | 4.5767 | 123.05 |  |  | 256 | 1.8839 | 1.8839 | 0.023343 | 0.023343
J500 | Briar Rd | Urban | 732 | 1.4042 | 3.7219 | 108.58 |  |  | 9 | 0.01113 | 0.01113 | 0.00019103 | 0.00019103 | 9 | 0.00077416 | 0.00077416
J502 | St Johns Rd | Urban | 760 | 1.5233 | 3.4748 | 177.07 |  |  | 25 | 1.086 | 1.086 | 0.01154 | 0.01154 | 25 | 0.0013405 | 0.0013405
J503 | Akuna Av & Cap Bank 1 | Urban | 410 |  | 3.5695 | 284.97 |  |  | 25 | 0.12129 | 0.12129 | 0.00075964 | 0.00075964
J504 | Docharty Rd + Aux No 1 | Urban | 1197 | 4.2999 | 1.7184 | 178.18 |  |  | 252 | 9.6815 | 9.6815 | 0.069299 | 0.069299 | 252 | 0.012869 | 0.012869
J506 | Collins Prom | Urban | 1184 |  | 5.7954 | 171.5 |  |  | 75 | 0.0775 | 0.0775 | 0.0010557 | 0.0010557 | 75 | 0.0046081 | 0.0046081
J507 | Oakley Rd | Urban | 865 | 5.9449 | 4.9741 | 211.68 |  |  | 9 | 0.027934 | 0.027934 | 0.00036865 | 0.00036865 | 9 | 0.00055297 | 0.00055297
J509 | MWS+DB | Urban | 273 | 5.0621 | 1.1103 | 183.21 |  |  | 6 | 1.1288 | 0.36162 | 0.00069708 | 0.00069708
J510 | Third Av | Urban | 1521 | 2.0066 | 6.2084 | 287.97 |  |  | 720 | 1.3678 | 1.3678 | 0.018902 | 0.018902 | 720 | 0.054372 | 0.054372
J512 | Quarter Sessions Rd | Urban | 1630 | 6.4266 | 3.2806 | 245.76 |  |  | 60 | 18.3572 | 0.19146 | 0.0026476 | 0.0026476 | 60 | 0.0021449 | 0.0021449
J514 | Bensley Rd | Urban | 1876 |  | 9.8222 | 247.37 |  |  | 162 | 3.6274 | 3.6274 | 0.049526 | 0.049526 | 162 | 0.0080533 | 0.0080533
J515 | Gordon Av + Aux No 3 | Urban | 551 | 0.88594 | 8.8273 | 190.77 |  |  | 4 | 0.0078444 | 0.0078444 | 8.937e-06 | 8.937e-06 | 4 | 7.1496e-05 | 7.1496e-05
J516 | Cumberland Rd | Urban | 1354 | 3.3305 | 2.8213 | 183.26 |  |  | 64 | 0.96522 | 0.96522 | 0.013548 | 0.013548 | 64 | 0.0060771 | 0.0060771
JBA2 | Macquarie St | Rural Short | 609 | 64.6671 | 0.11581 | 150.57 |  |  | 12852 | 238.1782 | 115.0934 | 1.4889 | 1.4889 | 12852 | 0.1309 | 0.1309
JBB2 | Golden Valley Rd | Rural Short | 307 | 44.1451 | 2.3402 | 49.77 |  |  | 8450 | 129.4679 | 76.4926 | 0.66002 | 0.66002 | 8450 | 0.033402 | 0.033402
KC1214 | Aldington Road | Rural Short | 223 | 12.5509 | 1.8969 | 140.56 |  |  | 36 | 0.020765 | 0.020765 | 0.00022789 | 0.00022789
KC1221 | Exeter Road | Rural Short | 445 | 15.3413 | 0.2074 | 229.39 |  |  | 20 | 0.94103 | 0.94103 | 0.0050717 | 0.0050717 | 20 | 0.00027258 | 0.00027258
KC1236 | Clifton Ave | Rural Short | 259 | 32.5063 | 0.4413 | 141.54 |  |  | 100 | 0.51678 | 0.51678 | 0.0052505 | 0.0052505 | 100 | 0.00011171 | 0.00011171
KC1262 | Cross Street | Rural Short | 322 | 18.8023 | 0.05393 | 56.09 |  |  | 16 | 0.046937 | 0.046937 | 0.00078198 | 0.00078198 | 16 | 1.7874e-05 | 1.7874e-05
KC1284 | Gurner Ave | Rural Short | 847 | 24.3323 | 0.09901 | 160.64 |  |  | 252 | 1.1257 | 1.1257 | 0.016187 | 0.016187 | 252 | 0.0057911 | 0.0057911
KC1288 | Mamre Road | Rural Short | 353 | 18.0113 | 2.2242 | 122.97 |  |  | 54 | 1.3975 | 1.3975 | 0.0099736 | 0.0099736 | 54 | 0.00049265 | 0.00049265
KMA2 | Gipps Street West | Urban | 1404 | 6.2047 | 2.3352 | 175.66 |  |  | 504 | 101.8839 | 47.5455 | 0.39098 | 0.39098 | 504 | 0.070003 | 0.070003
KMB2 | Princes Highway North | Urban | 1453 | 8.9764 | 1.6068 | 197.01 |  |  | 567 | 21.8243 | 21.8243 | 0.53924 | 0.53924 | 567 | 0.030404 | 0.030404
KMC2 | Hothersal Street North | Urban | 456 | 3.1783 | 2.568 | 163.98 |  |  | 63 | 0.22282 | 0.22282 | 0.014263 | 0.014263 | 63 | 0.0033078 | 0.0033078
KMD2 | Gipps Street ßEast | Urban | 1309 | 8.2473 | 3.4463 | 193.63 |  |  | 252 | 40.5465 | 2.5027 | 0.10834 | 0.10834 | 252 | 0.020457 | 0.020457
KME2 | Brown Street | Rural Short | 853 | 10.8511 | 2.5705 | 85.16 |  |  | 343 | 9.765 | 9.765 | 0.15863 | 0.15863 | 343 | 0.017407 | 0.017407
KMF2 | Hothersal St | Urban | 1451 | 5.7203 | 1.2431 | 220.92 |  |  | 384 | 62.0808 | 13.8885 | 0.35126 | 0.35126 | 384 | 0.034693 | 0.034693
KVA2 | Mount Scanzi Rd | Rural Short | 344 | 64.1802 | 0.42307 | 51.43 |  |  | 2888 | 22.8336 | 22.8336 | 0.27695 | 0.27695 | 2888 | 0.030649 | 0.030649
KVB2 | Kangaroo Valley | Rural Short | 382 | 47.5645 | 0.09313 | 98.19 |  |  | 3040 | 27.115 | 26.3329 | 0.38697 | 0.38697 | 3040 | 0.047545 | 0.047545
KVC2 | Dam Rd | Rural Short | 127 | 38.6361 |  | 20.76 |  |  | 121 | 0.67334 | 0.67334 | 0.0066357 | 0.0066357
KVD2 | Bendeela | Rural Short | 93 | 31.556 |  |  |  |  | 108 | 0.27442 | 0.27442 | 0.0050069 | 0.0050069 | 108 | 0.00036195 | 0.00036195
KYA2 | T & G SUB RAILWAY PDE | Urban | 243 |  | 1.9546 | 82.86 |  |  | 1 | 0.0002346 | 0.0002346 | 1.1171e-06 | 1.1171e-06 | 1 | 1.1171e-06 | 1.1171e-06
KYB2 | Grace Bros (East) Burelli St | Urban | 244 |  | 1.2251 | 130.8 |  |  | 4 | 0.011104 | 0.011104 | 6.0324e-05 | 6.0324e-05
KYC2 | CML Sub | Urban | 142 |  | 0.79135 | 118.15 | [7 empty] | 1 | 9.6072e-05 | 9.6072e-05
KYE2 | Grace Bros (West) Burelli St | Urban | 235 |  | 1.536 | 161.26 |  |  | 1 | 0.00035301 | 0.00035301 | 5.5856e-06 | 5.5856e-06 | 1 | 1.1171e-06 | 1.1171e-06
KYF2 | Wearne St | Urban | 296 | 0.91898 | 1.6215 | 154.57 |  |  | 1 | 0.00099871 | 0.00099871 | 0.0003329 | 0.0003329
KYH2 | IMB Burelli St | Urban | 375 | 0.25411 | 1.3492 | 186.33 |  |  | 1 | 0.0014299 | 0.0014299 | 0.00035748 | 0.00035748 | 1 | 0.00012065 | 0.00012065
L502 | Artisan Rd & Cap Bank 3 | Urban | 23 | 0.33653 | 1.5596 | 282.69 | [7 empty] | 1 | 5.9207e-05 | 5.9207e-05
L504 | Prime Dr | Urban | 105 | 1.194 | 1.4332 | 108.41 |  |  | 1 | 0.00089034 | 0.00089034 | 6.7027e-06 | 6.7027e-06
L508 | Early St & Cap Bank 1 | Urban | 821 |  | 2.1308 | 191.94 | [7 empty] | 2 | 0.00016757 | 0.00016757
L509 | Allen Pl & Restwell Rd | Urban | 790 | 0.65535 | 7.2465 |  |  |  | 8 | 0.0030028 | 0.0030028 | 4.4685e-05 | 4.4685e-05 | 8 | 1.3405e-05 | 1.3405e-05
L513 | Mimosa Rd South & Horsley Dr | Urban | 985 |  | 5.8594 | 234.88 |  |  | 16 | 0.025376 | 0.025376 | 0.00042451 | 0.00042451
L514 | Housman St + Aux No 1 | Urban |  |  | 0.33188 | 92.23 |  |  | 1 | 0.0014902 | 0.0014902 | 2.7928e-05 | 2.7928e-05
L516 | Faulklands St + Aux No 2 | Urban | 1276 |  | 8.4369 | 306.74 |  |  | 9 | 0.046007 | 0.046007 | 0.00018097 | 0.00018097
L521 |  | Urban | [11 empty] | 1 | 6.7027e-06 | 6.7027e-06
L526 | Ariel Cres | Urban | 867 | 1.8555 | 7.5372 | 262.21 |  |  | 18 | 0.94383 | 0.94383 | 0.010309 | 0.010309 | 18 | 0.0015986 | 0.0015986
L533 | Alpha St | Urban | 259 | 0.1533 | 2.3689 | 143.54 |  |  | 1 | 0.018565 | 0.018565 | 0.00027928 | 0.00027928
L534 | Flushcombe Rd | Urban | 536 | 2.4435 | 1.4935 | 71.5 |  |  | 16 | 0.12342 | 0.12342 | 0.00067921 | 0.00067921 | 16 | 0.00067921 | 0.00067921
L535 | Westpoint | Urban |  |  | 0.77993 | 21.71 | [7 empty] | 1 | 2.2342e-06 | 2.2342e-06
L537 | Reservoir Rd | Urban | 1642 | 6.3135 | 0.30185 | 247.35 |  |  | 735 | 18.9822 | 18.9822 | 0.31975 | 0.31975 | 735 | 0.044229 | 0.044229
L540 | Kelso Cres | Urban | 292 | 0.034252 | 2.05 | 275.05 |  |  | 1 | 0.0006457 | 0.0006457 | 2.2342e-06 | 2.2342e-06 | 1 | 3.5748e-05 | 3.5748e-05
L543 | Fifth Avenue | Urban | 811 | 1.864 | 3.5964 | 220.62 |  |  | 2 | 0.42828 | 0.42828 | 0.0038764 | 0.0038764 | 2 | 0.00013182 | 0.00013182
L544 | Vincent St | Urban | 1205 | 4.2672 | 1.52 | 139.97 |  |  | 8 | 0.088449 | 0.088449 | 0.00044685 | 0.00044685 | 8 | 0.00034184 | 0.00034184
L545 | Westpoint No 3 | Urban | 3 |  | 0.26165 | 205.44 | [7 empty] | 1 | 1.1171e-06 | 1.1171e-06
L579 | Roy St | Rural Short | 827 | 4.1782 | 3.2877 | 88.34 |  |  | 2 | 0.1546 | 0.1546 | 0.0018567 | 0.0018567 | 2 | 7.8198e-05 | 7.8198e-05
L580 | Methven St | Urban | 143 | 0.68151 | 1.3258 | 62.66 |  |  | 1 | 0.013366 | 0.013366 | 0.00016087 | 0.00016087
L582 | Lowther | Rural Short | 1210 | 155.1806 | 1.4232 | 93.57 |  |  | 23548 | 363.2061 | 363.2061 | 2.3204 | 2.3204 | 23548 | 0.15126 | 0.15126
L584 | Marrangaroo | Rural Short | 373 | 32.708 | 2.9994 | 146.43 |  |  | 1728 | 13.1237 | 13.1237 | 0.1073 | 0.1073 | 1728 | 0.021556 | 0.021556
L585 | Laurence St + Aux No 2 | Rural Short | 739 | 7.8112 | 1.6295 | 65.35 |  |  | 16 | 0.27984 | 0.27984 | 0.0033782 | 0.0033782
L588 | Hartley | Rural Short | 1036 | 65.4088 | 2.0254 | 151.55 |  |  | 4000 | 37.8827 | 37.8827 | 0.62693 | 0.62693 | 4000 | 0.035748 | 0.035748
L590 | Academy St | Rural Short | 78 | 0.65442 | 0.5677 | 6.39 |  |  | 1 | 0.0072903 | 0.0072903 | 8.7135e-05 | 8.7135e-05
L591 | Old Bowenfels | Rural Short | 1435 | 135.3318 | 5.2238 | 162.46 |  |  | 25308 | 346.0135 | 353.2855 | 2.3953 | 2.3953 | 25308 | 0.15922 | 0.15922
L940 | Singleton Rd | Rural Short | 548 | 39.9961 | 1.0405 | 110.97 |  |  | 1000 | 31.9016 | 31.9016 | 0.16578 | 0.16578 | 1000 | 0.023124 | 0.023124
L941 | Spinks Rd | Rural Short | 654 | 31.9016 | 0.0598 | 155.62 |  |  | 612 | 11.3794 | 11.3794 | 0.10335 | 0.10335 | 612 | 0.014237 | 0.014237
L942 | Wilberforce + Aux No 1 | Rural Short | 563 | 22.7973 | 0.43502 | 141.84 |  |  | 90 | 1.6896 | 1.6896 | 0.0186 | 0.0186 | 90 | 0.0016991 | 0.0016991
L946 | Aux No.2 | Rural Short | 487 | 37.4321 | 0.21001 | 148.41 |  |  | 512 | 2.8952 | 2.8952 | 0.074427 | 0.074427 | 512 | 0.0044327 | 0.0044327
L947 | Chestnut Dr | Rural Short | 850 | 19.3638 | 0.22448 | 229.79 |  |  | 539 | 2.7808 | 2.7808 | 0.071309 | 0.071309 | 539 | 0.01467 | 0.01467
L948 | Shepherds Rd | Rural Short | 716 | 21.7467 | 0.04417 | 208.99 |  |  | 1500 | 49.6715 | 49.6715 | 0.21583 | 0.21583 | 1500 | 0.030944 | 0.030944
M158 | Comalco Fabrications | Urban | 4 | 0.45171 | 1.4071 | 212.35 | [7 empty] | 1 | 1.1171e-06 | 1.1171e-06
M159 | Sammut St | Urban | 131 | 1.5249 | 0.76927 | 119.4 |  |  | 4 | 0.0061754 | 0.0061754 | 2.0108e-05 | 2.0108e-05 | 4 | 4.9153e-05 | 4.9153e-05
M160 | Cooper St | Urban | 49 | 3.0204 | 1.2734 | 199.69 |  |  | 4 | 0.015591 | 0.015591 | 0.00012512 | 0.00012512 | 4 | 3.5748e-05 | 3.5748e-05
M166 | Britton St | Urban | 71 | 1.4083 | 0.8955 | 219.49 |  |  | 2 | 0.0017516 | 0.0017516 | 1.564e-05 | 1.564e-05 | 2 | 3.2396e-05 | 3.2396e-05
M170 | ANZPAC ß& Sub 24275 | Urban | 10 |  | 2.3451 | 207.82 | [7 empty] | 2 | 1.8991e-05 | 1.8991e-05
M388 | Parliament Rd | Urban | 1099 | 2.1019 | 4.5631 | 270.53 |  |  | 50 | 0.2127 | 0.2127 | 0.012054 | 0.012054 | 50 | 0.0037703 | 0.0037703
M389 | River Rd | Urban | 431 | 4.1087 | 4.3547 | 369.18 |  |  | 45 | 1.9927 | 1.9927 | 0.019672 | 0.019672 | 45 | 0.00059319 | 0.00059319
M390 | Mowatt St | Urban | [6 empty] | 8 | 0.13198 | 0.13198 | 0.005179 | 0.005179 | 8 | 2.6811e-05 | 2.6811e-05
M391 | West Camden STP | Rural Short |  | 2.795 | 1.2011 | 306.42 |  |  | 3 | 0.00076076 | 0.00076076 | 1.3405e-05 | 1.3405e-05 | 3 | 5.3622e-05 | 5.3622e-05
M393 | South Camden | Urban | [6 empty] | 4 | 0.044146 | 0.044146 | 0.0025604 | 0.0025604
M393 |  | Urban |  |  |  | 216.06 |  |  | 4 | 0.044146 | 0.044146 | 0.0025604 | 0.0025604
M394 | Cawdor Rd & Aux No 2 | Urban | 500 | 17.8716 | 3.7759 | 354.78 |  |  | 24 | 0.38564 | 0.51702 | 0.0080634 | 0.0080634 | 24 | 0.00040216 | 0.00040216
M396 | Graham Hill Rd | Urban | 274 | 0.33866 | 3.0473 | 56.93 |  |  | 12 | 0.14969 | 0.19777 | 0.0025783 | 0.0025783
M397 | Richardson Rd | Urban | 623 | 0.31598 | 7.9734 | 115.53 |  |  | 54 | 0.46768 | 0.46768 | 0.013211 | 0.013211 | 54 | 0.0010356 | 0.0010356
M399 | Geordie St | Rural Short | 1062 | 32.2908 | 0.92898 | 92.7 |  |  | 162 | 3.0876 | 3.0876 | 0.025557 | 0.025557 | 162 | 0.0047958 | 0.0047958
M400 | Gray St | Urban | 762 | 3.7427 | 4.1923 | 183.53 |  |  | 4 | 0.28489 | 0.28489 | 0.0034229 | 0.0034229 | 4 | 6.9261e-05 | 6.9261e-05
MC1252 | The Northern Rd South | Rural Short | 481 | 9.5432 | 11.7033 |  |  |  | 64 | 1.1168 | 1.1168 | 0.0070602 | 0.0070602 | 64 | 0.0023415 | 0.0023415
MC1278 | The Northern Rd North | Rural Short | 29 | 11.5933 | 0.11662 |  |  |  | 4 | 0.011631 | 0.011631 | 0.00011171 | 0.00011171
MG1204 |  | Urban | [11 empty] | 1 | 2.2342e-06 | 2.2342e-06
MG1208 | Mittagong | Urban | 807 | 8.0758 | 0.91112 |  |  |  | 16 | 1.2974 | 1.2974 | 0.0087538 | 0.0087538 | 16 | 0.0021985 | 0.0021985
MG1219 | Yerrimbool | Rural Short | 576 | 39.1739 | 1.5841 |  |  |  | 288 | 6.2003 | 6.2003 | 0.03834 | 0.03834 | 288 | 0.034626 | 0.034626
MG1234 | Bong Bong Rd | Rural Short | 1086 | 10.2021 | 4.9141 | [8 empty] | 1 | 6.8144e-05 | 6.8144e-05
MG1267 | Hilltop | Rural Short | 1439 | 55.4071 | 0.81151 |  |  |  | 7056 | 320.3991 | 320.3991 | 3.572 | 3.572 | 7056 | 0.43932 | 0.43932
MG1282 | Willow Vale | Rural Short | 920 | 29.6426 | 1.8413 |  |  |  | 8 | 0.00090263 | 0.00090263 | 4.0216e-05 | 4.0216e-05 | 8 | 0.00080879 | 0.00080879
MG1286 | Welby | Rural Short | 1332 | 34.563 | 0.62077 |  |  |  | 12 | 0.2009 | 0.26531 | 0.0017382 | 0.0017382 | 12 | 0.0023996 | 0.0023996
MGA2 |  | Rural Short | [11 empty] | 1 | 4.4685e-06 | 4.4685e-06
MGB2 |  | Urban | [6 empty] | 1 | 0.016505 | 0.016505 | 0.00022231 | 0.00022231
MGC2 |  | Rural Short | [6 empty] | 96 | 0.054078 | 0.054078 | 0.00032173 | 0.00032173 | 96 | 0.0023236 | 0.0023236
MGD2 |  | Rural Short | [11 empty] | 16 | 0.0010702 | 0.0010702
MGE2 |  | Rural Short | [6 empty] | 45 | 0.014009 | 0.014009 | 0.0063173 | 0.0063173 | 45 | 0.0040116 | 0.0040116
MGF2 |  | Rural Short | [6 empty] | 64 | 2.6021 | 2.6021 | 0.020323 | 0.020323 | 64 | 0.018088 | 0.018088
MR2206 | Petal Parkway | Urban | 494 | 0.44323 | 6.9172 | 41.32 |  |  | 9 | 0.042197 | 0.042197 | 0.00044573 | 0.00044573 | 9 | 0.0001307 | 0.0001307
MR2224 | Hezlett Rd | Urban | 181 | 4.5113 | 6.296 | 52.2 |  |  | 1089 | 4.9302 | 4.9302 | 0.14599 | 0.14599 | 1089 | 0.012841 | 0.012841
MR2225 | Schofield Rd | Urban | 1274 | 1.3786 | 11.4087 | 173.51 |  |  | 3 | 0.0037301 | 0.0037301 | 4.0216e-05 | 4.0216e-05 | 3 | 6.591e-05 | 6.591e-05
MR2231 | Caddies Blvd | Urban | 806 |  | 13.4215 | 114.65 | [7 empty] | 1 | 3.5748e-05 | 3.5748e-05
MR2232 | Annangrove Rd | Urban | 894 | 31.1295 | 5.1717 | 173.05 |  |  | 4400 | 265.5489 | 265.5489 | 1.8376 | 1.8376 | 4400 | 0.14746 | 0.14746
MR2292 | Adelphi Rd | Urban | 907 | 1.4617 | 5.8647 | 143.08 |  |  | 24 | 1.1397 | 1.1397 | 0.023446 | 0.023446 | 24 | 0.0024085 | 0.0024085
MR2298 | Milford Dr | Urban | 1166 |  | 14.1212 | 188.43 |  |  | 1 | 0.0045701 | 0.0045701 | 1.3405e-05 | 1.3405e-05 | 1 | 3.9099e-05 | 3.9099e-05
MR2299 | Mungerie Road | Urban | 1421 |  | 11.3651 | 230.5 |  |  | 16 | 0.018535 | 0.018535 | 0.00022342 | 0.00022342 | 16 | 0.00055409 | 0.00055409
MVB2 | Headlams Rd | Rural Short | 1076 | 125.5426 | 0.80408 | 188.56 |  |  | 12168 | 153.2519 | 153.2519 | 1.3912 | 1.3912 | 12168 | 0.4969 | 0.4969
MVC2 | Medway | Rural Short | 746 | 78.8864 | 0.25034 | 91.68 |  |  | 3969 | 6.6066 | 6.6066 | 0.23647 | 0.23647 | 3969 | 0.1611 | 0.1611
MVD2 | Moss Vale | Rural Short | 1487 | 26.1258 | 2.3272 | 226.25 |  |  | 1008 | 10.2702 | 10.2702 | 0.29643 | 0.29643 | 1008 | 0.0086867 | 0.0086867
MVE2 | Sutton Forest | Rural Short | 461 | 13.2828 | 2.3833 | 152.31 |  |  | 200 | 0.042652 | 0.042652 | 0.010724 | 0.010724 | 200 | 0.0031279 | 0.0031279
MVF2 | Nowra Rd | Rural Short | 1030 | 83.4908 | 4.495 | 151.47 |  |  | 11616 | 35.5555 | 35.5555 | 0.74969 | 0.74969 | 11616 | 0.52392 | 0.52392
MVG2 | Berrima Junction | Urban | 12 | 2.8598 | 1.7248 | 229.59 |  |  | 1 | 1.3405e-05 | 1.3405e-05 | 1.3405e-05 | 1.3405e-05
MVH2 | Semkin Rd | Rural Short | 1490 | 49.3287 | 2.1067 | 206.32 |  |  | 12096 | 246.482 | 246.482 | 4.6461 | 4.6461 | 12096 | 0.3346 | 0.3346
MYC2 | Northfields Ave | Urban | 1243 | 4.0365 | 2.3583 | 236.43 |  |  | 1 | 0.0044819 | 0.0044819 | 7.4847e-05 | 7.4847e-05 | 1 | 8.937e-05 | 8.937e-05
MYE2 | Dumfries Ave | Rural Short | 402 | 6.3309 | 1.2656 | 51.13 |  |  | 1 | 7.7081e-05 | 7.7081e-05 | 1.1171e-06 | 1.1171e-06 | 1 | 3.3514e-06 | 3.3514e-06
MYG2 | Strone Ave | Urban | 1219 | 5.7597 | 3.2108 | 134.71 | [7 empty] | 6 | 0.00025247 | 0.00025247
MYK2 | Mount Ousley Rd | Urban | 891 | 1.9751 | 2.8663 | 182.87 |  |  | 4 | 0.042406 | 0.042406 | 8.937e-05 | 8.937e-05 | 4 | 7.7081e-05 | 7.7081e-05
MYM2 | McMahon St | Urban | 1346 | 7.5936 | 0.8613 | 133.65 |  |  | 9 | 0.033661 | 0.033661 | 0.00032508 | 0.00032508 | 9 | 0.0015081 | 0.0015081
MYP2 | University 2 | Urban |  |  | 1.5638 | 179.55 | [7 empty] | 2 | 4.0216e-05 | 4.0216e-05
MYQ2 | Madoline St | Urban | 1904 | 8.3566 | 2.1011 | 182.31 |  |  | 48 | 0.12943 | 0.12943 | 0.0020644 | 0.0020644 | 48 | 0.0067742 | 0.0067742
NA1207 | Kalandar St | Rural Short | 1972 | 35.2555 | 4.9807 | 225.31 |  |  | 594 | 16.7523 | 7.6729 | 0.061786 | 0.061786 | 594 | 0.029197 | 0.029197
NA1214 | Nowra Fair No1 | Urban | 695 | 3.1199 | 1.041 | 245.31 |  |  | 4 | 0.14786 | 0.14786 | 0.0031011 | 0.0031011 | 4 | 0.00014746 | 0.00014746
NA1218 | Egans Ln | Urban | 606 | 3.9257 | 0.94349 | 241.81 |  |  | 4 | 0.019447 | 0.019447 | 6.2559e-05 | 6.2559e-05 | 4 | 0.00016087 | 0.00016087
NA1225 | Albatross Rd | Urban | 455 | 29.6707 | 1.723 | 119.07 | [7 empty] | 2 | 2.1225e-05 | 2.1225e-05
NA1266 | Nowra Mall No1 | Urban | 1041 | 5.9115 | 1.2009 | 239.57 |  |  | 128 | 3.3942 | 3.3942 | 0.0047902 | 0.0047902 | 128 | 0.010724 | 0.010724
NA1270 | West Nowra | Rural Short | 668 | 57.896 | 3.5503 | 84.52 |  |  | 175 | 0.69319 | 0.69319 | 0.032061 | 0.032061 | 175 | 0.007373 | 0.007373
NA1281 | McKay St | Urban | 2259 | 5.4817 | 7.7811 | 224.46 |  |  | 80 | 12.6565 | 0.68587 | 0.0045132 | 0.0045132 | 80 | 0.011886 | 0.011886
NE1216 | Interchange No.1 | Urban | 22 | 5.3345 | 4.5276 |  |  |  | 2 | 0.0077137 | 0.00054962 | 4.4685e-06 | 4.4685e-06 | 2 | 2.0108e-05 | 2.0108e-05
NE1219 | Spare (Future Capacitor) | Urban | 1 |  | 2.6936 | 43.19 |  |  | 1 | 0.00033737 | 0 | 0 | 0
NE1249 | Ingram Micro 2 | Urban | 2 |  | 0.29478 | 31.56 |  |  | 1 | 0.00067586 | 0 | 0 | 0
NE1275 | Spare | Urban | 2 |  | 2.4741 | 37.96 |  |  | 1 | 0.00067586 | 0 | 0 | 0
NE1279 | Spare (Future Capacitor) | Urban | 3 | 0.31408 | 1.5939 | 22.47 |  |  | 1 | 0.0010143 | 0 | 0 | 0
NE1282 | Interchange No.2 | Urban | 5 | 0.09498 | 1.6188 | [8 empty] | 1 | 4.4685e-06 | 4.4685e-06
NG1210 | Silverdale | Rural Short | 632 | 37.2088 | 2.6463 | 213.75 |  |  | 512 | 1.0303 | 1.0303 | 0.036606 | 0.036606 | 512 | 0.014728 | 0.014728
NG1247 | Warragamba | Urban | 872 | 9.2523 | 0.11446 | 173.71 |  |  | 18 | 0.31837 | 0.31837 | 0.0063408 | 0.0063408 | 18 | 0.00027146 | 0.00027146
NG1262 | Ridgehaven | Urban | 422 | 11.0025 | 0.72234 | 222.75 |  |  | 32 | 0.11505 | 0.11505 | 0.00059878 | 0.00059878 | 32 | 0.00030386 | 0.00030386
NG1299 | PMS 26047 | Rural Short | 225 | 20.4075 | 0.95172 | 75.26 |  |  | 256 | 1.9683 | 1.9683 | 0.010331 | 0.010331 | 256 | 0.0085795 | 0.0085795
NN1214 | Glenlee Rd | Rural Short | 317 | 3.8245 | 4.8583 |  |  |  | 1 | 0.022528 | 0.022528 | 0.00033737 | 0.00033737
NN1233 | Kirkham Ln | Urban | 1042 | 31.0554 | 12.5919 |  |  |  | 75 | 0.89486 | 0.89486 | 0.02046 | 0.02046 | 75 | 0.0026532 | 0.0026532
NN1255 | Mowatt St | Urban | 1091 | 2.7794 | 9.3483 |  |  |  | 16 | 0.49048 | 0.49048 | 0.0050717 | 0.0050717
NN1277 | South Camden | Urban | 42 | 4.2285 | 0.24446 |  |  |  | 48 | 0.096184 | 0.096184 | 0.0013942 | 0.0013942 | 48 | 0.001269 | 0.001269
NWA2 | Pleasant Av | Urban | 1671 | 2.4534 | 3.3665 | 220.67 |  |  | 75 | 0.88092 | 0.88092 | 0.055951 | 0.055951 | 75 | 0.014606 | 0.014606
NWB2 | Bourke St | Urban | 1633 | 1.8859 | 1.8148 | 168.47 | [7 empty] | 1 | 5.3622e-05 | 5.3622e-05
NWD2 | Virginia St & Cap Bank 2 | Urban | 1526 | 1.9181 | 1.0963 | 254.85 |  |  | 54 | 2.3041 | 2.3041 | 0.084314 | 0.084314 | 54 | 0.011431 | 0.011431
NWE2 | Montague St | Urban | 462 | 3.1155 | 0.29518 | 84.6 |  |  | 3 | 0.00041222 | 0.00041222 | 3.3514e-06 | 3.3514e-06 | 3 | 0.00012177 | 0.00012177
NWF2 | Exeter Av No 2 | Urban | 1398 | 4.4519 | 2.4485 | 174.76 |  |  | 45 | 1.5665 | 1.5665 | 0.047154 | 0.047154 | 45 | 0.0024934 | 0.0024934
OA1207 | John St | Rural Short | 858 | 36.1551 | 0.03089 |  |  |  | 18 | 0.030719 | 0.030719 | 0.00032173 | 0.00032173 | 18 | 0.00079427 | 0.00079427
OA1233 | Werriberri St | Rural Short | 619 | 58.5083 | 0.27991 |  |  |  | 4 | 0.0012422 | 0.0012422 | 1.7874e-05 | 1.7874e-05 | 4 | 0.00011618 | 0.00011618
OA1244 | Quarry Rd | Rural Short | 356 | 23.9093 | 0.60817 | [8 empty] | 1 | 1.564e-05 | 1.564e-05
P608 | Dietz Ln | Rural Short | 153 | 26.5964 |  | 187.97 |  |  | 8670 | 113.944 | 113.944 | 1.8636 | 1.8636 | 8670 | 0.16142 | 0.16142
PCA2 | Wentworth St East | Urban | 67 | 5.1171 | 2.5727 | 90.69 |  |  | 9 | 0.0149 | 0.0149 | 0.0002346 | 0.0002346 | 9 | 1.0054e-05 | 1.0054e-05
PCB2 | Horne St | Urban | 1133 | 7.6152 | 1.535 | 161.31 |  |  | 392 | 29.0272 | 29.0272 | 0.16591 | 0.16591 | 392 | 0.02091 | 0.02091
PCC2 | SHELLHARBOUR RD & CAPACITOR BANK 1 | Urban | 42 | 0.27902 | 3.6092 | 165.11 |  |  | 4 | 0.532 | 0.532 | 0.0036329 | 0.0036329
PCD2 | Darcy Rd | Urban | 575 | 3.8191 | 1.0623 | 90.89 |  |  | 50 | 0.43873 | 0.43873 | 0.0041669 | 0.0041669 | 50 | 0.0024297 | 0.0024297
PCE2 | Horne St | Urban | 983 | 4.2924 | 0.6953 | 163.57 |  |  | 16 | 0.024934 | 0.024934 | 0.00025023 | 0.00025023 | 16 | 0.0029358 | 0.0029358
PCF2 | Wentworth Rd West | Urban | 673 | 2.2977 | 1.4478 | 179.24 |  |  | 4 | 0.04178 | 0.04178 | 0.0001564 | 0.0001564 | 4 | 4.4685e-06 | 4.4685e-06
PKA2 | Bruce Road | Urban | 1145 | 8.4359 | 0.73261 | 224.88 |  |  | 32 | 0.268 | 0.268 | 0.0023415 | 0.0023415 | 32 | 0.0021315 | 0.0021315
PKB2 | Wentworth Road | Urban | 1 | 0.22584 | 0.22745 | 2.3 |  |  | 1 | 0.00010054 | 0.00010054 | 1.1171e-06 | 1.1171e-06 | 1 | 1.1171e-06 | 1.1171e-06
PKC2 | Flagstaff Road | Urban | 857 | 8.1502 | 2.9509 | 130.84 |  |  | 180 | 7.4989 | 7.4989 | 0.097089 | 0.097089 | 180 | 0.026181 | 0.026181
PKD2 | Flagstaff Road | Urban | 1866 | 10.4373 | 3.5556 | 241.8 |  |  | 28 | 0.085455 | 0.085455 | 0.00095402 | 0.00095402 | 28 | 0.0018946 | 0.0018946
PKE2 | Oxlade Street | Urban | 1606 | 7.5707 | 0.589 | 176.69 |  |  | 75 | 9.0833 | 9.0833 | 0.059034 | 0.059034 | 75 | 0.005809 | 0.005809
PKF2 | Bruce Road | Urban | 1324 | 10.7678 | 1.1876 | 198.22 |  |  | 160 | 2.9499 | 2.9499 | 0.075562 | 0.075562 | 160 | 0.0087582 | 0.0087582
R208 | Hill St | Rural Short | 1056 | 10.2035 | 0.39633 | 100.45 |  |  | 49 | 3.3379 | 3.3379 | 0.030951 | 0.030951 | 49 | 0.00032843 | 0.00032843
R210 | Banksia Rd | Rural Short | 1160 | 17.3543 | 2.324 | 152.19 |  |  | 12 | 1.6488 | 1.6488 | 0.01553 | 0.01553 | 12 | 0.0011886 | 0.0011886
R211 | Waratah Rd | Rural Short | 1322 | 17.7698 | 0.7829 | 137.02 |  |  | 392 | 18.3279 | 18.3279 | 0.20091 | 0.20091 | 392 | 0.0054739 | 0.0054739
R212 | Glenlee | Urban | [6 empty] | 4 | 0.37854 | 0.37854 | 0.0018209 | 0.0018209
R212 |  | Urban |  |  |  | 148.63 |  |  | 4 | 0.37854 | 0.37854 | 0.0018209 | 0.0018209
R214 | Macarthur Rd | Urban | 1869 | 12.9424 | 9.7898 | 364.4 |  |  | 288 | 2.0525 | 2.0525 | 0.10193 | 0.10193 | 288 | 0.0070379 | 0.0070379
R215 | Catherine Fields | Urban | 642 | 6.8655 | 4.0017 | 296.74 |  |  | 880 | 15.8161 | 17.2939 | 0.26936 | 0.26936 | 880 | 0.039568 | 0.039568
R216 | Kirkham Ln + Aux No 1 | Rural Short | [6 empty] | 27 | 0.20443 | 0.20443 | 0.011783 | 0.011783 | 27 | 0.00066357 | 0.00066357
R216 |  | Rural Short |  |  |  | 347.37 |  |  | 27 | 0.20443 | 0.20443 | 0.011783 | 0.011783 | 27 | 0.00066357 | 0.00066357
R218 | Druitts Ln | Rural Short | [6 empty] | 1694 | 62.958 | 62.958 | 0.45263 | 0.45263 | 1694 | 0.0319 | 0.0319
R218 |  | Rural Short |  |  |  | 268.23 |  |  | 1694 | 62.958 | 62.958 | 0.45263 | 0.45263 | 1694 | 0.0319 | 0.0319
R245 |  | Urban | [11 empty] | 1 | 1.2288e-05 | 1.2288e-05
R247 | Old Bathurst Rd | Urban | 1059 | 5.2788 | 2.1152 | 191.12 |  |  | 2 | 0.0030095 | 0.0030095 | 6.0324e-05 | 6.0324e-05 | 2 | 0.00014299 | 0.00014299
R248 | Wilson Way | Urban | 1013 | 9.2544 | 1.2234 | 126.21 |  |  | 48 | 0.35094 | 0.35094 | 0.0013405 | 0.0013405 | 48 | 0.0011618 | 0.0011618
R250 | Murphy St | Urban | 1226 | 8.8918 | 0.9216 | 224.9 |  |  | 108 | 3.7528 | 3.7528 | 0.038025 | 0.038025 | 108 | 0.0043031 | 0.0043031
R251 | Glenbrook Rd + Aux No 3 | Urban | 325 | 1.9752 | 1.4452 | 190.9 |  |  | 540 | 5.6604 | 5.6604 | 0.13422 | 0.13422 | 540 | 0.023285 | 0.023285
R253 | Reserve Av + Aux No 2 | Urban | 1062 | 6.8818 | 0.79036 | 259.14 |  |  | 36 | 0.049225 | 0.049225 | 0.0011261 | 0.0011261 | 36 | 0.005179 | 0.005179
R254 | Short St | Urban | 1092 | 9.8411 | 2.2489 | 224.63 |  |  | 12 | 0.15966 | 0.15966 | 0.000744 | 0.000744 | 12 | 0.00067474 | 0.00067474
R256 | Hersey St | Urban | 1278 | 9.1565 | 1.0839 | 268.75 |  |  | 363 | 9.0888 | 9.0888 | 0.075205 | 0.075205 | 363 | 0.027034 | 0.027034
R257 | SPARE | Urban | 610 | 5.258 | 1.9371 |  |  |  | 9 | 0.034452 | 0.034452 | 0.00025135 | 0.00025135 | 9 | 0.0002413 | 0.0002413
R260 | Clarenc | Rural Short | 285 | 74.2401 | 0.3202 | 36.99 |  |  | 8192 | 225.51 | 225.51 | 0.97577 | 0.97577 | 8192 | 0.29113 | 0.29113
R290 | Upper Bylong Rd | Rural Short |  | 36.1507 |  |  |  |  | 147 | 0.063153 | 0.063153 | 0.0030263 | 0.0030263 | 147 | 0.0020801 | 0.0020801
R293 | Bylong South | Rural Short |  | 85.0851 |  |  |  |  | 2304 | 9.8755 | 9.8755 | 0.085741 | 0.085741 | 2304 | 0.0062916 | 0.0062916
RBA2 | Burrawang | Rural Short | 461 | 66.6011 | 1.8918 | 64.08 |  |  | 2016 | 22.0004 | 23.7825 | 0.11617 | 0.11617 | 2016 | 0.02177 | 0.02177
RBB2 | Jamberoo | Rural Short | 326 | 63.0208 | 1.032 | 85.3 |  |  | 3036 | 21.5019 | 22.3351 | 0.14692 | 0.14692 | 3036 | 0.057092 | 0.057092
RBC2 | Robertson | Rural Short | 473 | 37.1435 |  | 57.27 |  |  | 168 | 4.5221 | 5.1522 | 0.018455 | 0.018455 | 168 | 0.0030967 | 0.0030967
RBD2 | Myra Vale | Rural Short | 198 | 39.4564 |  | 43.33 |  |  | 135 | 0.50959 | 0.07631 | 0.00042227 | 0.00042227 | 135 | 0.0008546 | 0.0008546
RBE2 | East Kangaloon | Rural Short | 338 | 25.0685 | 1.7154 | 49.15 |  |  | 36 | 0.018593 | 0.018593 | 0.0045847 | 0.0045847 | 36 | 0.00047254 | 0.00047254
RS1203 | Martha St | Urban | 628 | 4.1028 | 2.4685 | 200.57 |  |  | 125 | 1.2657 | 1.2657 | 0.01955 | 0.01955 | 125 | 0.0012288 | 0.0012288
RS1207 | Main Roads | Urban | 1268 | 2.6602 | 2.7083 | 169.12 |  |  | 9 | 0.021214 | 0.021214 | 0.00016087 | 0.00016087
RS1236 |  | Urban | 46 |  |  | 36.99 | [7 empty] | 1 | 3.6865e-05 | 3.6865e-05
RS1262 | James Ruse Dr | Urban | 721 | 1.6707 | 3.2228 | 212.96 | [7 empty] | 1 | 1.1171e-06 | 1.1171e-06
RS1270 | Grand Av | Urban | 112 | 2.1783 | 1.296 | 58.04 | [7 empty] | 3 | 8.937e-06 | 8.937e-06
RS1296 | Wunderlich | Urban | 11 | 1.0196 | 1.2167 | 125.23 |  |  | 1 | 0.00032843 | 0.00032843 | 1.1171e-06 | 1.1171e-06
RV1280 | Collaery Rd | Urban | 1150 | 5.2551 | 2.1581 | 156.21 |  |  | 8 | 0.14598 | 0.14598 | 0.0008222 | 0.0008222 | 8 | 0.00080879 | 0.00080879
RVC2 | Doris Ave | Urban | 3050 | 13.9704 | 3.1505 | 214.42 |  |  | 972 | 34.1383 | 34.1383 | 1.1657 | 1.1657 | 972 | 0.11519 | 0.11519
RVD2 | Princes Highway North + Aux No.2 | Urban | 2007 | 6.6859 | 5.1433 | 209.25 |  |  | 64 | 4.8081 | 4.8081 | 0.07718 | 0.07718 | 64 | 0.0014299 | 0.0014299
RVF2 | Princes Highway South | Urban | 2534 | 11.7167 | 2.9313 | 282.83 |  |  | 294 | 10.9435 | 10.9435 | 0.24299 | 0.24299 | 294 | 0.014451 | 0.014451
RW1218 | Ellsmore Rd | Urban | 500 | 132.4075 | 0.29215 |  |  |  | 1 | 0.23501 | 0.23501 | 0.00056415 | 0.00056415 | 1 | 3.3514e-06 | 3.3514e-06
RW1255 | Penrose | Urban | 210 | 57.9774 | 0.72288 |  |  |  | 3 | 0.081565 | 0.081565 | 0.00016087 | 0.00016087 | 3 | 5.4739e-05 | 5.4739e-05
RW1281 | Exeter | Urban |  | 139.4727 | 0.2536 |  |  |  | 32 | 0.068484 | 0.068484 | 0.00036642 | 0.00036642 | 32 | 0.00064346 | 0.00064346
RW1292 | Bundanoon | Urban | 1496 | 47.252 | 3.3408 |  |  |  | 49 | 3.1346 | 3.1346 | 0.027002 | 0.027002 | 49 | 0.01259 | 0.01259
RWA2 |  | Rural Short | [6 empty] | 1960 | 0.88755 | 0.88755 | 0.0070379 | 0.0070379 | 1960 | 0.030435 | 0.030435
RWB2 |  | Rural Short | [6 empty] | 1800 | 1.7534 | 1.7534 | 0.019505 | 0.019505 | 1800 | 0.049153 | 0.049153
RWC2 |  | Rural Short | [6 empty] | 588 | 0.54013 | 0.54013 | 0.013513 | 0.013513 | 588 | 0.0026275 | 0.0026275
RWD2 |  | Rural Short | [6 empty] | 8464 | 71.0685 | 71.0685 | 0.6668 | 0.6668 | 8464 | 0.17551 | 0.17551
RWE2 |  | Rural Short | [6 empty] | 5200 | 12.454 | 12.454 | 0.090911 | 0.090911 | 5200 | 0.098307 | 0.098307
S326 | Chapman Av | Urban | [11 empty] | 6 | 0.00011841 | 0.00011841
S328 | Gladstone Rd | Urban | 318 | 0.6716 | 1.3119 | 168.24 |  |  | 1 | 0.00026141 | 0.00026141 | 2.2342e-06 | 2.2342e-06 | 1 | 7.9316e-05 | 7.9316e-05
S334 | Carrington Rd | Urban | 53 | 0.84707 | 0.8263 | 133.54 |  |  | 8 | 0.036713 | 0.036713 | 0.00037982 | 0.00037982 | 8 | 4.9153e-05 | 4.9153e-05
S335 | Ashford Rd | Urban | [11 empty] | 1 | 1.2288e-05 | 1.2288e-05
S590 | Patterson St | Urban | 482 | 2.6438 | 1.9659 | 223.88 |  |  | 12 | 0.049178 | 0.049178 | 0.00021449 | 0.00021449 | 12 | 0.00088476 | 0.00088476
S591 | Betty Cuthbert Av | Urban | 799 | 0.89725 | 3.0562 | 232.38 |  |  | 27 | 0.2239 | 0.2239 | 0.0015081 | 0.0015081 | 27 | 0.00014076 | 0.00014076
S594 | Alma St + Aux No 1 | Urban | 1500 | 3.9033 | 1.7398 | 207.44 |  |  | 36 | 2.2561 | 2.2561 | 0.021663 | 0.021663 | 36 | 0.0049969 | 0.0049969
S595 | Associated Products | Urban | 103 |  | 2.518 | 127.47 | [7 empty] | 1 | 3.3514e-06 | 3.3514e-06
S596 | Wang & Cap Bank 3 | Urban | 204 | 0.17799 | 5.3295 | 272.02 |  |  | 9 | 0.025604 | 0.025604 | 0.00018432 | 0.00018432
S597 | AWA | Urban | 46 |  | 1.454 | 88.59 | [7 empty] | 2 | 0.00017874 | 0.00017874
S598 | Calder Rd | Urban | 916 | 2.3433 | 1.9738 | 171.45 |  |  | 7 | 0.048999 | 0.048999 | 0.00104 | 0.00104 | 7 | 5.027e-05 | 5.027e-05
S599 | Kirby Rd | Urban | 805 | 3.2027 | 3.7518 | 191.56 |  |  | 90 | 0.5446 | 0.5446 | 0.003787 | 0.003787 | 90 | 0.0041825 | 0.0041825
S602 | Hope St | Urban | 136 | 1.8244 | 3.8033 | 179.71 | [7 empty] | 3 | 8.4901e-05 | 8.4901e-05
S604 | Rheem | Urban | 48 |  | 2.8731 | 187.9 | [7 empty] | 2 | 9.3838e-05 | 9.3838e-05
S606 | Pike St & Cap Bank 2 | Urban | 83 |  | 3.4655 | 107.03 |  |  | 1 | 0.0030207 | 0.0030207 | 1.4523e-05 | 1.4523e-05
S674 | Park Rd & Seamist Ave | Urban | 1944 | 5.9422 | 3.3406 | 264.75 |  |  | 539 | 9.9068 | 9.9068 | 0.051783 | 0.051783 | 539 | 0.017681 | 0.017681
S735 | Pitt Town Rd | Rural Short | 335 | 9.9198 | 0.48226 | 90.9 |  |  | 6 | 0.046678 | 0.046678 | 0.0053957 | 0.0053957 | 6 | 5.809e-05 | 5.809e-05
S737 | Roughley Rd | Rural Short | 788 | 32.0423 | 0.58023 | 229.82 |  |  | 475 | 1.3637 | 1.3637 | 0.098379 | 0.098379 | 475 | 0.016198 | 0.016198
S738 | Old Northern Rd + Aux No 3 | Rural Short | 965 | 34.8045 | 0.42495 | 283.84 |  |  | 780 | 24.9135 | 27.7344 | 0.28353 | 0.28353 | 780 | 0.014595 | 0.014595
S740 | Kenthurst Rd + Aux No 2 | Rural Short | 439 | 8.6596 | 1.8776 | 28.99 |  |  | 49 | 0.55699 | 0.55699 | 0.012684 | 0.012684
S741 | Emperor Rd | Rural Short | 700 | 25.9748 | 2.1026 | 208.52 |  |  | 64 | 1.0677 | 1.0677 | 0.015666 | 0.015666
S743 | Glenorie | Rural Short | 838 | 41.5378 | 1.5185 | 341.46 |  |  | 2940 | 104.1368 | 111.0665 | 0.57875 | 0.57875 | 2940 | 0.045511 | 0.045511
S744 | Round Corner | Urban | 699 | 6.6975 | 3.5306 | 223.11 |  |  | 27 | 0.067433 | 0.067433 | 0.0059922 | 0.0059922 | 27 | 0.00017092 | 0.00017092
S764 | Homestead Rd | Rural Short | 625 | 20.519 | 4.0968 | 234.5 |  |  | 72 | 2.0714 | 2.0714 | 0.017534 | 0.017534 | 72 | 0.0019304 | 0.0019304
S765 | Acacia Av | Urban | 1046 | 7.1102 | 8.3411 | 252.75 |  |  | 48 | 0.11396 | 0.11396 | 0.0013003 | 0.0013003 | 48 | 0.00032173 | 0.00032173
S766 | Luttrell St | Urban | 995 |  | 5.524 | 259.85 |  |  | 3 | 0.0022655 | 0.0022655 | 5.6973e-05 | 5.6973e-05 | 3 | 4.8036e-05 | 4.8036e-05
S768 | Glengarry + Capacitor Bank No.3 | Urban | 641 |  | 8.0882 | 283.62 |  |  | 2 | 0.00046025 | 0.00046025 | 2.2342e-06 | 2.2342e-06 | 2 | 4.1333e-05 | 4.1333e-05
S772 | Monarch Cct | Urban | 741 |  | 10.2192 | 201.37 | [7 empty] | 1 | 1.8991e-05 | 1.8991e-05
S774 | Garswood Rd | Urban | 946 |  | 5.0581 | 211.61 |  |  | 1 | 0.0022052 | 0.0022052 | 2.346e-05 | 2.346e-05
S775 | Oriole St | Urban | 600 |  | 2.2027 | 130.47 |  |  | 4 | 0.078634 | 0.078634 | 0.00027034 | 0.00027034
S776 | Glenmore Park Dr | Urban | 1008 | 0.83466 | 7.961 | 269.43 |  |  | 80 | 0.31031 | 0.31031 | 0.0010724 | 0.0010724 | 80 | 0.0023415 | 0.0023415
S785 | Oxford St | Urban | 1160 | 5.522 | 2.9696 | 393.6 |  |  | 16 | 0.14807 | 0.14807 | 0.011091 | 0.011091 | 16 | 0.00088476 | 0.00088476
S786 | Castlereagh Rd | Rural Short | 569 | 32.8545 | 2.3692 | 209.14 |  |  | 150 | 0.81787 | 0.81787 | 0.019438 | 0.019438 | 150 | 0.00097748 | 0.00097748
S788 | Crane Enfield | Rural Short | 817 | 13.7822 | 8.4192 | 213.32 |  |  | 1089 | 29.1256 | 29.1256 | 0.27394 | 0.27394 | 1089 | 0.038254 | 0.038254
S790 | Cranebrook | Rural Short | [6 empty] | 32 | 0.24231 | 0.24231 | 0.012842 | 0.012842 | 32 | 8.937e-05 | 8.937e-05
SC1204 | Tallawong Rd | Urban | 710 | 15.7316 | 2.6912 |  |  |  | 4 | 0.15854 | 0.15452 | 0.0030833 | 0.0030833 | 4 | 4.4685e-05 | 4.4685e-05
SC1238 | Carnarvon Rd | Urban | 1415 | 9.4479 | 0.72387 |  |  |  | 50 | 0.079572 | 0.079572 | 0.00064793 | 0.00064793 | 50 | 0.00047478 | 0.00047478
SC1241 | Alex Ave | Urban | 1129 | 4.885 | 10.3352 |  |  |  | 18 | 0.92271 | 0.92271 | 0.010557 | 0.010557 | 18 | 0.0035692 | 0.0035692
SC1271 | Advance St | Urban | 643 | 7.0252 | 0.61629 |  |  |  | 1 | 0.00043568 | 0.00043568 | 8.937e-06 | 8.937e-06
SC1289 | Hambledon Rd | Urban | 1375 | 4.5957 | 7.7393 |  |  |  | 32 | 0.46473 | 0.46473 | 0.0015461 | 0.0015461 | 32 | 0.00030386 | 0.00030386
SHA2 | Baragot Rd & Cap Bank 1 | Urban | 1563 |  | 9.3528 | 313.01 |  |  | 16 | 0.61746 | 0.61746 | 0.014549 | 0.014549
SHB2 | Strata Av | Urban | 1102 | 5.8865 | 4.5849 | 215.98 |  |  | 48 | 3.67 | 3.67 | 0.066665 | 0.066665 | 48 | 0.0047723 | 0.0047723
SHC2 | Shellcove | Urban | 1137 | 1.8238 | 8.3113 | 128.05 |  |  | 18 | 0.6831 | 0.6831 | 0.0174 | 0.0174 | 18 | 0.00039211 | 0.00039211
SHD2 | Tongarra Rd East | Urban | 1179 | 5.1973 | 2.933 | 149.42 |  |  | 256 | 2.066 | 2.066 | 0.063202 | 0.063202 | 256 | 0.026382 | 0.026382
SHE2 | Tongarra Rd West | Urban | 1530 | 7.8041 | 2.8174 | 196.01 |  |  | 96 | 1.114 | 1.114 | 0.059306 | 0.059306 | 96 | 0.0070959 | 0.0070959
SHF2 | Wattle Rd | Urban | 206 |  | 3.2105 | 176.42 |  |  | 1 | 0.003615 | 0.003615 | 0.00030162 | 0.00030162
SHG2 | Flinders | Urban | 414 |  | 4.2031 | 39.3 |  |  | 12 | 0.057744 | 0.057744 | 0.0037937 | 0.0037937 | 12 | 0.00048706 | 0.00048706
SHH2 | Burrinjuck Av | Urban | 261 | 5.4441 | 5.7822 | 135.28 |  |  | 180 | 2.8765 | 2.8765 | 0.0309 | 0.0309 | 180 | 0.0028956 | 0.0028956
SHJ2 | Jindabyne | Rural Short | 1300 | 16.5882 | 10.2971 | 122.57 |  |  | 360 | 1.3196 | 1.2284 | 0.081326 | 0.081326 | 360 | 0.011864 | 0.011864
SHK2 | Addison St | Urban | 1192 | 8.1882 | 2.4499 | 175.38 |  |  | 128 | 13.1683 | 13.1683 | 0.17981 | 0.17981 | 128 | 0.014496 | 0.014496
SN1208 | Flinders Estate No1 | Urban | 326 | 9.6088 | 2.1051 | 167.93 |  |  | 9 | 0.004826 | 0.004826 | 0.0021851 | 0.0021851 | 9 | 0.00019103 | 0.00019103
SN1219 | Albatross No1 | Urban | 41 | 8.2393 | 0.59987 | 227.63 |  |  | 4 | 0.00036642 | 0.00036642 | 0.00018321 | 0.00018321 | 4 | 4.4685e-06 | 4.4685e-06
SN1230 | Falls Creek | Rural Short | 365 | 46.8009 | 0.08471 | 76.55 |  |  | 676 | 2.3563 | 2.3563 | 0.098521 | 0.098521 | 676 | 0.016236 | 0.016236
SN1252 | Flinders Estate No2 | Urban | 68 | 5.6687 | 3.6838 | 81.61 |  |  | 9 | 0.00098865 | 0.00098865 | 0.00045914 | 0.00045914
SN1271 | South Nowra | Urban | 600 | 10.1262 | 2.432 | 111.78 |  |  | 60 | 3.403 | 0.10461 | 0.02766 | 0.02766 | 60 | 0.0023728 | 0.0023728
SN1282 | Albatross No2 | Rural Short | 28 | 7.2378 | 0.12245 | 54.87 |  |  | 9 | 0.049392 | 0.049392 | 0.00028487 | 0.00028487
SWC2 | Auburn St | Urban | 1798 | 7.1471 | 1.1928 | 196.91 |  |  | 684 | 46.5701 | 46.5701 | 0.28425 | 0.28425 | 684 | 0.13356 | 0.13356
SWD2 | Keira Street South | Urban | 285 | 2.4443 | 2.396 | 175.78 |  |  | 36 | 1.4738 | 1.4738 | 0.011844 | 0.011844 | 36 | 0.0017472 | 0.0017472
SWE2 | Corrimal Street | Urban | 1269 | 2.1453 | 2.3573 | 224.76 |  |  | 27 | 0.12328 | 0.12328 | 0.0037703 | 0.0037703 | 27 | 0.00049265 | 0.00049265
SWF2 | Kenny Street | Urban | 58 | 0.75935 | 0.05877 | 7.35 | [7 empty] | 1 | 3.3514e-06 | 3.3514e-06
SWG2 | Church Street & Capacitor Bank 3 | Urban | 220 | 0.83712 | 0.66922 | 284.19 |  |  | 1 | 0.014399 | 0.014399 | 9.7189e-05 | 9.7189e-05 | 1 | 4.4685e-06 | 4.4685e-06
SWH2 | Swan Street West | Urban | 985 | 3.9611 | 0.96817 | 171.78 | [7 empty] | 1 | 6.0324e-05 | 6.0324e-05
SWJ2 | Swan Street East | Urban | 704 | 2.449 | 2.3095 | 197.48 | [7 empty] | 2 | 1.3405e-05 | 1.3405e-05
SXA2 | Sussex North | Urban | 1293 | 6.7287 | 1.4808 | 122.83 |  |  | 50 | 0.95844 | 0.95844 | 0.015606 | 0.015606 | 50 | 0.0026532 | 0.0026532
SXB2 | Sussex South | Rural Short | 989 | 10.4779 | 0.34762 | 96.7 |  |  | 81 | 2.1795 | 2.1795 | 0.033601 | 0.033601
SXC2 | Wandandian | Rural Short | 409 | 43.306 | 0.59477 | 44.53 |  |  | 500 | 2.7845 | 2.7845 | 0.050941 | 0.050941 | 500 | 0.01631 | 0.01631
SXD2 | Berrara | Rural Short | 774 | 16.1446 | 0.19982 | 75.71 |  |  | 192 | 3.0531 | 3.0531 | 0.034559 | 0.034559 | 192 | 0.011654 | 0.011654
SZ1132 | Groves Ave | Rural Short | 338 | 7.4611 | 1.4339 |  |  |  | 25 | 0.98424 | 0.98424 | 0.0058481 | 0.0058481
SZ1142 | Walker St | Rural Short | 218 | 0.90739 | 1.2931 |  |  |  | 4 | 0.0091157 | 0.0091157 | 0.00054515 | 0.00054515
SZ1152 | Mileham St | Urban | 780 | 4.8978 | 0.53948 |  |  |  | 1 | 0.0018041 | 0.0018041 | 2.1225e-05 | 2.1225e-05 | 1 | 6.9261e-05 | 6.9261e-05
SZ1242 | Spare (Future Fairey Rd) | Urban | 762 | 21.8394 | 8.0625 |  |  |  | 72 | 1.0916 | 1.0916 | 0.0044908 | 0.0044908 | 72 | 0.0024934 | 0.0024934
SZ1252 |  | Rural Short | [6 empty] | 1 | 0.0019002 | 0.0019002 | 1.1171e-05 | 1.1171e-05
SZ1322 | Ham St | Urban | 1149 | 27.2821 | 2.3704 |  |  |  | 4 | 0.0039412 | 0.0039412 | 4.4685e-06 | 4.4685e-06 | 4 | 0.00059319 | 0.00059319
SZ1332 | Mulgrave Rd | Rural Short | 836 | 29.265 | 4.0634 |  |  |  | 16 | 0.53064 | 0.53064 | 0.0065776 | 0.0065776 | 16 | 0.00028151 | 0.00028151
SZ1342 | Argyle St | Urban | 700 | 6.5212 | 1.5054 |  |  |  | 4 | 0.0071228 | 0.0071228 | 0.0020644 | 0.0020644
SZ1352 | Berger Rd | Urban | 1125 | 1.4843 | 5.2845 |  |  |  | 4 | 0.8908 | 0.8908 | 0.0084901 | 0.0084901 | 4 | 9.8307e-05 | 9.8307e-05
T828 | Wolgan Rd | Rural Short | 264 | 93.3038 | 4.7953 | 63.52 |  |  | 3240 | 32.0964 | 32.0964 | 0.16629 | 0.16629 | 3240 | 0.037642 | 0.037642
T829 | Mudgee Rd | Rural Short | 18 | 5.8826 | 0.0462 | 113.34 |  |  | 2 | 0.0023638 | 0.0023638 | 4.0216e-05 | 4.0216e-05 | 2 | 2.2342e-06 | 2.2342e-06
T831 | Lidsdale | Rural Short | 1029 | 67.3592 | 3.5376 | 121.31 |  |  | 3600 | 20.751 | 20.751 | 0.24592 | 0.24592 | 3600 | 0.10858 | 0.10858
T834 | Cullen Bullen | Rural Short | 122 | 29.5795 | 0.22143 | 1.8 |  |  | 162 | 0.56417 | 0.56417 | 0.0047254 | 0.0047254 | 162 | 0.0014478 | 0.0014478
T836 | Brays Ln | Rural Short | 33 | 12.0971 | 0.79572 | 48.7 |  |  | 25 | 0.0413 | 0.0413 | 0.00057532 | 0.00057532 | 25 | 8.3784e-05 | 8.3784e-05
T838 | Portland | Rural Short | 631 | 23.8178 | 0.42909 | 98.58 |  |  | 16 | 0.78417 | 0.78417 | 0.0058671 | 0.0058671
T841 | Boulder Rd + Aux No 2 | Rural Short | 386 | 20.3573 | 0.36721 | 50.61 |  |  | 50 | 0.44 | 0.44 | 0.00092721 | 0.00092721 | 50 | 0.00025135 | 0.00025135
T842 | Pipers Flat Rd Sunny Corner | Rural Short | 219 | 42.1051 | 0.17075 | 55.78 |  |  | 196 | 0.76337 | 0.76337 | 0.0012981 | 0.0012981 | 196 | 0.0017516 | 0.0017516
T851 |  | Rural Short | [11 empty] | 8 | 0.00015863 | 0.00015863
T852 |  | Rural Short | [6 empty] | 9 | 0.015587 | 0.015587 | 0.00023795 | 0.00023795 | 9 | 8.0433e-05 | 8.0433e-05
T854 |  | Urban | [6 empty] | 1 | 0.028885 | 0.028885 | 0.00074065 | 0.00074065 | 1 | 1.3405e-05 | 1.3405e-05
T865 | Octavia Dr | Urban | 826 |  | 6.3012 | 221.26 |  |  | 36 | 0.53756 | 0.53756 | 0.0059252 | 0.0059252
T866 | Othello Av | Urban | 869 |  | 7.1749 | 301.7 |  |  | 81 | 4.6485 | 4.6485 | 0.052563 | 0.052563 | 81 | 0.0018097 | 0.0018097
T868 | Appin Rd | Rural Short | 1195 | 40.4071 | 6.1643 | 196.05 |  |  | 294 | 7.7612 | 7.7612 | 0.16717 | 0.16717 | 294 | 0.0042696 | 0.0042696
T869 | Copperfield Dr | Urban | 2060 | 0.56357 | 12.6229 | 295.78 |  |  | 196 | 19.6953 | 19.6953 | 0.27326 | 0.27326 | 196 | 0.010619 | 0.010619
T870 | Cleopatra + Aux No 2 | Urban | 817 |  | 6.986 | 155.64 |  |  | 4 | 0.025455 | 0.025455 | 9.3838e-05 | 9.3838e-05
T872 | Hamlet Av + Aux No 3 | Urban | 1249 |  | 7.7297 | 181.33 |  |  | 1 | 0.0078087 | 0.0078087 | 1.4523e-05 | 1.4523e-05
T874 | Demetrius Rd | Urban | 330 |  | 2.4857 | 57.45 |  |  | 1 | 0.00025247 | 0.00025247 | 1.1171e-06 | 1.1171e-06
T876 | Anthony Dr | Urban | 862 |  | 7.5608 | 217.45 |  |  | 4 | 0.042245 | 0.042245 | 0.00020555 | 0.00020555
T882 | Beatrice St & Cap Bank 2 | Urban | 651 | 1.5653 | 3.6402 | 280.8 |  |  | 18 | 0.44763 | 0.44763 | 0.0046249 | 0.0046249 | 18 | 0.00072389 | 0.00072389
T883 | Lamb St | Urban | 1258 | 1.1308 | 7.9382 | 209.78 |  |  | 25 | 1.8915 | 1.8915 | 0.027777 | 0.027777
T884 | PGH | Urban | 269 | 3.6737 | 6.5005 | 202.9 |  |  | 125 | 0.94704 | 0.94704 | 0.026839 | 0.026839 | 125 | 0.012651 | 0.012651
T887 | Woodstock Ave | Urban | 90 | 0.86882 | 3.0146 | 133.13 |  |  | 1 | 0.0018153 | 0.0018153 | 9.9424e-05 | 9.9424e-05
T888 | Hyatts Rd & Kellogg Rd | Urban | 602 | 3.2992 | 4.3191 | 248.99 |  |  | 16 | 0.53151 | 0.53151 | 0.0057018 | 0.0057018 | 16 | 0.00056303 | 0.00056303
T889 | Alice St | Urban | 1722 | 7.0911 | 5.2619 | 299.82 |  |  | 3 | 0.012269 | 0.012269 | 0.00019103 | 0.00019103 | 3 | 0.00031056 | 0.00031056
T890 | Woodvale Cl + Aux No 2 | Urban | 1475 | 1.9383 | 6.9286 | 209.27 |  |  | 75 | 2.3213 | 2.3213 | 0.025839 | 0.025839 | 75 | 0.0014243 | 0.0014243
T892 | Glendenning Rd and Aux No 3 | Urban | 61 | 0.85568 | 2.842 | 127.44 |  |  | 1 | 0.0021136 | 0.0021136 | 6.8144e-05 | 6.8144e-05 | 1 | 1.2288e-05 | 1.2288e-05
T893 | Wolseley St | Urban | 955 | 4.4573 | 1.5555 | 179.13 |  |  | 12 | 0.226 | 0.226 | 0.0068837 | 0.0068837 | 12 | 0.00017874 | 0.00017874
T894 | Rooty Hill Nth | Urban | 1391 | 3.2464 | 7.672 | 231.98 |  |  | 4 | 0.0012154 | 0.0012154 | 4.4685e-06 | 4.4685e-06 | 4 | 6.9261e-05 | 6.9261e-05
T895 | Beverly Pl | Urban | 325 | 1.1939 | 3.9668 | 152.54 |  |  | 8 | 0.003472 | 0.003472 | 4.0216e-05 | 4.0216e-05 | 8 | 8.937e-06 | 8.937e-06
T898 | Owen St | Urban | 48 | 0.2165 | 2.2133 | 133.58 | [7 empty] | 1 | 1.1171e-05 | 1.1171e-05
T899 | Duke St | Urban | 497 | 2.2726 | 2.3925 | 177.67 | [7 empty] | 2 | 9.2721e-05 | 9.2721e-05
T900 | Plumpton Rd & Cap Bank 3 | Urban | 1121 | 4.3065 | 7.4399 | 224.49 |  |  | 1 | 0.022917 | 0.022917 | 0.0012512 | 0.0012512
TZ9653 |  | Rural Short | [6 empty] | 9 | 0.0043769 | 0.0043769 | 2.346e-05 | 2.346e-05
ULB2 | Burrill Lake | Urban | 1382 | 10.0529 | 4.138 | 157.72 |  |  | 9 | 0.51365 | 0.51365 | 0.013814 | 0.013814 | 9 | 0.0010523 | 0.0010523
ULC2 | Narrawallee | Rural Short | 2655 | 18.0937 | 9.5786 | 251.7 |  |  | 48 | 3.0263 | 3.0263 | 0.072939 | 0.072939 | 48 | 0.0023951 | 0.0023951
ULD2 | Ulladulla Town | Urban | 886 | 3.8811 | 1.0572 | 200.87 |  |  | 12 | 0.08802 | 0.08802 | 0.00076411 | 0.00076411 | 12 | 0.0017516 | 0.0017516
ULE2 | Termeil | Rural Short | 1438 | 94.5974 | 2.4528 | 90.68 |  |  | 9472 | 335.076 | 335.076 | 3.3887 | 3.3887 | 9472 | 0.38836 | 0.38836
ULF2 | Ulladulla | Urban | 1705 | 11.6499 | 1.6494 | 192.33 |  |  | 208 | 4.2971 | 4.2971 | 0.10561 | 0.10561 | 208 | 0.018231 | 0.018231
ULH2 | Mollymook | Urban | 2174 | 10.6267 | 1.3005 | 222.01 |  |  | 360 | 12.5118 | 2.9696 | 0.12266 | 0.12266 | 360 | 0.0098128 | 0.0098128
ULJ2 | Milton | Rural Short | 1028 | 83.674 | 2.9306 | 130.36 |  |  | 5130 | 31.2852 | 32.6886 | 0.4642 | 0.4642 | 5130 | 0.18491 | 0.18491
ULL2 | Bawley Point | Rural Short | 539 | 29.9599 | 4.445 | 113.08 |  |  | 504 | 18.377 | 6.4081 | 0.065472 | 0.065472 | 504 | 0.030967 | 0.030967
UNB2 | Lady Penrhyn Dr & Cap No2 | Urban | 185 | 2.7851 | 0.34827 | 261.93 |  |  | 126 | 0.12499 | 0.12499 | 0.0022052 | 0.0022052 | 126 | 0.0073897 | 0.0073897
UNC2 | Five Islands Rd | Urban | 5 | 1.931 | 0.23553 | 281.6 |  |  | 425 | 11.6751 | 11.6751 | 0.24983 | 0.24983 | 425 | 0.030693 | 0.030693
UND2 | Charcoal Cl | Urban | 40 | 0.69712 | 1.0603 | 67.75 |  |  | 4 | 0.0047478 | 0.0047478 | 2.2342e-05 | 2.2342e-05
UNE2 | Glastonbury Avnue | Urban | 86 | 2.1422 | 1.2278 | 189.82 |  |  | 11 | 0.24543 | 0.24543 | 0.0010814 | 0.0010814 | 11 | 0.0010479 | 0.0010479
UNF2 | Doyle Av | Urban | 585 | 3.1017 | 1.5692 | 233.7 |  |  | 4 | 0.30738 | 0.30738 | 0.0048662 | 0.0048662 | 4 | 4.9153e-05 | 4.9153e-05
UNG2 | Berkeley Road West | Urban | 34 | 1.0417 | 0.33709 | 211.41 |  |  | 392 | 5.4555 | 5.4555 | 0.11942 | 0.11942 | 392 | 0.028738 | 0.028738
UNH2 | Nolan St West | Urban | 398 | 4.5727 | 0.43603 | 267.78 |  |  | 12 | 0.25677 | 0.25677 | 0.0031436 | 0.0031436 | 12 | 0.00080879 | 0.00080879
UNJ2 | Berkeley Road Sth & Cap No3 | Urban | 1344 | 6.2823 | 3.6913 | 294.57 |  |  | 72 | 2.6763 | 2.6763 | 0.072094 | 0.072094 | 72 | 0.0076109 | 0.0076109
W111 | MacQuariedale Road + Aux | Rural Short | 572 | 34.5833 | 0.14146 | 149.2 |  |  | 896 | 10.0772 | 10.0772 | 0.11323 | 0.11323 | 896 | 0.037821 | 0.037821
W112 | Brooks Point Rd | Rural Short | 285 | 18.6225 | 0.066258 | 56.51 |  |  | 8 | 0.0098128 | 0.0098128 | 5.809e-05 | 5.809e-05 | 8 | 0.00019661 | 0.00019661
W113 | Inghams | Urban | 338 | 4.2156 | 0.09517 | 145.79 | [7 empty] | 6 | 0.00066469 | 0.00066469
W114 | Elladale Rd | Rural Short | 34 | 13.7174 | 0.12232 | 21.89 |  |  | 16 | 0.0015461 | 0.0015461 | 3.5748e-05 | 3.5748e-05 | 16 | 0.00016533 | 0.00016533
W118 | Falcon St | Urban | 732 | 7.1258 | 0.64702 | 73.38 |  |  | 98 | 2.3821 | 2.3821 | 0.047154 | 0.047154 | 98 | 0.0046528 | 0.0046528
W120 | Kitchener St | Urban | 1208 | 12.8321 | 3.1487 | 144.76 |  |  | 900 | 11.1544 | 11.1544 | 0.15704 | 0.15704 | 900 | 0.060324 | 0.060324
W123 | Birdwood Pde + Aux No 2 | Urban | 998 | 7.2085 | 1.1829 | 114.92 |  |  | 45 | 6.2337 | 6.2337 | 0.035491 | 0.035491 | 45 | 0.0018801 | 0.0018801
W124 | Addington Rd | Rural Short | 1093 | 18.3947 | 1.687 | 155.26 |  |  | 686 | 13.0893 | 13.0893 | 0.13564 | 0.13564 | 686 | 0.061855 | 0.061855
W126 | Winbourne Rd | Rural Short | 81 | 1.2016 | 0.14399 | 8.35 |  |  | 2 | 0.0092855 | 0.0092855 | 0.00018097 | 0.00018097 | 2 | 0.00013852 | 0.00013852
W127 | Glendarra St | Rural Short | 801 | 8.698 | 2.36 | 85.99 |  |  | 360 | 5.4781 | 5.4781 | 0.072456 | 0.072456 | 360 | 0.018057 | 0.018057
W163 | Tarana | Rural Short | 212 | 67.1875 |  | 29.28 |  |  | 19573 | 207.7079 | 207.7079 | 0.55234 | 0.55234 | 19573 | 0.12233 | 0.12233
W164 | Range Road | Rural Short | 65 | 30.6487 |  | 12.55 |  |  | 243 | 0.67527 | 0.67527 | 0.0010858 | 0.0010858 | 243 | 0.00090487 | 0.00090487
W182 | Bushs Pet Food | Urban | 5 |  | 2.2157 | 251.22 |  |  | 9 | 0.019592 | 0.019592 | 2.0108e-05 | 2.0108e-05
W184 | Williamson Rd East | Urban | 40 |  | 5.0979 | 255.7 | [7 empty] | 4 | 1.2288e-05 | 1.2288e-05
W185 | Midlothian Rd + Cap Bank No 1 | Rural Short | 1454 | 19.6173 | 14.97 | 250.98 |  |  | 72 | 4.3277 | 4.3277 | 0.029908 | 0.029908 | 72 | 0.0022119 | 0.0022119
W188 | Denham Court Rd + Aux No 1 | Rural Short | 610 | 28.4928 | 2.8565 | 233.08 |  |  | 600 | 3.512 | 3.512 | 0.072993 | 0.072993 | 600 | 0.0037982 | 0.0037982
W190 | Stennett Rd + Aux No 2 | Urban | 241 | 0.82727 | 3.2424 | 161.59 |  |  | 1 | 0.00042562 | 0.00042562 | 1.7874e-05 | 1.7874e-05
W196 | Norwich Rd | Urban | 1033 | 3.7725 | 2.3292 | 285.25 |  |  | 100 | 0.20486 | 0.20486 | 0.0022789 | 0.0022789 | 100 | 0.00027928 | 0.00027928
WBB2 | Coledale | Urban | 1000 | 7.1774 | 0.0589 | 118.74 |  |  | 784 | 4.2482 | 4.2482 | 0.04767 | 0.04767 | 784 | 0.028738 | 0.028738
WBC2 | Morrison Ave North | Rural Short | 964 | 11.1944 | 1.7094 | 131.53 |  |  | 900 | 33.4346 | 33.4346 | 0.52573 | 0.52573 | 900 | 0.051388 | 0.051388
WBD2 | Morrison Ave South | Rural Short | 847 | 8.5828 | 0.42215 | 101.36 |  |  | 1500 | 31.0445 | 31.0445 | 0.19656 | 0.19656 | 1500 | 0.078645 | 0.078645
WBE2 | Clifton | Rural Short | 40 | 5.1372 | 0.09201 | 6.78 |  |  | 9 | 0.027846 | 0.027846 | 0.00026811 | 0.00026811 | 9 | 0.00026141 | 0.00026141
WD1210 | Cornwallis Rd | Rural Short | 281 | 8.3824 | 0.85029 |  |  |  | 25 | 0.0992 | 0.0992 | 0.0021114 | 0.0021114 | 25 | 0.00027928 | 0.00027928
WD1221 | Freemans Reach Rd | Rural Short | 526 | 19.3565 | 1.1585 |  |  |  | 72 | 0.54051 | 0.54051 | 0.0073864 | 0.0073864 | 72 | 0.00032173 | 0.00032173
WD1251 | Union St | Rural Short | 584 | 12.8043 | 2.6357 |  |  |  | 48 | 1.8346 | 1.8346 | 0.021945 | 0.021945 | 48 | 0.0046651 | 0.0046651
WD1284 | Brabyn St | Rural Short | 230 | 6.3202 | 1.21 |  |  |  | 50 | 0.1711 | 0.1711 | 0.0026699 | 0.0026699 | 50 | 0.0010333 | 0.0010333
WD1288 | Macquarie St | Rural Short | 94 | 0.86957 | 0.99372 |  |  |  | 1 | 0.0054024 | 0.0054024 | 0.00010501 | 0.00010501
WH1209 | Palmerstone Rd | Urban | 1670 | 9.6383 | 1.1363 | 246.55 | [7 empty] | 13 | 0.0021259 | 0.0021259
WH1213 | Sunblest Crescent | Urban | 139 |  | 2.8538 | 74.19 |  |  | 1 | 0.0002938 | 0.0002938 | 0.0001564 | 0.0001564
WH1220 | Cap Bank 3 | Urban | 187 |  | 1.7034 | 74.64 |  |  | 4 | 0.090918 | 0.090918 | 0.00083114 | 0.00083114
WH1224 | Mt Druitt Rd | Urban | 976 | 5.8578 | 2.9656 |  |  |  | 28 | 0.71613 | 0.71613 | 0.01528 | 0.01528 | 28 | 0.0038161 | 0.0038161
WH1235 | Semana St | Urban | 1120 | 6.4507 | 1.1998 | 162.24 |  |  | 9 | 0.0020611 | 0.0020611 | 1.0054e-05 | 1.0054e-05 | 9 | 0.001631 | 0.001631
WH1257 | Hythe St | Urban | 262 |  | 3.8286 | 266.35 | [7 empty] | 3 | 3.5748e-05 | 3.5748e-05
WH1261 | Rupertswood Rd | Urban | 956 | 0.46555 | 6.1776 | 263.17 |  |  | 1 | 0.00014969 | 0.00014969 | 1.1171e-06 | 1.1171e-06 | 1 | 3.0162e-05 | 3.0162e-05
WH1272 | Shoppingtown | Urban | 76 | 0.1014 | 1.5656 | 194.43 | [7 empty] | 3 | 5.027e-05 | 5.027e-05
WH1276 | North Parade | Urban | 63 | 0.09286 | 3.5518 | 126.29 |  |  | 1 | 0.0059431 | 0.0059431 | 7.0379e-05 | 7.0379e-05
WH1294 | Wehlow St | Urban | 984 | 2.9044 | 2.4016 | 250.82 |  |  | 27 | 1.8509 | 1.8509 | 0.019776 | 0.019776 | 27 | 0.0017293 | 0.0017293
WH1298 | Beames Rd | Urban | 1631 | 6.376 | 7.4396 | 327.06 |  |  | 9 | 0.037592 | 0.037592 | 0.00092833 | 0.00092833 | 9 | 0.00032173 | 0.00032173
WL1214 | Bernera Rd | Urban | 11 | 0.66404 | 0.81885 | 15 | [7 empty] | 1 | 3.3514e-06 | 3.3514e-06
WL1217 | Heckenberg Ave | Urban | 1550 | 7.0669 | 1.5523 | 133 |  |  | 45 | 3.6054 | 1.4968 | 0.026962 | 0.026962 | 45 | 0.00016757 | 0.00016757
WL1218 | Whitford Rd | Urban | 608 |  | 3.7634 | 140 |  |  | 4 | 0.18551 | 0.18551 | 0.0014344 | 0.0014344
WL1236 | Maxwell Ave | Urban | 1914 | 8.0417 | 1.5801 | 157.5 |  |  | 175 | 0.44342 | 0.44342 | 0.005513 | 0.005513 | 175 | 0.0075406 | 0.0075406
WL1251 | Hoxton Park Rd | Urban | 848 | 3.8054 | 3.631 | 180 |  |  | 8 | 1.5891 | 0.0015014 | 6.2559e-05 | 6.2559e-05 | 8 | 0.0001631 | 0.0001631
WL1277 | Banks Rd | Urban | 760 | 1.4377 | 3.9645 | 147 |  |  | 1 | 0.00015081 | 0.00015081 | 1.1171e-06 | 1.1171e-06
WL1280 | Jedda Rd | Urban | 333 | 3.4977 | 1.9098 | 200 |  |  | 2 | 0.069726 | 0.069726 | 0.00074177 | 0.00074177 | 2 | 3.3514e-06 | 3.3514e-06
WL1292 | Miller Rd | Urban | 2101 | 10.9547 | 3.6709 | 147 |  |  | 72 | 5.2649 | 6.7375 | 0.058501 | 0.058501 | 72 | 0.00096519 | 0.00096519
WL1295 | EE Training School | Urban | 1043 |  | 5.6221 | 126 |  |  | 1 | 0.00034854 | 0.00034854 | 1.3405e-05 | 1.3405e-05 | 1 | 1.1171e-06 | 1.1171e-06
WL1296 | Cartwright Ave | Urban | 137 | 1.267 | 2.5415 | 200 | [7 empty] | 4 | 0.0003653 | 0.0003653
WL1299 | Yarrawa St | Urban | 33 | 1.1268 | 2.4583 | 35 |  |  | 4 | 0.0012713 | 0.0012713 | 4.4685e-06 | 4.4685e-06
WQ1208 | Hassall St & Verrell St | Urban | 109 | 0.81753 | 1.8176 | 88.02 |  |  | 4 | 0.0034742 | 0.0034742 | 2.0108e-05 | 2.0108e-05 | 4 | 1.7874e-05 | 1.7874e-05
WQ1212 | Elizabeth Street | Urban | 109 | 1.962 | 1.715 | 199.8 |  |  | 1 | 0.0039267 | 0.0039267 | 2.1225e-05 | 2.1225e-05
WQ1227 | Verell Street | Urban | 216 | 1.6664 | 1.011 | 220.84 |  |  | 36 | 1.8434 | 1.8434 | 0.014049 | 0.014049 | 36 | 0.00031168 | 0.00031168
WQ1249 | Victoria Street | Urban | 534 | 2.2744 | 2.8603 | 194.05 |  |  | 72 | 2.5072 | 0.16672 | 0.010718 | 0.010718 | 72 | 0.0010456 | 0.0010456
WQ1260 | Widemere Rd | Urban | 128 | 3.7047 | 1.623 | 160.05 |  |  | 12 | 0.17185 | 0.17185 | 0.00088476 | 0.00088476 | 12 | 6.2559e-05 | 6.2559e-05
WQ1264 | Hargraves Place | Urban | 256 | 2.388 | 1.1906 | 149.16 |  |  | 4 | 0.05269 | 0.05269 | 0.0008222 | 0.0008222
WQ1271 | Davis Rd & Aux No 2 | Urban | 8 | 0.56134 | 0.6857 | 72.65 | [7 empty] | 2 | 2.2342e-06 | 2.2342e-06
WQ1275 | Wenban Place | Urban | 29 | 0.68075 | 2.2343 | 212.44 |  |  | 2 | 0.00096296 | 0.00096296 | 6.4793e-05 | 6.4793e-05 | 2 | 5.5856e-06 | 5.5856e-06
WQ1286 | Redfern Street | Urban | 32 | 0.77872 | 0.6618 | 84.82 |  |  | 1 | 0.00053063 | 0.00053063 | 3.5748e-05 | 3.5748e-05 | 1 | 8.937e-06 | 8.937e-06
WQ1290 | Walter Road | Urban | 89 | 1.6604 | 1.8272 | 257.44 | [7 empty] | 1 | 4.4685e-06 | 4.4685e-06
WRA2 | Landy Dr | Urban | 1454 | 8.2321 | 2.2428 | 185.15 |  |  | 256 | 6.8455 | 6.8455 | 0.13384 | 0.13384 | 256 | 0.038822 | 0.038822
WRB2 | Woodfull St | Urban | 1318 | 5.9047 | 1.0444 | 191.21 |  |  | 192 | 2.1304 | 2.1304 | 0.089897 | 0.089897 | 192 | 0.018231 | 0.018231
WRC2 | Wall St West | Urban | 1769 | 11.2989 | 0.68119 | 215.59 |  |  | 324 | 16.73 | 16.73 | 0.25059 | 0.25059 | 324 | 0.024934 | 0.024934
WRD2 | Wall St East | Urban | 1652 | 6.7614 | 0.48434 | 209.79 |  |  | 20 | 0.29036 | 0.29036 | 0.024163 | 0.024163 | 20 | 0.0021761 | 0.0021761
WRE2 | Trumper St East | Urban | 1823 | 9.6567 | 1.5113 | 181.31 |  |  | 256 | 14.8232 | 14.8232 | 0.29885 | 0.29885 | 256 | 0.04733 | 0.04733
WRF2 | Trumper St North | Urban | 1819 | 9.9571 | 1.86 | 187.66 |  |  | 200 | 2.3968 | 2.3968 | 0.11591 | 0.11591 | 200 | 0.027649 | 0.027649
WRG2 | Shellharbour Sq No1 & No1 AF Injectn Cell | Urban | 270 |  | 3.3662 | 78.5 |  |  | 1 | 0.0047377 | 0.0047377 | 0.00039434 | 0.00039434 | 1 | 2.2342e-05 | 2.2342e-05
WWB2 | Reserve St | Urban | 1804 | 10.9128 | 1.4758 | 205.09 |  |  | 245 | 23.8305 | 23.8305 | 0.21641 | 0.21641 | 245 | 0.022936 | 0.022936
WWC2 | Gilmore St South | Urban | 522 | 2.8998 | 0.57316 | 268.42 |  |  | 3 | 0.0077215 | 0.0077215 | 0.00010724 | 0.00010724 | 3 | 8.7135e-05 | 8.7135e-05
WWD2 | Dempster St | Urban | 1341 | 3.6634 | 0.82614 | 153.67 |  |  | 3 | 0.004464 | 0.004464 | 0.00012065 | 0.00012065 | 3 | 0.00027146 | 0.00027146
WWE2 | David St | Urban | 1523 | 7.5531 | 0.58163 | 283.95 |  |  | 220 | 5.385 | 2.4827 | 0.14537 | 0.14537 | 220 | 0.028062 | 0.028062
WWF2 | Fisher St | Urban | 1084 | 5.149 | 0.13017 | 285.44 |  |  | 225 | 1.6731 | 1.6731 | 0.11783 | 0.11783 | 225 | 0.023264 | 0.023264
WX1210 | Bushells Place | Urban | 30 | 0.44567 | 4.0667 | 199.52 |  |  | 1 | 0.0014992 | 0.0014992 | 4.9153e-05 | 4.9153e-05 | 1 | 1.0054e-05 | 1.0054e-05
WX1228 | Horsley Drive (West) | Urban | 52 | 2.3411 | 2.6726 | 56.41 |  |  | 1 | 0.0017137 | 0.0017137 | 6.7027e-06 | 6.7027e-06
WX1244 | Hallstrom Place | Urban | 397 | 2.9884 | 4.2434 | 246.75 |  |  | 36 | 0.1149 | 0.1149 | 0.00035524 | 0.00035524
WX1254 | Trivet Street | Urban | 58 | 1.623 | 0.65467 | 165.74 |  |  | 1 | 0.015604 | 0.015604 | 6.4793e-05 | 6.4793e-05 | 1 | 2.2342e-05 | 2.2342e-05
WX1258 | Bentley Street | Urban | 655 | 5.0255 | 2.9058 | 195.74 |  |  | 36 | 1.6505 | 1.6505 | 0.0066625 | 0.0066625
WX1270 | Potter Close | Urban | 76 | 1.2026 | 1.7472 | 260.16 | [7 empty] | 2 | 2.2342e-06 | 2.2342e-06
WX1280 | Walker Place | Urban | 522 | 3.5765 | 5.1092 | 282.83 |  |  | 1 | 0.0015975 | 0.0015975 | 2.4577e-05 | 2.4577e-05 | 1 | 2.5694e-05 | 2.5694e-05
WX1284 | Metters Place | Urban | 109 | 0.55683 | 2.8479 | 113.77 | [7 empty] | 2 | 3.9099e-05 | 3.9099e-05
X213 | Aarons Pass | Rural Short | 77 | 56.6456 | 0.21682 |  |  |  | 1372 | 3.9172 | 3.9172 | 0.032296 | 0.032296 | 1372 | 0.0070066 | 0.0070066
X217 | Cherry Tree Hill | Rural Short | 202 | 137.0974 | 0.15621 |  |  |  | 1792 | 2.4933 | 2.4933 | 0.078699 | 0.078699 | 1792 | 0.0097234 | 0.0097234
X459 |  | Rural Short | [6 empty] | 36 | 0.41527 | 0.41527 | 0.02348 | 0.02348
X463 |  | Rural Short | [6 empty] | 16 | 0.077743 | 0.077743 | 0.0051388 | 0.0051388
X473 |  | Rural Short | [6 empty] | 2000 | 17.6742 | 17.6742 | 0.3758 | 0.3758 | 2000 | 0.010724 | 0.010724
X479 |  | Rural Short | [6 empty] | 16 | 0.04817 | 0.04817 | 0.0031145 | 0.0031145 | 16 | 1.7874e-05 | 1.7874e-05
X492 | Australian Cement Co (22kV) | Rural Long | 291 | 238.4595 | 0.34578 | 8.37 |  |  | 18144 | 119.7151 | 119.7151 | 2.2127 | 2.2127 | 18144 | 0.13754 | 0.13754
X802 | Dabee Rd (22kV) | Rural Short | 182 | 152.8368 | 0.69276 | 52.84 |  |  | 4212 | 31.6746 | 31.6746 | 0.49615 | 0.49615 | 4212 | 0.02968 | 0.02968
X858 | Taylor St | Urban | 534 |  | 6.1209 | 260.15 |  |  | 2 | 0.1888 | 0.1888 | 0.0030676 | 0.0030676 | 2 | 9.1604e-05 | 9.1604e-05
X859 | Merelynne Av | Urban | 459 |  | 3.3882 | 130.64 |  |  | 1 | 0.0032575 | 0.0032575 | 2.0108e-05 | 2.0108e-05
X863 | Oakes Rd | Urban | 594 | 4.263 | 1.8116 | 102.08 |  |  | 6 | 0.0031972 | 0.0031972 | 6.0324e-05 | 6.0324e-05 | 6 | 0.00059989 | 0.00059989
X866 | Crane Rd & Aux 2 | Urban | 837 |  | 8.3763 | 218.85 | [7 empty] | 3 | 4.1333e-05 | 4.1333e-05
X867 | Stanton Dr | Urban | 973 | 1.7278 | 5.2099 | 286.15 |  |  | 25 | 0.042948 | 0.042948 | 0.00030721 | 0.00030721
X870 | Hill Rd | Urban | 708 |  | 6.1989 | 171.02 |  |  | 4 | 0.072287 | 0.072287 | 0.00022566 | 0.00022566
X871 | Oratava Rd | Urban | 838 | 1.9929 | 5.8647 | 216.63 |  |  | 16 | 0.26715 | 0.26715 | 0.0076858 | 0.0076858 | 16 | 0.00066134 | 0.00066134
X877 | Greendale Rd | Rural Short | 1321 | 106.3245 | 2.9179 | 344.35 |  |  | 20000 | 121.6856 | 121.6856 | 2.6865 | 2.6865 | 20000 | 0.29743 | 0.29743
X879 | The Northern Rd + Aux No 1 | Rural Short | 1020 | 37.5918 | 0.81804 | 231.08 |  |  | 2160 | 48.1874 | 48.1874 | 0.62195 | 0.62195 | 2160 | 0.040538 | 0.040538
X881 | Badgerys Creek Rd + Aux No 2 | Rural Short | 470 | 25.2076 | 2.6223 | 154.22 |  |  | 196 | 0.62108 | 0.62108 | 0.015014 | 0.015014 | 196 | 0.0078277 | 0.0078277
X883 | Coates Park Rd & Cap Bank 2 | Rural Short | 81 | 7.4525 | 0.46215 | 271.88 |  |  | 1 | 0.0030095 | 0.0030095 | 1.8991e-05 | 1.8991e-05
YYA2 | North Conjola | Rural Short | 1402 | 46.1714 | 0.82685 | 100 |  |  | 480 | 21.6934 | 19.3727 | 0.2163 | 0.2163 | 480 | 0.030296 | 0.030296
YYB2 | Bendalong | Rural Short | 722 | 26.4358 | 1.4901 | 104.43 |  |  | 288 | 5.1639 | 5.1639 | 0.07188 | 0.07188 | 288 | 0.0022521 | 0.0022521
Contents

## 5c. Network data outages
Endeavour Energy
Cause of Outages
2012-13
The information in templates 5a,b,c,d is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Causes of unplanned sustained outages
Nb: formulas need to be checked.
Cause of outage | Number of outages
Weather | 988
Equipment failure | 1682
Operational error | 0
Vegetation | 353
Animals | 140
Third party impacts | 366
Transmission failure | 16
Load shedding | 0
Inter-distributor connection failure | 0
Other | 1043
Contents

## 5d. Outcomes planned outages
Endeavour Energy
Planned Outages
2012-13
The information in templates 5a,b,c,d is used to monitor network performance and service outcomes for network customers. It will inform the AER's review of service improvement expenditure in future regulatory periods.
Table 1: Planned outages
Network categorisation
Planned outages | CBD | Urban | Rural short | Rural long | Whole network
SAIDI - after removing excluded events |  | 81.1 | 190.2 | 766 | 99.6
SAIFI - after removing excluded events |  | 0.2 | 0.37 | 1.16 | 0.23
Contents

## 6. Weighted av cost of debt
Endeavour Energy
Weighted average cost of debt
2012-13
This information will be used to compare the DBs cost against the benchmark cost of debt. There is no intention to set the regulated cost of debt for a business based on its actual cost of debt.
Notes: the specific method of calculating the weighted average cost of debt for the financial year is Endeavour Energy's choice but must be fully described. If the description of the methodology cannot fit in this worksheet, Endeavour can provide details as a separate attachment.
Table 1: Cost of debt
Weighted average cost of debt (%) | 2012-13 | Explanation of calculation method
| 6.818% | The methodology for determining the weighted average cost of debt is attached in the tab "Loan Summary" which has been appended to these RIN templates.
Contents

## 7. Asset installation
Endeavour Energy
Asset Installation
2012-13
This information is used in the AER’s replacement capex model. The model is used by the AER to assess forecast replacement capex proposals. It may also be used to monitor the asset age profile of the business over time. This will be used as a tool to monitor any improvements/deterioration in the overall asset age where capex has been approved to address network asset age.
Table 1: Asset age profile for distribution system assets
Asset group/category | Replacement life (years) |  | Actual replacement volumes (number of assets replaced) | Replacement unit cost | Asset failures | Total quantity | Year commissioned (number of assets commissioned in each year)
| Mean | Standard deviation |  |  |  |  | 1910 | 1911 | 1912 | 1913 | 1914 | 1915 | 1916 | 1917 | 1918 | 1919 | 1920 | 1921 | 1922 | 1923 | 1924 | 1925 | 1926 | 1927 | 1928 | 1929 | 1930 | 1931 | 1932 | 1933 | 1934 | 1935 | 1936 | 1937 | 1938 | 1939 | 1940 | 1941 | 1942 | 1943 | 1944 | 1945 | 1946 | 1947 | 1948 | 1949 | 1950 | 1951 | 1952 | 1953 | 1954 | 1955 | 1956 | 1957 | 1958 | 1959 | 1960 | 1961 | 1962 | 1963 | 1964 | 1965 | 1966 | 1967 | 1968 | 1969 | 1970 | 1971 | 1972 | 1973 | 1974 | 1975 | 1976 | 1977 | 1978 | 1979 | 1980 | 1981 | 1982 | 1983 | 1984 | 1985 | 1986 | 1987 | 1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | Quantity of Unknown Age
Poles
Concrete 11kV | 55 | 7.4162 |  | 6657 |  | 10380 | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 22 | 4 | 4 | 4 | 0 | 0 | 0 | 0 | 4 | 7 | 11 | 18 | 0 | 0 | 4 | 4 | 7 | 18 | 0 | 11 | 264 | 1618 | 1833 | 1937 | 2048 | 217 | 7 | 96 | 59 | 0 | 7 | 374 | 419 | 246 | 190 | 211 | 184 | 208 | 128 | 118 | 90
Concrete 132kV | 55 | 7.4162 |  | 23527 |  | 2016 | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 3 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | 2 | 51 | 314 | 356 | 376 | 398 | 42 | 1 | 18 | 11 | 0 | 1 | 73 | 82 | 48 | 37 | 41 | 36 | 41 | 25 | 23 | 17
Concrete 22kV | 55 | 7.4162 |  | 8134 |  | 1476 | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 38 | 231 | 263 | 277 | 293 | 31 | 1 | 14 | 9 | 0 | 1 | 53 | 60 | 35 | 27 | 30 | 26 | 29 | 18 | 17 | 12
Concrete 33kV | 55 | 7.4162 |  | 16001 |  | 758 | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 19 | 120 | 135 | 143 | 150 | 16 | 0 | 7 | 4 | 0 | 0 | 28 | 30 | 18 | 14 | 15 | 13 | 15 | 9 | 9 | 7
Concrete 66kV | 55 | 7.4162 |  | 19125 |  | 1199 | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 3 | 0 | 0 | 0 | 0 | 1 | 3 | 0 | 1 | 31 | 187 | 211 | 223 | 237 | 25 | 1 | 11 | 7 | 0 | 1 | 43 | 49 | 28 | 22 | 24 | 22 | 24 | 15 | 14 | 11
Concrete LV | 55 | 7.4162 |  | 5120 |  | 1188 | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 30 | 186 | 211 | 224 | 237 | 25 | 0 | 10 | 6 | 0 | 0 | 43 | 48 | 28 | 22 | 24 | 22 | 24 | 15 | 13 | 10
Steel 11kV | 55 | 7.4162 |  | 6160 |  | 155 | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 11 | 14 | 37 | 12 | 49 | 3 | 5 | 0
Steel 132kV | 55 | 7.4162 |  | 21446 |  | 124 | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 40 | 73 | 0 | 1 | 0 | 0
Steel 22kV | 55 | 7.4162 |  | 7556 |  | 15 | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0
Steel 33kV | 55 | 7.4162 |  | 15231 |  | 83 | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 6 | 0 | 0 | 22 | 0 | 0 | 25 | 13
Steel LV | 55 | 7.4162 |  | 4710 |  | 855 | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 3 | 34 | 97 | 23 | 2 | 11 | 5 | 0 | 0 | 0 | 0 | 7 | 34 | 513 | 31 | 17 | 9 | 16 | 14 | 2 | 6 | 0
Wood 11kV | 55 | 7.4162 |  | 5533 |  | 201328 | [35 empty] | 8 | 13 | 18 | 25 | 76 | 126 | 183 | 252 | 350 | 473 | 636 | 851 | 1125 | 1458 | 1703 | 1924 | 2011 | 2127 | 2285 | 2361 | 2308 | 2166 | 1965 | 1751 | 1532 | 1328 | 1259 | 1420 | 1579 | 1862 | 2204 | 2576 | 2967 | 3543 | 3955 | 4634 | 4869 | 4663 | 4745 | 4904 | 5067 | 6030 | 6273 | 5869 | 4182 | 4264 | 6030 | 5146 | 6273 | 5869 | 6030 | 6393 | 6191 | 5106 | 4904 | 5067 | 4663 | 3297 | 3094 | 4585 | 2816 | 3359 | 3712 | 3250 | 3676 | 2258 | 2102 | 1587
Wood 132kV | 55 | 7.4162 |  | 18893 |  | 3047 | [35 empty] | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 4 | 5 | 7 | 11 | 13 | 17 | 22 | 25 | 29 | 31 | 32 | 35 | 36 | 36 | 33 | 29 | 27 | 24 | 21 | 18 | 21 | 24 | 28 | 33 | 39 | 46 | 53 | 60 | 70 | 74 | 71 | 71 | 75 | 77 | 91 | 95 | 89 | 63 | 64 | 91 | 77 | 95 | 89 | 91 | 97 | 94 | 77 | 75 | 77 | 71 | 50 | 46 | 69 | 42 | 50 | 56 | 50 | 56 | 34 | 31 | 25
Wood 22kV | 55 | 7.4162 |  | 6731 |  | 7082 | [35 empty] | 0 | 0 | 0 | 0 | 2 | 3 | 7 | 9 | 12 | 16 | 22 | 29 | 39 | 51 | 60 | 67 | 71 | 76 | 80 | 83 | 81 | 76 | 69 | 61 | 54 | 48 | 44 | 50 | 56 | 66 | 77 | 91 | 105 | 125 | 139 | 163 | 171 | 165 | 167 | 172 | 178 | 213 | 221 | 206 | 147 | 150 | 213 | 181 | 221 | 206 | 213 | 225 | 218 | 180 | 172 | 178 | 165 | 117 | 109 | 162 | 99 | 118 | 130 | 115 | 129 | 79 | 74 | 56
Wood 33kV | 55 | 7.4162 |  | 12695 |  | 15865 | [35 empty] | 0 | 0 | 1 | 1 | 5 | 10 | 14 | 20 | 27 | 37 | 50 | 67 | 89 | 114 | 135 | 151 | 159 | 167 | 180 | 186 | 182 | 171 | 155 | 137 | 122 | 105 | 98 | 112 | 124 | 146 | 174 | 204 | 234 | 279 | 312 | 366 | 385 | 368 | 374 | 386 | 400 | 475 | 495 | 463 | 329 | 336 | 475 | 405 | 495 | 463 | 475 | 503 | 488 | 403 | 386 | 400 | 368 | 259 | 244 | 361 | 222 | 264 | 292 | 257 | 290 | 178 | 167 | 125
Wood 66kV | 55 | 7.4162 |  | 15796 |  | 3894 | [35 empty] | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 5 | 8 | 9 | 13 | 16 | 22 | 29 | 33 | 38 | 39 | 41 | 44 | 46 | 44 | 42 | 38 | 34 | 30 | 26 | 25 | 27 | 30 | 36 | 42 | 50 | 56 | 69 | 77 | 91 | 94 | 91 | 92 | 94 | 98 | 117 | 121 | 113 | 81 | 83 | 117 | 99 | 121 | 113 | 117 | 124 | 120 | 99 | 94 | 98 | 91 | 64 | 60 | 89 | 55 | 65 | 71 | 63 | 70 | 44 | 40 | 30
Wood LV | 55 | 7.4162 |  | 4073 |  | 55970 | [35 empty] | 1 | 3 | 5 | 7 | 20 | 35 | 50 | 70 | 98 | 131 | 177 | 236 | 313 | 406 | 475 | 534 | 560 | 592 | 636 | 655 | 643 | 602 | 547 | 487 | 427 | 369 | 351 | 394 | 439 | 517 | 613 | 717 | 823 | 985 | 1101 | 1289 | 1353 | 1297 | 1318 | 1363 | 1409 | 1676 | 1744 | 1630 | 1162 | 1185 | 1676 | 1431 | 1744 | 1630 | 1676 | 1776 | 1721 | 1422 | 1363 | 1409 | 1297 | 917 | 861 | 1276 | 784 | 933 | 1032 | 903 | 1022 | 628 | 584 | 440
Pole top structures
<asset type 1> |  |  |  | 0 |  | 0
<asset type 2> |  |  |  | 0 |  | 0
<asset type 3> |  |  |  | 0 |  | 0
Conductors
11/22kV | 50 | 7.0711 |  | 20700 |  | 10846 | Year commissioned (number of assets commissioned in each year) 1964: 112.6239; Year commissioned (number of assets commissioned in each year) 1965: 0; Year commissioned (number of assets commissioned in each year) 1966: 311.6073; Year commissioned (number of assets commissioned in each year) 1967: 161.7961; Year commissioned (number of assets commissioned in each year) 1968: 341.5696; Year commissioned (number of assets commissioned in each year) 1969: 191.7583; Year commissioned (number of assets commissioned in each year) 1970: 233.7055; Year commissioned (number of assets commissioned in each year) 1971: 467.411; Year commissioned (number of assets commissioned in each year) 1972: 299.6224; Year commissioned (number of assets commissioned in each year) 1973: 179.7735; Year commissioned (number of assets commissioned in each year) 1974: 203.7432; Year commissioned (number of assets commissioned in each year) 1975: 245.6904; Year commissioned (number of assets commissioned in each year) 1976: 239.6979; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 317.5998; Year commissioned (number of assets commissioned in each year) 1979: 89.8867; Year commissioned (number of assets commissioned in each year) 1980: 83.8943; Year commissioned (number of assets commissioned in each year) 1981: 491.3808; Year commissioned (number of assets commissioned in each year) 1982: 575.0422; Year commissioned (number of assets commissioned in each year) 1983: 843.723; Year commissioned (number of assets commissioned in each year) 1984: 838.7099; Year commissioned (number of assets commissioned in each year) 1985: 515.1177; Year commissioned (number of assets commissioned in each year) 1986: 370.3196; Year commissioned (number of assets commissioned in each year) 1987: 149.5784; Year commissioned (number of assets commissioned in each year) 1988: 251.45; Year commissioned (number of assets commissioned in each year) 1989: 238.4858; Year commissioned (number of assets commissioned in each year) 1990: 107.6312; Year commissioned (number of assets commissioned in each year) 1991: 316.3876; Year commissioned (number of assets commissioned in each year) 1992: 65.6841; Year commissioned (number of assets commissioned in each year) 1993: 10.7727; Year commissioned (number of assets commissioned in each year) 1994: 245.4575; Year commissioned (number of assets commissioned in each year) 1995: 64.7048; Year commissioned (number of assets commissioned in each year) 1996: 65.6841; Year commissioned (number of assets commissioned in each year) 1997: 166.5764; Year commissioned (number of assets commissioned in each year) 1998: 95.6463; Year commissioned (number of assets commissioned in each year) 1999: 52.7199; Year commissioned (number of assets commissioned in each year) 2000: 329.3518; Year commissioned (number of assets commissioned in each year) 2001: 364.3272; Year commissioned (number of assets commissioned in each year) 2002: 53.6992; Year commissioned (number of assets commissioned in each year) 2003: 628.5759; Year commissioned (number of assets commissioned in each year) 2004: 29.6314; Year commissioned (number of assets commissioned in each year) 2005: 189.9916; Year commissioned (number of assets commissioned in each year) 2006: 190.971; Year commissioned (number of assets commissioned in each year) 2007: 10; Year commissioned (number of assets commissioned in each year) 2008: 17; Year commissioned (number of assets commissioned in each year) 2009: 30; Year commissioned (number of assets commissioned in each year) 2010: 19; Year commissioned (number of assets commissioned in each year) 2011: 19; Year commissioned (number of assets commissioned in each year) 2012: 19
132kV Pole line | 55 | 7.4162 |  | 207000 |  | 698.0187 | [29 empty] | 37.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.1 | 78.6 | 54.5 | 0 | 0 | 0 | 0.7 | 0 | 15.7 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 | 0 | 45 | 0 | 0.1 | 1.8 | 0 | 0.9 | 0 | 133.7 | 0 | 11 | 1.6 | 0 | 0 | 72.6 | 4.3 | 4.3 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 28 | 31 | 32 | 35 | 29 | 4.4487 | 3.1141 | 6.0799 | 2.0761
132kV Tower line | 60 | 7.746 |  | 207000 |  | 534.95 | [40 empty] | 140.2 | 0 | 0 | 27.6 | 29.6 | 0 | 0 | 0 | 0 | 9.4 | 0 | 0 | 12.3 | 0 | 46.8 | 67.5 | 0 | 0 | 84.8 | 43.5 | 41 | 2.3 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 2.4 | 1.2 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.55 | 6 | 5 | 0 | 0 | 0 | 0 | 0
33kV | 55 | 7.4162 |  | 93150 |  | 1461.0184 | Year commissioned (number of assets commissioned in each year) 1964: 30.3; Year commissioned (number of assets commissioned in each year) 1965: 32.8373; Year commissioned (number of assets commissioned in each year) 1966: 61.5699; Year commissioned (number of assets commissioned in each year) 1967: 26.6803; Year commissioned (number of assets commissioned in each year) 1968: 55.4129; Year commissioned (number of assets commissioned in each year) 1969: 112.8781; Year commissioned (number of assets commissioned in each year) 1970: 43.0989; Year commissioned (number of assets commissioned in each year) 1971: 61.5699; Year commissioned (number of assets commissioned in each year) 1972: 90.3025; Year commissioned (number of assets commissioned in each year) 1973: 18.471; Year commissioned (number of assets commissioned in each year) 1974: 20.5233; Year commissioned (number of assets commissioned in each year) 1975: 30.7849; Year commissioned (number of assets commissioned in each year) 1976: 73.8838; Year commissioned (number of assets commissioned in each year) 1977: 2.0523; Year commissioned (number of assets commissioned in each year) 1978: 28.7326; Year commissioned (number of assets commissioned in each year) 1979: 32.8373; Year commissioned (number of assets commissioned in each year) 1980: 20.5233; Year commissioned (number of assets commissioned in each year) 1981: 88.2501; Year commissioned (number of assets commissioned in each year) 1982: 59.5175; Year commissioned (number of assets commissioned in each year) 1983: 82.0931; Year commissioned (number of assets commissioned in each year) 1984: 51.3082; Year commissioned (number of assets commissioned in each year) 1985: 10.2616; Year commissioned (number of assets commissioned in each year) 1986: 8.2093; Year commissioned (number of assets commissioned in each year) 1987: 16.4186; Year commissioned (number of assets commissioned in each year) 1988: 8.2093; Year commissioned (number of assets commissioned in each year) 1989: 12.314; Year commissioned (number of assets commissioned in each year) 1990: 18.471; Year commissioned (number of assets commissioned in each year) 1991: 22.5756; Year commissioned (number of assets commissioned in each year) 1992: 4.1047; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 30.7849; Year commissioned (number of assets commissioned in each year) 1995: 6.157; Year commissioned (number of assets commissioned in each year) 1996: 65.6745; Year commissioned (number of assets commissioned in each year) 1997: 14.3663; Year commissioned (number of assets commissioned in each year) 1998: 2.0523; Year commissioned (number of assets commissioned in each year) 1999: 12.314; Year commissioned (number of assets commissioned in each year) 2000: 28.7326; Year commissioned (number of assets commissioned in each year) 2001: 32.8373; Year commissioned (number of assets commissioned in each year) 2002: 2.0523; Year commissioned (number of assets commissioned in each year) 2003: 7.7593; Year commissioned (number of assets commissioned in each year) 2004: 6; Year commissioned (number of assets commissioned in each year) 2005: 18; Year commissioned (number of assets commissioned in each year) 2006: 18; Year commissioned (number of assets commissioned in each year) 2007: 17; Year commissioned (number of assets commissioned in each year) 2008: 19; Year commissioned (number of assets commissioned in each year) 2009: 12.0281; Year commissioned (number of assets commissioned in each year) 2010: 25.6116; Year commissioned (number of assets commissioned in each year) 2011: 12.2355; Year commissioned (number of assets commissioned in each year) 2012: 6.2214
66kV | 55 | 7.4162 |  | 103500 |  | 534.0214 | Year commissioned (number of assets commissioned in each year) 1956: 21.1575; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 0; Year commissioned (number of assets commissioned in each year) 1960: 2.7697; Year commissioned (number of assets commissioned in each year) 1961: 0; Year commissioned (number of assets commissioned in each year) 1962: 0; Year commissioned (number of assets commissioned in each year) 1963: 0; Year commissioned (number of assets commissioned in each year) 1964: 63.7027; Year commissioned (number of assets commissioned in each year) 1965: 0; Year commissioned (number of assets commissioned in each year) 1966: 0; Year commissioned (number of assets commissioned in each year) 1967: 0; Year commissioned (number of assets commissioned in each year) 1968: 2.7697; Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 11.0787; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 27.6968; Year commissioned (number of assets commissioned in each year) 1977: 22.1575; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 16.6181; Year commissioned (number of assets commissioned in each year) 1982: 52.6239; Year commissioned (number of assets commissioned in each year) 1983: 36.0059; Year commissioned (number of assets commissioned in each year) 1984: 38.7755; Year commissioned (number of assets commissioned in each year) 1985: 58.1633; Year commissioned (number of assets commissioned in each year) 1986: 49.8543; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 0; Year commissioned (number of assets commissioned in each year) 1989: 22.1575; Year commissioned (number of assets commissioned in each year) 1990: 13.8484; Year commissioned (number of assets commissioned in each year) 1991: 24.9271; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 8.309; Year commissioned (number of assets commissioned in each year) 1996: 8.309; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 13.8484; Year commissioned (number of assets commissioned in each year) 1999: 2.7697; Year commissioned (number of assets commissioned in each year) 2000: 2.7697; Year commissioned (number of assets commissioned in each year) 2001: 19.3878; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 2; Year commissioned (number of assets commissioned in each year) 2004: 0; Year commissioned (number of assets commissioned in each year) 2005: 0; Year commissioned (number of assets commissioned in each year) 2006: 2; Year commissioned (number of assets commissioned in each year) 2007: 0; Year commissioned (number of assets commissioned in each year) 2008: 2; Year commissioned (number of assets commissioned in each year) 2009: 1.8492; Year commissioned (number of assets commissioned in each year) 2010: 6.0099; Year commissioned (number of assets commissioned in each year) 2011: 0.34672; Year commissioned (number of assets commissioned in each year) 2012: 0.11557
LV | 50 | 7.0711 |  | 5140 |  | 14189.1297 | [29 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318.0513 | 571.2479 | 683.9079 | 786.6813 | 869.4173 | 923.1791 | 941.8286 | 923.3406 | 869.4173 | 787.0043 | 684.0694 | 571.7323 | 488.7907 | 361.0671 | 276.5559 | 235.4689 | 155.7172 | 118.3003 | 99.8527 | 83.8939 | 37.9 | 75.6905 | 53.419 | 53.7673 | 53.1101 | 52.1933 | 59.4084 | 82.804 | 79.8176 | 31.9681 | 38.7492 | 59.7383 | 60.5456 | 111.8882 | 117.7006 | 92.998 | 102.6853 | 184.5429 | 142.0803 | 181.2378 | 175.9098 | 90.8231 | 77.4223 | 100.3489 | 65.959 | 64.9903 | 65.7976 | 68.058 | 64.6674 | 72.7915 | 142.0727 | 90.9791 | 90.9791 | 112.7416 | 120.8878 | 116.491 | 98.4902 | 91.506 | 56.4458
SWER | 50 | 7.0711 |  | 2898 |  | 489.9386 | Year commissioned (number of assets commissioned in each year) 1964: 12.2895; Year commissioned (number of assets commissioned in each year) 1965: 0; Year commissioned (number of assets commissioned in each year) 1966: 0; Year commissioned (number of assets commissioned in each year) 1967: 0; Year commissioned (number of assets commissioned in each year) 1968: 5; Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 9.8316; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 7.3737; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 13.5184; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 4.9158; Year commissioned (number of assets commissioned in each year) 1979: 1.2289; Year commissioned (number of assets commissioned in each year) 1980: 23.5548; Year commissioned (number of assets commissioned in each year) 1981: 2.0482; Year commissioned (number of assets commissioned in each year) 1982: 23.5548; Year commissioned (number of assets commissioned in each year) 1983: 4.711; Year commissioned (number of assets commissioned in each year) 1984: 15.9763; Year commissioned (number of assets commissioned in each year) 1985: 27.4465; Year commissioned (number of assets commissioned in each year) 1986: 14.9522; Year commissioned (number of assets commissioned in each year) 1987: 27.2417; Year commissioned (number of assets commissioned in each year) 1988: 30.9285; Year commissioned (number of assets commissioned in each year) 1989: 52.6399; Year commissioned (number of assets commissioned in each year) 1990: 14.1329; Year commissioned (number of assets commissioned in each year) 1991: 4.3013; Year commissioned (number of assets commissioned in each year) 1992: 4.711; Year commissioned (number of assets commissioned in each year) 1993: 12.4943; Year commissioned (number of assets commissioned in each year) 1994: 28.8803; Year commissioned (number of assets commissioned in each year) 1995: 6.1447; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 106.7136; Year commissioned (number of assets commissioned in each year) 1999: 1.0241; Year commissioned (number of assets commissioned in each year) 2000: 4.0965; Year commissioned (number of assets commissioned in each year) 2001: 5.1206; Year commissioned (number of assets commissioned in each year) 2002: 1.0241; Year commissioned (number of assets commissioned in each year) 2003: 0.4297; Year commissioned (number of assets commissioned in each year) 2004: 16.6537; Year commissioned (number of assets commissioned in each year) 2005: 2; Year commissioned (number of assets commissioned in each year) 2006: 2; Year commissioned (number of assets commissioned in each year) 2007: 2; Year commissioned (number of assets commissioned in each year) 2008: 1; Year commissioned (number of assets commissioned in each year) 2009: 0; Year commissioned (number of assets commissioned in each year) 2010: 0; Year commissioned (number of assets commissioned in each year) 2011: 0; Year commissioned (number of assets commissioned in each year) 2012: 0
Underground cables
11kV | 60 | 7.746 |  | 222525 |  | 3557.0003 | Year commissioned (number of assets commissioned in each year) 1965: 10; Year commissioned (number of assets commissioned in each year) 1966: 4.3545; Year commissioned (number of assets commissioned in each year) 1967: 5.2153; Year commissioned (number of assets commissioned in each year) 1968: 7.5251; Year commissioned (number of assets commissioned in each year) 1969: 14.7603; Year commissioned (number of assets commissioned in each year) 1970: 9.8281; Year commissioned (number of assets commissioned in each year) 1971: 8.3867; Year commissioned (number of assets commissioned in each year) 1972: 23.1431; Year commissioned (number of assets commissioned in each year) 1973: 54.9551; Year commissioned (number of assets commissioned in each year) 1974: 50.0121; Year commissioned (number of assets commissioned in each year) 1975: 64.8111; Year commissioned (number of assets commissioned in each year) 1976: 39.656; Year commissioned (number of assets commissioned in each year) 1977: 20.7509; Year commissioned (number of assets commissioned in each year) 1978: 39.9756; Year commissioned (number of assets commissioned in each year) 1979: 74.6993; Year commissioned (number of assets commissioned in each year) 1980: 84.7134; Year commissioned (number of assets commissioned in each year) 1981: 121.6752; Year commissioned (number of assets commissioned in each year) 1982: 129.9095; Year commissioned (number of assets commissioned in each year) 1983: 98.2709; Year commissioned (number of assets commissioned in each year) 1984: 41.7608; Year commissioned (number of assets commissioned in each year) 1985: 56.9338; Year commissioned (number of assets commissioned in each year) 1986: 85.5461; Year commissioned (number of assets commissioned in each year) 1987: 72.6251; Year commissioned (number of assets commissioned in each year) 1988: 75.8744; Year commissioned (number of assets commissioned in each year) 1989: 91.2639; Year commissioned (number of assets commissioned in each year) 1990: 59.753; Year commissioned (number of assets commissioned in each year) 1991: 59.1335; Year commissioned (number of assets commissioned in each year) 1992: 29.3711; Year commissioned (number of assets commissioned in each year) 1993: 61.4702; Year commissioned (number of assets commissioned in each year) 1994: 85.2523; Year commissioned (number of assets commissioned in each year) 1995: 72.2721; Year commissioned (number of assets commissioned in each year) 1996: 55.4854; Year commissioned (number of assets commissioned in each year) 1997: 45.9652; Year commissioned (number of assets commissioned in each year) 1998: 116.6575; Year commissioned (number of assets commissioned in each year) 1999: 52.4345; Year commissioned (number of assets commissioned in each year) 2000: 113.0773; Year commissioned (number of assets commissioned in each year) 2001: 161.169; Year commissioned (number of assets commissioned in each year) 2002: 50.0288; Year commissioned (number of assets commissioned in each year) 2003: 101.0093; Year commissioned (number of assets commissioned in each year) 2004: 119.9267; Year commissioned (number of assets commissioned in each year) 2005: 151; Year commissioned (number of assets commissioned in each year) 2006: 151; Year commissioned (number of assets commissioned in each year) 2007: 161; Year commissioned (number of assets commissioned in each year) 2008: 176; Year commissioned (number of assets commissioned in each year) 2009: 96.3481; Year commissioned (number of assets commissioned in each year) 2010: 151; Year commissioned (number of assets commissioned in each year) 2011: 127; Year commissioned (number of assets commissioned in each year) 2012: 74
132kV | 45 | 6.7082 |  | 2173500 |  | 96.0438 | Year commissioned (number of assets commissioned in each year) 1961: 0; Year commissioned (number of assets commissioned in each year) 1962: 0; Year commissioned (number of assets commissioned in each year) 1963: 0; Year commissioned (number of assets commissioned in each year) 1964: 0; Year commissioned (number of assets commissioned in each year) 1965: 17.423; Year commissioned (number of assets commissioned in each year) 1966: 0; Year commissioned (number of assets commissioned in each year) 1967: 0; Year commissioned (number of assets commissioned in each year) 1968: 0; Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 23.125; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 0; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 0.08; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 0.75; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 0; Year commissioned (number of assets commissioned in each year) 1991: 0.28; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 5; Year commissioned (number of assets commissioned in each year) 1994: 1.55; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0.93; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0.4; Year commissioned (number of assets commissioned in each year) 2001: 4.254; Year commissioned (number of assets commissioned in each year) 2002: 0.516; Year commissioned (number of assets commissioned in each year) 2003: 0; Year commissioned (number of assets commissioned in each year) 2004: 0.55; Year commissioned (number of assets commissioned in each year) 2005: 0; Year commissioned (number of assets commissioned in each year) 2006: 5; Year commissioned (number of assets commissioned in each year) 2007: 4; Year commissioned (number of assets commissioned in each year) 2008: 7; Year commissioned (number of assets commissioned in each year) 2009: 4.3642; Year commissioned (number of assets commissioned in each year) 2010: 3.3869; Year commissioned (number of assets commissioned in each year) 2011: 13.7377; Year commissioned (number of assets commissioned in each year) 2012: 3.697
22kV | 60 | 7.746 |  | 222525 |  | 320.9999 | Year commissioned (number of assets commissioned in each year) 1965: 0; Year commissioned (number of assets commissioned in each year) 1966: 0; Year commissioned (number of assets commissioned in each year) 1967: 0; Year commissioned (number of assets commissioned in each year) 1968: 0; Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 0; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 0; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 0; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 0; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 18.1735; Year commissioned (number of assets commissioned in each year) 2000: 22.3673; Year commissioned (number of assets commissioned in each year) 2001: 36.3469; Year commissioned (number of assets commissioned in each year) 2002: 32.1531; Year commissioned (number of assets commissioned in each year) 2003: 20.9694; Year commissioned (number of assets commissioned in each year) 2004: 22.3673; Year commissioned (number of assets commissioned in each year) 2005: 43.3367; Year commissioned (number of assets commissioned in each year) 2006: 20.9694; Year commissioned (number of assets commissioned in each year) 2007: 27.9592; Year commissioned (number of assets commissioned in each year) 2008: 29.3571; Year commissioned (number of assets commissioned in each year) 2009: 8; Year commissioned (number of assets commissioned in each year) 2010: 24; Year commissioned (number of assets commissioned in each year) 2011: 11; Year commissioned (number of assets commissioned in each year) 2012: 4
33kV | 45 | 6.7082 |  | 1449000 |  | 154.5761 | Year commissioned (number of assets commissioned in each year) 1961: 2.9419; Year commissioned (number of assets commissioned in each year) 1962: 0; Year commissioned (number of assets commissioned in each year) 1963: 0; Year commissioned (number of assets commissioned in each year) 1964: 2.9171; Year commissioned (number of assets commissioned in each year) 1965: 0.7024; Year commissioned (number of assets commissioned in each year) 1966: 0.5702; Year commissioned (number of assets commissioned in each year) 1967: 0; Year commissioned (number of assets commissioned in each year) 1968: 0.124; Year commissioned (number of assets commissioned in each year) 1969: 0.2231; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0.8264; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0.6198; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0.0744; Year commissioned (number of assets commissioned in each year) 1977: 3.636; Year commissioned (number of assets commissioned in each year) 1978: 0.6611; Year commissioned (number of assets commissioned in each year) 1979: 9.3434; Year commissioned (number of assets commissioned in each year) 1980: 8.1314; Year commissioned (number of assets commissioned in each year) 1981: 12.5057; Year commissioned (number of assets commissioned in each year) 1982: 4.1208; Year commissioned (number of assets commissioned in each year) 1983: 6.7211; Year commissioned (number of assets commissioned in each year) 1984: 3.1512; Year commissioned (number of assets commissioned in each year) 1985: 3.1512; Year commissioned (number of assets commissioned in each year) 1986: 8.3518; Year commissioned (number of assets commissioned in each year) 1987: 6.4567; Year commissioned (number of assets commissioned in each year) 1988: 4.4183; Year commissioned (number of assets commissioned in each year) 1989: 1.6197; Year commissioned (number of assets commissioned in each year) 1990: 0.6611; Year commissioned (number of assets commissioned in each year) 1991: 2.435; Year commissioned (number of assets commissioned in each year) 1992: 4.5285; Year commissioned (number of assets commissioned in each year) 1993: 0.9145; Year commissioned (number of assets commissioned in each year) 1994: 9.2873; Year commissioned (number of assets commissioned in each year) 1995: 0.3195; Year commissioned (number of assets commissioned in each year) 1996: 3.3716; Year commissioned (number of assets commissioned in each year) 1997: 2.424; Year commissioned (number of assets commissioned in each year) 1998: 1.1294; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 7.1618; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 0.6423; Year commissioned (number of assets commissioned in each year) 2004: 2.1239; Year commissioned (number of assets commissioned in each year) 2005: 7; Year commissioned (number of assets commissioned in each year) 2006: 2; Year commissioned (number of assets commissioned in each year) 2007: 5; Year commissioned (number of assets commissioned in each year) 2008: 12.3087; Year commissioned (number of assets commissioned in each year) 2009: 3.5137; Year commissioned (number of assets commissioned in each year) 2010: 0.4104; Year commissioned (number of assets commissioned in each year) 2011: 8.0767; Year commissioned (number of assets commissioned in each year) 2012: 0
66kV | 45 | 6.7082 |  | 1966500 |  | 15.61 | Year commissioned (number of assets commissioned in each year) 1961: 0; Year commissioned (number of assets commissioned in each year) 1962: 0; Year commissioned (number of assets commissioned in each year) 1963: 0; Year commissioned (number of assets commissioned in each year) 1964: 0; Year commissioned (number of assets commissioned in each year) 1965: 0; Year commissioned (number of assets commissioned in each year) 1966: 0; Year commissioned (number of assets commissioned in each year) 1967: 0; Year commissioned (number of assets commissioned in each year) 1968: 0; Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0.4; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 0.58; Year commissioned (number of assets commissioned in each year) 1983: 0.06; Year commissioned (number of assets commissioned in each year) 1984: 0.17; Year commissioned (number of assets commissioned in each year) 1985: 2.29; Year commissioned (number of assets commissioned in each year) 1986: 0.615; Year commissioned (number of assets commissioned in each year) 1987: 2; Year commissioned (number of assets commissioned in each year) 1988: 2.8; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 2.23; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 0.99; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 1; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 0.0527; Year commissioned (number of assets commissioned in each year) 2004: 0.0169; Year commissioned (number of assets commissioned in each year) 2005: 0; Year commissioned (number of assets commissioned in each year) 2006: 0; Year commissioned (number of assets commissioned in each year) 2007: 0; Year commissioned (number of assets commissioned in each year) 2008: 0.5987; Year commissioned (number of assets commissioned in each year) 2009: 0.286; Year commissioned (number of assets commissioned in each year) 2010: 0.1828; Year commissioned (number of assets commissioned in each year) 2011: 1.0909; Year commissioned (number of assets commissioned in each year) 2012: 0.247
LV | 60 | 7.746 |  | 144900 |  | 11102.9999 | [36 empty] | 0.9153 | 0 | 0 | 0 | 0 | 0 | 1.8212 | 1.8307 | 0 | 0.9074 | 0 | 1.8307 | 7.2873 | 4.5678 | 8.2203 | 14.8651 | 9.5421 | 28.7095 | 11.6543 | 3.1926 | 15.9639 | 19.1196 | 27.5876 | 54.1125 | 36.0308 | 30.7465 | 84.8447 | 201.4706 | 183.3491 | 237.6036 | 145.3827 | 76.0747 | 146.5545 | 273.8546 | 310.5672 | 446.073 | 508.0111 | 384.2885 | 163.3055 | 222.6396 | 334.528 | 284.0005 | 296.7071 | 334.5821 | 219.0603 | 216.7889 | 107.6773 | 225.3556 | 312.5429 | 264.9565 | 203.4148 | 168.5128 | 427.6775 | 192.23 | 414.552 | 590.8607 | 183.4104 | 53.4594 | 236.9846 | 502.1532 | 435.6692 | 292.0779 | 363.8736 | 220 | 202 | 229 | 128
Services (incl. LV pillars and LV service pits)
OH Service | 35 | 5.9161 |  | 932 |  | 541119 | [40 empty] | 53 | 54 | 468 | 262 | 312 | 104 | 366 | 210 | 209 | 574 | 62 | 1264 | 1140 | 2104 | 2539 | 2174 | 2435 | 2970 | 2924 | 3560 | 2666 | 629 | 1252 | 1264 | 2899 | 7148 | 5837 | 6598 | 8231 | 11619 | 16544 | 39767 | 24967 | 17425 | 12294 | 15644 | 15737 | 14844 | 14571 | 15635 | 15989 | 12180 | 10646 | 10776 | 12490 | 11616 | 11474 | 7082 | 15579 | 18837 | 14602 | 15004 | 10186 | 16514 | 16763 | 13198 | 13198 | 13972 | 13972 | 7305 | 7946 | 6410 | 6025
UG Service | 60 | 7.746 |  | 3312 |  | 158208 | [40 empty] | 44 | 76 | 366 | 238 | 242 | 83 | 322 | 357 | 326 | 946 | 405 | 1368 | 1129 | 2179 | 3037 | 2544 | 3386 | 3768 | 4078 | 4055 | 3355 | 1430 | 1002 | 1344 | 1680 | 3680 | 3319 | 3740 | 4203 | 5105 | 8931 | 15341 | 2793 | 5935 | 5081 | 3819 | 2307 | 2983 | 2909 | 3077 | 3618 | 2827 | 2634 | 2626 | 2374 | 2063 | 1856 | 1398 | 1726 | 1992 | 2177 | 2337 | 1132 | 1643 | 1522 | 1960 | 1960 | 1643 | 1643 | 2136 | 2323 | 1874 | 1761
Distribution transformers
Pole mount | 35 | 5.9161 |  | 10294 |  | 19319 | [29 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | 11 | 53 | 37 | 43 | 12 | 50 | 27 | 26 | 77 | 115 | 150 | 123 | 239 | 310 | 346 | 404 | 450 | 458 | 508 | 434 | 198 | 139 | 178 | 193 | 418 | 406 | 442 | 506 | 622 | 1086 | 1730 | 369 | 828 | 730 | 618 | 312 | 376 | 377 | 414 | 464 | 355 | 360 | 341 | 295 | 309 | 218 | 187 | 200 | 249 | 242 | 293 | 221 | 272 | 191 | 181 | 142 | 164 | 120 | 157 | 52 | 330 | 150
Pad mount | 45 | 6.7082 |  | 49154 |  | 10615 | [29 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 5 | 5 | 8 | 0 | 11 | 14 | 29 | 14 | 10 | 22 | 22 | 22 | 16 | 17 | 18 | 45 | 51 | 53 | 35 | 46 | 79 | 96 | 231 | 130 | 144 | 163 | 239 | 305 | 443 | 412 | 319 | 228 | 283 | 285 | 274 | 284 | 275 | 298 | 228 | 176 | 202 | 259 | 225 | 204 | 230 | 214 | 271 | 229 | 190 | 298 | 426 | 373 | 382 | 248 | 274 | 225 | 197 | 124 | 485 | 212
Indoor | 35 | 5.9161 |  | 36824 |  | 83 | [29 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 1 | 0 | 6 | 1 | 2 | 2 | 4 | 16 | 0 | 4 | 9 | 0 | 5 | 3 | 3 | 5 | 1 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Distribution switchgear
11 & 22 Air break switch, 3 phase top pole | 35 | 5.9161 |  | 12420 |  | 10825 | Year commissioned (number of assets commissioned in each year) 1955: 1; Year commissioned (number of assets commissioned in each year) 1956: 0; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 1; Year commissioned (number of assets commissioned in each year) 1960: 8; Year commissioned (number of assets commissioned in each year) 1961: 13; Year commissioned (number of assets commissioned in each year) 1962: 18; Year commissioned (number of assets commissioned in each year) 1963: 23; Year commissioned (number of assets commissioned in each year) 1964: 48; Year commissioned (number of assets commissioned in each year) 1965: 43; Year commissioned (number of assets commissioned in each year) 1966: 37; Year commissioned (number of assets commissioned in each year) 1967: 24; Year commissioned (number of assets commissioned in each year) 1968: 37; Year commissioned (number of assets commissioned in each year) 1969: 72; Year commissioned (number of assets commissioned in each year) 1970: 81; Year commissioned (number of assets commissioned in each year) 1971: 80; Year commissioned (number of assets commissioned in each year) 1972: 101; Year commissioned (number of assets commissioned in each year) 1973: 64; Year commissioned (number of assets commissioned in each year) 1974: 81; Year commissioned (number of assets commissioned in each year) 1975: 149; Year commissioned (number of assets commissioned in each year) 1976: 165; Year commissioned (number of assets commissioned in each year) 1977: 190; Year commissioned (number of assets commissioned in each year) 1978: 165; Year commissioned (number of assets commissioned in each year) 1979: 247; Year commissioned (number of assets commissioned in each year) 1980: 149; Year commissioned (number of assets commissioned in each year) 1981: 128; Year commissioned (number of assets commissioned in each year) 1982: 140; Year commissioned (number of assets commissioned in each year) 1983: 176; Year commissioned (number of assets commissioned in each year) 1984: 212; Year commissioned (number of assets commissioned in each year) 1985: 224; Year commissioned (number of assets commissioned in each year) 1986: 149; Year commissioned (number of assets commissioned in each year) 1987: 190; Year commissioned (number of assets commissioned in each year) 1988: 196; Year commissioned (number of assets commissioned in each year) 1989: 190; Year commissioned (number of assets commissioned in each year) 1990: 224; Year commissioned (number of assets commissioned in each year) 1991: 175; Year commissioned (number of assets commissioned in each year) 1992: 129; Year commissioned (number of assets commissioned in each year) 1993: 120; Year commissioned (number of assets commissioned in each year) 1994: 127; Year commissioned (number of assets commissioned in each year) 1995: 81; Year commissioned (number of assets commissioned in each year) 1996: 95; Year commissioned (number of assets commissioned in each year) 1997: 83; Year commissioned (number of assets commissioned in each year) 1998: 102; Year commissioned (number of assets commissioned in each year) 1999: 348; Year commissioned (number of assets commissioned in each year) 2000: 230; Year commissioned (number of assets commissioned in each year) 2001: 337; Year commissioned (number of assets commissioned in each year) 2002: 435; Year commissioned (number of assets commissioned in each year) 2003: 465; Year commissioned (number of assets commissioned in each year) 2004: 530; Year commissioned (number of assets commissioned in each year) 2005: 624; Year commissioned (number of assets commissioned in each year) 2006: 686; Year commissioned (number of assets commissioned in each year) 2007: 745; Year commissioned (number of assets commissioned in each year) 2008: 700; Year commissioned (number of assets commissioned in each year) 2009: 481; Year commissioned (number of assets commissioned in each year) 2010: 280; Year commissioned (number of assets commissioned in each year) 2011: 265; Year commissioned (number of assets commissioned in each year) 2012: 161
11 & 22 Fuse, 3 phase set | 35 | 5.9161 |  | 2484 |  | 1563 | Year commissioned (number of assets commissioned in each year) 1970: 6; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 6; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 6; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 0; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 0; Year commissioned (number of assets commissioned in each year) 1989: 11; Year commissioned (number of assets commissioned in each year) 1990: 0; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 6; Year commissioned (number of assets commissioned in each year) 1999: 363; Year commissioned (number of assets commissioned in each year) 2000: 631; Year commissioned (number of assets commissioned in each year) 2001: 112; Year commissioned (number of assets commissioned in each year) 2002: 78; Year commissioned (number of assets commissioned in each year) 2003: 73; Year commissioned (number of assets commissioned in each year) 2004: 39; Year commissioned (number of assets commissioned in each year) 2005: 28; Year commissioned (number of assets commissioned in each year) 2006: 15; Year commissioned (number of assets commissioned in each year) 2007: 17; Year commissioned (number of assets commissioned in each year) 2008: 23; Year commissioned (number of assets commissioned in each year) 2009: 35; Year commissioned (number of assets commissioned in each year) 2010: 27; Year commissioned (number of assets commissioned in each year) 2011: 43; Year commissioned (number of assets commissioned in each year) 2012: 44
11 & 22 Link, 3 phase set | 35 | 5.9161 |  | 2070 |  | 9286 | Year commissioned (number of assets commissioned in each year) 1965: 8; Year commissioned (number of assets commissioned in each year) 1966: 0; Year commissioned (number of assets commissioned in each year) 1967: 0; Year commissioned (number of assets commissioned in each year) 1968: 0; Year commissioned (number of assets commissioned in each year) 1969: 8; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 8; Year commissioned (number of assets commissioned in each year) 1972: 16; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 0; Year commissioned (number of assets commissioned in each year) 1985: 8; Year commissioned (number of assets commissioned in each year) 1986: 0; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 0; Year commissioned (number of assets commissioned in each year) 1989: 65; Year commissioned (number of assets commissioned in each year) 1990: 0; Year commissioned (number of assets commissioned in each year) 1991: 137; Year commissioned (number of assets commissioned in each year) 1992: 16; Year commissioned (number of assets commissioned in each year) 1993: 16; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 16; Year commissioned (number of assets commissioned in each year) 1997: 8; Year commissioned (number of assets commissioned in each year) 1998: 146; Year commissioned (number of assets commissioned in each year) 1999: 865; Year commissioned (number of assets commissioned in each year) 2000: 720; Year commissioned (number of assets commissioned in each year) 2001: 1286; Year commissioned (number of assets commissioned in each year) 2002: 1391; Year commissioned (number of assets commissioned in each year) 2003: 1254; Year commissioned (number of assets commissioned in each year) 2004: 1011; Year commissioned (number of assets commissioned in each year) 2005: 987; Year commissioned (number of assets commissioned in each year) 2006: 736; Year commissioned (number of assets commissioned in each year) 2007: 134; Year commissioned (number of assets commissioned in each year) 2008: 140; Year commissioned (number of assets commissioned in each year) 2009: 68; Year commissioned (number of assets commissioned in each year) 2010: 81; Year commissioned (number of assets commissioned in each year) 2011: 85; Year commissioned (number of assets commissioned in each year) 2012: 76
11 & 22 Recloser, 3 phase electronic | 35 | 5.9161 |  | 51750 |  | 489 | Year commissioned (number of assets commissioned in each year) 1968: 2; Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 2; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 0; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 2; Year commissioned (number of assets commissioned in each year) 1987: 3; Year commissioned (number of assets commissioned in each year) 1988: 3; Year commissioned (number of assets commissioned in each year) 1989: 14; Year commissioned (number of assets commissioned in each year) 1990: 16; Year commissioned (number of assets commissioned in each year) 1991: 20; Year commissioned (number of assets commissioned in each year) 1992: 17; Year commissioned (number of assets commissioned in each year) 1993: 5; Year commissioned (number of assets commissioned in each year) 1994: 17; Year commissioned (number of assets commissioned in each year) 1995: 22; Year commissioned (number of assets commissioned in each year) 1996: 24; Year commissioned (number of assets commissioned in each year) 1997: 24; Year commissioned (number of assets commissioned in each year) 1998: 2; Year commissioned (number of assets commissioned in each year) 1999: 6; Year commissioned (number of assets commissioned in each year) 2000: 14; Year commissioned (number of assets commissioned in each year) 2001: 17; Year commissioned (number of assets commissioned in each year) 2002: 6; Year commissioned (number of assets commissioned in each year) 2003: 26; Year commissioned (number of assets commissioned in each year) 2004: 28; Year commissioned (number of assets commissioned in each year) 2005: 12; Year commissioned (number of assets commissioned in each year) 2006: 22; Year commissioned (number of assets commissioned in each year) 2007: 40; Year commissioned (number of assets commissioned in each year) 2008: 31; Year commissioned (number of assets commissioned in each year) 2009: 19; Year commissioned (number of assets commissioned in each year) 2010: 40; Year commissioned (number of assets commissioned in each year) 2011: 34; Year commissioned (number of assets commissioned in each year) 2012: 21
11 & 22 Sectionaliser | 35 | 5.9161 |  | 12420 |  | 53 | Year commissioned (number of assets commissioned in each year) 1995: 3; Year commissioned (number of assets commissioned in each year) 1996: 3; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 3; Year commissioned (number of assets commissioned in each year) 2001: 3; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 0; Year commissioned (number of assets commissioned in each year) 2004: 0; Year commissioned (number of assets commissioned in each year) 2005: 0; Year commissioned (number of assets commissioned in each year) 2006: 3; Year commissioned (number of assets commissioned in each year) 2007: 2; Year commissioned (number of assets commissioned in each year) 2008: 3; Year commissioned (number of assets commissioned in each year) 2009: 5; Year commissioned (number of assets commissioned in each year) 2010: 8; Year commissioned (number of assets commissioned in each year) 2011: 10; Year commissioned (number of assets commissioned in each year) 2012: 10
LV Link | 35 | 5.9161 |  | 1035 |  | 42285 | [40 empty] | 11 | 19 | 91 | 59 | 60 | 21 | 80 | 89 | 81 | 234 | 100 | 339 | 280 | 540 | 752 | 630 | 839 | 933 | 1010 | 1004 | 831 | 354 | 248 | 333 | 416 | 911 | 822 | 926 | 1041 | 1264 | 2212 | 3799 | 692 | 1470 | 1258 | 946 | 571 | 739 | 721 | 762 | 896 | 700 | 652 | 650 | 588 | 511 | 460 | 346 | 427 | 493 | 539 | 579 | 280 | 700 | 750 | 750 | 755 | 825 | 725 | 1282 | 730 | 814 | 345
Distribution 'other assets'
Pole sub | 45 | 6.7082 |  | 11907 |  | 19653 | [29 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 2 | 0 | 4 | 12 | 57 | 37 | 41 | 11 | 49 | 22 | 26 | 75 | 101 | 131 | 93 | 216 | 309 | 281 | 393 | 402 | 417 | 487 | 386 | 197 | 137 | 201 | 233 | 487 | 461 | 516 | 585 | 718 | 1242 | 798 | 392 | 923 | 864 | 695 | 325 | 419 | 419 | 443 | 521 | 387 | 342 | 336 | 315 | 276 | 241 | 189 | 235 | 253 | 397 | 313 | 301 | 388 | 268 | 264 | 193 | 197 | 40 | 215 | 71 | 190 | 110
Pad mount sub | 40 | 6.3246 |  | 30338 |  | 9957 | [29 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 4 | 6 | 0 | 0 | 4 | 8 | 12 | 16 | 11 | 14 | 16 | 23 | 8 | 30 | 25 | 32 | 59 | 26 | 36 | 59 | 75 | 177 | 124 | 143 | 160 | 224 | 291 | 454 | 394 | 267 | 193 | 306 | 258 | 223 | 250 | 257 | 253 | 193 | 173 | 180 | 217 | 192 | 191 | 137 | 265 | 292 | 270 | 268 | 315 | 434 | 416 | 399 | 288 | 280 | 33 | 258 | 153 | 324 | 229
Indoor sub | 40 | 6.3246 |  | 96371 |  | 532 | [29 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 3 | 17 | 4 | 6 | 3 | 3 | 5 | 2 | 2 | 7 | 2 | 6 | 4 | 5 | 5 | 8 | 44 | 5 | 7 | 10 | 8 | 14 | 8 | 11 | 20 | 9 | 16 | 13 | 29 | 17 | 15 | 11 | 22 | 8 | 9 | 15 | 11 | 4 | 3 | 10 | 13 | 10 | 6 | 7 | 19 | 18 | 17 | 14 | 7 | 0 | 6 | 2 | 5 | 5
Zone transformers
<=15MVA | 50 | 7.0711 | 1 | 1145620 |  | 72 | Year commissioned (number of assets commissioned in each year) 1951: 0; Year commissioned (number of assets commissioned in each year) 1952: 0; Year commissioned (number of assets commissioned in each year) 1953: 2; Year commissioned (number of assets commissioned in each year) 1954: 0; Year commissioned (number of assets commissioned in each year) 1955: 0; Year commissioned (number of assets commissioned in each year) 1956: 0; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 2; Year commissioned (number of assets commissioned in each year) 1960: 0; Year commissioned (number of assets commissioned in each year) 1961: 10; Year commissioned (number of assets commissioned in each year) 1962: 3; Year commissioned (number of assets commissioned in each year) 1963: 8; Year commissioned (number of assets commissioned in each year) 1964: 1; Year commissioned (number of assets commissioned in each year) 1965: 4; Year commissioned (number of assets commissioned in each year) 1966: 1; Year commissioned (number of assets commissioned in each year) 1967: 1; Year commissioned (number of assets commissioned in each year) 1968: 0; Year commissioned (number of assets commissioned in each year) 1969: 1; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 2; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 1; Year commissioned (number of assets commissioned in each year) 1981: 3; Year commissioned (number of assets commissioned in each year) 1982: 3; Year commissioned (number of assets commissioned in each year) 1983: 3; Year commissioned (number of assets commissioned in each year) 1984: 0; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 0; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 0; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 1; Year commissioned (number of assets commissioned in each year) 1991: 3; Year commissioned (number of assets commissioned in each year) 1992: 4; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 0; Year commissioned (number of assets commissioned in each year) 2002: 4; Year commissioned (number of assets commissioned in each year) 2003: 1; Year commissioned (number of assets commissioned in each year) 2004: 3; Year commissioned (number of assets commissioned in each year) 2005: 2; Year commissioned (number of assets commissioned in each year) 2006: 0; Year commissioned (number of assets commissioned in each year) 2007: 2; Year commissioned (number of assets commissioned in each year) 2008: 2; Year commissioned (number of assets commissioned in each year) 2009: 0; Year commissioned (number of assets commissioned in each year) 2010: 3; Year commissioned (number of assets commissioned in each year) 2011: 1; Year commissioned (number of assets commissioned in each year) 2012: 1
<=25MVA | 50 | 7.0711 | 1 | 1480127 |  | 172 | Year commissioned (number of assets commissioned in each year) 1951: 0; Year commissioned (number of assets commissioned in each year) 1952: 0; Year commissioned (number of assets commissioned in each year) 1953: 0; Year commissioned (number of assets commissioned in each year) 1954: 0; Year commissioned (number of assets commissioned in each year) 1955: 0; Year commissioned (number of assets commissioned in each year) 1956: 0; Year commissioned (number of assets commissioned in each year) 1957: 1; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 0; Year commissioned (number of assets commissioned in each year) 1960: 0; Year commissioned (number of assets commissioned in each year) 1961: 2; Year commissioned (number of assets commissioned in each year) 1962: 0; Year commissioned (number of assets commissioned in each year) 1963: 1; Year commissioned (number of assets commissioned in each year) 1964: 1; Year commissioned (number of assets commissioned in each year) 1965: 6; Year commissioned (number of assets commissioned in each year) 1966: 2; Year commissioned (number of assets commissioned in each year) 1967: 8; Year commissioned (number of assets commissioned in each year) 1968: 2; Year commissioned (number of assets commissioned in each year) 1969: 7; Year commissioned (number of assets commissioned in each year) 1970: 11; Year commissioned (number of assets commissioned in each year) 1971: 7; Year commissioned (number of assets commissioned in each year) 1972: 2; Year commissioned (number of assets commissioned in each year) 1973: 7; Year commissioned (number of assets commissioned in each year) 1974: 4; Year commissioned (number of assets commissioned in each year) 1975: 3; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 4; Year commissioned (number of assets commissioned in each year) 1978: 8; Year commissioned (number of assets commissioned in each year) 1979: 1; Year commissioned (number of assets commissioned in each year) 1980: 2; Year commissioned (number of assets commissioned in each year) 1981: 4; Year commissioned (number of assets commissioned in each year) 1982: 4; Year commissioned (number of assets commissioned in each year) 1983: 1; Year commissioned (number of assets commissioned in each year) 1984: 4; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 2; Year commissioned (number of assets commissioned in each year) 1987: 2; Year commissioned (number of assets commissioned in each year) 1988: 7; Year commissioned (number of assets commissioned in each year) 1989: 1; Year commissioned (number of assets commissioned in each year) 1990: 1; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 2; Year commissioned (number of assets commissioned in each year) 1994: 4; Year commissioned (number of assets commissioned in each year) 1995: 1; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 1; Year commissioned (number of assets commissioned in each year) 2001: 4; Year commissioned (number of assets commissioned in each year) 2002: 4; Year commissioned (number of assets commissioned in each year) 2003: 3; Year commissioned (number of assets commissioned in each year) 2004: 9; Year commissioned (number of assets commissioned in each year) 2005: 6; Year commissioned (number of assets commissioned in each year) 2006: 3; Year commissioned (number of assets commissioned in each year) 2007: 2; Year commissioned (number of assets commissioned in each year) 2008: 6; Year commissioned (number of assets commissioned in each year) 2009: 11; Year commissioned (number of assets commissioned in each year) 2010: 2; Year commissioned (number of assets commissioned in each year) 2011: 8; Year commissioned (number of assets commissioned in each year) 2012: 1
<=35MVA | 50 | 7.0711 | 0 | 1676452 |  | 62 | Year commissioned (number of assets commissioned in each year) 1951: 0; Year commissioned (number of assets commissioned in each year) 1952: 0; Year commissioned (number of assets commissioned in each year) 1953: 0; Year commissioned (number of assets commissioned in each year) 1954: 0; Year commissioned (number of assets commissioned in each year) 1955: 0; Year commissioned (number of assets commissioned in each year) 1956: 0; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 0; Year commissioned (number of assets commissioned in each year) 1960: 0; Year commissioned (number of assets commissioned in each year) 1961: 0; Year commissioned (number of assets commissioned in each year) 1962: 0; Year commissioned (number of assets commissioned in each year) 1963: 0; Year commissioned (number of assets commissioned in each year) 1964: 0; Year commissioned (number of assets commissioned in each year) 1965: 0; Year commissioned (number of assets commissioned in each year) 1966: 0; Year commissioned (number of assets commissioned in each year) 1967: 1; Year commissioned (number of assets commissioned in each year) 1968: 0; Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 1; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 6; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 4; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 4; Year commissioned (number of assets commissioned in each year) 1983: 3; Year commissioned (number of assets commissioned in each year) 1984: 2; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 5; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 0; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 1; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 2; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 2; Year commissioned (number of assets commissioned in each year) 2002: 1; Year commissioned (number of assets commissioned in each year) 2003: 3; Year commissioned (number of assets commissioned in each year) 2004: 6; Year commissioned (number of assets commissioned in each year) 2005: 4; Year commissioned (number of assets commissioned in each year) 2006: 6; Year commissioned (number of assets commissioned in each year) 2007: 1; Year commissioned (number of assets commissioned in each year) 2008: 0; Year commissioned (number of assets commissioned in each year) 2009: 7; Year commissioned (number of assets commissioned in each year) 2010: 3; Year commissioned (number of assets commissioned in each year) 2011: 0; Year commissioned (number of assets commissioned in each year) 2012: 0
<=45MVA | 50 | 7.0711 | 0 | 2360007 |  | 34 | Year commissioned (number of assets commissioned in each year) 1951: 0; Year commissioned (number of assets commissioned in each year) 1952: 0; Year commissioned (number of assets commissioned in each year) 1953: 0; Year commissioned (number of assets commissioned in each year) 1954: 0; Year commissioned (number of assets commissioned in each year) 1955: 0; Year commissioned (number of assets commissioned in each year) 1956: 0; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 0; Year commissioned (number of assets commissioned in each year) 1960: 0; Year commissioned (number of assets commissioned in each year) 1961: 0; Year commissioned (number of assets commissioned in each year) 1962: 0; Year commissioned (number of assets commissioned in each year) 1963: 0; Year commissioned (number of assets commissioned in each year) 1964: 0; Year commissioned (number of assets commissioned in each year) 1965: 0; Year commissioned (number of assets commissioned in each year) 1966: 0; Year commissioned (number of assets commissioned in each year) 1967: 0; Year commissioned (number of assets commissioned in each year) 1968: 0; Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 0; Year commissioned (number of assets commissioned in each year) 1985: 2; Year commissioned (number of assets commissioned in each year) 1986: 0; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 2; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 0; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 2; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 2; Year commissioned (number of assets commissioned in each year) 2001: 0; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 4; Year commissioned (number of assets commissioned in each year) 2004: 1; Year commissioned (number of assets commissioned in each year) 2005: 9; Year commissioned (number of assets commissioned in each year) 2006: 1; Year commissioned (number of assets commissioned in each year) 2007: 0; Year commissioned (number of assets commissioned in each year) 2008: 7; Year commissioned (number of assets commissioned in each year) 2009: 4; Year commissioned (number of assets commissioned in each year) 2010: 0; Year commissioned (number of assets commissioned in each year) 2011: 0; Year commissioned (number of assets commissioned in each year) 2012: 0
<=55MVA | 50 | 7.0711 | 0 | 2929789 |  | 8 | Year commissioned (number of assets commissioned in each year) 1951: 0; Year commissioned (number of assets commissioned in each year) 1952: 0; Year commissioned (number of assets commissioned in each year) 1953: 0; Year commissioned (number of assets commissioned in each year) 1954: 0; Year commissioned (number of assets commissioned in each year) 1955: 0; Year commissioned (number of assets commissioned in each year) 1956: 0; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 0; Year commissioned (number of assets commissioned in each year) 1960: 0; Year commissioned (number of assets commissioned in each year) 1961: 0; Year commissioned (number of assets commissioned in each year) 1962: 0; Year commissioned (number of assets commissioned in each year) 1963: 2; Year commissioned (number of assets commissioned in each year) 1964: 0; Year commissioned (number of assets commissioned in each year) 1965: 0; Year commissioned (number of assets commissioned in each year) 1966: 0; Year commissioned (number of assets commissioned in each year) 1967: 0; Year commissioned (number of assets commissioned in each year) 1968: 0; Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 0; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 0; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 0; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 0; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 2; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 2; Year commissioned (number of assets commissioned in each year) 1997: 2; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 0; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 0; Year commissioned (number of assets commissioned in each year) 2004: 0; Year commissioned (number of assets commissioned in each year) 2005: 0; Year commissioned (number of assets commissioned in each year) 2006: 0; Year commissioned (number of assets commissioned in each year) 2007: 0; Year commissioned (number of assets commissioned in each year) 2008: 0; Year commissioned (number of assets commissioned in each year) 2009: 0; Year commissioned (number of assets commissioned in each year) 2010: 0; Year commissioned (number of assets commissioned in each year) 2011: 0; Year commissioned (number of assets commissioned in each year) 2012: 0
<=5MVA | 50 | 7.0711 | 1 | 893527 |  | 23 | Year commissioned (number of assets commissioned in each year) 1951: 1; Year commissioned (number of assets commissioned in each year) 1952: 1; Year commissioned (number of assets commissioned in each year) 1953: 2; Year commissioned (number of assets commissioned in each year) 1954: 0; Year commissioned (number of assets commissioned in each year) 1955: 0; Year commissioned (number of assets commissioned in each year) 1956: 0; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 0; Year commissioned (number of assets commissioned in each year) 1960: 0; Year commissioned (number of assets commissioned in each year) 1961: 0; Year commissioned (number of assets commissioned in each year) 1962: 3; Year commissioned (number of assets commissioned in each year) 1963: 0; Year commissioned (number of assets commissioned in each year) 1964: 0; Year commissioned (number of assets commissioned in each year) 1965: 2; Year commissioned (number of assets commissioned in each year) 1966: 0; Year commissioned (number of assets commissioned in each year) 1967: 0; Year commissioned (number of assets commissioned in each year) 1968: 2; Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 1; Year commissioned (number of assets commissioned in each year) 1971: 4; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 3; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 1; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 0; Year commissioned (number of assets commissioned in each year) 1987: 1; Year commissioned (number of assets commissioned in each year) 1988: 0; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 0; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 1; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 1; Year commissioned (number of assets commissioned in each year) 2001: 0; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 0; Year commissioned (number of assets commissioned in each year) 2004: 0; Year commissioned (number of assets commissioned in each year) 2005: 0; Year commissioned (number of assets commissioned in each year) 2006: 0; Year commissioned (number of assets commissioned in each year) 2007: 0; Year commissioned (number of assets commissioned in each year) 2008: 0; Year commissioned (number of assets commissioned in each year) 2009: 0; Year commissioned (number of assets commissioned in each year) 2010: 0; Year commissioned (number of assets commissioned in each year) 2011: 0; Year commissioned (number of assets commissioned in each year) 2012: 0
120MVA | 50 | 7.0711 | 1 | 4339755 |  | 29 | Year commissioned (number of assets commissioned in each year) 1951: 0; Year commissioned (number of assets commissioned in each year) 1952: 0; Year commissioned (number of assets commissioned in each year) 1953: 0; Year commissioned (number of assets commissioned in each year) 1954: 0; Year commissioned (number of assets commissioned in each year) 1955: 0; Year commissioned (number of assets commissioned in each year) 1956: 0; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 0; Year commissioned (number of assets commissioned in each year) 1960: 0; Year commissioned (number of assets commissioned in each year) 1961: 0; Year commissioned (number of assets commissioned in each year) 1962: 0; Year commissioned (number of assets commissioned in each year) 1963: 1; Year commissioned (number of assets commissioned in each year) 1964: 2; Year commissioned (number of assets commissioned in each year) 1965: 0; Year commissioned (number of assets commissioned in each year) 1966: 2; Year commissioned (number of assets commissioned in each year) 1967: 2; Year commissioned (number of assets commissioned in each year) 1968: 1; Year commissioned (number of assets commissioned in each year) 1969: 4; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 2; Year commissioned (number of assets commissioned in each year) 1974: 1; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 2; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 1; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 1; Year commissioned (number of assets commissioned in each year) 1984: 0; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 0; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 0; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 0; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 0; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 0; Year commissioned (number of assets commissioned in each year) 2004: 1; Year commissioned (number of assets commissioned in each year) 2005: 1; Year commissioned (number of assets commissioned in each year) 2006: 5; Year commissioned (number of assets commissioned in each year) 2007: 0; Year commissioned (number of assets commissioned in each year) 2008: 3; Year commissioned (number of assets commissioned in each year) 2009: 0; Year commissioned (number of assets commissioned in each year) 2010: 0; Year commissioned (number of assets commissioned in each year) 2011: 0; Year commissioned (number of assets commissioned in each year) 2012: 0
60MVA | 50 | 7.0711 | 1 | 3498921 |  | 40 | Year commissioned (number of assets commissioned in each year) 1951: 0; Year commissioned (number of assets commissioned in each year) 1952: 0; Year commissioned (number of assets commissioned in each year) 1953: 0; Year commissioned (number of assets commissioned in each year) 1954: 0; Year commissioned (number of assets commissioned in each year) 1955: 0; Year commissioned (number of assets commissioned in each year) 1956: 0; Year commissioned (number of assets commissioned in each year) 1957: 2; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 0; Year commissioned (number of assets commissioned in each year) 1960: 0; Year commissioned (number of assets commissioned in each year) 1961: 0; Year commissioned (number of assets commissioned in each year) 1962: 3; Year commissioned (number of assets commissioned in each year) 1963: 0; Year commissioned (number of assets commissioned in each year) 1964: 0; Year commissioned (number of assets commissioned in each year) 1965: 0; Year commissioned (number of assets commissioned in each year) 1966: 1; Year commissioned (number of assets commissioned in each year) 1967: 1; Year commissioned (number of assets commissioned in each year) 1968: 1; Year commissioned (number of assets commissioned in each year) 1969: 2; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 2; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 1; Year commissioned (number of assets commissioned in each year) 1981: 3; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 0; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 0; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 1; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 0; Year commissioned (number of assets commissioned in each year) 1991: 1; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 1; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 3; Year commissioned (number of assets commissioned in each year) 2002: 1; Year commissioned (number of assets commissioned in each year) 2003: 3; Year commissioned (number of assets commissioned in each year) 2004: 0; Year commissioned (number of assets commissioned in each year) 2005: 1; Year commissioned (number of assets commissioned in each year) 2006: 8; Year commissioned (number of assets commissioned in each year) 2007: 0; Year commissioned (number of assets commissioned in each year) 2008: 3; Year commissioned (number of assets commissioned in each year) 2009: 0; Year commissioned (number of assets commissioned in each year) 2010: 0; Year commissioned (number of assets commissioned in each year) 2011: 2; Year commissioned (number of assets commissioned in each year) 2012: 0
Zone switchgear
11/22kV | 50 | 7.0711 | 16 | 139725 |  | 2297 | Year commissioned (number of assets commissioned in each year) 1954: 29; Year commissioned (number of assets commissioned in each year) 1955: 11; Year commissioned (number of assets commissioned in each year) 1956: 15; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 12; Year commissioned (number of assets commissioned in each year) 1960: 69; Year commissioned (number of assets commissioned in each year) 1961: 6; Year commissioned (number of assets commissioned in each year) 1962: 33; Year commissioned (number of assets commissioned in each year) 1963: 39; Year commissioned (number of assets commissioned in each year) 1964: 22; Year commissioned (number of assets commissioned in each year) 1965: 37; Year commissioned (number of assets commissioned in each year) 1966: 35; Year commissioned (number of assets commissioned in each year) 1967: 28; Year commissioned (number of assets commissioned in each year) 1968: 102; Year commissioned (number of assets commissioned in each year) 1969: 10; Year commissioned (number of assets commissioned in each year) 1970: 56; Year commissioned (number of assets commissioned in each year) 1971: 13; Year commissioned (number of assets commissioned in each year) 1972: 37; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 30; Year commissioned (number of assets commissioned in each year) 1976: 29; Year commissioned (number of assets commissioned in each year) 1977: 3; Year commissioned (number of assets commissioned in each year) 1978: 8; Year commissioned (number of assets commissioned in each year) 1979: 5; Year commissioned (number of assets commissioned in each year) 1980: 12; Year commissioned (number of assets commissioned in each year) 1981: 52; Year commissioned (number of assets commissioned in each year) 1982: 86; Year commissioned (number of assets commissioned in each year) 1983: 81; Year commissioned (number of assets commissioned in each year) 1984: 118; Year commissioned (number of assets commissioned in each year) 1985: 40; Year commissioned (number of assets commissioned in each year) 1986: 40; Year commissioned (number of assets commissioned in each year) 1987: 14; Year commissioned (number of assets commissioned in each year) 1988: 40; Year commissioned (number of assets commissioned in each year) 1989: 39; Year commissioned (number of assets commissioned in each year) 1990: 26; Year commissioned (number of assets commissioned in each year) 1991: 23; Year commissioned (number of assets commissioned in each year) 1992: 6; Year commissioned (number of assets commissioned in each year) 1993: 12; Year commissioned (number of assets commissioned in each year) 1994: 24; Year commissioned (number of assets commissioned in each year) 1995: 8; Year commissioned (number of assets commissioned in each year) 1996: 7; Year commissioned (number of assets commissioned in each year) 1997: 6; Year commissioned (number of assets commissioned in each year) 1998: 41; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 31; Year commissioned (number of assets commissioned in each year) 2001: 59; Year commissioned (number of assets commissioned in each year) 2002: 56; Year commissioned (number of assets commissioned in each year) 2003: 82; Year commissioned (number of assets commissioned in each year) 2004: 36; Year commissioned (number of assets commissioned in each year) 2005: 98; Year commissioned (number of assets commissioned in each year) 2006: 82; Year commissioned (number of assets commissioned in each year) 2007: 107; Year commissioned (number of assets commissioned in each year) 2008: 93; Year commissioned (number of assets commissioned in each year) 2009: 71; Year commissioned (number of assets commissioned in each year) 2010: 82; Year commissioned (number of assets commissioned in each year) 2011: 109; Year commissioned (number of assets commissioned in each year) 2012: 87
132kV | 50 | 7.0711 | 6 | 207000 |  | 297 | Year commissioned (number of assets commissioned in each year) 1954: 0; Year commissioned (number of assets commissioned in each year) 1955: 0; Year commissioned (number of assets commissioned in each year) 1956: 3; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 0; Year commissioned (number of assets commissioned in each year) 1960: 0; Year commissioned (number of assets commissioned in each year) 1961: 0; Year commissioned (number of assets commissioned in each year) 1962: 0; Year commissioned (number of assets commissioned in each year) 1963: 0; Year commissioned (number of assets commissioned in each year) 1964: 0; Year commissioned (number of assets commissioned in each year) 1965: 0; Year commissioned (number of assets commissioned in each year) 1966: 0; Year commissioned (number of assets commissioned in each year) 1967: 0; Year commissioned (number of assets commissioned in each year) 1968: 0; Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 0; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 6; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 1; Year commissioned (number of assets commissioned in each year) 1989: 4; Year commissioned (number of assets commissioned in each year) 1990: 37; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 3; Year commissioned (number of assets commissioned in each year) 1995: 2; Year commissioned (number of assets commissioned in each year) 1996: 4; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 9; Year commissioned (number of assets commissioned in each year) 1999: 11; Year commissioned (number of assets commissioned in each year) 2000: 13; Year commissioned (number of assets commissioned in each year) 2001: 4; Year commissioned (number of assets commissioned in each year) 2002: 1; Year commissioned (number of assets commissioned in each year) 2003: 8; Year commissioned (number of assets commissioned in each year) 2004: 11; Year commissioned (number of assets commissioned in each year) 2005: 22; Year commissioned (number of assets commissioned in each year) 2006: 7; Year commissioned (number of assets commissioned in each year) 2007: 35; Year commissioned (number of assets commissioned in each year) 2008: 40; Year commissioned (number of assets commissioned in each year) 2009: 10; Year commissioned (number of assets commissioned in each year) 2010: 25; Year commissioned (number of assets commissioned in each year) 2011: 16; Year commissioned (number of assets commissioned in each year) 2012: 25
33kV | 50 | 7.0711 | 17 | 146970 |  | 877 | Year commissioned (number of assets commissioned in each year) 1954: 0; Year commissioned (number of assets commissioned in each year) 1955: 1; Year commissioned (number of assets commissioned in each year) 1956: 0; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 4; Year commissioned (number of assets commissioned in each year) 1960: 5; Year commissioned (number of assets commissioned in each year) 1961: 9; Year commissioned (number of assets commissioned in each year) 1962: 4; Year commissioned (number of assets commissioned in each year) 1963: 7; Year commissioned (number of assets commissioned in each year) 1964: 5; Year commissioned (number of assets commissioned in each year) 1965: 1; Year commissioned (number of assets commissioned in each year) 1966: 6; Year commissioned (number of assets commissioned in each year) 1967: 7; Year commissioned (number of assets commissioned in each year) 1968: 19; Year commissioned (number of assets commissioned in each year) 1969: 28; Year commissioned (number of assets commissioned in each year) 1970: 3; Year commissioned (number of assets commissioned in each year) 1971: 14; Year commissioned (number of assets commissioned in each year) 1972: 6; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 5; Year commissioned (number of assets commissioned in each year) 1975: 2; Year commissioned (number of assets commissioned in each year) 1976: 3; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 15; Year commissioned (number of assets commissioned in each year) 1979: 5; Year commissioned (number of assets commissioned in each year) 1980: 15; Year commissioned (number of assets commissioned in each year) 1981: 24; Year commissioned (number of assets commissioned in each year) 1982: 31; Year commissioned (number of assets commissioned in each year) 1983: 27; Year commissioned (number of assets commissioned in each year) 1984: 40; Year commissioned (number of assets commissioned in each year) 1985: 9; Year commissioned (number of assets commissioned in each year) 1986: 1; Year commissioned (number of assets commissioned in each year) 1987: 2; Year commissioned (number of assets commissioned in each year) 1988: 1; Year commissioned (number of assets commissioned in each year) 1989: 8; Year commissioned (number of assets commissioned in each year) 1990: 126; Year commissioned (number of assets commissioned in each year) 1991: 7; Year commissioned (number of assets commissioned in each year) 1992: 1; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 17; Year commissioned (number of assets commissioned in each year) 1995: 2; Year commissioned (number of assets commissioned in each year) 1996: 30; Year commissioned (number of assets commissioned in each year) 1997: 4; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 6; Year commissioned (number of assets commissioned in each year) 2000: 3; Year commissioned (number of assets commissioned in each year) 2001: 12; Year commissioned (number of assets commissioned in each year) 2002: 6; Year commissioned (number of assets commissioned in each year) 2003: 22; Year commissioned (number of assets commissioned in each year) 2004: 32; Year commissioned (number of assets commissioned in each year) 2005: 21; Year commissioned (number of assets commissioned in each year) 2006: 25; Year commissioned (number of assets commissioned in each year) 2007: 37; Year commissioned (number of assets commissioned in each year) 2008: 47; Year commissioned (number of assets commissioned in each year) 2009: 39; Year commissioned (number of assets commissioned in each year) 2010: 40; Year commissioned (number of assets commissioned in each year) 2011: 62; Year commissioned (number of assets commissioned in each year) 2012: 31
66kV | 50 | 7.0711 | 10 | 159390 |  | 179 | Year commissioned (number of assets commissioned in each year) 1954: 0; Year commissioned (number of assets commissioned in each year) 1955: 0; Year commissioned (number of assets commissioned in each year) 1956: 4; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 0; Year commissioned (number of assets commissioned in each year) 1960: 4; Year commissioned (number of assets commissioned in each year) 1961: 0; Year commissioned (number of assets commissioned in each year) 1962: 0; Year commissioned (number of assets commissioned in each year) 1963: 0; Year commissioned (number of assets commissioned in each year) 1964: 0; Year commissioned (number of assets commissioned in each year) 1965: 0; Year commissioned (number of assets commissioned in each year) 1966: 2; Year commissioned (number of assets commissioned in each year) 1967: 0; Year commissioned (number of assets commissioned in each year) 1968: 0; Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 9; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 2; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 1; Year commissioned (number of assets commissioned in each year) 1981: 7; Year commissioned (number of assets commissioned in each year) 1982: 2; Year commissioned (number of assets commissioned in each year) 1983: 1; Year commissioned (number of assets commissioned in each year) 1984: 5; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 6; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 5; Year commissioned (number of assets commissioned in each year) 1989: 4; Year commissioned (number of assets commissioned in each year) 1990: 7; Year commissioned (number of assets commissioned in each year) 1991: 5; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 2; Year commissioned (number of assets commissioned in each year) 1996: 4; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 1; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 5; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 8; Year commissioned (number of assets commissioned in each year) 2004: 0; Year commissioned (number of assets commissioned in each year) 2005: 5; Year commissioned (number of assets commissioned in each year) 2006: 11; Year commissioned (number of assets commissioned in each year) 2007: 12; Year commissioned (number of assets commissioned in each year) 2008: 9; Year commissioned (number of assets commissioned in each year) 2009: 27; Year commissioned (number of assets commissioned in each year) 2010: 2; Year commissioned (number of assets commissioned in each year) 2011: 22; Year commissioned (number of assets commissioned in each year) 2012: 7
Zone 'other assets'
Capacitor Bank, 11kV | 50 | 7.0711 | 0 | 330770 |  | 113 | Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 0; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 0; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 0; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 0; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 0; Year commissioned (number of assets commissioned in each year) 2002: 28; Year commissioned (number of assets commissioned in each year) 2003: 55; Year commissioned (number of assets commissioned in each year) 2004: 15; Year commissioned (number of assets commissioned in each year) 2005: 0; Year commissioned (number of assets commissioned in each year) 2006: 1; Year commissioned (number of assets commissioned in each year) 2007: 2; Year commissioned (number of assets commissioned in each year) 2008: 2; Year commissioned (number of assets commissioned in each year) 2009: 0; Year commissioned (number of assets commissioned in each year) 2010: 3; Year commissioned (number of assets commissioned in each year) 2011: 6; Year commissioned (number of assets commissioned in each year) 2012: 1
Capacitor Bank, 132kV | 50 | 7.0711 | 0 | 983250 |  | 2 | Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 0; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 0; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 0; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 0; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 0; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 0; Year commissioned (number of assets commissioned in each year) 2004: 0; Year commissioned (number of assets commissioned in each year) 2005: 0; Year commissioned (number of assets commissioned in each year) 2006: 0; Year commissioned (number of assets commissioned in each year) 2007: 0; Year commissioned (number of assets commissioned in each year) 2008: 0; Year commissioned (number of assets commissioned in each year) 2009: 1; Year commissioned (number of assets commissioned in each year) 2010: 0; Year commissioned (number of assets commissioned in each year) 2011: 1; Year commissioned (number of assets commissioned in each year) 2012: 0
Capacitor Bank, 33kV | 50 | 7.0711 | 0 | 589950 |  | 37 | Year commissioned (number of assets commissioned in each year) 1969: 2; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 2; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 2; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 0; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 0; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 22; Year commissioned (number of assets commissioned in each year) 1991: 2; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 1; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 2; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 0; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 0; Year commissioned (number of assets commissioned in each year) 2004: 0; Year commissioned (number of assets commissioned in each year) 2005: 0; Year commissioned (number of assets commissioned in each year) 2006: 0; Year commissioned (number of assets commissioned in each year) 2007: 0; Year commissioned (number of assets commissioned in each year) 2008: 0; Year commissioned (number of assets commissioned in each year) 2009: 2; Year commissioned (number of assets commissioned in each year) 2010: 0; Year commissioned (number of assets commissioned in each year) 2011: 2; Year commissioned (number of assets commissioned in each year) 2012: 0
Capacitor Bank, 66kV | 50 | 7.0711 | 0 | 639630 |  | 5 | Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 1; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 0; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 0; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 0; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 2; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 0; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 0; Year commissioned (number of assets commissioned in each year) 2004: 0; Year commissioned (number of assets commissioned in each year) 2005: 0; Year commissioned (number of assets commissioned in each year) 2006: 0; Year commissioned (number of assets commissioned in each year) 2007: 0; Year commissioned (number of assets commissioned in each year) 2008: 2; Year commissioned (number of assets commissioned in each year) 2009: 0; Year commissioned (number of assets commissioned in each year) 2010: 0; Year commissioned (number of assets commissioned in each year) 2011: 0; Year commissioned (number of assets commissioned in each year) 2012: 0
Substation Establishment: Major Indoor | 50 | 7.0711 |  | 15525000 |  | 9 | Year commissioned (number of assets commissioned in each year) 1954: 0; Year commissioned (number of assets commissioned in each year) 1955: 0; Year commissioned (number of assets commissioned in each year) 1956: 0; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 0; Year commissioned (number of assets commissioned in each year) 1960: 0; Year commissioned (number of assets commissioned in each year) 1961: 0; Year commissioned (number of assets commissioned in each year) 1962: 0; Year commissioned (number of assets commissioned in each year) 1963: 0; Year commissioned (number of assets commissioned in each year) 1964: 0; Year commissioned (number of assets commissioned in each year) 1965: 0; Year commissioned (number of assets commissioned in each year) 1966: 1; Year commissioned (number of assets commissioned in each year) 1967: 0; Year commissioned (number of assets commissioned in each year) 1968: 0; Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 1; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 1; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 1; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 0; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 1; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 0; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 1; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 0; Year commissioned (number of assets commissioned in each year) 2004: 0; Year commissioned (number of assets commissioned in each year) 2005: 0; Year commissioned (number of assets commissioned in each year) 2006: 0; Year commissioned (number of assets commissioned in each year) 2007: 2; Year commissioned (number of assets commissioned in each year) 2008: 0; Year commissioned (number of assets commissioned in each year) 2009: 0; Year commissioned (number of assets commissioned in each year) 2010: 1; Year commissioned (number of assets commissioned in each year) 2011: 0; Year commissioned (number of assets commissioned in each year) 2012: 0
Substation Establishment: Major Outdoor | 50 | 7.0711 |  | 15525000 |  | 58 | Year commissioned (number of assets commissioned in each year) 1954: 0; Year commissioned (number of assets commissioned in each year) 1955: 0; Year commissioned (number of assets commissioned in each year) 1956: 1; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 1; Year commissioned (number of assets commissioned in each year) 1960: 0; Year commissioned (number of assets commissioned in each year) 1961: 3; Year commissioned (number of assets commissioned in each year) 1962: 0; Year commissioned (number of assets commissioned in each year) 1963: 1; Year commissioned (number of assets commissioned in each year) 1964: 3; Year commissioned (number of assets commissioned in each year) 1965: 3; Year commissioned (number of assets commissioned in each year) 1966: 3; Year commissioned (number of assets commissioned in each year) 1967: 3; Year commissioned (number of assets commissioned in each year) 1968: 4; Year commissioned (number of assets commissioned in each year) 1969: 2; Year commissioned (number of assets commissioned in each year) 1970: 2; Year commissioned (number of assets commissioned in each year) 1971: 2; Year commissioned (number of assets commissioned in each year) 1972: 3; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 3; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 2; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 1; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 1; Year commissioned (number of assets commissioned in each year) 1983: 1; Year commissioned (number of assets commissioned in each year) 1984: 1; Year commissioned (number of assets commissioned in each year) 1985: 1; Year commissioned (number of assets commissioned in each year) 1986: 1; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 1; Year commissioned (number of assets commissioned in each year) 1989: 1; Year commissioned (number of assets commissioned in each year) 1990: 1; Year commissioned (number of assets commissioned in each year) 1991: 1; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 2; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 1; Year commissioned (number of assets commissioned in each year) 2001: 1; Year commissioned (number of assets commissioned in each year) 2002: 1; Year commissioned (number of assets commissioned in each year) 2003: 0; Year commissioned (number of assets commissioned in each year) 2004: 0; Year commissioned (number of assets commissioned in each year) 2005: 1; Year commissioned (number of assets commissioned in each year) 2006: 1; Year commissioned (number of assets commissioned in each year) 2007: 0; Year commissioned (number of assets commissioned in each year) 2008: 2; Year commissioned (number of assets commissioned in each year) 2009: 2; Year commissioned (number of assets commissioned in each year) 2010: 1; Year commissioned (number of assets commissioned in each year) 2011: 0; Year commissioned (number of assets commissioned in each year) 2012: 0
Substation Establishment: Medium Indoor | 50 | 7.0711 |  | 11385000 |  | 19 | Year commissioned (number of assets commissioned in each year) 1954: 1; Year commissioned (number of assets commissioned in each year) 1955: 0; Year commissioned (number of assets commissioned in each year) 1956: 0; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 0; Year commissioned (number of assets commissioned in each year) 1960: 0; Year commissioned (number of assets commissioned in each year) 1961: 0; Year commissioned (number of assets commissioned in each year) 1962: 0; Year commissioned (number of assets commissioned in each year) 1963: 0; Year commissioned (number of assets commissioned in each year) 1964: 1; Year commissioned (number of assets commissioned in each year) 1965: 0; Year commissioned (number of assets commissioned in each year) 1966: 0; Year commissioned (number of assets commissioned in each year) 1967: 0; Year commissioned (number of assets commissioned in each year) 1968: 0; Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 1; Year commissioned (number of assets commissioned in each year) 1979: 1; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 3; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 0; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 0; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 1; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 0; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 2; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 0; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 0; Year commissioned (number of assets commissioned in each year) 2004: 1; Year commissioned (number of assets commissioned in each year) 2005: 0; Year commissioned (number of assets commissioned in each year) 2006: 0; Year commissioned (number of assets commissioned in each year) 2007: 0; Year commissioned (number of assets commissioned in each year) 2008: 2; Year commissioned (number of assets commissioned in each year) 2009: 1; Year commissioned (number of assets commissioned in each year) 2010: 0; Year commissioned (number of assets commissioned in each year) 2011: 0; Year commissioned (number of assets commissioned in each year) 2012: 5
Substation Establishment: Medium Outdoor | 50 | 7.0711 |  | 11385000 |  | 49 | Year commissioned (number of assets commissioned in each year) 1954: 0; Year commissioned (number of assets commissioned in each year) 1955: 0; Year commissioned (number of assets commissioned in each year) 1956: 0; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 0; Year commissioned (number of assets commissioned in each year) 1960: 1; Year commissioned (number of assets commissioned in each year) 1961: 0; Year commissioned (number of assets commissioned in each year) 1962: 2; Year commissioned (number of assets commissioned in each year) 1963: 2; Year commissioned (number of assets commissioned in each year) 1964: 0; Year commissioned (number of assets commissioned in each year) 1965: 2; Year commissioned (number of assets commissioned in each year) 1966: 2; Year commissioned (number of assets commissioned in each year) 1967: 2; Year commissioned (number of assets commissioned in each year) 1968: 1; Year commissioned (number of assets commissioned in each year) 1969: 3; Year commissioned (number of assets commissioned in each year) 1970: 1; Year commissioned (number of assets commissioned in each year) 1971: 3; Year commissioned (number of assets commissioned in each year) 1972: 3; Year commissioned (number of assets commissioned in each year) 1973: 2; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 1; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 1; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 1; Year commissioned (number of assets commissioned in each year) 1981: 1; Year commissioned (number of assets commissioned in each year) 1982: 1; Year commissioned (number of assets commissioned in each year) 1983: 3; Year commissioned (number of assets commissioned in each year) 1984: 1; Year commissioned (number of assets commissioned in each year) 1985: 1; Year commissioned (number of assets commissioned in each year) 1986: 2; Year commissioned (number of assets commissioned in each year) 1987: 1; Year commissioned (number of assets commissioned in each year) 1988: 0; Year commissioned (number of assets commissioned in each year) 1989: 2; Year commissioned (number of assets commissioned in each year) 1990: 0; Year commissioned (number of assets commissioned in each year) 1991: 2; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 1; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 1; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 0; Year commissioned (number of assets commissioned in each year) 2002: 1; Year commissioned (number of assets commissioned in each year) 2003: 1; Year commissioned (number of assets commissioned in each year) 2004: 0; Year commissioned (number of assets commissioned in each year) 2005: 0; Year commissioned (number of assets commissioned in each year) 2006: 0; Year commissioned (number of assets commissioned in each year) 2007: 1; Year commissioned (number of assets commissioned in each year) 2008: 0; Year commissioned (number of assets commissioned in each year) 2009: 0; Year commissioned (number of assets commissioned in each year) 2010: 1; Year commissioned (number of assets commissioned in each year) 2011: 0; Year commissioned (number of assets commissioned in each year) 2012: 2
Substation Establishment: Small Indoor | 50 | 7.0711 |  | 7245000 |  | 4 | Year commissioned (number of assets commissioned in each year) 1954: 0; Year commissioned (number of assets commissioned in each year) 1955: 0; Year commissioned (number of assets commissioned in each year) 1956: 0; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 0; Year commissioned (number of assets commissioned in each year) 1960: 0; Year commissioned (number of assets commissioned in each year) 1961: 1; Year commissioned (number of assets commissioned in each year) 1962: 0; Year commissioned (number of assets commissioned in each year) 1963: 0; Year commissioned (number of assets commissioned in each year) 1964: 0; Year commissioned (number of assets commissioned in each year) 1965: 0; Year commissioned (number of assets commissioned in each year) 1966: 0; Year commissioned (number of assets commissioned in each year) 1967: 0; Year commissioned (number of assets commissioned in each year) 1968: 0; Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 1; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 0; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 0; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 0; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 0; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 1; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 0; Year commissioned (number of assets commissioned in each year) 2004: 0; Year commissioned (number of assets commissioned in each year) 2005: 0; Year commissioned (number of assets commissioned in each year) 2006: 0; Year commissioned (number of assets commissioned in each year) 2007: 0; Year commissioned (number of assets commissioned in each year) 2008: 1; Year commissioned (number of assets commissioned in each year) 2009: 0; Year commissioned (number of assets commissioned in each year) 2010: 0; Year commissioned (number of assets commissioned in each year) 2011: 0; Year commissioned (number of assets commissioned in each year) 2012: 0
Substation Establishment: Small Outdoor | 50 | 7.0711 |  | 7245000 |  | 20 | Year commissioned (number of assets commissioned in each year) 1954: 0; Year commissioned (number of assets commissioned in each year) 1955: 0; Year commissioned (number of assets commissioned in each year) 1956: 0; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 0; Year commissioned (number of assets commissioned in each year) 1960: 1; Year commissioned (number of assets commissioned in each year) 1961: 0; Year commissioned (number of assets commissioned in each year) 1962: 0; Year commissioned (number of assets commissioned in each year) 1963: 0; Year commissioned (number of assets commissioned in each year) 1964: 1; Year commissioned (number of assets commissioned in each year) 1965: 2; Year commissioned (number of assets commissioned in each year) 1966: 0; Year commissioned (number of assets commissioned in each year) 1967: 0; Year commissioned (number of assets commissioned in each year) 1968: 2; Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 1; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 2; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 2; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 0; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 0; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 0; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 0; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 1; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 1; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 1; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 0; Year commissioned (number of assets commissioned in each year) 2002: 2; Year commissioned (number of assets commissioned in each year) 2003: 1; Year commissioned (number of assets commissioned in each year) 2004: 1; Year commissioned (number of assets commissioned in each year) 2005: 0; Year commissioned (number of assets commissioned in each year) 2006: 0; Year commissioned (number of assets commissioned in each year) 2007: 0; Year commissioned (number of assets commissioned in each year) 2008: 0; Year commissioned (number of assets commissioned in each year) 2009: 1; Year commissioned (number of assets commissioned in each year) 2010: 1; Year commissioned (number of assets commissioned in each year) 2011: 0; Year commissioned (number of assets commissioned in each year) 2012: 0
Substation Establishment: Type A | 50 | 7.0711 |  | 17595000 |  | 7 | Year commissioned (number of assets commissioned in each year) 1954: 0; Year commissioned (number of assets commissioned in each year) 1955: 0; Year commissioned (number of assets commissioned in each year) 1956: 1; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 0; Year commissioned (number of assets commissioned in each year) 1960: 0; Year commissioned (number of assets commissioned in each year) 1961: 0; Year commissioned (number of assets commissioned in each year) 1962: 0; Year commissioned (number of assets commissioned in each year) 1963: 0; Year commissioned (number of assets commissioned in each year) 1964: 0; Year commissioned (number of assets commissioned in each year) 1965: 0; Year commissioned (number of assets commissioned in each year) 1966: 0; Year commissioned (number of assets commissioned in each year) 1967: 0; Year commissioned (number of assets commissioned in each year) 1968: 0; Year commissioned (number of assets commissioned in each year) 1969: 1; Year commissioned (number of assets commissioned in each year) 1970: 0; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 0; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 0; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 1; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 0; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 1; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 0; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 0; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 1; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 0; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 0; Year commissioned (number of assets commissioned in each year) 2004: 0; Year commissioned (number of assets commissioned in each year) 2005: 0; Year commissioned (number of assets commissioned in each year) 2006: 0; Year commissioned (number of assets commissioned in each year) 2007: 0; Year commissioned (number of assets commissioned in each year) 2008: 1; Year commissioned (number of assets commissioned in each year) 2009: 0; Year commissioned (number of assets commissioned in each year) 2010: 0; Year commissioned (number of assets commissioned in each year) 2011: 0; Year commissioned (number of assets commissioned in each year) 2012: 1
Substation Establishment: Type B | 50 | 7.0711 |  | 28980000 |  | 15 | Year commissioned (number of assets commissioned in each year) 1954: 0; Year commissioned (number of assets commissioned in each year) 1955: 0; Year commissioned (number of assets commissioned in each year) 1956: 1; Year commissioned (number of assets commissioned in each year) 1957: 0; Year commissioned (number of assets commissioned in each year) 1958: 0; Year commissioned (number of assets commissioned in each year) 1959: 1; Year commissioned (number of assets commissioned in each year) 1960: 0; Year commissioned (number of assets commissioned in each year) 1961: 1; Year commissioned (number of assets commissioned in each year) 1962: 0; Year commissioned (number of assets commissioned in each year) 1963: 1; Year commissioned (number of assets commissioned in each year) 1964: 2; Year commissioned (number of assets commissioned in each year) 1965: 2; Year commissioned (number of assets commissioned in each year) 1966: 0; Year commissioned (number of assets commissioned in each year) 1967: 1; Year commissioned (number of assets commissioned in each year) 1968: 1; Year commissioned (number of assets commissioned in each year) 1969: 0; Year commissioned (number of assets commissioned in each year) 1970: 2; Year commissioned (number of assets commissioned in each year) 1971: 0; Year commissioned (number of assets commissioned in each year) 1972: 1; Year commissioned (number of assets commissioned in each year) 1973: 0; Year commissioned (number of assets commissioned in each year) 1974: 0; Year commissioned (number of assets commissioned in each year) 1975: 0; Year commissioned (number of assets commissioned in each year) 1976: 1; Year commissioned (number of assets commissioned in each year) 1977: 0; Year commissioned (number of assets commissioned in each year) 1978: 0; Year commissioned (number of assets commissioned in each year) 1979: 0; Year commissioned (number of assets commissioned in each year) 1980: 0; Year commissioned (number of assets commissioned in each year) 1981: 0; Year commissioned (number of assets commissioned in each year) 1982: 0; Year commissioned (number of assets commissioned in each year) 1983: 0; Year commissioned (number of assets commissioned in each year) 1984: 0; Year commissioned (number of assets commissioned in each year) 1985: 0; Year commissioned (number of assets commissioned in each year) 1986: 0; Year commissioned (number of assets commissioned in each year) 1987: 0; Year commissioned (number of assets commissioned in each year) 1988: 0; Year commissioned (number of assets commissioned in each year) 1989: 0; Year commissioned (number of assets commissioned in each year) 1990: 0; Year commissioned (number of assets commissioned in each year) 1991: 0; Year commissioned (number of assets commissioned in each year) 1992: 0; Year commissioned (number of assets commissioned in each year) 1993: 0; Year commissioned (number of assets commissioned in each year) 1994: 0; Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 0; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 0; Year commissioned (number of assets commissioned in each year) 2004: 0; Year commissioned (number of assets commissioned in each year) 2005: 0; Year commissioned (number of assets commissioned in each year) 2006: 0; Year commissioned (number of assets commissioned in each year) 2007: 0; Year commissioned (number of assets commissioned in each year) 2008: 1; Year commissioned (number of assets commissioned in each year) 2009: 0; Year commissioned (number of assets commissioned in each year) 2010: 0; Year commissioned (number of assets commissioned in each year) 2011: 0; Year commissioned (number of assets commissioned in each year) 2012: 0
SCADA and protection
GRN Radios | 10 | 3.1623 |  | 2484 |  | 745 | Year commissioned (number of assets commissioned in each year) 2006: 450; Year commissioned (number of assets commissioned in each year) 2008: 78; Year commissioned (number of assets commissioned in each year) 2009: 38; Year commissioned (number of assets commissioned in each year) 2010: 126; Year commissioned (number of assets commissioned in each year) 2011: 53
Microwave Civil Works | 40 | 6.3246 |  | 49163 |  | 24 | Year commissioned (number of assets commissioned in each year) 1984: 2; Year commissioned (number of assets commissioned in each year) 1987: 1; Year commissioned (number of assets commissioned in each year) 1992: 1; Year commissioned (number of assets commissioned in each year) 1993: 2; Year commissioned (number of assets commissioned in each year) 1994: 2; Year commissioned (number of assets commissioned in each year) 1996: 1; Year commissioned (number of assets commissioned in each year) 1997: 2; Year commissioned (number of assets commissioned in each year) 2001: 1; Year commissioned (number of assets commissioned in each year) 2002: 2; Year commissioned (number of assets commissioned in each year) 2003: 2; Year commissioned (number of assets commissioned in each year) 2004: 1; Year commissioned (number of assets commissioned in each year) 2006: 2; Year commissioned (number of assets commissioned in each year) 2007: 2; Year commissioned (number of assets commissioned in each year) 2008: 2; Year commissioned (number of assets commissioned in each year) 2009: 1
Microwave Equipment | 15 | 3.873 |  | 98325 |  | 44 | Year commissioned (number of assets commissioned in each year) 2002: 7; Year commissioned (number of assets commissioned in each year) 2003: 3; Year commissioned (number of assets commissioned in each year) 2004: 2; Year commissioned (number of assets commissioned in each year) 2005: 6; Year commissioned (number of assets commissioned in each year) 2006: 2; Year commissioned (number of assets commissioned in each year) 2007: 4; Year commissioned (number of assets commissioned in each year) 2008: 7; Year commissioned (number of assets commissioned in each year) 2009: 7; Year commissioned (number of assets commissioned in each year) 2010: 4; Year commissioned (number of assets commissioned in each year) 2011: 2
Microwave Towers | 50 | 7.0711 |  | 49163 |  | 27 | Year commissioned (number of assets commissioned in each year) 1984: 2; Year commissioned (number of assets commissioned in each year) 1987: 1; Year commissioned (number of assets commissioned in each year) 1992: 1; Year commissioned (number of assets commissioned in each year) 1993: 2; Year commissioned (number of assets commissioned in each year) 1994: 2; Year commissioned (number of assets commissioned in each year) 1996: 1; Year commissioned (number of assets commissioned in each year) 1997: 2; Year commissioned (number of assets commissioned in each year) 2001: 1; Year commissioned (number of assets commissioned in each year) 2002: 2; Year commissioned (number of assets commissioned in each year) 2003: 2; Year commissioned (number of assets commissioned in each year) 2004: 1; Year commissioned (number of assets commissioned in each year) 2006: 2; Year commissioned (number of assets commissioned in each year) 2007: 2; Year commissioned (number of assets commissioned in each year) 2008: 2; Year commissioned (number of assets commissioned in each year) 2009: 2; Year commissioned (number of assets commissioned in each year) 2010: 2
Pilot Cables | 45 | 6.7082 |  | 103500 |  | 779.88 | [40 empty] | 0 | 0 | 0 | 0 | 0 | 4.17 | 31.57 | 11.42 | 10 | 0 | 23.88 | 22.42 | 0 | 32.02 | 63.32 | 59.95 | 54.48 | 9.79 | 37.47 | 59.22 | 58.07 | 53.73 | 30.07 | 8.76 | 4.9 | 16.4 | 30 | 1.2 | 27.17 | 40.25 | 0 | 14.44 | 35.92 | 0 | 3.44 | 0 | 1.4 | 2.57 | 0.08 | 1.8 | 0.2 | 23.03 | 0 | 0 | 6.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Reclosers | 10 | 3.1623 |  | 4916 |  | 371 | Year commissioned (number of assets commissioned in each year) 2003: 7; Year commissioned (number of assets commissioned in each year) 2004: 135; Year commissioned (number of assets commissioned in each year) 2005: 47; Year commissioned (number of assets commissioned in each year) 2006: 25; Year commissioned (number of assets commissioned in each year) 2007: 38; Year commissioned (number of assets commissioned in each year) 2008: 32; Year commissioned (number of assets commissioned in each year) 2009: 3; Year commissioned (number of assets commissioned in each year) 2010: 44; Year commissioned (number of assets commissioned in each year) 2011: 40
Repeaters | 10 | 3.1623 |  | 14801 |  | 36 | Year commissioned (number of assets commissioned in each year) 2004: 1; Year commissioned (number of assets commissioned in each year) 2005: 7; Year commissioned (number of assets commissioned in each year) 2006: 5; Year commissioned (number of assets commissioned in each year) 2007: 8; Year commissioned (number of assets commissioned in each year) 2008: 8; Year commissioned (number of assets commissioned in each year) 2009: 4; Year commissioned (number of assets commissioned in each year) 2010: 3
SCADA Sub sites | 10 | 3.1623 |  | 324990 |  | 228 | Year commissioned (number of assets commissioned in each year) 1980: 3; Year commissioned (number of assets commissioned in each year) 1989: 1; Year commissioned (number of assets commissioned in each year) 1990: 4; Year commissioned (number of assets commissioned in each year) 1992: 1; Year commissioned (number of assets commissioned in each year) 1993: 3; Year commissioned (number of assets commissioned in each year) 1994: 4; Year commissioned (number of assets commissioned in each year) 1995: 4; Year commissioned (number of assets commissioned in each year) 1996: 4; Year commissioned (number of assets commissioned in each year) 1997: 1; Year commissioned (number of assets commissioned in each year) 1999: 4; Year commissioned (number of assets commissioned in each year) 2000: 9; Year commissioned (number of assets commissioned in each year) 2001: 13; Year commissioned (number of assets commissioned in each year) 2002: 15; Year commissioned (number of assets commissioned in each year) 2003: 50; Year commissioned (number of assets commissioned in each year) 2004: 19; Year commissioned (number of assets commissioned in each year) 2005: 15; Year commissioned (number of assets commissioned in each year) 2006: 12; Year commissioned (number of assets commissioned in each year) 2007: 8; Year commissioned (number of assets commissioned in each year) 2008: 10; Year commissioned (number of assets commissioned in each year) 2009: 12; Year commissioned (number of assets commissioned in each year) 2010: 12; Year commissioned (number of assets commissioned in each year) 2011: 12; Year commissioned (number of assets commissioned in each year) 2012: 12
Other
33kV Air Break Switch | 35 | 5.9161 |  | 20700 |  | 108 | Year commissioned (number of assets commissioned in each year) 1995: 6; Year commissioned (number of assets commissioned in each year) 1996: 6; Year commissioned (number of assets commissioned in each year) 1997: 7; Year commissioned (number of assets commissioned in each year) 1998: 7; Year commissioned (number of assets commissioned in each year) 1999: 7; Year commissioned (number of assets commissioned in each year) 2000: 7; Year commissioned (number of assets commissioned in each year) 2001: 7; Year commissioned (number of assets commissioned in each year) 2002: 7; Year commissioned (number of assets commissioned in each year) 2003: 7; Year commissioned (number of assets commissioned in each year) 2004: 7; Year commissioned (number of assets commissioned in each year) 2005: 7; Year commissioned (number of assets commissioned in each year) 2006: 7; Year commissioned (number of assets commissioned in each year) 2007: 7; Year commissioned (number of assets commissioned in each year) 2008: 7; Year commissioned (number of assets commissioned in each year) 2009: 2; Year commissioned (number of assets commissioned in each year) 2010: 3; Year commissioned (number of assets commissioned in each year) 2011: 4; Year commissioned (number of assets commissioned in each year) 2012: 3
33kV Drop Out Fuse | 35 | 5.9161 |  | 14490 |  | 4 | Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 0; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 1; Year commissioned (number of assets commissioned in each year) 2004: 1; Year commissioned (number of assets commissioned in each year) 2005: 0; Year commissioned (number of assets commissioned in each year) 2006: 1; Year commissioned (number of assets commissioned in each year) 2007: 0; Year commissioned (number of assets commissioned in each year) 2008: 1; Year commissioned (number of assets commissioned in each year) 2009: 0; Year commissioned (number of assets commissioned in each year) 2010: 0
33kV Under Slung Link | 35 | 5.9161 |  | 10350 |  | 27 | Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 0; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 0; Year commissioned (number of assets commissioned in each year) 2004: 2; Year commissioned (number of assets commissioned in each year) 2005: 7; Year commissioned (number of assets commissioned in each year) 2006: 5; Year commissioned (number of assets commissioned in each year) 2007: 6; Year commissioned (number of assets commissioned in each year) 2008: 7; Year commissioned (number of assets commissioned in each year) 2009: 0; Year commissioned (number of assets commissioned in each year) 2010: 0
66kV Air Break Switch | 35 | 5.9161 |  | 23288 |  | 35 | Year commissioned (number of assets commissioned in each year) 1995: 0; Year commissioned (number of assets commissioned in each year) 1996: 0; Year commissioned (number of assets commissioned in each year) 1997: 0; Year commissioned (number of assets commissioned in each year) 1998: 0; Year commissioned (number of assets commissioned in each year) 1999: 0; Year commissioned (number of assets commissioned in each year) 2000: 0; Year commissioned (number of assets commissioned in each year) 2001: 0; Year commissioned (number of assets commissioned in each year) 2002: 0; Year commissioned (number of assets commissioned in each year) 2003: 6; Year commissioned (number of assets commissioned in each year) 2004: 6; Year commissioned (number of assets commissioned in each year) 2005: 5; Year commissioned (number of assets commissioned in each year) 2006: 5; Year commissioned (number of assets commissioned in each year) 2007: 6; Year commissioned (number of assets commissioned in each year) 2008: 6; Year commissioned (number of assets commissioned in each year) 2009: 0; Year commissioned (number of assets commissioned in each year) 2010: 0; Year commissioned (number of assets commissioned in each year) 2012: 1
Towers | 60 | 7.746 |  | 64170 |  | 889 | Year commissioned (number of assets commissioned in each year) 1950: 180; Year commissioned (number of assets commissioned in each year) 1954: 111; Year commissioned (number of assets commissioned in each year) 1959: 25; Year commissioned (number of assets commissioned in each year) 1964: 47; Year commissioned (number of assets commissioned in each year) 1965: 68; Year commissioned (number of assets commissioned in each year) 1967: 7; Year commissioned (number of assets commissioned in each year) 1968: 119; Year commissioned (number of assets commissioned in each year) 1969: 114; Year commissioned (number of assets commissioned in each year) 1970: 51; Year commissioned (number of assets commissioned in each year) 1971: 3; Year commissioned (number of assets commissioned in each year) 1972: 2; Year commissioned (number of assets commissioned in each year) 1976: 119; Year commissioned (number of assets commissioned in each year) 1977: 3; Year commissioned (number of assets commissioned in each year) 1980: 9; Year commissioned (number of assets commissioned in each year) 1981: 3; Year commissioned (number of assets commissioned in each year) 1985: 23; Year commissioned (number of assets commissioned in each year) 1989: 4; Year commissioned (number of assets commissioned in each year) 2002: 1
Contents