## Cover
LRMC Model
2020-25
January 2019

## Required Inputs
Sheet | Cell | Input | Notes | Source Information
Inputs – network configuration | D7 | Rate of Return | Pre Tax Real WACC | AER PTRM
Inputs – network configuration | D8 | CPI (estimated) |  | AER PTRM
Inputs – network configuration | D9 | Calculation base date |  | Date at which calculated prices are to apply
Inputs – network configuration | D10 | Peak Demand MW | 500MW - as per UK. Does not affect outcomes.
Inputs – network configuration | D12-D15 | Opex Allowance | % of ORC as Opex | Estimated
Inputs – network configuration | D20:D25 | DLFs | By Voltage Level | AEMO
Inputs – network configuration | D31:E38 | Average Feeder Lengths and Proportion UG:OH | By Voltage Level, Type and Location | 110kV - NFM (David Penington)
33kV – Based on “typical system”
11kV – Reliability Intranet Site
Inputs – network configuration | D41:E41 | Total LV Feeder Length | By Type (OH/UG) | 2017 DAPR
Inputs – network configuration | D47:D49 | Proportion of contributed assets | For HV and LV | Estimated from capital contributions policy
Inputs – network configuration | F54:F58 | Total No. of Feeders |  | Per Building Block Drawings within workbook
Inputs – network configuration | D63 | Direct Transformation 110kV/11kV | zone capacity for 110/10 as a % of total | From RIN
Inputs – network configuration | D66:F74 | Urban/rural split | Proportions for substation type | Estimated
Inputs – tariff class | F7:F14 | Anytime Max Demand | By Tariff Class | DCOS Model
Inputs – tariff class | H7:H14 | System Peak Demand | By Tariff Class | DCOS Model
Inputs – tariff class | M18 | 2017/18 Max Demand |  | DCOS Model
Inputs – tariff class | D30:D38 | 2013-14 Consumption | GWh, by Tariff Class | DCOS Model
Inputs – tariff class | F30:F38 | 2013-14 Power Factor lower limit | By Tariff Class | Rules
Standard Estimates | E8:E25 | Estimated unit costs |  | Original estimates indexed by CPI
Standard Estimates | R8:R17 | Asset standard lives |  | AER PTRM

## Model Notes
LRIC Model Notes
Filename: Energex - Revised Proposal - 10.003 - 2020-25 LRMC Model - December 2019.xlsx
Description
In the UK, distribution companies use a Common Distribution Charging Model (CDCM) or a ‘500MW model’ as the foundation for setting distribution tariffs. This model calculates costs on a long run incremental cost (LRIC) basis. The model represents a hypothetical, independent network which is designed as an extension to the existing network and reflects the configuration and geographic characteristics of the existing network. The model is designed such that it is capable of supplying 500MW of diversified demand at each voltage level (note that this level of demand is adjustable). Under the National Electricity Rules, Distributors must base their tariffs on the LRMC od supply. Current models for LRMC are based on the average incremental cost (AIC) approach, which uses forecast demand and expense . This approach is widely used by other Australian distributors, however it may not produce reliable results when demand is expected to stabilise or decrease. The development of a LRIC model for Energex will allow the LRMC to be calculated independently of future demand and expenditure, leading to a more stable estimate over time that truly reflects long run considerations.
Key Assumptions
- 500MW capacity at individual grid supply point (TNCP) level - design of a hypothetical network on a greenfield site - based on current network configuration - incorporates modern equivalent assets - no embedded generation - no spare capacity for future growth - emergency ratings can be used in fault or outage situations - the proportion of UG and OH assets at each network level reflects current Ergon average - average lengths of overhead and underground cable are used at each voltage level - based on shared assets only, no customer specific assets are included - unit costs using normal procurement methods, based on Ergon standard estimates - unit costs reflect total purchase and installation, including building and civil works and overheads - land costs are not included
Worksheets
| Inputs - network configuration | Inputs for the LRIC network model calculations are entered. Blue figures represent a data entry field.
| Inputs - tariff class | Tariff class data for the network is entered, including demand, energy, power factors. Blue figures represent a data entry field.
| Standard estimates | Standard estimates are sourced from internal data or the annual RIN. The assumed capacity for each transformer is provided.
| Calcs - LRIC - Asset costs | Standard estimates and key assumptions used to calculate the total asset cost (in $) for the hypothetical 500MW network.
| Asset diagrams | Overall summary of the details of the 500MW model in terms of capacity and configuration, including asset diagrams and estimated quantities.
| Calcs - LRIC - $kW by voltage | The network cost in $ is used with the WACC to estimate annualised rates in $/kW at each voltage level.
| Calcs - Energex TC | The 500MW model $/kW costs are used in conjunction with calculated network share (at time of peak demand) to translate the costs to each tariff class.

## Version Control
Version Control
Filename: Energex - Revised Proposal - 10.003 - 2020-25 LRMC Model - December 2019.xlsx
| Version | Date | Description/Updates
| Draft 0.1 | 2013-08-09 | Initial draft for review
| Draft 0.2 | 2013-09-25 | Combine ICC into one "tariff"
| Draft 0.6 | 2013-07-22 | Reviewed for network diagram to be complient with new safet net standard in the DA Updated standard estimates.
| v16 | 2018-11-30 | Revised and updated.
Asset weighted average lives added.
Asset escalation added.

## Inputs - network configuration
Input Parameters - for network model
Filename: Energex - Revised Proposal - 10.003 - 2020-25 LRMC Model - December 2019.xlsx
1. General
| Rate of Return | 3.43% | Real vanilla WACC 2018/19 March 2018 update
| CPI | 2.5% | CPI estimate as per PTRM.
| Calculation base date | 2019-07-01 | To align with tariff submission.
| Peak Demand MW | 500 | As per UK models
| Opex Allowance |  |  |  | Legend
| 110 | 1.5% |  |  | Trans | 132, 110kV
| 33 | 2% |  |  | ST | 66, 33kV
| 11 | 2% |  |  | HV | 22, 11kV
| LV | 2.5% |  |  | LV | 400, 230V
2. Distribution Loss Factors
| Voltage Level | 2018/19 DLF | Reference
| 110kV | 1.0037 | As published by AEMO for Queensland 1 July 2018
| 33kV | 1.009
| 11kV bus | 1.0131
| 11kV line | 1.0198
| LV bus | 1.0337
| LV line | 1.0534
3. Feeder Data and Calculations
|  | Avg Feeder Lengths (km) |  | Proportions (%)
| Voltage Level | OH | UG | OH | UG | Notes
| 110kV Feeder - City | 3.981 | 3.065 | 30% | 70% | Lengths of 110kV feeders calculated based on data from NFM (contact: David Pennington), proportions rounded to nearest 5% based on total length of each type
| 110kV Feeder - Urban | 11.301 | 3.533 | 90% | 10%
| 110kV Feeder - Rural | 20.052 | 4.317 | 100% | 0%
| 33kV Feeder - Urban | 6.6367 | 4.015 | 50% | 50% | Avg lengths and proportions based on a typical 33kV Urban and a typical 33kV Rural system (Cleveland and Kalbar/Nudgee areas used).
| 33kV Feeder - Rural | 13.4911 |  | 100% | 0%
| 11kV Feeder - City |  | 0.386 | 0% | 100% | Avg lengths calculated based on data from Reliability intranet site, proportions rounded to nearest 5% based on total length of each type
| 11kV Feeder - Urban | 4.889 | 4.241 | 50% | 50%
| 11kV Feeder - Rural | 45.86 | 8.124 | 75% | 25%
| LV for 500 MW | 1611.4024 | 1330.5814 | 54.77% | 45.23% | Proportion based on MW
| LV total length km | 14202 | 11727 | DAPR 2017/18-2021/22
| System demand | 4406.7204 | MW
4. Contributed assets
| Voltage Level | Proportion
| HV | 25%
| 11kV/LV | 25%
| LV | 90%
5. Feeder lengths
3.3 | Voltage Level | No. of feeders OH | No. of feeders UG | Total Feeders (no.) | OH Length (km) | UG Length (km) | Feeder Voltage | Notes
| 110/11kV - City | 0.6 | 1.4 | 2 | 2.3886 | 4.291 | 110kV | Feeder numbers are as per building block drawings
| 110/33kV - Urban | 1.8 | 0.2 | 2 | 20.3418 | 0.7066 | 110kV
| 110/33kV - Rural | 2 | 0 | 2 | 40.104 | 0 | 110kV
| 33kV/11kV - Urban | 3 | 3 | 6 | 19.91 | 12.045 | 33kV
| 33kV/11kV - Rural | 4 | 0 | 4 | 53.9646 | 0 | 33kV
6. Substation Data
| Direct Transformation 110kV/11kV | 30% | Based on share of 110/11kV Zone capacity (3255 MVA) of total 10270 MVA (for both 110/33 and 110/11)
| Voltage Level | Urban % | Rural % | City | Notes
TNCP
| 110kV | 100% | 0% |  | Rounded to nearest 5% - based on 40 Urban BSP and 1 Rural BSP
110/33kV
33kV
| 33/11kV | 80% | 20% |  | Rounded to nearest 5% - based on 157 Urban and 46 Rural (excl 110/11kV subs)
| 110kV/11kV |  |  | 100% | Assume all 110/11kV is in CBD
11kV
| 11kV/LV | 70% | 20% | 10% | Rounded to nearest 5% - based on numbers of 11kV feeders - 249 City, 1610 Urban, 417 Rural
LV

## Inputs - tariff class
Input Parameters - Energex Tariff Class
Tariff Details and Consumption/Demand Data | [5 empty] | Calculations for 2017/18
Summer 2017/18 demands
| Tariff Class | 2017/18 demand at system peak MW |  | 2012 anytime max demand MW |  | 2012 demand at system peak MW | 2018/19 DLF | 2013/14 Load Factor | Loss Load Factor 30%*LF + 70%*LF^2 | Peak Loss at system peak demand | 2017/18 demand at system peak MW | 2017/18 ATMD MW scaled |  |  | Class | Pricing zone | Voltage level | 1900-09-30 14:24 |  | 1900-06-11 14:24 |  | 1900-09-15 14:24 |  | Average |  | pf
| ICC 110kV | 37.1697 |  | 42 |  | 35 | 1.0037 | 70.12% | 53.36% | 0.18072 | 37.1697 | 38.8355 | [5 empty] | MW | MVA | MW | MVA | MW | MVA | MW | MVA
| ICC 33kV | 145.832 |  | 124 |  | 122 | 1.009 | 94.41% | 90.72% | 1.3659 | 145.832 | 152.3674 |  |  | System |  |  | 4814 |  | 4716 |  | 4557 |  | 4695.6667
| ICC 11kV Bus | 89.0142 |  | 81 |  | 79 | 1.0131 | 82.58% | 72.51% | 1.328 | 89.0142 | 93.0033 |  |  | ICC | South East | 132/110kV | 40.7966 | 45.4537 | 28.8382 | 31.6373 | 41.8744 | 47.6886 | 37.1697 | 41.5932 | 0.89365
| CAC 33kV | 0 |  | 16 |  | 14 | 1.009 |  |  |  |  | 0 |  |  | ICC | South East | 33kV | 154.9678 | 165.9727 | 154.6512 | 166.1114 | 127.8772 | 137.3703 | 145.832 | 156.4848 | 0.93192
| CAC 11kV Bus | 136.5634 |  | 133 |  | 130 | 1.0131 | 70.78% | 56.3% | 2.2491 | 136.5634 | 142.6835 |  |  | ICC | South East | 22/11kV Bus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAC 11kV Line | 454.9392 |  | 515 |  | 497 | 1.0198 | 67.07% | 51.61% | 11.7063 | 454.9392 | 475.3271 |  |  | ICC | South East | 22/11kV Line | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SAC Demand LV Bus | 526.5083 |  | 546.5 |  | 503 | 1.0337 | 62.98% | 46.66% | 23.9498 | 526.5083 | 550.1036 |  |  | ICC | South East | 11kV | 94.4715 | 104.0372 | 84.1874 | 93.0956 | 88.3837 | 97.128 | 89.0142 | 98.0869 | 0.9075
| SAC Demand LV Line | 526.5083 |  | 546.5 |  | 503 | 1.0534 | 62.98% | 46.66% | 37.9501 | 526.5083 | 550.1036 |  |  | CAC | South East | 132/110kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SAC Non Demand LV Line | 2490.1853 |  | 2449 |  | 2379 | 1.0534 | 47.51% | 30.05% | 210.2165 | 2490.1853 | 2601.782 |  |  | CAC | South East | 33kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total | 4406.7204 |  | 4453 |  | 4262 |  |  |  |  | 4406.7204 | 4604.206 |  |  | CAC | South East | 22/11kV Bus | 148.9776 | 159.2439 | 116.2509 | 124.6078 | 144.4618 | 154.9087 | 136.5634 | 146.2534 | 0.93375
| Losses | 288.9463 |  |  |  | 222 |  |  |  | 288.9463 | 288.9463 |  |  |  | CAC | South East | 22/11kV Line | 517.2613 | 560.2014 | 356.6538 | 386.4986 | 490.9024 | 531.6858 | 454.9392 | 492.7952 | 0.92318
| System peak | 4695.6667 |  |  |  | 4484 |  |  |  |  | 4695.6667 |  |  |  | CAC | South East | 11kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Check | OK |  |  |  | 104.5% |  | Loss discrepancy |  |  | 0 | [6 empty] | 956.4746 | 1034.9088 | 740.5815 | 801.9507 | 893.4995 | 968.7813 | 863.5185 | 935.2136 | 0.92334
|  |  |  | Split |  |  |  | LV adjustment |  |  | 1.0467 | [6 empty] | 956.4746 | 1034.9088 | 740.5815 | 801.9507 | 893.4995 | 968.7813
| Scaling Factor | 0
| Tariff Class | 2013/14 Consumption GWh | 2017/18 Anytime Max Demand MW | Power Factor |  | 2017/18 demand at system peak MW | 110 | 110/33kV | 33 | 33/11kV | 110/11kV | 11 | 11kV/LV | LV
| ICC 110kV | 215 | 38.8355 | 0.95 |  | 37.1697 | 37.1697
| ICC 33kV | 1009 | 152.3674 | 0.9 |  | 145.832 | 145.832 | 145.832 | 72.916
| ICC 11kV Bus | 571.5 | 93.0033 | 0.9 |  | 89.0142 | 89.0142 | 62.3099 | 62.3099 | 62.3099 | 26.7043
| CAC 33kV | 135.5 | 0 | 0.9 |  | 0 | 0 | 0 | 0
| CAC 11kV Bus | 806 | 142.6835 | 0.9 |  | 136.5634 | 136.5634 | 95.5944 | 95.5944 | 95.5944 | 40.969
| CAC 11kV Line | 2920 | 475.3271 | 0.9 |  | 454.9392 | 454.9392 | 318.4574 | 318.4574 | 318.4574 | 136.4818 | 454.9392
| SAC Demand LV Bus | 2775.05 | 550.1036 | 0.9 |  | 526.5083 | 526.5083 | 368.5558 | 368.5558 | 368.5558 | 157.9525 | 526.5083 | 526.5083
| SAC Demand LV Line | 2775.05 | 550.1036 | 0.9 |  | 526.5083 | 526.5083 | 368.5558 | 368.5558 | 368.5558 | 157.9525 | 526.5083 | 526.5083 | 526.5083
| SAC Non Demand LV Line | 9901 | 2601.782 | 0.9 |  | 2490.1853 | 2490.1853 | 1743.1297 | 1743.1297 | 1743.1297 | 747.0556 | 2490.1853 | 2490.1853 | 2490.1853
| Total (*excl EGs) | 21108.1 | 4604.206 |  |  | 4406.7204 | 4406.7204 | 3102.4351 | 3029.5191 | 2956.603 | 1267.1156 | 3998.141 | 3543.2018 | 3016.6936
Voltage Level Share - based on contribution to peak demand
| Voltage Level | 2017/18 demand at system peak MW | Percentage of maximum
| 110 | 4406.7204 | 100%
| 110/33kV | 3102.4351 | 70.4%
| 33 | 3029.5191 | 68.75%
| 33/11kV | 2956.603 | 67.09%
| 110/11kV | 1267.1156 | 28.75%
| 11 | 3998.141 | 90.73%
| 11kV/LV | 3543.2018 | 80.4%
| LV | 3016.6936 | 68.46%
| Tariff Class | 2017/18 Demand at System Peak MW | 2017/18 Demand on 110/11 MW | 2017/18 Demand on 110/33 MW | 2017/18 Demand on 33/11 MW
| ICC 110kV | 37.1697
| ICC 33kV | 145.832 |  | 145.832
| ICC 11kV Bus | 89.0142 | 26.7043 | 62.3099 | 62.3099
| CAC 33kV | 0 |  | 0
| CAC 11kV Bus | 136.5634 | 40.969 | 95.5944 | 95.5944
| CAC 11kV Line | 454.9392 | 136.4818 | 318.4574 | 318.4574
| SAC Demand LV Bus | 526.5083 | 157.9525 | 368.5558 | 368.5558
| SAC Demand LV Line | 526.5083 | 157.9525 | 368.5558 | 368.5558
| SAC Non Demand LV Line | 2490.1853 | 747.0556 | 1743.1297 | 1743.1297
| Total | 4406.7204 | 1267.1156 | 3102.4351 | 2956.603
| Check | 4406.7204 | 1267.1156 | 3102.4351 | 2956.603
| Tariff Class | 110kV | 110/33kV | 33kV | 33/11kV | 110kV/11kV | 11kV | 11kV/LV | LV
|  | 4406.7204 | 3102.4351 | 3029.5191 | 2956.603 | 1267.1156 | 3998.141 | 3543.2018 | 3016.6936
| ICC 110kV | 0.8435%
| ICC 33kV | 3.309% | 4.701% | 2.407%
| ICC 11kV Bus | 2.02% | 2.008% | 2.057% | 2.107% | 2.107%
| CAC 33kV | 0% | 0% | 0%
| CAC 11kV Bus | 3.099% | 3.081% | 3.155% | 3.233% | 3.233% | 0%
| CAC 11kV Line | 10.32% | 10.26% | 10.51% | 10.77% | 10.77% | 11.38%
| SAC Demand LV Bus | 11.95% | 11.88% | 12.17% | 12.47% | 12.47% | 13.17% | 14.86%
| SAC Demand LV Line | 11.95% | 11.88% | 12.17% | 12.47% | 12.47% | 13.17% | 14.86% | 17.45%
| SAC Non Demand LV Line | 56.51% | 56.19% | 57.54% | 58.96% | 58.96% | 62.28% | 70.28% | 82.55%
|  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%

## Standard estimates
Energex Standard Estimates
| source: | http://thesource/npp/npmo/vspa/_layouts/xlviewer.aspx?id=/npp/npmo/vspa/Lists/RoadmapTable/Attachments/14/Transmission%20Estimation%20List%20of%20C20%20Standard%20Estimates.xlsx&Source=http%3A%2F%2Fthesource%2Fnpp%2Fnpmo%2Fvspa%2FPages%2FEstimateRoadmap%2Easpx%3FGroupString%3D%253B%2523POW%2520Capex%253B%2523%26IsGroupRender%3DTRUE&DefaultItemOpen=1
| Estimate No. | Description | Valuation | Estimate | Escalation | Escalation | Unit Cost | Capacity Calculations MVA |  |  |  | Reference | Asset | PTRM | Standard
|  |  |  | date | 2018-07-01 | 2019-07-01 |  | Installed | Factor | Usable | Notes |  | Life | Asset Class Name | Life
| PDCODCA07-01 | 1km LV Underground cable | 279615 | 2015-07-01 | 1.0512 | 1.0774 | 301263.8141 |  |  |  | 240mm^2 4C Aluminium Cable, incl pillars | Estimates sourced from Annual RIN - 2012/13 | 60 | OH Sub-transmission lines | 50.54
| PDCODCA08-11 | 1km LV Overhead on timber poles | 53881 | 2015-07-01 | 1.0512 | 1.0774 | 58052.6637 |  |  |  | 4x95mm^2 LVABC, incl timber poles |  | 45 | UG Sub-transmission cables | 45
| 165193 | Pole Transformer 315kVA | 72912 | 2015-07-01 | 1.0512 | 1.0774 | 78557.1132 | 0.315 | 115% | 0.36225 |  |  | 40.58 | OH Distribution Lines | 45
| 1695096 | Padmount Transformer 750kVA | 304259 | 2015-07-01 | 1.0512 | 1.0774 | 327815.8425 | 0.75 | 115% | 0.8625 |  |  | 40.58 | UG Distribution Cables | 60
| 118120 | 2 Feeder, 2 Dry Type Transformer | 858676 | 2015-07-01 | 1.0512 | 1.0774 | 925157.8306 | 3 | 85% | 2.55 | 85% loading criteria | Supply and planning manual | 40.58 | Distribution Equipment | 35
| 118127 - Urban | Double Modular Substation | 9636641 | 2015-07-01 | 1.0512 | 1.0774 | 10382744.9256 | 25 | 115% | 38.75 | includes 6MVA of transfer, 4MVA of mobile generation | Factor based on plant rating manual assuming mixed load. Usable calculated based on typical available transfer in the current network, generation the Customer Outcomes Standard. | 45 | Substation Bays | 45
| 118127 - Rural | Double Modular Substation | 9636641 | 2015-07-01 | 1.0512 | 1.0774 | 10382744.9256 | 25 | 115% | 40.75 | includes 1MVA of transfer, 10MVA of mobile generation |  | 45 | Substation Establishment | 57.57
| 118131 | 33/11kV 25MVA Masonry Building Zone Substation | 12622139 | 2015-07-01 | 1.0512 | 1.0774 | 13599391.0796 | 25 | 115% | 38.75 | includes 6MVA of transfer, 4MVA of mobile generation |  | 45 | Distribution Substation Switchgear | 45
| 118123 | Rural Midi Modular Substation | 1936358 | 2015-07-01 | 1.0512 | 1.0774 | 2086277.9052 | 8 | 115% | 9.2 | limited to transformer capacity |  | 45 | Zone Transformers | 50
| 118143 | 110/11kV 2 x 60MVA, 110kv GIS ID & 11kV ID Masonry | 23783427 | 2015-07-01 | 1.0512 | 1.0774 | 25624826.7418 | 60 | 115% | 69 | CBD - no transfers |  | 57.57 | Distribution Transformers | 40.58
| 118145 | 110/33kV 2 x 80MVA, 110kV GIS OD & 33kV Pre-Fab | 17596081 | 2015-07-01 | 1.0512 | 1.0774 | 18958433.8271 | 80 | 115% | 110 | includes 18 MVA of transfer |  | 57.57
| 384667 | 1km 11kV UG Feeder 400mm2 AL | 821928.44 | 2015-07-01 | 1.0512 | 1.0774 | 885565.1403 | 7.125 | 66% | 4.7025 | added for CBD 3 feeder mesh feeders - each mesh includes 3 feeders | Installed Capacity from Netowrk Building blocks. Factor and usable based on Customer Outcomes Standard. | 60
| 118167 | 1km 11kV UG Feeder 240mm2 | 699896.052 | 2015-07-01 | 1.0512 | 1.0774 | 754084.5594 | 7.505 | 80% | 6.004 | Standard rating of 11kV UG 240mm3 CU XLPE is 7.9MVA, Power factor 95% |  | 60
| 118168 | 1km 11kV OH Feeder (PLUTO or MOON) | 178690.896 | 2015-07-01 | 1.0512 | 1.0774 | 192525.7975 | 7.315 | 80% | 5.852 | Standard rating 11kV OH Moon conductor is 7.7MVA, Power factor 95% |  | 45
| 118222 | 110kV SCCT on concrete poles (1km SULPHUR) | 2658038.39 | 2018-07-01 | 1 | 1.025 | 2724443.3031 | [5 empty] | 50.54
| 118229 | 33kV DCCT OH (CONC/ ROAD RES) / 1KM | 1856493.17 | 2018-07-01 | 1 | 1.025 | 1902873.3382 |  |  |  | no longer had a standard estimate for single circuit 33kV DCCT used. |  | 50.54
| 118242 | 145kV Single Circuit UG Complex (1600mm2 cable 1km) | 5097655 | 2015-07-01 | 1.0512 | 1.0774 | 5492334.0595 | [5 empty] | 45
| 118246 | 33kV Double Circuit Underground (630mm2 1km) | 3015057.08 | 2018-07-01 | 1 | 1.025 | 3090381.2755 | [5 empty] | 45
97767474.1426
|  | CPI index 30 Jun 2015 | 107.5
|  | CPI index 30 Jun 2018 | 113
105.1%
Note on I20: Nerida Kemp: Assumes economies of scale factor of 90%
Note on I21: Nerida Kemp: assumes economies of scale factor of 90%

## Calcs - LRIC - Asset costs
Calculations - LRIC Model - Asset Costs
Required Capacity (excl. losses)
| Voltage Level | Total MW | Urban MW | Rural MW | City MW
| 110kV | 500
| 110/33kV | 352.0118 | 352.0118 | 0 | 0
| 33kV | 343.7385
| 33/11kV | 335.4652 | 268.3722 | 67.093 | 0
| 110/11kV | 143.7708 | 0 | 0 | 143.7708
| 11kV | 453.6413
| 11kV/LV | 402.0225 | 281.4158 | 80.4045 | 40.2023
| LV | 342.2833
| Voltage Level | Voltage ID | Building Block Description | Estimate No. |  |  | Build blk cap MW |  | Cap MW | Multiplier | Total Qty |  | Total Asset Cost | Asset | Weighted Average Lives
|  |  |  | No. | Unit Qty | Unit | Installed | Total | Required |  |  |  |  | Life | 110kV | 110/33kV | 33kV | 33/11kV | 110/11kV | 11kV | 11kV/LV | LV
| 110kV/33kV - Urban | 110/33kV | 2 x 80MVA Bulk Supply Sub | 118145 | 1 | no. | 110 | 110 | 352.0118 | 3.2001 | 3.2001 | units | 56309345.5666 | 57.57 |  | 57.57
|  | 110kV | 110kV OH Feeder | 118222 | 20.3418 | km |  |  |  |  | 65.0959 | km | 173027509.4617 | 50.54 | 50.54
|  | 110kV | 110kV UG Feeder | 118242 | 0.7066 | km |  |  |  |  | 2.2612 | km | 11526795.822 | 45 | 45
| 110kV/33kV - Rural | 110/33kV | 2 x 80MVA Bulk Supply Sub | 118145 | 1 | no. | 110 | 110 | 0 | 0 | 0 | units | 0 | 57.57 |  | 57.57
|  | 110kV | 110kV OH Feeder | 118222 | 40.104 | km |  |  |  |  | 0 | km | 0 | 50.54 | 50.54
|  | 110kV | 110kV UG Feeder | 118242 | 0 | km |  |  |  |  | 0 | km | 0 | 45 | 45
| 110kV/11kV - City | 110/11kV | 2 x 60MVA Bulk Supply Sub | 118143 | 1 | no. | 69 | 69 | 143.7708 | 2.0836 | 2.0836 | units | 49555982.1811 | 57.57 |  |  |  |  | 57.57
|  | 110kV | 110kV OH Feeder | 118222 | 2.3886 | km |  |  |  |  | 4.977 | km | 13228979.1545 | 50.54 | 50.54
|  | 110kV | 110kV UG Feeder | 118242 | 4.291 | km |  |  |  |  | 8.9409 | km | 45577511.5076 | 45 | 45
| 33kV/11kV - Urban | 33/11kV | 2 x 25MVA Modular Zone Sub | 118127 - Urban | 2 | no. | 77.5 | 116.25 | 268.3722 | 2.3086 | 4.6172 | units | 44493875.2018 | 45 |  |  |  | 45
|  | 33/11kV | 33/11kV 25MVA Masonry Building Zone Substation | 118131 | 1 | no. | 38.75 |  |  |  | 2.3086 | units | 29139192.663 | 45 |  |  |  | 45
|  | 33kV | 33kV DCCT OH (CONC/ ROAD RES) / 1KM | 118229 | 9.955 | km |  |  |  |  | 22.9819 | km | 42665729.5989 | 50.54 |  |  | 50.54
|  | 33kV | 33kV UG Feeder | 118246 | 12.045 | km |  |  |  |  | 27.8068 | km | 83839156.3061 | 45 |  |  | 45
| 33kV/11kV - Rural | 33/11kV | 2 x 25MVA Modular Zone Sub | 118127 - Rural | 2 | no. | 81.5 | 90.7 | 67.093 | 0.73972 | 1.4794 | units | 14256926.6599 | 45 |  |  |  | 45
|  | 33/11kV | 1 x 8MVA Midi Modular Sub | 118123 | 1 | no. | 9.2 |  |  |  | 0.73972 | units | 1432372.2339 | 45 |  |  |  | 45
|  | 33kV | 33kV DCCT OH (CONC/ ROAD RES) / 1KM | 118229 | 26.9823 | km |  |  |  |  | 19.9595 | km | 37054617.2913 | 50.54 |  |  | 50.54
|  | 33kV | 33kV UG Feeder | 118246 | 0 | km |  |  |  |  | 0 | km | 0 | 45 |  |  | 45
| 11kV/LV - City | 11kV | 11kV UG Feeder | 384667 | 0.386 | km | 14.1075 | 14.1075 | 40.2023 | 2.8497 | 1.1 | km | 904110.8018 | 60 | [5 empty] | 60
|  | 11kV/LV | 2 Feeder, 2 Dry Type Transformer | 118120 | 1 | no. | 2.55 | 2.55 | 40.2023 | 15.7656 | 15.7656 | units | 13537533.6257 | 40.58 | [6 empty] | 40.58
| 11kV/LV - Urban | 11kV/LV | 750kVA Padmount DT | 1695096 | 1 | no. | 0.8625 | 0.8625 | 281.4158 | 326.2792 | 326.2792 | units | 99273372.0825 | 40.58 | [6 empty] | 40.58
|  | 11kV | 11kV UG Feeder | 118167 | 4.241 | km | 6.004 | 6.004 | 140.7079 | 23.4357 | 99.3908 | km | 69563204.698 | 60 | [5 empty] | 60
|  | 11kV | 11kV OH Feeder | 118168 | 4.889 | km | 5.852 | 5.852 | 140.7079 | 24.0444 | 117.5531 | km | 21005672.7334 | 45 | [5 empty] | 45
| 11kV/LV - Rural | 11kV/LV | 315kVA Pole DT | 165193 | 1 | no. | 0.36225 | 0.36225 | 80.4045 | 221.9586 | 221.9586 | units | 16183446.5219 | 40.58 | [6 empty] | 40.58
|  | 11kV | 11kV UG Feeder | 118167 | 8.124 | km | 6.004 | 6.004 | 20.1011 | 3.348 | 27.1988 | km | 19036328.1897 | 60 | [5 empty] | 60
|  | 11kV | 11kV OH Feeder | 118168 | 45.86 | km | 5.852 | 5.852 | 60.3034 | 10.3047 | 472.5757 | km | 84444977.1983 | 45 | [5 empty] | 45
| LV | LV | LV UG Feeder | PDCODCA07-01 | 1611.4024 | km |  |  |  | 1 | 1611.4024 | km | 450572295.5007 | 60 | [7 empty] | 60
|  | LV | LV OH Feeder | PDCODCA08-11 | 1330.5814 | km |  |  |  | 1 | 1330.5814 | km | 71693054.3838 | 45 | [7 empty] | 45
[13 empty] | 1448321989.384 |  | 49.24 | 57.57 | 47.7002 | 45 | 57.57 | 51.8865 | 40.58 | 57.9409
Summary
| Voltage Level | Asset Cost | Wgtd Avg Life |  |  | DAPR 2017/18-2021/22
| 110kV | 243360795.9457 | 49.24 |  |  | Assets |  | 2012/13 | 2013/14 | 2014/15 | 2015/16 | 2016/17
| 110/33kV | 56309345.5666 | 57.57 |  |  | Total OH and UG |  | 51879 | 52176 | 52635 | 53270 | 53774
| 33kV | 163559503.1964 | 47.7002 |  |  | Lines km
| 33/11kV | 89322366.7585 | 45 |  |  | Total |  | 35094 | 35112 | 35171 | 35177 | 35120
| 110/11kV | 49555982.1811 | 57.57 |  |  | LV |  | 14262 | 14242 | 14226 | 14222 | 14202
| 11kV | 194954293.6212 | 51.8865 |  |  | HV |  | 17529 | 17541 | 17553 | 17571 | 17572
| 11kV/LV | 128994352.2301 | 40.58 |  |  | 33 kV |  | 2130 | 2196 | 2219 | 2211 | 2193
| LV | 522265349.8845 | 57.9409 |  |  | 132/110 kV |  | 1173 | 1173 | 1173 | 1173 | 1154
|  | 1448321989.384 |  |  |  | Cables km
[6 empty] | Total |  | 16785 | 17064 | 17464 | 18093 | 18654
[6 empty] | LV |  | 10457 | 10599 | 10848 | 11300 | 11727
[6 empty] | HV |  | 5290 | 5421 | 5547 | 5754 | 5917
[6 empty] | 33 kV |  | 892 | 892 | 913 | 883 | 8455
[6 empty] | 132/110 kV |  | 146 | 152 | 156 | 156 | 164
Other Equipment
[6 empty] | Bulk Supply Substations |  | 41 | 42 | 42 | 42 | 42
[6 empty] | Zone Substations |  | 238 | 242 | 244 | 246 | 246
[6 empty] | Poles |  | 658886 | 661714 | 667469 | 675459 | 683529
[6 empty] | Distribution Transformers |  | 47436 | 47875 | 48436 | 49093 | 49781
[6 empty] | Street Lights |  | 345807 | 348716 | 354691 | 362907 | 372164
Customer Numbers
[6 empty] | Residential |  | 1235740 | 1250326 | 1271644 | 1297106 | 1323876
[6 empty] | Other |  | 111455 | 113489 | 113801 | 114522 | 115592
[6 empty] | Total |  | 1347195 | 1363815 | 1385445 | 1411628 | 1439468

## Calcs - LRIC - $kW by voltage
Calculations - LRIC Model - $/kW Rates by Voltage Level
0.042347
| Voltage Level | DLF | % of load through network level | Demand MW (incl losses) | Asset Cost | Asset Life | Proportion contributed | Assets $/kW/yr | Opex rate | Opex $/yr | Opex $/kW/yr | Total $/yr | Total $/kW/yr
| 110 kV | 1.0037 | 100% | 498.1568 | 243361000 | 49.24 |  | 20.6874 | 1.5% | 3650415 | 7.3278 | 247011415 | 28.0152
| 110/33kV | 1.009 | 70.4% | 348.8719 | 56309000 | 57.57 |  | 6.4635 | 1.5% | 844635 | 2.421 | 57153635 | 8.8846
| 33kV | 1.009 | 68.75% | 340.6725 | 163560000 | 47.7002 |  | 20.5886 | 2% | 3271200 | 9.6022 | 166831200 | 30.1907
| 33/11kV | 1.0131 | 67.09% | 331.1275 | 89322000 | 45 |  | 11.8505 | 2% | 1786440 | 5.395 | 91108440 | 17.2455
| 110kV/11kV | 1.0131 | 28.75% | 141.9118 | 49556000 | 57.57 |  | 13.9841 | 2% | 991120 | 6.9841 | 50547120 | 20.9682
| 11kV | 1.0198 | 90.73% | 444.8336 | 194954000 | 51.8865 | 25% | 13.6459 | 2% | 3899080 | 8.7653 | 198853080 | 22.4112
| 11kV/LV | 1.0337 | 80.4% | 388.9161 | 128994000 | 40.58 | 25% | 11.4448 | 2.5% | 3224850 | 8.2919 | 132218850 | 19.7366
| LV | 1.0534 | 68.46% | 324.9319 | 522265000 | 57.9409 | 90% | 6.4232 | 2.5% | 13056625 | 40.1826 | 535321625 | 46.6059
[5 empty] | 1448321000 |  |  |  |  | 30724365 |  | 1479045365
Adjusted for contributed assets

## Calcs - Energex TC
Calculations - Application to Energex Tariff Class
Voltage level cost allocation
| Voltage Level | LRIC Model $/kW/yr | Demand Allocator (MW) | Allocated Cost $/yr
| 110kV | 28.0152 | 4406.7204 | 123455346.5198
| 110/33kV | 8.8846 | 3102.4351 | 27563819.3217
| 33kV | 30.1907 | 3029.5191 | 91463446.3615
| 33/11kV | 17.2455 | 2956.603 | 50988110.3595
| 110kV/11kV | 20.9682 | 1267.1156 | 26569131.5658
| 11kV | 22.4112 | 3998.141 | 89603096.2753
| 11kV/LV | 19.7366 | 3543.2018 | 69930916.2282
| LV | 46.6059 | 3016.6936 | 140595630.8306
620169497.4624
Tariff class cost allocation
| Tariff Class | 110kV | 110/33kV | 33kV | 33/11kV | 110kV/11kV | 11kV | 11kV/LV | LV | Total
|  | 123455346.5198 | 27563819.3217 | 91463446.3615 | 50988110.3595 | 26569131.5658 | 89603096.2753 | 69930916.2282 | 140595630.8306
| ICC 110kV | 1041318.4201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1041318.4201
| ICC 33kV | 4085519.8466 | 1295655.694 | 2201388.9992 | 0 | 0 | 0 | 0 | 0 | 7582564.5397
| ICC 11kV Bus | 2493753.7475 | 553597.2054 | 1881183.1007 | 1074565.9957 | 559940.0549 | 0 | 0 | 0 | 6563040.1042
| CAC 33kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAC 11kV Bus | 3825858.2417 | 849315.7887 | 2886066.7887 | 1648573.8317 | 859046.839 | 0 | 0 | 0 | 10068861.4897
| CAC 11kV Line | 12745232.0368 | 2829359.0916 | 9614467.8063 | 5491958.8461 | 2861776.5222 | 10195728.1192 | 0 | 0 | 43738522.4222
| SAC Demand LV Bus | 14750257.9339 | 3274461.8746 | 11126975.141 | 6355930.54 | 3311979.0781 | 11799676.8634 | 10391506.9019 | 0 | 61010788.3329
| SAC Demand LV Line | 14750257.9339 | 3274461.8746 | 11126975.141 | 6355930.54 | 3311979.0781 | 11799676.8634 | 10391506.9019 | 24538376.9284 | 85549165.2614
| SAC Non Demand LV Line | 69763148.3593 | 15486967.7928 | 52626389.3846 | 30061150.6059 | 15664409.9936 | 55808014.4293 | 49147902.4245 | 116057253.9021 | 404615236.8922
|  | 123455346.5198 | 27563819.3217 | 91463446.3615 | 50988110.3595 | 26569131.5658 | 89603096.2753 | 69930916.2282 | 140595630.8306 | 620169497.4624
Voltage level LRMC rates based on ATMD estimate
| Voltage Level | Allocated Cost $ | 2017/18 ATMD MW scaled | LRMC $/kW/annum | Power Factor | LRMC $/kVA/annum
| 110 kV | 1041318.4201 | 38.8355 | 26.8136 | 0.95 | 25.4729
| 33 kV | 7582564.5397 | 152.3674 | 49.765 | 0.9 | 44.7885
| HV Bus | 16631901.594 | 235.6868 | 70.5678 | 0.9 | 63.511
| HV line | 43738522.4222 | 475.3271 | 92.0177 | 0.9 | 82.816
| LV Bus | 61010788.3329 | 550.1036 | 110.9078 | 0.9 | 99.817
| LV line | 490164402.1535 | 3151.8856 | 155.5147 | 0.9 | 139.9632
|  | 620169497.4624 | 4604.206
4604.206
Voltage level LRMC rates based on Coincident MD estimate
| Voltage Level | Allocated Cost $ | 2017/18 demand at system peak MW | LRMC $/kW/annum | Power Factor | LRMC $/kVA/annum
| 110 kV | 1041318.4201 | 37.1697 | 28.0152 | 0.95 | 26.6145
| 33 kV | 7582564.5397 | 145.832 | 51.9952 | 0.9 | 46.7957
| HV Bus | 16631901.594 | 225.5776 | 73.7303 | 0.9 | 66.3573
| HV line | 43738522.4222 | 454.9392 | 96.1415 | 0.9 | 86.5273
| LV Bus | 61010788.3329 | 526.5083 | 115.8781 | 0.9 | 104.2903
| LV line | 490164402.1535 | 3016.6936 | 162.484 | 0.9 | 146.2356
|  | 620169497.4624 | 4406.7204
4406.7204
Rates for comparison with 2015
| Voltage Level | Allocated Cost $ | 2017/18 demand at system peak MW | LRMC $/kW/annum | Power Factor | LRMC $/kVA/annum
| Subtransmission | 8623882.9599 | 183.0017 | 47.1246 | 0.9 | 42.4121
| High Voltage | 60370424.0161 | 680.5168 | 88.7126 | 0.9 | 79.8414
| Low voltage | 551175190.4864 | 3543.2018 | 155.5585 | 0.9 | 140.0027
|  | 620169497.4624 | 4406.7204
4406.7204

## Asset Diagrams
Voltage Level | Building Blocks | [8 empty] | Notes
110kV | Type 1: Urban 110kV/33kV |  |  | Type 2: Rural 110kV/33kV |  |  | Type 3: City 110/11kV |  |  | A proportion of the Energex network is direct transformation from 110kV to 11kV. Assume 30% of network is 110/11kV and 70% is 110/33kV. Units required are rounded up to the nearest whole number. Average lengths and proportions of overhead line vs cable are based on the current Energex network.
|  | % of network 110/33kV | #REF! |  |  |  |  | % of network 110/11kV | 30%
|  | % urban | 100% |  |  |  |  | % city | 100%
|  | Required capacity MW | 352.0118 |  |  |  |  | Required capacity MW | 143.7708
|  | Substation capacity MW | 110 |  |  |  |  | Substation capacity MW | 69
|  | Feeders per substation | 2 |  |  |  |  | Feeders per substation | 2
|  | OH Length km | 20.3418 |  |  |  |  | OH Length km | 2.3886
|  | UG Length km | 0.7066 |  |  |  |  | UG Length km | 4.291
|  | Building Block units required | 3.2001 |  |  |  |  | Building Block units required | 2.0836
33kV | Type 1: Urban |  |  | Type 2: Rural |  |  | Type 3: City |  |  | Units required are rounded up to the nearest whole number. Average lengths and proportions of overhead line vs cable are based on the current Energex network.
|  | % urban | 80% |  | % rural | 20%
|  | Required capacity MW | 268.3722 |  | Required capacity MW | 67.093
|  | Building block capacity MW | 116.25 |  | Building block capacity MW | 90.7
|  | Feeders per building block | 6 |  | Feeders per building block | 4
|  | OH Length km | 9.955 |  | OH Length km | 26.9823
|  | UG Length km | 12.045 |  | UG Length km | 0
|  | Building Block units required | 2.3086 |  | Building Block units required | 0.73972
11kV | Type 1: Urban |  |  | Type 2: Rural |  |  | Type 3: City
|  | 11kV Feeder capacity MW | 6.004 |  | 11kV Feeder capacity MW | 5.852 |  | 11kV 3 Feeder mesh capacity MW | 14.1075 | Urban system - Padmount transformers
|  | % urban | 70% |  | % rural | 20% |  | % city | 10% | Rural system - Pole transformers
City system - cable only
|  | Required capacity MW | 281.4158 |  | Required capacity MW | 80.4045 |  | Required capacity MW | 40.2023
|  | Feeders required | 47.4801 |  | Feeders required | 13.6527 |  | Meshes required | 2.8497
|  | Transformer capacity MW | 0.8625 |  | Transformer capacity MW | 0.36225 |  | Transformer capacity MW | 2.55
|  | Units required | 326.2792 |  | Units required | 221.9586 |  | Units required | 15.7656
LV | Asset quantities for LV line are based on an estimate of the length required for 500MW. This estimate is based on the average residential ADMD, and customer numbers and line length in the current Energex network.