Analysis Paper

Essential Energy Pole Performance – External Decay

| Endorsed | Approved |
| --- | --- |
| Version: 0.5 |  |
| Date: 20/08/2013 |  |
| Status: DRAFT – UNCONTROLLED COPY IF PRINTED |  |

Revision History

This document is under version control

| Version No | Reason for Update | Date issued |
| --- | --- | --- |
| 0.1 | First Draft | 15/8/2013 |
| 0.2 | Updated numerous sections – included D1 analysis | 20/10/2013 |
| 0.3 | Draft for review | 11/11/2013 |
| 0.4 | Updated draft with corrections and clarifications (minor) for wider review | 18/11/2013 |
| 0.5 | Updated after comments from reviewers, added Appendix A and Condemnation analysis section, fixed minor typos and added additional data in some sections. – For final review | 09/01/2014 |
| FINAL | Minor typos fixed - FINAL FOR SIGNING |  |

Distribution List

| Department | Recipient | Recipient Status | Date issued |
| --- | --- | --- | --- |
| Manager Primary Systems | Brian Glawson | Reviewer |  |
| Principal Engineer | Leith Elder | Reviewer |  |
| Standards Team | Standards team – all | Reviewer |  |
| Group Mgr Maintenance and Refurb Strategy | Neil Chapman | Reviewer |  |
| Manager Planning | Tony Scroope | Reviewer |  |
| Group Mgr Engineering Network Forecast and Reporting | Ian Thompson | Reviewer |  |
| Senior Consulting Engineer | Chris Dalitz | Reviewer |  |
| Manager Network Risk Strategy | Greg Bell | Reviewer |  |

TABLE OF CONTENTS

INTRODUCTION	4

EXECUTIVE STATISTICAL SUMMARY	4

Durability 2 Pole Species	4

Treatment	4

Durability 1 Pole Species	4

Treatment	4

Summary and Observations;	5

PEC Poles	5

CCA Poles	5

Recommendations	5

GENERAL POLE INFORMATION	6

POLE TREATMENT AND DURABILITY 2 PERFORMANCE	7

DATA SOURCES	7

DATA CONSIDERATIONS	7

Durability 2 Poles Initial Data	8

Data Filtering	8

Data Cleansing	9

DURABILITY 2 POLE PERFORMANCE AND TREATMENT ANALYSIS	11

Statistical Examination – Durability 2 Treatment Type	13

Statistical Examination – Durability 2 Pole Species	13

Durability 2 Spatial Analysis	13

Durability 2 PEC External Decay Spatial Analysis	16

Durability 2 CCA External Decay Spatial Analysis	16

Durability 2 Spatial Analysis - Summary	16

DETAILED HIGH RISK AREA DURABILITY 2 ANALYSIS	26

Durability 2 Treatment Hypothesis Examination	27

Overall Statistics Durability 2 Poles	29

POLE TREATMENT AND DURABILITY 1 PERFORMANCE	31

Durability 1 Spatial Analysis	34

DETAILED HIGH RISK AREA DURABILITY 1 ANALYSIS	40

D1 Species Performance Analysis	42

Grey Box	42

Ironbark	42

Red Ironbark	43

Tallow wood	45

Overall Statistics D1 Poles	47

STATISTICAL EXTREMES ANALYSIS	49

CONDEMNATION ANALYSIS	51

External Decay Pole Condemnation Rate	51

POLE ANALYSIS FINDINGS SUMMARY	54

Durability 2 Pole Species	54

Treatment	54

Durability 1 Pole Species	54

Treatment	54

Entire Network Treatment Performance Summary	55

Summary and Observations;	55

PEC Poles	55

CCA Poles	55

Options for Fiscal Evaluation	56

Recommendations	56

APPENDIX A: DECAY HIGH RISK AREAS AND TERMITES	57

Decay	57

High Risk Areas – Definition	58

Insect Damage Zones	59

Correlation with Prior Studies	62

APPENDIX B DURABILITY 2 PERFORMANCE BY SELECTED DEPOT	63

# INTRODUCTION

This paper has been prepared to support a range of Design and Construction Standards initiatives that are designed to look at cost and life optimisation with regards to pole selection and performance.

# EXECUTIVE STATISTICAL SUMMARY

## Durability 2 Pole Species

- From an external decay perspective CCA treated Spotted Gum poles do not perform as well as CCA treated Blackbutt poles.

- A PEC treated Spotted Gum pole is better than a CCA treated Spotted Gum pole with approximately half the normalised percentage of poles with decay for a PEC treated Spotted Gum versus a CCA spotted Gum in high risk areas  (see Table 7)

- There are no signs of a Blackbutt pole performing statistically worse than a Spotted Gum pole in any of the Essential Energy footprint from an external decay perspective on average by depot.

## Treatment

- If a PEC pole or a CCA pole experience decay then the average life and standard deviation are not significantly different enough to suggest that a PEC pole performs better than a CCA or visa versa. For selected depots the average age for a D2 pole with external decay irrespective of treatment is around 38 years. For the entire network this figure is around 36.5 years.

- There is however a lower chance that a D2 PEC pole will experience decay than a D2 CCA pole. For the entire network a PEC pole has a chance of experiencing external decay of 0.72% versus a CCA pole of 3.6% (roughly 5:1 ratio in favour of PEC). For high risk areas (selected depots) a PEC pole has a 1.42% of experiencing external decay versus a CCA pole of 5.85% (roughly a 4:1 ratio in favour of PEC). The performance of CCA is significantly influenced by the external decay found in CCA treated Spotted Gum poles.

## Durability 1 Pole Species

- Based on the analysis some possible differences for PEC treated poles and CCA treated poles were found around pole species. In general PEC treated poles performed better than CCA treated poles with the possible exception of Red Ironbark, and Tallowwood species. For these species it is reasonable to conclude after examination that they probably have similar performance outcomes irrespective of treatment type.

## Treatment

- If a PEC pole or a CCA pole experience decay then the average life for a PEC pole at decay inception would appear to be on average higher for some species than the equivalent CCA pole of the same species. For selected depots the average age for a D1 pole with external decay irrespective of treatment is around 37 years. For the entire network this figure is around 35 years.

- There is however a lower chance that a D1 PEC pole will experience decay than a D1 CCA pole. For the entire network a PEC pole has a chance of experiencing external decay of 0.87% versus a CCA pole of 1.2% (roughly 1.4:1 ratio in favour of PEC). For high risk areas (selected depots) a PEC pole has a 3.12% chance of experiencing external decay versus a CCA pole of 3.67% (roughly a 1.2:1 ratio in favour of PEC). The finding for high risk areas needs to be considered in light of the statistically low population of PEC poles in the worse areas for external decay. As the PEC poles are not distributed across the footprint like CCA poles in the areas of high risk it is probable that the figure is not reliable.

## Summary and Observations;

- The findings support the argument that PEC poles are better performers than CCA poles in regards to external decay inception irrespective of durability group.

### PEC Poles

- Examination of durability grouping found that D1 PEC poles have a 0.87% of external decay versus a D2 PEC pole of 0.72% for the entire network. Considering the statistical analysis and variations in inspection regimes with regard to the measurement of external diameter it is proposed that D1 PEC poles perform in a similar manner to D2 PEC treated poles over the entire network. When considering the high risk areas D1 PEC poles were found to have a 3.12% chance of experiencing external decay versus D2 PEC poles of 1.42%. However the low population of D1 PEC poles in the high risk areas calls into question the 3.12% figure. Given the similarity for D1 and D2 PEC treated poles overall the network it is probably reasonable to conclude that a similar result should have been found for the high risk areas, but was not due to a statistically small sample size and lack of representation of D1 PEC poles in high risk areas.

### CCA Poles

- Examination of durability grouping found that D1 CCA poles have a 1.2% chance of external decay versus a D2 CCA pole of 3.6% for the entire network. When considering the high risk areas D1 CCA poles were found to have a 3.67% chance of experiencing external decay versus D2 CCA poles of 5.85%.

- The data demonstrates a difference for CCA treated poles depending on durability grouping which is not found for PEC treated poles. In general it was found that D2 PEC poles performed from an external decay perspective in a similar manner to D1 PEC poles. PEC is thus the better treatment overall.

## Recommendations

- The options listed for fiscal evaluation are modelled using NPV techniques to determine the value or otherwise of the options to Essential Energy.

- Similar modelling is performed assessing pole performance from an internal decay perspective.

# GENERAL POLE INFORMATION

This paper looks at the performance of timber poles, in particular the treatment type and durability class. The following table applies to the species in each durability class.

| Pole Species | Durability Class |
| --- | --- |
| Grey Box | D1 |
| Coast Grex Box | D1 |
| Grey Gum | D1 |
| Red Ironbark | D1 |
| Grey Ironbark | D1 |
| White Mahogany | D1 |
| Ironbark | D1 |
| Tallowwood | D1 |
| Blackbutt | D2 |
| Spotted Gum | D2 |

# POLE TREATMENT AND DURABILITY 2 PERFORMANCE

Essential Energy has over 1.2M timber poles installed on its network. The two most common treatment types used are Pigment Emulsified Creosote (PEC) and Copper Chrome Arsenic (CCA); these treatments are impregnated into the pole in order to retard decay. Both treatment types are applied after harvest at supplier’s treatment facilities and both impregnate the sap wood of the pole, thus the retention of the sap wood is critical to the efficacy of the treatment. Being external treatments, it is logical to conclude that the effectiveness or otherwise of the treatment can be measured by the rate at which external cellular decay is retarded.

During inspection Essential Energy pole inspectors are asked to measure the external diameter above ground and at the ‘critical zone’. The definition of the ‘critical zone’ is left to the inspector’s judgement however generally the critical zone can be defined as between 0 and 450mm below ground, the revised inspection manual will define it as between 0 and 350mm. It is in this zone that the pole will generally experience its greatest mechanical loading and decay at this point will reduce the strength and thus the life of the pole.

Data was obtained from WASP for all in-service poles and matched to a similar extract of pole spatial information out of Smallworld. A calculation was performed using the ‘Above Ground Diameter’ and ‘Critical Zone Diameter’ such that a percentage external decay figure was obtained for every pole.

Percentage External Decay=1-Critical Zone DiameterAbove Ground Diameter

Analysis of the pole treatments applied and their performance over time was examined focusing on two of the most common durability 2 species Blackbutt and Spotted Gum. Durability 2 pole were selected for analysis as it is these poles for which the treatments are applied to with the intent to achieve similar performance to a Durability 1 pole. Furthermore the question of Blackbutt service performance versus Spotted Gum can also be addressed.

# DATA SOURCES

Data was obtained from WASP, Smallworld and some data validation work on spatial location of assets out of the reliability database.

The WASP data set was for all poles currently on the network as of the 29 April 2013 and also all system update dates for critical zone and ground line diameters. The Smallworld data set was obtained for all poles listing their depot, latitude and longitude and region to match to the WASP data set. The reliability data set was used to verify the match and plug any holes in the data match.

# DATA CONSIDERATIONS

As with all data systems ‘errors’ and interpretation problems are introduced over time due to the design and configuration of the data capture systems, combined with historical business rules and human error these data ‘errors’ can cause statistical anomalies and invalid conclusions. Essential Energy’s systems are not immune to this occurrence. Generally speaking from a high level data analysis one can accept that the ‘errors’ will be evenly spread across the data set and thus will not affect the analysis outcomes greatly or alter comparisons. However the more granular the analysis the more likely it is that these ‘errors’ will influence the analysis and it is inversely proportional. As the data is sliced into smaller blocks there is more chance that the errors will influence the conclusions. It is for that reason that an understanding of the business rules, historical context of the data, the system architecture and a good understanding of the asset the data is representing is required to filter out these ‘errors’ such that a cleansed data set is used for detailed analysis.

This section details the steps taken to arrive at a cleansed data set.

## Durability 2 Poles Initial Data

In the raw data set the numbers fall as per the following table for Blackbutt and Spotted Gum;

Table 1 Initial Data Statistics

| Poles Treatment | Species |  |  |
| --- | --- | --- | --- |
|  | Blackbutt | Spotted Gum | Grand Total |
| Copper Chrome Arsenic(CCA) | 104,324 | 189,443 | 293,767 |
| Copper Chrome Napthenate(CCN) | 812 | 988 | 1,800 |
| Desapped Durable(DES) | 171 | 147 | 318 |
| Low Temperature Creosote | 4,156 | 5,340 | 9,496 |
| Natural Round | 3,402 | 3,320 | 6,722 |
| Pigment Emulsified Creosote | 50,230 | 40,694 | 90,924 |
| Pressure Impregnated(PI) | 53,821 | 81,234 | 135,055 |
| Unknown Timber | 604 | 707 | 1,311 |
| Grand Total | 217,520 | 321,973 | 539,393 |

## Data Filtering

The data was filtered to arrive at a dataset which can be used as a starting point for further analysis. The filters applied were;

- Pole Material – Timber only (due to some corrupt data there are a limited number of steel or concrete poles with species listed against them. The data team are working on this data to fix problems).

- Wall thickness – If there was no wall thickness measure on the pole the pole was excluded from the analysis.

- Only Essential Energy poles were included. Whilst private poles could have been included they have been excluded, as over time it is not certain that private poles have had the same level of maintenance and care as Essential Energy owned poles. Thus the management practices of private poles could unduly affect the analysis and are excluded.

After filtering the number of poles for Blackbutt and Spotted Gum that were PEC or CCA treated was as follows:

Table 2 Durability 2 poles Filtered Data Statistics

|  | Species |  |  |
| --- | --- | --- | --- |
| Poles Treatment | Blackbutt | Spotted Gum | Grand Total |
| Copper Chrome Arsenic(CCA) | 89,819 | 177,216 | 267,035 |
| Pigment Emulsified Creosote | 48,397 | 38,591 | 86,988 |
| Grand Total | 138,216 | 215,807 | 354,023 |

## Data Cleansing

After filtering, the data was cleansed to remove as much of the data in error as possible, some of this is due to business rules applied to the data others due to the inherent data structure and system design. Some of the cleansing was also done as a result of cross system data comparisons i.e. matching WASP data to Smallworld data for spatial analysis.

- Records with an installed date of 01/01/1901 or 01/01/1900 were removed. This is a legacy date used for some assets for the initial data transfer to WASP in 2002 where the date of the asset is unknown.

- Records where an install date was not populated were excluded as an age for the pole cannot be determined.

- Records for which a latitude or longitude couldn’t be determined were removed from the analysis. These records were generally deleted poles or poles with no depot attached to them in WASP.

- WASP has only one record for the physical pole and the pole location. Consequently there is no asset hierarchy separation between the pole and its spatial data. This model of asset hierarchy has limitations as extracting historical information is difficult to do with accuracy. When a pole is replaced if the asset condition history is not correctly managed then the history of the previous pole can be attached to the new pole. To remove as much of this as possible a data extract from WASP was obtained and the latest critical zone diameter update date in WASP was compared to the recorded install date of the pole. Any records that had a critical diameter date prior to the install date were removed from the analysis.

- Another consequence of the WASP asset hierarchy is that it is possible for the previous conditional data to be valid for the ‘new’ pole or that the update date for the critical diameter measurement is the same as the date for install. (Due to the update processes in WASP, the update date for attributes and conditional measures is system driven when an attribute is updated in WASP).  To remove this error the date for install was compared to closed and completed pole replacement tasks if the date installed year minus the pole replacement task year was less than 2 the records was excluded where a critical zone diameter percentage external decay was greater than 0. The advantage of this is that the pole replace task completion date is manually entered so in theory is what actually happened, by using the percentage decay as a guide it is reasonable to expect there would be no external decay for any pole that is only 2 years old. Hence more ‘dubious’ records are removed from the analysis by this method.

- Duplicate pole numbers; in the raw data extract there was a number of records (28,762 records) found for where poles have the same pole number these records were removed from the data set. In this case all records for the pole were removed in order to ensure that no conditional data was incorrectly attributed to the wrong pole. Note it is quite acceptable for poles to have the same asset label. This is a legacy issue due to the formation of Essential Energy and predecessor organisations numbering regimes.

- PEC poles; Essential Energy and its’ predecessors ceased to buy PEC poles around 2002 roughly at the formation of Country Energy. The WASP extract has PEC poles that are younger than this so PEC poles younger than 11 years have been removed from the data set.

- Human error and data typos: It is reasonable to assume that a treated pole less than 5 years old will have less than 5% external decay (5% decay on a 320mm pole is around 16mm of external decay far more than would be expected on a 5 year old pole). However these sorts of figures are found in the data set. They can be attributed to a number of human related errors. For example someone updates the install year, but puts in the wrong date, or transposes some numbers. To remove these obvious errors any pole that had more than 5% of decay that was less than 5 years old was removed from the data set.

As a result of this cleansing activity the following pole data remained for detailed analysis and is the basis of the pole treatment and Blackbutt versus Spotted Gum species analysis.

Table 3 Durability 2 Final Cleansed Data for analysis statistics

|  | Species |  |  |
| --- | --- | --- | --- |
| Poles Treatment | Blackbutt | Spotted Gum | Grand Total |
| Copper Chrome Arsenic(CCA) | 72,677 | 164,294 | 236,971 |
| Pigment Emulsified Creosote | 45,861 | 37,338 | 83,199 |
| Grand Total | 118,538 | 201,632 | 320,170 |

The remaining data as shown in Table 3 after all the cleaning and filtering is still a very large number of poles for analysis and it is reasonable to conclude that the results of the analysis will be valid given the high population figures.

# DURABILITY 2 POLE PERFORMANCE AND TREATMENT ANALYSIS

The statistical breakdown of the cleansed data by pole treatment and D2 species is as shown in the following table. As the data is for every pole the last inspection date can be over 4 years old. (Note: Essential Energy employs a 4 year inspection cycle with a 6 months buffer)

The population of CCA treated poles is increasing whereas the population of PEC poles is static. Thus for the statistical comparison in order to compare like with like populations any CCA pole that was younger than 11 years has been excluded from the statistical analysis. By 2002 all of the Country Energy area had ceased to use PEC poles; however some regions ceased using PEC well before 2002.

Table 4 Durability 2 Statistical breakdown Percentage External Decay

|  |  | Durability 2 Percentage of External Decay |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Pole Species | Pole Treatment | 0% | > 0-10% | > 10-20% | > 20-30% | > 30-40% | Grand Total |
| Blackbutt | CCA | 39,282 | 323 | 65 | 3 | 3 | 39,676 |
|  | PEC | 44,780 | 231 | 20 | 2 |  | 45,033 |
| Spotted Gum | CCA | 134,976 | 3,887 | 2,002 | 205 | 16 | 141,086 |
|  | PEC | 36,894 | 288 | 51 | 7 | 3 | 37,243 |
| Grand Total |  | 255,932 | 4,729 | 2,138 | 217 | 22 | 263,038 |

The following table is the same data but by percentage of the total population by species and treatment type.

Table 5 Durability 2 Statistical breakdown Percentage External Decay – Population Percentage

|  |  | Durability 2 Percentage of External Decay |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Pole Species | Pole Treatment | 0% | > 0-10% | > 10-20% | > 20-30% | > 30-40% | Grand Total |
| Blackbutt | CCA | 99.007% | 0.814% | 0.164% | 0.008% | 0.008% | 100% |
|  | PEC | 99.438% | 0.513% | 0.044% | 0.004% | 0.000% | 100% |
| Spotted Gum | CCA | 95.669% | 2.755% | 1.419% | 0.145% | 0.011% | 100% |
|  | PEC | 99.063% | 0.773% | 0.137% | 0.019% | 0.008% | 100% |
| Grand Total |  | 97.298% | 1.798% | 0.813% | 0.082% | 0.008% | 100% |

The next table shows the split up by per cent decay and average age of the poles including standard deviation.

Table 6 Durability 2 Statistical breakdown Percentage External Decay – age and standard deviation

|  |  | Durability 2 Percentage of External Decay |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Pole Species | Pole Treatment | 0% |  |  | > 0-10% |  |  | > 10-20% |  |  | > 20-30% |  |  | > 30-40% |  |  | Grand Total |  |  |
|  |  | Pole Count | Avg Age | Std Dev | Pole Count | Avg Age | Std Dev | Pole Count | Avg Age | Std Dev | Pole Count | Avg Age | Std Dev | Pole Count | Avg Age | Std Dev | Pole Count | Avg Age | Std Dev |
| Blackbutt | CCA | 39,307 | 24.9 | 8.8 | 323 | 34.7 | 9.9 | 65 | 34.9 | 8.5 | 3 | 37.0 | 9.6 | 3 | 35.3 | 11.6 | 39,701 | 25.0 | 8.8 |
|  | PEC | 44,801 | 26.7 | 9.6 | 231 | 31.6 | 8.9 | 20 | 40.6 | 15.9 | 2 | 39.5 | 2.1 |  |  |  | 45,054 | 26.7 | 9.6 |
| Spotted Gum | CCA | 135,018 | 25.8 | 8.3 | 3,887 | 37.9 | 6.3 | 2,002 | 39.0 | 5.5 | 205 | 39.5 | 4.9 | 16 | 37.9 | 6.9 | 141,128 | 26.4 | 8.6 |
|  | PEC | 36,895 | 32.1 | 8.5 | 288 | 36.2 | 8.7 | 51 | 36.8 | 11.7 | 7 | 41.3 | 13.2 | 3 | 27.0 | 2.0 | 37,244 | 32.1 | 8.5 |
| Grand Total |  | 256,021 | 26.7 | 8.9 | 4,729 | 37.3 | 7.1 | 2,138 | 38.8 | 6.1 | 217 | 39.6 | 5.4 | 22 | 36.1 | 7.8 | 263,127 | 27.0 | 9.1 |

## Statistical Examination – Durability 2 Treatment Type

Examination of Table 4, Table 5 and Table 6 shows that irrespective of the species of the pole that PEC poles perform better than CCA treated poles. In Table 4 it can be seen that the number of PEC poles with external decay are lower than CCA poles for the same percentage grouping of external decay, Table 5 shows that the overall percentage of the total population of PEC poles by species for each decay grouping is lower than the equivalent grouping for CCA.

In reviewing Table 6  it is important to note that the CCA pole population has been censored to poles prior to 2002 to align the population to that of PEC poles. Consequently the average ages (grand totals) by treatment type and species are much the same. However if the CCA pole population was not censored then there would be a significant age difference as the PEC pole population is older than the CCA pole population.

The key question with regard to expected extra life of a PEC pole versus a CCA pole cannot be directly inferred from these tables as the geographical influence on the poles performance are not reflected in these tables. The spatial representation of the data plays a key part in interpreting this data set and is covered in a later section. However it is reasonable to conclude from Table 4, Table 5, and Table 6 that a PEC treated pole will perform better than a CCA treated pole. The degree to which this is true will be examined later.

## Statistical Examination – Durability 2 Pole Species

Reviewing Table 4, Table 5 and Table 6 it is apparent that PEC poles of both species perform approximately the same; however the same is not true for CCA treated poles. There is a distinct difference between a CCA treated Blackbutt pole and a Spotted Gum CCA treated pole.

Generally speaking a Spotted Gum CCA treated pole will experience more external decay than a Blackbutt treated pole. This conclusion is supported by the percentage of the population by species and treatment falling into each decay group, where Spotted Gum CCA treated poles has a much higher percentage of the total population than Blackbutt CCA poles. Examination of Table 6 shows that this higher percentage cannot be attributed to a significance difference in the average age profile for CCA treated Spotted Gum when compared to CCA treated Blackbutt.  The apparent exception here is for the 0-10% external decay band where the figures in Table 6 suggest a higher average age for CCA treated Spotted Gum versus CCA treated Blackbutt of approximately 3 years in favour of Blackbutt. This difference needs to be considered in light of the percentage of the population as shown in Table 5 where CCA treated Spotted Gum poles have roughly 3 times more chance of decay than CCA treated Blackbutt poles in this decay band. When the standard deviation is considered for the 0-10% external decay for CCA Spotted Gum versus CCA Blackbutt it is apparent that there is a wider spread in the Blackbutt population, this may be attributed to geographical location as shown in a later section.

Nevertheless based on the statistical figures in Table 4, Table 5, and Table 6 for all the other decay grouping the age profile for CCA treated Blackbutt versus CCA Spotted Gum and the standard deviations are very similar (within the bounds of statistical variation) but there are simply more Spotted Gum poles in each grouping. The conclusion is clear CCA treated Spotted Gum poles experience more external decay than Blackbutt poles. This statement needs to be measured against the spatial analysis in following sections.

## Durability 2 Spatial Analysis

The following figures show the spatial representation of the durability 2 poles by species and treatment type. As can be seen from Figures 1 – 4 whilst PEC and CCA poles are spread across the network PEC poles have their highest population density on the western side of the Great Dividing Range concentrating in the Northern part of the state. CCA poles are also spread across the state concentrating on the eastern seaboard and Central Tablelands. Consequently geographical location may play a significant part in the outcomes of the statistical analysis presented previously.

There is no geographical distinction based on species shown in the spatial analysis with Blackbutt and Spotted Gum distributed randomly throughout the footprint. These figures include all CCA poles (the CCA pole population has not been censored for the spatial representations)

Figure 1 CCA Spotted Gum 0% External Decay

Figure 2 CCA Blackbutt 0% External Decay

Figure 3 PEC Spotted Gum 0% External Decay

Figure 4 PEC Blackbutt 0% External Decay

## Durability 2 PEC External Decay Spatial Analysis

Examination of the figures for PEC external decay when compared to the zero decay figures for PEC (Figure 3 and Figure 4) shows clustering around Dubbo, minor clustering around Port Macquarie, Armidale and Inverell (see Figure 20), thereafter the distribution is relatively random for PEC poles with external decay and doesn’t follow the population density plots shown in Figure 3 and Figure 4. Of particular note is the lack of coastal issues with PEC poles.

## Durability 2 CCA External Decay Spatial Analysis

Examination of the figures for CCA external decay show significant clustering on the eastern seaboard from Taree through to the QLD boarder. Towns affected are Taree, Port Macquarie, Kempsey, Coffs Harbour, Grafton, Ballina, Lismore, Byron Bay, Casino, Kyogle, Coolangatta / Tweed Heads. Clustering is also found inland at Bathurst and Griffith. Some additional clustering is found at Moruya and Batemans Bay (see Figure 21). Interestingly the external decay for CCA poles aligns reasonably well with the population density plots (Figure 1 and Figure 2) suggesting that CCA decay is not as random as PEC poles and is associated with population density in high exposure areas.

## Durability 2 Spatial Analysis - Summary

Based on the spatial analysis it is apparent that PEC poles tend to have a more random external decay distribution over the footprint than CCA poles. CCA poles tend to have clusters of external decay that correlate to the population density of CCA poles in a particular area, this is not as apparent for PEC poles. The worst areas for CCA pole external decay is on the eastern seaboard of NSW from Taree up to the border. For PEC poles the worst area is Dubbo, this is due in part to the high PEC population in Dubbo which is also somewhat older than other PEC areas.

Given this spatial intelligence a more detailed analysis will be presented in a later section focusing on the depots in the high risk areas for PEC and CCA poles.

Further detailed analysis of pole performance with regard to external decay using spatial data is presented using Google Earth cadastre information. These views clearly show that there is a geographical component to the external decay for poles.

Figure 5 CCA Spotted Gum 0 - 10% External Decay

Figure 6 CCA Blackbutt 0 - 10% External Decay

Figure 7 PEC Spotted Gum 0 - 10% External Decay

Figure 8 PEC Blackbutt 0 - 10% External Decay

Figure 9 CCA Spotted Gum 10 - 20% External Decay

Figure 10 CCA Blackbutt 10 -20% External Decay

Figure 11 PEC Spotted Gum 10 - 20% External Decay

Figure 12 PEC Blackbutt 10 - 20% External Decay

Figure 13 CCA Spotted Gum 20 - 30% External Decay

Figure 14 CCA Blackbutt 20 - 30% External Decay

Figure 15 PEC Spotted Gum 20 - 30% External Decay

Figure 16 PEC Blackbutt 20 - 30% External Decay

Figure 17 CCA Spotted Gum 30 - 40% External Decay

Figure 18 CCA Blackbutt 30 - 40% External Decay

Figure 19 PEC Spotted Gum 30 - 40% External Decay

Figure 20 All PEC poles with External Decay

Figure 21 All CCA poles with External Decay

# DETAILED HIGH RISK AREA DURABILITY 2 ANALYSIS

Based on the above spatial analysis a detailed analysis for the depots / towns where clustering of external decay is evident for PEC and CCA poles has been performed. This removes the ‘randomly’ distributed decayed poles from the analysis and provides a view of pole treatment and species performance in the ‘worst’ environments.

The depots selected for detailed analysis are;

Taree, Port Macquarie, Kempsey, Coffs Harbour, Grafton, Ballina, Lismore, Casino, Kyogle, Coolangatta/Tweed Heads, Bathurst, Griffith, Moruya, Dubbo, Armidale and Inverell.

A full data analysis by the above depots is presented in APPENDIX A  the summary figures from this analysis are presented in the following tables;

Table 7 Durability 2 Pole External Decay by Selected Depot - Part A

|  |  | Durability 2 Pole Decay analysis – Selected Depots |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Pole Species | Pole Treatment | 0% |  |  |  | > 0-10% |  |  |  | > 10-20% |  |  |  |
|  |  | Pole Count | % of Pop | Avg Age | Std Dev | Pole Count | % of Pop | Avg Age | Std Dev | Pole Count | % of Pop | Avg Age | Std Dev |
| Blackbutt | CCA | 13,186 | 98.27% | 28.3 | 8.6 | 179 | 1.33% | 36.9 | 9.1 | 48 | 0.36% | 35.9 | 7.4 |
|  | PEC | 9,762 | 98.92% | 29.2 | 10.4 | 96 | 0.97% | 34.2 | 7.3 | 9 | 0.09% | 49.0 | 19.7 |
| Spotted Gum | CCA | 56,858 | 93.24% | 28.0 | 8.1 | 2,440 | 4.00% | 38.4 | 5.6 | 1494 | 2.45% | 39.2 | 5.3 |
|  | PEC | 8,305 | 98.18% | 34.1 | 9.2 | 126 | 1.49% | 38.3 | 8.5 | 24 | 0.28% | 40.5 | 13.0 |
| Grand Total |  | 88,111 | 95.02% | 28.7 | 8.7 | 2,841 | 3.06% | 38.1 | 6.1 | 1,575 | 1.70% | 39.2 | 5.8 |

Table 8 Durability 2 Pole External Decay by Selected Depot - Part B

|  |  | Durability 2 Pole Decay analysis – Selected Depots |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Pole Species | Pole Treatment | > 20-30% |  |  |  | > 30-40% |  |  |  | Grand Total |  |  |
|  |  | Pole Count | % of Pop | Avg Age | Std Dev | Pole Count | % of Pop | Avg Age | Std Dev | Pole Count | Avg Age | Std Dev |
| Blackbutt | CCA | 2 | 0.01% | 42.5 | 2.1 | 3 | 0.02% | 35.3 | 11.6 | 13,418 | 28.4 | 8.6 |
|  | PEC | 2 | 0.02% | 39.5 | 2.1 |  | 0.00% |  |  | 9,869 | 29.2 | 10.4 |
| Spotted Gum | CCA | 178 | 0.29% | 40.0 | 4.0 | 12 | 0.02% | 41.3 | 1.6 | 60,982 | 28.7 | 8.4 |
|  | PEC | 4 | 0.05% | 45.3 | 5.4 |  | 0.00% |  |  | 8,459 | 34.2 | 9.2 |
| Grand Total |  | 186 | 0.20% | 40.2 | 4.1 | 15 | 0.02% | 40.1 | 5.2 | 92,728 | 29.2 | 8.9 |

Given that Table 7 and Table 8 represent the worst depots in Essential Energy for external decay issues the data presented has some interesting outcomes. Despite anecdotal evidence to suggest a PEC pole will last longer with external decay this assertion is not supported by the data. In examining the 0-10% external decay grouping it can been seen that irrespective of the treatment type there is no significant difference in average age or standard deviation, differences are notable between species as discussed in prior sections. However if the percentage of the population by species figures are examined there is a clear distinction between the treatment type employed. For Blackbutt the percentage of the population figures suggest there is minimal difference in treatment, however for Spotted Gum there is a distinct difference PEC treated Spotted Gum poles are clearly better than CCA treated Spotted Gum poles. In examining the 10-20% external decay grouping the performance distinction by population for Spotted Gum as noted in the 0-10% grouping is present, however it is notable that there is a difference for Blackbutt between PEC and CCA by percentage of the population for PEC treated Blackbutt poles. This conclusion needs to be moderated by the small sample size and reference to Table 5 should be made to support this argument.

The following hypothesis is drawn for the preceding analysis in regards to treatment.

- For PEC treated poles if the pole species is Spotted Gum there is a higher probability that the pole will rot externally than if it is a Blackbutt pole (1.49% versus 0.97% respectively, 0–10% decay band).

- For a CCA pole Spotted Gum has a higher probability of external decay than Blackbutt (4% versus 1.33% respectively, 0–10% decay band).

- There is a notable difference between a CCA treated Spotted Gum pole and a PEC Spotted Gum pole. The PEC treated Spotted Gum has a lower probability of external decay than its CCA treated sister (1.49% versus 4% respectively, 0-10% decay band).

The data also suggests that for a PEC pole any external decay is arrested or proceeds more slowly than a CCA pole as can be noted from the percentage of the population figures for the 10-20% external decay as shown in Table 7 and Table 5. This hypothesis will be examined further to test its veracity.

## Durability 2 Treatment Hypothesis Examination

The question is does a PEC pole that experiences external decay either have the decay arrested by the treatment or proceeds less quickly than a CCA treated pole. To test this hypothesis the following charts and table were developed to examine the progress of decay for the full Essential Energy data set (not selected depots).

Figure 22 0-10% External Decay CCA poles by D2 species

Figure 23 0-10% External Decay PEC poles by D2 species

Figure 22 and Figure 23 do not show any significant difference in the shape and distribution of the curve for PEC when compared to CCA, this suggest that external decay in PEC poles is not arrested (stopped) any more than it is in a CCA pole but it is possible that it is retarded which is explored in Table 9.

Table 9 Durability 2 External Decay 0-10% by Treatment

| Percentage External Decay | Treatment | Number of Poles | Average Age | Standard Deviation |
| --- | --- | --- | --- | --- |
| 0 | Pigment Emulsified Creosote | 4 | 30.3 | 7.6 |
|  | Copper Chrome Arsenic(CCA) | 1 | 31.0 |  |
| 1 | Pigment Emulsified Creosote | 1 | 31.0 |  |
|  | Copper Chrome Arsenic(CCA) | 10 | 36.7 | 7.5 |
| 2 | Pigment Emulsified Creosote | 2 | 29.5 | 4.9 |
|  | Copper Chrome Arsenic(CCA) | 97 | 32.8 | 10.2 |
| 3 | Pigment Emulsified Creosote | 106 | 30.4 | 7.2 |
|  | Copper Chrome Arsenic(CCA) | 565 | 36.9 | 7.6 |
| 4 | Pigment Emulsified Creosote | 115 | 35.1 | 10.1 |
|  | Copper Chrome Arsenic(CCA) | 901 | 37.0 | 6.7 |
| 5 | Pigment Emulsified Creosote | 19 | 39.4 | 7.8 |
|  | Copper Chrome Arsenic(CCA) | 137 | 38.4 | 6.4 |
| 6 | Pigment Emulsified Creosote | 99 | 32.8 | 9.9 |
|  | Copper Chrome Arsenic(CCA) | 465 | 37.7 | 6.9 |
| 7 | Pigment Emulsified Creosote | 77 | 34.2 | 7.5 |
|  | Copper Chrome Arsenic(CCA) | 808 | 37.8 | 6.5 |
| 8 | Pigment Emulsified Creosote | 55 | 37.7 | 9.0 |
|  | Copper Chrome Arsenic(CCA) | 724 | 38.8 | 6.1 |
| 9 | Pigment Emulsified Creosote | 26 | 36.5 | 7.0 |
|  | Copper Chrome Arsenic(CCA) | 305 | 38.4 | 5.3 |
| 10 | Pigment Emulsified Creosote | 15 | 39.6 | 8.2 |
|  | Copper Chrome Arsenic(CCA) | 197 | 39.1 | 5.5 |
| Grand Total |  | 4,729 | 37.3 | 7.1 |

From Table 9 it is clear there is no significant difference in the treatment types in terms of average age or standard deviation where there is a sufficient sample size. Consequently it is reasonable to suggest that the external decay once present in PEC pole is not retarded any more so than what is possible with a CCA pole.

After detailed examination it is apparent that the data does not support the proposed hypothesis that PEC pole with external decay will not continue to decay any slower than a CCA pole, however it is possible that a PEC pole particularly a Spotted Gum is simply less likely to experience external decay at all when compared to a CCA pole. To examine this possibility the percentage of the population in the 0 – 40% decay grouping will be examined by treatment type as shown for the entire network in the following tables.

## Overall Statistics Durability 2 Poles

The following tables present the overall statistics by treatment type for D2 poles.

Table 10 Durability 2 (Blackbutt and Spotted Gum) Pole External Decay Statistics - Entire Network

| Durability 2 Pole External Decay – Entire Network |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Treatment | 0% |  | > 0 – 40% |  | Grand Total |  |
|  | Num of Poles | % of Pop | Num of Poles | % of Pop | Num of Poles | % of Pop |
| Copper Chrome Arsenic(CCA) | 174,258 | 96.40% | 6504 | 3.60% | 180,762 | 100.00% |
| Pigment Emulsified Creosote | 81,674 | 99.27% | 602 | 0.73% | 82,276 | 100.00% |
| Grand Total | 255,932 | 97.30% | 7106 | 2.70% | 263,038 | 100.00% |

Table 11 Durability 2 Poles External Decay Age Statistics - Entire Network

| Durability 2 Pole External Decay – Entire Network |  |  |  |  |
| --- | --- | --- | --- | --- |
| Treatment | 0% |  | > 0 – 40% |  |
|  | Avg Age | Std Dev | Avg Age | Std Dev |
| Copper Chrome Arsenic(CCA) | 25.66 | 8.45 | 38.15 | 6.40 |
| Pigment Emulsified Creosote | 29.09 | 9.51 | 34.69 | 9.71 |

Table 12 Durability 2 (Blackbutt and Spotted Gum) External Decay Statistics – Selected Depots

| Durability 2 Pole External Decay – Selected Depots |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Treatment | 0% |  | > 0 – 40% |  | Grand Total |  |
|  | Num of Poles | % of Pop | Num of Poles | % of Pop | Num of Poles | % of Pop |
| Copper Chrome Arsenic(CCA) | 70,044 | 94.15% | 4356 | 5.85% | 74,400 | 100.00% |
| Pigment Emulsified Creosote | 18,067 | 98.58% | 261 | 1.42% | 18,328 | 100.00% |
| Grand Total | 88,111 | 95.02% | 4617 | 4.98% | 92,728 | 100.00% |

Table 13 Durability 2 Poles External Decay Age Statistics – Selected Depots

| Durability 2 Pole External Decay – Selected Depots |  |  |  |  |
| --- | --- | --- | --- | --- |
| Treatment | 0% |  | > 0 – 40% |  |
|  | Avg Age | Std Dev | Avg Age | Std Dev |
| Copper Chrome Arsenic(CCA) | 28.07 | 8.20 | 38.69 | 5.67 |
| Pigment Emulsified Creosote | 31.42 | 10.17 | 37.47 | 9.61 |

Examination of Table 10 shows that a PEC pole for the entire network on average has a 0.73% chance of experiencing external decay, where as a CCA pole has a 3.60% chance of experiencing external decay (roughly a 5:1 ratio in favour of PEC). Investigation of Table 12 for the selected high risk depots again shows a better performance from PEC poles; in these areas a PEC pole has a 1.42% chance of experiencing external decay versus a CCA pole with a 5.85% chance (roughly a 4:1 ratio). These figures do not need to be normalised to the age of the poles as it can be seen from Table 6 and Table 9 the pole irrespective of treatment have within the realms of reasonable statistical variation much the same average age when they experience external decay irrespective of treatment type used. The performance of CCA poles in regards to external decay is significantly influences by CCA treated Spotted Gum poles which are more prone to external decay than a CCA treated Blackbutt pole.

The conclusion is thus, a PEC pole is simply not as prone to the inception of external decay, however if it gets external decay it will decay in a like manner to CCA treated poles.

# POLE TREATMENT AND DURABILITY 1 PERFORMANCE

Essential Energy has over 1.2M timber poles installed on its network. The two most common treatment types used are Pigment Emulsified Creosote (PEC) and Copper Chrome Arsenic (CCA). This section will evaluate the performance of CCA or PEC treated Durability 1 class poles as defined by AS5604.

To arrive at a filtered and cleansed data set the same criteria and methods for filtering and cleansing were performed as detailed in the Data Filtering and Data Cleansing sections.

As for D2 poles the population of CCA treated poles is increasing whereas the population of PEC poles is static. Thus for the statistical comparison in order to compare like with like populations any CCA pole that was younger than 11 years has been excluded from the statistical analysis. This allows for as close as can be practically achieved a ‘like for like’ comparison between PEC poles and CCA poles given that by 2002 all of the Country Energy areas had ceased to use PEC even though some were much earlier. Most of the excluded CCA poles (less than 11 years) fall into the 0 decay grouping.

(Note for the spatial analysis all poles irrespective of their age were included, this allowed for a full presentation of the high risk areas).

The following tables show the statistical breakdown of durability class 1 poles by species and treatment type for external decay.

Table 14 Durability 1 Statistical breakdown Percentage External Decay

|  |  | Percentage of External Decay |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Pole Species | Pole Treatment | 0% | 0-10% | 10-20% | 20-30% | 30-40% | Grand Total |
| Coast Grey Box | Copper Chrome Arsenic(CCA) | 3,818 | 77 | 33 | 3 |  | 3,931 |
|  | Pigment Emulsified Creosote | 684 | 4 | 1 |  |  | 689 |
| Grey Box | Copper Chrome Arsenic(CCA) | 5,019 | 40 | 8 |  |  | 5,067 |
|  | Pigment Emulsified Creosote | 1,578 | 12 | 1 |  |  | 1,591 |
| Grey Gum | Copper Chrome Arsenic(CCA) | 5,513 | 61 | 3 |  |  | 5,577 |
|  | Pigment Emulsified Creosote | 1,950 | 12 | 1 |  |  | 1,963 |
| Grey Ironbark | Copper Chrome Arsenic(CCA) | 11,093 | 142 | 22 |  |  | 11,257 |
|  | Pigment Emulsified Creosote | 4,541 | 28 | 5 | 1 |  | 4,575 |
| Ironbark | Copper Chrome Arsenic(CCA) | 19,643 | 159 | 54 | 3 |  | 19,859 |
|  | Pigment Emulsified Creosote | 6,679 | 69 | 7 |  | 1 | 6,756 |
| Red Ironbark | Copper Chrome Arsenic(CCA) | 5,516 | 66 | 6 |  |  | 5,588 |
|  | Pigment Emulsified Creosote | 3,819 | 20 | 2 |  |  | 3,841 |
| Tallowwood | Copper Chrome Arsenic(CCA) | 7,448 | 35 | 8 |  |  | 7,491 |
|  | Pigment Emulsified Creosote | 2,668 | 26 | 4 |  |  | 2,698 |
| White Mahogany | Copper Chrome Arsenic(CCA) | 2,612 | 13 | 3 |  |  | 2,628 |
|  | Pigment Emulsified Creosote | 994 | 6 |  |  |  | 1,000 |
| Grand Total |  | 83,575 | 770 | 158 | 7 | 1 | 84,511 |

Table 15 Durability 1 Statistical breakdown Percentage External Decay – Population Percentage

|  |  | Percentage of External Decay |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Pole Species | Pole Treatment | 0% | 0-10% | 10-20% | 20-30% | 30-40% | Grand Total |
| Coast Grey Box | Copper Chrome Arsenic(CCA) | 97.13% | 1.96% | 0.84% | 0.08% | 0.00% | 100% |
|  | Pigment Emulsified Creosote | 99.27% | 0.58% | 0.15% | 0.00% | 0.00% | 100% |
| Grey Box | Copper Chrome Arsenic(CCA) | 99.05% | 0.79% | 0.16% | 0.00% | 0.00% | 100% |
|  | Pigment Emulsified Creosote | 99.18% | 0.75% | 0.06% | 0.00% | 0.00% | 100% |
| Grey Gum | Copper Chrome Arsenic(CCA) | 98.85% | 1.09% | 0.05% | 0.00% | 0.00% | 100% |
|  | Pigment Emulsified Creosote | 99.34% | 0.61% | 0.05% | 0.00% | 0.00% | 100% |
| Grey Ironbark | Copper Chrome Arsenic(CCA) | 98.54% | 1.26% | 0.20% | 0.00% | 0.00% | 100% |
|  | Pigment Emulsified Creosote | 99.26% | 0.61% | 0.11% | 0.02% | 0.00% | 100% |
| Ironbark | Copper Chrome Arsenic(CCA) | 98.91% | 0.80% | 0.27% | 0.02% | 0.00% | 100% |
|  | Pigment Emulsified Creosote | 98.86% | 1.02% | 0.10% | 0.00% | 0.01% | 100% |
| Red Ironbark | Copper Chrome Arsenic(CCA) | 98.71% | 1.18% | 0.11% | 0.00% | 0.00% | 100% |
|  | Pigment Emulsified Creosote | 99.43% | 0.52% | 0.05% | 0.00% | 0.00% | 100% |
| Tallowwood | Copper Chrome Arsenic(CCA) | 99.43% | 0.47% | 0.11% | 0.00% | 0.00% | 100% |
|  | Pigment Emulsified Creosote | 98.89% | 0.96% | 0.15% | 0.00% | 0.00% | 100% |
| White Mahogany | Copper Chrome Arsenic(CCA) | 99.39% | 0.49% | 0.11% | 0.00% | 0.00% | 100% |
|  | Pigment Emulsified Creosote | 99.40% | 0.60% | 0.00% | 0.00% | 0.00% | 100% |
| Grand Total |  | 98.89% | 0.91% | 0.19% | 0.01% | 0.00% | 100% |

Table 15 presents an interesting data set when compared to the equivalent table of data for Durability 2 poles (Table 5). Overall based on these tables a D1 pole has a lower chance of external decay than a D2 pole (for the 0 – 10% decay grouping a D2 pole has a 1.798% of decay, for a D1 pole 0.91%). However for D2 poles the external decay figures are significantly influenced by the performance of Spotted Gum poles. If the D2 class consisted of Blackbutt only then the performance from an external decay population percentage will be similar to that of D1 pole. However this conclusion needs to be moderated by an assessment of the average age for external decay for D1 poles and spatial analysis which is presented below.

Table 16 Durability 1 Statistical breakdown Percentage External Decay – age and standard deviation

|  |  | Durability 1 Percentage of External Decay |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Pole Species | Pole Treatment | 0% |  |  | > 0-10% |  |  | > 10-20% |  |  | > 20-30% |  |  | > 30-40% |  |  | Grand Total |  |  |
|  |  | Pole Count | Avg Age | Std Dev | Pole Count | Avg Age | Std Dev | Pole Count | Avg Age | Std Dev | Pole Count | Avg Age | Std Dev | Pole Count | Avg Age | Std Dev | Pole Count | Avg Age | Std Dev |
| Coast Grey Box | CCA | 3,820 | 25.8 | 6.7 | 77 | 36.8 | 7.3 | 33 | 37.3 | 6.2 | 3 | 36.7 | 5.8 |  |  |  | 3,933 | 26.1 | 6.9 |
|  | PEC | 684 | 26.7 | 8.6 | 4 | 40.0 | 13.0 | 1 | 44.0 |  |  |  |  |  |  |  | 689 | 26.8 | 8.7 |
| Grey Box | CCA | 5,020 | 22.2 | 7.3 | 40 | 32.7 | 8.8 | 8 | 33.9 | 8.7 |  |  |  |  |  |  | 5,068 | 22.3 | 7.4 |
|  | PEC | 1,579 | 29.0 | 8.4 | 12 | 36.0 | 17.2 | 1 | 18.0 |  |  |  |  |  |  |  | 1,592 | 29.0 | 8.6 |
| Grey Gum | CCA | 5,516 | 25.4 | 6.6 | 61 | 30.6 | 8.7 | 3 | 38.0 | 11.1 |  |  |  |  |  |  | 5,580 | 25.5 | 6.7 |
|  | PEC | 1,948 | 29.9 | 8.1 | 12 | 32.9 | 9.7 | 1 | 56.0 |  |  |  |  |  |  |  | 1,961 | 29.9 | 8.1 |
| Grey Ironbark | CCA | 11,096 | 24.0 | 7.5 | 142 | 40.7 | 8.7 | 22 | 37.3 | 8.4 |  |  |  |  |  |  | 11,260 | 24.2 | 7.8 |
|  | PEC | 4,541 | 27.9 | 7.1 | 28 | 30.0 | 12.0 | 5 | 27.6 | 3.9 | 1 | 28.0 |  |  |  |  | 4,575 | 27.9 | 7.2 |
| Ironbark | CCA | 19,653 | 22.6 | 7.7 | 161 | 33.1 | 9.5 | 54 | 36.8 | 8.3 | 3 | 40.0 | 1.0 |  |  |  | 19,871 | 22.8 | 7.8 |
|  | PEC | 6,682 | 33.7 | 9.6 | 69 | 39.2 | 10.9 | 7 | 35.9 | 10.2 |  |  |  | 1 | 40 |  | 6,759 | 33.7 | 9.6 |
| Red Ironbark | CCA | 5,517 | 26.4 | 6.5 | 66 | 36.7 | 8.8 | 6 | 42.8 | 9.0 |  |  |  |  |  |  | 5,589 | 26.6 | 6.7 |
|  | PEC | 3,819 | 28.1 | 6.9 | 20 | 30.4 | 10.3 | 2 | 24.0 | 0.0 |  |  |  |  |  |  | 3,841 | 28.1 | 6.9 |
| Tallowwood | CCA | 7,450 | 24.4 | 6.8 | 35 | 35.2 | 10.2 | 9 | 35.8 | 10.9 |  |  |  |  |  |  | 7,494 | 24.5 | 6.8 |
|  | PEC | 2,668 | 30.6 | 7.9 | 26 | 33.2 | 9.4 | 4 | 32.0 | 3.8 |  |  |  |  |  |  | 2,698 | 30.6 | 7.9 |
| White Mahogany | CCA | 2,612 | 25.1 | 6.3 | 13 | 28.6 | 9.0 | 3 | 33.0 | 5.6 |  |  |  |  |  |  | 2,628 | 25.1 | 6.3 |
|  | PEC | 994 | 29.1 | 7.5 | 6 | 34.5 | 7.9 |  |  |  |  |  |  |  |  |  | 1,000 | 29.1 | 7.5 |
| Grand Total |  | 83,599 | 25.7 | 8.2 | 772 | 35.4 | 10.0 | 159 | 36.4 | 8.4 | 7 | 36.9 | 5.4 | 1 | 40 |  | 84,538 | 25.8 | 8.3 |

Comparing Table 16 to Table 6 doesn’t show a significant difference in the average age for external decay of a D1 pole versus a D2 pole. However it is clear from Table 16 that some D1 species have a much higher average age than D2 species for external decay. Based on this table it can be stated that a D1 pole with external decay will have it occur (if it occurs) at roughly the same time as a D2 pole. The question is does it progress more slowly than a D2 pole and is there spatial differences to the external decay found in D2 poles versus D1 poles.

## Durability 1 Spatial Analysis

The following figures show the spatial representation of the durability 1 poles by species and treatment type.

Figure 24 D1 CCA poles 0 Per cent External Decay

Figure 25 D1 PEC poles 0 per cent External Decay

Figure 26 D1 CCA 0 - 10% External Decay

Figure 27 D1 PEC 0 - 10% External Decay

Figure 28 D1 CCA 20 - 30% External Decay

Figure 29 D1 PEC 20 - 30 % External Decay

Figure 30 D1 PEC 30 - 40% External Decay

Figure 31 All D1 PEC Poles with External Decay

Figure 32 All D1 CCA Poles with External Decay

Examination of Figure 24 to Figure 32 shows some interesting results for D1 PEC poles the lack of PEC treated D1 poles  on the eastern seaboard makes it difficult to assess the performance of D1 PEC poles in this area. However based on the external decay figures for CCA and PEC poles the high risk areas are; Dubbo, Grenfell, Cowra, Griffith, Taree, Port Macquarie, Kempsey, Coffs Harbour, Grafton, Ballina, Lismore, Casino, Murwillumbah, Tweed Heads and Coolangatta.

# DETAILED HIGH RISK AREA DURABILITY 1 ANALYSIS

The depots for detailed analysis are;

Dubbo, Grenfell, Cowra, Griffith, Taree Port Macquarie, Kempsey, Coffs Harbour, Grafton, Ballina, Lismore, Casino,  Murwillumbah, Tweed Heads.

Given that Table 17 and Table 8 represent the worst depots in Essential Energy for external decay issues the data presented has some interesting outcomes. In examining the 0-0% external decay grouping it can been seen that for some species there is a distinctly better performance if they are PEC treated, whilst in some cases the converse is true with a CCA pole performing better based on average age and percentage of population. However as noted in the spatial analysis there are few D1 PEC on the North Coast, based on the D2 analysis it is clear this area is the worst for external decay, this assertion is also supported by the  amount of decay found in CCA treated D1 poles in these areas.

For PEC treated D1 poles based on the data in the tables for the 0–10% external decay grouping  Grey Box, Ironbark, Red Ironbark and Tallowwood PEC treated poles performance is not as good as for the same species treated with CCA based on the average age, standard deviation or percentage of the population. Some of this can be attributed to a low sample size thus a reduced confidence in the figures particularly for Grey Box, and Red Ironbark. For Ironbark whist there is a higher percentage of the population with external decay than CCA the average age is 7 years higher and the standard deviation is 3 years tighter indicating on average a Ironbark PEC will experience external decay later than a CCA treated pole and will tend to be more closely grouped in terms of the age when external decay is found than a CCA Ironbark pole.

Table 17 Durability 1 Pole External Decay by Selected Depot - Part A

|  |  | Durability 1 Pole Decay analysis – Selected Depots |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Pole Species | Pole Treatment | 0% |  |  |  | > 0-10% |  |  |  | > 10-20% |  |  |  |
|  |  | Pole Count | % of Pop | Avg Age | Std Dev | Pole Count | % of Pop | Avg Age | Std Dev | Pole Count | % of Pop | Avg Age | Std Dev |
| Coast Grey Box | CCA | 1,681 | 95.3% | 26.2 | 7.2 | 56 | 3.2% | 37.9 | 7.2 | 24 | 1.4% | 38.1 | 6.0 |
|  | PEC | 70 | 97.2% | 27.1 | 8.8 | 1 | 1.4% | 41.0 |  | 1 | 1.4% | 44.0 |  |
| Grey Box | CCA | 722 | 95.8% | 26.2 | 8.9 | 26 | 3.4% | 32.7 | 9.7 | 6 | 0.8% | 34.0 | 9.5 |
|  | PEC | 75 | 96.2% | 28.1 | 8.0 | 3 | 3.8% | 29.0 | 1.7 |  | 0.0% |  |  |
| Grey Gum | CCA | 762 | 95.3% | 28.3 | 8.2 | 38 | 4.8% | 29.9 | 9.4 |  | 0.0% |  |  |
|  | PEC | 367 | 97.3% | 30.7 | 8.0 | 9 | 2.4% | 35.6 | 9.3 | 1 | 0.3% | 56.0 |  |
| Grey Ironbark | CCA | 3,444 | 96.0% | 26.0 | 8.9 | 127 | 3.5% | 41.7 | 8.1 | 18 | 0.5% | 38.6 | 8.1 |
|  | PEC | 523 | 98.9% | 28.1 | 7.3 | 5 | 0.9% | 28.6 | 2.6 | 1 | 0.2% | 34.0 |  |
| Ironbark | CCA | 3,615 | 96.3% | 25.0 | 9.4 | 100 | 2.7% | 33.7 | 9.8 | 36 | 1.0% | 37.9 | 8.3 |
|  | PEC | 669 | 94.4% | 32.1 | 9.3 | 37 | 5.2% | 40.7 | 6.1 | 3 | 0.4% | 39.3 | 15.9 |
| Red Ironbark | CCA | 1,982 | 97.0% | 26.7 | 7.1 | 57 | 2.8% | 37.5 | 8.7 | 5 | 0.2% | 46.4 | 2.6 |
|  | PEC | 262 | 97.8% | 26.2 | 6.1 | 6 | 2.2% | 27.8 | 3.8 |  | 0.0% |  |  |
| Tallowwood | CCA | 1,345 | 97.9% | 25.6 | 7.9 | 23 | 1.7% | 34.3 | 11.0 | 6 | 0.4% | 37.3 | 11.5 |
|  | PEC | 476 | 96.9% | 31.0 | 7.8 | 12 | 2.4% | 36.9 | 9.5 | 3 | 0.6% | 33.7 | 2.3 |
| White Mahogany | CCA | 462 | 98.7% | 26.2 | 7.5 | 5 | 1.1% | 34.6 | 5.9 | 1 | 0.2% | 34.0 |  |
|  | PEC | 138 | 99.3% | 27.9 | 7.4 | 1 | 0.7% | 31.0 |  |  | 0.0% |  |  |
| Grand Total |  | 16,593 | 96.4% | 26.6 | 8.6 | 506 | 2.9% | 36.8 | 9.4 | 105 | 0.6% | 38.3 | 8.2 |

Table 18 Durability 1 Pole External Decay by Selected Depot - Part B

|  |  | Durability 1 Pole Decay analysis – Selected Depots |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Pole Species | Pole Treatment | > 20-30% |  |  |  | Grand Total |  |  |
|  |  | Pole Count | % of Pop | Avg Age | Std Dev | Pole Count | Avg Age | Std Dev |
| Coast Grey Box | CCA | 3 | 0.2% | 36.7 | 5.8 | 1,764 | 26.7 | 7.6 |
|  | PEC |  | 0.0% |  |  | 72 | 27.6 | 9.0 |
| Grey Box | CCA |  | 0.0% |  |  | 754 | 26.5 | 9.0 |
|  | PEC |  | 0.0% |  |  | 78 | 28.1 | 7.9 |
| Grey Gum | CCA |  | 0.0% |  |  | 800 | 28.3 | 8.3 |
|  | PEC |  | 0.0% |  |  | 377 | 30.9 | 8.1 |
| Grey Ironbark | CCA |  | 0.0% |  |  | 3,589 | 26.6 | 9.4 |
|  | PEC |  | 0.0% |  |  | 529 | 28.1 | 7.3 |
| Ironbark | CCA | 3 | 0.1% | 40.0 | 1.0 | 3,754 | 25.4 | 9.6 |
|  | PEC |  | 0.0% |  |  | 709 | 32.6 | 9.4 |
| Red Ironbark | CCA |  | 0.0% |  |  | 2,044 | 27.0 | 7.4 |
|  | PEC |  | 0.0% |  |  | 268 | 26.2 | 6.0 |
| Tallowwood | CCA |  | 0.0% |  |  | 1,374 | 25.8 | 8.1 |
|  | PEC |  | 0.0% |  |  | 491 | 31.2 | 7.9 |
| White Mahogany | CCA |  | 0.0% |  |  | 468 | 26.3 | 7.6 |
|  | PEC |  | 0.0% |  |  | 139 | 27.9 | 7.4 |
| Grand Total |  | 6 | 0.0% | 38.3 | 4.1 | 17,210 | 27.0 | 8.8 |

## D1 Species Performance Analysis

Unlike the D2 poles analysis there is a difference for some D1 pole species in the way they perform based on the treatment. As noted Grey Box, Ironbark, Red Ironbark and Tallowwood PEC treated poles appear to perform worse than the same species treated with CCA.

### Grey Box

Examining the figures for Grey Box it can be seen that the total number of PEC poles is 78 versus 754 for CCA. The small number of PEC poles in this case (and overall for Grey Box) suggest that any variation between a PEC and a CCA treated Grey Box pole are not significant and can be considered statistical anomalies.

### Ironbark

In the case of Ironbark there is an adequate sample size for CCA and PEC treated poles. However PEC treated Ironbark poles are significantly more likely to have external decay based on population analysis than a CCA pole. This needs to be considered in the light of the fact that an Ironbark PEC pole will have a higher average age (approx. 7 years) for external decay than a CCA treated Ironbark pole. Potentially the difference could be simply attributed to an aged PEC population versus a CCA population.

Table 19 Ironbark External Decay 0 - 10% by Treatment – Selected Depots

| Percentage External Decay | Treatment | Number of Poles | Average Age | Standard Deviation |
| --- | --- | --- | --- | --- |
| 2 | Pigment Emulsified Creosote | 1 | 50.0 |  |
|  | Copper Chrome Arsenic(CCA) | 8 | 25.1 | 11.4 |
| 3 | Pigment Emulsified Creosote | 2 | 35.0 | 1.4 |
|  | Copper Chrome Arsenic(CCA) | 9 | 28.1 | 9.8 |
| 4 | Pigment Emulsified Creosote | 2 | 46.5 | 4.9 |
|  | Copper Chrome Arsenic(CCA) | 30 | 34.1 | 10.6 |
| 5 | Pigment Emulsified Creosote | 1 | 41.0 |  |
|  | Copper Chrome Arsenic(CCA) | 4 | 30.3 | 8.7 |
| 6 | Pigment Emulsified Creosote | 6 | 36.2 | 5.5 |
|  | Copper Chrome Arsenic(CCA) | 4 | 22.5 | 8.5 |
| 7 | Pigment Emulsified Creosote | 8 | 37.8 | 6.3 |
|  | Copper Chrome Arsenic(CCA) | 17 | 38.2 | 5.7 |
| 8 | Pigment Emulsified Creosote | 13 | 41.9 | 4.3 |
|  | Copper Chrome Arsenic(CCA) | 17 | 37.4 | 8.0 |
| 9 | Pigment Emulsified Creosote | 2 | 45.5 | 4.9 |
|  | Copper Chrome Arsenic(CCA) | 11 | 35.6 | 7.5 |
| 10 | Pigment Emulsified Creosote | 2 | 49.0 | 0.0 |
|  | Copper Chrome Arsenic(CCA) | 2 | 40.0 | 0.0 |
| Grand Total |  | 139 | 35.6 | 9.4 |

Table 19 provides some insight into the population and age distinction between PEC and CCA for Ironbark poles. It is clear that whilst there may be a higher representation of PEC poles with external decay the average age of PEC poles with decay is much higher. For all of the decay percentages a PEC average age is much higher with a tighter standard deviation (excluding the 7% decay band, where the average ages for PEC versus CCA are virtually the same).

The conclusion drawn from the above table that a PEC treated Ironbark pole will experience external decay much later than a CCA pole needs to be moderated by the spatial intelligence on PEC treated Ironbark poles as shown in Figure 33. This figure throws doubt on the aforementioned conclusion. Clearly in the worst decay areas (North Coast) there is virtually no PEC treated Ironbark poles.

Figure 33 Ironbark Pole Spatial Distribution

Given the above spatial information and the figures for Ironbark PEC performance versus CCA treated poles at selected depots the average age for decay in the 0–10% range is not significantly different to the overall network. Thus the likeliest cause for the higher percentage by population of PEC poles with external decay is simply the result of a much older PEC pole population.

Considering all the factors it is concluded that an Ironbark PEC pole is better than an Ironbark CCA pole in terms of external decay due to a higher average age for decay inception despite a much older pole population when compared to CCA.

### Red Ironbark

For Red Ironbark PEC treated poles the average age for the 0- 10% external decay band is 27.8 years whereas for CCA treated Red Ironbark poles the figure is 37.5 years. Spatially plotting the Red Ironbark poles shows an interesting outcome. CCA Red Ironbark poles are prominent in the Far North Coast in the worst area for external decay. Furthermore the external decay present in PEC poles is unusually distributed as shown in Table 20.

Table 20 Red Ironbark External Decay 0 - 10% by Treatment – Selected Depots

| Percentage External Decay | Treatment | Number of Poles | Average Age | Standard Deviation |
| --- | --- | --- | --- | --- |
| 2 | Copper Chrome Arsenic(CCA) | 3 | 28 | 0 |
| 3 | Copper Chrome Arsenic(CCA) | 13 | 38.6 | 10.5 |
| 4 | Copper Chrome Arsenic(CCA) | 19 | 39.4 | 8.6 |
| 5 | Copper Chrome Arsenic(CCA) | 2 | 25.5 | 4.9 |
| 6 | Pigment Emulsified Creosote | 4 | 30.3 | 0.5 |
|  | Copper Chrome Arsenic(CCA) | 5 | 34.6 | 4.9 |
| 7 | Pigment Emulsified Creosote | 2 | 23 | 1.4 |
|  | Copper Chrome Arsenic(CCA) | 8 | 35.4 | 6.9 |
| 8 | Copper Chrome Arsenic(CCA) | 2 | 36 | 9.9 |
| 9 | Copper Chrome Arsenic(CCA) | 2 | 47 | 4.2 |
| 10 | Copper Chrome Arsenic(CCA) | 3 | 43.7 | 5.7 |
| Grand Total |  | 63 | 36.6 | 8.9 |

Figure 34 Red Ironbark Spatial Distribution

Based on the evidence presented it would seem at face value that a PEC Red Ironbark pole is not as good a performer as a CCA treated Red Ironbark pole from an external decay perspective. However it must be noted that the number of PEC poles with external decay is statistically small and the percentage of PEC poles with external decay is lower than CCA (2.2 % versus 2.8% of the Red Ironbark pole population for selected depots). Given the data scarcity and slight differences in the population percentage figures it is not possible to conclusively state that a Red Ironbark PEC pole is not as good as a Red Ironbark CCA pole but conversely CCA poles are located in the worst areas. Thus for the purposes of this analysis it will be assumed they are as equally good.

### Tallow wood

For Tallowwood poles PEC treated poles were found to have a higher percentage of the population with external decay in the 0–10% decay band than CCA treated Tallowwood poles. (2.4% versus 1.7% of the Tallowwood pole population for selected depots). The average age for decay however for a PEC treated Tallowwood pole was higher than a CCA treated pole (36.9 years versus 34.3 years for selected depots).

The reasons for this difference may be explained by the geographical location or age profile for external decay as shown in the following tables and figures.

Table 21 Tallowwood External Decay 0 - 10% by Treatment – Selected Depots

| Percentage External Decay | Treatment | Number of Poles | Average Age | Standard Deviation |
| --- | --- | --- | --- | --- |
| 2 | Pigment Emulsified Creosote | 1 | 52.0 |  |
|  | Copper Chrome Arsenic(CCA) | 6 | 25.2 | 2.9 |
| 3 | Pigment Emulsified Creosote | 5 | 30.4 | 9.2 |
| 4 | Pigment Emulsified Creosote | 3 | 39.7 | 12.7 |
|  | Copper Chrome Arsenic(CCA) | 4 | 37.8 | 9.5 |
| 5 | Pigment Emulsified Creosote | 1 | 33.0 |  |
|  | Copper Chrome Arsenic(CCA) | 1 | 45.0 |  |
| 6 | Pigment Emulsified Creosote | 2 | 29.0 | 4.2 |
|  | Copper Chrome Arsenic(CCA) | 1 | 42.0 |  |
| 7 | Pigment Emulsified Creosote | 2 | 30.5 | 12.0 |
|  | Copper Chrome Arsenic(CCA) | 2 | 52.0 | 17.0 |
| 8 | Pigment Emulsified Creosote | 2 | 39.5 | 3.5 |
|  | Copper Chrome Arsenic(CCA) | 2 | 39.5 | 0.7 |
| 9 | Pigment Emulsified Creosote | 1 | 41.0 |  |
|  | Copper Chrome Arsenic(CCA) | 1 | 21.0 |  |
| 10 | Copper Chrome Arsenic(CCA) | 1 | 43.0 |  |
| Grand Total |  | 35 | 35.2 | 10.5 |

Figure 35 Tallowwood Spatial Distribution

In general it is clear that based on Table 21 and Table 18 that the PEC population is at least 6 years older on average than the CCA pole population for poles with external decay. It is thus not surprising that there is a slight increase in the overall pole population percentage to 2.8% for PEC versus 2.2% for CCA. However despite this explanation it is clear from Figure 35 that there is virtually no PEC treated Tallowwood poles located in the worst areas for external decay.

At best is could be assumed that the performance outcomes of a PEC Tallowwood pole is similar to that of a CCA treated Tallowwood pole based on the data available.

## Overall Statistics D1 Poles

After detailed analysis the following statistics regarding D1 poles and treatment type are presented.

Table 22 Durability 1 Pole External Decay Statistics - Entire Network

| Durability 1 Pole External Decay – Entire Network |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Treatment | 0% |  | > 0 – 40% |  | Grand Total |  |
|  | Num of Poles | % of Pop | Num of Poles | % of Pop | Num of Poles | % of Pop |
| Copper Chrome Arsenic(CCA) | 60,662 | 98.80% | 736 | 1.20% | 61,398 | 60,662 |
| Pigment Emulsified Creosote | 22,913 | 99.13% | 200 | 0.87% | 23,113 | 22,913 |
| Grand Total | 83,575 | 98.89% | 936 | 1.11% | 84,511 | 83,575 |

Table 23 Durability 1 Pole External Decay Age Statistics - Entire Network

| Durability 1 Pole External Decay – Entire Network |  |  |  |  |
| --- | --- | --- | --- | --- |
| Treatment | 0% |  | > 0 – 40% |  |
|  | Avg Age | Std Dev | Avg Age | Std Dev |
| Copper Chrome Arsenic(CCA) | 24.00 | 7.35 | 35.81 | 9.27 |
| Pigment Emulsified Creosote | 30.19 | 8.55 | 34.84 | 11.45 |

The same data for the selected depots (areas with the worst external decay for D1 poles) is shown in Table 24 and Table 25.

Table 24 Durability 1 Pole External Decay Statistics - Selected Depots

| Durability 1 Pole External Decay – Selected Depots |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Treatment | 0% |  | > 0 – 40% |  | Grand Total |  |
|  | Num of Poles | % of Pop | Num of Poles | % of Pop | Num of Poles | % of Pop |
| Copper Chrome Arsenic(CCA) | 14,013 | 96.33% | 534 | 3.67% | 14,547 | 14,013 |
| Pigment Emulsified Creosote | 2,580 | 96.88% | 83 | 3.12% | 2663 | 2,580 |
| Grand Total | 16,593 | 96.41% | 617 | 3.59% | 17,210 | 16,593 |

Table 25 Durability 1 Pole External Decay Age Statistics - Selected Depots

| Durability 1 Pole External Decay – Selected Depots |  |  |  |  |
| --- | --- | --- | --- | --- |
| Treatment | 0% |  | > 0 – 40% |  |
|  | Avg Age | Std Dev | Avg Age | Std Dev |
| Copper Chrome Arsenic(CCA) | 26.02 | 8.50 | 37.05 | 9.30 |
| Pigment Emulsified Creosote | 29.84 | 8.28 | 37.28 | 8.40 |

Table 24 suggests that D1 poles in selected areas are at a much higher risk of external decay than the network overall. Significantly from a population analysis perspective it would seem that when a D1 PEC pole is compared to D2 PEC poles in the worst areas that a D1 PEC pole actually performs from a percentage of the population far worse than a D2 PEC pole.

However as noted in prior section there are few PEC poles in the worst areas of Essential Energy. This has resulted in very few PEC poles in the analysis for comparison purposes. To demonstrate this problem visually Figure 36 shows all D1 poles with external decay in the footprint. From this it can be seen that there are few D1 PEC poles in the selected areas with external decay. Coupled with the low overall population of D1 PEC poles in these areas (2580) it is not unreasonable to suggest there is a statistical confidence issue, with a small data set of D1 PEC poles which are not uniformly represented over the footprint in the areas of interest versus a statistically significant D1 CCA pole population evenly distributed across the areas of interest.

Figure 36 All D1 Poles with External Decay

# STATISTICAL EXTREMES ANALYSIS

Based on the preceding analysis some early and late life decay issues are found in the poles. In order to test if this is geographically based some analysis looking at the average age by durability class and associated standard deviation has been performed.

Examining Table 11 and Table 23 the standard deviation for poles with external decay is significant and worthy of further examination to determine if there is something specific for poles one standard deviation from the average for each durability class.

Table 26 Durability Class Age Statistics

| Durability Class Pole External Decay – Entire Network |  |  |  |  |
| --- | --- | --- | --- | --- |
| Treatment | 0% |  | 0 – 40% |  |
|  | Avg Age | Std Dev | Avg Age | Std Dev |
| Durability 1 Poles | 25.70 | 8.17 | 35.64 | 9.75 |
| Durability 2 Poles | 26.75 | 8.95 | 37.86 | 6.81 |

Using the data presented in Table 26 spatial charts were built to show the poles one standard deviation either side of the average older or young by durability class.

Figure 37 Durability Class One Standard Deviation or Lower

Figure 38 Durability Class One Standard Deviation or Higher

Examining Figure 37 and Figure 38 it is clear that for one standard deviation lower or higher than the mean that the spatial distribution is random in nature. This would suggest that asset inspectors are not biased in a particular region.

# CONDEMNATION ANALYSIS

Essential Energy’s data set for condemned poles unfortunately suffers from the current WASP asset hierarchical structure where the pole site and physical pole are the same record. On condemnation the pole attributes are over-written and the means for identifying condemned poles is to look for a ‘condemned pole task’ that is completed for that pole site. The reason (cause) for the condemnation is stored in the task record and is thus readily accessible. However the details about the condemned pole itself are somewhat more difficult to obtain. This requires trawling through the attribute audit trail to see when the attribute was changed (if at all) and the date it was changed to ensure it is after the task was completed. In most cases trying to reconstruct the pole attributes programmatically is near to impossible. As a result it is not possible to accurately model the percentages for external decay based on treatment type or species.

Nevertheless if it is assumed that;

- The probabilities of a pole experiencing external decay based on treatment and species are reflective of the mix expected in the condemned poled due to external decay,

And

- The historical casual mix for condemnation is likely to be the same  mix for the foreseeable future

Then the lack of data for treatment type for condemned poles is immaterial as the influence of treatment on condemnation will be reflected in the probability of a pole having external decay as presented in this paper in conjunction with the overall external decay condemnation rate.

## External Decay Pole Condemnation Rate

The following table presents the number of condemned poles per annum by cause from 2004 – 2012 and the percentage of the condemned pole population that each cause represents.

Table 27 Condemned Timber Poles by Cause Statistics

|  | Condemned Timber Poles by Cause Statistics |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| YEAR | 2004 |  | 2005 |  | 2006 |  | 2007 |  | 2008 |  | 2009 |  | 2010 |  | 2011 |  | 2012 |  | Grand Total |
| Cause Description | Pole Count | % of Pop | Pole Count | % of Pop | Pole Count | % of Pop | Pole Count | % of Pop | Pole Count | % of Pop | Pole Count | % of Pop | Pole Count | % of Pop | Pole Count | % of Pop | Pole Count | % of Pop | Pole Count |
| External Decay Above | 315 | 5.20% | 392 | 6.36% | 329 | 4.74% | 241 | 3.99% | 217 | 3.51% | 227 | 3.83% | 322 | 6.91% | 443 | 7.55% | 390 | 7.11% | 2876 |
| External Decay Below | 611 | 10.08% | 400 | 6.49% | 578 | 8.33% | 556 | 9.21% | 672 | 10.88% | 692 | 11.67% | 405 | 8.69% | 484 | 8.24% | 423 | 7.71% | 4821 |
| Internal Decay Above | 844 | 13.92% | 746 | 12.11% | 1037 | 14.95% | 929 | 15.38% | 679 | 10.99% | 613 | 10.33% | 645 | 13.84% | 956 | 16.28% | 967 | 17.62% | 7416 |
| Internal Decay Below | 2028 | 33.45% | 2080 | 33.76% | 2296 | 33.10% | 1711 | 28.33% | 1801 | 29.16% | 1661 | 28.00% | 1210 | 25.97% | 1518 | 25.86% | 1325 | 24.14% | 15630 |
| Internal Pipe | 308 | 5.08% | 457 | 7.42% | 423 | 6.10% | 481 | 7.96% | 533 | 8.63% | 536 | 9.04% | 385 | 8.26% | 359 | 6.11% | 374 | 6.81% | 3856 |
| Termite (Insect) Damage | 1956 | 32.27% | 2087 | 33.87% | 2274 | 32.78% | 2121 | 35.12% | 2275 | 36.83% | 2203 | 37.14% | 1692 | 36.32% | 2111 | 35.96% | 2009 | 36.61% | 18728 |
| Grand Total | 6062 | 100% | 6162 | 100% | 6937 | 100% | 6039 | 100% | 6177 | 100% | 5932 | 100% | 4659 | 100% | 5871 | 100% | 5488 | 100% | 53327 |

From Table 27 the following figures can be derived;

- Average number of poles condemned per annum due to external decay 855.22

- Percentage of condemned poles per annum condemned due to external decay

Figure 39 Percentage of Condemned poles due to external decay

To determine the probability of a pole in the total timber population being condemned due to external decay the number of timber poles inspected per annum needs to be determined as shown in Table 28.

Table 28 Number of poles inspected per annum

| Total number of Timber poles inspected per annum |  |  |  |  |
| --- | --- | --- | --- | --- |
| Year of inspection | 2009 | 2010 | 2011 | 2012 |
| Count of poles inspected | 219353 | 235634 | 273870 | 310736 |

Thus from Table 28 the average number of timber poles inspected per annum is 283047. From this the probability of an inspected pole being condemned due to external decay is;

Prob of inspected pole condemned due to external decay =avg number of poles condemned per annum due to external decayavg number of timber poles inspected per annum

Prob of inspected pole condemned due to external decay = 0.3%

At this point it is worth recalling that the prior discussions have identified the probability of a pole based on treatment type having external decay, but it is not clear how probable it is that this pole will be condemned and as noted above this cannot readily be determined from the WASP data set.

Now in order to determine the likelihood of a pole which is found to have external decay by measuring the wall thicknesses being condemned it is necessary to determine how many poles per inspection cycle are found with external decay. These poles need to be newly discovered poles with external decay in order to allow the probability calculations to work correctly. Using WASP data and coding for all poles with the earliest record showing external decay the following table has been derived.

Table 29 Number of poles each year with external decay

| Number of poles each year (newly discovered) identified with external decay |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Year of inspection | 2008 | 2009 | 2010 | 2012 | 2013 |
| Count of poles with external decay | 6538 | 8194 | 6154 | 7105 | 6966 |

Thus from Table 29 it is possible to calculate the average number of poles per annum that have newly discovered external decay (6766.66) and then from this determine the probability of a pole with external decay being condemned.

Prob of pole with external decay being condemned =avg number of poles condemned per annum due to external decayavg number of timber poles found with external decay per annum

Prob of pole with external decay being condemned = 12.64%

Using the above information and information presented in the POLE ANALYSIS FINDINGS SUMMARY section it is possible to calculate the probability of a pole based on treatment type being condemned, an example follows;

For a PEC pole the probability of the pole having external decay is 0.76%, the probability of any inspected pole with external decay being condemned is 12.64%. Thus the probability of a PEC pole with external decay being condemned is;

Prob of a PEC pole with external decay being condemned	= 0.76% * 12.64%

= 0.096%

As a further example the probability of a D2 CCA pole having external decay is 3.6%. Thus the probability of a D2 CCA pole with external decay being condemned is;

Prob of a D2 CCA pole with external decay being condemned	= 3.6% * 12.64%

= 0.455%

As can be seen the probability figures for treated poles are small, the vast majority of poles found with external decay that are condemned are natural round or older treatment type poles (PI, HTC etc.).

This can then be utilised in a NPV to determine the risk cost for each treatment type.

# POLE ANALYSIS FINDINGS SUMMARY

This section will present the findings of the external decay analysis.

## Durability 2 Pole Species

- From an external decay perspective CCA treated Spotted Gum poles do not perform as well as CCA treated Blackbutt poles.

- A PEC treated Spotted Gum pole is better than a CCA treated Spotted Gum pole with approximately half the normalised percentage of poles with decay for a PEC treated Spotted Gum versus a CCA spotted Gum in high risk areas (see Table 7).

- There are no signs of a Blackbutt pole performing statistically worse than a Spotted Gum pole in any of the Essential Energy footprint from an external decay perspective on average by depot.

## Treatment

- Anecdotal evidence supporting the assertion that a PEC pole performs better that a CCA pole when both have external decay is not supported by the data in this analysis.

- If a PEC pole or a CCA pole experience decay then the average life and standard deviation are not significantly different enough to suggest that a PEC pole performs better than a CCA or visa versa. For selected depots the average age for a D2 pole with external decay irrespective of treatment is around 38 years. For the entire network this figure is around 36.5 years.

- There is however a lower chance that a D2 PEC pole will experience decay than a D2 CCA pole. For the entire network a PEC pole has a chance of experiencing external decay of 0.72% versus a CCA pole of 3.6% (roughly 5:1 ratio in favour of PEC). For high risk areas (selected depots) a PEC pole has a 1.42% of experiencing external decay versus a CCA pole of 5.85% (roughly a 4:1 ratio in favour of PEC). The performance of CCA is significantly influenced by the external decay found in CCA treated Spotted Gum poles.

## Durability 1 Pole Species

- Based on the analysis some possible differences for PEC treated poles and CCA treated pole were found around pole species. In general PEC treated poles performed better than CCA treated poles with the possible exception of Red Ironbark, and Tallowwood species. For these species on examination in detail it is reasonable to conclude that they probably have similar performance outcomes irrespective of treatment type.

## Treatment

- As for D2 poles no evidence was found to support the anecdotal assertion that a PEC pole with external decay will perform any better than a CCA pole with external decay in terms of the progression the external decay.

- If a PEC pole or a CCA pole experience decay then the average life for a PEC pole at decay inception would appear to be on average higher for some species than the equivalent CCA pole of the same species. For selected depots the average age for a D1 pole with external decay irrespective of treatment is around 37 years. For the entire network this figure is around 35 years.

- There is however a lower chance that a D1 PEC pole will experience decay than a D1 CCA pole. For the entire network a PEC pole has a chance of experiencing external decay of 0.87% versus a CCA pole of 1.2% (roughly 1.4:1 ratio in favour of PEC). For high risk areas (selected depots) a PEC pole has a 3.12% of experiencing external decay versus a CCA pole of 3.67% (roughly a 1.2:1 ratio in favour of PEC). The finding for high risk areas needs to be considered in light of the statistically low population of PEC poles in the worse areas for external decay. As the PEC poles are not distributed across the footprint like CCA poles in the areas of high risk it is probable that the figure is not reliable.

## Entire Network Treatment Performance Summary

Overall the performance of CCA versus PEC in regards to external decay is summarised in the following table

Table 30 Treatment Statistical Data - Entire Network

| Treatment Statistical Data - Entire Network |  |  |  |
| --- | --- | --- | --- |
| Treatment | Prob of External Decay | Earliest decay Inception age | Avg Decay Age |
| CCA | 2.98% | 31 | 38 |
| PEC | 0.76% | 24 | 34 |

## Summary and Observations;

- The findings support the argument that PEC poles are better performers than CCA poles in regards to external decay inception irrespective of strength group.

### PEC Poles

- Examination of durability grouping found that D1 PEC poles have a 0.87% of external decay versus a D2 PEC pole of 0.72% for the entire network. Considering the statistical analysis and variations in inspection regimes with regard to the measurement of external diameter it is the proposed that D1 PEC poles perform in a similar manner to D2 PEC treated poles over the entire network. When considering the high risk areas D1 PEC poles were found to have a 3.12% chance of experiencing external decay versus D2 PEC poles of 1.42%. However the low population of D1 PEC poles in the high risk areas calls into question the 3.12% figure. Given the similarity for D1 and D2 PEC treated poles overall the network it is probably reasonable to conclude that a similar result should have been found for the high risk areas, but was not due to a statistically small sample size and lack of representation of D1 PEC poles in high risk areas.

### CCA Poles

- Examination of durability grouping found that D1 CCA poles have a 1.2% of external decay versus a D2 CCA pole of 3.6% for the entire network. When considering the high risk areas D1 CCA poles were found to have a 3.67% chance of experiencing external decay versus D2 CCA poles of 5.85%.

- The data demonstrates a difference for CCA treated poles depending on durability grouping which is not found for PEC treated poles. In general it was found that D2 PEC poles performed from an external decay perspective in a similar manner to D1 PEC poles. PEC is thus the better treatment overall.

### Options for Fiscal Evaluation

Based on this analysis the following options are presented for whole of life fiscal evaluation (NPV).

- Have all poles treated with PEC. For this option pole durability segregation will not be necessary as it has been demonstrated there is minimal (if any) difference between a D1 PEC pole and a D2 PEC pole from an external decay perspective.

- Direct all CCA treated D1 poles to the high risk areas (North Coast etc.); this option will require pole species segregation.

- Consider PEC treatment only for the high risk areas (North Coast etc.) this will require treatment segregation, but may have a lower cost impact than species segregation.

- Do nothing – maintain status quo.

It is proposed that for the purposes of fiscal evaluation that the probability of experiencing external decay is utilised along with the average cost for replacement. (In other words the ‘average’ age for external decay is not considered in the fiscal evaluation as it is not probabilistic but is deterministic and that is not how decay operates in the field). This approach has its deficiencies;

- It is assumed that a pole will have the same chance of external decay for its entire life. Practically this is not true but is a function of exposure to the right moisture and temperature conditions in conjunction with oxidation. To mitigate this deficiency it is proposed that the standard deviation figures are used to set the lower age boundary at which the probabilistic costs for replacement will apply. For example if the average age for external decay is 37 years and there is a standard deviation of 7 years then the probabilistic costs will apply from 30 years.

- The presumption of a probabilistic replacement cost assumes irrespective of age so even setting an inception age as discussed above will not model real life conditions.

## Recommendations

- The options listed for fiscal evaluation are modelled using NPV techniques to determine the value or otherwise of the options to Essential Energy.

- Similar modelling is performed assessing pole performance from an internal decay perspective.

# APPENDIX A: DECAY HIGH RISK AREAS AND TERMITES

The analysis presented in this paper is consistent with research performed by a number of past studies which have identified areas of high risk and the mode for timber decay. This appendix will provide a summary of this research and provide some background into the definition of ‘high risk’ as used in this analysis paper.

## Decay

Decay in timber occurs in the presence of moisture and oxygen. The amount of moisture available is critical to the inception of decay, too little moisture and the decay process is difficult to start. Typically the amount of free water in the timber needs to be above 20% moisture content to cause ongoing decay, additionally the fungal growth also needs temperatures between 25 to 40 degrees to thrive.  By virtue of the treatment processes applied to timber products such as PEC and CCA the ‘food’ used by the fungal decay is rendered useless for the fungus, effectively retarding fungal decay. If oxygen can be removed from the equation the fungal decay is also unable to start, which is why the decay often occurs in the critical zone where the moisture content is relatively high compared to the rest of the pole and there is access to oxygen. There are differences in the decay with respect to above ground and below ground decay which has led to differing durability ratings (heart wood) and this is termed natural durability. The following figure shows the in ground decay hazard zones for Australia with zone D being the worst area.

Figure 40 In-Ground Decay Hazard Zones

As this paper is examining external decay it is worth reviewing the areas with the worst potential for above ground decay as shown in Figure 41.

Figure 41 Above Ground Decay Hazard Zones

## High Risk Areas – Definition

During analysis of the Essential Energy data set reference was not made to the above charts in order to define the areas of high risk. Rather the data was used to determine areas (depots) that had the worst percentage of the population (normalised) with external decay over the entire footprint. It just so happened that the areas of high risk as identified via this process line up almost exactly with the above maps of Australia showing the worst areas for external decay. This correlation helps to provide evidence that the WASP data set is accurate and in line with prior research once the data has been filtered and cleansed.

## Insect Damage Zones

Of interest a map of Australia has been produced showing the areas for the worst termite damage, most of NSW falls in the Zone B classification. Note: Zone D is the worst areas for termite damage.

Figure 42 Termite Hazard Zones

Whilst not in the scope of this paper a spatial plot of all poles in WASP condemned due to termites since the beginning of records aligns well with Figure 42 showing termite damage spread across the state.

Figure 43 Termite Condemned Poles

In regards to termite susceptibility and treatment concerns have been raised around Blackbutt and a propensity to star crack / barrel crack allowing the heart wood to be exposed to termite attack. Whilst the WASP data set is problematic in regards to identifying the actual species for records were it was possible to reasonably identify the prior species a spatial plot has been produced as shown in Figure 44. Filtering this data set for CCA treated poles resulted in Figure 45, whislt the WASP data is sparse the data presented in this figure cannot support the concerns around Blackbutt. There is no more clustering of Blackbutt than there is of Spotted Gum in regards to termite attack.

Figure 44 D2 Spotted Gum and Blackbutt Termite Condemned Poles

Figure 45 D2 CCA Treated Spotted Gum and Blackbutt Termite Condemned Poles

## Correlation with Prior Studies

The findings of this analysis paper are consistent with the findings of prior studies

- CSIRO Journal of the Institution of Engineers (Aust) Jan-Feb issue, J.D.Boyd 1961

  - Concluded that; “With preservative treatment.....on some 20 treated Australian species....it is possible to say that proper impregnation treatments.....give reliable and satisfactory protection. Almost irrespective of species, natural durability, growth rate.”

- Soft Rot Study Panel 1982: A survey of the incident of soft rot degrade in preservative treated utility poles in NSW

  - Concluded that treated poles performed very well in regards to soft rot, and suggested an increase in the amount of CCA or a change to creosote could reduce the onset of soft rot.

- Power Poles and Crossarm Forum: An Assessment of soft rot in preservative-treated poles in two test sites and two network areas in New South Wales – May 2013

  - Concluded that Blackbutt poles were not any worse than Spotted Gum with regards to soft rot, in fact they performed better irrespective of treatment type (PEC or CCA)

  - PEC poles performed better than CCA with regards to soft rot

# APPENDIX B DURABILITY 2 PERFORMANCE BY SELECTED DEPOT

The following table shows the performance of D2 poles by depot and treatment type for the high risk areas

|  |  |  | Durability 2 External Decay by Selected Depots |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 0 |  |  |  | 0 - 10% |  |  |  | 10 - 20% |  |  |  | 20 - 30% |  |  |  | 30 - 40% |  |  |  | Grand Total |  |  |
| Depot | Species | Treatment | Num of poles | Avg Age | Std Dev | % of Pop | Num of poles | Avg Age | Std Dev | % of Pop | Num of poles | Avg Age | Std Dev | % of Pop | Num of poles | Avg Age | Std Dev | % of Pop | Num of poles | Avg Age | Std Dev | % of Pop | Num of poles | Avg Age | Std Dev |
| Armidale Depot | Blackbutt | Copper Chrome Arsenic(CCA) | 1,087 | 23.5 | 12.8 | 99.6% | 4 | 35.5 | 0.6 | 0.4% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 1,091 | 23.5 | 12.8 |
|  |  | Pigment Emulsified Creosote | 1,536 | 37.4 | 9.2 | 98.8% | 12 | 38.4 | 8.5 | 0.8% | 5 | 39.6 | 1.1 | 0.32% | 2 | 39.5 | 2.1 | 0.1% |  |  |  | 0.0% | 1,555 | 37.5 | 9.2 |
|  | Spotted Gum | Copper Chrome Arsenic(CCA) | 2,876 | 24.5 | 6.9 | 99.8% | 6 | 28.0 | 4.0 | 0.2% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 2,882 | 24.5 | 6.9 |
|  |  | Pigment Emulsified Creosote | 1,581 | 41.0 | 4.9 | 99.4% | 8 | 45.3 | 5.1 | 0.5% | 2 | 60.5 | 10.6 | 0.13% |  |  |  | 0.0% |  |  |  | 0.0% | 1,591 | 41.0 | 5.0 |
| Ballina Depot | Blackbutt | Copper Chrome Arsenic(CCA) | 1,044 | 17.8 | 10.6 | 97.8% | 16 | 39.9 | 5.2 | 1.5% | 7 | 36.9 | 5.4 | 0.66% | 1 | 41.0 |  | 0.1% |  |  |  | 0.0% | 1,068 | 18.3 | 11.0 |
|  |  | Pigment Emulsified Creosote | 115 | 13.7 | 1.5 | 100.0% |  |  |  | 0.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 115 | 13.7 | 1.5 |
|  | Spotted Gum | Copper Chrome Arsenic(CCA) | 3,591 | 23.8 | 8.2 | 84.0% | 209 | 38.2 | 5.4 | 4.9% | 349 | 39.4 | 4.7 | 8.16% | 121 | 40.7 | 3.2 | 2.8% | 7 | 41.7 | 1.7 | 0.2% | 4,277 | 26.3 | 9.6 |
|  |  | Pigment Emulsified Creosote | 31 | 16.2 | 4.1 | 96.9% |  |  |  | 0.0% | 1 | 40.0 |  | 3.13% |  |  |  | 0.0% |  |  |  | 0.0% | 32 | 16.9 | 5.8 |
| Bathurst Depot | Blackbutt | Copper Chrome Arsenic(CCA) | 2,128 | 22.3 | 10.9 | 99.4% | 12 | 39.7 | 8.9 | 0.6% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 2,140 | 22.4 | 10.9 |
|  |  | Pigment Emulsified Creosote | 2 | 42.5 | 0.7 | 100.0% |  |  |  | 0.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 2 | 42.5 | 0.7 |
|  | Spotted Gum | Copper Chrome Arsenic(CCA) | 5,375 | 26.9 | 9.6 | 96.6% | 144 | 38.8 | 3.7 | 2.6% | 47 | 38.4 | 2.0 | 0.84% |  |  |  | 0.0% |  |  |  | 0.0% | 5,566 | 27.3 | 9.7 |
|  |  | Pigment Emulsified Creosote | 2 | 45.5 | 3.5 | 100.0% |  |  |  | 0.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 2 | 45.5 | 3.5 |
| Casino Depot | Blackbutt | Copper Chrome Arsenic(CCA) | 1,105 | 12.0 | 9.2 | 97.3% | 18 | 38.9 | 7.2 | 1.6% | 12 | 37.5 | 7.0 | 1.06% |  |  |  | 0.0% | 1 | 43.0 |  | 0.1% | 1,136 | 12.7 | 10.1 |
|  |  | Pigment Emulsified Creosote | 133 | 13.9 | 3.4 | 100.0% |  |  |  | 0.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 133 | 13.9 | 3.4 |
|  | Spotted Gum | Copper Chrome Arsenic(CCA) | 3,859 | 21.4 | 8.7 | 94.6% | 109 | 40.2 | 6.0 | 2.7% | 103 | 40.4 | 5.1 | 2.52% | 6 | 39.5 | 6.1 | 0.1% | 3 | 40.7 | 1.2 | 0.1% | 4,080 | 22.4 | 9.6 |
|  |  | Pigment Emulsified Creosote | 18 | 15.2 | 5.9 | 100.0% |  |  |  | 0.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 18 | 15.2 | 5.9 |
| Coffs Harbour Depot | Blackbutt | Copper Chrome Arsenic(CCA) | 2,450 | 23.8 | 12.5 | 99.4% | 10 | 32.9 | 12.8 | 0.4% | 5 | 37.2 | 6.5 | 0.20% |  |  |  | 0.0% | 1 | 41.0 |  | 0.0% | 2,466 | 23.8 | 12.5 |
|  |  | Pigment Emulsified Creosote | 149 | 14.9 | 4.6 | 100.0% |  |  |  | 0.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 149 | 14.9 | 4.6 |
|  | Spotted Gum | Copper Chrome Arsenic(CCA) | 8,058 | 27.3 | 8.9 | 94.5% | 276 | 39.7 | 4.3 | 3.2% | 181 | 39.7 | 4.5 | 2.12% | 11 | 37.9 | 5.6 | 0.1% | 1 | 42.0 |  | 0.0% | 8,527 | 28.0 | 9.2 |
|  |  | Pigment Emulsified Creosote | 33 | 22.1 | 12.6 | 100.0% |  |  |  | 0.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 33 | 22.1 | 12.6 |
| Dubbo Depot | Blackbutt | Copper Chrome Arsenic(CCA) | 693 | 10.4 | 7.3 | 99.3% | 5 | 8.6 | 8.8 | 0.7% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 698 | 10.4 | 7.3 |
|  |  | Pigment Emulsified Creosote | 2,517 | 31.6 | 6.8 | 97.1% | 73 | 32.8 | 6.5 | 2.8% | 1 | 31.0 |  | 0.04% |  |  |  | 0.0% |  |  |  | 0.0% | 2,591 | 31.7 | 6.8 |
|  | Spotted Gum | Copper Chrome Arsenic(CCA) | 645 | 17.8 | 10.3 | 99.5% | 3 | 19.3 | 13.6 | 0.5% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 648 | 17.8 | 10.3 |
|  |  | Pigment Emulsified Creosote | 1,923 | 34.1 | 5.6 | 96.8% | 61 | 36.3 | 6.0 | 3.1% | 2 | 30.0 | 2.8 | 0.10% | 1 | 38.0 |  | 0.1% |  |  |  | 0.0% | 1,987 | 34.2 | 5.6 |
| Grafton Depot | Blackbutt | Copper Chrome Arsenic(CCA) | 1,932 | 16.7 | 11.5 | 99.7% | 5 | 39.2 | 2.9 | 0.3% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 1,937 | 16.8 | 11.6 |
|  |  | Pigment Emulsified Creosote | 323 | 13.5 | 3.1 | 100.0% |  |  |  | 0.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 323 | 13.5 | 3.1 |
|  | Spotted Gum | Copper Chrome Arsenic(CCA) | 5,733 | 23.4 | 8.5 | 97.6% | 99 | 38.9 | 5.8 | 1.7% | 40 | 40.7 | 2.4 | 0.68% |  |  |  | 0.0% |  |  |  | 0.0% | 5,872 | 23.8 | 8.7 |
|  |  | Pigment Emulsified Creosote | 49 | 16.3 | 8.5 | 100.0% |  |  |  | 0.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 49 | 16.3 | 8.5 |
| Griffith Depot | Blackbutt | Copper Chrome Arsenic(CCA) | 622 | 35.4 | 4.8 | 95.8% | 23 | 37.3 | 3.5 | 3.5% | 4 | 36.5 | 4.0 | 0.62% |  |  |  | 0.0% |  |  |  | 0.0% | 649 | 35.5 | 4.8 |
|  |  | Pigment Emulsified Creosote | 15 | 44.2 | 3.0 | 100.0% |  |  |  | 0.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 15 | 44.2 | 3.0 |
|  | Spotted Gum | Copper Chrome Arsenic(CCA) | 3,365 | 36.0 | 4.4 | 87.4% | 326 | 38.2 | 3.1 | 8.5% | 157 | 38.8 | 2.7 | 4.08% |  |  |  | 0.0% |  |  |  | 0.0% | 3,848 | 36.3 | 4.4 |
|  |  | Pigment Emulsified Creosote | 36 | 44.5 | 2.2 | 97.3% | 1 | 44.0 |  | 2.7% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 37 | 44.5 | 2.2 |
| Inverell Depot | Blackbutt | Copper Chrome Arsenic(CCA) | 632 | 11.7 | 10.1 | 100.0% |  |  |  | 0.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 632 | 11.7 | 10.1 |
|  |  | Pigment Emulsified Creosote | 3,349 | 28.9 | 9.6 | 99.8% | 5 | 34.2 | 7.9 | 0.1% | 3 | 70.7 | 21.4 | 0.09% |  |  |  | 0.0% |  |  |  | 0.0% | 3,357 | 28.9 | 9.7 |
|  | Spotted Gum | Copper Chrome Arsenic(CCA) | 1,200 | 21.5 | 11.0 | 99.6% | 2 | 31.0 | 8.5 | 0.2% | 3 | 33.3 | 6.8 | 0.25% |  |  |  | 0.0% |  |  |  | 0.0% | 1,205 | 21.5 | 11.0 |
|  |  | Pigment Emulsified Creosote | 3,530 | 33.0 | 9.8 | 99.2% | 19 | 47.8 | 9.5 | 0.5% | 6 | 48.2 | 2.5 | 0.17% | 3 | 47.7 | 2.9 | 0.1% |  |  |  | 0.0% | 3,558 | 33.1 | 9.8 |
| Kempsey Depot | Blackbutt | Copper Chrome Arsenic(CCA) | 1,191 | 21.4 | 14.2 | 99.0% | 12 | 33.8 | 11.0 | 1.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 1,203 | 21.5 | 14.2 |
|  |  | Pigment Emulsified Creosote | 318 | 23.7 | 11.7 | 99.4% | 2 | 50.5 | 0.7 | 0.6% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 320 | 23.9 | 11.9 |
|  | Spotted Gum | Copper Chrome Arsenic(CCA) | 3,253 | 29.2 | 11.2 | 92.0% | 215 | 37.3 | 3.9 | 6.1% | 47 | 37.1 | 4.7 | 1.33% | 18 | 37.9 | 1.7 | 0.5% | 1 | 39.0 |  | 0.0% | 3,534 | 29.9 | 11.0 |
|  |  | Pigment Emulsified Creosote | 218 | 29.2 | 11.1 | 98.6% | 2 | 44.5 | 7.8 | 0.9% | 1 | 49.0 |  | 0.45% |  |  |  | 0.0% |  |  |  | 0.0% | 221 | 29.4 | 11.2 |
| Kyogle Depot | Blackbutt | Copper Chrome Arsenic(CCA) | 621 | 13.2 | 9.1 | 98.9% | 5 | 27.4 | 12.3 | 0.8% | 1 | 14.0 |  | 0.16% | 1 | 44.0 |  | 0.2% |  |  |  | 0.0% | 628 | 13.3 | 9.2 |
|  |  | Pigment Emulsified Creosote | 89 | 14.0 | 1.3 | 100.0% |  |  |  | 0.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 89 | 14.0 | 1.3 |
|  | Spotted Gum | Copper Chrome Arsenic(CCA) | 2,694 | 21.0 | 7.5 | 97.4% | 55 | 35.9 | 8.5 | 2.0% | 15 | 39.6 | 7.9 | 0.54% | 1 | 45.0 |  | 0.0% |  |  |  | 0.0% | 2,765 | 21.4 | 7.9 |
|  |  | Pigment Emulsified Creosote | 11 | 12.9 | 2.0 | 100.0% |  |  |  | 0.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 11 | 12.9 | 2.0 |
| Lismore Depot | Blackbutt | Copper Chrome Arsenic(CCA) | 1,520 | 16.2 | 11.3 | 98.7% | 16 | 37.5 | 23.9 | 1.0% | 4 | 43.3 | 8.1 | 0.26% |  |  |  | 0.0% |  |  |  | 0.0% | 1,540 | 16.5 | 11.8 |
|  |  | Pigment Emulsified Creosote | 181 | 15.7 | 6.9 | 100.0% |  |  |  | 0.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 181 | 15.7 | 6.9 |
|  | Spotted Gum | Copper Chrome Arsenic(CCA) | 6,095 | 24.3 | 8.3 | 91.4% | 282 | 40.0 | 7.1 | 4.2% | 282 | 41.8 | 5.1 | 4.23% | 10 | 41.1 | 3.0 | 0.1% |  |  |  | 0.0% | 6,669 | 25.7 | 9.4 |
|  |  | Pigment Emulsified Creosote | 28 | 18.1 | 11.0 | 93.3% | 1 | 39.0 |  | 3.3% | 1 | 52.0 |  | 3.33% |  |  |  | 0.0% |  |  |  | 0.0% | 30 | 20.0 | 12.8 |
| Moruya Depot | Blackbutt | Copper Chrome Arsenic(CCA) | 2,440 | 24.6 | 11.5 | 99.7% | 4 | 39.0 | 2.9 | 0.2% | 4 | 37.5 | 5.3 | 0.16% |  |  |  | 0.0% |  |  |  | 0.0% | 2,448 | 24.7 | 11.5 |
|  | Spotted Gum | Copper Chrome Arsenic(CCA) | 5,213 | 29.4 | 10.2 | 97.3% | 69 | 39.2 | 3.6 | 1.3% | 70 | 39.2 | 3.0 | 1.31% | 7 | 37.7 | 5.4 | 0.1% |  |  |  | 0.0% | 5,359 | 29.7 | 10.2 |
|  |  | Pigment Emulsified Creosote | 3 | 33.7 | 15.0 | 100.0% |  |  |  | 0.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 3 | 33.7 | 15.0 |
| Port Macquarie Depot | Blackbutt | Copper Chrome Arsenic(CCA) | 1,351 | 19.8 | 12.1 | 97.1% | 33 | 29.6 | 9.2 | 2.4% | 7 | 31.3 | 7.5 | 0.50% |  |  |  | 0.0% | 1 | 22.0 |  | 0.1% | 1,392 | 20.1 | 12.1 |
|  |  | Pigment Emulsified Creosote | 499 | 26.2 | 11.2 | 99.2% | 4 | 39.0 | 4.1 | 0.8% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 503 | 26.3 | 11.2 |
|  | Spotted Gum | Copper Chrome Arsenic(CCA) | 2,592 | 23.1 | 10.2 | 91.8% | 145 | 32.6 | 6.9 | 5.1% | 86 | 29.1 | 7.4 | 3.05% |  |  |  | 0.0% |  |  |  | 0.0% | 2,823 | 23.8 | 10.3 |
|  |  | Pigment Emulsified Creosote | 478 | 28.8 | 10.1 | 92.6% | 31 | 33.7 | 7.3 | 6.0% | 7 | 28.3 | 12.2 | 1.36% |  |  |  | 0.0% |  |  |  | 0.0% | 516 | 29.1 | 10.0 |
| Taree Depot | Blackbutt | Copper Chrome Arsenic(CCA) | 1,835 | 20.5 | 13.2 | 99.4% | 8 | 32.3 | 3.5 | 0.4% | 4 | 26.5 | 14.4 | 0.22% |  |  |  | 0.0% |  |  |  | 0.0% | 1,847 | 20.5 | 13.2 |
|  |  | Pigment Emulsified Creosote | 609 | 26.2 | 9.2 | 100.0% |  |  |  | 0.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 609 | 26.2 | 9.2 |
|  | Spotted Gum | Copper Chrome Arsenic(CCA) | 4,629 | 26.9 | 9.9 | 96.6% | 113 | 36.0 | 3.6 | 2.4% | 51 | 35.8 | 4.3 | 1.06% | 1 | 40.0 |  | 0.0% |  |  |  | 0.0% | 4,794 | 27.2 | 9.9 |
|  |  | Pigment Emulsified Creosote | 362 | 30.3 | 9.1 | 98.1% | 3 | 38.3 | 12.7 | 0.8% | 4 | 41.0 | 8.5 | 1.08% |  |  |  | 0.0% |  |  |  | 0.0% | 369 | 30.5 | 9.2 |
| Tweed Heads Depot | Blackbutt | Copper Chrome Arsenic(CCA) | 721 | 19.6 | 11.7 | 97.2% | 19 | 38.1 | 9.4 | 2.6% | 2 | 15.0 | 14.1 | 0.27% |  |  |  | 0.0% |  |  |  | 0.0% | 742 | 20.1 | 12.0 |
|  |  | Pigment Emulsified Creosote | 80 | 13.4 | 1.1 | 100.0% |  |  |  | 0.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 80 | 13.4 | 1.1 |
|  | Spotted Gum | Copper Chrome Arsenic(CCA) | 3,613 | 28.3 | 10.5 | 88.6% | 395 | 38.6 | 6.9 | 9.7% | 66 | 39.4 | 6.5 | 1.62% | 3 | 33.3 | 15.0 | 0.1% |  |  |  | 0.0% | 4077 | 29.5 | 10.7 |
|  |  | Pigment Emulsified Creosote | 39 | 14.2 | 1.3 | 100.0% |  |  |  | 0.0% |  |  |  | 0.00% |  |  |  | 0.0% |  |  |  | 0.0% | 39 | 14.2 | 1.3 |
| Grand Total |  |  | 102,420 | 25.7 | 11.0 | 95.7% | 2860 | 37.9 | 6.6 | 2.7% | 1580 | 39.0 | 6.1 | 1.48% | 186 | 40.1 | 4.1 | 0.2% | 15 | 40.1 | 5.2 | 0.0% | 107061 | 26.3 | 11.2 |

Note the average age for decay for D1 poles is very similar to D2 poles (within a year). Whilst the average age is lower for D1 poles than D2 poles the critical metric is the probability of decay even occurring in the pole. So it is acceptable to have a lower average age for D1 poles as long as the probability of decay is lower than D2 poles if the premise that D1 pole is better than a D2 pole is to be supported. This is in fact the case irrespective of treatment or geographical location.

The revised critical zone figures of 0 – 350mm that will be incorporated in the revised inspection manual are also the same as used at Ausgrid and Endeavour.

In the case of duplicate pole numbers investigation found some suspect data, it is considered that the errors were particular to one area of Essential Energy. However from an analysis and coding perspective it was easier to remove all poles with duplicate numbers rather than to try and code around the errors. The removal of these 28762 records cannot be considered statistically significant at an organisational level but when depot based analysis is performed the suspect data found in this data set has an influence.

Note: external decay greater than 40% has not been included as there were a total of 6 poles that were calculated as having more than 40% external decay, all these poles has some suspect data and were best excluded. For 13 pole records it was not possible to calculate a per cent decay figure due to missing data (i.e. no ground diameter measurements)

This conclusion is supported by recent research commissioned by the ENA Power Poles and Crossarm forum. “ An Assessment of soft rot in preservative treated poles in two test sites and two network areas in New South Wales”, W.D Gardner, M.A Powell and C.Kirton May 2013.

The lower than expected average age for decay shown here is in the main due to a number of PEC poles with low decay figures (1% – 3 %) and very low average ages as shown in Table 9. It is not clear why this has occurred and maybe down to measurement errors in the external decay measurements as a result of callipers used on the poles which can have 10 – 15mm of error in the actual measurement. If these poles were excluded then the average age for external decay inception is similar to that of CCA poles. Thus it is concluded that given the small number of PEC poles with external decay that this average age figure can be attributed to data errors. This conclusion is supported by the percentage of the population of PEC poles that have signs of external decay.

One possible explanation for this is that Spotted Gum poles have on average a much higher sap wood thickness than many D1 poles. However it is equally likely that the problem is related to the very low population of PEC D1 poles in these areas causing statistical confidence issues.

Causes for condemnation have been limited to causes that can be attributed to the decay of timber or the natural prevalence to insect damage.

This is one standard deviation away from the mean (average)

Chart from Forest and Wood Products Australia – Decay in ground Manual 3 CSIRO No 2008

Chart from Forest and Wood Products Australia – Decay above ground Manual 4 CSIRO No 2008

Chart from Timber Service Life Design Guide Forest and Wood Products Australia - 2007