## Run Extract (hidden)
[12 empty] | 1 | 2 | 3 | 4 | 5 | 6
[12 empty] | Option 1 | Option 2 | Option 3 | Option 4 | Option 5 | Option 6
[10 empty] | Address | Value Metric | Emergency stake pole upon failure and follow up planned replacement with Titan | Replace Pole upon failure with class S3 (Wood) - fault | Replace Pole upon failure with class S3 (Wood) and constrained by REPEX model - fault | Replace Pole upon failure with class S4 (Wood) - fault | Replace Pole upon failure with FRC (Titan) - fault
[11 empty] | UARM - Environment and Community - Fire Risk | 5118247.8445 | 5117538.7402 | 4804610.6271 | 5076250.8581 | 5118247.8445
[11 empty] | UARM - Safety & People - Worker | 2703805.2218 | 2703430.6471 | 2538120.8072 | 2681619.5837 | 2703805.2218
Notes | [10 empty] | UARM - Network Performance Risk | 438286393.2967 | 438225672.2282 | 411428974.581 | 434690102.0833 | 438286393.2967
Need to open the .xlsm Investment Summary report from Copperleaf in the Trusted folder Save in the preferred location as an .xlsx Need to test environment - other and when two of the same value models have been selected with a different name | [10 empty] | UARM - Environment and Community - Other Risk | 11953044.4801 | 11951388.4679 | 11220582.9331 | 11854965.6093 | 11953044.4801
[11 empty] | UARM - Financial Risk | 11953.0412 | 11951.3822 | 11220.5435 | 11854.9582 | 11953.0412
[11 empty] | UARM - Safety & People - Public | 8128070.2093 | 8126944.1444 | 7629996.3911 | 8061376.6044 | 8128070.2093
[11 empty] | Terminal Value | 14780928.4651 | 16965935.2816 | 12745873.0967 | 17608584.3453 | 19279471.911
[11 empty] | Total Investment Cost | 31933207.5476 | 37225081.8224 | 28318127.4483 | 38580736.8596 | 41422792.8084
Options
| Option | 2025 | 2026 | 2027 | 2028 | 2029
| Baseline | 306747358.7 | 336624095.52 | 368142076.47 | 401203771.03 | 435677662.14
| Emergency stake pole upon failure and follow up planned replacement with Titan | 304399633.64 | 331818788.56 | 360604880.23 | 390605972.17 | 421858662.31
| Replace Pole upon failure with class S3 (Wood) - fault | 304399633.64 | 331818788.56 | 360604880.25 | 390605972.34 | 421858663.37
| Replace Pole upon failure with class S3 (Wood) and constrained by REPEX model - fault | 304527005.74 | 332067986.59 | 361006254.07 | 391178038.65 | 422554021.53
| Replace Pole upon failure with class S4 (Wood) - fault | 304399633.64 | 331818788.57 | 360604881.07 | 390605982.42 | 421858725.85
| Replace Pole upon failure with FRC (Titan) - fault | 304399633.64 | 331818788.56 | 360604880.23 | 390605972.17 | 421858662.31
Option Breakdown | [7 empty] | Folder and File Paths
| Option 3 |  |  |  |  | Greater 0 | (Multiple Items)
| Recommended Option - Value | [6 empty] | This File Path | \\TNAD.tasnetworks.com.au\user$\user_folders\BahramabadiM\My Documents\Trusted\InvestmentTemplate.xlsm
| Value Function Measure | Value | Value in % | Greater 0 |  | Row Labels | Sum of Value in % | Folder Path | H:\RPSAM\SAM\R24 IES\final draft\
Option 3 | UARM - Environment and Community - Fire Risk | 4804.6106 | 1% | 1 | K20 | Terminal Value | 2.66% | File Name | InvestmentSummary_R24_D_OH_REPOL_Replace_Pole_Fault.xlsx
Option 3 | UARM - Safety & People - Worker | 2538.1208 | 0.53% | 1 | K21 | Total Investment Cost | 5.92% | File Path | H:\RPSAM\SAM\R24 IES\final draft\InvestmentSummary_R24_D_OH_REPOL_Replace_Pole_Fault.xlsx
Option 3 | UARM - Network Performance Risk | 411428.9746 | 85.95% | 1 | K22 | UARM - Environment and Community - Fire Risk | 1%
Option 3 | UARM - Environment and Community - Other Risk | 11220.5829 | 2.34% | 1 | K23 | UARM - Environment and Community - Other Risk | 2.34%
Option 3 | UARM - Financial Risk | 11.2205 | 0% | 1 | K24 | UARM - Financial Risk | 0%
Option 3 | UARM - Safety & People - Public | 7629.9964 | 1.59% | 1 | K25 | UARM - Network Performance Risk | 85.95%
Option 3 | Terminal Value | 12745.8731 | 2.66% | 1 | K26 | UARM - Safety & People - Public | 1.59%
Option 3 | Total Investment Cost | -28318.1274 | 5.92% | 1 | K27 | UARM - Safety & People - Worker | 0.53%
Option 3 |  |  |  | 0 | K28
Option 3 |  |  |  | 0 | K29
Option 3 |  |  |  | 0 | K30 |  |  | 1 | InvestmentSummary_R24_D_ND_PRHVR_Augment_HV_Fdr_TRIP.xlsx
Option 3 |  |  |  | 0 | K31 |  |  | 2 | InvestmentSummary_R24_D_OH_REPOL_Basic Fleet Pole Replacement.xlsx
Option 3 |  |  |  | 0 | K32 |  |  | 3 | InvestmentSummary_R24_T_ND_AUGSB_W Coast Reliability Improvement.xlsx
Option 3 |  |  |  | 0 | K33 |  |  | 4 | InvestmentSummary_R24_T_ND_AUGSB_Upper Derwent 110 kV Losses.xlsx
| Total | 422061.2515 | 99.99% |  |  |  |  | 5 | InvestmentSummary_R24_D_OH_SIWES_Bird_Mitigation.xlsx
[8 empty] | 6 | InvestmentSummary_R24_D_SB_REGMS_GMS_Replacement of GMS.xlsx
[8 empty] | 7 | InvestmentSummary_R24_D_OH_REPOL_Complex Design.xlsx
Start | Option 1 |  |  |  |  | Greater 0 | 1 | 8 | InvestmentSummary_R24_D_PQ_PQTXV_Power_Quality_LV_Tformers.xlsx
| Value Function Measure | Value | Value in % | Greater 0 |  |  |  | 9 | InvestmentSummary_R24_D_ND_PQLVV_Aug_HV_LV_Conductor.xlsx
Option 1 | UARM - Environment and Community - Fire Risk | 5118.2478 | 1% | 1 | K20 | Row Labels | Sum of Value in % | 10 | InvestmentSummary_R24_D_CA_SOLCP_Crossover_Extension_OH.xlsx
Option 1 | UARM - Safety & People - Worker | 2703.8052 | 0.53% | 1 | K21 | Terminal Value | 2.88% | 11 | InvestmentSummary_R24_D_CI_SOIRR_Irrigation_Supply.xlsx
Option 1 | UARM - Network Performance Risk | 438286.3933 | 85.45% | 1 | K22 | Total Investment Cost | 6.23% | 12 | InvestmentSummary_R24_D_AMIPD_AM Improvement Program.xlsx
Option 1 | UARM - Environment and Community - Other Risk | 11953.0445 | 2.33% | 1 | K23 | UARM - Environment and Community - Fire Risk | 1% | 13 | InvestmentSummary_R24_D_CI_SOPOR_Permanent_Residence_OH.xlsx
Option 1 | UARM - Financial Risk | 11.953 | 0% | 1 | K24 | UARM - Environment and Community - Other Risk | 2.33% | 14 | InvestmentSummary_R24_D_CI_SUPOR_Permanent_Residence_UG.xlsx
Option 1 | UARM - Safety & People - Public | 8128.0702 | 1.58% | 1 | K25 | UARM - Financial Risk | 0% | 15 | InvestmentSummary_R24_D_CI_SOGSI_General_Supply_OH.xlsx
Option 1 | Terminal Value | 14780.9285 | 2.88% | 1 | K26 | UARM - Network Performance Risk | 85.45% | 16 | InvestmentSummary_R24_D_CI_SUGSI_General_Supply_UG.xlsx
Option 1 | Total Investment Cost | -31933.2075 | 6.23% | 1 | K27 | UARM - Safety & People - Public | 1.58% | 17 | InvestmentSummary_R24_D_CI_SUSBD_Subdivision_UG.xlsx
Option 1 |  |  |  | 0 | K28 | UARM - Safety & People - Worker | 0.53% | 18 | InvestmentSummary_R24_D_CI_SOSDI_Subdivision_OH.xlsx
Option 1 |  |  |  | 0 | K29 |  |  | 19 | InvestmentSummary_R24_D_CI_SUSUB_Augment_Dist_Substations.xlsx
Option 1 |  |  |  | 0 | K30 |  |  | 20 | InvestmentSummary_R24_T_ND_LAEMP_SELA.xlsx
Option 1 |  |  |  | 0 | K31 |  |  | 21 | InvestmentSummary_R24_D_CA_DESDB_Prelim_Drive_by_Design.xlsx
Option 1 |  |  |  | 0 | K32 |  |  | 22 | InvestmentSummary_R24_D_CI_SUMPR_Major_Commercial.xlsx
Option 1 |  |  |  | 0 | K33 |  |  | 23 | InvestmentSummary_R24_D_CI_EASEN_Easements_Non_Major_Comm.xlsx
| Total | 449049.235 | 100% |  |  |  |  | 24 | InvestmentSummary_R24_D_ND_PRHVR_Rosebery_Supply_Improve.xlsx
[8 empty] | 25 | InvestmentSummary_R24_D_ND_CAHVF_Huonville_Supply_Improvement.xlsx
[8 empty] | 26 | InvestmentSummary_R24_D_ND_CAHVF_Aug_Fdr_Network_Access.xlsx
[8 empty] | 27 | InvestmentSummary_R24_D_ND_PRHVR_Deloraine_Supply_Improve.xlsx
| Option 2 |  |  |  |  | Greater 0 | 1 | 28 | InvestmentSummary_R24_D_ND_CALVF_Augment_LV_Fdr_Capacity.xlsx
| Value Function Measure | Value | Value in % | Greater 0 |  |  |  | 29 | InvestmentSummary_R24_D_ND_CAHVF_Augment_HV_Fdr_Trunk.xlsx
Option 2 | UARM - Environment and Community - Fire Risk | 5117.5387 | 0.98% | 1 | K20 | Row Labels | Sum of Value in % | 30 | InvestmentSummary_R24_D_ND_CAHVF_Aug_Pole_Mtd_Regulator.xlsx
Option 2 | UARM - Safety & People - Worker | 2703.4306 | 0.52% | 1 | K21 | Terminal Value | 3.26% | 31 | InvestmentSummary_R24_D_ND_CAHVF_Aug_Grnd_Mtd_Regulator.xlsx
Option 2 | UARM - Network Performance Risk | 438225.6722 | 84.22% | 1 | K22 | Total Investment Cost | 7.15% | 32 | InvestmentSummary_R24_D_ND_CAHVF_22kV_Emu_Bay_Feeders.xlsx
Option 2 | UARM - Environment and Community - Other Risk | 11951.3885 | 2.3% | 1 | K23 | UARM - Environment and Community - Fire Risk | 0.98% | 33 | InvestmentSummary_R24_D_ND_CAHVF_Augment_HV_Fdr_Capacity.xlsx
Option 2 | UARM - Financial Risk | 11.9514 | 0% | 1 | K24 | UARM - Environment and Community - Other Risk | 2.3% | 34 | InvestmentSummary_R24_D_ND_CAHVF_Aug_SubStd_Cond_Capacity.xlsx
Option 2 | UARM - Safety & People - Public | 8126.9441 | 1.56% | 1 | K25 | UARM - Financial Risk | 0% | 35 | InvestmentSummary_R24_D_ND_LANDZ_LandAcq_ZoneSubs.xlsx
Option 2 | Terminal Value | 16965.9353 | 3.26% | 1 | K26 | UARM - Network Performance Risk | 84.22% | 36 | InvestmentSummary_R24_D_ND_CATXU_Aug_Dist_Sub.xlsx
Option 2 | Total Investment Cost | -37225.0818 | 7.15% | 1 | K27 | UARM - Safety & People - Public | 1.56% | 37
Option 2 |  |  |  | 0 | K28 | UARM - Safety & People - Worker | 0.52% | 38
Option 2 |  |  |  | 0 | K29 |  |  | 39
Option 2 |  |  |  | 0 | K30 |  |  | 40
Option 2 |  |  |  | 0 | K31 |  |  | 41
Option 2 |  |  |  | 0 | K32 |  |  | 42
Option 2 |  |  |  | 0 | K33 |  |  | 43
| Total | 445877.7791 | 99.99%
| Option 3 |  |  |  |  | Greater 0 | 1
| Value Function Measure | Value | Value in % | Greater 0
Option 3 | UARM - Environment and Community - Fire Risk | 4804.6106 | 1% | 1 | K20 | Row Labels | Sum of Value in %
Option 3 | UARM - Safety & People - Worker | 2538.1208 | 0.53% | 1 | K21 | Terminal Value | 2.66%
Option 3 | UARM - Network Performance Risk | 411428.9746 | 85.95% | 1 | K22 | Total Investment Cost | 5.92%
Option 3 | UARM - Environment and Community - Other Risk | 11220.5829 | 2.34% | 1 | K23 | UARM - Environment and Community - Fire Risk | 1%
Option 3 | UARM - Financial Risk | 11.2205 | 0% | 1 | K24 | UARM - Environment and Community - Other Risk | 2.34%
Option 3 | UARM - Safety & People - Public | 7629.9964 | 1.59% | 1 | K25 | UARM - Financial Risk | 0%
Option 3 | Terminal Value | 12745.8731 | 2.66% | 1 | K26 | UARM - Network Performance Risk | 85.95%
Option 3 | Total Investment Cost | -28318.1274 | 5.92% | 1 | K27 | UARM - Safety & People - Public | 1.59%
Option 3 |  |  |  | 0 | K28 | UARM - Safety & People - Worker | 0.53%
Option 3 |  |  |  | 0 | K29
Option 3 |  |  |  | 0 | K30
Option 3 |  |  |  | 0 | K31
Option 3 |  |  |  | 0 | K32
Option 3 |  |  |  | 0 | K33
| Total | 422061.2515 | 99.99%
| Option 4 |  |  |  |  | Greater 0 | 1
| Value Function Measure | Value | Value in % | Greater 0
Option 4 | UARM - Environment and Community - Fire Risk | 5076.2509 | 0.98% | 1 | K20 | Row Labels | Sum of Value in %
Option 4 | UARM - Safety & People - Worker | 2681.6196 | 0.52% | 1 | K21 | Terminal Value | 3.4%
Option 4 | UARM - Network Performance Risk | 434690.1021 | 83.83% | 1 | K22 | Total Investment Cost | 7.44%
Option 4 | UARM - Environment and Community - Other Risk | 11854.9656 | 2.29% | 1 | K23 | UARM - Environment and Community - Fire Risk | 0.98%
Option 4 | UARM - Financial Risk | 11.855 | 0% | 1 | K24 | UARM - Environment and Community - Other Risk | 2.29%
Option 4 | UARM - Safety & People - Public | 8061.3766 | 1.55% | 1 | K25 | UARM - Financial Risk | 0%
Option 4 | Terminal Value | 17608.5843 | 3.4% | 1 | K26 | UARM - Network Performance Risk | 83.83%
Option 4 | Total Investment Cost | -38580.7369 | 7.44% | 1 | K27 | UARM - Safety & People - Public | 1.55%
Option 4 |  |  |  | 0 | K28 | UARM - Safety & People - Worker | 0.52%
Option 4 |  |  |  | 0 | K29
Option 4 |  |  |  | 0 | K30
Option 4 |  |  |  | 0 | K31
Option 4 |  |  |  | 0 | K32
Option 4 |  |  |  | 0 | K33
| Total | 441404.0172 | 100%
| Option 5 |  |  |  |  | Greater 0 | 1
| Value Function Measure | Value | Value in % | Greater 0
Option 5 | UARM - Environment and Community - Fire Risk | 5118.2478 | 0.97% | 1 | K20 | Row Labels | Sum of Value in %
Option 5 | UARM - Safety & People - Worker | 2703.8052 | 0.51% | 1 | K21 | Terminal Value | 3.66%
Option 5 | UARM - Network Performance Risk | 438286.3933 | 83.18% | 1 | K22 | Total Investment Cost | 7.86%
Option 5 | UARM - Environment and Community - Other Risk | 11953.0445 | 2.27% | 1 | K23 | UARM - Environment and Community - Fire Risk | 0.97%
Option 5 | UARM - Financial Risk | 11.953 | 0% | 1 | K24 | UARM - Environment and Community - Other Risk | 2.27%
Option 5 | UARM - Safety & People - Public | 8128.0702 | 1.54% | 1 | K25 | UARM - Financial Risk | 0%
Option 5 | Terminal Value | 19279.4719 | 3.66% | 1 | K26 | UARM - Network Performance Risk | 83.18%
Option 5 | Total Investment Cost | -41422.7928 | 7.86% | 1 | K27 | UARM - Safety & People - Public | 1.54%
Option 5 |  |  |  | 0 | K28 | UARM - Safety & People - Worker | 0.51%
Option 5 |  |  |  | 0 | K29
Option 5 |  |  |  | 0 | K30
Option 5 |  |  |  | 0 | K31
Option 5 |  |  |  | 0 | K32
Option 5 |  |  |  | 0 | K33
| Total | 444058.1932 | 99.99%
| Option 6 |  |  |  |  | Greater 0 | 0
| Value Function Measure | Value | Value in % | Greater 0
Option 6 |  |  |  | 0 | K20 | Row Labels | Sum of Value in %
Option 6 |  |  |  | 0 | K21 |  | 0%
Option 6 |  |  |  | 0 | K22
Option 6 |  |  |  | 0 | K23
Option 6 |  |  |  | 0 | K24
Option 6 |  |  |  | 0 | K25
Option 6 |  |  |  | 0 | K26
Option 6 |  |  |  | 0 | K27
Option 6 |  |  |  | 0 | K28
Option 6 |  |  |  | 0 | K29
Option 6 |  |  |  | 0 | K30
Option 6 |  |  |  | 0 | K31
Option 6 |  |  |  | 0 | K32
Option 6 |  |  |  | 0 | K33
| Total | 0 | 0%

## Summary
Investment Evaluation Summary |  |  |  | Investment Code |  | Report Start Year |  | NPV Period | Base Fiscal Year | Currency Scale
|  |  |  | PRJ000654 |  | 2025 |  | 25 | FY23 | Literal
|  |  |  | Investment Name | [5 empty] | Scenario
|  |  |  | R24_D_OH_REPOL_Replace_Pole_Fault | [5 empty] | Approved
Value Function |  | TasNetworks Value Function |  | Version |  | 0.1 |  | Date |  | 2022-10-31
Investment Description
Description |  | Reactive program to restore supply to customers by replacing poles that have failed in service. | [9 empty] | TRUE
Functional Area |  | REPOL |  |  | Department |  |  | Asset Strategy
Works Initiator |  |  |  |  | Portfolio |  |  | Dx - Renewal
Investment Category |  | Prescribed Services - Asset Renewal |  |  | Needs Item Reference
Investment Type |  | Network Project |  |  | Document No. |  |  | R2355521
Investment Stage |  | Gate 2 – Investment Evaluation Summary |  |  | Project Zone Location
PPM ID |  |  |  |  | Regulatory Test Required |  |  | No
Investment Summary
Problem Definition |  | Existing wood poles need replacement under fault response for damage resulting from causes including excessive strong winds and storms, vegetation impacts, bushfires and vehicle collisions. The trended historical average pole failure rate is approximately 180 poles per annum that require replacement under fault conditions to restore supply to customers. | [9 empty] | TRUE
Recommendation |  | Replace Pole upon failure with class S3 (Wood) and constrained by REPEX model - fault, is recommended for approval as it best satisfies the customer and business needs. | [9 empty] | TRUE
Alternative Spend Profile
Name |  | Status | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV | Alternative Start Date
Emergency stake pole upon failure and follow up planned replacement with Titan |  | Candidate | 2120000 | 2120000 | 2120000 | 2120000 | 2120000 | 10600000 | 44520000 | 449049235.01 | 4547400%
Replace Pole upon failure with class S3 (Wood) - fault |  | Candidate | 2471000 | 2471000 | 2471000 | 2471000 | 2471000 | 12355000 | 51900000 | 445877779.07 | 4547400%
Replace Pole upon failure with class S3 (Wood) and constrained by REPEX model - fault |  | Recommended | 1880000 | 1880000 | 1880000 | 1880000 | 1880000 | 9400000 | 39480000 | 422061251.53 | 4547400%
Replace Pole upon failure with class S4 (Wood) - fault |  | Candidate | 2561000 | 2561000 | 2561000 | 2561000 | 2561000 | 12805000 | 53790000 | 441404017.18 | 4547400%
Replace Pole upon failure with FRC (Titan) - fault |  | Candidate | 2750000 | 2750000 | 2750000 | 2750000 | 2750000 | 13750000 | 57750000 | 444058193.2 | 4547400%
0
Leader Endorsement
Name |  |  | Governance |  | Signature |  |  | Comments |  |  | Date
|  |  | Submission | [7 empty] | 4486500%
|  |  | Endorsement | [7 empty] | 4486500%
|  |  | Approval | [7 empty] | 4486500%
Investment Attachments
Date | Attachment Name |  | Description

## Investment Overview
Investment Evaluation Summary |  | Copperleaf Investment Code |  | Report Start Year | NPV Period | Base Fiscal Year | Currency Scale
|  | PRJ000654 |  | 2025 | 25 | FY23 | Literal
|  | Investment Name |  |  |  |  | Scenario
|  | R24_D_OH_REPOL_Replace_Pole_Fault |  |  |  |  | Approved
Value Function | TasNetworks Value Function | Version |  | 0.1 | Date |  | 2022-10-31
Functional Area | REPOL |  | Department |  | Asset Strategy
Works Initiator |  |  | Portfolio |  | Dx - Renewal
Investment Category | Prescribed Services - Asset Renewal |  | Needs Item Reference
Investment Type | Network Project |  | Document No. |  | R2355521
Investment Stage | Gate 2 – Investment Evaluation Summary |  | Project Zone Location
PPM ID |  |  | Regulatory Test Required |  | No
Investment Overview
01. Overview | Background |  | TasNetworks has approximately 240,000 support structures installed on the distribution network to provide support, insulation and adequate clearances between live electrical assets (overhead conductors, overhead switchgear and pole mounted transformers) and the ground, vegetation and building infrastructure. Wood poles are used extensively within the distribution network because they historically represent the least cost whole-of-life option for the majority of circumstances for support structures. Wood poles have an expected service life of between 40 and 50 years with the average age of the wood pole population being 33 years. Staking of wood poles is a commonly used method deployed to reinforce the structural strength of wood poles at ground level and subsequently prolong the serviceable life of the pole. Staking wood poles commenced in 2002 and the current staked wood pole population is approximately 29,000 poles. Wood poles are generally staked at 30-45 years of age with the staked pole typically lasting 10-15 years after staking. Staking has proven to be a cost-effective way of ensuring the service life of 40-50 years is attained. Approximately 90 per cent of structures are wood poles which are vulnerable to bushfires and other ground fires and susceptible to pole top fires from pollution or other hardware failures. The remaining 10 per cent are non-wood pole type with relatively longer service life, higher supply reliability and higher resilience to bushfire and wind. |  |  |  |  | TRUE
| Problem Definition |  | Existing wood poles need replacement under fault response for damage resulting from causes including excessive strong winds and storms, vegetation impacts, bushfires and vehicle collisions. The trended historical average pole failure rate is approximately 180 poles per annum that require replacement under fault conditions to restore supply to customers. |  |  |  |  | FALSE
02. Customer Needs and Impact | Customer Needs and impact |  | TasNetworks has a customer and stakeholder engagement strategy to inform the existing program of work and the upcoming revenue submission. The feedback obtained informs the approach taken by TasNetworks to align our investments with customer needs and impacts. Customer needs addressed by this investment include: - affordability; - supply reliability and safety of the current network; - resilience to future impacts including climate change; and - investment in future networks to unlock community benefits in renewable energy products and services. |  |  |  |  | TRUE

## Objectives and Analysis
Investment Evaluation Summary |  | Copperleaf Investment Code |  | Report Start Year | NPV Period | Base Fiscal Year | Currency Scale
|  | PRJ000654 |  | 2025 | 25 | FY23 | Literal
|  | Investment Name |  |  |  |  | Scenario
|  | R24_D_OH_REPOL_Replace_Pole_Fault |  |  |  |  | Approved
Value Function | TasNetworks Value Function | Version |  | 0.1 | Date |  | 2022-10-31
Functional Area | REPOL |  | Department |  | Asset Strategy
Works Initiator |  |  | Portfolio |  | Dx - Renewal
Investment Category | Prescribed Services - Asset Renewal |  | Needs Item Reference
Investment Type | Network Project |  | Document No. |  | R2355521
Investment Stage | Gate 2 – Investment Evaluation Summary |  | Project Zone Location
PPM ID |  |  | Regulatory Test Required |  | No
Objectives and Analysis
03. Business Performance Objectives | Safety and Wellbeing |  | Performance Measure: Significant incidents Investment impact on performance: Replacement of poles reduces the risk of a pole failure resulting in bushfire starts and injury. Performance Measure: Reportable incidents Investment impact on performance: Replacement of poles reduces the risk of a pole failure resulting in bushfire starts and injury. |  |  |  |  | TRUE
| Our Customers |  | Performance Measure: Customer net promoter score Investment impact on performance: Replacement of poles reduces the risk of a pole failure resulting in bushfire starts and injury. |  |  |  |  | FALSE
| Our People |  | Performance Measure: Employee engagement Investment impact on performance: Maintain our vision of ‘powering a bright future.’ |  |  |  |  | FALSE
| Our Business - Sustained Cost Management |  | Performance Measure: Capital expenditure Investment impact on performance: Replacement reduces our total cost when compared to managing end of life pole failures. Performance Measure: Operational expenditure Investment impact on performance: Replacement reduces our operational cost in replacing poles in poor condition in a planned way prior to failure. |  |  |  |  | FALSE
| Our Business - Network Service |  | Performance Measure: Service incentive bonuses earned - distribution. Investment impact on performance: Replacement of poles will reduce the risk of failure and therefore minimise prolonged outages. |  |  |  |  | FALSE
04. Business Risks | Death or Injury (Employee) |  | Employee impacted by pole or contacts live conductors directly or indirectly after they fall to ground following pole failure. |  |  |  |  | FALSE
| Death or Injury (Public) |  | Public impacted by pole or contacts live conductors directly or indirectly after they fall to ground following pole failure. |  |  |  |  | FALSE
| Sustainable and Predictable Pricing | [6 empty] | FALSE
| Widespread Power Disruption |  | An average of 180 assisted pole failures occur per year currently. |  |  |  |  | FALSE
| Bushfire Start |  | TasNetworks has recorded ground fire starts from pole failures. |  |  |  |  | FALSE
| Loss of Major Industrial | [6 empty] | FALSE
| Customer Focus |  | Customers have an expectation of consistent and reliable power supply which these assets provide. |  |  |  |  | FALSE
| Business Continuity Management | [6 empty] | FALSE
| Cyber Security | [6 empty] | FALSE
| Private Assets | [6 empty] | FALSE
Energy Policy and Regulation
Project Marinus (D&A)
Tasmanian Power System Complexity
| Emerging Complexity of the NEM | [6 empty] | FALSE
05. Strategic Objectives | Strategic Objectives |  | The strategic objective is to manage the risk to customers by developing a risk based strategic plan. This includes replacing poles that fail in service. in order to restore supply to customers. |  |  |  |  | FALSE
| Strategic Document #1 |  | Towards 2030 We continually assess what value means to our customers to better serve all our stakeholders: Ensuring our electricity network remains resilient and fit-for-purpose by proactively maintaining assets, designing out risks, and making prudent investments of long-term value: The long-term impact of asset maintenance and renewal has been reviewed out to 2050. The analysis clearly demonstrates work should be done to mitigate risks to customers now and into the future. To ensure our capital is used wisely, we will streamline our investment planning to achieve optimised investment strategies and have the best delivery model: Investment planning has been developed to align all asset categories. The plan has been developed out to 2050 to ensure the long-term objectives of optimising investment strategies is achieved. |  |  |  |  | FALSE
| Strategic Document #2 |  | TasNetworks Business Plan |  |  |  |  | FALSE
| Strategic Document #3 |  | Network Climate Change Resilience and Adaptation Strategy |  |  |  |  | FALSE
| Strategic Document #4 |  | Bushfire Risk Mitigation Plan |  |  |  |  | FALSE
| Strategic Document #5 |  | Overhead Line Support Structures Asset Management Plan |  |  |  |  | FALSE
06. Project Objectives | Project Objectives |  | This program provides for the capitalisation of pole replacement costs incurred when poles fail in service and must be replaced to restore supply to customers. |  |  |  |  | FALSE
07. Options Analysis | Benchmarking |  | TasNetworks uses other Australian network service provider’s findings to help drive the pole asset management strategy. All other Australian NSPs utilise either a condition or a risk (likelihood and consequence of failure) based pole replacement program. Benchmarking is completed informally and also formally through the: - Regulatory information notice process; - International Wildfire Risk Management Consortium; and - Distribution Industry Working Group. Wider Industry & USC Wood rot R&D, with field trials conducted in SE QLD. |  |  |  |  | TRUE
| Expert Findings |  | Expert analysis is used to design and assess the condition of wood poles. These findings are then used to develop TasNetworks asset management strategies. Examples of these resources are: - Australian Standard for Design of Overhead Lines AS/NZS 7000 - 2016; - SAA HB 331:2020 Overhead Design Manual ; - Economic Evaluation of Treated Wooden Pole Inspection Cycles (R295189); - Network Policy NN R AM 11 Wood pole reinstatement by ground-line reinforcement (NW10149727); - ENA DOC 015-2006 National Guidelines for Prevention of Unauthorised Access to Electricity Infrastructure; - Nathan Spencer, Leith Elder, Pole Service Life - An analysis of Country Energy Data , White Paper it is published accessible on http://www.koppers.com.au/Utility-Poles/default.aspx; - Timber – Natural Durability Ratings AS 5604 – 2005; - UTAS Final Report Identification of soft rot decay fungi in eucalypt power pole samples( R 719238); and - Energy Network Association (ENA) Pole Fire Test. |  |  |  |  | FALSE
08. Investment Timing | Investment Timing |  | The program will continue for the whole regulatory period and beyond with forecast volumes remaining steady over the longer term. |  |  |  |  | TRUE
09. Expected Outcomes and Benefits | Expected Outcomes and Benefits |  | The benefits to TasNetworks from implementation of the recommended option will be: - risk to public, property, reliability and fire starts managed to an acceptable level; - capital investment managed to lowest sustainable cost; - maintain network performance; and - improved bushfire resilience. |  |  |  |  | TRUE
10. Assumptions | Assumptions |  | The 65 year service life expectation for Fibreglass Reinforced Concrete (FRC) Titan poles is supported by written advice from Supplier. It is considered to be conservative compared to R&D literature on other composite poles for 75 year service expectation from composite pole academic researchers. |  |  |  |  | TRUE
11. Regulatory Considerations | Regulatory Investment Test |  | A RIT-D is not required because this is a high volume, low cost, program to replace assets that have failed in service.
| Meet or manage the expected demand for Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | No
| Comply with all applicable regulatory obligations associated with the provision of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
| Maintain the quality, reliability and security of supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
| Maintain the reliability and security of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
| Maintain the safety of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
12. Recommendation | Recommendation |  | Replace Pole upon failure with class S3 (Wood) and constrained by REPEX model - fault, is recommended for approval as it best satisfies the customer and business needs. |  |  |  |  | TRUE

## Economic Analysis
alternative
| Investment Evaluation Summary |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[5 empty] | PRJ000654 |  | 2025 |  | 25 | FY23 | Literal
[5 empty] | Investment Name | [5 empty] | Scenario
[5 empty] | R24_D_OH_REPOL_Replace_Pole_Fault | [5 empty] | Approved
autofit | Value Function |  |  | TasNetworks Value Function | Version |  | 0.1 |  | Date |  | 2022-10-31
Economic Analysis
| Parameter |  |  |  | Value | Unit | Source of Values
75679 | NPV Period |  |  |  | 25 | Years | TasNetworks requirement
autofit | First Fiscal Year of Forecast |  |  |  | FY23 | - | TasNetworks requirement
| Weighted Average Cost of Capital (WACC) |  |  |  | 2.82 | % | 2019-24 Revenue determination and ISP 2022 draft data
| Voluntary load shedding assumed? |  |  |  | No | - | N/A
| Reduction in system losses considered? |  |  |  | No | - | N/A
| Value of Customer Reliability applied |  |  | Very large business customer - Services | 10.93 | $/kWh | AER - Values of Customer Reliability - Annual adjustment summary - December 2021
|  |  |  | Residential | 17.08 | $/kWh
|  |  |  | Very large business customer - Metals | 20.6 | $/kWh
|  |  |  | Very large business customer - Transmission | 27.43 | $/kWh
|  |  |  | Very large business customer - Mines | 36.47 | $/kWh
|  |  |  | Business customer - Agricultural | 39.28 | $/kWh
|  |  |  | Business customer - Commercial | 46.18 | $/kWh
|  |  |  | Very large business customer - Distribution | 58.8 | $/kWh
|  |  |  | Business customer - Industrial | 66.16 | $/kWh
autofit |  |  |  | Very large business customer - Industrial | 122.39 | $/kWh
Sensitivity to Project Timing
|  | 1 | Navigate to Copperleaf Portfolio and search for your Investment
|  | 2 | Navigate to the Value Comparison Page for your Investment through the breadcrumb menu
|  | 3 | Once on the Value Comparison Page, select "Value by Start Date" in the drop-down menu in the top-left corner of the page
|  | 4 | This screen will show the value change over time for each option in your investment
|  | 5 | With the snipping tool on your PC, take a screenshot of the chart and copy + paste it in this section of the report
Options Considered
| Options Summary |  |  |  | R24 Expenditure ($M) | NPV ($M) | Preferred Option | Reason for selection/rejection
| Emergency stake pole upon failure and follow up planned replacement with Titan |  |  |  | 10.6 | 449.0492 | No | This option is rejected following portfolio optimisation to balance risk and expenditure across all asset classes. Whilst it effectively manages risk, it has higher capital expenditure compared to selected option.
| Replace Pole upon failure with class S3 (Wood) - fault |  |  |  | 12.355 | 445.8778 | No | This option is rejected following portfolio optimisation to balance risk and expenditure across all asset classes. Whilst it effectively manages risk, it has higher capital expenditure compared to selected option.
| Replace Pole upon failure with class S3 (Wood) and constrained by REPEX model - fault |  |  |  | 9.4 | 422.0613 | Yes | This option is selected following portfolio optimisation to balance risk and expenditure across all asset classes. It effectively manages risk and has lower capital expenditure compared to other options.
| Replace Pole upon failure with class S4 (Wood) - fault |  |  |  | 12.805 | 441.404 | No | This option is rejected following portfolio optimisation to balance risk and expenditure across all asset classes. Whilst it effectively manages risk, it has higher capital expenditure compared to selected option.
| Replace Pole upon failure with FRC (Titan) - fault |  |  |  | 13.75 | 444.0582 | No | This option is rejected following portfolio optimisation to balance risk and expenditure across all asset classes. Whilst it effectively manages risk, it has higher capital expenditure compared to selected option.
0
NPV Components

## Needs Assessment (hidden)
Needs Assessment Form |  | Copperleaf Investment Code |  | Report Start Year | NPV Period | Base Fiscal Year | Currency Scale
|  | PRJ000654 |  | 2025 | 25 | FY23 | Literal
|  | Investment Name |  |  |  |  | Scenario
|  | R24_D_OH_REPOL_Replace_Pole_Fault |  |  |  |  | Approved
Value Function | TasNetworks Value Function | Version |  | 0.1 | Date |  | 2022-10-31
Functional Area | REPOL |  | Department |  | Asset Strategy
Works Initiator |  |  | Portfolio |  | Dx - Renewal
Investment Category | Prescribed Services - Asset Renewal |  | Needs Item Reference
Investment Type | Network Project |  | Document No. |  | R2355521
Investment Stage | Gate 2 – Investment Evaluation Summary |  | Project Zone Location
PPM ID |  |  | Regulatory Test Required |  | No
Investment Overview
01. Overview | Background |  | TasNetworks has approximately 240,000 support structures installed on the distribution network to provide support, insulation and adequate clearances between live electrical assets (overhead conductors, overhead switchgear and pole mounted transformers) and the ground, vegetation and building infrastructure. Wood poles are used extensively within the distribution network because they historically represent the least cost whole-of-life option for the majority of circumstances for support structures. Wood poles have an expected service life of between 40 and 50 years with the average age of the wood pole population being 33 years. Staking of wood poles is a commonly used method deployed to reinforce the structural strength of wood poles at ground level and subsequently prolong the serviceable life of the pole. Staking wood poles commenced in 2002 and the current staked wood pole population is approximately 29,000 poles. Wood poles are generally staked at 30-45 years of age with the staked pole typically lasting 10-15 years after staking. Staking has proven to be a cost-effective way of ensuring the service life of 40-50 years is attained. Approximately 90 per cent of structures are wood poles which are vulnerable to bushfires and other ground fires and susceptible to pole top fires from pollution or other hardware failures. The remaining 10 per cent are non-wood pole type with relatively longer service life, higher supply reliability and higher resilience to bushfire and wind. |  |  |  |  | TRUE
| Problem Definition |  | Existing wood poles need replacement under fault response for damage resulting from causes including excessive strong winds and storms, vegetation impacts, bushfires and vehicle collisions. The trended historical average pole failure rate is approximately 180 poles per annum that require replacement under fault conditions to restore supply to customers. |  |  |  |  | FALSE
02. Customer Needs and Impact | Customer Needs and impact |  | TasNetworks has a customer and stakeholder engagement strategy to inform the existing program of work and the upcoming revenue submission. The feedback obtained informs the approach taken by TasNetworks to align our investments with customer needs and impacts. Customer needs addressed by this investment include: - affordability; - supply reliability and safety of the current network; - resilience to future impacts including climate change; and - investment in future networks to unlock community benefits in renewable energy products and services. |  |  |  |  | TRUE
03. Business Objectives | Business Objectives
04. Project Objectives | Project Objectives |  | This program provides for the capitalisation of pole replacement costs incurred when poles fail in service and must be replaced to restore supply to customers. |  |  |  |  | FALSE
05. Risk Objective | Risk if not progressed | [6 empty] | TRUE
06. Investment Timing | Investment Timing |  | The program will continue for the whole regulatory period and beyond with forecast volumes remaining steady over the longer term. |  |  |  |  | TRUE
07. Business Consulatation | Business Consulatation | [6 empty] | TRUE

## Option 1
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000654 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_D_OH_REPOL_Replace_Pole_Fault | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-31
Alternative Overview
75679 | Alternative Name |  | Emergency stake pole upon failure and follow up planned replacement with Titan
autofit | Description |  | Reactive program to install emergency stake upon failure to ensure public safety with subsequent pole replacement using FRC (Titan) poles.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | This option is rejected following portfolio optimisation to balance risk and expenditure across all asset classes. Whilst it effectively manages risk, it has higher capital expenditure compared to selected option.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Emergency stake pole upon failure and follow up planned replacement with Titan |  | Capex |  |  | 2070000 | 2070000 | 2070000 | 2070000 | 2070000 | 10350000 | 44520000 | 449049235.01
|  |  | Opex |  |  | 50000 | 50000 | 50000 | 50000 | 50000 | 250000
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | UARM - Environment and Community - Fire Risk |  |  | 5118.2478 | 1%
[9 empty] | UARM - Safety & People - Worker |  |  | 2703.8052 | 0.53%
[9 empty] | UARM - Network Performance Risk |  |  | 438286.3933 | 85.45%
[9 empty] | UARM - Environment and Community - Other Risk |  |  | 11953.0445 | 2.33%
[9 empty] | UARM - Financial Risk |  |  | 11.953 | 0%
[9 empty] | UARM - Safety & People - Public |  |  | 8128.0702 | 1.58%
[9 empty] | Terminal Value |  |  | 14780.9285 | 2.88%
[9 empty] | Total Investment Cost |  |  | -31933.2075 | 6.23%
[9 empty] | Total |  |  | 449049.235
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 2070000 | 2070000 | 2070000 | 2070000 | 2070000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | OPEX Cost |  | Outcome | 2024 | 0 | Dollar | 50000 | 50000 | 50000 | 50000 | 50000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -31933.2075 | Dollar | 2120000 | 2120000 | 2120000 | 2120000 | 2120000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 14780.9285 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Baseline |  | 0 | Dollar | 3367661.75 | 3695667 | 4041690.84 | 4404662.53 | 4783138.17
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Outcome | 2024 | 5118.2478 | Dollar | 3341886.98 | 3642911.38 | 3958942.85 | 4288313.35 | 4631424.67
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Baseline |  | 0 | Dollar | 1779027.05 | 1952301.64 | 2135094.87 | 2326841.09 | 2526777.57
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Outcome | 2024 | 2703.8052 | Dollar | 1765411.06 | 1924432.54 | 2091381.77 | 2265377.58 | 2446632.22
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE | UARM - PA to Investment | UARM - Network Performance Risk |  | Baseline |  | 0 | Dollar | 288380001.86 | 316467785.42 | 346098539.02 | 377180572.07 | 409590242.42
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE | UARM - PA to Investment | UARM - Network Performance Risk |  | Outcome | 2024 | 438286.3933 | Dollar | 286172853.41 | 311950209.66 | 339012653.51 | 367217346.08 | 396598693.9
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Baseline |  | 0 | Dollar | 7864763.86 | 8630780.17 | 9438876.7 | 10286552.85 | 11170436.63
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Outcome | 2024 | 11953.0445 | Dollar | 7804570.01 | 8507575.83 | 9245628.85 | 10014833.53 | 10816128.21
| UARM - PA to Investment | UARM - Financial Risk |  | Baseline |  | 0 | Dollar | 7864.76 | 8630.78 | 9438.88 | 10286.55 | 11170.44
| UARM - PA to Investment | UARM - Financial Risk |  | Outcome | 2024 | 11.953 | Dollar | 7804.57 | 8507.58 | 9245.63 | 10014.83 | 10816.13
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE | UARM - PA to Investment | UARM - Safety & People - Public |  | Baseline |  | 0 | Dollar | 5348039.42 | 5868930.51 | 6418436.16 | 6994855.94 | 7595896.91
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE | UARM - PA to Investment | UARM - Safety & People - Public |  | Outcome | 2024 | 8128.0702 | Dollar | 5307107.61 | 5785151.57 | 6287027.62 | 6810086.8 | 7354967.18
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 306747358.7 | 336624095.52 | 368142076.47 | 401203771.03 | 435677662.14
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 304399633.64 | 331818788.56 | 360604880.23 | 390605972.17 | 421858662.31
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 2
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000654 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_D_OH_REPOL_Replace_Pole_Fault | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-31
Alternative Overview
75679 | Alternative Name |  | Replace Pole upon failure with class S3 (Wood) - fault
autofit | Description |  | Reactive program using class S3 wood poles for replacement of poles upon failure.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | This option is rejected following portfolio optimisation to balance risk and expenditure across all asset classes. Whilst it effectively manages risk, it has higher capital expenditure compared to selected option.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Replace Pole upon failure with class S3 (Wood) - fault |  | Capex |  |  | 2376000 | 2376000 | 2376000 | 2376000 | 2376000 | 11880000 | 51900000 | 445877779.07
|  |  | Opex |  |  | 95000 | 95000 | 95000 | 95000 | 95000 | 475000
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | UARM - Environment and Community - Fire Risk |  |  | 5117.5387 | 0.98%
[9 empty] | UARM - Safety & People - Worker |  |  | 2703.4306 | 0.52%
[9 empty] | UARM - Network Performance Risk |  |  | 438225.6722 | 84.22%
[9 empty] | UARM - Environment and Community - Other Risk |  |  | 11951.3885 | 2.3%
[9 empty] | UARM - Financial Risk |  |  | 11.9514 | 0%
[9 empty] | UARM - Safety & People - Public |  |  | 8126.9441 | 1.56%
[9 empty] | Terminal Value |  |  | 16965.9353 | 3.26%
[9 empty] | Total Investment Cost |  |  | -37225.0818 | 7.15%
[9 empty] | Total |  |  | 445877.7791
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 2376000 | 2376000 | 2376000 | 2376000 | 2376000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | OPEX Cost |  | Outcome | 2024 | 0 | Dollar | 95000 | 95000 | 95000 | 95000 | 95000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -37225.0818 | Dollar | 2471000 | 2471000 | 2471000 | 2471000 | 2471000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 16965.9353 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Baseline |  | 0 | Dollar | 3367661.75 | 3695667 | 4041690.84 | 4404662.53 | 4783138.17
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Outcome | 2024 | 5117.5387 | Dollar | 3341886.98 | 3642911.38 | 3958942.85 | 4288313.35 | 4631424.68
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Baseline |  | 0 | Dollar | 1779027.05 | 1952301.64 | 2135094.87 | 2326841.09 | 2526777.57
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Outcome | 2024 | 2703.4306 | Dollar | 1765411.06 | 1924432.54 | 2091381.77 | 2265377.58 | 2446632.22
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE | UARM - PA to Investment | UARM - Network Performance Risk |  | Baseline |  | 0 | Dollar | 288380001.86 | 316467785.42 | 346098539.02 | 377180572.07 | 409590242.42
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE | UARM - PA to Investment | UARM - Network Performance Risk |  | Outcome | 2024 | 438225.6722 | Dollar | 286172853.41 | 311950209.66 | 339012653.53 | 367217346.25 | 396598694.9
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Baseline |  | 0 | Dollar | 7864763.86 | 8630780.17 | 9438876.7 | 10286552.85 | 11170436.63
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Outcome | 2024 | 11951.3885 | Dollar | 7804570.01 | 8507575.83 | 9245628.85 | 10014833.53 | 10816128.24
| UARM - PA to Investment | UARM - Financial Risk |  | Baseline |  | 0 | Dollar | 7864.76 | 8630.78 | 9438.88 | 10286.55 | 11170.44
| UARM - PA to Investment | UARM - Financial Risk |  | Outcome | 2024 | 11.9514 | Dollar | 7804.57 | 8507.58 | 9245.63 | 10014.83 | 10816.13
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE | UARM - PA to Investment | UARM - Safety & People - Public |  | Baseline |  | 0 | Dollar | 5348039.42 | 5868930.51 | 6418436.16 | 6994855.94 | 7595896.91
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE | UARM - PA to Investment | UARM - Safety & People - Public |  | Outcome | 2024 | 8126.9441 | Dollar | 5307107.61 | 5785151.57 | 6287027.62 | 6810086.8 | 7354967.2
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 306747358.7 | 336624095.52 | 368142076.47 | 401203771.03 | 435677662.14
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 304399633.64 | 331818788.56 | 360604880.25 | 390605972.34 | 421858663.37
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 3
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000654 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_D_OH_REPOL_Replace_Pole_Fault | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-31
Alternative Overview
75679 | Alternative Name |  | Replace Pole upon failure with class S3 (Wood) and constrained by REPEX model - fault
autofit | Description |  | Reactive program using class S3 wood poles for replacement of poles upon failure with capital expenditure constrained by the outputs of the REPEX model.
autofit | Alternative Status |  | Recommended
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | This option is selected following portfolio optimisation to balance risk and expenditure across all asset classes. It effectively manages risk and has lower capital expenditure compared to other options.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Replace Pole upon failure with class S3 (Wood) and constrained by REPEX model - fault |  | Capex |  |  | 1785000 | 1785000 | 1785000 | 1785000 | 1785000 | 8925000 | 39480000 | 422061251.53
|  |  | Opex |  |  | 95000 | 95000 | 95000 | 95000 | 95000 | 475000
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | UARM - Environment and Community - Fire Risk |  |  | 4804.6106 | 1%
[9 empty] | UARM - Safety & People - Worker |  |  | 2538.1208 | 0.53%
[9 empty] | UARM - Network Performance Risk |  |  | 411428.9746 | 85.95%
[9 empty] | UARM - Environment and Community - Other Risk |  |  | 11220.5829 | 2.34%
[9 empty] | UARM - Financial Risk |  |  | 11.2205 | 0%
[9 empty] | UARM - Safety & People - Public |  |  | 7629.9964 | 1.59%
[9 empty] | Terminal Value |  |  | 12745.8731 | 2.66%
[9 empty] | Total Investment Cost |  |  | -28318.1274 | 5.92%
[9 empty] | Total |  |  | 422061.2515
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 1785000 | 1785000 | 1785000 | 1785000 | 1785000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | OPEX Cost |  | Outcome | 2024 | 0 | Dollar | 95000 | 95000 | 95000 | 95000 | 95000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -28318.1274 | Dollar | 1880000 | 1880000 | 1880000 | 1880000 | 1880000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 12745.8731 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Baseline |  | 0 | Dollar | 3367661.75 | 3695667 | 4041690.84 | 4404662.53 | 4783138.17
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Outcome | 2024 | 4804.6106 | Dollar | 3343285.35 | 3645647.23 | 3963349.38 | 4294593.85 | 4639058.75
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Baseline |  | 0 | Dollar | 1779027.05 | 1952301.64 | 2135094.87 | 2326841.09 | 2526777.57
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Outcome | 2024 | 2538.1208 | Dollar | 1766149.78 | 1925877.8 | 2093709.6 | 2268695.36 | 2450665.06
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE | UARM - PA to Investment | UARM - Network Performance Risk |  | Baseline |  | 0 | Dollar | 288380001.86 | 316467785.42 | 346098539.02 | 377180572.07 | 409590242.42
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE | UARM - PA to Investment | UARM - Network Performance Risk |  | Outcome | 2024 | 411428.9746 | Dollar | 286292598.74 | 312184486.26 | 339389993.97 | 367755158.48 | 397252416.54
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Baseline |  | 0 | Dollar | 7864763.86 | 8630780.17 | 9438876.7 | 10286552.85 | 11170436.63
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Outcome | 2024 | 11220.5829 | Dollar | 7807835.73 | 8513965.08 | 9255919.76 | 10029500.87 | 10833956.68
| UARM - PA to Investment | UARM - Financial Risk |  | Baseline |  | 0 | Dollar | 7864.76 | 8630.78 | 9438.88 | 10286.55 | 11170.44
| UARM - PA to Investment | UARM - Financial Risk |  | Outcome | 2024 | 11.2205 | Dollar | 7807.84 | 8513.97 | 9255.92 | 10029.5 | 10833.96
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE | UARM - PA to Investment | UARM - Safety & People - Public |  | Baseline |  | 0 | Dollar | 5348039.42 | 5868930.51 | 6418436.16 | 6994855.94 | 7595896.91
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE | UARM - PA to Investment | UARM - Safety & People - Public |  | Outcome | 2024 | 7629.9964 | Dollar | 5309328.3 | 5789496.25 | 6294025.44 | 6820060.59 | 7367090.54
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 306747358.7 | 336624095.52 | 368142076.47 | 401203771.03 | 435677662.14
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 304527005.74 | 332067986.59 | 361006254.07 | 391178038.65 | 422554021.53
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 4
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000654 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_D_OH_REPOL_Replace_Pole_Fault | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-31
Alternative Overview
75679 | Alternative Name |  | Replace Pole upon failure with class S4 (Wood) - fault
autofit | Description |  | Reactive program using class S4 wood poles for replacement of poles upon failure.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | This option is rejected following portfolio optimisation to balance risk and expenditure across all asset classes. Whilst it effectively manages risk, it has higher capital expenditure compared to selected option.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Replace Pole upon failure with class S4 (Wood) - fault |  | Capex |  |  | 2466000 | 2466000 | 2466000 | 2466000 | 2466000 | 12330000 | 53790000 | 441404017.18
|  |  | Opex |  |  | 95000 | 95000 | 95000 | 95000 | 95000 | 475000
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | UARM - Environment and Community - Fire Risk |  |  | 5076.2509 | 0.98%
[9 empty] | UARM - Safety & People - Worker |  |  | 2681.6196 | 0.52%
[9 empty] | UARM - Network Performance Risk |  |  | 434690.1021 | 83.83%
[9 empty] | UARM - Environment and Community - Other Risk |  |  | 11854.9656 | 2.29%
[9 empty] | UARM - Financial Risk |  |  | 11.855 | 0%
[9 empty] | UARM - Safety & People - Public |  |  | 8061.3766 | 1.55%
[9 empty] | Terminal Value |  |  | 17608.5843 | 3.4%
[9 empty] | Total Investment Cost |  |  | -38580.7369 | 7.44%
[9 empty] | Total |  |  | 441404.0172
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 2466000 | 2466000 | 2466000 | 2466000 | 2466000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | OPEX Cost |  | Outcome | 2024 | 0 | Dollar | 95000 | 95000 | 95000 | 95000 | 95000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -38580.7369 | Dollar | 2561000 | 2561000 | 2561000 | 2561000 | 2561000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 17608.5843 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Baseline |  | 0 | Dollar | 3367661.75 | 3695667 | 4041690.84 | 4404662.53 | 4783138.17
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Outcome | 2024 | 5076.2509 | Dollar | 3341886.98 | 3642911.38 | 3958942.86 | 4288313.46 | 4631425.36
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Baseline |  | 0 | Dollar | 1779027.05 | 1952301.64 | 2135094.87 | 2326841.09 | 2526777.57
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Outcome | 2024 | 2681.6196 | Dollar | 1765411.06 | 1924432.54 | 2091381.78 | 2265377.64 | 2446632.58
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE | UARM - PA to Investment | UARM - Network Performance Risk |  | Baseline |  | 0 | Dollar | 288380001.86 | 316467785.42 | 346098539.02 | 377180572.07 | 409590242.42
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE | UARM - PA to Investment | UARM - Network Performance Risk |  | Outcome | 2024 | 434690.1021 | Dollar | 286172853.41 | 311950209.67 | 339012654.3 | 367217355.72 | 396598753.65
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Baseline |  | 0 | Dollar | 7864763.86 | 8630780.17 | 9438876.7 | 10286552.85 | 11170436.63
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Outcome | 2024 | 11854.9656 | Dollar | 7804570.01 | 8507575.83 | 9245628.87 | 10014833.79 | 10816129.84
| UARM - PA to Investment | UARM - Financial Risk |  | Baseline |  | 0 | Dollar | 7864.76 | 8630.78 | 9438.88 | 10286.55 | 11170.44
| UARM - PA to Investment | UARM - Financial Risk |  | Outcome | 2024 | 11.855 | Dollar | 7804.57 | 8507.58 | 9245.63 | 10014.83 | 10816.13
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE | UARM - PA to Investment | UARM - Safety & People - Public |  | Baseline |  | 0 | Dollar | 5348039.42 | 5868930.51 | 6418436.16 | 6994855.94 | 7595896.91
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE | UARM - PA to Investment | UARM - Safety & People - Public |  | Outcome | 2024 | 8061.3766 | Dollar | 5307107.61 | 5785151.57 | 6287027.63 | 6810086.98 | 7354968.29
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 306747358.7 | 336624095.52 | 368142076.47 | 401203771.03 | 435677662.14
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 304399633.64 | 331818788.57 | 360604881.07 | 390605982.42 | 421858725.85
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 5
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000654 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_D_OH_REPOL_Replace_Pole_Fault | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-31
Alternative Overview
75679 | Alternative Name |  | Replace Pole upon failure with FRC (Titan) - fault
autofit | Description |  | Reactive program using FRC (Titan) poles for replacement of poles upon failure.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | This option is rejected following portfolio optimisation to balance risk and expenditure across all asset classes. Whilst it effectively manages risk, it has higher capital expenditure compared to selected option.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Replace Pole upon failure with FRC (Titan) - fault |  | Capex |  |  | 2700000 | 2700000 | 2700000 | 2700000 | 2700000 | 13500000 | 57750000 | 444058193.2
|  |  | Opex |  |  | 50000 | 50000 | 50000 | 50000 | 50000 | 250000
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | UARM - Environment and Community - Fire Risk |  |  | 5118.2478 | 0.97%
[9 empty] | UARM - Safety & People - Worker |  |  | 2703.8052 | 0.51%
[9 empty] | UARM - Network Performance Risk |  |  | 438286.3933 | 83.18%
[9 empty] | UARM - Environment and Community - Other Risk |  |  | 11953.0445 | 2.27%
[9 empty] | UARM - Financial Risk |  |  | 11.953 | 0%
[9 empty] | UARM - Safety & People - Public |  |  | 8128.0702 | 1.54%
[9 empty] | Terminal Value |  |  | 19279.4719 | 3.66%
[9 empty] | Total Investment Cost |  |  | -41422.7928 | 7.86%
[9 empty] | Total |  |  | 444058.1932
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 2700000 | 2700000 | 2700000 | 2700000 | 2700000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | OPEX Cost |  | Outcome | 2024 | 0 | Dollar | 50000 | 50000 | 50000 | 50000 | 50000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -41422.7928 | Dollar | 2750000 | 2750000 | 2750000 | 2750000 | 2750000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 19279.4719 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Baseline |  | 0 | Dollar | 3367661.75 | 3695667 | 4041690.84 | 4404662.53 | 4783138.17
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Outcome | 2024 | 5118.2478 | Dollar | 3341886.98 | 3642911.38 | 3958942.85 | 4288313.35 | 4631424.67
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Baseline |  | 0 | Dollar | 1779027.05 | 1952301.64 | 2135094.87 | 2326841.09 | 2526777.57
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Outcome | 2024 | 2703.8052 | Dollar | 1765411.06 | 1924432.54 | 2091381.77 | 2265377.58 | 2446632.22
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE | UARM - PA to Investment | UARM - Network Performance Risk |  | Baseline |  | 0 | Dollar | 288380001.86 | 316467785.42 | 346098539.02 | 377180572.07 | 409590242.42
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE | UARM - PA to Investment | UARM - Network Performance Risk |  | Outcome | 2024 | 438286.3933 | Dollar | 286172853.41 | 311950209.66 | 339012653.51 | 367217346.08 | 396598693.9
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Baseline |  | 0 | Dollar | 7864763.86 | 8630780.17 | 9438876.7 | 10286552.85 | 11170436.63
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Outcome | 2024 | 11953.0445 | Dollar | 7804570.01 | 8507575.83 | 9245628.85 | 10014833.53 | 10816128.21
| UARM - PA to Investment | UARM - Financial Risk |  | Baseline |  | 0 | Dollar | 7864.76 | 8630.78 | 9438.88 | 10286.55 | 11170.44
| UARM - PA to Investment | UARM - Financial Risk |  | Outcome | 2024 | 11.953 | Dollar | 7804.57 | 8507.58 | 9245.63 | 10014.83 | 10816.13
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE | UARM - PA to Investment | UARM - Safety & People - Public |  | Baseline |  | 0 | Dollar | 5348039.42 | 5868930.51 | 6418436.16 | 6994855.94 | 7595896.91
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE | UARM - PA to Investment | UARM - Safety & People - Public |  | Outcome | 2024 | 8128.0702 | Dollar | 5307107.61 | 5785151.57 | 6287027.62 | 6810086.8 | 7354967.18
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 306747358.7 | 336624095.52 | 368142076.47 | 401203771.03 | 435677662.14
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 304399633.64 | 331818788.56 | 360604880.23 | 390605972.17 | 421858662.31
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 6 (hidden)
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000654 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_D_OH_REPOL_Replace_Pole_Fault | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-31
Alternative Overview
75679 | Alternative Name
autofit | Description
autofit | Alternative Status
autofit | Alternative Start Date
Reason for selection/rejection
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
0
0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Total |  |  | 0
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 0 | 0 | 0 | 0 | 0
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## TextFormatting (hidden)
Index | 8
Column Width | 238
Font | Calibri
Font Size | 11
Font Colour
Text | Sheet | Group | Field | Row Height | Row Number
Reactive program to restore supply to customers by replacing poles that have failed in service. | Investment Summary | Header | Description | 15 | 9
TasNetworks has approximately 240,000 support structures installed on the distribution network to provide support, insulation and adequate clearances between live electrical assets (overhead conductors, overhead switchgear and pole mounted transformers) and the ground, vegetation and building infrastructure. Wood poles are used extensively within the distribution network because they historically represent the least cost whole-of-life option for the majority of circumstances for support structures. Wood poles have an expected service life of between 40 and 50 years with the average age of the wood pole population being 33 years. Staking of wood poles is a commonly used method deployed to reinforce the structural strength of wood poles at ground level and subsequently prolong the serviceable life of the pole. Staking wood poles commenced in 2002 and the current staked wood pole population is approximately 29,000 poles. Wood poles are generally staked at 30-45 years of age with the staked pole typically lasting 10-15 years after staking. Staking has proven to be a cost-effective way of ensuring the service life of 40-50 years is attained. Approximately 90 per cent of structures are wood poles which are vulnerable to bushfires and other ground fires and susceptible to pole top fires from pollution or other hardware failures. The remaining 10 per cent are non-wood pole type with relatively longer service life, higher supply reliability and higher resilience to bushfire and wind. | Investment Summary | 0.1 Overview | Background | 210 | 16
Existing wood poles need replacement under fault response for damage resulting from causes including excessive strong winds and storms, vegetation impacts, bushfires and vehicle collisions. The trended historical average pole failure rate is approximately 180 poles per annum that require replacement under fault conditions to restore supply to customers. | Investment Summary | 0.1 Overview | Problem Definition | 45 | 17
TasNetworks has a customer and stakeholder engagement strategy to inform the existing program of work and the upcoming revenue submission. The feedback obtained informs the approach taken by TasNetworks to align our investments with customer needs and impacts. Customer needs addressed by this investment include: - affordability; - supply reliability and safety of the current network; - resilience to future impacts including climate change; and - investment in future networks to unlock community benefits in renewable energy products and services. | Investment Summary | 02. Customer Needs and Impact | Customer Needs and impact | 135 | 18
Performance Measure: Significant incidents Investment impact on performance: Replacement of poles reduces the risk of a pole failure resulting in bushfire starts and injury. Performance Measure: Reportable incidents Investment impact on performance: Replacement of poles reduces the risk of a pole failure resulting in bushfire starts and injury. | Objectives and Analysis | 03. Business Performance Objectives | Safety and Wellbeing | 135 | 17
Performance Measure: Customer net promoter score Investment impact on performance: Replacement of poles reduces the risk of a pole failure resulting in bushfire starts and injury. | Objectives and Analysis | 03. Business Performance Objectives | Our Customers | 60 | 18
Performance Measure: Employee engagement Investment impact on performance: Maintain our vision of ‘powering a bright future.’ | Objectives and Analysis | 03. Business Performance Objectives | Our People | 45 | 19
Performance Measure: Capital expenditure Investment impact on performance: Replacement reduces our total cost when compared to managing end of life pole failures. Performance Measure: Operational expenditure Investment impact on performance: Replacement reduces our operational cost in replacing poles in poor condition in a planned way prior to failure. | Objectives and Analysis | 03. Business Performance Objectives | Our Business - Sustained Cost Management | 135 | 20
Performance Measure: Service incentive bonuses earned - distribution. Investment impact on performance: Replacement of poles will reduce the risk of failure and therefore minimise prolonged outages. | Objectives and Analysis | 03. Business Performance Objectives | Our Business - Network Service | 60 | 21
Employee impacted by pole or contacts live conductors directly or indirectly after they fall to ground following pole failure. | Objectives and Analysis | 04. Business Risks | Death or Injury (Employee) | 15 | 23
Public impacted by pole or contacts live conductors directly or indirectly after they fall to ground following pole failure. | Objectives and Analysis | 04. Business Risks | Death or Injury (Public) | 15 | 24
| Objectives and Analysis | 04. Business Risks | Sustainable and Predictable Pricing | 15 | 25
An average of 180 assisted pole failures occur per year currently. | Objectives and Analysis | 04. Business Risks | Widespread Power Disruption | 15 | 26
TasNetworks has recorded ground fire starts from pole failures. | Objectives and Analysis | 04. Business Risks | Bushfire Start | 15 | 27
| Objectives and Analysis | 04. Business Risks | Loss of Major Industrial | 15 | 28
Customers have an expectation of consistent and reliable power supply which these assets provide. | Objectives and Analysis | 04. Business Risks | Customer Focus | 15 | 29
| Objectives and Analysis | 04. Business Risks | Business Continuity Management | 15 | 30
| Objectives and Analysis | 04. Business Risks | Cyber Security | 15 | 31
| Objectives and Analysis | 04. Business Risks | Private Assets | 15 | 32
| Objectives and Analysis | 04. Business Risks | Energy Policy and Regulation | 15 | 33
| Objectives and Analysis | 04. Business Risks | Project Marinus (D&A) | 15 | 34
| Objectives and Analysis | 04. Business Risks | Tasmanian Power System Complexity | 15 | 35
| Objectives and Analysis | 04. Business Risks | Emerging Complexity of the NEM | 15 | 36
The strategic objective is to manage the risk to customers by developing a risk based strategic plan. This includes replacing poles that fail in service. in order to restore supply to customers. | Objectives and Analysis | 05. Strategic Objectives | Strategic Objectives | 30 | 38
Towards 2030 We continually assess what value means to our customers to better serve all our stakeholders: Ensuring our electricity network remains resilient and fit-for-purpose by proactively maintaining assets, designing out risks, and making prudent investments of long-term value: The long-term impact of asset maintenance and renewal has been reviewed out to 2050. The analysis clearly demonstrates work should be done to mitigate risks to customers now and into the future. To ensure our capital is used wisely, we will streamline our investment planning to achieve optimised investment strategies and have the best delivery model: Investment planning has been developed to align all asset categories. The plan has been developed out to 2050 to ensure the long-term objectives of optimising investment strategies is achieved. | Objectives and Analysis | 05. Strategic Objectives | Strategic Document #1 | 165 | 39
TasNetworks Business Plan | Objectives and Analysis | 05. Strategic Objectives | Strategic Document #2 | 15 | 40
Network Climate Change Resilience and Adaptation Strategy | Objectives and Analysis | 05. Strategic Objectives | Strategic Document #3 | 15 | 41
Bushfire Risk Mitigation Plan | Objectives and Analysis | 05. Strategic Objectives | Strategic Document #4 | 15 | 42
Overhead Line Support Structures Asset Management Plan | Objectives and Analysis | 05. Strategic Objectives | Strategic Document #5 | 15 | 43
This program provides for the capitalisation of pole replacement costs incurred when poles fail in service and must be replaced to restore supply to customers. | Objectives and Analysis | 06. Project Objectives | Project Objectives | 30 | 44
TasNetworks uses other Australian network service provider’s findings to help drive the pole asset management strategy. All other Australian NSPs utilise either a condition or a risk (likelihood and consequence of failure) based pole replacement program. Benchmarking is completed informally and also formally through the: - Regulatory information notice process; - International Wildfire Risk Management Consortium; and - Distribution Industry Working Group. Wider Industry & USC Wood rot R&D, with field trials conducted in SE QLD. | Objectives and Analysis | 07. Options Analysis | Benchmarking | 105 | 45
Expert analysis is used to design and assess the condition of wood poles. These findings are then used to develop TasNetworks asset management strategies. Examples of these resources are: - Australian Standard for Design of Overhead Lines AS/NZS 7000 - 2016; - SAA HB 331:2020 Overhead Design Manual ; - Economic Evaluation of Treated Wooden Pole Inspection Cycles (R295189); - Network Policy NN R AM 11 Wood pole reinstatement by ground-line reinforcement (NW10149727); - ENA DOC 015-2006 National Guidelines for Prevention of Unauthorised Access to Electricity Infrastructure; - Nathan Spencer, Leith Elder, Pole Service Life - An analysis of Country Energy Data , White Paper it is published accessible on http://www.koppers.com.au/Utility-Poles/default.aspx; - Timber – Natural Durability Ratings AS 5604 – 2005; - UTAS Final Report Identification of soft rot decay fungi in eucalypt power pole samples( R 719238); and - Energy Network Association (ENA) Pole Fire Test. | Objectives and Analysis | 07. Options Analysis | Expert Findings | 180 | 46
The program will continue for the whole regulatory period and beyond with forecast volumes remaining steady over the longer term. | Objectives and Analysis | 08. Investment Timing | Investment Timing | 30 | 47
The benefits to TasNetworks from implementation of the recommended option will be: - risk to public, property, reliability and fire starts managed to an acceptable level; - capital investment managed to lowest sustainable cost; - maintain network performance; and - improved bushfire resilience. | Objectives and Analysis | 09. Expected Outcomes and Benefits | Expected Outcomes and Benefits | 75 | 48
The 65 year service life expectation for Fibreglass Reinforced Concrete (FRC) Titan poles is supported by written advice from Supplier. It is considered to be conservative compared to R&D literature on other composite poles for 75 year service expectation from composite pole academic researchers. | Objectives and Analysis | 10. Assumptions | Assumptions | 45 | 49
A RIT-D is not required because this is a high volume, low cost, program to replace assets that have failed in service. | Objectives and Analysis | 11. Regulatory Considerations | Regulatory Investment Test | 15 | 50
No | Objectives and Analysis | 11. Regulatory Considerations | Meet or manage the expected demand for Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 51
Yes | Objectives and Analysis | 11. Regulatory Considerations | Comply with all applicable regulatory obligations associated with the provision of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 52
Yes | Objectives and Analysis | 11. Regulatory Considerations | Maintain the quality, reliability and security of supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 53
Yes | Objectives and Analysis | 11. Regulatory Considerations | Maintain the reliability and security of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 54
Yes | Objectives and Analysis | 11. Regulatory Considerations | Maintain the safety of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 55
Replace Pole upon failure with class S3 (Wood) and constrained by REPEX model - fault, is recommended for approval as it best satisfies the customer and business needs. | Objectives and Analysis | 12. Recommendation | Recommendation | 30 | 56
Reactive program to install emergency stake upon failure to ensure public safety with subsequent pole replacement using FRC (Titan) poles. | Option 1 | Description |  | 15
This option is rejected following portfolio optimisation to balance risk and expenditure across all asset classes. Whilst it effectively manages risk, it has higher capital expenditure compared to selected option. | Option 1 | Reason for selection/rejection |  | 15
Reactive program using class S3 wood poles for replacement of poles upon failure. | Option 2 | Description |  | 15
This option is rejected following portfolio optimisation to balance risk and expenditure across all asset classes. Whilst it effectively manages risk, it has higher capital expenditure compared to selected option. | Option 2 | Reason for selection/rejection |  | 15
Reactive program using class S3 wood poles for replacement of poles upon failure with capital expenditure constrained by the outputs of the REPEX model. | Option 3 | Description |  | 15
This option is selected following portfolio optimisation to balance risk and expenditure across all asset classes. It effectively manages risk and has lower capital expenditure compared to other options. | Option 3 | Reason for selection/rejection |  | 15
Reactive program using class S4 wood poles for replacement of poles upon failure. | Option 4 | Description |  | 15
This option is rejected following portfolio optimisation to balance risk and expenditure across all asset classes. Whilst it effectively manages risk, it has higher capital expenditure compared to selected option. | Option 4 | Reason for selection/rejection |  | 15
Reactive program using FRC (Titan) poles for replacement of poles upon failure. | Option 5 | Description |  | 15
This option is rejected following portfolio optimisation to balance risk and expenditure across all asset classes. Whilst it effectively manages risk, it has higher capital expenditure compared to selected option. | Option 5 | Reason for selection/rejection |  | 15
| Option 6 | Description
| Option 6 | Reason for selection/rejection