## Run Extract (hidden)
[12 empty] | 1 | 2 | 3 | 4 | 5 | 6
[12 empty] | Option 1 | Option 2 | Option 3 | Option 4 | Option 5 | Option 6
[10 empty] | Address | Value Metric | 25 per cent less volumes than historical volumes | 25 per cent more volumes than historical volumes | Planned Renewal
[11 empty] | Terminal Value | 14713.4412 | 24522.402 | 19617.9216
[11 empty] | UARM - Environment and Community - Fire Risk | 0 | 0 | 0
Notes | [10 empty] | UARM - Safety & People - Worker | 0 | 0 | 0
Need to open the .xlsm Investment Summary report from Copperleaf in the Trusted folder Save in the preferred location as an .xlsx Need to test environment - other and when two of the same value models have been selected with a different name | [10 empty] | UARM - Network Performance Risk | 0 | 0 | 0
[11 empty] | UARM - Environment and Community - Other Risk | 0 | 0 | 0
[11 empty] | UARM - Financial Risk | 5956286.7396 | 9927150.1052 | 7941712.6178
[11 empty] | UARM - Safety & People - Public | 0 | 0 | 0
[11 empty] | Total Investment Cost | 8184529.341 | 13640882.235 | 10912705.788
Options
| Option | 2025 | 2026 | 2027 | 2028 | 2029
| Baseline | 15156344.94 | 15156343.79 | 15156343.09 | 15156342.59 | 15156342.24
| 25 per cent less volumes than historical volumes | 14746344.36 | 14746341.92 | 14746340.25 | 14746338.96 | 14746337.92
| 25 per cent more volumes than historical volumes | 14473010.69 | 14473000.45 | 14473000.14 | 14473000.33 | 14473000.84
| Planned Renewal | 14609677.52 | 14609674.68 | 14609672.69 | 14609671.14 | 14609669.88
Option Breakdown | [7 empty] | Folder and File Paths
| Option 2 |  |  |  |  | Greater 0 | (Multiple Items)
| Recommended Option - Value | [6 empty] | This File Path | \\TNAD.tasnetworks.com.au\user$\user_folders\BahramabadiM\My Documents\Trusted\InvestmentTemplate.xlsm
| Value Function Measure | Value | Value in % | Greater 0 |  | Row Labels | Sum of Value in % | Folder Path | H:\RPSAM\SAM\R24 IES\final draft\
Option 2 | Terminal Value | 24.5224 | 0.1% | 1 | K20 | Terminal Value | 0.1% | File Name | InvestmentSummary_R24_T_SC_RENSC_SCADA RENEWAL OTHER DEVICES.xlsx
Option 2 | UARM - Environment and Community - Fire Risk | 0 | 0% | 1 | K21 | Total Investment Cost | 57.82% | File Path | H:\RPSAM\SAM\R24 IES\final draft\InvestmentSummary_R24_T_SC_RENSC_SCADA RENEWAL OTHER DEVICES.xlsx
Option 2 | UARM - Safety & People - Worker | 0 | 0% | 1 | K22 | UARM - Environment and Community - Fire Risk | 0%
Option 2 | UARM - Network Performance Risk | 0 | 0% | 1 | K23 | UARM - Environment and Community - Other Risk | 0%
Option 2 | UARM - Environment and Community - Other Risk | 0 | 0% | 1 | K24 | UARM - Financial Risk | 42.08%
Option 2 | UARM - Financial Risk | 9927.1501 | 42.08% | 1 | K25 | UARM - Network Performance Risk | 0%
Option 2 | UARM - Safety & People - Public | 0 | 0% | 1 | K26 | UARM - Safety & People - Public | 0%
Option 2 | Total Investment Cost | -13640.8822 | 57.82% | 1 | K27 | UARM - Safety & People - Worker | 0%
Option 2 |  |  |  | 0 | K28
Option 2 |  |  |  | 0 | K29
Option 2 |  |  |  | 0 | K30 |  |  | 1 | InvestmentSummary_R24_D_ND_PRHVR_Augment_HV_Fdr_TRIP.xlsx
Option 2 |  |  |  | 0 | K31 |  |  | 2 | InvestmentSummary_R24_D_OH_REPOL_Basic Fleet Pole Replacement.xlsx
Option 2 |  |  |  | 0 | K32 |  |  | 3 | InvestmentSummary_R24_T_ND_AUGSB_W Coast Reliability Improvement.xlsx
Option 2 |  |  |  | 0 | K33 |  |  | 4 | InvestmentSummary_R24_T_ND_AUGSB_Upper Derwent 110 kV Losses.xlsx
| Total | -3689.2097 | 100% |  |  |  |  | 5 | InvestmentSummary_R24_D_OH_SIWES_Bird_Mitigation.xlsx
[8 empty] | 6 | InvestmentSummary_R24_D_SB_REGMS_GMS_Replacement of GMS.xlsx
[8 empty] | 7 | InvestmentSummary_R24_D_OH_REPOL_Complex Design.xlsx
Start | Option 1 |  |  |  |  | Greater 0 | 1 | 8 | InvestmentSummary_R24_D_PQ_PQTXV_Power_Quality_LV_Tformers.xlsx
| Value Function Measure | Value | Value in % | Greater 0 |  |  |  | 9 | InvestmentSummary_R24_D_ND_PQLVV_Aug_HV_LV_Conductor.xlsx
Option 1 | Terminal Value | 14.7134 | 0.1% | 1 | K20 | Row Labels | Sum of Value in % | 10 | InvestmentSummary_R24_D_CA_SOLCP_Crossover_Extension_OH.xlsx
Option 1 | UARM - Environment and Community - Fire Risk | 0 | 0% | 1 | K21 | Terminal Value | 0.1% | 11 | InvestmentSummary_R24_D_CI_SOIRR_Irrigation_Supply.xlsx
Option 1 | UARM - Safety & People - Worker | 0 | 0% | 1 | K22 | Total Investment Cost | 57.82% | 12 | InvestmentSummary_R24_D_AMIPD_AM Improvement Program.xlsx
Option 1 | UARM - Network Performance Risk | 0 | 0% | 1 | K23 | UARM - Environment and Community - Fire Risk | 0% | 13 | InvestmentSummary_R24_D_CI_SOPOR_Permanent_Residence_OH.xlsx
Option 1 | UARM - Environment and Community - Other Risk | 0 | 0% | 1 | K24 | UARM - Environment and Community - Other Risk | 0% | 14 | InvestmentSummary_R24_D_CI_SUPOR_Permanent_Residence_UG.xlsx
Option 1 | UARM - Financial Risk | 5956.2867 | 42.08% | 1 | K25 | UARM - Financial Risk | 42.08% | 15 | InvestmentSummary_R24_D_CI_SOGSI_General_Supply_OH.xlsx
Option 1 | UARM - Safety & People - Public | 0 | 0% | 1 | K26 | UARM - Network Performance Risk | 0% | 16 | InvestmentSummary_R24_D_CI_SUGSI_General_Supply_UG.xlsx
Option 1 | Total Investment Cost | -8184.5293 | 57.82% | 1 | K27 | UARM - Safety & People - Public | 0% | 17 | InvestmentSummary_R24_D_CI_SUSBD_Subdivision_UG.xlsx
Option 1 |  |  |  | 0 | K28 | UARM - Safety & People - Worker | 0% | 18 | InvestmentSummary_R24_D_CI_SOSDI_Subdivision_OH.xlsx
Option 1 |  |  |  | 0 | K29 |  |  | 19 | InvestmentSummary_R24_D_CI_SUSUB_Augment_Dist_Substations.xlsx
Option 1 |  |  |  | 0 | K30 |  |  | 20 | InvestmentSummary_R24_T_ND_LAEMP_SELA.xlsx
Option 1 |  |  |  | 0 | K31 |  |  | 21 | InvestmentSummary_R24_D_CA_DESDB_Prelim_Drive_by_Design.xlsx
Option 1 |  |  |  | 0 | K32 |  |  | 22 | InvestmentSummary_R24_D_CI_SUMPR_Major_Commercial.xlsx
Option 1 |  |  |  | 0 | K33 |  |  | 23 | InvestmentSummary_R24_D_CI_EASEN_Easements_Non_Major_Comm.xlsx
| Total | -2213.5292 | 100% |  |  |  |  | 24 | InvestmentSummary_R24_D_ND_PRHVR_Rosebery_Supply_Improve.xlsx
[8 empty] | 25 | InvestmentSummary_R24_D_ND_CAHVF_Huonville_Supply_Improvement.xlsx
[8 empty] | 26 | InvestmentSummary_R24_D_ND_CAHVF_Aug_Fdr_Network_Access.xlsx
[8 empty] | 27 | InvestmentSummary_R24_D_ND_PRHVR_Deloraine_Supply_Improve.xlsx
| Option 2 |  |  |  |  | Greater 0 | 1 | 28 | InvestmentSummary_R24_D_ND_CALVF_Augment_LV_Fdr_Capacity.xlsx
| Value Function Measure | Value | Value in % | Greater 0 |  |  |  | 29 | InvestmentSummary_R24_D_ND_CAHVF_Augment_HV_Fdr_Trunk.xlsx
Option 2 | Terminal Value | 24.5224 | 0.1% | 1 | K20 | Row Labels | Sum of Value in % | 30 | InvestmentSummary_R24_D_ND_CAHVF_Aug_Pole_Mtd_Regulator.xlsx
Option 2 | UARM - Environment and Community - Fire Risk | 0 | 0% | 1 | K21 | Terminal Value | 0.1% | 31 | InvestmentSummary_R24_D_ND_CAHVF_Aug_Grnd_Mtd_Regulator.xlsx
Option 2 | UARM - Safety & People - Worker | 0 | 0% | 1 | K22 | Total Investment Cost | 57.82% | 32 | InvestmentSummary_R24_D_ND_CAHVF_22kV_Emu_Bay_Feeders.xlsx
Option 2 | UARM - Network Performance Risk | 0 | 0% | 1 | K23 | UARM - Environment and Community - Fire Risk | 0% | 33 | InvestmentSummary_R24_D_ND_CAHVF_Augment_HV_Fdr_Capacity.xlsx
Option 2 | UARM - Environment and Community - Other Risk | 0 | 0% | 1 | K24 | UARM - Environment and Community - Other Risk | 0% | 34 | InvestmentSummary_R24_D_ND_CAHVF_Aug_SubStd_Cond_Capacity.xlsx
Option 2 | UARM - Financial Risk | 9927.1501 | 42.08% | 1 | K25 | UARM - Financial Risk | 42.08% | 35 | InvestmentSummary_R24_D_ND_LANDZ_LandAcq_ZoneSubs.xlsx
Option 2 | UARM - Safety & People - Public | 0 | 0% | 1 | K26 | UARM - Network Performance Risk | 0% | 36 | InvestmentSummary_R24_D_ND_CATXU_Aug_Dist_Sub.xlsx
Option 2 | Total Investment Cost | -13640.8822 | 57.82% | 1 | K27 | UARM - Safety & People - Public | 0% | 37
Option 2 |  |  |  | 0 | K28 | UARM - Safety & People - Worker | 0% | 38
Option 2 |  |  |  | 0 | K29 |  |  | 39
Option 2 |  |  |  | 0 | K30 |  |  | 40
Option 2 |  |  |  | 0 | K31 |  |  | 41
Option 2 |  |  |  | 0 | K32 |  |  | 42
Option 2 |  |  |  | 0 | K33 |  |  | 43
| Total | -3689.2097 | 100%
| Option 3 |  |  |  |  | Greater 0 | 1
| Value Function Measure | Value | Value in % | Greater 0
Option 3 | Terminal Value | 19.6179 | 0.1% | 1 | K20 | Row Labels | Sum of Value in %
Option 3 | UARM - Environment and Community - Fire Risk | 0 | 0% | 1 | K21 | Terminal Value | 0.1%
Option 3 | UARM - Safety & People - Worker | 0 | 0% | 1 | K22 | Total Investment Cost | 57.82%
Option 3 | UARM - Network Performance Risk | 0 | 0% | 1 | K23 | UARM - Environment and Community - Fire Risk | 0%
Option 3 | UARM - Environment and Community - Other Risk | 0 | 0% | 1 | K24 | UARM - Environment and Community - Other Risk | 0%
Option 3 | UARM - Financial Risk | 7941.7126 | 42.08% | 1 | K25 | UARM - Financial Risk | 42.08%
Option 3 | UARM - Safety & People - Public | 0 | 0% | 1 | K26 | UARM - Network Performance Risk | 0%
Option 3 | Total Investment Cost | -10912.7058 | 57.82% | 1 | K27 | UARM - Safety & People - Public | 0%
Option 3 |  |  |  | 0 | K28 | UARM - Safety & People - Worker | 0%
Option 3 |  |  |  | 0 | K29
Option 3 |  |  |  | 0 | K30
Option 3 |  |  |  | 0 | K31
Option 3 |  |  |  | 0 | K32
Option 3 |  |  |  | 0 | K33
| Total | -2951.3752 | 100%
| Option 4 |  |  |  |  | Greater 0 | 0
| Value Function Measure | Value | Value in % | Greater 0
Option 4 |  |  |  | 0 | K20 | Row Labels | Sum of Value in %
Option 4 |  |  |  | 0 | K21 |  | 0%
Option 4 |  |  |  | 0 | K22
Option 4 |  |  |  | 0 | K23
Option 4 |  |  |  | 0 | K24
Option 4 |  |  |  | 0 | K25
Option 4 |  |  |  | 0 | K26
Option 4 |  |  |  | 0 | K27
Option 4 |  |  |  | 0 | K28
Option 4 |  |  |  | 0 | K29
Option 4 |  |  |  | 0 | K30
Option 4 |  |  |  | 0 | K31
Option 4 |  |  |  | 0 | K32
Option 4 |  |  |  | 0 | K33
| Total | 0 | 0%
| Option 5 |  |  |  |  | Greater 0 | 0
| Value Function Measure | Value | Value in % | Greater 0
Option 5 |  |  |  | 0 | K20 | Row Labels | Sum of Value in %
Option 5 |  |  |  | 0 | K21 |  | 0%
Option 5 |  |  |  | 0 | K22
Option 5 |  |  |  | 0 | K23
Option 5 |  |  |  | 0 | K24
Option 5 |  |  |  | 0 | K25
Option 5 |  |  |  | 0 | K26
Option 5 |  |  |  | 0 | K27
Option 5 |  |  |  | 0 | K28
Option 5 |  |  |  | 0 | K29
Option 5 |  |  |  | 0 | K30
Option 5 |  |  |  | 0 | K31
Option 5 |  |  |  | 0 | K32
Option 5 |  |  |  | 0 | K33
| Total | 0 | 0%
| Option 6 |  |  |  |  | Greater 0 | 0
| Value Function Measure | Value | Value in % | Greater 0
Option 6 |  |  |  | 0 | K20 | Row Labels | Sum of Value in %
Option 6 |  |  |  | 0 | K21 |  | 0%
Option 6 |  |  |  | 0 | K22
Option 6 |  |  |  | 0 | K23
Option 6 |  |  |  | 0 | K24
Option 6 |  |  |  | 0 | K25
Option 6 |  |  |  | 0 | K26
Option 6 |  |  |  | 0 | K27
Option 6 |  |  |  | 0 | K28
Option 6 |  |  |  | 0 | K29
Option 6 |  |  |  | 0 | K30
Option 6 |  |  |  | 0 | K31
Option 6 |  |  |  | 0 | K32
Option 6 |  |  |  | 0 | K33
| Total | 0 | 0%

## Summary
Investment Evaluation Summary |  |  |  | Investment Code |  | Report Start Year |  | NPV Period | Base Fiscal Year | Currency Scale
|  |  |  | PRJ000628 |  | 2025 |  | 25 | FY23 | Literal
|  |  |  | Investment Name | [5 empty] | Scenario
|  |  |  | R24_T_SC_RENSC_SCADA RENEWAL OTHER DEVICES | [5 empty] | Approved
Value Function |  | TasNetworks Value Function |  | Version |  | 0.1 |  | Date |  | 2022-11-03
Investment Description
Description |  | This program includes the renewal of SCADA and automations equipment that is required to monitor the state and health of primary and secondary assets associated with the transmission network which includes: Power Quality Meters (PQM); Phasor Measurement Unit (PMU); Phasor Data Concentrator (PDC); Automatic Voltage Regulators (AVR); Bay Controllers (BC); and Global Positioning System (GPS) clocks. | [9 empty] | TRUE
Functional Area |  | rensc |  |  | Department |  |  | Asset Strategy
Works Initiator |  |  |  |  | Portfolio |  |  | Tx - Renewal
Investment Category |  | Prescribed Services - Asset Renewal |  |  | Needs Item Reference
Investment Type |  | Network Project |  |  | Document No.
Investment Stage |  | Gate 2 – Investment Evaluation Summary |  |  | Project Zone Location
PPM ID |  |  |  |  | Regulatory Test Required |  |  | No
Investment Summary
Problem Definition |  | TasNetworks' aging SCADA and automation devices exhibit high failure rates resulting in operational safety, reliability and maintenance issues, non-conformance to the AEMO and AER rules, and diminished network visibility and control. This in turn will trigger network constraints, increased customer outages and failure to disable circuit breaker auto reclose on high bushfire risk days, which can lead to increased risk of a bushfire start from TasNetworks assets. The aged assets are also without manufacturers support which increases the risk for cyber attacks Devices with no manufacturer support, i.e. software updates, increases TasNetworks’ cyber security risk and has the potential for a cyber-attack to take control of our network causing incorrect network operations and major impact to customer supply. | [9 empty] | TRUE
Recommendation |  | The recommended option includes the renewal of SCADA and automations equipment that is required to monitor the state and health of primary and secondary assets associated with the transmission network which includes: Power Quality Meters; Phasor Measurement Units; Phasor Data Concentrators; Automatic Voltage Regulators; Bay Controllers; and Global Positioning System clocks. This option will assist TasNetworks to meet AER compliance regulations and network performance requirements and reduce cyber security risk. The program selected aligns with multiple business strategic objectives, intelligent asset management, and provides real time data for NOCS and AEMO. This option will maintain the fleet in a condition that manages risk now and into the future. | [9 empty] | TRUE
Alternative Spend Profile
Name |  | Status | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV | Alternative Start Date
25 per cent less volumes than historical volumes |  | Candidate | 990000 | 990000 | 990000 | 990000 | 990000 | 4950000 | 9900000 | -2228242.6 | 4547400%
25 per cent more volumes than historical volumes |  | Recommended | 1650000 | 1650000 | 1650000 | 1650000 | 1650000 | 8250000 | 16500000 | -3713732.13 | 4547400%
Planned Renewal |  | Candidate | 1320000 | 1320000 | 1320000 | 1320000 | 1320000 | 6600000 | 13200000 | -2970993.17 | 4547400%
0
0
0
Leader Endorsement
Name |  |  | Governance |  | Signature |  |  | Comments |  |  | Date
|  |  | Submission | [7 empty] | 4486800%
|  |  | Endorsement | [7 empty] | 4486800%
|  |  | Approval | [7 empty] | 4486800%
Investment Attachments
Date | Attachment Name |  | Description
4484754% | SCADA Systems Asset Management Plan (Transmission).docx |  | Approved SCADA AMP

## Investment Overview
Investment Evaluation Summary |  | Copperleaf Investment Code |  | Report Start Year | NPV Period | Base Fiscal Year | Currency Scale
|  | PRJ000628 |  | 2025 | 25 | FY23 | Literal
|  | Investment Name |  |  |  |  | Scenario
|  | R24_T_SC_RENSC_SCADA RENEWAL OTHER DEVICES |  |  |  |  | Approved
Value Function | TasNetworks Value Function | Version |  | 0.1 | Date |  | 2022-11-03
Functional Area | rensc |  | Department |  | Asset Strategy
Works Initiator |  |  | Portfolio |  | Tx - Renewal
Investment Category | Prescribed Services - Asset Renewal |  | Needs Item Reference
Investment Type | Network Project |  | Document No.
Investment Stage | Gate 2 – Investment Evaluation Summary |  | Project Zone Location
PPM ID |  |  | Regulatory Test Required |  | No
Investment Overview
01. Overview | Background |  | TasNetworks owns and operates 110 kV and 220 kV transmission network and associated substation assets and are compelled to meet Australian Energy Regulator (AER) National Electricity Rules (NER) and Australian Energy Market Operator (AEMO) standards, specifically for SCADA and automation systems, which include: - AEMO data and communications standard; - AEMO power system security guidelines (Chapters 13, 14 and 16); - NER sections 4.11.1 Remote control and monitoring devices; - NER sections 4.11.2 Operational control and indication communication facilities; and - NER rule clause 4 .11.1(d) provision of remote monitoring equipment. SCADA and automations systems are required to monitor the state and health of primary and secondary assets associated with the transmission network and include the following equipment: - Power Quality Meters (PQM); - Phasor Measurement Unit (PMU); - Phasor Data Concentrator (PDC); - Automatic Voltage Regulators (AVRs); - Networks Switches; - Bay Controllers(BCs); and - Global Positioning System (GPS) clocks. The SCADA and automation systems provide control of primary plant such as circuit breakers, disconnectors, tap changers for voltage regulation and control for system contingency schemes such as under/over frequency, network overload, generator run-back, and anti-islanding schemes. Local operators once had to manually operate a disconnector directly beneath the primary plant, but this can now be done through the SCADA system from within the substation control room. The SCADA and automation systems provide the Network Operations Control Centre and AEMO, in real time, data for primary equipment operations, phasor measurements (used for state estimations) and alarms that may require immediate action. The SCADA and automation systems also provide remote engineering access to equipment such as protection relays, power quality meters and condition monitoring equipment, allowing faster post fault analysis and equipment health monitoring as required to meet NER and AEMO rules, and alleviate the need for personnel to travel to sites. |  |  |  |  | TRUE
| Problem Definition |  | TasNetworks' aging SCADA and automation devices exhibit high failure rates resulting in operational safety, reliability and maintenance issues, non-conformance to the AEMO and AER rules, and diminished network visibility and control. This in turn will trigger network constraints, increased customer outages and failure to disable circuit breaker auto reclose on high bushfire risk days, which can lead to increased risk of a bushfire start from TasNetworks assets. The aged assets are also without manufacturers support which increases the risk for cyber attacks Devices with no manufacturer support, i.e. software updates, increases TasNetworks’ cyber security risk and has the potential for a cyber-attack to take control of our network causing incorrect network operations and major impact to customer supply. |  |  |  |  | FALSE
02. Customer Needs and Impact | Customer Needs and impact |  | TasNetworks has a customer and stakeholder engagement strategy to inform the existing program of work and the upcoming revenue submission. The feedback obtained informs the approach taken by TasNetworks to align our investments with customer needs and impacts. Customer needs addressed by this investment include: - affordability; and - supply reliability and safety of the current network; Consumers have also identified safety, restoration of faults/emergencies and supply reliability as the highest performing services offered by TasNetworks. The correct operation of SCADA and automation devices are critical to enable TasNetworks to offer services that also meet these top priorities. |  |  |  |  | TRUE

## Objectives and Analysis
Investment Evaluation Summary |  | Copperleaf Investment Code |  | Report Start Year | NPV Period | Base Fiscal Year | Currency Scale
|  | PRJ000628 |  | 2025 | 25 | FY23 | Literal
|  | Investment Name |  |  |  |  | Scenario
|  | R24_T_SC_RENSC_SCADA RENEWAL OTHER DEVICES |  |  |  |  | Approved
Value Function | TasNetworks Value Function | Version |  | 0.1 | Date |  | 2022-11-03
Functional Area | rensc |  | Department |  | Asset Strategy
Works Initiator |  |  | Portfolio |  | Tx - Renewal
Investment Category | Prescribed Services - Asset Renewal |  | Needs Item Reference
Investment Type | Network Project |  | Document No.
Investment Stage | Gate 2 – Investment Evaluation Summary |  | Project Zone Location
PPM ID |  |  | Regulatory Test Required |  | No
Objectives and Analysis
03. Business Performance Objectives | Safety and Wellbeing |  | Failed devices leads to putting operational personal in the vicinity of primary equipment during operation. Failure to maintain our devices will require increased driving to site, operator fatigue and CO2 emissions. |  |  |  |  | TRUE
| Our Customers |  | Failed devices can affect major industrials, as network constraints may be imposed, reducing quality of supply and reliability with the result of poor customer experience. Failed devices require driving to site increasing carbon footprint. |  |  |  |  | FALSE
| Our People | [6 empty] | FALSE
| Our Business - Sustained Cost Management |  | Failure to maintain devices can lead to failure to meet AEMO operating standards and procedures, which in turn can lead to penalties (TasNetworks may incur fines for compliance breaches to NER 4.11.2) or network constraints. Failure to maintain devices will also increase cost of having to man substations, longer outages due to repairs of unsupported devices and increases cyber security risk by having old unsupported equipment. |  |  |  |  | FALSE
| Our Business - Network Service | [6 empty] | FALSE
04. Business Risks | Death or Injury (Employee) |  | If the identified SCADA device (such as a bay controller) fails, this will require transmission lines and other equipment to be monitored and operated onsite, placing operators in close proximity to the EHV equipment. This will increase the risk of a safety incident if there is a failure of the primary equipment or an operational error. |  |  |  |  | FALSE
| Death or Injury (Public) | [6 empty] | FALSE
| Sustainable and Predictable Pricing |  | Once dedicated spares have fully depleted and manufacturer support has ceased, the rectification of a failed device becomes an unplanned refurbishment by installing a different model of device in place of the failed device. For this equipment, this requires replacement of the device and all associated wiring, which involves redesign and re-commissioning of the scheme under fault response conditions. These unplanned costs are not included in normal operational or capital budgets and can have an effect on the delivery of the planned program of work. |  |  |  |  | FALSE
| Widespread Power Disruption |  | Incorrectly installed or failed SCADA devices could cause incorrect operation of special protection and control schemes leading to a significant loss of supply event. |  |  |  |  | FALSE
| Bushfire Start |  | Failed SCADA devices can lead to in-operability of circuit breakers ( i.e.: unable to remotely disable auto reclosers) when required on high bushfire days. |  |  |  |  | FALSE
| Loss of Major Industrial |  | Failed devices can affect major industrial customers, as network constraints may be imposed, reducing quality of supply and reliability with result in poor customer experience. |  |  |  |  | FALSE
| Customer Focus |  | Material supply interruption and contribution towards: - substandard performance(STIPs); - unavailability of network services; - negative impact on community values and expectations; - increased customer complaints; - reputation damage; and - climate change. |  |  |  |  | FALSE
| Business Continuity Management | [6 empty] | FALSE
| Cyber Security |  | Obsolete equipment increases the potential for cyber-attacks on the operational network, which can cause incorrect operations of primary equipment and lengthy outages to customers. |  |  |  |  | FALSE
| Private Assets | [6 empty] | FALSE
| Energy Policy and Regulation |  | Failure to meet Department of Home Affair’s legislation (i.e. cyber security), AER and AEMO regulations. such as NER rule 6A.6.7 (3)(1) “the quality, reliability or security of supply of prescribed transmission services”.
Project Marinus (D&A)
| Tasmanian Power System Complexity |  | Failed devices (bay controllers, power quality meters, phasor measurement units, etc.) can cause network operations and AEMO to lose visibility of certain parts of the network leading to increase in low inertia system strength conditions leading to imposed network constraints.
| Emerging Complexity of the NEM | [6 empty] | FALSE
05. Strategic Objectives | Strategic Objectives |  | TasNetworks 21-22 business plan, Safety- Reduce Loss time injuries: Newer devices will reduce the operational safety risk. Transmission network strategy: Utilising these systems will provide real time data of assets assisting in the power systems team to model the network. |  |  |  |  | FALSE
| Strategic Document #1 |  | TasNetworks Three year business plan Clean energy future: New devices will lead to less driving to sites for operational issues assisting in a clean energy future Intelligent asset management: Utilising new devices for these systems provides real time data for asset management and operational control and improving TasNetworks’ ability to make data driven decisions. Improving our protection and security of assets and data: Bringing these systems up to latest technology will assist in the protection of these assets from cyber-attacks and / or data breaches. |  |  |  |  | FALSE
| Strategic Document #2 |  | NER NER section 4 .11.1(d) power system security support: Provides AER power system security requirements such as High Speed system Monitoring (HSM) and psymetrix (i.e. early warning of degraded power system damping). NER rule 6A.6.7 (3)(1) “the quality, reliability or security of supply of prescribed transmission services”. |  |  |  |  | FALSE
| Strategic Document #3 |  | TasNetworks towards 2030 Efficiency: Artificial intelligence used to optimise grid performance, reduce safety risks, optimising alternative solutions. |  |  |  |  | FALSE
| Strategic Document #4 |  | SCADA and Automation Asset Management Plan |  |  |  |  | FALSE
| Strategic Document #5 | [6 empty] | FALSE
06. Project Objectives | Project Objectives |  | Risk mitigation of substation SCADA and automation equipment to ensure we meet our business objectives, customers’ expectations, regulatory and compliance requirements outlined by AER and AEMO, provide real time data for more efficient network operations and minimising cyber security risk. |  |  |  |  | FALSE
07. Options Analysis | Benchmarking |  | TasNetworks participates in regulatory information notice (RIN) reporting annually. Which benchmarks TasNetworks transmission expenditure against other transmission service providers (TasNetworks) to provide a score on efficiency. TasNetworks reports on: - number of assets in service; - capital expenditure and asset replacements; - operational expenditure and asset failures; and - number of inspected / maintained assets. Additionally, other options were considered during the development of this IES that did not proceed to economic analysis. They included: Install New Technology Description - Install alternative new technology not currently used by TasNetworks. Reason for Rejection - Not assessed due to no existing TasNetworks standard on how to install, test and commission. High level economic assessment indicated much higher cost due to non-standard replacement rather than like-for-like. |  |  |  |  | TRUE
| Expert Findings |  | TasNetworks have formally conducted asset category forums involving experts in the strategy, engineering, and field maintenance areas to discuss issues with the protection equipment and to trigger initiatives to rectify the identified issues. These forums, known as the Management Operating System (MOS), in particular the ‘J’ meetings are held monthly to regularly capture information relating to the protection asset category. |  |  |  |  | FALSE
08. Investment Timing | Investment Timing |  | This program is a continuation of an existing program due to the size of this asset portfolio. This program runs for the FY2025-29 years with the capital investment spread over a five-year period to accommodate timing of services, resources, invoicing and financial closeout. It is anticipated that investment on this asset portfolio will be required into further regulatory periods. |  |  |  |  | TRUE
09. Expected Outcomes and Benefits | Expected Outcomes and Benefits |  | The benefits to TasNetworks from implementation of the preferred option should be: - alignment with TasNetworks business objectives such as zero harm; - alignment with customer expectations such as reducing carbon footprint by less driving; - faster restoration of supply to our customers; - limit AEMO infringement notices for non-compliance to the data and communications standard, NER sections 4.11.1 and 4.11.2, minimising cyber security risks by providing added security features and minimise last minutes security patches; and - Maintaining a reliable SCADA system to provide real time data of assets. Improved network asset management and monitoring to provide data driven decisions and intelligent asset management. |  |  |  |  | TRUE
10. Assumptions | Assumptions |  | This is a compliance program for TasNetworks to meet AER and AEMO obligations such as, - AEMO data and communications standard. - AEMO power system security guidelines (Chapters 13, 14 and 16). - NER sections 4.11.1 Remote control and monitoring devices. - NER sections 4.11.2 Operational control and indication communication facilities; and - NER rule clause 4 .11.1(d) provision of remote monitoring equipment. - It is assumed that the data and the TQR inputs are correct (data in TQR was has only quantified asset failure data as the other data for other risks is not quantified), and the failure curves associated with this asset are correct to allow copperleaf to perform its correct calculations. - Advice from an external consult was that this is a compliance based program, hence no other risks have been quantified other than financial based from rectification of asset failures. |  |  |  |  | TRUE
11. Regulatory Considerations | Regulatory Investment Test |  | This initiative relates to a program of work for asset renewal where individual assets are replaced when they fail a serviceability test and therefore a RIT-T is not required.
| Meet or manage the expected demand for Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
| Comply with all applicable regulatory obligations associated with the provision of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
| Maintain the quality, reliability and security of supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
| Maintain the reliability and security of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
| Maintain the safety of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
12. Recommendation | Recommendation |  | The recommended option includes the renewal of SCADA and automations equipment that is required to monitor the state and health of primary and secondary assets associated with the transmission network which includes: Power Quality Meters; Phasor Measurement Units; Phasor Data Concentrators; Automatic Voltage Regulators; Bay Controllers; and Global Positioning System clocks. This option will assist TasNetworks to meet AER compliance regulations and network performance requirements and reduce cyber security risk. The program selected aligns with multiple business strategic objectives, intelligent asset management, and provides real time data for NOCS and AEMO. This option will maintain the fleet in a condition that manages risk now and into the future. |  |  |  |  | TRUE

## Economic Analysis
alternative
| Investment Evaluation Summary |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[5 empty] | PRJ000628 |  | 2025 |  | 25 | FY23 | Literal
[5 empty] | Investment Name | [5 empty] | Scenario
[5 empty] | R24_T_SC_RENSC_SCADA RENEWAL OTHER DEVICES | [5 empty] | Approved
autofit | Value Function |  |  | TasNetworks Value Function | Version |  | 0.1 |  | Date |  | 2022-11-03
Economic Analysis
| Parameter |  |  |  | Value | Unit | Source of Values
75679 | NPV Period |  |  |  | 25 | Years | TasNetworks requirement
autofit | First Fiscal Year of Forecast |  |  |  | FY23 | - | TasNetworks requirement
| Weighted Average Cost of Capital (WACC) |  |  |  | 2.82 | % | 2019-24 Revenue determination and ISP 2022 draft data
| Voluntary load shedding assumed? |  |  |  | No | - | N/A
| Reduction in system losses considered? |  |  |  | No | - | N/A
| Value of Customer Reliability applied |  |  | Very large business customer - Services | 10.93 | $/kWh | AER - Values of Customer Reliability - Annual adjustment summary - December 2021
|  |  |  | Residential | 17.08 | $/kWh
|  |  |  | Very large business customer - Metals | 20.6 | $/kWh
|  |  |  | Very large business customer - Transmission | 27.43 | $/kWh
|  |  |  | Very large business customer - Mines | 36.47 | $/kWh
|  |  |  | Business customer - Agricultural | 39.28 | $/kWh
|  |  |  | Business customer - Commercial | 46.18 | $/kWh
|  |  |  | Very large business customer - Distribution | 58.8 | $/kWh
|  |  |  | Business customer - Industrial | 66.16 | $/kWh
autofit |  |  |  | Very large business customer - Industrial | 122.39 | $/kWh
Sensitivity to Project Timing
|  | 1 | Navigate to Copperleaf Portfolio and search for your Investment
|  | 2 | Navigate to the Value Comparison Page for your Investment through the breadcrumb menu
|  | 3 | Once on the Value Comparison Page, select "Value by Start Date" in the drop-down menu in the top-left corner of the page
|  | 4 | This screen will show the value change over time for each option in your investment
|  | 5 | With the snipping tool on your PC, take a screenshot of the chart and copy + paste it in this section of the report
Options Considered
| Options Summary |  |  |  | R24 Expenditure ($M) | NPV ($M) | Preferred Option | Reason for selection/rejection
| 25 per cent less volumes than historical volumes |  |  |  | 4.95 | -2.2282 | No | Rejected: This option will increase risks to people, potentially not meeting AER network performance and regulatory requirements. This will create a bow wave of failures and regulator issues. Also limits the alignment with strategic business objectives, such as intelligent asset management.
| 25 per cent more volumes than historical volumes |  |  |  | 8.25 | -3.7137 | Yes | Recommended: This option will allow TasNetworks to meet AER compliance regulations and network performance requirements, as well as reduce cyber security risk. Aligns with multiple strategic objectives, intelligent asset management and provides real time data for NOCS and AEMO. This option will maintain the fleet in a condition that manages risk now and into the future.
| Planned Renewal |  |  |  | 6.6 | -2.971 | No | Rejected: This will increase risks to people, potentially not meeting AER network performance and regulatory requirements compared to the recommended option. This will create a bow wave of failures (increase costs) and regulatory issues. Also limits the alignment with business strategic objectives, such as intelligent asset management.
0
0
0
NPV Components

## Needs Assessment (hidden)
Needs Assessment Form |  | Copperleaf Investment Code |  | Report Start Year | NPV Period | Base Fiscal Year | Currency Scale
|  | PRJ000628 |  | 2025 | 25 | FY23 | Literal
|  | Investment Name |  |  |  |  | Scenario
|  | R24_T_SC_RENSC_SCADA RENEWAL OTHER DEVICES |  |  |  |  | Approved
Value Function | TasNetworks Value Function | Version |  | 0.1 | Date |  | 2022-11-03
Functional Area | rensc |  | Department |  | Asset Strategy
Works Initiator |  |  | Portfolio |  | Tx - Renewal
Investment Category | Prescribed Services - Asset Renewal |  | Needs Item Reference
Investment Type | Network Project |  | Document No.
Investment Stage | Gate 2 – Investment Evaluation Summary |  | Project Zone Location
PPM ID |  |  | Regulatory Test Required |  | No
Investment Overview
01. Overview | Background |  | TasNetworks owns and operates 110 kV and 220 kV transmission network and associated substation assets and are compelled to meet Australian Energy Regulator (AER) National Electricity Rules (NER) and Australian Energy Market Operator (AEMO) standards, specifically for SCADA and automation systems, which include: - AEMO data and communications standard; - AEMO power system security guidelines (Chapters 13, 14 and 16); - NER sections 4.11.1 Remote control and monitoring devices; - NER sections 4.11.2 Operational control and indication communication facilities; and - NER rule clause 4 .11.1(d) provision of remote monitoring equipment. SCADA and automations systems are required to monitor the state and health of primary and secondary assets associated with the transmission network and include the following equipment: - Power Quality Meters (PQM); - Phasor Measurement Unit (PMU); - Phasor Data Concentrator (PDC); - Automatic Voltage Regulators (AVRs); - Networks Switches; - Bay Controllers(BCs); and - Global Positioning System (GPS) clocks. The SCADA and automation systems provide control of primary plant such as circuit breakers, disconnectors, tap changers for voltage regulation and control for system contingency schemes such as under/over frequency, network overload, generator run-back, and anti-islanding schemes. Local operators once had to manually operate a disconnector directly beneath the primary plant, but this can now be done through the SCADA system from within the substation control room. The SCADA and automation systems provide the Network Operations Control Centre and AEMO, in real time, data for primary equipment operations, phasor measurements (used for state estimations) and alarms that may require immediate action. The SCADA and automation systems also provide remote engineering access to equipment such as protection relays, power quality meters and condition monitoring equipment, allowing faster post fault analysis and equipment health monitoring as required to meet NER and AEMO rules, and alleviate the need for personnel to travel to sites. |  |  |  |  | TRUE
| Problem Definition |  | TasNetworks' aging SCADA and automation devices exhibit high failure rates resulting in operational safety, reliability and maintenance issues, non-conformance to the AEMO and AER rules, and diminished network visibility and control. This in turn will trigger network constraints, increased customer outages and failure to disable circuit breaker auto reclose on high bushfire risk days, which can lead to increased risk of a bushfire start from TasNetworks assets. The aged assets are also without manufacturers support which increases the risk for cyber attacks Devices with no manufacturer support, i.e. software updates, increases TasNetworks’ cyber security risk and has the potential for a cyber-attack to take control of our network causing incorrect network operations and major impact to customer supply. |  |  |  |  | FALSE
02. Customer Needs and Impact | Customer Needs and impact |  | TasNetworks has a customer and stakeholder engagement strategy to inform the existing program of work and the upcoming revenue submission. The feedback obtained informs the approach taken by TasNetworks to align our investments with customer needs and impacts. Customer needs addressed by this investment include: - affordability; and - supply reliability and safety of the current network; Consumers have also identified safety, restoration of faults/emergencies and supply reliability as the highest performing services offered by TasNetworks. The correct operation of SCADA and automation devices are critical to enable TasNetworks to offer services that also meet these top priorities. |  |  |  |  | TRUE
03. Business Objectives | Business Objectives
04. Project Objectives | Project Objectives |  | Risk mitigation of substation SCADA and automation equipment to ensure we meet our business objectives, customers’ expectations, regulatory and compliance requirements outlined by AER and AEMO, provide real time data for more efficient network operations and minimising cyber security risk. |  |  |  |  | FALSE
05. Risk Objective | Risk if not progressed | [6 empty] | TRUE
06. Investment Timing | Investment Timing |  | This program is a continuation of an existing program due to the size of this asset portfolio. This program runs for the FY2025-29 years with the capital investment spread over a five-year period to accommodate timing of services, resources, invoicing and financial closeout. It is anticipated that investment on this asset portfolio will be required into further regulatory periods. |  |  |  |  | TRUE
07. Business Consulatation | Business Consulatation | [6 empty] | TRUE

## Option 1
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000628 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_T_SC_RENSC_SCADA RENEWAL OTHER DEVICES | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-11-03
Alternative Overview
75679 | Alternative Name |  | 25 per cent less volumes than historical volumes
autofit | Description |  | 25 per cent less volumes than historical volumes - to assess sensitivity outcome of risk/cost analysis.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | Rejected: This option will increase risks to people, potentially not meeting AER network performance and regulatory requirements. This will create a bow wave of failures and regulator issues. Also limits the alignment with strategic business objectives, such as intelligent asset management.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| 25 per cent less volumes than historical volumes |  | Capex |  |  | 990000 | 990000 | 990000 | 990000 | 990000 | 4950000 | 9900000 | -2228242.6
|  |  | Opex |  |  | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Terminal Value |  |  | 14.7134 | 0.1%
[9 empty] | UARM - Environment and Community - Fire Risk |  |  | 0 | 0%
[9 empty] | UARM - Safety & People - Worker |  |  | 0 | 0%
[9 empty] | UARM - Network Performance Risk |  |  | 0 | 0%
[9 empty] | UARM - Environment and Community - Other Risk |  |  | 0 | 0%
[9 empty] | UARM - Financial Risk |  |  | 5956.2867 | 42.08%
[9 empty] | UARM - Safety & People - Public |  |  | 0 | 0%
[9 empty] | Total Investment Cost |  |  | -8184.5293 | 57.82%
[9 empty] | Total |  |  | -2213.5292
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 990000 | 990000 | 990000 | 990000 | 990000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -8184.5293 | Dollar | 990000 | 990000 | 990000 | 990000 | 990000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 14.7134 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE | UARM - PA to Investment | UARM - Network Performance Risk |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE | UARM - PA to Investment | UARM - Network Performance Risk |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE | UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
| UARM - PA to Investment | UARM - Financial Risk |  | Baseline |  | 0 | Dollar | 15156344.94 | 15156343.79 | 15156343.09 | 15156342.59 | 15156342.24
| UARM - PA to Investment | UARM - Financial Risk |  | Outcome | 2024 | 5956.2867 | Dollar | 14746344.36 | 14746341.92 | 14746340.25 | 14746338.96 | 14746337.92
| UARM - PA to Investment | UARM - Safety & People - Public |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE | UARM - PA to Investment | UARM - Safety & People - Public |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 15156344.94 | 15156343.79 | 15156343.09 | 15156342.59 | 15156342.24
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 14746344.36 | 14746341.92 | 14746340.25 | 14746338.96 | 14746337.92
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 2
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000628 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_T_SC_RENSC_SCADA RENEWAL OTHER DEVICES | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-11-03
Alternative Overview
75679 | Alternative Name |  | 25 per cent more volumes than historical volumes
autofit | Description |  | 25 per cent more volumes than historical volumes - to assess sensitivity outcome of risk/cost analysis.
autofit | Alternative Status |  | Recommended
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | Recommended: This option will allow TasNetworks to meet AER compliance regulations and network performance requirements, as well as reduce cyber security risk. Aligns with multiple strategic objectives, intelligent asset management and provides real time data for NOCS and AEMO. This option will maintain the fleet in a condition that manages risk now and into the future.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| 25 per cent more volumes than historical volumes |  | Capex |  |  | 1650000 | 1650000 | 1650000 | 1650000 | 1650000 | 8250000 | 16500000 | -3713732.13
|  |  | Opex |  |  | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Terminal Value |  |  | 24.5224 | 0.1%
[9 empty] | UARM - Environment and Community - Fire Risk |  |  | 0 | 0%
[9 empty] | UARM - Safety & People - Worker |  |  | 0 | 0%
[9 empty] | UARM - Network Performance Risk |  |  | 0 | 0%
[9 empty] | UARM - Environment and Community - Other Risk |  |  | 0 | 0%
[9 empty] | UARM - Financial Risk |  |  | 9927.1501 | 42.08%
[9 empty] | UARM - Safety & People - Public |  |  | 0 | 0%
[9 empty] | Total Investment Cost |  |  | -13640.8822 | 57.82%
[9 empty] | Total |  |  | -3689.2097
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 1650000 | 1650000 | 1650000 | 1650000 | 1650000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -13640.8822 | Dollar | 1650000 | 1650000 | 1650000 | 1650000 | 1650000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 24.5224 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE | UARM - PA to Investment | UARM - Network Performance Risk |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE | UARM - PA to Investment | UARM - Network Performance Risk |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE | UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
| UARM - PA to Investment | UARM - Financial Risk |  | Baseline |  | 0 | Dollar | 15156344.94 | 15156343.79 | 15156343.09 | 15156342.59 | 15156342.24
| UARM - PA to Investment | UARM - Financial Risk |  | Outcome | 2024 | 9927.1501 | Dollar | 14473010.69 | 14473000.45 | 14473000.14 | 14473000.33 | 14473000.84
| UARM - PA to Investment | UARM - Safety & People - Public |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE | UARM - PA to Investment | UARM - Safety & People - Public |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 15156344.94 | 15156343.79 | 15156343.09 | 15156342.59 | 15156342.24
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 14473010.69 | 14473000.45 | 14473000.14 | 14473000.33 | 14473000.84
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 3
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000628 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_T_SC_RENSC_SCADA RENEWAL OTHER DEVICES | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-11-03
Alternative Overview
75679 | Alternative Name |  | Planned Renewal
autofit | Description |  | This option includes planned replacement based on historical volumes to mitigate aging fleet and defects/failures.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | Rejected: This will increase risks to people, potentially not meeting AER network performance and regulatory requirements compared to the recommended option. This will create a bow wave of failures (increase costs) and regulatory issues. Also limits the alignment with business strategic objectives, such as intelligent asset management.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Planned Renewal |  | Capex |  |  | 1320000 | 1320000 | 1320000 | 1320000 | 1320000 | 6600000 | 13200000 | -2970993.17
|  |  | Opex |  |  | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Terminal Value |  |  | 19.6179 | 0.1%
[9 empty] | UARM - Environment and Community - Fire Risk |  |  | 0 | 0%
[9 empty] | UARM - Safety & People - Worker |  |  | 0 | 0%
[9 empty] | UARM - Network Performance Risk |  |  | 0 | 0%
[9 empty] | UARM - Environment and Community - Other Risk |  |  | 0 | 0%
[9 empty] | UARM - Financial Risk |  |  | 7941.7126 | 42.08%
[9 empty] | UARM - Safety & People - Public |  |  | 0 | 0%
[9 empty] | Total Investment Cost |  |  | -10912.7058 | 57.82%
[9 empty] | Total |  |  | -2951.3752
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 1320000 | 1320000 | 1320000 | 1320000 | 1320000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -10912.7058 | Dollar | 1320000 | 1320000 | 1320000 | 1320000 | 1320000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 19.6179 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE | UARM - PA to Investment | UARM - Network Performance Risk |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE | UARM - PA to Investment | UARM - Network Performance Risk |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE | UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
| UARM - PA to Investment | UARM - Financial Risk |  | Baseline |  | 0 | Dollar | 15156344.94 | 15156343.79 | 15156343.09 | 15156342.59 | 15156342.24
| UARM - PA to Investment | UARM - Financial Risk |  | Outcome | 2024 | 7941.7126 | Dollar | 14609677.52 | 14609674.68 | 14609672.69 | 14609671.14 | 14609669.88
| UARM - PA to Investment | UARM - Safety & People - Public |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE | UARM - PA to Investment | UARM - Safety & People - Public |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 15156344.94 | 15156343.79 | 15156343.09 | 15156342.59 | 15156342.24
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 14609677.52 | 14609674.68 | 14609672.69 | 14609671.14 | 14609669.88
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 4 (hidden)
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000628 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_T_SC_RENSC_SCADA RENEWAL OTHER DEVICES | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-11-03
Alternative Overview
75679 | Alternative Name
autofit | Description
autofit | Alternative Status
autofit | Alternative Start Date
Reason for selection/rejection
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
0
0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Total |  |  | 0
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 0 | 0 | 0 | 0 | 0
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 5 (hidden)
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000628 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_T_SC_RENSC_SCADA RENEWAL OTHER DEVICES | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-11-03
Alternative Overview
75679 | Alternative Name
autofit | Description
autofit | Alternative Status
autofit | Alternative Start Date
Reason for selection/rejection
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
0
0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Total |  |  | 0
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 0 | 0 | 0 | 0 | 0
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 6 (hidden)
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000628 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_T_SC_RENSC_SCADA RENEWAL OTHER DEVICES | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-11-03
Alternative Overview
75679 | Alternative Name
autofit | Description
autofit | Alternative Status
autofit | Alternative Start Date
Reason for selection/rejection
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
0
0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Total |  |  | 0
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 0 | 0 | 0 | 0 | 0
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## TextFormatting (hidden)
Index | 8
Column Width | 238
Font | Calibri
Font Size | 11
Font Colour
Text | Sheet | Group | Field | Row Height | Row Number
This program includes the renewal of SCADA and automations equipment that is required to monitor the state and health of primary and secondary assets associated with the transmission network which includes: Power Quality Meters (PQM); Phasor Measurement Unit (PMU); Phasor Data Concentrator (PDC); Automatic Voltage Regulators (AVR); Bay Controllers (BC); and Global Positioning System (GPS) clocks. | Investment Summary | Header | Description | 120 | 9
TasNetworks owns and operates 110 kV and 220 kV transmission network and associated substation assets and are compelled to meet Australian Energy Regulator (AER) National Electricity Rules (NER) and Australian Energy Market Operator (AEMO) standards, specifically for SCADA and automation systems, which include: - AEMO data and communications standard; - AEMO power system security guidelines (Chapters 13, 14 and 16); - NER sections 4.11.1 Remote control and monitoring devices; - NER sections 4.11.2 Operational control and indication communication facilities; and - NER rule clause 4 .11.1(d) provision of remote monitoring equipment. SCADA and automations systems are required to monitor the state and health of primary and secondary assets associated with the transmission network and include the following equipment: - Power Quality Meters (PQM); - Phasor Measurement Unit (PMU); - Phasor Data Concentrator (PDC); - Automatic Voltage Regulators (AVRs); - Networks Switches; - Bay Controllers(BCs); and - Global Positioning System (GPS) clocks. The SCADA and automation systems provide control of primary plant such as circuit breakers, disconnectors, tap changers for voltage regulation and control for system contingency schemes such as under/over frequency, network overload, generator run-back, and anti-islanding schemes. Local operators once had to manually operate a disconnector directly beneath the primary plant, but this can now be done through the SCADA system from within the substation control room. The SCADA and automation systems provide the Network Operations Control Centre and AEMO, in real time, data for primary equipment operations, phasor measurements (used for state estimations) and alarms that may require immediate action. The SCADA and automation systems also provide remote engineering access to equipment such as protection relays, power quality meters and condition monitoring equipment, allowing faster post fault analysis and equipment health monitoring as required to meet NER and AEMO rules, and alleviate the need for personnel to travel to sites. | Investment Summary | 0.1 Overview | Background | 409.5 | 16
TasNetworks' aging SCADA and automation devices exhibit high failure rates resulting in operational safety, reliability and maintenance issues, non-conformance to the AEMO and AER rules, and diminished network visibility and control. This in turn will trigger network constraints, increased customer outages and failure to disable circuit breaker auto reclose on high bushfire risk days, which can lead to increased risk of a bushfire start from TasNetworks assets. The aged assets are also without manufacturers support which increases the risk for cyber attacks Devices with no manufacturer support, i.e. software updates, increases TasNetworks’ cyber security risk and has the potential for a cyber-attack to take control of our network causing incorrect network operations and major impact to customer supply. | Investment Summary | 0.1 Overview | Problem Definition | 105 | 17
TasNetworks has a customer and stakeholder engagement strategy to inform the existing program of work and the upcoming revenue submission. The feedback obtained informs the approach taken by TasNetworks to align our investments with customer needs and impacts. Customer needs addressed by this investment include: - affordability; and - supply reliability and safety of the current network; Consumers have also identified safety, restoration of faults/emergencies and supply reliability as the highest performing services offered by TasNetworks. The correct operation of SCADA and automation devices are critical to enable TasNetworks to offer services that also meet these top priorities. | Investment Summary | 02. Customer Needs and Impact | Customer Needs and impact | 165 | 18
Failed devices leads to putting operational personal in the vicinity of primary equipment during operation. Failure to maintain our devices will require increased driving to site, operator fatigue and CO2 emissions. | Objectives and Analysis | 03. Business Performance Objectives | Safety and Wellbeing | 30 | 17
Failed devices can affect major industrials, as network constraints may be imposed, reducing quality of supply and reliability with the result of poor customer experience. Failed devices require driving to site increasing carbon footprint. | Objectives and Analysis | 03. Business Performance Objectives | Our Customers | 45 | 18
| Objectives and Analysis | 03. Business Performance Objectives | Our People | 15 | 19
Failure to maintain devices can lead to failure to meet AEMO operating standards and procedures, which in turn can lead to penalties (TasNetworks may incur fines for compliance breaches to NER 4.11.2) or network constraints. Failure to maintain devices will also increase cost of having to man substations, longer outages due to repairs of unsupported devices and increases cyber security risk by having old unsupported equipment. | Objectives and Analysis | 03. Business Performance Objectives | Our Business - Sustained Cost Management | 75 | 20
| Objectives and Analysis | 03. Business Performance Objectives | Our Business - Network Service | 15 | 21
If the identified SCADA device (such as a bay controller) fails, this will require transmission lines and other equipment to be monitored and operated onsite, placing operators in close proximity to the EHV equipment. This will increase the risk of a safety incident if there is a failure of the primary equipment or an operational error. | Objectives and Analysis | 04. Business Risks | Death or Injury (Employee) | 45 | 23
| Objectives and Analysis | 04. Business Risks | Death or Injury (Public) | 15 | 24
Once dedicated spares have fully depleted and manufacturer support has ceased, the rectification of a failed device becomes an unplanned refurbishment by installing a different model of device in place of the failed device. For this equipment, this requires replacement of the device and all associated wiring, which involves redesign and re-commissioning of the scheme under fault response conditions. These unplanned costs are not included in normal operational or capital budgets and can have an effect on the delivery of the planned program of work. | Objectives and Analysis | 04. Business Risks | Sustainable and Predictable Pricing | 75 | 25
Incorrectly installed or failed SCADA devices could cause incorrect operation of special protection and control schemes leading to a significant loss of supply event. | Objectives and Analysis | 04. Business Risks | Widespread Power Disruption | 30 | 26
Failed SCADA devices can lead to in-operability of circuit breakers ( i.e.: unable to remotely disable auto reclosers) when required on high bushfire days. | Objectives and Analysis | 04. Business Risks | Bushfire Start | 30 | 27
Failed devices can affect major industrial customers, as network constraints may be imposed, reducing quality of supply and reliability with result in poor customer experience. | Objectives and Analysis | 04. Business Risks | Loss of Major Industrial | 30 | 28
Material supply interruption and contribution towards: - substandard performance(STIPs); - unavailability of network services; - negative impact on community values and expectations; - increased customer complaints; - reputation damage; and - climate change. | Objectives and Analysis | 04. Business Risks | Customer Focus | 105 | 29
| Objectives and Analysis | 04. Business Risks | Business Continuity Management | 15 | 30
Obsolete equipment increases the potential for cyber-attacks on the operational network, which can cause incorrect operations of primary equipment and lengthy outages to customers. | Objectives and Analysis | 04. Business Risks | Cyber Security | 30 | 31
| Objectives and Analysis | 04. Business Risks | Private Assets | 15 | 32
Failure to meet Department of Home Affair’s legislation (i.e. cyber security), AER and AEMO regulations. such as NER rule 6A.6.7 (3)(1) “the quality, reliability or security of supply of prescribed transmission services”. | Objectives and Analysis | 04. Business Risks | Energy Policy and Regulation | 30 | 33
| Objectives and Analysis | 04. Business Risks | Project Marinus (D&A) | 15 | 34
Failed devices (bay controllers, power quality meters, phasor measurement units, etc.) can cause network operations and AEMO to lose visibility of certain parts of the network leading to increase in low inertia system strength conditions leading to imposed network constraints. | Objectives and Analysis | 04. Business Risks | Tasmanian Power System Complexity | 45 | 35
| Objectives and Analysis | 04. Business Risks | Emerging Complexity of the NEM | 15 | 36
TasNetworks 21-22 business plan, Safety- Reduce Loss time injuries: Newer devices will reduce the operational safety risk. Transmission network strategy: Utilising these systems will provide real time data of assets assisting in the power systems team to model the network. | Objectives and Analysis | 05. Strategic Objectives | Strategic Objectives | 75 | 38
TasNetworks Three year business plan Clean energy future: New devices will lead to less driving to sites for operational issues assisting in a clean energy future Intelligent asset management: Utilising new devices for these systems provides real time data for asset management and operational control and improving TasNetworks’ ability to make data driven decisions. Improving our protection and security of assets and data: Bringing these systems up to latest technology will assist in the protection of these assets from cyber-attacks and / or data breaches. | Objectives and Analysis | 05. Strategic Objectives | Strategic Document #1 | 120 | 39
NER NER section 4 .11.1(d) power system security support: Provides AER power system security requirements such as High Speed system Monitoring (HSM) and psymetrix (i.e. early warning of degraded power system damping). NER rule 6A.6.7 (3)(1) “the quality, reliability or security of supply of prescribed transmission services”. | Objectives and Analysis | 05. Strategic Objectives | Strategic Document #2 | 60 | 40
TasNetworks towards 2030 Efficiency: Artificial intelligence used to optimise grid performance, reduce safety risks, optimising alternative solutions. | Objectives and Analysis | 05. Strategic Objectives | Strategic Document #3 | 30 | 41
SCADA and Automation Asset Management Plan | Objectives and Analysis | 05. Strategic Objectives | Strategic Document #4 | 15 | 42
| Objectives and Analysis | 05. Strategic Objectives | Strategic Document #5 | 15 | 43
Risk mitigation of substation SCADA and automation equipment to ensure we meet our business objectives, customers’ expectations, regulatory and compliance requirements outlined by AER and AEMO, provide real time data for more efficient network operations and minimising cyber security risk. | Objectives and Analysis | 06. Project Objectives | Project Objectives | 45 | 44
TasNetworks participates in regulatory information notice (RIN) reporting annually. Which benchmarks TasNetworks transmission expenditure against other transmission service providers (TasNetworks) to provide a score on efficiency. TasNetworks reports on: - number of assets in service; - capital expenditure and asset replacements; - operational expenditure and asset failures; and - number of inspected / maintained assets. Additionally, other options were considered during the development of this IES that did not proceed to economic analysis. They included: Install New Technology Description - Install alternative new technology not currently used by TasNetworks. Reason for Rejection - Not assessed due to no existing TasNetworks standard on how to install, test and commission. High level economic assessment indicated much higher cost due to non-standard replacement rather than like-for-like. | Objectives and Analysis | 07. Options Analysis | Benchmarking | 225 | 45
TasNetworks have formally conducted asset category forums involving experts in the strategy, engineering, and field maintenance areas to discuss issues with the protection equipment and to trigger initiatives to rectify the identified issues. These forums, known as the Management Operating System (MOS), in particular the ‘J’ meetings are held monthly to regularly capture information relating to the protection asset category. | Objectives and Analysis | 07. Options Analysis | Expert Findings | 60 | 46
This program is a continuation of an existing program due to the size of this asset portfolio. This program runs for the FY2025-29 years with the capital investment spread over a five-year period to accommodate timing of services, resources, invoicing and financial closeout. It is anticipated that investment on this asset portfolio will be required into further regulatory periods. | Objectives and Analysis | 08. Investment Timing | Investment Timing | 60 | 47
The benefits to TasNetworks from implementation of the preferred option should be: - alignment with TasNetworks business objectives such as zero harm; - alignment with customer expectations such as reducing carbon footprint by less driving; - faster restoration of supply to our customers; - limit AEMO infringement notices for non-compliance to the data and communications standard, NER sections 4.11.1 and 4.11.2, minimising cyber security risks by providing added security features and minimise last minutes security patches; and - Maintaining a reliable SCADA system to provide real time data of assets. Improved network asset management and monitoring to provide data driven decisions and intelligent asset management. | Objectives and Analysis | 09. Expected Outcomes and Benefits | Expected Outcomes and Benefits | 120 | 48
This is a compliance program for TasNetworks to meet AER and AEMO obligations such as, - AEMO data and communications standard. - AEMO power system security guidelines (Chapters 13, 14 and 16). - NER sections 4.11.1 Remote control and monitoring devices. - NER sections 4.11.2 Operational control and indication communication facilities; and - NER rule clause 4 .11.1(d) provision of remote monitoring equipment. - It is assumed that the data and the TQR inputs are correct (data in TQR was has only quantified asset failure data as the other data for other risks is not quantified), and the failure curves associated with this asset are correct to allow copperleaf to perform its correct calculations. - Advice from an external consult was that this is a compliance based program, hence no other risks have been quantified other than financial based from rectification of asset failures. | Objectives and Analysis | 10. Assumptions | Assumptions | 165 | 49
This initiative relates to a program of work for asset renewal where individual assets are replaced when they fail a serviceability test and therefore a RIT-T is not required. | Objectives and Analysis | 11. Regulatory Considerations | Regulatory Investment Test | 30 | 50
Yes | Objectives and Analysis | 11. Regulatory Considerations | Meet or manage the expected demand for Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 51
Yes | Objectives and Analysis | 11. Regulatory Considerations | Comply with all applicable regulatory obligations associated with the provision of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 52
Yes | Objectives and Analysis | 11. Regulatory Considerations | Maintain the quality, reliability and security of supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 53
Yes | Objectives and Analysis | 11. Regulatory Considerations | Maintain the reliability and security of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 54
Yes | Objectives and Analysis | 11. Regulatory Considerations | Maintain the safety of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 55
The recommended option includes the renewal of SCADA and automations equipment that is required to monitor the state and health of primary and secondary assets associated with the transmission network which includes: Power Quality Meters; Phasor Measurement Units; Phasor Data Concentrators; Automatic Voltage Regulators; Bay Controllers; and Global Positioning System clocks. This option will assist TasNetworks to meet AER compliance regulations and network performance requirements and reduce cyber security risk. The program selected aligns with multiple business strategic objectives, intelligent asset management, and provides real time data for NOCS and AEMO. This option will maintain the fleet in a condition that manages risk now and into the future. | Objectives and Analysis | 12. Recommendation | Recommendation | 210 | 56
25 per cent less volumes than historical volumes - to assess sensitivity outcome of risk/cost analysis. | Option 1 | Description |  | 15
Rejected: This option will increase risks to people, potentially not meeting AER network performance and regulatory requirements. This will create a bow wave of failures and regulator issues. Also limits the alignment with strategic business objectives, such as intelligent asset management. | Option 1 | Reason for selection/rejection |  | 15
25 per cent more volumes than historical volumes - to assess sensitivity outcome of risk/cost analysis. | Option 2 | Description |  | 15
Recommended: This option will allow TasNetworks to meet AER compliance regulations and network performance requirements, as well as reduce cyber security risk. Aligns with multiple strategic objectives, intelligent asset management and provides real time data for NOCS and AEMO. This option will maintain the fleet in a condition that manages risk now and into the future. | Option 2 | Reason for selection/rejection |  | 30
This option includes planned replacement based on historical volumes to mitigate aging fleet and defects/failures. | Option 3 | Description |  | 15
Rejected: This will increase risks to people, potentially not meeting AER network performance and regulatory requirements compared to the recommended option. This will create a bow wave of failures (increase costs) and regulatory issues. Also limits the alignment with business strategic objectives, such as intelligent asset management. | Option 3 | Reason for selection/rejection |  | 30
| Option 4 | Description
| Option 4 | Reason for selection/rejection
| Option 5 | Description
| Option 5 | Reason for selection/rejection
| Option 6 | Description
| Option 6 | Reason for selection/rejection