## Run Extract (hidden)
[12 empty] | 1 | 2 | 3 | 4 | 5 | 6
[12 empty] | Option 1 | Option 2 | Option 3 | Option 4 | Option 5 | Option 6
[10 empty] | Address | Value Metric | Option 1: Kiosk substation replacement at 50 years | Option 2: Kiosk substation replacement at 52 years | Option 3: Kiosk substation replacement at 55 years | Option 4: Financially constrained at $2.85 m p.a.
[11 empty] | UARM - Environment and Community - Fire Risk | 0 | 0 | 0 | 0
[11 empty] | UARM - Safety & People - Worker | 4508340.5675 | 4215155.2995 | 3665923.494 | 3001881.0726
Notes | [10 empty] | UARM - Network Performance Risk | 33472645.2788 | 31295860.6194 | 27218031.7436 | 22287779.5253
Need to open the .xlsm Investment Summary report from Copperleaf in the Trusted folder Save in the preferred location as an .xlsx Need to test environment - other and when two of the same value models have been selected with a different name | [10 empty] | UARM - Environment and Community - Other Risk | 5610183.514 | 5245343.4615 | 4561878.8575 | 3735543.7975
[11 empty] | UARM - Financial Risk | 57986392.8502 | 54215436.2532 | 47151202.6629 | 38610272.0014
[11 empty] | UARM - Safety & People - Public | 1782668.4166 | 1666738.3944 | 1449563.513 | 1186990.7678
[11 empty] | Terminal Value | 24305573.5143 | 22362719.2246 | 21928454.2824 | 19073429.6904
[11 empty] | Total Investment Cost | 71273425.4105 | 66072954.086 | 60676963.6821 | 51585917.4903
Options
| Option | 2025 | 2026 | 2027 | 2028 | 2029
| Baseline | 30679855.67 | 22084582.49 | 17860416.89 | 15381297.57 | 13718868
| Option 1: Kiosk substation replacement at 50 years | 21884914.83 | 14007081.17 | 10077036.1 | 7695204.49 | 5846177
| Option 2: Kiosk substation replacement at 52 years | 22576050.59 | 14626148.16 | 10651561.65 | 8290674.14 | 6479960.87
| Option 3: Kiosk substation replacement at 55 years | 24078418.31 | 15886260.45 | 11908141.95 | 9529623.14 | 7784279.2
| Option 4: Financially constrained at $2.85 m p.a. | 25709088.51 | 17309751.65 | 13359483.59 | 10889847.22 | 9219195.89
Option Breakdown | [7 empty] | Folder and File Paths
| Option 4 |  |  |  |  | Greater 0 | (Multiple Items)
| Recommended Option - Value | [6 empty] | This File Path | \\TNAD.tasnetworks.com.au\user$\user_folders\BahramabadiM\My Documents\Trusted\InvestmentTemplate.xlsm
| Value Function Measure | Value | Value in % | Greater 0 |  | Row Labels | Sum of Value in % | Folder Path | H:\RPSAM\SAM\R24 IES\final draft\
Option 4 | UARM - Environment and Community - Fire Risk | 0 | 0% | 1 | K20 | Terminal Value | 13.67% | File Name | InvestmentSummary_R24_D_SB_REGMS_GMS_Replacement of GMS.xlsx
Option 4 | UARM - Safety & People - Worker | 3001.8811 | 2.15% | 1 | K21 | Total Investment Cost | 36.98% | File Path | H:\RPSAM\SAM\R24 IES\final draft\InvestmentSummary_R24_D_SB_REGMS_GMS_Replacement of GMS.xlsx
Option 4 | UARM - Network Performance Risk | 22287.7795 | 15.98% | 1 | K22 | UARM - Environment and Community - Fire Risk | 0%
Option 4 | UARM - Environment and Community - Other Risk | 3735.5438 | 2.68% | 1 | K23 | UARM - Environment and Community - Other Risk | 2.68%
Option 4 | UARM - Financial Risk | 38610.272 | 27.68% | 1 | K24 | UARM - Financial Risk | 27.68%
Option 4 | UARM - Safety & People - Public | 1186.9908 | 0.85% | 1 | K25 | UARM - Network Performance Risk | 15.98%
Option 4 | Terminal Value | 19073.4297 | 13.67% | 1 | K26 | UARM - Safety & People - Public | 0.85%
Option 4 | Total Investment Cost | -51585.9175 | 36.98% | 1 | K27 | UARM - Safety & People - Worker | 2.15%
Option 4 |  |  |  | 0 | K28
Option 4 |  |  |  | 0 | K29
Option 4 |  |  |  | 0 | K30 |  |  | 1 | InvestmentSummary_R24_D_ND_PRHVR_Augment_HV_Fdr_TRIP.xlsx
Option 4 |  |  |  | 0 | K31 |  |  | 2 | InvestmentSummary_R24_D_OH_REPOL_Basic Fleet Pole Replacement.xlsx
Option 4 |  |  |  | 0 | K32 |  |  | 3 | InvestmentSummary_R24_T_ND_AUGSB_W Coast Reliability Improvement.xlsx
Option 4 |  |  |  | 0 | K33 |  |  | 4 | InvestmentSummary_R24_T_ND_AUGSB_Upper Derwent 110 kV Losses.xlsx
| Total | 36309.9794 | 99.99% |  |  |  |  | 5 | InvestmentSummary_R24_D_OH_SIWES_Bird_Mitigation.xlsx
[8 empty] | 6 | InvestmentSummary_R24_D_SB_REGMS_GMS_Replacement of GMS.xlsx
[8 empty] | 7 | InvestmentSummary_R24_D_OH_REPOL_Complex Design.xlsx
Start | Option 1 |  |  |  |  | Greater 0 | 1 | 8 | InvestmentSummary_R24_D_PQ_PQTXV_Power_Quality_LV_Tformers.xlsx
| Value Function Measure | Value | Value in % | Greater 0 |  |  |  | 9 | InvestmentSummary_R24_D_ND_PQLVV_Aug_HV_LV_Conductor.xlsx
Option 1 | UARM - Environment and Community - Fire Risk | 0 | 0% | 1 | K20 | Row Labels | Sum of Value in % | 10 | InvestmentSummary_R24_D_CA_SOLCP_Crossover_Extension_OH.xlsx
Option 1 | UARM - Safety & People - Worker | 4508.3406 | 2.27% | 1 | K21 | Terminal Value | 12.22% | 11 | InvestmentSummary_R24_D_CI_SOIRR_Irrigation_Supply.xlsx
Option 1 | UARM - Network Performance Risk | 33472.6453 | 16.83% | 1 | K22 | Total Investment Cost | 35.83% | 12 | InvestmentSummary_R24_D_AMIPD_AM Improvement Program.xlsx
Option 1 | UARM - Environment and Community - Other Risk | 5610.1835 | 2.82% | 1 | K23 | UARM - Environment and Community - Fire Risk | 0% | 13 | InvestmentSummary_R24_D_CI_SOPOR_Permanent_Residence_OH.xlsx
Option 1 | UARM - Financial Risk | 57986.3929 | 29.15% | 1 | K24 | UARM - Environment and Community - Other Risk | 2.82% | 14 | InvestmentSummary_R24_D_CI_SUPOR_Permanent_Residence_UG.xlsx
Option 1 | UARM - Safety & People - Public | 1782.6684 | 0.9% | 1 | K25 | UARM - Financial Risk | 29.15% | 15 | InvestmentSummary_R24_D_CI_SOGSI_General_Supply_OH.xlsx
Option 1 | Terminal Value | 24305.5735 | 12.22% | 1 | K26 | UARM - Network Performance Risk | 16.83% | 16 | InvestmentSummary_R24_D_CI_SUGSI_General_Supply_UG.xlsx
Option 1 | Total Investment Cost | -71273.4254 | 35.83% | 1 | K27 | UARM - Safety & People - Public | 0.9% | 17 | InvestmentSummary_R24_D_CI_SUSBD_Subdivision_UG.xlsx
Option 1 |  |  |  | 0 | K28 | UARM - Safety & People - Worker | 2.27% | 18 | InvestmentSummary_R24_D_CI_SOSDI_Subdivision_OH.xlsx
Option 1 |  |  |  | 0 | K29 |  |  | 19 | InvestmentSummary_R24_D_CI_SUSUB_Augment_Dist_Substations.xlsx
Option 1 |  |  |  | 0 | K30 |  |  | 20 | InvestmentSummary_R24_T_ND_LAEMP_SELA.xlsx
Option 1 |  |  |  | 0 | K31 |  |  | 21 | InvestmentSummary_R24_D_CA_DESDB_Prelim_Drive_by_Design.xlsx
Option 1 |  |  |  | 0 | K32 |  |  | 22 | InvestmentSummary_R24_D_CI_SUMPR_Major_Commercial.xlsx
Option 1 |  |  |  | 0 | K33 |  |  | 23 | InvestmentSummary_R24_D_CI_EASEN_Easements_Non_Major_Comm.xlsx
| Total | 56392.3787 | 100% |  |  |  |  | 24 | InvestmentSummary_R24_D_ND_PRHVR_Rosebery_Supply_Improve.xlsx
[8 empty] | 25 | InvestmentSummary_R24_D_ND_CAHVF_Huonville_Supply_Improvement.xlsx
[8 empty] | 26 | InvestmentSummary_R24_D_ND_CAHVF_Aug_Fdr_Network_Access.xlsx
[8 empty] | 27 | InvestmentSummary_R24_D_ND_PRHVR_Deloraine_Supply_Improve.xlsx
| Option 2 |  |  |  |  | Greater 0 | 1 | 28 | InvestmentSummary_R24_D_ND_CALVF_Augment_LV_Fdr_Capacity.xlsx
| Value Function Measure | Value | Value in % | Greater 0 |  |  |  | 29 | InvestmentSummary_R24_D_ND_CAHVF_Augment_HV_Fdr_Trunk.xlsx
Option 2 | UARM - Environment and Community - Fire Risk | 0 | 0% | 1 | K20 | Row Labels | Sum of Value in % | 30 | InvestmentSummary_R24_D_ND_CAHVF_Aug_Pole_Mtd_Regulator.xlsx
Option 2 | UARM - Safety & People - Worker | 4215.1553 | 2.28% | 1 | K21 | Terminal Value | 12.08% | 31 | InvestmentSummary_R24_D_ND_CAHVF_Aug_Grnd_Mtd_Regulator.xlsx
Option 2 | UARM - Network Performance Risk | 31295.8606 | 16.91% | 1 | K22 | Total Investment Cost | 35.7% | 32 | InvestmentSummary_R24_D_ND_CAHVF_22kV_Emu_Bay_Feeders.xlsx
Option 2 | UARM - Environment and Community - Other Risk | 5245.3435 | 2.83% | 1 | K23 | UARM - Environment and Community - Fire Risk | 0% | 33 | InvestmentSummary_R24_D_ND_CAHVF_Augment_HV_Fdr_Capacity.xlsx
Option 2 | UARM - Financial Risk | 54215.4363 | 29.29% | 1 | K24 | UARM - Environment and Community - Other Risk | 2.83% | 34 | InvestmentSummary_R24_D_ND_CAHVF_Aug_SubStd_Cond_Capacity.xlsx
Option 2 | UARM - Safety & People - Public | 1666.7384 | 0.9% | 1 | K25 | UARM - Financial Risk | 29.29% | 35 | InvestmentSummary_R24_D_ND_LANDZ_LandAcq_ZoneSubs.xlsx
Option 2 | Terminal Value | 22362.7192 | 12.08% | 1 | K26 | UARM - Network Performance Risk | 16.91% | 36 | InvestmentSummary_R24_D_ND_CATXU_Aug_Dist_Sub.xlsx
Option 2 | Total Investment Cost | -66072.9541 | 35.7% | 1 | K27 | UARM - Safety & People - Public | 0.9% | 37
Option 2 |  |  |  | 0 | K28 | UARM - Safety & People - Worker | 2.28% | 38
Option 2 |  |  |  | 0 | K29 |  |  | 39
Option 2 |  |  |  | 0 | K30 |  |  | 40
Option 2 |  |  |  | 0 | K31 |  |  | 41
Option 2 |  |  |  | 0 | K32 |  |  | 42
Option 2 |  |  |  | 0 | K33 |  |  | 43
| Total | 52928.2992 | 99.99%
| Option 3 |  |  |  |  | Greater 0 | 1
| Value Function Measure | Value | Value in % | Greater 0
Option 3 | UARM - Environment and Community - Fire Risk | 0 | 0% | 1 | K20 | Row Labels | Sum of Value in %
Option 3 | UARM - Safety & People - Worker | 3665.9235 | 2.2% | 1 | K21 | Terminal Value | 13.16%
Option 3 | UARM - Network Performance Risk | 27218.0317 | 16.33% | 1 | K22 | Total Investment Cost | 36.41%
Option 3 | UARM - Environment and Community - Other Risk | 4561.8789 | 2.74% | 1 | K23 | UARM - Environment and Community - Fire Risk | 0%
Option 3 | UARM - Financial Risk | 47151.2027 | 28.29% | 1 | K24 | UARM - Environment and Community - Other Risk | 2.74%
Option 3 | UARM - Safety & People - Public | 1449.5635 | 0.87% | 1 | K25 | UARM - Financial Risk | 28.29%
Option 3 | Terminal Value | 21928.4543 | 13.16% | 1 | K26 | UARM - Network Performance Risk | 16.33%
Option 3 | Total Investment Cost | -60676.9637 | 36.41% | 1 | K27 | UARM - Safety & People - Public | 0.87%
Option 3 |  |  |  | 0 | K28 | UARM - Safety & People - Worker | 2.2%
Option 3 |  |  |  | 0 | K29
Option 3 |  |  |  | 0 | K30
Option 3 |  |  |  | 0 | K31
Option 3 |  |  |  | 0 | K32
Option 3 |  |  |  | 0 | K33
| Total | 45298.0909 | 100%
| Option 4 |  |  |  |  | Greater 0 | 1
| Value Function Measure | Value | Value in % | Greater 0
Option 4 | UARM - Environment and Community - Fire Risk | 0 | 0% | 1 | K20 | Row Labels | Sum of Value in %
Option 4 | UARM - Safety & People - Worker | 3001.8811 | 2.15% | 1 | K21 | Terminal Value | 13.67%
Option 4 | UARM - Network Performance Risk | 22287.7795 | 15.98% | 1 | K22 | Total Investment Cost | 36.98%
Option 4 | UARM - Environment and Community - Other Risk | 3735.5438 | 2.68% | 1 | K23 | UARM - Environment and Community - Fire Risk | 0%
Option 4 | UARM - Financial Risk | 38610.272 | 27.68% | 1 | K24 | UARM - Environment and Community - Other Risk | 2.68%
Option 4 | UARM - Safety & People - Public | 1186.9908 | 0.85% | 1 | K25 | UARM - Financial Risk | 27.68%
Option 4 | Terminal Value | 19073.4297 | 13.67% | 1 | K26 | UARM - Network Performance Risk | 15.98%
Option 4 | Total Investment Cost | -51585.9175 | 36.98% | 1 | K27 | UARM - Safety & People - Public | 0.85%
Option 4 |  |  |  | 0 | K28 | UARM - Safety & People - Worker | 2.15%
Option 4 |  |  |  | 0 | K29
Option 4 |  |  |  | 0 | K30
Option 4 |  |  |  | 0 | K31
Option 4 |  |  |  | 0 | K32
Option 4 |  |  |  | 0 | K33
| Total | 36309.9794 | 99.99%
| Option 5 |  |  |  |  | Greater 0 | 0
| Value Function Measure | Value | Value in % | Greater 0
Option 5 |  |  |  | 0 | K20 | Row Labels | Sum of Value in %
Option 5 |  |  |  | 0 | K21 |  | 0%
Option 5 |  |  |  | 0 | K22
Option 5 |  |  |  | 0 | K23
Option 5 |  |  |  | 0 | K24
Option 5 |  |  |  | 0 | K25
Option 5 |  |  |  | 0 | K26
Option 5 |  |  |  | 0 | K27
Option 5 |  |  |  | 0 | K28
Option 5 |  |  |  | 0 | K29
Option 5 |  |  |  | 0 | K30
Option 5 |  |  |  | 0 | K31
Option 5 |  |  |  | 0 | K32
Option 5 |  |  |  | 0 | K33
| Total | 0 | 0%
| Option 6 |  |  |  |  | Greater 0 | 0
| Value Function Measure | Value | Value in % | Greater 0
Option 6 |  |  |  | 0 | K20 | Row Labels | Sum of Value in %
Option 6 |  |  |  | 0 | K21 |  | 0%
Option 6 |  |  |  | 0 | K22
Option 6 |  |  |  | 0 | K23
Option 6 |  |  |  | 0 | K24
Option 6 |  |  |  | 0 | K25
Option 6 |  |  |  | 0 | K26
Option 6 |  |  |  | 0 | K27
Option 6 |  |  |  | 0 | K28
Option 6 |  |  |  | 0 | K29
Option 6 |  |  |  | 0 | K30
Option 6 |  |  |  | 0 | K31
Option 6 |  |  |  | 0 | K32
Option 6 |  |  |  | 0 | K33
| Total | 0 | 0%

## Summary
Investment Evaluation Summary |  |  |  | Investment Code |  | Report Start Year |  | NPV Period | Base Fiscal Year | Currency Scale
|  |  |  | PRJ000609 |  | 2025 |  | 25 | FY23 | Literal
|  |  |  | Investment Name | [5 empty] | Scenario
|  |  |  | R24_D_SB_REGMS_GMS_Replacement of GMS | [5 empty] | Approved
Value Function |  | TasNetworks Value Function |  | Version |  | 0.1 |  | Date |  | 2022-10-28
Investment Description
Description |  | Replacement of kiosk and fence type substations on the distribution network. | [9 empty] | TRUE
Functional Area |  | REGMS |  |  | Department |  |  | Asset Strategy
Works Initiator |  |  |  |  | Portfolio |  |  | Dx - Renewal
Investment Category |  | Standard Control - Reliability & Quality Maintained |  |  | Needs Item Reference
Investment Type |  | Network Project |  |  | Document No.
Investment Stage |  | Gate 2 – Investment Evaluation Summary |  |  | Project Zone Location
PPM ID |  |  |  |  | Regulatory Test Required |  |  | No
Investment Summary
Problem Definition |  | HV GMSs have several technical and legacy design issues that require replacement to ensure ongoing risk mitigation. Issues include: - HV switchgear using oil as an insulating medium; - LV switchboards with exposed live fronts; - Degradation of epoxy enclosures; - Oil containment deficiencies; In some cases, operating restrictions have been imposed due to operational safety issues associated with HV switchgear and LV switchboards. Both asset failures and inoperability issues can result in a loss of customer supply and have a negative impact on network performance. As a result of the risk presented by this equipment a management plan has been deemed necessary to mitigate these risks | [9 empty] | TRUE
Recommendation |  | It is recommended that Option 4 is approved as the preferred investment option. This option was selected as an outcome of a business optimisation process being applied across all network investments. A financial constraint was applied to this program. | [9 empty] | TRUE
Alternative Spend Profile
Name |  | Status | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV | Alternative Start Date
Option 1: Kiosk substation replacement at 50 years |  | Candidate | 6374116 | 6374116 | 6374116 | 6374116 | 6374116 | 31870580 | 92929470 | 56392378.73 | 4547400%
Option 2: Kiosk substation replacement at 52 years |  | Candidate | 5830656 | 5830656 | 5830656 | 5830656 | 5830656 | 29153280 | 86438710 | 52928299.17 | 4547400%
Option 3: Kiosk substation replacement at 55 years |  | Candidate | 4727812 | 4727812 | 4727812 | 4727812 | 4727812 | 23639060 | 81834680 | 45298090.87 | 4547400%
Option 4: Financially constrained at $2.85 m p.a. |  | Recommended | 3524116 | 3524116 | 3524116 | 3524116 | 3524116 | 17620580 | 71079470 | 36309979.36 | 4547400%
0
0
Leader Endorsement
Name |  |  | Governance |  | Signature |  |  | Comments |  |  | Date
|  |  | Submission | [7 empty] | 4486200%
|  |  | Endorsement | [7 empty] | 4486200%
|  |  | Approval | [7 empty] | 4486200%
Investment Attachments
Date | Attachment Name |  | Description

## Investment Overview
Investment Evaluation Summary |  | Copperleaf Investment Code |  | Report Start Year | NPV Period | Base Fiscal Year | Currency Scale
|  | PRJ000609 |  | 2025 | 25 | FY23 | Literal
|  | Investment Name |  |  |  |  | Scenario
|  | R24_D_SB_REGMS_GMS_Replacement of GMS |  |  |  |  | Approved
Value Function | TasNetworks Value Function | Version |  | 0.1 | Date |  | 2022-10-28
Functional Area | REGMS |  | Department |  | Asset Strategy
Works Initiator |  |  | Portfolio |  | Dx - Renewal
Investment Category | Standard Control - Reliability & Quality Maintained |  | Needs Item Reference
Investment Type | Network Project |  | Document No.
Investment Stage | Gate 2 – Investment Evaluation Summary |  | Project Zone Location
PPM ID |  |  | Regulatory Test Required |  | No
Investment Overview
01. Overview | Background |  | TasNetworks owns and maintains approximately 2080 high voltage (HV) ground mounted distribution substations (GMS) on the distribution network. These substations comprise the following construction types: - Fence type (85); - Steel, fibreglass and block wall kiosks (1647); and - Building type, isolated and integrated (348). The HV GMS are supplied at both 11 kV and 22 kV and range in size from 300 kVA to 4500 kVA. Within these substations there is a variety of configurations and equipment, with approximately twenty different makes and models of HV switchgear. HV GMSs are actively managed and receive routine inspections and maintenance to maximise their service life. Many of the older substations were installed in the early 1960s and are at or near the end of their service life. Even with routine maintenance TasNetworks’ steel, fibreglass and block wall kiosk substations deteriorate over time resulting in a finite operational life for these assets. As the assets age, the probability of an in service failure occurring increases. TasNetworks' experience has been that the failure rate of the assets typically increases after 45 to 50 years of service. Currently there are approximately ten asset failures per annum (including HV switchgear, transformers, low voltage (LV) switchboards and failure of the substation enclosures). |  |  |  |  | TRUE
| Problem Definition |  | HV GMSs have several technical and legacy design issues that require replacement to ensure ongoing risk mitigation. Issues include: - HV switchgear using oil as an insulating medium; - LV switchboards with exposed live fronts; - Degradation of epoxy enclosures; - Oil containment deficiencies; In some cases, operating restrictions have been imposed due to operational safety issues associated with HV switchgear and LV switchboards. Both asset failures and inoperability issues can result in a loss of customer supply and have a negative impact on network performance. As a result of the risk presented by this equipment a management plan has been deemed necessary to mitigate these risks |  |  |  |  | FALSE
02. Customer Needs and Impact | Customer Needs and impact |  | TasNetworks has a customer and stakeholder engagement strategy to inform the existing program of work and the upcoming revenue submission. The feedback obtained informs the approach taken by TasNetworks to align our investments with customer needs and impacts. Customer needs addressed by this investment include: - affordability; and - supply reliability and safety of the current network; Consumers have identified safety, restoration of faults/emergencies and supply reliability as the highest performing services offered by TasNetworks. The reliable operation of GMS are critical to enable TasNetworks to offer services that also meet these top priorities Customers will continue to be consulted through routine TasNetworks processes, including the Voice of the customer program, the Annual Planning Review and ongoing regular customer liaison meetings. |  |  |  |  | TRUE

## Objectives and Analysis
Investment Evaluation Summary |  | Copperleaf Investment Code |  | Report Start Year | NPV Period | Base Fiscal Year | Currency Scale
|  | PRJ000609 |  | 2025 | 25 | FY23 | Literal
|  | Investment Name |  |  |  |  | Scenario
|  | R24_D_SB_REGMS_GMS_Replacement of GMS |  |  |  |  | Approved
Value Function | TasNetworks Value Function | Version |  | 0.1 | Date |  | 2022-10-28
Functional Area | REGMS |  | Department |  | Asset Strategy
Works Initiator |  |  | Portfolio |  | Dx - Renewal
Investment Category | Standard Control - Reliability & Quality Maintained |  | Needs Item Reference
Investment Type | Network Project |  | Document No.
Investment Stage | Gate 2 – Investment Evaluation Summary |  | Project Zone Location
PPM ID |  |  | Regulatory Test Required |  | No
Objectives and Analysis
03. Business Performance Objectives | Safety and Wellbeing |  | Performance measure: Harm to people. Investment objective: The kiosk substations and the assets contained within them do not result in any incidents that result in harm to members of the public or operational personnel. |  |  |  |  | TRUE
| Our Customers |  | Performance measure: Customer net promoter score Investment objective: The reliability of supply to customer is either maintained at its current level, or higher. |  |  |  |  | FALSE
| Our People |  | Performance measure: Effort required to manage the assets. Investment objective: There is a reduction in effort (and cost) required to manage the assets when they're replaced. |  |  |  |  | FALSE
| Our Business - Sustained Cost Management |  | Performance measure: Level of capital and operational expenditure required over the long term. Investment objective: The strategy and investment required to deliver it can be accurately forecasted and it can either reduce or be maintained at a sustainable level over the long term. |  |  |  |  | FALSE
| Our Business - Network Service |  | Performance measure: Network performance. Investment objective: The assets and their performance result do not have a negative impact on network. |  |  |  |  | FALSE
04. Business Risks | Death or Injury (Employee) |  | Failure of equipment within HV GMA (e.g. HV switchgear, transformer or LV switchgear) in the presence of TasNetworks personnel results in injury or death, typically while equipment is being operated. |  |  |  |  | FALSE
| Death or Injury (Public) |  | Catastrophic failure of equipment within HV GMS in the presence of member of the public resulting in injury. |  |  |  |  | FALSE
| Sustainable and Predictable Pricing |  | Under investment in the assets results in increased asset failures resulting in injuries, notable impact on network performance and operation restrictions. With a resultant significant increase in unplanned investment required, with wider business impact. |  |  |  |  | FALSE
| Widespread Power Disruption |  | Asset failure e.g. HV GMS resulting in loss of high voltage distribution feeders for an extended duration, with resultant network performance and customer impact. |  |  |  |  | FALSE
| Bushfire Start | [6 empty] | FALSE
| Loss of Major Industrial | [6 empty] | FALSE
| Customer Focus |  | Under investment in the assets results in increased asset failures and more frequent disruptions to customer supply. |  |  |  |  | FALSE
| Business Continuity Management | [6 empty] | FALSE
| Cyber Security | [6 empty] | FALSE
| Private Assets | [6 empty] | FALSE
Energy Policy and Regulation
Project Marinus (D&A)
Tasmanian Power System Complexity
| Emerging Complexity of the NEM | [6 empty] | FALSE
05. Strategic Objectives | Strategic Objectives |  | The objective of this planned asset replacement program is to ensure that the planned replacement of the assets when they reach end of life results to ensure the HV GMS on the network are maintained in a reliable and safe operating condition. |  |  |  |  | FALSE
| Strategic Document #1 |  | TasNetworks’ Business Plan: Reduction in safety risk - Planned asset replacement when assets reach end of life ensures the assets will remain in a safe and reliable operating condition. |  |  |  |  | FALSE
| Strategic Document #2 |  | Ground Mounted Substations Asset Management Plan |  |  |  |  | FALSE
| Strategic Document #3 |  | Towards 2030 Ensuring our electricity network remains resilient and fit-for-purpose by proactively maintaining it, designing out risks, and making prudent investments of long-term value: The long-term impact of asset maintenance and renewal has been reviewed out to 2050. The analysis clearly demonstrates work should be done to mitigate risks to customers now and into the future. To ensure our capital is used wisely, we will streamline our investment planning to achieve optimised investment strategies and have the best delivery model: Investment planning has been developed to align all asset categories. The plan has been developed out to 2050 to ensure the long-term objectives of optimising investment strategies is achieved. |  |  |  |  | FALSE
| Strategic Document #4 |  | TasNetworks Business Plan 2020-21 Our services reflect our customers’ needs and expectations: The businesses and communities of Tasmania rely on these assets for continuous and reliable supply. Define and efficiently deliver our work: This work supports a long-term program which aims to support deliverability. We operate our business to be sustainable: The proposed program is designed to build in sustainability in supply and deliverability. |  |  |  |  | FALSE
| Strategic Document #5 | [6 empty] | FALSE
06. Project Objectives | Project Objectives |  | This program aims to manage the higher risk assets prior to an in-service failure to ensure the safety risk can be managed at an acceptable level and network reliability can be maintained at its current level. |  |  |  |  | FALSE
07. Options Analysis | Benchmarking |  | The proactive replacement of these assets prior to failure occurring is a strategy also undertaken by other DNSP’s. TasNetworks currently has the second oldest average age for distribution ground mounted HV GMS in Australia. There is currently only one distribution network service provider (DNSP) with an older average age for its HV GMS. The DNSP has initiated a ‘fast track recovery program’ to reduce presented by these assets. This occurred as a result of an increasing number of failure occurring, with significant detrimental impacts e.g. fires resulting. The program consists of an increase in the rate of replacement for these assets and improved their condition monitoring practices for these assets. TasNetworks has adopted the condition monitoring practices they have now put in place. Options to delay replacement would either see TasNetworks maintain its position of having one of the oldest fleets for this asset type, with a possibly of having the oldest fleet over the long term. TasNetworks will continue to monitor the condition of the assets and failure rate to ascertain whether future investment practices need to adjust to ensure risk is managed within TasNetworks risk appetite. |  |  |  |  | TRUE
| Expert Findings |  | Through utility network forums and the engagement of external experts, TasNetworks was able to quantify the risk for these assets. In many situation this risk was deemed to be so high under operation of the asset that operational restrictions and additional hierarchy of control mitigations were necessary. The networks study that was undertaken for the entire network, with a focus on safety risks under fault conditions provided further support for the continuation of this asset replacement program at or above its current level. The findings of the study also reinforced the need to ensure that the new equipment being installed on the network was of a modern design with arc fault containment capability. |  |  |  |  | FALSE
08. Investment Timing | Investment Timing |  | This program is an extension of an existing program and while the rate of replacement of the asset may vary based on risk and business need, the program will continue for the long term. |  |  |  |  | TRUE
09. Expected Outcomes and Benefits | Expected Outcomes and Benefits |  | The expected outcomes and benefits to TasNetworks from the selected option, Option 4 will be: - Reduction in network reliability. - Reduction in reliability of customer supply. - Existing operational bans on equipment would remain for an extended period. |  |  |  |  | TRUE
10. Assumptions | Assumptions |  | The following assumptions have been made in this analysis: -That the Total Quantified Risk (TQR) developed and used as the primary input in the options analysis is fit for purpose. - That the asset life cycle curves provided and used for these asset correctly reflect the lifecycle of the assets. -The Copperleaf program used for analysing the network investment programs was able to select the most appropriate investment option for the business. The following estimated inputs (based on historical data) were used for the quantification of risk: -Every 10 years through working on these results in a 'Moderate' injury to an employee. - When an asset failure occurs e.g. HV switchgear fault it results in a loss of 2MVA of load for an average duration of 2 hours. - The cost of repairing a failed asset is $100k. - The cost of reactively replacing a failed asset is $100k. |  |  |  |  | TRUE
11. Regulatory Considerations | Regulatory Investment Test |  | The level of investment for the program was under the threshold for requiring a RIT to be undertaken.
| Meet or manage the expected demand for Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
| Comply with all applicable regulatory obligations associated with the provision of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
| Maintain the quality, reliability and security of supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
| Maintain the reliability and security of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
| Maintain the safety of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
12. Recommendation | Recommendation |  | It is recommended that Option 4 is approved as the preferred investment option. This option was selected as an outcome of a business optimisation process being applied across all network investments. A financial constraint was applied to this program. |  |  |  |  | TRUE

## Economic Analysis
alternative
| Investment Evaluation Summary |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[5 empty] | PRJ000609 |  | 2025 |  | 25 | FY23 | Literal
[5 empty] | Investment Name | [5 empty] | Scenario
[5 empty] | R24_D_SB_REGMS_GMS_Replacement of GMS | [5 empty] | Approved
autofit | Value Function |  |  | TasNetworks Value Function | Version |  | 0.1 |  | Date |  | 2022-10-28
Economic Analysis
| Parameter |  |  |  | Value | Unit | Source of Values
75679 | NPV Period |  |  |  | 25 | Years | TasNetworks requirement
autofit | First Fiscal Year of Forecast |  |  |  | FY23 | - | TasNetworks requirement
| Weighted Average Cost of Capital (WACC) |  |  |  | 2.82 | % | 2019-24 Revenue determination and ISP 2022 draft data
| Voluntary load shedding assumed? |  |  |  | No | - | N/A
| Reduction in system losses considered? |  |  |  | No | - | N/A
| Value of Customer Reliability applied |  |  | Very large business customer - Services | 10.93 | $/kWh | AER - Values of Customer Reliability - Annual adjustment summary - December 2021
|  |  |  | Residential | 17.08 | $/kWh
|  |  |  | Very large business customer - Metals | 20.6 | $/kWh
|  |  |  | Very large business customer - Transmission | 27.43 | $/kWh
|  |  |  | Very large business customer - Mines | 36.47 | $/kWh
|  |  |  | Business customer - Agricultural | 39.28 | $/kWh
|  |  |  | Business customer - Commercial | 46.18 | $/kWh
|  |  |  | Very large business customer - Distribution | 58.8 | $/kWh
|  |  |  | Business customer - Industrial | 66.16 | $/kWh
autofit |  |  |  | Very large business customer - Industrial | 122.39 | $/kWh
Sensitivity to Project Timing
|  | 1 | Navigate to Copperleaf Portfolio and search for your Investment
|  | 2 | Navigate to the Value Comparison Page for your Investment through the breadcrumb menu
|  | 3 | Once on the Value Comparison Page, select "Value by Start Date" in the drop-down menu in the top-left corner of the page
|  | 4 | This screen will show the value change over time for each option in your investment
|  | 5 | With the snipping tool on your PC, take a screenshot of the chart and copy + paste it in this section of the report
Options Considered
| Options Summary |  |  |  | R24 Expenditure ($M) | NPV ($M) | Preferred Option | Reason for selection/rejection
| Option 1: Kiosk substation replacement at 50 years |  |  |  | 31.8706 | 56.3924 | No | Rejected: This option represents the historical preferred strategy This option would require a notable increase in future expenditure. For asset replacement to occur at 50 years of service the rate of delivery would need to increase from approximately 20 substations per annum to 30 for the period from 1/7/2024 – 20/6/2029.
| Option 2: Kiosk substation replacement at 52 years |  |  |  | 29.1533 | 52.9283 | No | Rejected: This option would result in the targeted safety risk for the assets remaining at ‘Medium’ for the long term. Whilst this option would nominally be the recommended option, as an outcome of a business optimisation process being applied across all network investments, a financial constraint was applied to this program which resulted in insufficient funding for this option to be delivered.
| Option 3: Kiosk substation replacement at 55 years |  |  |  | 23.6391 | 45.2981 | No | Rejected: This option was not recommended because of the increasing risk over the long term.
| Option 4: Financially constrained at $2.85 m p.a. |  |  |  | 17.6206 | 36.31 | Yes | This option was recommended as an outcome of a business optimisation process being applied across all network investments. A financial constraint was applied to this program.
0
0
NPV Components

## Needs Assessment (hidden)
Needs Assessment Form |  | Copperleaf Investment Code |  | Report Start Year | NPV Period | Base Fiscal Year | Currency Scale
|  | PRJ000609 |  | 2025 | 25 | FY23 | Literal
|  | Investment Name |  |  |  |  | Scenario
|  | R24_D_SB_REGMS_GMS_Replacement of GMS |  |  |  |  | Approved
Value Function | TasNetworks Value Function | Version |  | 0.1 | Date |  | 2022-10-28
Functional Area | REGMS |  | Department |  | Asset Strategy
Works Initiator |  |  | Portfolio |  | Dx - Renewal
Investment Category | Standard Control - Reliability & Quality Maintained |  | Needs Item Reference
Investment Type | Network Project |  | Document No.
Investment Stage | Gate 2 – Investment Evaluation Summary |  | Project Zone Location
PPM ID |  |  | Regulatory Test Required |  | No
Investment Overview
01. Overview | Background |  | TasNetworks owns and maintains approximately 2080 high voltage (HV) ground mounted distribution substations (GMS) on the distribution network. These substations comprise the following construction types: - Fence type (85); - Steel, fibreglass and block wall kiosks (1647); and - Building type, isolated and integrated (348). The HV GMS are supplied at both 11 kV and 22 kV and range in size from 300 kVA to 4500 kVA. Within these substations there is a variety of configurations and equipment, with approximately twenty different makes and models of HV switchgear. HV GMSs are actively managed and receive routine inspections and maintenance to maximise their service life. Many of the older substations were installed in the early 1960s and are at or near the end of their service life. Even with routine maintenance TasNetworks’ steel, fibreglass and block wall kiosk substations deteriorate over time resulting in a finite operational life for these assets. As the assets age, the probability of an in service failure occurring increases. TasNetworks' experience has been that the failure rate of the assets typically increases after 45 to 50 years of service. Currently there are approximately ten asset failures per annum (including HV switchgear, transformers, low voltage (LV) switchboards and failure of the substation enclosures). |  |  |  |  | TRUE
| Problem Definition |  | HV GMSs have several technical and legacy design issues that require replacement to ensure ongoing risk mitigation. Issues include: - HV switchgear using oil as an insulating medium; - LV switchboards with exposed live fronts; - Degradation of epoxy enclosures; - Oil containment deficiencies; In some cases, operating restrictions have been imposed due to operational safety issues associated with HV switchgear and LV switchboards. Both asset failures and inoperability issues can result in a loss of customer supply and have a negative impact on network performance. As a result of the risk presented by this equipment a management plan has been deemed necessary to mitigate these risks |  |  |  |  | FALSE
02. Customer Needs and Impact | Customer Needs and impact |  | TasNetworks has a customer and stakeholder engagement strategy to inform the existing program of work and the upcoming revenue submission. The feedback obtained informs the approach taken by TasNetworks to align our investments with customer needs and impacts. Customer needs addressed by this investment include: - affordability; and - supply reliability and safety of the current network; Consumers have identified safety, restoration of faults/emergencies and supply reliability as the highest performing services offered by TasNetworks. The reliable operation of GMS are critical to enable TasNetworks to offer services that also meet these top priorities Customers will continue to be consulted through routine TasNetworks processes, including the Voice of the customer program, the Annual Planning Review and ongoing regular customer liaison meetings. |  |  |  |  | TRUE
03. Business Objectives | Business Objectives
04. Project Objectives | Project Objectives |  | This program aims to manage the higher risk assets prior to an in-service failure to ensure the safety risk can be managed at an acceptable level and network reliability can be maintained at its current level. |  |  |  |  | FALSE
05. Risk Objective | Risk if not progressed | [6 empty] | TRUE
06. Investment Timing | Investment Timing |  | This program is an extension of an existing program and while the rate of replacement of the asset may vary based on risk and business need, the program will continue for the long term. |  |  |  |  | TRUE
07. Business Consulatation | Business Consulatation | [6 empty] | TRUE

## Option 1
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000609 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_D_SB_REGMS_GMS_Replacement of GMS | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-28
Alternative Overview
75679 | Alternative Name |  | Option 1: Kiosk substation replacement at 50 years
autofit | Description |  | This option consists of proactively replacing the assets based on the criteria defined in Section 1, but with a target of replacing the asset prior to them reaching 50 years of service life.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | Rejected: This option represents the historical preferred strategy This option would require a notable increase in future expenditure. For asset replacement to occur at 50 years of service the rate of delivery would need to increase from approximately 20 substations per annum to 30 for the period from 1/7/2024 – 20/6/2029.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Option 1: Kiosk substation replacement at 50 years |  | Capex |  |  | 5700000 | 5700000 | 5700000 | 5700000 | 5700000 | 28500000 | 92929470 | 56392378.73
|  |  | Opex |  |  | 674116 | 674116 | 674116 | 674116 | 674116 | 3370580
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | UARM - Environment and Community - Fire Risk |  |  | 0 | 0%
[9 empty] | UARM - Safety & People - Worker |  |  | 4508.3406 | 2.27%
[9 empty] | UARM - Network Performance Risk |  |  | 33472.6453 | 16.83%
[9 empty] | UARM - Environment and Community - Other Risk |  |  | 5610.1835 | 2.82%
[9 empty] | UARM - Financial Risk |  |  | 57986.3929 | 29.15%
[9 empty] | UARM - Safety & People - Public |  |  | 1782.6684 | 0.9%
[9 empty] | Terminal Value |  |  | 24305.5735 | 12.22%
[9 empty] | Total Investment Cost |  |  | -71273.4254 | 35.83%
[9 empty] | Total |  |  | 56392.3787
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 5700000 | 5700000 | 5700000 | 5700000 | 5700000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | OPEX Cost |  | Outcome | 2024 | 0 | Dollar | 674116 | 674116 | 674116 | 674116 | 674116
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -71273.4254 | Dollar | 6374116 | 6374116 | 6374116 | 6374116 | 6374116
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 24305.5735 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Baseline |  | 0 | Dollar | 1338186.24 | 963279.77 | 779031.18 | 670897.57 | 598386.14
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Outcome | 2024 | 4508.3406 | Dollar | 954570.72 | 610957.35 | 439537.63 | 335647.5 | 254997.08
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE | UARM - PA to Investment | UARM - Network Performance Risk |  | Baseline |  | 0 | Dollar | 9935503.43 | 7151971.23 | 5783998.31 | 4981149.08 | 4442780.35
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE | UARM - PA to Investment | UARM - Network Performance Risk |  | Outcome | 2024 | 33472.6453 | Dollar | 7087309.95 | 4536116.61 | 3263393.02 | 2492049.88 | 1893252.44
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Baseline |  | 0 | Dollar | 1665240.29 | 1198706.31 | 969427.17 | 834865.61 | 744632.31
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Outcome | 2024 | 5610.1835 | Dollar | 1187868.75 | 760275.93 | 546961.06 | 417680.08 | 317318.62
| UARM - PA to Investment | UARM - Financial Risk |  | Baseline |  | 0 | Dollar | 17211785.93 | 12389729.28 | 10019919.11 | 8629101.91 | 7696457.96
| UARM - PA to Investment | UARM - Financial Risk |  | Outcome | 2024 | 57986.3929 | Dollar | 12277713.21 | 7858149.18 | 5653344.33 | 4317106.76 | 3279779.02
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE | UARM - PA to Investment | UARM - Safety & People - Public |  | Baseline |  | 0 | Dollar | 529139.78 | 380895.9 | 308041.12 | 265283.4 | 236611.24
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE | UARM - PA to Investment | UARM - Safety & People - Public |  | Outcome | 2024 | 1782.6684 | Dollar | 377452.2 | 241582.1 | 173800.06 | 132720.27 | 100829.84
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 30679855.67 | 22084582.49 | 17860416.89 | 15381297.57 | 13718868
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 21884914.83 | 14007081.17 | 10077036.1 | 7695204.49 | 5846177
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 2
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000609 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_D_SB_REGMS_GMS_Replacement of GMS | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-28
Alternative Overview
75679 | Alternative Name |  | Option 2: Kiosk substation replacement at 52 years
autofit | Description |  | This option consists of proactive replacing the assets based on the criteria defined in Section 1, but with a target of replacing the asset prior to them reaching 52 years of service life.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | Rejected: This option would result in the targeted safety risk for the assets remaining at ‘Medium’ for the long term. Whilst this option would nominally be the recommended option, as an outcome of a business optimisation process being applied across all network investments, a financial constraint was applied to this program which resulted in insufficient funding for this option to be delivered.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Option 2: Kiosk substation replacement at 52 years |  | Capex |  |  | 5130000 | 5130000 | 5130000 | 5130000 | 5130000 | 25650000 | 86438710 | 52928299.17
|  |  | Opex |  |  | 700656 | 700656 | 700656 | 700656 | 700656 | 3503280
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | UARM - Environment and Community - Fire Risk |  |  | 0 | 0%
[9 empty] | UARM - Safety & People - Worker |  |  | 4215.1553 | 2.28%
[9 empty] | UARM - Network Performance Risk |  |  | 31295.8606 | 16.91%
[9 empty] | UARM - Environment and Community - Other Risk |  |  | 5245.3435 | 2.83%
[9 empty] | UARM - Financial Risk |  |  | 54215.4363 | 29.29%
[9 empty] | UARM - Safety & People - Public |  |  | 1666.7384 | 0.9%
[9 empty] | Terminal Value |  |  | 22362.7192 | 12.08%
[9 empty] | Total Investment Cost |  |  | -66072.9541 | 35.7%
[9 empty] | Total |  |  | 52928.2992
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 5130000 | 5130000 | 5130000 | 5130000 | 5130000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | OPEX Cost |  | Outcome | 2024 | 0 | Dollar | 700656 | 700656 | 700656 | 700656 | 700656
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -66072.9541 | Dollar | 5830656 | 5830656 | 5830656 | 5830656 | 5830656
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 22362.7192 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Baseline |  | 0 | Dollar | 1338186.24 | 963279.77 | 779031.18 | 670897.57 | 598386.14
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Outcome | 2024 | 4215.1553 | Dollar | 984716.5 | 637959.66 | 464597.14 | 361620.54 | 282641.3
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE | UARM - PA to Investment | UARM - Network Performance Risk |  | Baseline |  | 0 | Dollar | 9935503.43 | 7151971.23 | 5783998.31 | 4981149.08 | 4442780.35
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE | UARM - PA to Investment | UARM - Network Performance Risk |  | Outcome | 2024 | 31295.8606 | Dollar | 7311130.48 | 4736598.07 | 3449449.97 | 2684889.47 | 2098499.88
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Baseline |  | 0 | Dollar | 1665240.29 | 1198706.31 | 969427.17 | 834865.61 | 744632.31
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Outcome | 2024 | 5245.3435 | Dollar | 1225382.2 | 793877.63 | 578145.15 | 450000.96 | 351719.12
| UARM - PA to Investment | UARM - Financial Risk |  | Baseline |  | 0 | Dollar | 17211785.93 | 12389729.28 | 10019919.11 | 8629101.91 | 7696457.96
| UARM - PA to Investment | UARM - Financial Risk |  | Outcome | 2024 | 54215.4363 | Dollar | 12665449.09 | 8205453.57 | 5975660.41 | 4651172.75 | 3635339.77
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE | UARM - PA to Investment | UARM - Safety & People - Public |  | Baseline |  | 0 | Dollar | 529139.78 | 380895.9 | 308041.12 | 265283.4 | 236611.24
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE | UARM - PA to Investment | UARM - Safety & People - Public |  | Outcome | 2024 | 1666.7384 | Dollar | 389372.32 | 252259.23 | 183708.98 | 142990.42 | 111760.8
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 30679855.67 | 22084582.49 | 17860416.89 | 15381297.57 | 13718868
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 22576050.59 | 14626148.16 | 10651561.65 | 8290674.14 | 6479960.87
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 3
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000609 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_D_SB_REGMS_GMS_Replacement of GMS | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-28
Alternative Overview
75679 | Alternative Name |  | Option 3: Kiosk substation replacement at 55 years
autofit | Description |  | This option consists of proactive replacing the assets based on the criteria defined in Section 1, but with a target of replacing the asset prior to them reaching 55 years of service life.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | Rejected: This option was not recommended because of the increasing risk over the long term.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Option 3: Kiosk substation replacement at 55 years |  | Capex |  |  | 3990000 | 3990000 | 3990000 | 3990000 | 3990000 | 19950000 | 81834680 | 45298090.87
|  |  | Opex |  |  | 737812 | 737812 | 737812 | 737812 | 737812 | 3689060
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | UARM - Environment and Community - Fire Risk |  |  | 0 | 0%
[9 empty] | UARM - Safety & People - Worker |  |  | 3665.9235 | 2.2%
[9 empty] | UARM - Network Performance Risk |  |  | 27218.0317 | 16.33%
[9 empty] | UARM - Environment and Community - Other Risk |  |  | 4561.8789 | 2.74%
[9 empty] | UARM - Financial Risk |  |  | 47151.2027 | 28.29%
[9 empty] | UARM - Safety & People - Public |  |  | 1449.5635 | 0.87%
[9 empty] | Terminal Value |  |  | 21928.4543 | 13.16%
[9 empty] | Total Investment Cost |  |  | -60676.9637 | 36.41%
[9 empty] | Total |  |  | 45298.0909
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 3990000 | 3990000 | 3990000 | 3990000 | 3990000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | OPEX Cost |  | Outcome | 2024 | 0 | Dollar | 737812 | 737812 | 737812 | 737812 | 737812
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -60676.9637 | Dollar | 4727812 | 4727812 | 4727812 | 4727812 | 4727812
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 21928.4543 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Baseline |  | 0 | Dollar | 1338186.24 | 963279.77 | 779031.18 | 670897.57 | 598386.14
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Outcome | 2024 | 3665.9235 | Dollar | 1050246.4 | 692922.92 | 519406.34 | 415660.71 | 339532.73
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE | UARM - PA to Investment | UARM - Network Performance Risk |  | Baseline |  | 0 | Dollar | 9935503.43 | 7151971.23 | 5783998.31 | 4981149.08 | 4442780.35
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE | UARM - PA to Investment | UARM - Network Performance Risk |  | Outcome | 2024 | 27218.0317 | Dollar | 7797664.05 | 5144678.54 | 3856386.63 | 3086116.32 | 2520896.24
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Baseline |  | 0 | Dollar | 1665240.29 | 1198706.31 | 969427.17 | 834865.61 | 744632.31
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Outcome | 2024 | 4561.8789 | Dollar | 1306927.67 | 862273.97 | 646349.77 | 517248.6 | 422514.87
| UARM - PA to Investment | UARM - Financial Risk |  | Baseline |  | 0 | Dollar | 17211785.93 | 12389729.28 | 10019919.11 | 8629101.91 | 7696457.96
| UARM - PA to Investment | UARM - Financial Risk |  | Outcome | 2024 | 47151.2027 | Dollar | 13508296.32 | 8912392.45 | 6680617.81 | 5346238.76 | 4367078.8
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE | UARM - PA to Investment | UARM - Safety & People - Public |  | Baseline |  | 0 | Dollar | 529139.78 | 380895.9 | 308041.12 | 265283.4 | 236611.24
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE | UARM - PA to Investment | UARM - Safety & People - Public |  | Outcome | 2024 | 1449.5635 | Dollar | 415283.87 | 273992.57 | 205381.4 | 164358.75 | 134256.56
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 30679855.67 | 22084582.49 | 17860416.89 | 15381297.57 | 13718868
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 24078418.31 | 15886260.45 | 11908141.95 | 9529623.14 | 7784279.2
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 4
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000609 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_D_SB_REGMS_GMS_Replacement of GMS | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-28
Alternative Overview
75679 | Alternative Name |  | Option 4: Financially constrained at $2.85 m p.a.
autofit | Description |  | This option consists of proactively replacing the assets based on the criteria defined in Section 1 at reduced volumes in comparison to other options.
autofit | Alternative Status |  | Recommended
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | This option was recommended as an outcome of a business optimisation process being applied across all network investments. A financial constraint was applied to this program.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Option 4: Financially constrained at $2.85 m p.a. |  | Capex |  |  | 2850000 | 2850000 | 2850000 | 2850000 | 2850000 | 14250000 | 71079470 | 36309979.36
|  |  | Opex |  |  | 674116 | 674116 | 674116 | 674116 | 674116 | 3370580
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | UARM - Environment and Community - Fire Risk |  |  | 0 | 0%
[9 empty] | UARM - Safety & People - Worker |  |  | 3001.8811 | 2.15%
[9 empty] | UARM - Network Performance Risk |  |  | 22287.7795 | 15.98%
[9 empty] | UARM - Environment and Community - Other Risk |  |  | 3735.5438 | 2.68%
[9 empty] | UARM - Financial Risk |  |  | 38610.272 | 27.68%
[9 empty] | UARM - Safety & People - Public |  |  | 1186.9908 | 0.85%
[9 empty] | Terminal Value |  |  | 19073.4297 | 13.67%
[9 empty] | Total Investment Cost |  |  | -51585.9175 | 36.98%
[9 empty] | Total |  |  | 36309.9794
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 2850000 | 2850000 | 2850000 | 2850000 | 2850000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | OPEX Cost |  | Outcome | 2024 | 0 | Dollar | 674116 | 674116 | 674116 | 674116 | 674116
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -51585.9175 | Dollar | 3524116 | 3524116 | 3524116 | 3524116 | 3524116
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 19073.4297 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Baseline |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Outcome | 2024 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Baseline |  | 0 | Dollar | 1338186.24 | 963279.77 | 779031.18 | 670897.57 | 598386.14
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Outcome | 2024 | 3001.8811 | Dollar | 1121372.56 | 755012.4 | 582710.6 | 474990.62 | 402120.57
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE | UARM - PA to Investment | UARM - Network Performance Risk |  | Baseline |  | 0 | Dollar | 9935503.43 | 7151971.23 | 5783998.31 | 4981149.08 | 4442780.35
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE | UARM - PA to Investment | UARM - Network Performance Risk |  | Outcome | 2024 | 22287.7795 | Dollar | 8325747.68 | 5605668.38 | 4326395.68 | 3526617.45 | 2985586.16
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Baseline |  | 0 | Dollar | 1665240.29 | 1198706.31 | 969427.17 | 834865.61 | 744632.31
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Outcome | 2024 | 3735.5438 | Dollar | 1395437.14 | 939538.18 | 725125.65 | 591078.8 | 500399.24
| UARM - PA to Investment | UARM - Financial Risk |  | Baseline |  | 0 | Dollar | 17211785.93 | 12389729.28 | 10019919.11 | 8629101.91 | 7696457.96
| UARM - PA to Investment | UARM - Financial Risk |  | Outcome | 2024 | 38610.272 | Dollar | 14423122.87 | 9710988.97 | 7494838.77 | 6109341.62 | 5172085.15
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE | UARM - PA to Investment | UARM - Safety & People - Public |  | Baseline |  | 0 | Dollar | 529139.78 | 380895.9 | 308041.12 | 265283.4 | 236611.24
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE | UARM - PA to Investment | UARM - Safety & People - Public |  | Outcome | 2024 | 1186.9908 | Dollar | 443408.26 | 298543.72 | 230412.89 | 187818.73 | 159004.77
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 30679855.67 | 22084582.49 | 17860416.89 | 15381297.57 | 13718868
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 25709088.51 | 17309751.65 | 13359483.59 | 10889847.22 | 9219195.89
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 5 (hidden)
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000609 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_D_SB_REGMS_GMS_Replacement of GMS | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-28
Alternative Overview
75679 | Alternative Name
autofit | Description
autofit | Alternative Status
autofit | Alternative Start Date
Reason for selection/rejection
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
0
0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Total |  |  | 0
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 0 | 0 | 0 | 0 | 0
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 6 (hidden)
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000609 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_D_SB_REGMS_GMS_Replacement of GMS | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-28
Alternative Overview
75679 | Alternative Name
autofit | Description
autofit | Alternative Status
autofit | Alternative Start Date
Reason for selection/rejection
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
0
0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Total |  |  | 0
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 0 | 0 | 0 | 0 | 0
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## TextFormatting (hidden)
Index | 8
Column Width | 238
Font | Calibri
Font Size | 11
Font Colour
Text | Sheet | Group | Field | Row Height | Row Number
Replacement of kiosk and fence type substations on the distribution network. | Investment Summary | Header | Description | 15 | 9
TasNetworks owns and maintains approximately 2080 high voltage (HV) ground mounted distribution substations (GMS) on the distribution network. These substations comprise the following construction types: - Fence type (85); - Steel, fibreglass and block wall kiosks (1647); and - Building type, isolated and integrated (348). The HV GMS are supplied at both 11 kV and 22 kV and range in size from 300 kVA to 4500 kVA. Within these substations there is a variety of configurations and equipment, with approximately twenty different makes and models of HV switchgear. HV GMSs are actively managed and receive routine inspections and maintenance to maximise their service life. Many of the older substations were installed in the early 1960s and are at or near the end of their service life. Even with routine maintenance TasNetworks’ steel, fibreglass and block wall kiosk substations deteriorate over time resulting in a finite operational life for these assets. As the assets age, the probability of an in service failure occurring increases. TasNetworks' experience has been that the failure rate of the assets typically increases after 45 to 50 years of service. Currently there are approximately ten asset failures per annum (including HV switchgear, transformers, low voltage (LV) switchboards and failure of the substation enclosures). | Investment Summary | 0.1 Overview | Background | 270 | 16
HV GMSs have several technical and legacy design issues that require replacement to ensure ongoing risk mitigation. Issues include: - HV switchgear using oil as an insulating medium; - LV switchboards with exposed live fronts; - Degradation of epoxy enclosures; - Oil containment deficiencies; In some cases, operating restrictions have been imposed due to operational safety issues associated with HV switchgear and LV switchboards. Both asset failures and inoperability issues can result in a loss of customer supply and have a negative impact on network performance. As a result of the risk presented by this equipment a management plan has been deemed necessary to mitigate these risks | Investment Summary | 0.1 Overview | Problem Definition | 195 | 17
TasNetworks has a customer and stakeholder engagement strategy to inform the existing program of work and the upcoming revenue submission. The feedback obtained informs the approach taken by TasNetworks to align our investments with customer needs and impacts. Customer needs addressed by this investment include: - affordability; and - supply reliability and safety of the current network; Consumers have identified safety, restoration of faults/emergencies and supply reliability as the highest performing services offered by TasNetworks. The reliable operation of GMS are critical to enable TasNetworks to offer services that also meet these top priorities Customers will continue to be consulted through routine TasNetworks processes, including the Voice of the customer program, the Annual Planning Review and ongoing regular customer liaison meetings. | Investment Summary | 02. Customer Needs and Impact | Customer Needs and impact | 210 | 18
Performance measure: Harm to people. Investment objective: The kiosk substations and the assets contained within them do not result in any incidents that result in harm to members of the public or operational personnel. | Objectives and Analysis | 03. Business Performance Objectives | Safety and Wellbeing | 45 | 17
Performance measure: Customer net promoter score Investment objective: The reliability of supply to customer is either maintained at its current level, or higher. | Objectives and Analysis | 03. Business Performance Objectives | Our Customers | 30 | 18
Performance measure: Effort required to manage the assets. Investment objective: There is a reduction in effort (and cost) required to manage the assets when they're replaced. | Objectives and Analysis | 03. Business Performance Objectives | Our People | 30 | 19
Performance measure: Level of capital and operational expenditure required over the long term. Investment objective: The strategy and investment required to deliver it can be accurately forecasted and it can either reduce or be maintained at a sustainable level over the long term. | Objectives and Analysis | 03. Business Performance Objectives | Our Business - Sustained Cost Management | 45 | 20
Performance measure: Network performance. Investment objective: The assets and their performance result do not have a negative impact on network. | Objectives and Analysis | 03. Business Performance Objectives | Our Business - Network Service | 30 | 21
Failure of equipment within HV GMA (e.g. HV switchgear, transformer or LV switchgear) in the presence of TasNetworks personnel results in injury or death, typically while equipment is being operated. | Objectives and Analysis | 04. Business Risks | Death or Injury (Employee) | 30 | 23
Catastrophic failure of equipment within HV GMS in the presence of member of the public resulting in injury. | Objectives and Analysis | 04. Business Risks | Death or Injury (Public) | 15 | 24
Under investment in the assets results in increased asset failures resulting in injuries, notable impact on network performance and operation restrictions. With a resultant significant increase in unplanned investment required, with wider business impact. | Objectives and Analysis | 04. Business Risks | Sustainable and Predictable Pricing | 45 | 25
Asset failure e.g. HV GMS resulting in loss of high voltage distribution feeders for an extended duration, with resultant network performance and customer impact. | Objectives and Analysis | 04. Business Risks | Widespread Power Disruption | 30 | 26
| Objectives and Analysis | 04. Business Risks | Bushfire Start | 15 | 27
| Objectives and Analysis | 04. Business Risks | Loss of Major Industrial | 15 | 28
Under investment in the assets results in increased asset failures and more frequent disruptions to customer supply. | Objectives and Analysis | 04. Business Risks | Customer Focus | 15 | 29
| Objectives and Analysis | 04. Business Risks | Business Continuity Management | 15 | 30
| Objectives and Analysis | 04. Business Risks | Cyber Security | 15 | 31
| Objectives and Analysis | 04. Business Risks | Private Assets | 15 | 32
| Objectives and Analysis | 04. Business Risks | Energy Policy and Regulation | 15 | 33
| Objectives and Analysis | 04. Business Risks | Project Marinus (D&A) | 15 | 34
| Objectives and Analysis | 04. Business Risks | Tasmanian Power System Complexity | 15 | 35
| Objectives and Analysis | 04. Business Risks | Emerging Complexity of the NEM | 15 | 36
The objective of this planned asset replacement program is to ensure that the planned replacement of the assets when they reach end of life results to ensure the HV GMS on the network are maintained in a reliable and safe operating condition. | Objectives and Analysis | 05. Strategic Objectives | Strategic Objectives | 45 | 38
TasNetworks’ Business Plan: Reduction in safety risk - Planned asset replacement when assets reach end of life ensures the assets will remain in a safe and reliable operating condition. | Objectives and Analysis | 05. Strategic Objectives | Strategic Document #1 | 30 | 39
Ground Mounted Substations Asset Management Plan | Objectives and Analysis | 05. Strategic Objectives | Strategic Document #2 | 15 | 40
Towards 2030 Ensuring our electricity network remains resilient and fit-for-purpose by proactively maintaining it, designing out risks, and making prudent investments of long-term value: The long-term impact of asset maintenance and renewal has been reviewed out to 2050. The analysis clearly demonstrates work should be done to mitigate risks to customers now and into the future. To ensure our capital is used wisely, we will streamline our investment planning to achieve optimised investment strategies and have the best delivery model: Investment planning has been developed to align all asset categories. The plan has been developed out to 2050 to ensure the long-term objectives of optimising investment strategies is achieved. | Objectives and Analysis | 05. Strategic Objectives | Strategic Document #3 | 195 | 41
TasNetworks Business Plan 2020-21 Our services reflect our customers’ needs and expectations: The businesses and communities of Tasmania rely on these assets for continuous and reliable supply. Define and efficiently deliver our work: This work supports a long-term program which aims to support deliverability. We operate our business to be sustainable: The proposed program is designed to build in sustainability in supply and deliverability. | Objectives and Analysis | 05. Strategic Objectives | Strategic Document #4 | 150 | 42
| Objectives and Analysis | 05. Strategic Objectives | Strategic Document #5 | 15 | 43
This program aims to manage the higher risk assets prior to an in-service failure to ensure the safety risk can be managed at an acceptable level and network reliability can be maintained at its current level. | Objectives and Analysis | 06. Project Objectives | Project Objectives | 30 | 44
The proactive replacement of these assets prior to failure occurring is a strategy also undertaken by other DNSP’s. TasNetworks currently has the second oldest average age for distribution ground mounted HV GMS in Australia. There is currently only one distribution network service provider (DNSP) with an older average age for its HV GMS. The DNSP has initiated a ‘fast track recovery program’ to reduce presented by these assets. This occurred as a result of an increasing number of failure occurring, with significant detrimental impacts e.g. fires resulting. The program consists of an increase in the rate of replacement for these assets and improved their condition monitoring practices for these assets. TasNetworks has adopted the condition monitoring practices they have now put in place. Options to delay replacement would either see TasNetworks maintain its position of having one of the oldest fleets for this asset type, with a possibly of having the oldest fleet over the long term. TasNetworks will continue to monitor the condition of the assets and failure rate to ascertain whether future investment practices need to adjust to ensure risk is managed within TasNetworks risk appetite. | Objectives and Analysis | 07. Options Analysis | Benchmarking | 210 | 45
Through utility network forums and the engagement of external experts, TasNetworks was able to quantify the risk for these assets. In many situation this risk was deemed to be so high under operation of the asset that operational restrictions and additional hierarchy of control mitigations were necessary. The networks study that was undertaken for the entire network, with a focus on safety risks under fault conditions provided further support for the continuation of this asset replacement program at or above its current level. The findings of the study also reinforced the need to ensure that the new equipment being installed on the network was of a modern design with arc fault containment capability. | Objectives and Analysis | 07. Options Analysis | Expert Findings | 120 | 46
This program is an extension of an existing program and while the rate of replacement of the asset may vary based on risk and business need, the program will continue for the long term. | Objectives and Analysis | 08. Investment Timing | Investment Timing | 30 | 47
The expected outcomes and benefits to TasNetworks from the selected option, Option 4 will be: - Reduction in network reliability. - Reduction in reliability of customer supply. - Existing operational bans on equipment would remain for an extended period. | Objectives and Analysis | 09. Expected Outcomes and Benefits | Expected Outcomes and Benefits | 60 | 48
The following assumptions have been made in this analysis: -That the Total Quantified Risk (TQR) developed and used as the primary input in the options analysis is fit for purpose. - That the asset life cycle curves provided and used for these asset correctly reflect the lifecycle of the assets. -The Copperleaf program used for analysing the network investment programs was able to select the most appropriate investment option for the business. The following estimated inputs (based on historical data) were used for the quantification of risk: -Every 10 years through working on these results in a 'Moderate' injury to an employee. - When an asset failure occurs e.g. HV switchgear fault it results in a loss of 2MVA of load for an average duration of 2 hours. - The cost of repairing a failed asset is $100k. - The cost of reactively replacing a failed asset is $100k. | Objectives and Analysis | 10. Assumptions | Assumptions | 165 | 49
The level of investment for the program was under the threshold for requiring a RIT to be undertaken. | Objectives and Analysis | 11. Regulatory Considerations | Regulatory Investment Test | 15 | 50
Yes | Objectives and Analysis | 11. Regulatory Considerations | Meet or manage the expected demand for Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 51
Yes | Objectives and Analysis | 11. Regulatory Considerations | Comply with all applicable regulatory obligations associated with the provision of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 52
Yes | Objectives and Analysis | 11. Regulatory Considerations | Maintain the quality, reliability and security of supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 53
Yes | Objectives and Analysis | 11. Regulatory Considerations | Maintain the reliability and security of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 54
Yes | Objectives and Analysis | 11. Regulatory Considerations | Maintain the safety of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 55
It is recommended that Option 4 is approved as the preferred investment option. This option was selected as an outcome of a business optimisation process being applied across all network investments. A financial constraint was applied to this program. | Objectives and Analysis | 12. Recommendation | Recommendation | 60 | 56
This option consists of proactively replacing the assets based on the criteria defined in Section 1, but with a target of replacing the asset prior to them reaching 50 years of service life. | Option 1 | Description |  | 15
Rejected: This option represents the historical preferred strategy This option would require a notable increase in future expenditure. For asset replacement to occur at 50 years of service the rate of delivery would need to increase from approximately 20 substations per annum to 30 for the period from 1/7/2024 – 20/6/2029. | Option 1 | Reason for selection/rejection |  | 45
This option consists of proactive replacing the assets based on the criteria defined in Section 1, but with a target of replacing the asset prior to them reaching 52 years of service life. | Option 2 | Description |  | 15
Rejected: This option would result in the targeted safety risk for the assets remaining at ‘Medium’ for the long term. Whilst this option would nominally be the recommended option, as an outcome of a business optimisation process being applied across all network investments, a financial constraint was applied to this program which resulted in insufficient funding for this option to be delivered. | Option 2 | Reason for selection/rejection |  | 60
This option consists of proactive replacing the assets based on the criteria defined in Section 1, but with a target of replacing the asset prior to them reaching 55 years of service life. | Option 3 | Description |  | 15
Rejected: This option was not recommended because of the increasing risk over the long term. | Option 3 | Reason for selection/rejection |  | 15
This option consists of proactively replacing the assets based on the criteria defined in Section 1 at reduced volumes in comparison to other options. | Option 4 | Description |  | 15
This option was recommended as an outcome of a business optimisation process being applied across all network investments. A financial constraint was applied to this program. | Option 4 | Reason for selection/rejection |  | 15
| Option 5 | Description
| Option 5 | Reason for selection/rejection
| Option 6 | Description
| Option 6 | Reason for selection/rejection