## Run Extract (hidden)
[12 empty] | 1 | 2 | 3 | 4 | 5 | 6
[12 empty] | Option 1 | Option 2 | Option 3 | Option 4 | Option 5 | Option 6
[10 empty] | Address | Value Metric | Option 1: Construct a new 22 kV three-phase line to Zeehan from Strahan | Option 2: Construct a new 220/22 kV injection point at Pieman Switching Station | Option 3: Construct a new 44 kV three-phase line into Trial Harbour Zone sub from Renison Bell | Option 4: Provide diesel generation support to Zeehan township | Option 5: 44/22 kV injection point at Zeehan
[11 empty] | Terminal Value | 2230255.0393 | 1828723.1133 | 2122022.0741 | 559556.6272 | 1753040.8279
[11 empty] | Network Performance Risk | 4280038.7734 | 4280038.7734 | 4280038.7734 | 4280038.7734 | 2203025.0336
Notes | [10 empty] | Total Investment Cost | 5682267.1302 | 5188213.2227 | 5406510.0489 | 2757570.8131 | 4928283.7619
Need to open the .xlsm Investment Summary report from Copperleaf in the Trusted folder Save in the preferred location as an .xlsx Need to test environment - other and when two of the same value models have been selected with a different name
Options
| Option | 2025 | 2026 | 2027 | 2028 | 2029
| Baseline | 511632 | 511632 | 511632 | 511632 | 511632
| Option 1: Construct a new 22 kV three-phase line to Zeehan from Strahan | 511632 | 511632 | 511632 | 511632 | 511632
| Option 2: Construct a new 220/22 kV injection point at Pieman Switching Station | 511632 | 511632 | 511632 | 511632 | 511632
| Option 3: Construct a new 44 kV three-phase line into Trial Harbour Zone sub from Renison Bell | 511632 | 511632 | 511632 | 511632 | 511632
| Option 4: Provide diesel generation support to Zeehan township | 511632 | 511632 | 511632 | 511632 | 511632
| Option 5: 44/22 kV injection point at Zeehan | 511632 | 511632 | 511632 | 511632 | 511632
Option Breakdown | [7 empty] | Folder and File Paths
| Option 2 |  |  |  |  | Greater 0 | (Multiple Items)
| Recommended Option - Value | [6 empty] | This File Path | \\TNAD.tasnetworks.com.au\user$\user_folders\browningr\My Documents\Trusted\InvestmentTemplate.xlsm
| Value Function Measure | Value | Value in % | Greater 0 |  | Row Labels | Sum of Value in % | Folder Path | N:\NWITSolutions\Oracle\AIP Queries\Copperleaf\Investment Summary Reports\
Option 2 | Terminal Value | 1828.7231 | 16.19% | 1 | K20 | Network Performance Risk | 37.89% | File Name | InvestmentSummary_R24_T_ND_AUGSB_W Coast Reliability Improvement.xlsx
Option 2 | Network Performance Risk | 4280.0388 | 37.89% | 1 | K21 | Terminal Value | 16.19% | File Path | N:\NWITSolutions\Oracle\AIP Queries\Copperleaf\Investment Summary Reports\InvestmentSummary_R24_T_ND_AUGSB_W Coast Reliability Improvement.xlsx
Option 2 | Total Investment Cost | -5188.2132 | 45.93% | 1 | K22 | Total Investment Cost | 45.93%
Option 2 |  |  |  | 0 | K23
Option 2 |  |  |  | 0 | K24
Option 2 |  |  |  | 0 | K25
Option 2 |  |  |  | 0 | K26
Option 2 |  |  |  | 0 | K27
Option 2 |  |  |  | 0 | K28
Option 2 |  |  |  | 0 | K29
Option 2 |  |  |  | 0 | K30 |  |  | 1 | InvestmentSummary_R24_D_ND_PRHVR_Augment_HV_Fdr_TRIP.xlsx
Option 2 |  |  |  | 0 | K31 |  |  | 2 | InvestmentSummary_R24_D_OH_REPOL_Basic Fleet Pole Replacement.xlsx
Option 2 |  |  |  | 0 | K32 |  |  | 3 | InvestmentSummary_R24_T_ND_AUGSB_W Coast Reliability Improvement.xlsx
Option 2 |  |  |  | 0 | K33 |  |  | 4 | InvestmentSummary_R24_T_ND_AUGSB_Upper Derwent 110 kV Losses.xlsx
| Total | 920.5487 | 100% |  |  |  |  | 5 | InvestmentSummary_R24_D_OH_SIWES_Bird_Mitigation.xlsx
[8 empty] | 6 | InvestmentSummary_R24_D_SB_REGMS_GMS_Replacement of GMS.xlsx
[8 empty] | 7 | InvestmentSummary_R24_D_OH_REPOL_Complex Design.xlsx
Start | Option 1 |  |  |  |  | Greater 0 | 1 | 8 | InvestmentSummary_R24_D_PQ_PQTXV_Power_Quality_LV_Tformers.xlsx
| Value Function Measure | Value | Value in % | Greater 0 |  |  |  | 9 | InvestmentSummary_R24_D_ND_PQLVV_Aug_HV_LV_Conductor.xlsx
Option 1 | Terminal Value | 2230.255 | 16.28% | 1 | K20 | Row Labels | Sum of Value in % | 10 | InvestmentSummary_R24_D_CA_SOLCP_Crossover_Extension_OH.xlsx
Option 1 | Financial benefit - OPEX | -1505.0882 | 10.99% | 1 | K21 | Financial benefit - OPEX | 10.99% | 11 | InvestmentSummary_R24_D_CI_SOIRR_Irrigation_Supply.xlsx
Option 1 | Network Performance Risk | 4280.0388 | 31.25% | 1 | K22 | Network Performance Risk | 31.25% | 12 | InvestmentSummary_R24_D_AMIPD_AM Improvement Program.xlsx
Option 1 | Total Investment Cost | -5682.2671 | 41.48% | 1 | K23 | Terminal Value | 16.28% | 13 | InvestmentSummary_R24_D_CI_SOPOR_Permanent_Residence_OH.xlsx
Option 1 |  |  |  | 0 | K24 | Total Investment Cost | 41.48% | 14 | InvestmentSummary_R24_D_CI_SUPOR_Permanent_Residence_UG.xlsx
Option 1 |  |  |  | 0 | K25 |  |  | 15 | InvestmentSummary_R24_D_CI_SOGSI_General_Supply_OH.xlsx
Option 1 |  |  |  | 0 | K26 |  |  | 16 | InvestmentSummary_R24_D_CI_SUGSI_General_Supply_UG.xlsx
Option 1 |  |  |  | 0 | K27 |  |  | 17 | InvestmentSummary_R24_D_CI_SUSBD_Subdivision_UG.xlsx
Option 1 |  |  |  | 0 | K28 |  |  | 18 | InvestmentSummary_R24_D_CI_SOSDI_Subdivision_OH.xlsx
Option 1 |  |  |  | 0 | K29 |  |  | 19 | InvestmentSummary_R24_D_CI_SUSUB_Augment_Dist_Substations.xlsx
Option 1 |  |  |  | 0 | K30 |  |  | 20 | InvestmentSummary_R24_T_ND_LAEMP_SELA.xlsx
Option 1 |  |  |  | 0 | K31 |  |  | 21 | InvestmentSummary_R24_D_CA_DESDB_Prelim_Drive_by_Design.xlsx
Option 1 |  |  |  | 0 | K32 |  |  | 22 | InvestmentSummary_R24_D_CI_SUMPR_Major_Commercial.xlsx
Option 1 |  |  |  | 0 | K33 |  |  | 23 | InvestmentSummary_R24_D_CI_EASEN_Easements_Non_Major_Comm.xlsx
| Total | -677.0616 | 100% |  |  |  |  | 24 | InvestmentSummary_R24_D_ND_PRHVR_Rosebery_Supply_Improve.xlsx
[8 empty] | 25 | InvestmentSummary_R24_D_ND_CAHVF_Huonville_Supply_Improvement.xlsx
[8 empty] | 26 | InvestmentSummary_R24_D_ND_CAHVF_Aug_Fdr_Network_Access.xlsx
[8 empty] | 27 | InvestmentSummary_R24_D_ND_PRHVR_Deloraine_Supply_Improve.xlsx
| Option 2 |  |  |  |  | Greater 0 | 1 | 28 | InvestmentSummary_R24_D_ND_CALVF_Augment_LV_Fdr_Capacity.xlsx
| Value Function Measure | Value | Value in % | Greater 0 |  |  |  | 29 | InvestmentSummary_R24_D_ND_CAHVF_Augment_HV_Fdr_Trunk.xlsx
Option 2 | Terminal Value | 1828.7231 | 16.19% | 1 | K20 | Row Labels | Sum of Value in % | 30 | InvestmentSummary_R24_D_ND_CAHVF_Aug_Pole_Mtd_Regulator.xlsx
Option 2 | Network Performance Risk | 4280.0388 | 37.89% | 1 | K21 | Network Performance Risk | 37.89% | 31 | InvestmentSummary_R24_D_ND_CAHVF_Aug_Grnd_Mtd_Regulator.xlsx
Option 2 | Total Investment Cost | -5188.2132 | 45.93% | 1 | K22 | Terminal Value | 16.19% | 32 | InvestmentSummary_R24_D_ND_CAHVF_22kV_Emu_Bay_Feeders.xlsx
Option 2 |  |  |  | 0 | K23 | Total Investment Cost | 45.93% | 33 | InvestmentSummary_R24_D_ND_CAHVF_Augment_HV_Fdr_Capacity.xlsx
Option 2 |  |  |  | 0 | K24 |  |  | 34 | InvestmentSummary_R24_D_ND_CAHVF_Aug_SubStd_Cond_Capacity.xlsx
Option 2 |  |  |  | 0 | K25 |  |  | 35 | InvestmentSummary_R24_D_ND_LANDZ_LandAcq_ZoneSubs.xlsx
Option 2 |  |  |  | 0 | K26 |  |  | 36
Option 2 |  |  |  | 0 | K27 |  |  | 37
Option 2 |  |  |  | 0 | K28 |  |  | 38
Option 2 |  |  |  | 0 | K29 |  |  | 39
Option 2 |  |  |  | 0 | K30 |  |  | 40
Option 2 |  |  |  | 0 | K31 |  |  | 41
Option 2 |  |  |  | 0 | K32 |  |  | 42
Option 2 |  |  |  | 0 | K33 |  |  | 43
| Total | 920.5487 | 100%
| Option 3 |  |  |  |  | Greater 0 | 1
| Value Function Measure | Value | Value in % | Greater 0
Option 3 | Terminal Value | 2122.0221 | 16.4% | 1 | K20 | Row Labels | Sum of Value in %
Option 3 | Financial benefit - OPEX | -1129.4182 | 8.73% | 1 | K21 | Financial benefit - OPEX | 8.73%
Option 3 | Network Performance Risk | 4280.0388 | 33.08% | 1 | K22 | Network Performance Risk | 33.08%
Option 3 | Total Investment Cost | -5406.51 | 41.79% | 1 | K23 | Terminal Value | 16.4%
Option 3 |  |  |  | 0 | K24 | Total Investment Cost | 41.79%
Option 3 |  |  |  | 0 | K25
Option 3 |  |  |  | 0 | K26
Option 3 |  |  |  | 0 | K27
Option 3 |  |  |  | 0 | K28
Option 3 |  |  |  | 0 | K29
Option 3 |  |  |  | 0 | K30
Option 3 |  |  |  | 0 | K31
Option 3 |  |  |  | 0 | K32
Option 3 |  |  |  | 0 | K33
| Total | -133.8674 | 100%
| Option 4 |  |  |  |  | Greater 0 | 1
| Value Function Measure | Value | Value in % | Greater 0
Option 4 | Terminal Value | 559.5566 | 5.77% | 1 | K20 | Row Labels | Sum of Value in %
Option 4 | Financial benefit - OPEX | -2095.0828 | 21.62% | 1 | K21 | Financial benefit - OPEX | 21.62%
Option 4 | Network Performance Risk | 4280.0388 | 44.16% | 1 | K22 | Network Performance Risk | 44.16%
Option 4 | Total Investment Cost | -2757.5708 | 28.45% | 1 | K23 | Terminal Value | 5.77%
Option 4 |  |  |  | 0 | K24 | Total Investment Cost | 28.45%
Option 4 |  |  |  | 0 | K25
Option 4 |  |  |  | 0 | K26
Option 4 |  |  |  | 0 | K27
Option 4 |  |  |  | 0 | K28
Option 4 |  |  |  | 0 | K29
Option 4 |  |  |  | 0 | K30
Option 4 |  |  |  | 0 | K31
Option 4 |  |  |  | 0 | K32
Option 4 |  |  |  | 0 | K33
| Total | -13.0582 | 100%
| Option 5 |  |  |  |  | Greater 0 | 1
| Value Function Measure | Value | Value in % | Greater 0
Option 5 | Terminal Value | 1753.0408 | 19.73% | 1 | K20 | Row Labels | Sum of Value in %
Option 5 | Network Performance Risk | 2203.025 | 24.8% | 1 | K21 | Network Performance Risk | 24.8%
Option 5 | Total Investment Cost | -4928.2838 | 55.47% | 1 | K22 | Terminal Value | 19.73%
Option 5 |  |  |  | 0 | K23 | Total Investment Cost | 55.47%
Option 5 |  |  |  | 0 | K24
Option 5 |  |  |  | 0 | K25
Option 5 |  |  |  | 0 | K26
Option 5 |  |  |  | 0 | K27
Option 5 |  |  |  | 0 | K28
Option 5 |  |  |  | 0 | K29
Option 5 |  |  |  | 0 | K30
Option 5 |  |  |  | 0 | K31
Option 5 |  |  |  | 0 | K32
Option 5 |  |  |  | 0 | K33
| Total | -972.2179 | 100%
| Option 6 |  |  |  |  | Greater 0 | 0
| Value Function Measure | Value | Value in % | Greater 0
Option 6 |  |  |  | 0 | K20 | Row Labels | Sum of Value in %
Option 6 |  |  |  | 0 | K21 |  | 0%
Option 6 |  |  |  | 0 | K22
Option 6 |  |  |  | 0 | K23
Option 6 |  |  |  | 0 | K24
Option 6 |  |  |  | 0 | K25
Option 6 |  |  |  | 0 | K26
Option 6 |  |  |  | 0 | K27
Option 6 |  |  |  | 0 | K28
Option 6 |  |  |  | 0 | K29
Option 6 |  |  |  | 0 | K30
Option 6 |  |  |  | 0 | K31
Option 6 |  |  |  | 0 | K32
Option 6 |  |  |  | 0 | K33
| Total | 0 | 0%

## Summary
Investment Evaluation Summary |  |  |  | Investment Code |  | Report Start Year |  | NPV Period | Base Fiscal Year | Currency Scale
|  |  |  | PRJ000865 |  | 2025 |  | 25 | FY23 | Literal
|  |  |  | Investment Name | [5 empty] | Scenario
|  |  |  | R24_T_ND_AUGSB_W Coast Reliability Improvement | [5 empty] | Approved
Value Function |  | TasNetworks Value Function |  | Version |  | 0.1 |  | Date |  | 2022-10-27
Investment Description
Description |  | Construction of a new 220/22 kV injection point at Pieman switching station. | [9 empty] | TRUE
Functional Area |  | AUGSB |  |  | Department |  |  | System Planning
Works Initiator |  |  |  |  | Portfolio |  |  | Tx - Augmentation
Investment Category |  | Prescribed Services - Augmentation |  |  | Needs Item Reference
Investment Type |  | Network Project |  |  | Document No. |  |  | R0002304380
Investment Stage |  | Gate 2 - Investment Evaluation Summary |  |  | Project Zone Location |  |  | URL Link
PPM ID |  |  |  |  | Regulatory Test Required |  |  | Yes
Investment Summary
Problem Definition |  | The Tasmanian Electricity Code (the Code) infers that TasNetworks must use reasonable endeavours to ensure that unplanned interruptions do not exceed frequency and duration limits. The reliability for this community does not meet its performance requirements, and has consistently failed to do so for at least the past five years. Zeehan is one of seven communities TasNetworks has identified to improve supply reliability performance over the next seven years. TasNetworks has developed a variety of solutions to address reliability performance in this area. One of the most recent reliability improvement initiatives focuses on improving the 44 kV switching arrangement at Renison Bell which aims to improve accessibility and operability of the 44 kV switchgear for safety and operational improvements. Whilst this initiative offers inherent reliability benefits to downstream customers for fault finding activities and for planned outages, it does little to influence overall unplanned outage performance (particularly outage frequency) since only a very small percentage of outages occur on the upstream line section which has full supply diversity. | [9 empty] | TRUE
Recommendation |  | Option 2 is the preferred option. This option yields the highest NPV and comprehensively addresses the problem definition presented previously, when accounting for the combination of capital costs, operation and maintenance and unserved energy costs. Option 2 is a reasonable endeavour to contribute to Zeehan High Density supply reliability community meeting its supply reliability targets set in the Tasmanian Electricity Code and is compatible with future West Coast strategic development requirements. It is recommended that the preferred option, Option 2 is approved and progressed as it best satisfies the customer and business needs. It will contribute to Zeehan High Density supply reliability community meeting its supply reliability targets set in the Tasmanian Electricity Code. | [9 empty] | TRUE
Alternative Spend Profile
Name |  | Status | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV | Alternative Start Date
Option 1: Construct a new 22 kV three-phase line to Zeehan from Strahan |  | Candidate | 0 | 0 | 0 | 0 | 6800000 | 6800000 | 6800000 | -677061.55 | 4693500%
Option 2: Construct a new 220/22 kV injection point at Pieman Switching Station |  | Recommended | 0 | 0 | 0 | 0 | 6208763 | 6208763 | 6208763 | 920548.66 | 4693500%
Option 3: Construct a new 44 kV three-phase line into Trial Harbour Zone sub from Renison Bell |  | Candidate | 0 | 0 | 0 | 0 | 6470000 | 6470000 | 6470000 | -133867.41 | 4693500%
Option 4: Provide diesel generation support to Zeehan township |  | Candidate | 0 | 0 | 0 | 0 | 3300000 | 3300000 | 3300000 | -13058.24 | 4693500%
Option 5: 44/22 kV injection point at Zeehan |  | Candidate | 0 | 0 | 0 | 0 | 5897704 | 5897704 | 5897704 | -972217.9 | 4693500%
0
Leader Endorsement
Name |  |  | Governance |  | Signature |  |  | Comments |  |  | Date
|  |  | Submission | [7 empty] | 4486100%
|  |  | Endorsement | [7 empty] | 4486100%
|  |  | Approval | [7 empty] | 4486100%
Investment Attachments
Date | Attachment Name |  | Description
4485948% | Investment Estimate

## Investment Overview
Investment Evaluation Summary |  | Copperleaf Investment Code |  | Report Start Year | NPV Period | Base Fiscal Year | Currency Scale
|  | PRJ000865 |  | 2025 | 25 | FY23 | Literal
|  | Investment Name |  |  |  |  | Scenario
|  | R24_T_ND_AUGSB_W Coast Reliability Improvement |  |  |  |  | Approved
Value Function | TasNetworks Value Function | Version |  | 0.1 | Date |  | 2022-10-27
Functional Area | AUGSB |  | Department |  | System Planning
Works Initiator |  |  | Portfolio |  | Tx - Augmentation
Investment Category | Prescribed Services - Augmentation |  | Needs Item Reference
Investment Type | Network Project |  | Document No. |  | R0002304380
Investment Stage | Gate 2 - Investment Evaluation Summary |  | Project Zone Location |  | URL Link
PPM ID |  |  | Regulatory Test Required |  | Yes
Investment Overview
01. Overview | Background |  | The township of Zeehan is situated approximately 30 km south-west of Rosebery on the West Coast as shown in Figure 1. Zeehan is a mining township, with many of its residents working at the Renison Bell (Bluestone Mines), Avebury (Mallee Resources) and Commstock (Zeehan Zinc) mines. There are only 630 customers connected in this community, however loading levels are regularly in excess of 20 MVA (or equivalent to 5,000 residential customers in a typical residential network). This is due to the size of the mining loads. Zeehan is supplied by an 8 km overhead 22 kV feeder (99981) from Trial Harbour Zone Substation, which in turn is supplied from a partially redundant 44 kV feeder from Rosebery Substation (97013) approximately 35 km in length. The distribution network traverses heavy terrain where access is limited at various times of the year due to the weather and condition of access tracks. It is subjected to numerous vegetation and major weather-related events which have the tendency to cause lengthy outages. A 44 kV interconnection to an adjacent feeder (97014) exists approximately 10 km electrically from Rosebery at Renison Bell. Whilst this provides partial route diversity, it is not a reliable back-up since the remaining 25 km section remains exposed to outages. Eighty percent of these outages are attributable to weather-related events, with the longer events being caused mostly from vegetation contact (large trees falling across the lines) from outside the clearance zone. When interruptions occur, line crews are dispatched from Queenstown while EHV field operators are required to be dispatched from Burnie which is at least a 1.5-hour drive to Rosebery and a further 30 minutes to Zeehan. The reliability community of Zeehan is classified as High Density Rural meaning its reliability performance measures set by the Tasmanian Electricity Code (the Code) are: - System Average Interruption Frequency Index (SAIFI) – 4 interruptions per year - System Average Interruption Duration Index (SAIDI) – 480 minutes per year Approximately fifty percent of the faults occur on the 44 kV network between Renison Bell and the Zeehan Township, while the remaining fifty percent occur on both 44 and 22 kV network sections between Zeehan and Trial Harbour. Both sections of the route are radial sections without network diversity. |  |  |  |  | TRUE
| Problem Definition |  | The Tasmanian Electricity Code (the Code) infers that TasNetworks must use reasonable endeavours to ensure that unplanned interruptions do not exceed frequency and duration limits. The reliability for this community does not meet its performance requirements, and has consistently failed to do so for at least the past five years. Zeehan is one of seven communities TasNetworks has identified to improve supply reliability performance over the next seven years. TasNetworks has developed a variety of solutions to address reliability performance in this area. One of the most recent reliability improvement initiatives focuses on improving the 44 kV switching arrangement at Renison Bell which aims to improve accessibility and operability of the 44 kV switchgear for safety and operational improvements. Whilst this initiative offers inherent reliability benefits to downstream customers for fault finding activities and for planned outages, it does little to influence overall unplanned outage performance (particularly outage frequency) since only a very small percentage of outages occur on the upstream line section which has full supply diversity. |  |  |  |  | FALSE
02. Customer Needs and Impact | Customer Needs and impact |  | TasNetworks has held a number of customer engagement forums at Zeehan, the most recent of which occurred during July 2022. Community representatives were especially concerned about the duration of outages affecting the township as not all customers were able to be restored during a fault on the main line. TasNetworks has listened to this concern and is currently in the process of providing additional generational support to Zeehan so that all customers will be able to be resupplied under contingency situations, until such time as the longer term solution takes effect. TasNetworks has also engaged with the Reset Advisory Committee (RAC), a committee representing the needs of TasNetworks customers and stakeholders. One of their suggestions was to defer any major network augments (this project) to the end of the regulatory period to allow maximum time for a deployable consumer energy resource (CER) solution to become available (currently TasNetworks has no turn-key deployable solution). TasNetworks has listened to this request and has deferred this project in case a valid non-network solution becomes available. We will continue to monitor Zeehan’s performance and if we are not seeing an improvement with the existing initiatives then we will pursue the long-term transmission preferred solution described in this IES. |  |  |  |  | TRUE

## Objectives and Analysis
Investment Evaluation Summary |  | Copperleaf Investment Code |  | Report Start Year | NPV Period | Base Fiscal Year | Currency Scale
|  | PRJ000865 |  | 2025 | 25 | FY23 | Literal
|  | Investment Name |  |  |  |  | Scenario
|  | R24_T_ND_AUGSB_W Coast Reliability Improvement |  |  |  |  | Approved
Value Function | TasNetworks Value Function | Version |  | 0.1 | Date |  | 2022-10-27
Functional Area | AUGSB |  | Department |  | System Planning
Works Initiator |  |  | Portfolio |  | Tx - Augmentation
Investment Category | Prescribed Services - Augmentation |  | Needs Item Reference
Investment Type | Network Project |  | Document No. |  | R0002304380
Investment Stage | Gate 2 - Investment Evaluation Summary |  | Project Zone Location |  | URL Link
PPM ID |  |  | Regulatory Test Required |  | Yes
Objectives and Analysis
03. Business Performance Objectives | Safety and Wellbeing | [6 empty] | TRUE
| Our Customers |  | Customer net promoter score and customer complaints - Improve customer experience by reducing duration of supply interruptions for identified outages. |  |  |  |  | FALSE
| Our People | [6 empty] | FALSE
| Our Business - Sustained Cost Management | [6 empty] | FALSE
| Our Business - Network Service |  | Outcomes under Service Target Performance Incentive Scheme (STPIS) – transmission and distribution - Improve STPIS returns by bringing poorly performing communities up to regulated performance standards. |  |  |  |  | FALSE
04. Business Risks | Death or Injury (Employee) | [6 empty] | FALSE
| Death or Injury (Public) | [6 empty] | FALSE
| Sustainable and Predictable Pricing | [6 empty] | FALSE
| Widespread Power Disruption |  | Significant outage affecting the Zeehan High Density Rural reliability community |  |  |  |  | FALSE
| Bushfire Start | [6 empty] | FALSE
| Loss of Major Industrial | [6 empty] | FALSE
| Customer Focus |  | Business operations cause events that impact on the customer experience . This leads to material reductions in customer satisfaction and limits our ability to deliver on our customer service strategy, negatively impacting on our vision to be trusted by our customer and create a better tomorrow. Reputation - Some publicity in local and state press, with limited social media coverage, impacting the TasNetworks reputation - Can be managed within the relevant TasNetworks division No material impact on shareholder reputation |  |  |  |  | FALSE
| Business Continuity Management | [6 empty] | FALSE
| Cyber Security | [6 empty] | FALSE
| Private Assets | [6 empty] | FALSE
Energy Policy and Regulation
Project Marinus (D&A)
Tasmanian Power System Complexity
| Emerging Complexity of the NEM | [6 empty] | FALSE
05. Strategic Objectives | Strategic Objectives |  | This project is required to achieve the network capital expenditure objectives. It is required to assist the Zeehan High Density Rural supply reliability community comply with its supply reliability performance for outage duration. It is not required to meet or manage expected demand, nor for the safety of the distribution system through the supply of standard control services |  |  |  |  | FALSE
| Strategic Document #1 | [6 empty] | FALSE
| Strategic Document #2 | [6 empty] | FALSE
| Strategic Document #3 | [6 empty] | FALSE
| Strategic Document #4 | [6 empty] | FALSE
| Strategic Document #5 | [6 empty] | FALSE
06. Project Objectives | Project Objectives |  | The objective of this project is to maintain a long-term, safe and reliable electricity supply into Zeehan and the broader west coast community through prescribed services to: - Manage customer expectations; - Manage risk; and - Meet our reliability requirements. |  |  |  |  | FALSE
07. Options Analysis | Benchmarking |  | A number of other initiatives have been developed to address reliability performance which include: - In-depth reliability study to identify chief outage causes – 2018/19 - Asset upgrade along 44 kV sub-transmission corridor (insulators and defective poles) – 2018/19 - New 44 kV air-break switches – 2018/19 - Substandard services replaced in township to improve LV reliability – 2019/20 - Distance to fault protection relay functionality added at Rosebery Substation to expedite fault response 2019/20 - Spares storage facility installed at Zeehan to facilitate faster fault response – 2019/20 - Additional load break switches installed at Zeehan to improve remote switching and fault indication – 2020/21 - 1 MVA temporary back-up generator system to re-supply Zeehan township (using trailer-mount movable generators) – 2020/21 - High resolution disturbance recorder introduced to Zeehan for post-fault analysis – 2020/21 - Communications network upgrade to Trial Harbour Zone Substation – 2022/23 - Additional temporary generational support project to increase total generation capability to 2.25 MVA, allowing town to be resupplied during winter peak loading period – 2022/23. Following the consistent poor performance and recent customer engagement forums with the west coast community, it became clear that additional measures should be considered to address the reliability issues associated with the 25 km of single-circuit supply into the township. This IES investigates potential options to meet the identified needs. |  |  |  |  | TRUE
| Expert Findings |  | In April 2020 the Zeehan Reliability Improvement Project (this project in its original form) passed through the Gated Investment process and was signed off by the TasNetworks Executive, with the preferred option identified as the installation of a new diesel generation facility at the former Zeehan Zone Substation site (Option 4). However after hearing the community’s concerns at the aforementioned engagement forums and evaluating against the timing of this preferred solution, it was decided that a shorter-term temporary solution was also required to improve the community’s reliability performance. TasNetworks deployed two trailer-mount 500 kVA diesel generators at the Zeehan Township for this purpose to resupply the township until such time as a permanent solution can be deployed. At the time of writing these generators have been successfully commissioned into service, along with a containerised 1.5 MVA substation with associated HV and LV connections, plus over ten dispersed HV load break switches throughout the township. The solution is remotely deployable and the load break switches allow for cold load pickup by segmenting the total load into manageable portions for the generators. However the two available generators are not purpose-built (re-purposed from TasNetworks’ mobile generator fleet) and are limited to servicing the township’s total load requirements for approximately two thirds of the time. These shorter term works were originally developed as a prelude to Option 4 (described below) such that the network augmentations needed to facilitate the short-term solution could then be utilised as part of the final solution. However after TasNetworks progressed the project through the design phase, the detailed estimate was revised, resulting in increased capital costs of the option. This prompted a reassessment of the project’s options which now forms the basis of this revised proposal. TasNetworks considers that the costs attributable to the temporary generator solution are not misplaced as the equipment (excluding the HV load break switches – which are deemed necessary in this remote community regardless of the final solution) is deployable elsewhere in the network. TasNetworks is responsible for the ongoing performance of its reliability in accordance with the Tasmanian Electricity Code. A solution is required to ensure TasNetworks can manage its ongoing supply obligations to its West Coast customers. A long term, sustainable solution is needed. TasNetworks has considered the merits of one non-network solution and four network-based solutions, and now views the network-based options more favourably at this time, mostly due to the level of uncertainty and expense required to implement the non-network solution. |  |  |  |  | FALSE
08. Investment Timing | Investment Timing |  | Zeehan High Density Rural supply reliability community currently does not meet its supply reliability targets. Therefore, this solution will be prioritised to be implemented early in the upcoming 24-29 period. |  |  |  |  | TRUE
09. Expected Outcomes and Benefits | Expected Outcomes and Benefits |  | Following the completion of this project, the benefits to TasNetworks from implementation of the preferred option will be: - The reliability of supply to Zeehan and the wider west coast community would be safeguarded for the medium to longer term; - The site would be compliant with jurisdictional supply/reliability requirements; and - The back-up supply arrangement at Zeehan would no longer be unreliable, unsafe, or resource-intensive. |  |  |  |  | TRUE
10. Assumptions | Assumptions |  | No particular assumptions were used in undertaking in the analysis that may affect the outcome of the outcome of this investment evaluation summary. |  |  |  |  | TRUE
11. Regulatory Considerations | Regulatory Investment Test |  | Accounting for cost escalation sensitivities, it is reasonable to assume that the most expensive, credible option will continue to exceed the $6 million cost threshold once project cost estimates progress through to business case. Initiation of a RIT-D for this project will be subject to further cost optimisation and bottom up analysis.
| Meet or manage the expected demand for Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | No
| Comply with all applicable regulatory obligations associated with the provision of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
| Maintain the quality, reliability and security of supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
| Maintain the reliability and security of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | No
| Maintain the safety of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | No
12. Recommendation | Recommendation |  | Option 2 is the preferred option. This option yields the highest NPV and comprehensively addresses the problem definition presented previously, when accounting for the combination of capital costs, operation and maintenance and unserved energy costs. Option 2 is a reasonable endeavour to contribute to Zeehan High Density supply reliability community meeting its supply reliability targets set in the Tasmanian Electricity Code and is compatible with future West Coast strategic development requirements. It is recommended that the preferred option, Option 2 is approved and progressed as it best satisfies the customer and business needs. It will contribute to Zeehan High Density supply reliability community meeting its supply reliability targets set in the Tasmanian Electricity Code. |  |  |  |  | TRUE

## Economic Analysis
alternative
| Investment Evaluation Summary |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[5 empty] | PRJ000865 |  | 2025 |  | 25 | FY23 | Literal
[5 empty] | Investment Name | [5 empty] | Scenario
[5 empty] | R24_T_ND_AUGSB_W Coast Reliability Improvement | [5 empty] | Approved
autofit | Value Function |  |  | TasNetworks Value Function | Version |  | 0.1 |  | Date |  | 2022-10-27
Economic Analysis
| Parameter |  |  |  | Value | Unit | Source of Values
75679 | NPV Period |  |  |  | 25 | Years | TasNetworks requirement
autofit | First Fiscal Year of Forecast |  |  |  | FY23 | - | TasNetworks requirement
| Weighted Average Cost of Capital (WACC) |  |  |  | 2.82 | % | 2019-24 Revenue determination and ISP 2022 draft data
| Voluntary load shedding assumed? |  |  |  | No | - | N/A
| Reduction in system losses considered? |  |  |  | No | - | N/A
| Value of Customer Reliability applied |  |  | Very large business customer - Services | 10.93 | $/kWh | Weighted VCR - Weighting information is based on whole state one year data (received 14/07/2021)
|  |  |  | User Specified | 32.3 | $/kWh
|  |  |  | Residential | 17.08 | $/kWh
|  |  |  | Very large business customer - Metals | 20.6 | $/kWh
|  |  |  | Very large business customer - Transmission | 27.43 | $/kWh
|  |  |  | Very large business customer - Mines | 36.47 | $/kWh
|  |  |  | Business customer - Agricultural | 39.28 | $/kWh
|  |  |  | Business customer - Commercial | 46.18 | $/kWh
|  |  |  | Very large business customer - Distribution | 58.8 | $/kWh
|  |  |  | Business customer - Industrial | 66.16 | $/kWh
autofit |  |  |  | Very large business customer - Industrial | 122.39 | $/kWh
Sensitivity to Project Timing
|  | 1 | Navigate to Copperleaf Portfolio and search for your Investment
|  | 2 | Navigate to the Value Comparison Page for your Investment through the breadcrumb menu
|  | 3 | Once on the Value Comparison Page, select "Value by Start Date" in the drop-down menu in the top-left corner of the page
|  | 4 | This screen will show the value change over time for each option in your investment
|  | 5 | With the snipping tool on your PC, take a screenshot of the chart and copy + paste it in this section of the report
Options Considered
| Options Summary |  |  |  | R24 Expenditure ($M) | NPV ($M) | Preferred Option | Reason for selection/rejection
| Option 1: Construct a new 22 kV three-phase line to Zeehan from Strahan |  |  |  | 6.8 | -0.67706 | No | Rejected due to the level of expenditure involved to fully mitigate risk (delivers lower benefit at lower cost).
| Option 2: Construct a new 220/22 kV injection point at Pieman Switching Station |  |  |  | 6.2088 | 0.92055 | Yes | Selected – has reliable impact to SAIFI, meets the problem definition, contributing to Zeehan High Density supply reliability community meeting its supply reliability targets set in the Tasmanian Electricity Code.
| Option 3: Construct a new 44 kV three-phase line into Trial Harbour Zone sub from Renison Bell |  |  |  | 6.47 | -0.13387 | No | Rejected due to the level of expenditure involved to manage risk. Requires additional investment to that stated to achieve the same reliability benefit as Preferred Option.
| Option 4: Provide diesel generation support to Zeehan township |  |  |  | 3.3 | -0.013058 | No | This option does not align with customer expectations. Additionally this option is outside TasNetworks’ risk appetite.
| Option 5: 44/22 kV injection point at Zeehan |  |  |  | 5.8977 | -0.97222 | No | Rejected due to the level of expenditure involved to fully mitigate risk (delivers lower benefit at lower cost)
0
NPV Components

## Needs Assessment (hidden)
Needs Assessment Form |  | Copperleaf Investment Code |  | Report Start Year | NPV Period | Base Fiscal Year | Currency Scale
|  | PRJ000865 |  | 2025 | 25 | FY23 | Literal
|  | Investment Name |  |  |  |  | Scenario
|  | R24_T_ND_AUGSB_W Coast Reliability Improvement |  |  |  |  | Approved
Value Function | TasNetworks Value Function | Version |  | 0.1 | Date |  | 2022-10-27
Functional Area | AUGSB |  | Department |  | System Planning
Works Initiator |  |  | Portfolio |  | Tx - Augmentation
Investment Category | Prescribed Services - Augmentation |  | Needs Item Reference
Investment Type | Network Project |  | Document No. |  | R0002304380
Investment Stage | Gate 2 - Investment Evaluation Summary |  | Project Zone Location
PPM ID |  |  | Regulatory Test Required |  | Yes
Investment Overview
01. Overview | Background |  | The township of Zeehan is situated approximately 30 km south-west of Rosebery on the West Coast as shown in Figure 1. Zeehan is a mining township, with many of its residents working at the Renison Bell (Bluestone Mines), Avebury (Mallee Resources) and Commstock (Zeehan Zinc) mines. There are only 630 customers connected in this community, however loading levels are regularly in excess of 20 MVA (or equivalent to 5,000 residential customers in a typical residential network). This is due to the size of the mining loads. Zeehan is supplied by an 8 km overhead 22 kV feeder (99981) from Trial Harbour Zone Substation, which in turn is supplied from a partially redundant 44 kV feeder from Rosebery Substation (97013) approximately 35 km in length. The distribution network traverses heavy terrain where access is limited at various times of the year due to the weather and condition of access tracks. It is subjected to numerous vegetation and major weather-related events which have the tendency to cause lengthy outages. A 44 kV interconnection to an adjacent feeder (97014) exists approximately 10 km electrically from Rosebery at Renison Bell. Whilst this provides partial route diversity, it is not a reliable back-up since the remaining 25 km section remains exposed to outages. Eighty percent of these outages are attributable to weather-related events, with the longer events being caused mostly from vegetation contact (large trees falling across the lines) from outside the clearance zone. When interruptions occur, line crews are dispatched from Queenstown while EHV field operators are required to be dispatched from Burnie which is at least a 1.5-hour drive to Rosebery and a further 30 minutes to Zeehan. The reliability community of Zeehan is classified as High Density Rural meaning its reliability performance measures set by the Tasmanian Electricity Code (the Code) are: - System Average Interruption Frequency Index (SAIFI) – 4 interruptions per year - System Average Interruption Duration Index (SAIDI) – 480 minutes per year Approximately fifty percent of the faults occur on the 44 kV network between Renison Bell and the Zeehan Township, while the remaining fifty percent occur on both 44 and 22 kV network sections between Zeehan and Trial Harbour. Both sections of the route are radial sections without network diversity. |  |  |  |  | TRUE
| Problem Definition |  | The Tasmanian Electricity Code (the Code) infers that TasNetworks must use reasonable endeavours to ensure that unplanned interruptions do not exceed frequency and duration limits. The reliability for this community does not meet its performance requirements, and has consistently failed to do so for at least the past five years. Zeehan is one of seven communities TasNetworks has identified to improve supply reliability performance over the next seven years. TasNetworks has developed a variety of solutions to address reliability performance in this area. One of the most recent reliability improvement initiatives focuses on improving the 44 kV switching arrangement at Renison Bell which aims to improve accessibility and operability of the 44 kV switchgear for safety and operational improvements. Whilst this initiative offers inherent reliability benefits to downstream customers for fault finding activities and for planned outages, it does little to influence overall unplanned outage performance (particularly outage frequency) since only a very small percentage of outages occur on the upstream line section which has full supply diversity. |  |  |  |  | FALSE
02. Customer Needs and Impact | Customer Needs and impact |  | TasNetworks has held a number of customer engagement forums at Zeehan, the most recent of which occurred during July 2022. Community representatives were especially concerned about the duration of outages affecting the township as not all customers were able to be restored during a fault on the main line. TasNetworks has listened to this concern and is currently in the process of providing additional generational support to Zeehan so that all customers will be able to be resupplied under contingency situations, until such time as the longer term solution takes effect. TasNetworks has also engaged with the Reset Advisory Committee (RAC), a committee representing the needs of TasNetworks customers and stakeholders. One of their suggestions was to defer any major network augments (this project) to the end of the regulatory period to allow maximum time for a deployable consumer energy resource (CER) solution to become available (currently TasNetworks has no turn-key deployable solution). TasNetworks has listened to this request and has deferred this project in case a valid non-network solution becomes available. We will continue to monitor Zeehan’s performance and if we are not seeing an improvement with the existing initiatives then we will pursue the long-term transmission preferred solution described in this IES. |  |  |  |  | TRUE
03. Business Objectives | Business Objectives
04. Project Objectives | Project Objectives |  | The objective of this project is to maintain a long-term, safe and reliable electricity supply into Zeehan and the broader west coast community through prescribed services to: - Manage customer expectations; - Manage risk; and - Meet our reliability requirements. |  |  |  |  | FALSE
05. Risk Objective | Risk if not progressed | [6 empty] | TRUE
06. Investment Timing | Investment Timing |  | Zeehan High Density Rural supply reliability community currently does not meet its supply reliability targets. Therefore, this solution will be prioritised to be implemented early in the upcoming 24-29 period. |  |  |  |  | TRUE
07. Business Consulatation | Business Consulatation | [6 empty] | TRUE

## Option 1
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000865 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_T_ND_AUGSB_W Coast Reliability Improvement | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-27
Alternative Overview
75679 | Alternative Name |  | Option 1: Construct a new 22 kV three-phase line to Zeehan from Strahan
autofit | Description |  | A new 22 kV line would be constructed between Strahan and Zeehan predominantly following Henty Road, a distance of approximately 40 km. This option will provide a second feeder supply to Zeehan.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4693500%
| Reason for selection/rejection |  | Rejected due to the level of expenditure involved to fully mitigate risk (delivers lower benefit at lower cost).
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Option 1: Construct a new 22 kV three-phase line to Zeehan from Strahan |  | Capex |  |  | 0 | 0 | 0 | 0 | 6800000 | 6800000 | 6800000 | -677061.55
|  |  | Opex |  |  | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Terminal Value |  |  | 2230.255 | 16.28%
[9 empty] | Financial benefit - OPEX |  |  | -1505.0882 | 10.99%
[9 empty] | Network Performance Risk |  |  | 4280.0388 | 31.25%
[9 empty] | Total Investment Cost |  |  | -5682.2671 | 41.48%
[9 empty] | Total |  |  | -677.0616
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Financial Benefits & Costs | Financial benefit - OPEX |  | Outcome | 2029 | -1505.0882 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2028 | 0 | Dollar | 0 | 0 | 0 | 0 | 6800000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | OPEX Cost |  | Outcome |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2028 | -5682.2671 | Dollar | 0 | 0 | 0 | 0 | 6800000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | Network Performance | Network Performance Risk |  | Baseline |  | 0 | Dollar | 511632 | 511632 | 511632 | 511632 | 511632
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | Network Performance | Network Performance Risk |  | Outcome | 2022 | 4280.0388 | Dollar | 511632 | 511632 | 511632 | 511632 | 511632
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | Terminal Value | Terminal Value |  | Outcome | 2048 | 2230.255 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 511632 | 511632 | 511632 | 511632 | 511632
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 511632 | 511632 | 511632 | 511632 | 511632
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 2
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000865 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_T_ND_AUGSB_W Coast Reliability Improvement | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-27
Alternative Overview
75679 | Alternative Name |  | Option 2: Construct a new 220/22 kV injection point at Pieman Switching Station
autofit | Description |  | A new 220/22 kV transformer with associated switchgear would be installed at the Pieman Switching Station site near Reece Power Station and a 22 kV interconnection would be established with the existing feeder from Trial Harbour following Heemskirk Road (Feeder 99981). This option will provide a second, diverse feeder supply to Zeehan.
autofit | Alternative Status |  | Recommended
autofit | Alternative Start Date |  | 4693500%
| Reason for selection/rejection |  | Selected – has reliable impact to SAIFI, meets the problem definition, contributing to Zeehan High Density supply reliability community meeting its supply reliability targets set in the Tasmanian Electricity Code.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Option 2: Construct a new 220/22 kV injection point at Pieman Switching Station |  | Capex |  |  | 0 | 0 | 0 | 0 | 6208763 | 6208763 | 6208763 | 920548.66
|  |  | Opex |  |  | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Terminal Value |  |  | 1828.7231 | 16.19%
[9 empty] | Network Performance Risk |  |  | 4280.0388 | 37.89%
[9 empty] | Total Investment Cost |  |  | -5188.2132 | 45.93%
[9 empty] | Total |  |  | 920.5487
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2028 | 0 | Dollar | 0 | 0 | 0 | 0 | 6208763
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | OPEX Cost |  | Outcome |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2028 | -5188.2132 | Dollar | 0 | 0 | 0 | 0 | 6208763
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Network Performance | Network Performance Risk |  | Baseline |  | 0 | Dollar | 511632 | 511632 | 511632 | 511632 | 511632
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | Network Performance | Network Performance Risk |  | Outcome | 2022 | 4280.0388 | Dollar | 511632 | 511632 | 511632 | 511632 | 511632
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 1828.7231 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 511632 | 511632 | 511632 | 511632 | 511632
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 511632 | 511632 | 511632 | 511632 | 511632
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 3
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000865 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_T_ND_AUGSB_W Coast Reliability Improvement | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-27
Alternative Overview
75679 | Alternative Name |  | Option 3: Construct a new 44 kV three-phase line into Trial Harbour Zone sub from Renison Bell
autofit | Description |  | Build a new 44 kV three-phase line (Feeder 97014 extension) from Renison Bell to Trial Harbour Zone Substation which follows the existing roadway, a distance of approximately 25 km, to allow dual 44 kV sub-transmission circuits to supply Trial Harbour Zone Substation. This solution requires modifications to Trial Harbour 44 kV bus to provide sectionalising and connectivity to Renison Bell 44 kV interface.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4693500%
| Reason for selection/rejection |  | Rejected due to the level of expenditure involved to manage risk. Requires additional investment to that stated to achieve the same reliability benefit as Preferred Option.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Option 3: Construct a new 44 kV three-phase line into Trial Harbour Zone sub from Renison Bell |  | Capex |  |  | 0 | 0 | 0 | 0 | 6470000 | 6470000 | 6470000 | -133867.41
|  |  | Opex |  |  | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Terminal Value |  |  | 2122.0221 | 16.4%
[9 empty] | Financial benefit - OPEX |  |  | -1129.4182 | 8.73%
[9 empty] | Network Performance Risk |  |  | 4280.0388 | 33.08%
[9 empty] | Total Investment Cost |  |  | -5406.51 | 41.79%
[9 empty] | Total |  |  | -133.8674
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Financial Benefits & Costs | Financial benefit - OPEX |  | Outcome | 2029 | -1129.4182 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2028 | 0 | Dollar | 0 | 0 | 0 | 0 | 6470000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | OPEX Cost |  | Outcome |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2028 | -5406.51 | Dollar | 0 | 0 | 0 | 0 | 6470000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | Network Performance | Network Performance Risk |  | Baseline |  | 0 | Dollar | 511632 | 511632 | 511632 | 511632 | 511632
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | Network Performance | Network Performance Risk |  | Outcome | 2022 | 4280.0388 | Dollar | 511632 | 511632 | 511632 | 511632 | 511632
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | Terminal Value | Terminal Value |  | Outcome | 2048 | 2122.0221 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 511632 | 511632 | 511632 | 511632 | 511632
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 511632 | 511632 | 511632 | 511632 | 511632
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 4
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000865 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_T_ND_AUGSB_W Coast Reliability Improvement | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-27
Alternative Overview
75679 | Alternative Name |  | Option 4: Provide diesel generation support to Zeehan township
autofit | Description |  | Build a new semi-permanent diesel generation facility at the former Zeehan Zone Substation site (which is in the Zeehan township) capable of re-supplying Zeehan and Granville Harbour for an outage of the existing feeder.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4693500%
| Reason for selection/rejection |  | This option does not align with customer expectations. Additionally this option is outside TasNetworks’ risk appetite.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Option 4: Provide diesel generation support to Zeehan township |  | Capex |  |  | 0 | 0 | 0 | 0 | 3300000 | 3300000 | 3300000 | -13058.24
|  |  | Opex |  |  | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Terminal Value |  |  | 559.5566 | 5.77%
[9 empty] | Financial benefit - OPEX |  |  | -2095.0828 | 21.62%
[9 empty] | Network Performance Risk |  |  | 4280.0388 | 44.16%
[9 empty] | Total Investment Cost |  |  | -2757.5708 | 28.45%
[9 empty] | Total |  |  | -13.0582
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Financial Benefits & Costs | Financial benefit - OPEX |  | Outcome | 2029 | -2095.0828 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2028 | 0 | Dollar | 0 | 0 | 0 | 0 | 3300000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | OPEX Cost |  | Outcome |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2028 | -2757.5708 | Dollar | 0 | 0 | 0 | 0 | 3300000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | Network Performance | Network Performance Risk |  | Baseline |  | 0 | Dollar | 511632 | 511632 | 511632 | 511632 | 511632
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | Network Performance | Network Performance Risk |  | Outcome | 2022 | 4280.0388 | Dollar | 511632 | 511632 | 511632 | 511632 | 511632
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | Terminal Value | Terminal Value |  | Outcome | 2048 | 559.5566 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 511632 | 511632 | 511632 | 511632 | 511632
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 511632 | 511632 | 511632 | 511632 | 511632
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 5
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000865 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_T_ND_AUGSB_W Coast Reliability Improvement | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-27
Alternative Overview
75679 | Alternative Name |  | Option 5: 44/22 kV injection point at Zeehan
autofit | Description |  | This option involves establishing a new 44 / 22 kV supply at Zeehan. This will be achieved by installing a new 44 /22 kV transformer with a teed connection to feeder 97013 at Zeehan. A new load break switch installed downstream to the transformer tee, in conjunction with fault passage indicators will initially allow faster supply restoration to Zeehan and Trial Harbour loads by isolating the faulted section between the tee and Trail Harbor, which is one of the identified, low reliability sections. The second stage of works consists of a 44 kV feeder extension from Renison Bell to the Zeehan tee downstream of the load break switch. By then operating the load break switch normally open, a diverse supply path is provided by feeder 97013 from Rosebery to Zeehan.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4693500%
| Reason for selection/rejection |  | Rejected due to the level of expenditure involved to fully mitigate risk (delivers lower benefit at lower cost)
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Option 5: 44/22 kV injection point at Zeehan |  | Capex |  |  | 0 | 0 | 0 | 0 | 5897704 | 5897704 | 5897704 | -972217.9
|  |  | Opex |  |  | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Terminal Value |  |  | 1753.0408 | 19.73%
[9 empty] | Network Performance Risk |  |  | 2203.025 | 24.8%
[9 empty] | Total Investment Cost |  |  | -4928.2838 | 55.47%
[9 empty] | Total |  |  | -972.2179
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2028 | 0 | Dollar | 0 | 0 | 0 | 0 | 5897704
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | OPEX Cost |  | Outcome |  | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2028 | -4928.2838 | Dollar | 0 | 0 | 0 | 0 | 5897704
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Network Performance | Network Performance Risk |  | Baseline |  | 0 | Dollar | 511632 | 511632 | 511632 | 511632 | 511632
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | Network Performance | Network Performance Risk |  | Outcome | 2022 | 2203.025 | Dollar | 511632 | 511632 | 511632 | 511632 | 511632
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 1753.0408 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 511632 | 511632 | 511632 | 511632 | 511632
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 511632 | 511632 | 511632 | 511632 | 511632
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 6 (hidden)
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000865 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_T_ND_AUGSB_W Coast Reliability Improvement | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-27
Alternative Overview
75679 | Alternative Name
autofit | Description
autofit | Alternative Status
autofit | Alternative Start Date
Reason for selection/rejection
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
0
0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Total |  |  | 0
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 0 | 0 | 0 | 0 | 0
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## TextFormatting (hidden)
Index | 8
Column Width | 238
Font | Calibri
Font Size | 11
Font Colour
Text | Sheet | Group | Field | Row Height | Row Number
| Investment Summary | Header | Description | 15 | 9
The township of Zeehan is situated approximately 30 km south-west of Rosebery on the West Coast as shown in Figure 1. Zeehan is a mining township, with many of its residents working at the Renison Bell (Bluestone Mines), Avebury (Mallee Resources) and Commstock (Zeehan Zinc) mines. There are only 630 customers connected in this community, however loading levels are regularly in excess of 20 MVA (or equivalent to 5,000 residential customers in a typical residential network). This is due to the size of the mining loads, one of which is the largest single distribution network-connected customer with a contracted demand in excess of 18 MVA. Zeehan is supplied by an 8 km overhead 22 kV feeder (99981) from Trial Harbour Zone Substation, which in turn is supplied from a partially redundant 44 kV feeder from Rosebery Substation (97013) approximately 35 km in length. The distribution network traverses heavy terrain where access is limited at various times of the year due to the weather and condition of access tracks. It is subjected to numerous vegetation and major weather-related events which have the tendency to cause lengthy outages. A 44 kV interconnection to an adjacent feeder (97014) exists approximately 10 km electrically from Rosebery at Renison Bell. Whilst this provides partial route diversity, it is not a reliable back-up since the remaining 25 km section remains exposed to outages. Eighty percent of these outages are attributable to weather-related events, with the longer events being caused mostly from vegetation contact (large trees falling across the lines) from outside the clearance zone. When interruptions occur, line crews are dispatched from Queenstown while EHV field operators are required to be dispatched from Burnie which is at least a 1.5-hour drive to Rosebery and a further 30 minutes to Zeehan. The reliability community of Zeehan is classified as High Density Rural meaning its reliability performance measures set by the Tasmanian Electricity Code (the Code) are: - System Average Interruption Frequency Index (SAIFI) – 4 interruptions per year - System Average Interruption Duration Index (SAIDI) – 480 minutes per year Approximately fifty percent of the faults occur on the 44 kV network between Renison Bell and the Zeehan Township, while the remaining fifty percent occur on both 44 and 22 kV network sections between Zeehan and Trial Harbour. Both sections of the route are radial sections without network diversity. | Investment Summary | 0.1 Overview | Background | 375 | 16
The Tasmanian Electricity Code (the Code) infers that TasNetworks must use reasonable endeavours to ensure that unplanned interruptions do not exceed frequency and duration limits. The reliability for this community does not meet its performance requirements, and has consistently failed to do so for at least the past five years. Zeehan is one of seven communities TasNetworks has identified to improve supply reliability performance over the next seven years. TasNetworks has developed a variety of solutions to address reliability performance in this area. One of the most recent reliability improvement initiatives focuses on improving the 44 kV switching arrangement at Renison Bell which aims to improve accessibility and operability of the 44 kV switchgear for safety and operational improvements. Whilst this initiative offers inherent reliability benefits to downstream customers for fault finding activities and for planned outages, it does little to influence overall unplanned outage performance (particularly outage frequency) since only a very small percentage of outages occur on the upstream line section which has full supply diversity. | Investment Summary | 0.1 Overview | Problem Definition | 180 | 17
TasNetworks has held a number of customer engagement forums at Zeehan, the most recent of which occurred during July 2022. Community representatives were especially concerned about the duration of outages affecting the township as not all customers were able to be restored during a fault on the main line. TasNetworks has listened to this concern and is currently in the process of providing additional generational support to Zeehan so that all customers will be able to be resupplied under contingency situations, until such time as the longer term solution takes effect. TasNetworks has also engaged with the Reset Advisory Committee (RAC), a committee representing the needs of TasNetworks customers and stakeholders. One of their suggestions was to defer any major network augments (this project) to the end of the regulatory period to allow maximum time for a deployable consumer energy resource (CER) solution to become available (currently TasNetworks has no turn-key deployable solution). TasNetworks has listened to this request and has deferred this project in case a valid non-network solution becomes available. We will continue to monitor Zeehan’s performance and if we are not seeing an improvement with the existing initiatives then we will pursue the long-term transmission preferred solution described in this IES. | Investment Summary | 02. Customer Needs and Impact | Customer Needs and impact | 180 | 18
| Objectives and Analysis | 03. Business Performance Objectives | Safety and Wellbeing | 15 | 17
Customer net promoter score and customer complaints - Improve customer experience by reducing duration of supply interruptions for identified outages. | Objectives and Analysis | 03. Business Performance Objectives | Our Customers | 30 | 18
| Objectives and Analysis | 03. Business Performance Objectives | Our People | 15 | 19
| Objectives and Analysis | 03. Business Performance Objectives | Our Business - Sustained Cost Management | 15 | 20
Outcomes under Service Target Performance Incentive Scheme (STPIS) – transmission and distribution - Improve STPIS returns by bringing poorly performing communities up to regulated performance standards. | Objectives and Analysis | 03. Business Performance Objectives | Our Business - Network Service | 30 | 21
| Objectives and Analysis | 04. Business Risks | Death or Injury (Employee) | 15 | 23
| Objectives and Analysis | 04. Business Risks | Death or Injury (Public) | 15 | 24
| Objectives and Analysis | 04. Business Risks | Sustainable and Predictable Pricing | 15 | 25
Significant outage affecting the Zeehan High Density Rural reliability community | Objectives and Analysis | 04. Business Risks | Widespread Power Disruption | 15 | 26
| Objectives and Analysis | 04. Business Risks | Bushfire Start | 15 | 27
| Objectives and Analysis | 04. Business Risks | Loss of Major Industrial | 15 | 28
Business operations cause events that impact on the customer experience . This leads to material reductions in customer satisfaction and limits our ability to deliver on our customer service strategy, negatively impacting on our vision to be trusted by our customer and create a better tomorrow. Reputation - Some publicity in local and state press, with limited social media coverage, impacting the TasNetworks reputation - Can be managed within the relevant TasNetworks division No material impact on shareholder reputation | Objectives and Analysis | 04. Business Risks | Customer Focus | 135 | 29
| Objectives and Analysis | 04. Business Risks | Business Continuity Management | 15 | 30
| Objectives and Analysis | 04. Business Risks | Cyber Security | 15 | 31
| Objectives and Analysis | 04. Business Risks | Private Assets | 15 | 32
| Objectives and Analysis | 04. Business Risks | Energy Policy and Regulation | 15 | 33
| Objectives and Analysis | 04. Business Risks | Project Marinus (D&A) | 15 | 34
| Objectives and Analysis | 04. Business Risks | Tasmanian Power System Complexity | 15 | 35
| Objectives and Analysis | 04. Business Risks | Emerging Complexity of the NEM | 15 | 36
This project is required to achieve the network capital expenditure objectives. It is required to assist the Zeehan High Density Rural supply reliability community comply with its supply reliability performance for outage duration. It is not required to meet or manage expected demand, nor for the safety of the distribution system through the supply of standard control services | Objectives and Analysis | 05. Strategic Objectives | Strategic Objectives | 60 | 38
| Objectives and Analysis | 05. Strategic Objectives | Strategic Document #1 | 15 | 39
| Objectives and Analysis | 05. Strategic Objectives | Strategic Document #2 | 15 | 40
| Objectives and Analysis | 05. Strategic Objectives | Strategic Document #3 | 15 | 41
| Objectives and Analysis | 05. Strategic Objectives | Strategic Document #4 | 15 | 42
| Objectives and Analysis | 05. Strategic Objectives | Strategic Document #5 | 15 | 43
The objective of this project is to maintain a long-term, safe and reliable electricity supply into Zeehan and the broader west coast community through prescribed services to: - Manage customer expectations; - Manage risk; and - Meet our reliability requirements. | Objectives and Analysis | 06. Project Objectives | Project Objectives | 75 | 44
A number of other initiatives have been developed to address reliability performance which include: - In-depth reliability study to identify chief outage causes – 2018/19 - Asset upgrade along 44 kV sub-transmission corridor (insulators and defective poles) – 2018/19 - New 44 kV air-break switches – 2018/19 - Substandard services replaced in township to improve LV reliability – 2019/20 - Distance to fault protection relay functionality added at Rosebery Substation to expedite fault response 2019/20 - Spares storage facility installed at Zeehan to facilitate faster fault response – 2019/20 - Additional load break switches installed at Zeehan to improve remote switching and fault indication – 2020/21 - 1 MVA temporary back-up generator system to re-supply Zeehan township (using trailer-mount movable generators) – 2020/21 - High resolution disturbance recorder introduced to Zeehan for post-fault analysis – 2020/21 - Communications network upgrade to Trial Harbour Zone Substation – 2022/23 - Additional temporary generational support project to increase total generation capability to 2.25 MVA, allowing town to be resupplied during winter peak loading period – 2022/23. Following the consistent poor performance and recent customer engagement forums with the west coast community, it became clear that additional measures should be considered to address the reliability issues associated with the 25 km of single-circuit supply into the township. This IES investigates potential options to meet the identified needs. | Objectives and Analysis | 07. Options Analysis | Benchmarking | 300 | 45
In April 2020 the Zeehan Reliability Improvement Project (this project in its original form) passed through the Gated Investment process and was signed off by the TasNetworks Executive, with the preferred option identified as the installation of a new diesel generation facility at the former Zeehan Zone Substation site (Option 4). However after hearing the community’s concerns at the aforementioned engagement forums and evaluating against the timing of this preferred solution, it was decided that a shorter-term temporary solution was also required to improve the community’s reliability performance. TasNetworks deployed two trailer-mount 500 kVA diesel generators at the Zeehan Township for this purpose to resupply the township until such time as a permanent solution can be deployed. At the time of writing these generators have been successfully commissioned into service, along with a containerised 1.5 MVA substation with associated HV and LV connections, plus over ten dispersed HV load break switches throughout the township. The solution is remotely deployable and the load break switches allow for cold load pickup by segmenting the total load into manageable portions for the generators. However the two available generators are not purpose-built (re-purposed from TasNetworks’ mobile generator fleet) and are limited to servicing the township’s total load requirements for approximately two thirds of the time. These shorter term works were originally developed as a prelude to Option 4 (described below) such that the network augmentations needed to facilitate the short-term solution could then be utilised as part of the final solution. However after TasNetworks progressed the project through the design phase, the detailed estimate was revised, resulting in increased capital costs of the option. This prompted a reassessment of the project’s options which now forms the basis of this revised proposal. TasNetworks considers that the costs attributable to the temporary generator solution are not misplaced as the equipment (excluding the HV load break switches – which are deemed necessary in this remote community regardless of the final solution) is deployable elsewhere in the network. TasNetworks is responsible for the ongoing performance of its reliability in accordance with the Tasmanian Electricity Code. A solution is required to ensure TasNetworks can manage its ongoing supply obligations to its West Coast customers. A long term, sustainable solution is needed. TasNetworks has considered the merits of one non-network solution and four network-based solutions, and now views the network-based options more favourably at this time, mostly due to the level of uncertainty and expense required to implement the non-network solution. | Objectives and Analysis | 07. Options Analysis | Expert Findings | 405 | 46
Zeehan High Density Rural supply reliability community currently does not meet its supply reliability targets. Therefore, this solution will be prioritised to be implemented early in the upcoming 24-29 period. | Objectives and Analysis | 08. Investment Timing | Investment Timing | 30 | 47
Following the completion of this project, the benefits to TasNetworks from implementation of the preferred option will be: - The reliability of supply to Zeehan and the wider west coast community would be safeguarded for the medium to longer term; - The site would be compliant with jurisdictional supply/reliability requirements; and - The back-up supply arrangement at Zeehan would no longer be unreliable, unsafe, or resource-intensive. | Objectives and Analysis | 09. Expected Outcomes and Benefits | Expected Outcomes and Benefits | 90 | 48
No particular assumptions were used in undertaking in the analysis that may affect the outcome of the outcome of this investment evaluation summary. | Objectives and Analysis | 10. Assumptions | Assumptions | 30 | 49
Accounting for cost escalation sensitivities, it is reasonable to assume that the most expensive, credible option will continue to exceed the $6 million cost threshold once project cost estimates progress through to business case. Initiation of a RIT-D for this project will be subject to further cost optimisation and bottom up analysis. | Objectives and Analysis | 11. Regulatory Considerations | Regulatory Investment Test | 45 | 50
No | Objectives and Analysis | 11. Regulatory Considerations | Meet or manage the expected demand for Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 51
Yes | Objectives and Analysis | 11. Regulatory Considerations | Comply with all applicable regulatory obligations associated with the provision of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 52
Yes | Objectives and Analysis | 11. Regulatory Considerations | Maintain the quality, reliability and security of supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 53
No | Objectives and Analysis | 11. Regulatory Considerations | Maintain the reliability and security of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 54
No | Objectives and Analysis | 11. Regulatory Considerations | Maintain the safety of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 55
Option 2 is the preferred option. Although this option yields the highest NPV, it comprehensively addresses the problem definition presented previously, when accounting for the combination of capital costs, operation and maintenance and unserved energy costs. Option 5, whilst yielding a marginally higher NPV, results in residual risk and unserved energy to the network. Option 2 is a reasonable endeavour to contribute to Zeehan High Density supply reliability community meeting its supply reliability targets set in the Tasmanian Electricity Code and is compatible with future West Coast strategic development requirements. It is recommended that the preferred option, Option 2 is approved and progressed as it best satisfies the customer and business needs. It will contribute to Zeehan High Density supply reliability community meeting its supply reliability targets set in the Tasmanian Electricity Code. | Objectives and Analysis | 12. Recommendation | Recommendation | 150 | 56
A new 22 kV line would be constructed between Strahan and Zeehan predominantly following Henty Road, a distance of approximately 40 km. This option will provide a second feeder supply to Zeehan. | Option 1 | Description |  | 15
Rejected due to the level of expenditure involved to fully mitigate risk (delivers lower benefit at lower cost). | Option 1 | Reason for selection/rejection |  | 15
A new 220/22 kV transformer with associated switchgear would be installed at the Pieman Switching Station site near Reece Power Station and a 22 kV interconnection would be established with the existing feeder from Trial Harbour following Heemskirk Road (Feeder 99981). This option will provide a second, diverse feeder supply to Zeehan. | Option 2 | Description |  | 30
Selected – has reliable impact to SAIFI, meets the problem definition, contributing to Zeehan High Density supply reliability community meeting its supply reliability targets set in the Tasmanian Electricity Code. | Option 2 | Reason for selection/rejection |  | 15
Build a new 44 kV three-phase line (Feeder 97014 extension) from Renison Bell to Trial Harbour Zone Substation which follows the existing roadway, a distance of approximately 25 km, to allow dual 44 kV sub-transmission circuits to supply Trial Harbour Zone Substation. This solution requires modifications to Trial Harbour 44 kV bus to provide sectionalising and connectivity to Renison Bell 44 kV interface. | Option 3 | Description |  | 30
Rejected due to the level of expenditure involved to manage risk. Requires additional investment to that stated to achieve the same reliability benefit as Preferred Option. | Option 3 | Reason for selection/rejection |  | 15
Build a new semi-permanent diesel generation facility at the former Zeehan Zone Substation site (which is in the Zeehan township) capable of re-supplying Zeehan and Granville Harbour for an outage of the existing feeder. | Option 4 | Description |  | 15
This option does not align with customer expectations. Additionally this option is outside TasNetworks’ risk appetite. | Option 4 | Reason for selection/rejection |  | 15
This option involves establishing a new 44 / 22 kV supply at Zeehan. This will be achieved by installing a new 44 /22 kV transformer with a teed connection to feeder 97013 at Zeehan. A new load break switch installed downstream to the transformer tee, in conjunction with fault passage indicators will initially allow faster supply restoration to Zeehan and Trial Harbour loads by isolating the faulted section between the tee and Trail Harbor, which is one of the identified, low reliability sections. The second stage of works consists of a 44 kV feeder extension from Renison Bell to the Zeehan tee downstream of the load break switch. By then operating the load break switch normally open, a diverse supply path is provided by feeder 97013 from Rosebery to Zeehan. | Option 5 | Description |  | 45
Rejected due to the level of expenditure involved to fully mitigate risk (delivers lower benefit at lower cost) | Option 5 | Reason for selection/rejection |  | 15
| Option 6 | Description
| Option 6 | Reason for selection/rejection