## Run Extract (hidden)
[12 empty] | 1 | 2 | 3 | 4 | 5 | 6
[12 empty] | Option 1 | Option 2 | Option 3 | Option 4 | Option 5 | Option 6
[10 empty] | Address | Value Metric | Option 0: WA transformer - 2037 | Option 1: TU Transformer - 2037 | Option 2: WA transformer - 2027 | Option 3: TU transformer and TA connection into 220 kV - 2027 | Option 4: TU transformer only - 2027
[11 empty] | Terminal Value | 14437997.2434 | 21170989.1308 | 13857662.6392 | 19750979.7127 | 17257624.9166
[11 empty] | Total Investment Cost | 27486164.0361 | 42566533.3609 | 30851684.6224 | 61803215.9103 | 58324663.9804
Notes
Need to open the .xlsm Investment Summary report from Copperleaf in the Trusted folder Save in the preferred location as an .xlsx Need to test environment - other and when two of the same value models have been selected with a different name
Options
| Option | 2025 | 2026 | 2027 | 2028 | 2029
| Baseline | 0 | 0 | 0 | 0 | 0
Option 0: WA transformer - 2037
Option 1: TU Transformer - 2037
Option 2: WA transformer - 2027
Option 3: TU transformer and TA connection into 220 kV - 2027
Option 4: TU transformer only - 2027
Option Breakdown | [7 empty] | Folder and File Paths
| Option 3 |  |  |  |  | Greater 0 | (Multiple Items)
| Recommended Option - Value | [6 empty] | This File Path | \\TNAD.tasnetworks.com.au\user$\user_folders\browningr\My Documents\Trusted\InvestmentTemplate.xlsm
| Value Function Measure | Value | Value in % | Greater 0 |  | Row Labels | Sum of Value in % | Folder Path | N:\NWITSolutions\Oracle\AIP Queries\Copperleaf\Investment Summary Reports\
Option 3 | Terminal Value | 13857.6626 | 17% | 1 | K20 | Cost Avoidance - CAPEX | 32.12% | File Name | InvestmentSummary_R24_T_ND_AUGSB_Upper Derwent 110 kV Losses.xlsx
Option 3 | Financial Benefit - CAPEX | 9404.9084 | 11.54% | 1 | K21 | Cost Avoidance - OPEX | 1.5% | File Path | N:\NWITSolutions\Oracle\AIP Queries\Copperleaf\Investment Summary Reports\InvestmentSummary_R24_T_ND_AUGSB_Upper Derwent 110 kV Losses.xlsx
Option 3 | Cost Avoidance - CAPEX | 26185.7024 | 32.12% | 1 | K22 | Financial Benefit - CAPEX | 11.54%
Option 3 | Cost Avoidance - OPEX | 1220.702 | 1.5% | 1 | K23 | Terminal Value | 17%
Option 3 | Total Investment Cost | -30851.6846 | 37.85% | 1 | K24 | Total Investment Cost | 37.85%
Option 3 |  |  |  | 0 | K25
Option 3 |  |  |  | 0 | K26
Option 3 |  |  |  | 0 | K27
Option 3 |  |  |  | 0 | K28
Option 3 |  |  |  | 0 | K29
Option 3 |  |  |  | 0 | K30 |  |  | 1 | InvestmentSummary_R24_D_ND_PRHVR_Augment_HV_Fdr_TRIP.xlsx
Option 3 |  |  |  | 0 | K31 |  |  | 2 | InvestmentSummary_R24_D_OH_REPOL_Basic Fleet Pole Replacement.xlsx
Option 3 |  |  |  | 0 | K32 |  |  | 3 | InvestmentSummary_R24_T_ND_AUGSB_W Coast Reliability Improvement.xlsx
Option 3 |  |  |  | 0 | K33 |  |  | 4 | InvestmentSummary_R24_T_ND_AUGSB_Upper Derwent 110 kV Losses.xlsx
| Total | 19817.2908 | 100% |  |  |  |  | 5 | InvestmentSummary_R24_D_OH_SIWES_Bird_Mitigation.xlsx
[8 empty] | 6 | InvestmentSummary_R24_D_SB_REGMS_GMS_Replacement of GMS.xlsx
[8 empty] | 7 | InvestmentSummary_R24_D_OH_REPOL_Complex Design.xlsx
Start | Option 1 |  |  |  |  | Greater 0 | 1 | 8 | InvestmentSummary_R24_D_PQ_PQTXV_Power_Quality_LV_Tformers.xlsx
| Value Function Measure | Value | Value in % | Greater 0 |  |  |  | 9 | InvestmentSummary_R24_D_ND_PQLVV_Aug_HV_LV_Conductor.xlsx
Option 1 | Terminal Value | 14437.9972 | 20.82% | 1 | K20 | Row Labels | Sum of Value in % | 10 | InvestmentSummary_R24_D_CA_SOLCP_Crossover_Extension_OH.xlsx
Option 1 | Cost Avoidance - CAPEX | 26185.7024 | 37.77% | 1 | K21 | Cost Avoidance - CAPEX | 37.77% | 11 | InvestmentSummary_R24_D_CI_SOIRR_Irrigation_Supply.xlsx
Option 1 | Cost Avoidance - OPEX | 1220.702 | 1.76% | 1 | K22 | Cost Avoidance - OPEX | 1.76% | 12 | InvestmentSummary_R24_D_AMIPD_AM Improvement Program.xlsx
Option 1 | Total Investment Cost | -27486.164 | 39.65% | 1 | K23 | Terminal Value | 20.82% | 13 | InvestmentSummary_R24_D_CI_SOPOR_Permanent_Residence_OH.xlsx
Option 1 |  |  |  | 0 | K24 | Total Investment Cost | 39.65% | 14 | InvestmentSummary_R24_D_CI_SUPOR_Permanent_Residence_UG.xlsx
Option 1 |  |  |  | 0 | K25 |  |  | 15 | InvestmentSummary_R24_D_CI_SOGSI_General_Supply_OH.xlsx
Option 1 |  |  |  | 0 | K26 |  |  | 16 | InvestmentSummary_R24_D_CI_SUGSI_General_Supply_UG.xlsx
Option 1 |  |  |  | 0 | K27 |  |  | 17 | InvestmentSummary_R24_D_CI_SUSBD_Subdivision_UG.xlsx
Option 1 |  |  |  | 0 | K28 |  |  | 18 | InvestmentSummary_R24_D_CI_SOSDI_Subdivision_OH.xlsx
Option 1 |  |  |  | 0 | K29 |  |  | 19 | InvestmentSummary_R24_D_CI_SUSUB_Augment_Dist_Substations.xlsx
Option 1 |  |  |  | 0 | K30 |  |  | 20 | InvestmentSummary_R24_T_ND_LAEMP_SELA.xlsx
Option 1 |  |  |  | 0 | K31 |  |  | 21 | InvestmentSummary_R24_D_CA_DESDB_Prelim_Drive_by_Design.xlsx
Option 1 |  |  |  | 0 | K32 |  |  | 22 | InvestmentSummary_R24_D_CI_SUMPR_Major_Commercial.xlsx
Option 1 |  |  |  | 0 | K33 |  |  | 23 | InvestmentSummary_R24_D_CI_EASEN_Easements_Non_Major_Comm.xlsx
| Total | 14358.2376 | 100% |  |  |  |  | 24 | InvestmentSummary_R24_D_ND_PRHVR_Rosebery_Supply_Improve.xlsx
[8 empty] | 25 | InvestmentSummary_R24_D_ND_CAHVF_Huonville_Supply_Improvement.xlsx
[8 empty] | 26 | InvestmentSummary_R24_D_ND_CAHVF_Aug_Fdr_Network_Access.xlsx
[8 empty] | 27 | InvestmentSummary_R24_D_ND_PRHVR_Deloraine_Supply_Improve.xlsx
| Option 2 |  |  |  |  | Greater 0 | 1 | 28 | InvestmentSummary_R24_D_ND_CALVF_Augment_LV_Fdr_Capacity.xlsx
| Value Function Measure | Value | Value in % | Greater 0 |  |  |  | 29 | InvestmentSummary_R24_D_ND_CAHVF_Augment_HV_Fdr_Trunk.xlsx
Option 2 | Terminal Value | 21170.9891 | 20.75% | 1 | K20 | Row Labels | Sum of Value in % | 30 | InvestmentSummary_R24_D_ND_CAHVF_Aug_Pole_Mtd_Regulator.xlsx
Option 2 | Financial Benefit - CAPEX | 10877.6193 | 10.66% | 1 | K21 | Cost Avoidance - CAPEX | 25.67% | 31 | InvestmentSummary_R24_D_ND_CAHVF_Aug_Grnd_Mtd_Regulator.xlsx
Option 2 | Cost Avoidance - CAPEX | 26185.7024 | 25.67% | 1 | K22 | Cost Avoidance - OPEX | 1.2% | 32 | InvestmentSummary_R24_D_ND_CAHVF_22kV_Emu_Bay_Feeders.xlsx
Option 2 | Cost Avoidance - OPEX | 1220.702 | 1.2% | 1 | K23 | Financial Benefit - CAPEX | 10.66% | 33 | InvestmentSummary_R24_D_ND_CAHVF_Augment_HV_Fdr_Capacity.xlsx
Option 2 | Total Investment Cost | -42566.5334 | 41.72% | 1 | K24 | Terminal Value | 20.75% | 34 | InvestmentSummary_R24_D_ND_CAHVF_Aug_SubStd_Cond_Capacity.xlsx
Option 2 |  |  |  | 0 | K25 | Total Investment Cost | 41.72% | 35 | InvestmentSummary_R24_D_ND_LANDZ_LandAcq_ZoneSubs.xlsx
Option 2 |  |  |  | 0 | K26 |  |  | 36
Option 2 |  |  |  | 0 | K27 |  |  | 37
Option 2 |  |  |  | 0 | K28 |  |  | 38
Option 2 |  |  |  | 0 | K29 |  |  | 39
Option 2 |  |  |  | 0 | K30 |  |  | 40
Option 2 |  |  |  | 0 | K31 |  |  | 41
Option 2 |  |  |  | 0 | K32 |  |  | 42
Option 2 |  |  |  | 0 | K33 |  |  | 43
| Total | 16888.4795 | 100%
| Option 3 |  |  |  |  | Greater 0 | 1
| Value Function Measure | Value | Value in % | Greater 0
Option 3 | Terminal Value | 13857.6626 | 17% | 1 | K20 | Row Labels | Sum of Value in %
Option 3 | Financial Benefit - CAPEX | 9404.9084 | 11.54% | 1 | K21 | Cost Avoidance - CAPEX | 32.12%
Option 3 | Cost Avoidance - CAPEX | 26185.7024 | 32.12% | 1 | K22 | Cost Avoidance - OPEX | 1.5%
Option 3 | Cost Avoidance - OPEX | 1220.702 | 1.5% | 1 | K23 | Financial Benefit - CAPEX | 11.54%
Option 3 | Total Investment Cost | -30851.6846 | 37.85% | 1 | K24 | Terminal Value | 17%
Option 3 |  |  |  | 0 | K25 | Total Investment Cost | 37.85%
Option 3 |  |  |  | 0 | K26
Option 3 |  |  |  | 0 | K27
Option 3 |  |  |  | 0 | K28
Option 3 |  |  |  | 0 | K29
Option 3 |  |  |  | 0 | K30
Option 3 |  |  |  | 0 | K31
Option 3 |  |  |  | 0 | K32
Option 3 |  |  |  | 0 | K33
| Total | 19817.2908 | 100%
| Option 4 |  |  |  |  | Greater 0 | 1
| Value Function Measure | Value | Value in % | Greater 0
Option 4 | Terminal Value | 19750.9797 | 14.09% | 1 | K20 | Row Labels | Sum of Value in %
Option 4 | Financial Benefit - CAPEX | 31232.219 | 22.28% | 1 | K21 | Cost Avoidance - CAPEX | 18.68%
Option 4 | Cost Avoidance - CAPEX | 26185.7024 | 18.68% | 1 | K22 | Cost Avoidance - OPEX | 0.87%
Option 4 | Cost Avoidance - OPEX | 1220.702 | 0.87% | 1 | K23 | Financial Benefit - CAPEX | 22.28%
Option 4 | Total Investment Cost | -61803.2159 | 44.08% | 1 | K24 | Terminal Value | 14.09%
Option 4 |  |  |  | 0 | K25 | Total Investment Cost | 44.08%
Option 4 |  |  |  | 0 | K26
Option 4 |  |  |  | 0 | K27
Option 4 |  |  |  | 0 | K28
Option 4 |  |  |  | 0 | K29
Option 4 |  |  |  | 0 | K30
Option 4 |  |  |  | 0 | K31
Option 4 |  |  |  | 0 | K32
Option 4 |  |  |  | 0 | K33
| Total | 16586.3872 | 100%
| Option 5 |  |  |  |  | Greater 0 | 1
| Value Function Measure | Value | Value in % | Greater 0
Option 5 | Terminal Value | 17257.6249 | 13.86% | 1 | K20 | Row Labels | Sum of Value in %
Option 5 | Financial Benefit - CAPEX | 21485.7802 | 17.26% | 1 | K21 | Cost Avoidance - CAPEX | 21.04%
Option 5 | Cost Avoidance - CAPEX | 26185.7024 | 21.04% | 1 | K22 | Cost Avoidance - OPEX | 0.98%
Option 5 | Cost Avoidance - OPEX | 1220.702 | 0.98% | 1 | K23 | Financial Benefit - CAPEX | 17.26%
Option 5 | Total Investment Cost | -58324.664 | 46.86% | 1 | K24 | Terminal Value | 13.86%
Option 5 |  |  |  | 0 | K25 | Total Investment Cost | 46.86%
Option 5 |  |  |  | 0 | K26
Option 5 |  |  |  | 0 | K27
Option 5 |  |  |  | 0 | K28
Option 5 |  |  |  | 0 | K29
Option 5 |  |  |  | 0 | K30
Option 5 |  |  |  | 0 | K31
Option 5 |  |  |  | 0 | K32
Option 5 |  |  |  | 0 | K33
| Total | 7825.1455 | 100%
| Option 6 |  |  |  |  | Greater 0 | 0
| Value Function Measure | Value | Value in % | Greater 0
Option 6 |  |  |  | 0 | K20 | Row Labels | Sum of Value in %
Option 6 |  |  |  | 0 | K21 |  | 0%
Option 6 |  |  |  | 0 | K22
Option 6 |  |  |  | 0 | K23
Option 6 |  |  |  | 0 | K24
Option 6 |  |  |  | 0 | K25
Option 6 |  |  |  | 0 | K26
Option 6 |  |  |  | 0 | K27
Option 6 |  |  |  | 0 | K28
Option 6 |  |  |  | 0 | K29
Option 6 |  |  |  | 0 | K30
Option 6 |  |  |  | 0 | K31
Option 6 |  |  |  | 0 | K32
Option 6 |  |  |  | 0 | K33
| Total | 0 | 0%

## Summary
Investment Evaluation Summary |  |  |  | Investment Code |  | Report Start Year |  | NPV Period | Base Fiscal Year | Currency Scale
|  |  |  | PRJ000874 |  | 2025 |  | 25 | FY23 | Literal
|  |  |  | Investment Name | [5 empty] | Scenario
|  |  |  | R24_T_ND_AUGSB_Upper Derwent 110 kV Losses | [5 empty] | Approved
Value Function |  | TasNetworks Value Function |  | Version |  | 0.1 |  | Date |  | 2022-10-27
Investment Description
Description |  | Reducing losses in the Upper Derwent 110 kV transmission network | [9 empty] | TRUE
Functional Area |  | AUGSB |  |  | Department |  |  | System Planning
Works Initiator |  |  |  |  | Portfolio |  |  | Tx - Augmentation
Investment Category |  | Prescribed Services - Augmentation |  |  | Needs Item Reference |  |  | R0001972235
Investment Type |  | Network Project |  |  | Document No. |  |  | R0002295926
Investment Stage |  | Gate 2 - Investment Evaluation Summary |  |  | Project Zone Location |  |  | URL Link
PPM ID |  |  |  |  | Regulatory Test Required |  |  | Yes
Investment Summary
Problem Definition |  | There is potential that there is benefit to customers (i.e. a market benefit) in procuring a network augmentation (e.g. providing a local interconnection between the 110 and 220 kV), which will allow for more efficient transfer of the power through the 220 kV network, reducing network losses. A network transformer in the Upper Derwent network will be required in time irrespective of the benefit of network loss reduction. The problem definition being assessed for this investment is whether there is a case to advance installation of the network transformer to provide that benefit of reduced network losses. | [9 empty] | TRUE
Recommendation |  | The preferred Option is Option 2, which includes installation of a 220/110 kV network transformer at Waddamana substation and associated necessary works at Waddamana Substation. This option provides the most economic solution to reduce network losses in the Upper Derwent 110 kV transmission network. It is the preferred option in the base case and the majority of sensitivities analysed. This option contributes to mitigating business risks by implementing projects that provide a net market benefit to support customer focus, and reduce the risk of widespread power disruption though minimising impact of double circuit failures. It is recommended that the preferred option (option 2) is approved and progressed as it best satisfies the customer and business needs. | [9 empty] | TRUE
Alternative Spend Profile
Name |  | Status | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV | Alternative Start Date
Option 0: WA transformer - 2037 |  | Candidate | 0 | 0 | 0 | 0 | 0 | 0 | 41221578 | 14358237.59 | 4912600%
Option 1: TU Transformer - 2037 |  | Candidate | 0 | 0 | 0 | 0 | 0 | 0 | 63215280 | 16888479.5 | 4912600%
Option 2: WA transformer - 2027 |  | Recommended | 940936 | 4258761 | 4459038 | 47580 | 47580 | 9753895 | 43191447 | 19817290.8 | 4547400%
Option 3: TU transformer and TA connection into 220 kV - 2027 |  | Candidate | 4785777 | 18974239 | 25783882 | 244059 | 244059 | 50032016 | 75888248 | 16586387.19 | 4547400%
Option 4: TU transformer only - 2027 |  | Candidate | 4737229 | 18925691 | 24764380 | 195511 | 195511 | 48818322 | 70936376 | 7825145.55 | 4547400%
0
Leader Endorsement
Name |  |  | Governance |  | Signature |  |  | Comments |  |  | Date
|  |  | Submission | [7 empty] | 4486100%
|  |  | Endorsement | [7 empty] | 4486100%
|  |  | Approval | [7 empty] | 4486100%
Investment Attachments
Date | Attachment Name |  | Description
4484851% | R0002030418 |  | Investment Estimate
4484851% | R0001972235 |  | Needs Form
4484851% | TL425 TL426 Waddamana–Tungatinah 110 kV transmission line CAR
4484851% | WA–PM corridor augmentation analysis

## Investment Overview
Investment Evaluation Summary |  | Copperleaf Investment Code |  | Report Start Year | NPV Period | Base Fiscal Year | Currency Scale
|  | PRJ000874 |  | 2025 | 25 | FY23 | Literal
|  | Investment Name |  |  |  |  | Scenario
|  | R24_T_ND_AUGSB_Upper Derwent 110 kV Losses |  |  |  |  | Approved
Value Function | TasNetworks Value Function | Version |  | 0.1 | Date |  | 2022-10-27
Functional Area | AUGSB |  | Department |  | System Planning
Works Initiator |  |  | Portfolio |  | Tx - Augmentation
Investment Category | Prescribed Services - Augmentation |  | Needs Item Reference |  | R0001972235
Investment Type | Network Project |  | Document No. |  | R0002295926
Investment Stage | Gate 2 - Investment Evaluation Summary |  | Project Zone Location |  | URL Link
PPM ID |  |  | Regulatory Test Required |  | Yes
Investment Overview
01. Overview | Background |  | The transmission network in the Upper Derwent area evolved with the 110 kV network and generation, then a 220 kV network was developed to support increased power transfers. There is no 110-to-220 kV interconnection in the Upper Derwent area. There is 250 MW generation capacity from power stations connected to Tungatinah Substation, which is transmitted via the 110 kV network to Palmerston Substation and the southern transmission network. Power transfer is more efficient at higher voltages. The current reduces in proportionate to the voltage increase for a given power transfer—and network losses are proportional to the square-of-the-current. Therefore network losses will reduce by a factor of four if generation in the Upper Derwent 110 kV network were connected to the 220 kV network (i.e. a doubling of the voltage). |  |  |  |  | TRUE
| Problem Definition |  | There is potential that there is benefit to customers (i.e. a market benefit) in procuring a network augmentation (e.g. providing a local interconnection between the 110 and 220 kV), which will allow for more efficient transfer of the power through the 220 kV network, reducing network losses. A network transformer in the Upper Derwent network will be required in time irrespective of the benefit of network loss reduction. The problem definition being assessed for this investment is whether there is a case to advance installation of the network transformer to provide that benefit of reduced network losses. |  |  |  |  | FALSE
02. Customer Needs and Impact | Customer Needs and impact |  | Reducing network losses provides benefit to customers through lower wholesale energy costs. |  |  |  |  | TRUE

## Objectives and Analysis
Investment Evaluation Summary |  | Copperleaf Investment Code |  | Report Start Year | NPV Period | Base Fiscal Year | Currency Scale
|  | PRJ000874 |  | 2025 | 25 | FY23 | Literal
|  | Investment Name |  |  |  |  | Scenario
|  | R24_T_ND_AUGSB_Upper Derwent 110 kV Losses |  |  |  |  | Approved
Value Function | TasNetworks Value Function | Version |  | 0.1 | Date |  | 2022-10-27
Functional Area | AUGSB |  | Department |  | System Planning
Works Initiator |  |  | Portfolio |  | Tx - Augmentation
Investment Category | Prescribed Services - Augmentation |  | Needs Item Reference |  | R0001972235
Investment Type | Network Project |  | Document No. |  | R0002295926
Investment Stage | Gate 2 - Investment Evaluation Summary |  | Project Zone Location |  | URL Link
PPM ID |  |  | Regulatory Test Required |  | Yes
Objectives and Analysis
03. Business Performance Objectives | Safety and Wellbeing | [6 empty] | TRUE
| Our Customers |  | Customer net promoter score - Delivering sustainable prices through procuring augmentations that provide a net economic benefit. |  |  |  |  | FALSE
| Our People | [6 empty] | FALSE
| Our Business - Sustained Cost Management |  | Deliver initiatives in line with approved budgets. |  |  |  |  | FALSE
| Our Business - Network Service | [6 empty] | FALSE
04. Business Risks | Death or Injury (Employee) | [6 empty] | FALSE
| Death or Injury (Public) | [6 empty] | FALSE
| Sustainable and Predictable Pricing | [6 empty] | FALSE
| Widespread Power Disruption |  | The proposed solution helps to reduce the risk of a system collapse resulting from a double circuit failure of the Liapootah–Waddamana–Palmerston 220 kV transmission line by splitting it into two sections (i.e. Liapootah–Waddamana and Waddamana–Palmerston). Under the proposed option, if a fault occurs, either one of these two sections can be lost, instead of the entire line, as is the case with the current network arrangement. |  |  |  |  | FALSE
| Bushfire Start | [6 empty] | FALSE
| Loss of Major Industrial | [6 empty] | FALSE
| Customer Focus |  | Implementation will provide a positive net market benefit and will reduce the cost to customers. |  |  |  |  | FALSE
| Business Continuity Management | [6 empty] | FALSE
| Cyber Security | [6 empty] | FALSE
| Private Assets | [6 empty] | FALSE
Energy Policy and Regulation
Project Marinus (D&A)
Tasmanian Power System Complexity
| Emerging Complexity of the NEM | [6 empty] | FALSE
05. Strategic Objectives | Strategic Objectives |  | #1 - Towards 2030 |  |  |  |  | FALSE
| Strategic Document #1 |  | Strategic planning of the network, including supporting transmission for Marinus Link - Reducing network losses will allow more energy to be delivered from what is generated. Long-term solutions to address network complexities such as inertia and fault-level shortfalls - Establishing a 220/110 kV network transformer at Waddamana Substation will improve system strength by increasing the coupling between Upper Derwent 110 kV generation and system strength nodes. |  |  |  |  | FALSE
| Strategic Document #2 | [6 empty] | FALSE
| Strategic Document #3 | [6 empty] | FALSE
| Strategic Document #4 | [6 empty] | FALSE
| Strategic Document #5 | [6 empty] | FALSE
06. Project Objectives | Project Objectives |  | The objective is to procure a solution that maximises the benefits to all those who participate in the market. |  |  |  |  | FALSE
07. Options Analysis | Benchmarking |  | Benchmarking is not applicable to this IES. |  |  |  |  | TRUE
| Expert Findings |  | Expert findings is not applicable to this IES. |  |  |  |  | FALSE
08. Investment Timing | Investment Timing |  | TasNetworks is expecting to commission the most economical option (WA transformer – 2027) by 2027. This option is economic to implement as soon as possible. |  |  |  |  | TRUE
09. Expected Outcomes and Benefits | Expected Outcomes and Benefits |  | All options provide additional benefits to system strength and the stability of the power system. Establishing a 220/110 kV network transformer at either Waddamana or Tungatinah substations will improve system strength by increasing the coupling between the Upper Derwent 110 kV generation and the Waddamana 220 kV system strength node. It is noted that the benefit will vary between the Waddamana and Tungatinah locations, which is to be further assessed. The benefit will also vary between the various option timings with the 2027 option timings providing the benefit ahead of 2037 option timings. This benefit will reduce the reliance on currently-contracted synchronous condenser support to maintain the required system strength levels in the network. Splitting the Liapootah–Waddamana–Palmerston 220 kV circuit into two sections will improve the system security due to a double circuit failure of the Liapootah–Waddamana–Palmerston line significantly by reducing the contingency size. This is proposed across all options, however the benefit will be realised earlier in the 2027 option timings compared to the 2037 option timings. This has not been quantified at this stage. However, they are not expected to change the preferred option, and the majority of options already provide a net economic benefit without these additional benefits. The benefits to TasNetworks from implementation of the preferred option will be to: - reduce network losses; - provide the most economic solution to customers through proceeding with augmentations which provide a net economic benefit; - increase the security of the network and reduce the impact of double circuit failure by splitting the existing Liapootah–Waddamana–Palmerston 220 kV transmission circuits into two at Waddamana Substation; and - benefit system strength by increasing the coupling between Upper Derwent 110 kV generation and Waddamana 220 kV system strength node. |  |  |  |  | TRUE
10. Assumptions | Assumptions |  | The following assumptions were made in developing the options: A network transformer at Waddamana Substation with conversion of Waddamana–Palmerston 110 kV transmission flows to 220 kV Previous analysis identified a need for the upgrading of the existing Waddamana–Palmerston 110 kV transmission circuit to 220 kV by 2037, resulting from the forecast wind developments in the Central Highlands REZ reaching 790 MW. When this occurs, a network transformer in the area is needed as an alternative to the existing Waddamana–Palmerston 110 kV transmission circuit to keep the connection from the Upper Derwent 110 kV to the northern transmission network, if a network transformer has not already been installed as a loss reduction measure. The upgrade of the Waddamana–Palmerston 110 kV transmission circuit to 220 kV is common for all options. Therefore, its cost is not included in the options analysis. A network transformer installed in the area by 2037, is considered as the base line for the options analysis. Replacement of Tungatinah–Waddamana 110 kV transmission lines Condition assessment reports for the Tungatinah–Waddamana 110 kV transmission lines (TL425 and TL426) were prepared in 2018, indicating that these circuits are expected to remain serviceable for another 20 years (i.e., 2038). By that time, these circuits will be 82 and 85 years old respectively and it is assumed that these circuits are to be replaced by that time, if a 220 kV connection is not established at Tungatinah. The requirement of these circuits directly links to the remaining connection from Waddamana Substation 110 kV bus to the rest of the network (i.e., the proposed network transformer at Waddamana Substation and Waddamana–Palmerston 110 kV transmission circuit). The replacement for TL425 and TL426 or alternative development necessary under each option, is included in the analysis in 2038. |  |  |  |  | TRUE
11. Regulatory Considerations | Regulatory Investment Test |  | This project will be required to undertake the regulatory investment test for transmission (RIT-T), as the most expensive credible option exceeds the current cost threshold ($7 million).
| Meet or manage the expected demand for Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | No
| Comply with all applicable regulatory obligations associated with the provision of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | No
| Maintain the quality, reliability and security of supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
| Maintain the reliability and security of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | No
| Maintain the safety of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | No
12. Recommendation | Recommendation |  | The preferred Option is Option 2, which includes installation of a 220/110 kV network transformer at Waddamana substation and associated necessary works at Waddamana Substation. This option provides the most economic solution to reduce network losses in the Upper Derwent 110 kV transmission network. It is the preferred option in the base case and the majority of sensitivities analysed. This option contributes to mitigating business risks by implementing projects that provide a net market benefit to support customer focus, and reduce the risk of widespread power disruption though minimising impact of double circuit failures. It is recommended that the preferred option (option 2) is approved and progressed as it best satisfies the customer and business needs. |  |  |  |  | TRUE

## Economic Analysis
alternative
| Investment Evaluation Summary |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[5 empty] | PRJ000874 |  | 2025 |  | 25 | FY23 | Literal
[5 empty] | Investment Name | [5 empty] | Scenario
[5 empty] | R24_T_ND_AUGSB_Upper Derwent 110 kV Losses | [5 empty] | Approved
autofit | Value Function |  |  | TasNetworks Value Function | Version |  | 0.1 |  | Date |  | 2022-10-27
Economic Analysis
| Parameter |  |  |  | Value | Unit | Source of Values
75679 | NPV Period |  |  |  | 25 | Years | TasNetworks requirement
autofit | First Fiscal Year of Forecast |  |  |  | FY23 | - | TasNetworks requirement
| Weighted Average Cost of Capital (WACC) |  |  |  | 2.82 | % | 2019-24 Revenue determination and ISP 2022 draft data
| Voluntary load shedding assumed? |  |  |  | No | - | N/A
| Reduction in system losses considered? |  |  |  | No | - | N/A
| Value of Customer Reliability applied |  |  | Very large business customer - Services | 10.93 | $/kWh | AER - Values of Customer Reliability - Annual adjustment summary - December 2021
|  |  |  | Residential | 17.08 | $/kWh
|  |  |  | Very large business customer - Metals | 20.6 | $/kWh
|  |  |  | Very large business customer - Transmission | 27.43 | $/kWh
|  |  |  | Very large business customer - Mines | 36.47 | $/kWh
|  |  |  | Business customer - Agricultural | 39.28 | $/kWh
|  |  |  | Business customer - Commercial | 46.18 | $/kWh
|  |  |  | Very large business customer - Distribution | 58.8 | $/kWh
|  |  |  | Business customer - Industrial | 66.16 | $/kWh
autofit |  |  |  | Very large business customer - Industrial | 122.39 | $/kWh
Sensitivity to Project Timing
|  | 1 | Navigate to Copperleaf Portfolio and search for your Investment
|  | 2 | Navigate to the Value Comparison Page for your Investment through the breadcrumb menu
|  | 3 | Once on the Value Comparison Page, select "Value by Start Date" in the drop-down menu in the top-left corner of the page
|  | 4 | This screen will show the value change over time for each option in your investment
|  | 5 | With the snipping tool on your PC, take a screenshot of the chart and copy + paste it in this section of the report
Options Considered
| Options Summary |  |  |  | R24 Expenditure ($M) | NPV ($M) | Preferred Option | Reason for selection/rejection
| Option 0: WA transformer - 2037 |  |  |  | 0 | 14.3582 | No | This is not the highest NPV option.
| Option 1: TU Transformer - 2037 |  |  |  | 0 | 16.8885 | No | This is not the highest NPV option (marginally lower to the preferred option).
| Option 2: WA transformer - 2027 |  |  |  | 9.7539 | 19.8173 | Yes | This is the highest NPV option. It also has additional benefit.
| Option 3: TU transformer and TA connection into 220 kV - 2027 |  |  |  | 50.032 | 16.5864 | No | This is not the highest NPV option.
| Option 4: TU transformer only - 2027 |  |  |  | 48.8183 | 7.8251 | No | This is not the highest NPV option.
0
NPV Components

## Needs Assessment (hidden)
Needs Assessment Form |  | Copperleaf Investment Code |  | Report Start Year | NPV Period | Base Fiscal Year | Currency Scale
|  | PRJ000874 |  | 2025 | 25 | FY23 | Literal
|  | Investment Name |  |  |  |  | Scenario
|  | R24_T_ND_AUGSB_Upper Derwent 110 kV Losses |  |  |  |  | Approved
Value Function | TasNetworks Value Function | Version |  | 0.1 | Date |  | 2022-10-27
Functional Area | AUGSB |  | Department |  | System Planning
Works Initiator |  |  | Portfolio |  | Tx - Augmentation
Investment Category | Prescribed Services - Augmentation |  | Needs Item Reference |  | R0001972235
Investment Type | Network Project |  | Document No. |  | R0002295926
Investment Stage | Gate 2 - Investment Evaluation Summary |  | Project Zone Location
PPM ID |  |  | Regulatory Test Required |  | Yes
Investment Overview
01. Overview | Background |  | The transmission network in the Upper Derwent area evolved with the 110 kV network and generation, then a 220 kV network was developed to support increased power transfers. There is no 110-to-220 kV interconnection in the Upper Derwent area. There is 250 MW generation capacity from power stations connected to Tungatinah Substation, which is transmitted via the 110 kV network to Palmerston Substation and the southern transmission network. Power transfer is more efficient at higher voltages. The current reduces in proportionate to the voltage increase for a given power transfer—and network losses are proportional to the square-of-the-current. Therefore network losses will reduce by a factor of four if generation in the Upper Derwent 110 kV network were connected to the 220 kV network (i.e. a doubling of the voltage). |  |  |  |  | TRUE
| Problem Definition |  | There is potential that there is benefit to customers (i.e. a market benefit) in procuring a network augmentation (e.g. providing a local interconnection between the 110 and 220 kV), which will allow for more efficient transfer of the power through the 220 kV network, reducing network losses. A network transformer in the Upper Derwent network will be required in time irrespective of the benefit of network loss reduction. The problem definition being assessed for this investment is whether there is a case to advance installation of the network transformer to provide that benefit of reduced network losses. |  |  |  |  | FALSE
02. Customer Needs and Impact | Customer Needs and impact |  | Reducing network losses provides benefit to customers through lower wholesale energy costs. |  |  |  |  | TRUE
03. Business Objectives | Business Objectives
04. Project Objectives | Project Objectives |  | The objective is to procure a solution that maximises the benefits to all those who participate in the market. |  |  |  |  | FALSE
05. Risk Objective | Risk if not progressed | [6 empty] | TRUE
06. Investment Timing | Investment Timing |  | TasNetworks is expecting to commission the most economical option (WA transformer – 2027) by 2027. This option is economic to implement as soon as possible. |  |  |  |  | TRUE
07. Business Consulatation | Business Consulatation | [6 empty] | TRUE

## Option 1
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000874 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_T_ND_AUGSB_Upper Derwent 110 kV Losses | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-27
Alternative Overview
75679 | Alternative Name |  | Option 0: WA transformer - 2037
autofit | Description |  | This option is the ‘business as usual’ development of the network and includes the following works to be commissioned in 2037 (Tungatinah–Waddamana 110 kV circuit replacement in 2038): - Install a network transformer at Waddamana Substation; - Split the existing Liapootah–Waddamana–Palmerston 220 kV circuits into Liapootah–Waddamana and Waddamana–Palmerston; and - Replace Tungatinah–Waddamana 110 kV circuits (by 2038). The installation of a Waddamana network transformer is required to keep a connection from Tungatinah to the northern transmission network as an alternative to the Waddamana–Palmerston 110 kV circuit. The Tungatinah–Waddamana circuit replacement is also to keep the northern connection by addressing the issue of those asset lives.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4912600%
| Reason for selection/rejection |  | This is not the highest NPV option.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Option 0: WA transformer - 2037 |  | Capex |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 41221578 | 14358237.59
|  |  | Opex |  |  | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Terminal Value |  |  | 14437.9972 | 20.82%
[9 empty] | Cost Avoidance - CAPEX |  |  | 26185.7024 | 37.77%
[9 empty] | Cost Avoidance - OPEX |  |  | 1220.702 | 1.76%
[9 empty] | Total Investment Cost |  |  | -27486.164 | 39.65%
[9 empty] | Total |  |  | 14358.2376
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Financial Benefits & Costs | Cost Avoidance - CAPEX |  | Outcome | 2034 | 26185.7024 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Financial Benefits & Costs | Cost Avoidance - OPEX |  | Outcome | 2034 | 1220.702 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2034 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Investment Cost | OPEX Cost |  | Outcome | 2037 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | Investment Cost | Total Investment Cost |  | Outcome | 2034 | -27486.164 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 14437.9972 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 0 | 0 | 0 | 0 | 0
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 2
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000874 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_T_ND_AUGSB_Upper Derwent 110 kV Losses | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-27
Alternative Overview
75679 | Alternative Name |  | Option 1: TU Transformer - 2037
autofit | Description |  | This option includes the following works to be commissioned in 2037 : - Install a network transformer and 220 kV switchyard at Tungatinah Substation; - Build a double circuit 220 kV transmission line from Dee to Tungatinah; - Install two 220 kV cables from Tarraleah Power Station to the new Tungatinah 220 kV switchyard (approx. 500 m); - Split the existing Liapootah–Waddamana–Palmerston 220 kV circuits into Liapootah–Waddamana (now becoming Liapootah– Tungatinah–Waddamana) and Waddamana–Palmerston; and - Replace Tungatinah–Lake Echo section of TL425 (in 2038). By establishing a network transformer at Tungatinah Substation, it would provide a connection from Tungatinah to the northern transmission network. The rearrangement of the Liapootah–Waddamana–Palmerston 220 kV circuits at Waddamana is needed to make them three ended circuits instead of four ended circuits, which is unacceptable form a network protection perspective.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4912600%
| Reason for selection/rejection |  | This is not the highest NPV option (marginally lower to the preferred option).
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Option 1: TU Transformer - 2037 |  | Capex |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 63215280 | 16888479.5
|  |  | Opex |  |  | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Terminal Value |  |  | 21170.9891 | 20.75%
[9 empty] | Financial Benefit - CAPEX |  |  | 10877.6193 | 10.66%
[9 empty] | Cost Avoidance - CAPEX |  |  | 26185.7024 | 25.67%
[9 empty] | Cost Avoidance - OPEX |  |  | 1220.702 | 1.2%
[9 empty] | Total Investment Cost |  |  | -42566.5334 | 41.72%
[9 empty] | Total |  |  | 16888.4795
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Financial Benefits & Costs | Cost Avoidance - CAPEX |  | Outcome | 2034 | 26185.7024 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Financial Benefits & Costs | Cost Avoidance - OPEX |  | Outcome | 2034 | 1220.702 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Financial Benefits & Costs | Financial Benefit - CAPEX |  | Outcome | 2037 | 10877.6193 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2034 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | Investment Cost | OPEX Cost |  | Outcome | 2038 | 0 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2034 | -42566.5334 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | Terminal Value | Terminal Value |  | Outcome | 2048 | 21170.9891 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 0 | 0 | 0 | 0 | 0
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 3
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000874 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_T_ND_AUGSB_Upper Derwent 110 kV Losses | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-27
Alternative Overview
75679 | Alternative Name |  | Option 2: WA transformer - 2027
autofit | Description |  | This option includes the same scope as Option 0, except that it is to be commissioned in 2027 (replacement of the Tungatinah–Waddamana 110 kV circuits remains in 2038) to reduce the transmission losses in the Upper Derwent area of the 110 kV network.
autofit | Alternative Status |  | Recommended
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | This is the highest NPV option. It also has additional benefit.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Option 2: WA transformer - 2027 |  | Capex |  |  | 893356 | 4211181 | 4411458 | 0 | 0 | 9515995 | 43191447 | 19817290.8
|  |  | Opex |  |  | 47580 | 47580 | 47580 | 47580 | 47580 | 237900
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Terminal Value |  |  | 13857.6626 | 17%
[9 empty] | Financial Benefit - CAPEX |  |  | 9404.9084 | 11.54%
[9 empty] | Cost Avoidance - CAPEX |  |  | 26185.7024 | 32.12%
[9 empty] | Cost Avoidance - OPEX |  |  | 1220.702 | 1.5%
[9 empty] | Total Investment Cost |  |  | -30851.6846 | 37.85%
[9 empty] | Total |  |  | 19817.2908
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Financial Benefits & Costs | Cost Avoidance - CAPEX |  | Outcome | 2034 | 26185.7024 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Financial Benefits & Costs | Cost Avoidance - OPEX |  | Outcome | 2034 | 1220.702 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Financial Benefits & Costs | Financial Benefit - CAPEX |  | Outcome | 2022 | 9404.9084 | Dollar | 495821.7 | 452364.66 | 470765.79 | 615236.49 | 906105.42
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 893356 | 4211181 | 4411458 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | Investment Cost | OPEX Cost |  | Outcome | 2024 | 0 | Dollar | 47580 | 47580 | 47580 | 47580 | 47580
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -30851.6846 | Dollar | 940936 | 4258761 | 4459038 | 47580 | 47580
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | Terminal Value | Terminal Value |  | Outcome | 2048 | 13857.6626 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 0 | 0 | 0 | 0 | 0
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 4
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000874 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_T_ND_AUGSB_Upper Derwent 110 kV Losses | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-27
Alternative Overview
75679 | Alternative Name |  | Option 3: TU transformer and TA connection into 220 kV - 2027
autofit | Description |  | This option includes the same scope as Option 1, except that it is to be commissioned in 2027 (replacement of the Tungatinah–Lake Echo section of the TL425 remains in 2038), to reduce the transmission losses in the Upper Derwent area of the 110 kV network.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | This is not the highest NPV option.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Option 3: TU transformer and TA connection into 220 kV - 2027 |  | Capex |  |  | 4541718 | 18730180 | 25539823 | 0 | 0 | 48811721 | 75888248 | 16586387.19
|  |  | Opex |  |  | 244059 | 244059 | 244059 | 244059 | 244059 | 1220295
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Terminal Value |  |  | 19750.9797 | 14.09%
[9 empty] | Financial Benefit - CAPEX |  |  | 31232.219 | 22.28%
[9 empty] | Cost Avoidance - CAPEX |  |  | 26185.7024 | 18.68%
[9 empty] | Cost Avoidance - OPEX |  |  | 1220.702 | 0.87%
[9 empty] | Total Investment Cost |  |  | -61803.2159 | 44.08%
[9 empty] | Total |  |  | 16586.3872
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Financial Benefits & Costs | Cost Avoidance - CAPEX |  | Outcome | 2034 | 26185.7024 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Financial Benefits & Costs | Cost Avoidance - OPEX |  | Outcome | 2034 | 1220.702 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Financial Benefits & Costs | Financial Benefit - CAPEX |  | Outcome | 2022 | 31232.219 | Dollar | 1070301.87 | 1005446.97 | 1087449.66 | 1313931.96 | 1924536.24
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 4541718 | 18730180 | 25539823 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | Investment Cost | OPEX Cost |  | Outcome | 2024 | 0 | Dollar | 244059 | 244059 | 244059 | 244059 | 244059
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -61803.2159 | Dollar | 4785777 | 18974239 | 25783882 | 244059 | 244059
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | Terminal Value | Terminal Value |  | Outcome | 2048 | 19750.9797 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 0 | 0 | 0 | 0 | 0
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 5
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000874 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_T_ND_AUGSB_Upper Derwent 110 kV Losses | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-27
Alternative Overview
75679 | Alternative Name |  | Option 4: TU transformer only - 2027
autofit | Description |  | This option includes the same scope and timing as Option 3, except for the existing Tarraleah Power Station maintains a 110 kV connection to the Tungatinah Substation.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | This is not the highest NPV option.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Option 4: TU transformer only - 2027 |  | Capex |  |  | 4541718 | 18730180 | 24568869 | 0 | 0 | 47840767 | 70936376 | 7825145.55
|  |  | Opex |  |  | 195511 | 195511 | 195511 | 195511 | 195511 | 977555
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Terminal Value |  |  | 17257.6249 | 13.86%
[9 empty] | Financial Benefit - CAPEX |  |  | 21485.7802 | 17.26%
[9 empty] | Cost Avoidance - CAPEX |  |  | 26185.7024 | 21.04%
[9 empty] | Cost Avoidance - OPEX |  |  | 1220.702 | 0.98%
[9 empty] | Total Investment Cost |  |  | -58324.664 | 46.86%
[9 empty] | Total |  |  | 7825.1455
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Financial Benefits & Costs | Cost Avoidance - CAPEX |  | Outcome | 2034 | 26185.7024 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Financial Benefits & Costs | Cost Avoidance - OPEX |  | Outcome | 2034 | 1220.702 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Financial Benefits & Costs | Financial Benefit - CAPEX |  | Outcome | 2022 | 21485.7802 | Dollar | 1161105.4818 | 1127405.8026 | 1270852.9317 | 952396.5231 | 1430309.6082
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 4541718 | 18730180 | 24568869 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | Investment Cost | OPEX Cost |  | Outcome | 2024 | 0 | Dollar | 195511 | 195511 | 195511 | 195511 | 195511
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -58324.664 | Dollar | 4737229 | 18925691 | 24764380 | 195511 | 195511
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | Terminal Value | Terminal Value |  | Outcome | 2048 | 17257.6249 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 0 | 0 | 0 | 0 | 0
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 6 (hidden)
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000874 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_T_ND_AUGSB_Upper Derwent 110 kV Losses | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-27
Alternative Overview
75679 | Alternative Name
autofit | Description
autofit | Alternative Status
autofit | Alternative Start Date
Reason for selection/rejection
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
0
0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Total |  |  | 0
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 0 | 0 | 0 | 0 | 0
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## TextFormatting (hidden)
Index | 8
Column Width | 238
Font | Calibri
Font Size | 11
Font Colour
Text | Sheet | Group | Field | Row Height | Row Number
Reducing losses in the Upper Derwent 110 kV transmission network | Investment Summary | Header | Description | 15 | 9
The transmission network in the Upper Derwent area evolved with the 110 kV network and generation, then a 220 kV network was developed to support increased power transfers. There is no 110-to-220 kV interconnection in the Upper Derwent area. There is 250 MW generation capacity from power stations connected to Tungatinah Substation, which is transmitted via the 110 kV network to Palmerston Substation and the southern transmission network. Power transfer is more efficient at higher voltages. The current reduces in proportionate to the voltage increase for a given power transfer—and network losses are proportional to the square-of-the-current. Therefore network losses will reduce by a factor of four if generation in the Upper Derwent 110 kV network were connected to the 220 kV network (i.e. a doubling of the voltage). | Investment Summary | 0.1 Overview | Background | 150 | 16
There is potential that there is benefit to customers (i.e. a market benefit) in procuring a network augmentation (e.g. providing a local interconnection between the 110 and 220 kV), which will allow for more efficient transfer of the power through the 220 kV network, reducing network losses. A network transformer in the Upper Derwent network will be required in time irrespective of the benefit of network loss reduction. The problem definition being assessed for this investment is whether there is a case to advance installation of the network transformer to provide that benefit of reduced network losses. | Investment Summary | 0.1 Overview | Problem Definition | 105 | 17
Reducing network losses provides benefit to customers through lower wholesale energy costs. | Investment Summary | 02. Customer Needs and Impact | Customer Needs and impact | 15 | 18
| Objectives and Analysis | 03. Business Performance Objectives | Safety and Wellbeing | 15 | 17
Customer net promoter score - Delivering sustainable prices through procuring augmentations that provide a net economic benefit. | Objectives and Analysis | 03. Business Performance Objectives | Our Customers | 30 | 18
| Objectives and Analysis | 03. Business Performance Objectives | Our People | 15 | 19
Deliver initiatives in line with approved budgets. | Objectives and Analysis | 03. Business Performance Objectives | Our Business - Sustained Cost Management | 15 | 20
| Objectives and Analysis | 03. Business Performance Objectives | Our Business - Network Service | 15 | 21
| Objectives and Analysis | 04. Business Risks | Death or Injury (Employee) | 15 | 23
| Objectives and Analysis | 04. Business Risks | Death or Injury (Public) | 15 | 24
| Objectives and Analysis | 04. Business Risks | Sustainable and Predictable Pricing | 15 | 25
The proposed solution helps to reduce the risk of a system collapse resulting from a double circuit failure of the Liapootah–Waddamana–Palmerston 220 kV transmission line by splitting it into two sections (i.e. Liapootah–Waddamana and Waddamana–Palmerston). Under the proposed option, if a fault occurs, either one of these two sections can be lost, instead of the entire line, as is the case with the current network arrangement. | Objectives and Analysis | 04. Business Risks | Widespread Power Disruption | 60 | 26
| Objectives and Analysis | 04. Business Risks | Bushfire Start | 15 | 27
| Objectives and Analysis | 04. Business Risks | Loss of Major Industrial | 15 | 28
Implementation will provide a positive net market benefit and will reduce the cost to customers. | Objectives and Analysis | 04. Business Risks | Customer Focus | 15 | 29
| Objectives and Analysis | 04. Business Risks | Business Continuity Management | 15 | 30
| Objectives and Analysis | 04. Business Risks | Cyber Security | 15 | 31
| Objectives and Analysis | 04. Business Risks | Private Assets | 15 | 32
| Objectives and Analysis | 04. Business Risks | Energy Policy and Regulation | 15 | 33
| Objectives and Analysis | 04. Business Risks | Project Marinus (D&A) | 15 | 34
| Objectives and Analysis | 04. Business Risks | Tasmanian Power System Complexity | 15 | 35
| Objectives and Analysis | 04. Business Risks | Emerging Complexity of the NEM | 15 | 36
#1 - Towards 2030 | Objectives and Analysis | 05. Strategic Objectives | Strategic Objectives | 15 | 38
Strategic planning of the network, including supporting transmission for Marinus Link - Reducing network losses will allow more energy to be delivered from what is generated. Long-term solutions to address network complexities such as inertia and fault-level shortfalls - Establishing a 220/110 kV network transformer at Waddamana Substation will improve system strength by increasing the coupling between Upper Derwent 110 kV generation and system strength nodes. | Objectives and Analysis | 05. Strategic Objectives | Strategic Document #1 | 90 | 39
| Objectives and Analysis | 05. Strategic Objectives | Strategic Document #2 | 15 | 40
| Objectives and Analysis | 05. Strategic Objectives | Strategic Document #3 | 15 | 41
| Objectives and Analysis | 05. Strategic Objectives | Strategic Document #4 | 15 | 42
| Objectives and Analysis | 05. Strategic Objectives | Strategic Document #5 | 15 | 43
The objective is to procure a solution that maximises the benefits to all those who participate in the market. | Objectives and Analysis | 06. Project Objectives | Project Objectives | 15 | 44
Benchmarking is not applicable to this IES. | Objectives and Analysis | 07. Options Analysis | Benchmarking | 15 | 45
Expert findings is not applicable to this IES. | Objectives and Analysis | 07. Options Analysis | Expert Findings | 15 | 46
TasNetworks is expecting to commission the most economical option (WA transformer – 2027) by 2027. This option is economic to implement as soon as possible. | Objectives and Analysis | 08. Investment Timing | Investment Timing | 30 | 47
All options provide additional benefits to system strength and the stability of the power system. Establishing a 220/110 kV network transformer at either Waddamana or Tungatinah substations will improve system strength by increasing the coupling between the Upper Derwent 110 kV generation and the Waddamana 220 kV system strength node. It is noted that the benefit will vary between the Waddamana and Tungatinah locations, which is to be further assessed. The benefit will also vary between the various option timings with the 2027 option timings providing the benefit ahead of 2037 option timings. This benefit will reduce the reliance on currently-contracted synchronous condenser support to maintain the required system strength levels in the network. Splitting the Liapootah–Waddamana–Palmerston 220 kV circuit into two sections will improve the system security due to a double circuit failure of the Liapootah–Waddamana–Palmerston line significantly by reducing the contingency size. This is proposed across all options, however the benefit will be realised earlier in the 2027 option timings compared to the 2037 option timings. This has not been quantified at this stage. However, they are not expected to change the preferred option, and the majority of options already provide a net economic benefit without these additional benefits. The benefits to TasNetworks from implementation of the preferred option will be to: - reduce network losses; - provide the most economic solution to customers through proceeding with augmentations which provide a net economic benefit; - increase the security of the network and reduce the impact of double circuit failure by splitting the existing Liapootah–Waddamana–Palmerston 220 kV transmission circuits into two at Waddamana Substation; and - benefit system strength by increasing the coupling between Upper Derwent 110 kV generation and Waddamana 220 kV system strength node. | Objectives and Analysis | 09. Expected Outcomes and Benefits | Expected Outcomes and Benefits | 345 | 48
The following assumptions were made in developing the options: A network transformer at Waddamana Substation with conversion of Waddamana–Palmerston 110 kV transmission flows to 220 kV Previous analysis identified a need for the upgrading of the existing Waddamana–Palmerston 110 kV transmission circuit to 220 kV by 2037, resulting from the forecast wind developments in the Central Highlands REZ reaching 790 MW. When this occurs, a network transformer in the area is needed as an alternative to the existing Waddamana–Palmerston 110 kV transmission circuit to keep the connection from the Upper Derwent 110 kV to the northern transmission network, if a network transformer has not already been installed as a loss reduction measure. The upgrade of the Waddamana–Palmerston 110 kV transmission circuit to 220 kV is common for all options. Therefore, its cost is not included in the options analysis. A network transformer installed in the area by 2037, is considered as the base line for the options analysis. Replacement of Tungatinah–Waddamana 110 kV transmission lines Condition assessment reports for the Tungatinah–Waddamana 110 kV transmission lines (TL425 and TL426) were prepared in 2018, indicating that these circuits are expected to remain serviceable for another 20 years (i.e., 2038). By that time, these circuits will be 82 and 85 years old respectively and it is assumed that these circuits are to be replaced by that time, if a 220 kV connection is not established at Tungatinah. The requirement of these circuits directly links to the remaining connection from Waddamana Substation 110 kV bus to the rest of the network (i.e., the proposed network transformer at Waddamana Substation and Waddamana–Palmerston 110 kV transmission circuit). The replacement for TL425 and TL426 or alternative development necessary under each option, is included in the analysis in 2038. | Objectives and Analysis | 10. Assumptions | Assumptions | 360 | 49
This project will be required to undertake the regulatory investment test for transmission (RIT-T), as the most expensive credible option exceeds the current cost threshold ($7 million). | Objectives and Analysis | 11. Regulatory Considerations | Regulatory Investment Test | 30 | 50
No | Objectives and Analysis | 11. Regulatory Considerations | Meet or manage the expected demand for Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 51
No | Objectives and Analysis | 11. Regulatory Considerations | Comply with all applicable regulatory obligations associated with the provision of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 52
Yes | Objectives and Analysis | 11. Regulatory Considerations | Maintain the quality, reliability and security of supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 53
No | Objectives and Analysis | 11. Regulatory Considerations | Maintain the reliability and security of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 54
No | Objectives and Analysis | 11. Regulatory Considerations | Maintain the safety of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 55
The preferred Option is Option 2, which includes installation of a 220/110 kV network transformer at Waddamana substation and associated necessary works at Waddamana Substation. This option provides the most economic solution to reduce network losses in the Upper Derwent 110 kV transmission network. It is the preferred option in the base case and the majority of sensitivities analysed. This option contributes to mitigating business risks by implementing projects that provide a net market benefit to support customer focus, and reduce the risk of widespread power disruption though minimising impact of double circuit failures. It is recommended that the preferred option (option 2) is approved and progressed as it best satisfies the customer and business needs. | Objectives and Analysis | 12. Recommendation | Recommendation | 135 | 56
This option is the ‘business as usual’ development of the network and includes the following works to be commissioned in 2037 (Tungatinah–Waddamana 110 kV circuit replacement in 2038): - Install a network transformer at Waddamana Substation; - Split the existing Liapootah–Waddamana–Palmerston 220 kV circuits into Liapootah–Waddamana and Waddamana–Palmerston; and - Replace Tungatinah–Waddamana 110 kV circuits (by 2038). The installation of a Waddamana network transformer is required to keep a connection from Tungatinah to the northern transmission network as an alternative to the Waddamana–Palmerston 110 kV circuit. The Tungatinah–Waddamana circuit replacement is also to keep the northern connection by addressing the issue of those asset lives. | Option 1 | Description |  | 120
This is not the highest NPV option. | Option 1 | Reason for selection/rejection |  | 15
This option includes the following works to be commissioned in 2037 : - Install a network transformer and 220 kV switchyard at Tungatinah Substation; - Build a double circuit 220 kV transmission line from Dee to Tungatinah; - Install two 220 kV cables from Tarraleah Power Station to the new Tungatinah 220 kV switchyard (approx. 500 m); - Split the existing Liapootah–Waddamana–Palmerston 220 kV circuits into Liapootah–Waddamana (now becoming Liapootah– Tungatinah–Waddamana) and Waddamana–Palmerston; and - Replace Tungatinah–Lake Echo section of TL425 (in 2038). By establishing a network transformer at Tungatinah Substation, it would provide a connection from Tungatinah to the northern transmission network. The rearrangement of the Liapootah–Waddamana–Palmerston 220 kV circuits at Waddamana is needed to make them three ended circuits instead of four ended circuits, which is unacceptable form a network protection perspective. | Option 2 | Description |  | 150
This is not the highest NPV option (marginally lower to the preferred option). | Option 2 | Reason for selection/rejection |  | 15
This option includes the same scope as Option 0, except that it is to be commissioned in 2027 (replacement of the Tungatinah–Waddamana 110 kV circuits remains in 2038) to reduce the transmission losses in the Upper Derwent area of the 110 kV network. | Option 3 | Description |  | 15
This is the highest NPV option. It also has additional benefit. | Option 3 | Reason for selection/rejection |  | 15
This option includes the same scope as Option 1, except that it is to be commissioned in 2027 (replacement of the Tungatinah–Lake Echo section of the TL425 remains in 2038), to reduce the transmission losses in the Upper Derwent area of the 110 kV network. | Option 4 | Description |  | 15
This is not the highest NPV option. | Option 4 | Reason for selection/rejection |  | 15
This option includes the same scope and timing as Option 3, except for the existing Tarraleah Power Station maintains a 110 kV connection to the Tungatinah Substation. | Option 5 | Description |  | 15
This is not the highest NPV option. | Option 5 | Reason for selection/rejection |  | 15
| Option 6 | Description
| Option 6 | Reason for selection/rejection