## Cover
Jemena Electricity Networks (Vic) Ltd
2021-26 Electricity Distribution Price Review Revised Proposal
Attachment 04-04
Coolaroo and Greenvale Bushfire Mitigation Obligation Compliance Works cost estimate
2020-12-03
Public
Project name | COO and GVE bushfire mitigation compliance (REFCL) works
Dollar basis | Direct unescalated capex (Real 2018 - Mid Period)

## GVE
ITEM | Qty | Unit |  | Unit Labour (hr) | Unit Labour $/hr) | Total Labour (hr) | Total Labour ($) | Contract | Unit | Total | Unit | Total | Unit
REFCL
GFN | 1 | ea | [7 empty] | 4000000 | ea | 4000000
Subtotals - REFCL Works | [11 empty] | 4000000
Civil & structural
Site preparation & subsurface works | 1 | site | [7 empty] | 1300000 | site | 1300000
Humeceptor | 1 | ea | [7 empty] | 82500 | site | 82500
Access Road | 1 | site | [7 empty] | 20000 | site | 20000
Switchroom/Control Building | 1 | site | [7 empty] | 540000 | site | 540000
Earth Grid trenching | 1 | site | [7 empty] | 35000 | site | 35000
Transformer foundations & enclosure | 1 | site | [7 empty] | 450000 | site | 450000
Other Foundations | 1 | Bus | [7 empty] | 100000 | site | 100000
Conduits & pits | 1 | site | [7 empty] | 150000 | site | 150000
Security Fence | 1 | site | [7 empty] | 130000 | site | 130000
Yard surfacing | 1 | site | [7 empty] | 87500 | site | 87500
Subtotal - Civils & Structural | [11 empty] | 2895000
Primary & Secondary
Transformer 20/33MVA | 1 | ea | 850000 | [8 empty] | 850000
66kV CB | 1 | ea | 80000 | [8 empty] | 80000
66kV VT (with structures) | 1 | ea | 35000 | [8 empty] | 35000
66kV Disconnectors (with structures) | 3 | ea | 30000 | [8 empty] | 90000
66kV bus (with structures) | 1 | bus | 50000 | [8 empty] | 50000
66kV Surge Diverters | 6 | ea | 1500 | [8 empty] | 9000
22kV switchboard | 1 | ea | 450000 | [8 empty] | 450000
Transformer cables | 1 | lot | 86500 | [8 empty] | 86500
Feeder cables | 1 | lot | 15000 | [8 empty] | 15000
22kV CHP | 3 | ea | 20000 | [8 empty] | 60000
Station Services Transformer | 2 | ea | 20000 | [8 empty] | 40000
NER | 1 | ea | 50000 | [8 empty] | 50000
NER cables | 1 | lot | 10000 | [8 empty] | 10000
Earthgrid | 1 | lot | 80000 | [8 empty] | 80000
Miscellaneous Primary | 1 | site | 30000 | [8 empty] | 30000
Protection Panels & Relays | 18 | panels | 50000 | [8 empty] | 900000
Comms/SCADA | 1 | site | 50000 | [8 empty] | 50000
FOC connections | 10 | km | [5 empty] | 80000 |  |  |  | 800000
Battery systems | 1 | ea | 200000 | [8 empty] | 200000
AC distribution system | 1 | site | 50000 | [8 empty] | 50000
Secondary cables, tray's, ducts etc. | 1 | bus | 60000 | [8 empty] | 60000
Miscellaneous secondary | 1 | site | 30000 | [8 empty] | 30000
Installation Labour | 1 | site |  | 8000 | 120 | 8000 | 960000 |  |  |  |  | 960000
Network Operator | 1 |  |  |  | 120 | 600 | 72000 |  |  |  |  | 72000
Commissioning | 1 | [6 empty] | 500000 |  |  |  | 500000
Subtotal - Primary & Secondary | [5 empty] | 8600 | 1032000 |  |  |  |  | 5557500
ZSS Design & PM
Project management team | 1 |  |  | 6000 | hrs | 160 | 960000 |  |  |  |  | 960000
Asset Management & Design | 1 | [6 empty] | 1100000 |  |  |  | 1100000
Subtotals - Design & PM | [11 empty] | 2060000
Other items
Land Procurement | 1 |  | 2800000 | [6 empty] | 2800000 | site | 2800000
Site Investigations & assessment (eg geotech) | 1 | [6 empty] | 100000 | ea |  |  | 100000
Plant Hire | 1 | [6 empty] | 100000 | ea |  |  | 100000
Site Facilities | 1 | [6 empty] | 100000 | ea |  |  | 100000
Subtotals - Other items | [11 empty] | 3100000
22kV & 66kV works
22kV feeder - OH | 0.1 | km | 200000 | [8 empty] | 20000
22kV feeder - UG | 1 | km | 1350000 | [8 empty] | 1350000
66kV works | 5.8 | km | 650000 | [8 empty] | 3770000
Hardening & Balancing | 1 | Lot | 1500000 | [6 empty] | 1500000 |  | 1500000
Subtotals - 22kV & 66kV Feeder Works | [11 empty] | 6640000
Risk
Allow 10% on Civils | 10% |  | 2895000 | [8 empty] | 289500
Subtotal - Risk | [11 empty] | 289500
Total | [11 empty] | 24542000

## COO
ITEM | Qty | Unit |  | Unit Labour (hr) | Unit Labour $/hr) | Total Labour (hr) | Total Labour ($) | Contract | Unit | Total | Unit | Total | Unit
REFCL
GFN | 0 | ea | [7 empty] | 4000000 | ea | 0
Subtotals - REFCL Works | [11 empty] | 0
Civil & structural
Site preparation & subsurface works | 0 | site | [7 empty] | 1300000 | site | 0
Humeceptor | 0 | ea | [7 empty] | 82500 | site | 0
Access Road | 0 | site | [7 empty] | 20000 | site | 0
Switchroom/Control Building | 0 | site | [7 empty] | 540000 | site | 0
Earth Grid trenching | 0 | site | [7 empty] | 35000 | site | 0
Transformer foundations & enclosure | 0 | site | [7 empty] | 450000 | site | 0
Other Foundations | 0 | Bus | [7 empty] | 100000 | site | 0
Conduits & pits | 0 | site | [7 empty] | 150000 | site | 0
Security Fence | 0 | site | [7 empty] | 130000 | site | 0
Yard surfacing | 0 | site | [7 empty] | 87500 | site | 0
Subtotal - Civils & Structural | [11 empty] | 0
Primary & Secondary
Transformer 20/33MVA | 0 | ea | 850000 | [8 empty] | 0
66kV CB | 0 | ea | 80000 | [8 empty] | 0
66kV VT (with structures) | 0 | ea | 35000 | [8 empty] | 0
66kV Disconnectors (with structures) | 0 | ea | 30000 | [8 empty] | 0
66kV bus (with structures) | 0 | bus | 50000 | [8 empty] | 0
66kV Surge Diverters | 0 | ea | 1500 | [8 empty] | 0
22kV switchboard | 0 | ea | 450000 | [8 empty] | 0
Transformer cables | 0 | lot | 86000 | [8 empty] | 0
Feeder cables | 0 | lot | 15000 | [8 empty] | 0
22kV CHP | 0 | ea | 20000 | [8 empty] | 0
Station Services Transformer | 0 | ea | 20000 | [8 empty] | 0
NER | 0 | ea | 50000 | [8 empty] | 0
NER cables | 0 | lot | 10000 | [8 empty] | 0
Earthgrid | 0 | lot | 80000 | [8 empty] | 0
Miscellaneous Primary | 0 | site | 30000 | [8 empty] | 0
Protection Panels & Relays | 0 | panels | 50000 | [8 empty] | 0
Comms/SCADA | 0 | site | 50000 | [8 empty] | 0
FOC connections | 0 | km | [5 empty] | 80000 |  |  |  | 0
Battery systems | 0 | ea | 200000 | [8 empty] | 0
AC distribution system | 0 | site | 50000 | [8 empty] | 0
Secondary cables, tray's, ducts etc. | 0 | bus | 60000 | [8 empty] | 0
Miscellaneous secondary | 0 | site | 30000 | [8 empty] | 0
Installation Labour | 0 | site | [9 empty] | 0
Network Operator | 0 | [10 empty] | 0
Commissioning | 0 | [10 empty] | 0
Subtotal - Primary & Secondary | [11 empty] | 0
ZSS Design & PM
Project management team | 1 |  |  | 1200 | hrs | 160 | 192000 |  |  |  |  | 192000
Asset Management & Design | 1 | [6 empty] | 250000 |  |  |  | 250000
Subtotals - Design & PM | [11 empty] | 442000
Other items
Land Procurement | 0 | [9 empty] | site | 0
Site Investigations & assessment (eg geotech) | 0 | [6 empty] | 100000 | ea |  |  | 0
Plant Hire | 0 | [6 empty] | 100000 | ea |  |  | 0
Site Facilities | 0 | [6 empty] | 100000 | ea |  |  | 0
Subtotals - Other items | [11 empty] | 0
22kV & 66kV works
22kV feeder - OH | 0.2 | km | 200000 | [8 empty] | 40000
22kV feeder - UG | 3.3 | km | 1350000 | [8 empty] | 4455000
66kV works | 0 | km | 650000 | [8 empty] | 0
Hardening & Balancing | 0 | Lot | 1500000 | [8 empty] | 0
Subtotals - 22kV & 66kV Feeder Works | [11 empty] | 4495000
Risk
Allow 10% on Feeder works | 10% |  | 4455000 | [8 empty] | 445500
Subtotal - Risk | [11 empty] | 445500
Total | [11 empty] | 5382500