## Input¦Inflation
CPI escalation
| Inflation escalator - real June 2018 dollars to real June 2021 dollars | 1.0419 | Updated 14 Oct 20
| Inflation escalator - real June 2018 dollars to real December 2020 dollars | 1.0403 | Updated 14 Oct 20
| Inflation escalator - real June 2020 dollars to real June 2018 dollars | 0.96726 | Updated 14 Oct 20

## Input¦Cost escalation
Opex Step Change Forecast - cost escalation
| Labour Escalation Index | Source | FY22 | FY23 | FY24 | FY25 | FY26
| BIS Labour escalation from 2018 to nominal | Calculated | 1.0351 | 1.0396 | 1.045 | 1.0541 | 1.0665 | Updated 14 Oct 20
| Incremental cumulative escalation factor | Calculated | 3.508% | 3.958% | 4.501% | 5.406% | 6.649%

## Input¦Fault test workings
Raw activity cost input - real June 2018 dollars, excluding real price escalation
Primary earth fault testing
This is a mandated annual compliance test. As per the current practice ESV witness tests on every feeder before the bushfire season.
One day will be required to test one feeder and will include creating high impedence and low impedence tests on each phase thereby carrying out six tests on the day.
| Break-down of estimated activities required per feeder test |  | Number of resources required on test | $ rate/hr | Hrs required per feeder test | $ Total cost | Notes
| Team #1 - at fault site | Fault truck crew | 2 | 130 | 15 | 1950 | Undertake the connections at test points
|  | Tester in charge | 1 | 128 | 7.5 | 960 | Supervise the testing at site
|  | Testers | 2 | 128 | 15 | 1920 | Carry out the testing
|  | Line crew | 2 | 100 | 15 | 1500 | Test connections
|  | Field crew | 2 | 100 | 15 | 1500 | To attend to any unplanned faults
|  | Underground crew | 2 | 100 | 15 | 1500 | To attend to any unplanned faults
| Team #2 - control centre | Dedicated controller | 1 | 123.72 | 7.5 | 927.9 | To monitor all switching and devices such as sectionalisers
| Team #3 - at zone substation | Tester in charge | 1 | 128 | 7.5 | 960 | Be available to manage testing issues at ZSS
|  | Engineer | 1 | 140 | 7.5 | 1050 | Supervise & oversee any issues at ZSS
|  | Compliance engineers | 3 | 120 | 22.5 | 2700 | Record data
| Other cost items | EWP hire | 8 | 200 | 60 | 12000 | Required for connections during the tests
|  | Travel time (1 hr per test) |  |  |  | 3595.72 | 1 hour travel per site resource per test
|  | Traffic management |  |  |  | 805
|  | Network access |  | 124 | 2 | 248
|  | Switching instructions |  | 124 | 2 | 248
| Sub-total per feeder test |  |  |  |  | 31864.62
| Allowance for environmental factors |  |  |  |  | 6372.924 | 20% allowance for test not being able to be completed due to any reason, such as weather
| Pre-testing activities |  |  |  |  | 19118.772 | Assumed 50% of activities will need to be performed as a pre-test prior to attendance of ESV at actual test
| Total for fault testing per feeder |  |  |  |  | 57356.316
| Number of feeders - GVE |  | 3 |  |  | 172068.948
| Number of feeders - KLO |  | 1 |  |  | 57356.316
| Total |  |  |  |  | 229425.264

## Input¦Forecast
Raw activity cost input - real June 2020 dollars, excluding real price escalation
[5 empty] | FY22 | FY23 | FY24 | FY25 | FY26 | Notes and assumptions
| Development of specifications and procurement of trest truck and gear | $'s | Real 2020 | Mid Year | 0 | 30000 | 0 | 0 | 0 | Development of specifications and procurement arrangements (e.g. liaison with vendor on fabrication) for test truck and equipment, as these are not off-the-shelf products.
Assumed 20 days @ $1500/day as this activity would need to be undertaken by an external consultant with specialist knowledge of this equipment and requirements.
| Primary earth fault testing | $'s | Real 2020 | Mid Year | 0 | 0 | 229425.264 | 229425.264 | 229425.264 | Refer to sheet 'Input¦Fault test workings'. Required annually from FY24 onwards.
| Insulation testing | $'s | Real 2020 | Mid Year | 0 | 0 | 40000 | 40000 | 40000 | Assumed $20k per REFCL per discussion with other DNSPs. 1 x REFCL at COO and 1 x REFCL for KLO22. Required from FY24 onwards
| Data analysis and reports | $'s | Real 2020 | Mid Year | 0 | 0 | 42000 | 42000 | 42000 | Analysis of data from annual testing and business-as-usual REFCL operations. Assumed total effort of 9 weeks (337.5 hrs @ $124.44/hr) across the year. Required from FY24 onwards
| Network balancing | $'s | Real 2020 | Mid Year | 0 | 0 | 66300 | 66300 | 66300 | Network monitoring. Assumed 0.5 day per week for 11 months (24 days) and 2 weeks (10 days) prior to compliance testing = total 255 hrs p.a. Allowed for 2 man crew @ $130/hr (including fleet) = $66,300 p.a.. Required from from FY24 onwards
| Equipment maintenance | $'s | Real 2020 | Mid Year | 0 | 0 | 6000 | 6000 | 6000 | Estimate of additional maintenance cost for equipment added as a result of network hardening and balancing, based on high-level discussion with other DNSPs.
| Change manangement and documentation | $'s | Real 2020 | Mid Year | 0 | 0 | 4800 | 4800 | 4800 | Making changes to work instructions, O&M procedures, safety procedures and asset management strategies to integrate advanced REFCL equipment (as JEN does not have any of these assets currently).
Initial documentation changes to occur as part of REFCL capital works projects.
For annual documentation review, updates and communications required for FY24 onwards, assumed 5 days p.a. @ $120/hr = total $4800 p.a.
| Training and capability building | $'s | Real 2020 | Mid Year | 0 | 0 | 19740 | 19740 | 19740 | Provision of training to staff and contractors who need to work in proximity to advanced REFCL equipment (as JEN does not have any of these assets currently).
Initial training to occur as part of REFCL capital works projects.
For annual refresher training required for FY24 onwards, assumed 5 days @ $1500/day for training prepratation and delivery, plus 8 hours for trainees (10 staff @ $120/hr and 1 staff @ 80/hr) plus $2000 for documentation and facilities.
Opex Step Change Forecast - real June 2018 dollars | [9 empty] | Section check: | Ok
Forecast
| Direct expenditure items | Unit | Basis | Timing | FY22 | FY23 | FY24 | FY25 | FY26 | Labour proportion (%) |  | Total FY22-FY26
| Development of specifications and procurement of trest truck and gear | $'s | Real 2018 | Mid Year | 0 | 29017.7169 | 0 | 0 | 0 | 100% | Ok
| Primary earth fault testing | $'s | Real 2018 | Mid Year | 0 | 0 | 221913.2453 | 221913.2453 | 221913.2453 | 100% | Ok
| Insulation testing | $'s | Real 2018 | Mid Year | 0 | 0 | 38690.2892 | 38690.2892 | 38690.2892 | 100% | Ok
| Data analysis and reports | $'s | Real 2018 | Mid Year | 0 | 0 | 40624.8036 | 40624.8036 | 40624.8036 | 100% | Ok
| Network balancing | $'s | Real 2018 | Mid Year | 0 | 0 | 64129.1543 | 64129.1543 | 64129.1543 | 100% | Ok
| Equipment maintenance | $'s | Real 2018 | Mid Year | 0 | 0 | 5803.5434 | 5803.5434 | 5803.5434 | 100% | Ok
| Change manangement and documentation | $'s | Real 2018 | Mid Year | 0 | 0 | 4642.8347 | 4642.8347 | 4642.8347 | 100% | Ok
| Training and capability building | $'s | Real 2018 | Mid Year | 0 | 0 | 19093.6577 | 19093.6577 | 19093.6577 | 100% | Ok
| Real labour cost escalation | $'s | Real 2018 | Mid Year | 0 | 1148.4366 | 17776.2735 | 21347.0825 | 26256.1232
| Total | $'s | Real 2018 | Mid Year | 0 | 30166.1535 | 412673.8018 | 416244.6107 | 421153.6514 |  |  | 1280238.2174

## Output¦Summary
Opex Step Change Forecast - output
| Opex step change title: | REFCL testing and maintenance
| Escalator check: | Ok
| Opex step change forecast | Unit | Basis | Timing | FY22 | FY23 | FY24 | FY25 | FY26 | Total FY22-26
| REFCL testing and maintenance | $millions | Real 2018 | Mid Year | 0 | 0.030166 | 0.41267 | 0.41624 | 0.42115 | 1.2802
| REFCL testing and maintenance | $millions | Real 2020 | End Year | 0 | 0.031382 | 0.4293 | 0.43302 | 0.43812 | 1.3318

## Output¦Table for report
Output for step change report - Table x - Opex cost estimate for REFCL maintenance and testing (June 2021 dollars, $M)
| Activity | RY22 | RY23 | RY24 | RY25 | RY26
| Primary earth fault testing | 0 | 0 | 0.24161 | 0.24371 | 0.24658
| Insulation testing | 0 | 0 | 0.042125 | 0.04249 | 0.042991
| Data analysis and reporting | 0 | 0 | 0.044231 | 0.044614 | 0.04514
| Network balancing | 0 | 0 | 0.069823 | 0.070427 | 0.071257
| Equipment maintenance | 0 | 0 | 0.0063188 | 0.0063735 | 0.0064486
| Change management | 0 | 0 | 0.005055 | 0.0050988 | 0.0051589
| Training | 0 | 0 | 0.020789 | 0.020969 | 0.021216
| Development of test equipment specifications | 0 | 0.03143 | 0 | 0 | 0
| Total | 0 | 0.03143 | 0.42996 | 0.43368 | 0.43879
|  | Ok | Ok | Ok | Ok | Ok