## Sheet1
[5 empty] | DNSP forecast | RM study 1 | RM study 2 | RM study 3 | DNSP forecast | RM study 1 | RM study 2 | RM study 3 | RM study 4 | RM study 1 | RM study 2 | RM study 3 | RM study 1 | DNSP forecast | RM study 4
[5 empty] | AC | AC | AC | AC | AD | AD | AD | AD | AD | Z | Z | Z | AA | AA | AA
| Model Asset |  | DNSP calibration (2012/13-2016/17) |  | AC: Regulatory period forecast (2019/20-2023/24) - Repex ($'000); AD: Regulatory period forecast (2019/20-2023/24) - volumes; Z: Model parameters
[6 empty] | Repex model - AER assessment studies |  |  |  | Repex model - AER assessment studies |  |  | Repex model | unit cost ($'000) |  |  | Lives (years)
Assessed | group | category | Repex ($'000) | volumes | DNSP forecast | historical | forecast | AER benchmark | DNSP forecast | historical | forecast | AER benchmark | BM life | historical | forecast | AER benchmark | historical | forecast* | AER benchmark*
y | Poles |  | 8894.9321 | 223 | 20841.5978 | 29363.3042 | 11924.4862 | 7525.0398 | 1184 | 724.7952 | 724.7952 | 724.7952 | 3243.0542 | [6 empty] | 8.9171
y | OH conductors |  | 2466.9874 | 39.3916 | 5174.5139 | 5488.8214 | 9751.4321 | 6843.1336 | 53.9238 | 106.7209 | 106.7209 | 106.7209 | 36.4442 | [6 empty] | -4.5769
y | UG cables |  | 28778.9233 | 540.6405 | 32038.8841 | 64217.13 | 53454.9984 | 72660.5242 | 418.858 | 923.4984 | 923.4984 | 923.4984 | 830.4371 | [6 empty] | -21.4161
y | Services |  | 532.8218 | 110 | 387.3967 | 2043.2464 | 73.7359 | 598.7677 | 2216.198 | 421.8373 | 421.8373 | 421.8373 | 1633.4918 | [6 empty] | 0.31366
y | Transformers |  | 26080.7312 | 492 | 24948.4722 | 19787.317 | 29453.7573 | 36658.3686 | 665.2851 | 415.2467 | 415.2467 | 415.2467 | 231.3536 | [6 empty] | -4.5053
y | Switchgear |  | 48167.9617 | 1065 | 17135.9908 | 27169.415 | 22943.5854 | 20561.0973 | 657.4854 | 940.1483 | 940.1483 | 940.1483 | 204.524 | [6 empty] | -5.8076
| Assessed total |  | 114922.3575 | 2470.0321 | 100526.8555 | 148069.234 | 127601.9952 | 144846.9313 | 5195.7502 | 3532.2468 | 3532.2468 | 3532.2468 | 6179.3049 | [6 empty] | -27.0751
| Not assessed |  | 86972.2155 | 2843.2 | AC: 45651.3638; AD: 2651.2241
|  | Total | 201894.573 | 5313.2321 | AC: 146178.2193; AD: 7846.9743
| 127601.9952 | AER alternative estimate for assessable repex - ($'000)
supports DNSP forecast
| Model Asset |  | DNSP calibration (2012/12-2016/17) |  | AC: Regulatory period forecast (2019/20-2023/24) - Repex ($'000); AD: Regulatory period forecast (2019/20-2023/24) - volumes; Z: Model parameters
[6 empty] | Repex model - AER assessment studies |  |  |  | Repex model - AER assessment studies |  |  | Repex model | unit cost ($'000) |  |  | Lives (years)
Assessed | group | category | Repex ($'000) | volumes | DNSP forecast | historical | forecast | AER benchmark | DNSP forecast | historical | forecast | AER benchmark | BM life | historical | forecast | AER benchmark | historical | forecast* | AER benchmark*
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ˂ = 1 kV; Wood - Staked | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ˂ = 1 kV; Wood - Unstaked | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 1 kV & < = 11 kV; Wood - Staked | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 1 kV & < = 11 kV; Wood - Unstaked | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ˃ 11 kV & < = 22 kV; Wood - Staked | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ˃ 11 kV & < = 22 kV; Wood - Unstaked | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 22 kV & < = 66 kV; Wood - Staked | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 22 kV & < = 66 kV; Wood - Unstaked | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 66 kV & < = 132 kV; Wood - Staked | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 66 kV & < = 132 kV; Wood - Unstaked | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 132 kV; Wood - Staked | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 132 kV; Wood - Unstaked | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ˂ = 1 kV; Concrete | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 1 kV & < = 11 kV; Concrete | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ˃ 11 kV & < = 22 kV; Concrete | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Poles | > 22 kV & < = 66 kV; Concrete | 0 | 0 | 0 | 0.49023 | 0.49023 | 0.49023 | 0 | 0.024011 | 0.024011 | 0.024011 | 29.1793 | 20.417 | 20.417 | 20.417 | 79.3832 | 84.7097 | 45.1145
|  | > 66 kV & < = 132 kV; Concrete | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 132 kV; Concrete | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Poles | ˂ = 1 kV; Steel | 3103.9005 | 77.8974 | 4002.437 | 9387.6582 | 3752.6293 | 2138.1454 | 251.2821 | 235.5986 | 235.5986 | 235.5986 | 793.0947 | 39.846 | 15.9281 | 9.0754 | 66.3845 | 65.9516 | 57.3701
| Poles | > 1 kV & < = 11 kV; Steel | 2898.3004 | 50.0769 | 3583.9161 | 9597.8294 | 2611.9826 | 1415.6417 | 227.5385 | 165.8316 | 165.8316 | 165.8316 | 725.0909 | 57.877 | 15.7508 | 8.5366 | 63.2928 | 61.1514 | 51.5377
| Poles | ˃ 11 kV & < = 22 kV; Steel | 1450.8398 | 74.188 | 6818.535 | 4697.7029 | 4122.4435 | 2410.4111 | 397.3162 | 240.2149 | 240.2149 | 240.2149 | 1542.5213 | 19.5563 | 17.1615 | 10.0344 | 67.3315 | 63.9389 | 53.5236
| Poles | > 22 kV & < = 66 kV; Steel | 1057.2577 | 14.8376 | 663.9825 | 3495.853 | 680.5979 | 915.7359 | 47.8632 | 49.061 | 49.061 | 49.061 | 77.6255 | 71.2553 | 13.8725 | 18.6653 | 59.1057 | 59.2682 | 55.9882
| Poles | > 66 kV & < = 132 kV; Steel | 384.6337 | 6 | 5772.7273 | 2183.7704 | 756.3426 | 644.6155 | 260 | 34.0652 | 34.0652 | 34.0652 | 75.5425 | 64.1056 | 22.2028 | 18.923 | 54.5367 | 40.5357 | 50
|  | > 132 kV; Steel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OH conductors | ˂ = 1 kV | 196.7198 | 1.1716 | 1058.1984 | 935.3654 | 1151.0263 | 368.3613 | 5.1217 | 5.571 | 5.571 | 5.571 | 4.7737 | 167.9 | 206.6116 | 66.1216 | 74.2971 | 74.7539 | 75.1273
| OH conductors | > 1 kV & < = 11 kV | 627.9007 | 3.097 | 612.9646 | 2113.6822 | 2367.9971 | 613.5684 | 2.6986 | 10.4253 | 10.4253 | 10.4253 | 1.8192 | 202.7448 | 227.1387 | 58.8536 | 65.3001 | 73.4302 | 75.4291
| OH conductors | ˃ 11 kV & < = 22 kV ; SWER | 0 | 0 | 0 | 0.44849 | 0.44849 | 0.44849 | 0 | 0.0090398 | 0.0090398 | 0.0090398 | 3.1974e-08 | 49.613 | 49.613 | 49.613 | 50 | 52.9877 | 80.1479
|  | ˃ 11 kV & < = 22 kV ; Single-Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OH conductors | ˃ 11 kV & < = 22 kV ; Multiple-Phase | 940.5908 | 35.123 | 3060.3272 | 2428.387 | 6221.0219 | 5850.6355 | 44.6082 | 90.6793 | 90.6793 | 90.6793 | 14.353 | 26.7799 | 68.6046 | 64.5201 | 59.1861 | 64.0198 | 70.74
| OH conductors | > 22 kV & < = 66 kV | 701.7761 | 0 | 176.0541 | 5.2504 | 5.2504 | 3.3891 | 0.51643 | 0.015401 | 0.015401 | 0.015401 | 0.02679 | 340.9091 | 340.9091 | 220.0523 | 88.8614 | 75.8711 | 87.0063
| OH conductors | > 66 kV & < = 132 kV | 0 | 0 | 266.9696 | 5.6878 | 5.6878 | 6.7309 | 0.97889 | 0.020855 | 0.020855 | 0.020855 | 15.4715 | 272.7273 | 272.7273 | 322.7396 | 72.1993 | 60.174 | 50
|  | > 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UG cables | ˂ = 1 kV | 375.936 | 0.855 | 2798.5888 | 1256.385 | 716.7835 | 696.7552 | 11.1565 | 2.8574 | 2.8574 | 2.8574 | 1.4973 | 439.6912 | 250.8494 | 243.8402 | 63.9555 | 55.9682 | 67.8862
| UG cables | > 1 kV & < = 11 kV | 15332.1767 | 39.668 | 26123.8925 | 33700.4454 | 43159.5956 | 58718.6823 | 52.7755 | 87.1911 | 87.1911 | 87.1911 | 1.7844 | 386.5125 | 495 | 673.4482 | 45.0144 | 48.6066 | 67.5282
| UG cables | > 11 kV & < = 22 kV | 2771.2221 | 3.2736 | 389.1464 | 3929.2303 | 2157.7061 | 2674.7552 | 0.8371 | 4.6415 | 4.6415 | 4.6415 | 0.61106 | 846.5495 | 464.876 | 576.2738 | 46.0746 | 59.024 | 60.923
|  | > 22 kV & < = 33 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UG cables | > 33 kV & < = 66 kV | 5813.6924 | 0.84395 | 168.8854 | 17858.6525 | 1446.2113 | 3097.9148 | 0.30274 | 2.5925 | 2.5925 | 2.5925 | 0.32844 | 6888.6692 | 557.8512 | 1194.9675 | 48.3389 | 60.3674 | 60
|  | > 66 kV & < = 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 132 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Services | ˂ = 11 kV ; Residential ; Simple Type | 532.8218 | 110 | 387.3967 | 2043.2464 | 73.7359 | 598.7677 | 2216.198 | 421.8242 | 421.8242 | 421.8242 | 1431.0402 | 4.8438 | 0.1748 | 1.4195 | 66.7419 | 55.1943 | 58.4265
| Services | ˂ = 11 kV ; Commercial & Industrial ; Simple Type | 0 | 0 | 0 | 1.3146e-05 | 1.3146e-05 | 1.3146e-05 | 0 | 0.013146 | 0.013146 | 0.013146 | 202.4515 | 0.001 | 0.001 | 0.001 | 109.304 | 113.292 | 61.1129
|  | ˂ = 11 kV ; Residential ; Complex Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ˂ = 11 kV ; Commercial & Industrial ; Complex Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ˂ = 11 kV ; Subdivision ; Complex Type | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 11 kV & < = 22 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 11 kV & < = 22 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 22 kV & < = 33 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 22 kV & < = 33 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 33 kV & < = 66 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 33 kV & < = 66 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 66 kV & < = 132 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 66 kV & < = 132 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 132 kV ; Commercial & Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 132 kV ; Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformers | Pole Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | 0 | 0 | 67.2265 | 25.8518 | 25.8518 | 68.7169 | 10.8459 | 4.1708 | 4.1708 | 4.1708 | 0.46502 | 6.1983 | 6.1983 | 16.4759 | 43.5164 | 37.2739 | 54.9857
| Transformers | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase | 108.251 | 0 | 9.8669e-06 | 8.7953e-05 | 3.2982e-05 | 0.0001167 | 5.9695e-07 | 5.3211e-06 | 5.3211e-06 | 5.3211e-06 | 8.9435e-08 | 16.5289 | 6.1983 | 21.9318 | 43.5164 | 37.2739 | 52.183
|  | Pole Mounted ; < = 22kV ; > 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformers | Pole Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | 254.1286 | 60 | 403.2417 | 163.1443 | 238.7511 | 485.8218 | 65.0563 | 38.5185 | 38.5185 | 38.5185 | 9.4384 | 4.2355 | 6.1983 | 12.6127 | 43.5164 | 37.2739 | 58.1134
| Transformers | Pole Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 3373.847 | 272 | 3691.6075 | 1555.4111 | 2072.6852 | 3409.3758 | 223.3423 | 125.3975 | 125.3975 | 125.3975 | 36.5968 | 12.4038 | 16.5289 | 27.1886 | 39.5934 | 32.0514 | 53.2179
| Transformers | Pole Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase | 0 | 0 | 0.0020123 | 0.032492 | 0.032492 | 0.099908 | 0.00012174 | 0.0019658 | 0.0019658 | 0.0019658 | 6.82e-05 | 16.5289 | 16.5289 | 50.8242 | 39.5934 | 32.0514 | 47.8496
| Transformers | Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Single Phase | 0 | 0 | 1308.1908 | 3680.3192 | 7667.3316 | 3285.8929 | 35.1758 | 98.9597 | 98.9597 | 98.9597 | 124.1853 | 37.1901 | 77.4793 | 33.2044 | 42.8717 | 44.3662 | 40
| Transformers | Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Single Phase | 463.6866 | 17 | 2186.3634 | 43.2637 | 48.347 | 45.4562 | 207.0944 | 0.624 | 0.624 | 0.624 | 0.80743 | 69.3331 | 77.4793 | 72.8466 | 42.8717 | 44.3662 | 40
|  | Kiosk Mounted ; < = 22kV ; > 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformers | Kiosk Mounted ; < = 22kV ; < = 60 kVA ; Multiple Phase | 0 | 0 | 17.5423 | 27.6276 | 57.5574 | 50.2476 | 0.47169 | 0.74287 | 0.74287 | 0.74287 | 0.21159 | 37.1901 | 77.4793 | 67.6394 | 42.8717 | 44.3662 | 52.2155
| Transformers | Kiosk Mounted ; < = 22kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 5546.6455 | 80 | 5715.2818 | 5992.4694 | 6696.5531 | 3403.951 | 73.7652 | 86.4302 | 86.4302 | 86.4302 | 31.2908 | 69.3331 | 77.4793 | 39.3838 | 42.8717 | 44.3662 | 50.7296
| Transformers | Kiosk Mounted ; < = 22kV ; > 600 kVA ; Multiple Phase | 706.2166 | 11 | 1004.2538 | 653.5989 | 978.0784 | 783.0063 | 10.4529 | 10.1804 | 10.1804 | 10.1804 | 2.2311 | 64.2015 | 96.0744 | 76.9129 | 36.6828 | 36.3833 | 49.531
|  | Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Single Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; < = 60 kVA ; Multiple Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformers | Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 60 kVA and < = 600 kVA ; Multiple Phase | 483.4208 | 7 | 1558.6441 | 917.3523 | 1578.0885 | 1013.1877 | 13.1197 | 13.2834 | 13.2834 | 13.2834 | 5.4626 | 69.0601 | 118.8017 | 76.2748 | 51.373 | 51.5091 | 58.7492
| Transformers | Ground Outdoor / Indoor Chamber Mounted; ˂ 22 kV ; > 600 kVA ; Multiple Phase | 1451.3732 | 18 | 1236.4251 | 2005.6909 | 2055.7582 | 3301.4642 | 14.9607 | 24.8747 | 24.8747 | 24.8747 | 1.864 | 80.6318 | 82.6446 | 132.7239 | 40.6814 | 45.3436 | 58.1867
| Transformers | Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; < = 15 MVA | 234.6577 | 1 | 0 | 668.5116 | 1172.9948 | 1172.9948 | 0 | 2.8489 | 2.8489 | 2.8489 | 9.3829 | 234.6577 | 411.739 | 411.739 | 57.3325 | 86.6071 | 40
|  | Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 15 MVA and < = 40 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Ground Outdoor / Indoor Chamber Mounted; > = 22 kV & < = 33 kV ; > 40 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformers | Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; < = 15 MVA | 691.7466 | 2.7368 | 5808.2469 | 839.0432 | 4820.2778 | 4529.9285 | 4 | 3.3196 | 3.3196 | 3.3196 | 3.2858 | 252.7536 | 1452.0617 | 1364.5968 | 57.5125 | 16.7511 | 40
| Transformers | Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 15 MVA and < = 40 MVA | 9310.5415 | 13.6842 | 1482.438 | 2326.2066 | 844.7309 | 6575.9986 | 6 | 3.419 | 3.419 | 3.419 | 3.9652 | 680.3857 | 247.073 | 1923.3956 | 44.4526 | 15.108 | 40
|  | Ground Outdoor / Indoor Chamber Mounted; > 33 kV & < = 66 kV ; > 40 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformers | Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; < = 100 MVA | 3456.216 | 9.5789 | 469.0083 | 888.7939 | 1155.3098 | 8490.8172 | 1 | 2.4633 | 2.4633 | 2.4633 | 1.7285 | 360.8138 | 469.0083 | 3446.9225 | 36.184 | 45.0595 | 40
|  | Ground Outdoor / Indoor Chamber Mounted; > 66 kV & < = 132 kV ; > 100 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Transformers | Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; < = 100 MVA | 0 | 0 | 0 | 1.2013e-05 | 41.4092 | 41.4092 | 0 | 0.012013 | 0.012013 | 0.012013 | 0.43819 | 0.001 | 3446.9225 | 3446.9225 | 76.4605 | 80.9314 | 40
|  | Ground Outdoor / Indoor Chamber Mounted; > 132 kV ; > 100 MVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ˂ = 11 kV ; Fuse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Switchgear | ˂ = 11 kV ; Switch | 13726.1812 | 567.115 | 8300.8073 | 10930.2774 | 11789.2387 | 5151.7437 | 317.9708 | 451.5986 | 451.5986 | 451.5986 | 50.2472 | 24.2035 | 26.1056 | 11.4078 | 44.2612 | 48.4358 | 63.2149
| Switchgear | ˂ = 11 kV ; Circuit Breaker | 9674.3505 | 94 | 1994.7185 | 2888.9242 | 881.5032 | 2996.6212 | 63.5185 | 28.07 | 28.07 | 28.07 | 7.2038 | 102.9186 | 31.4038 | 106.7554 | 40.7855 | 16.8723 | 56.4559
| Switchgear | > 11 kV & < = 22 kV ; Switch | 1875.9333 | 298.885 | 2680.3946 | 2494.1435 | 4926.222 | 4314.5972 | 216.2185 | 397.3819 | 397.3819 | 397.3819 | 83.4896 | 6.2764 | 12.3967 | 10.8576 | 47.109 | 52.6428 | 59.491
| Switchgear | > 11 kV & < = 22 kV ; Circuit Breaker | 6045.9739 | 22 | 976.7207 | 2948.5404 | 709.1332 | 1056.2732 | 14.7777 | 10.7291 | 10.7291 | 10.7291 | 10.488 | 274.817 | 66.0943 | 98.4493 | 48.3243 | 42.2572 | 48.7265
|  | > 22 kV & < = 33 kV ; Switch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 22 kV & < = 33 kV ; Circuit Breaker | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Switchgear | > 33 kV & < = 66 kV ; Switch | 1198.8728 | 17 | 236.5702 | 1658.9995 | 505.9289 | 1860.9339 | 11 | 23.5246 | 23.5246 | 23.5246 | 1.0288 | 70.5219 | 21.5064 | 79.1059 | 40.9096 | 47.7502 | 60.8652
| Switchgear | > 33 kV & < = 66 kV ; Circuit Breaker | 12709.5884 | 40 | 2946.7795 | 4645.8173 | 1267.2414 | 2316.6101 | 34 | 14.6215 | 14.6215 | 14.6215 | 13.1523 | 317.7397 | 86.67 | 158.4391 | 37.9079 | 10.8207 | 40
| Switchgear | > 66 kV & < = 132 kV ; Switch | 0 | 0 | 0 | 3.9554 | 3.9554 | 3.9554 | 0 | 0.023534 | 0.023534 | 0.023534 | 31.4583 | 168.0705 | 168.0705 | 168.0705 | 68.5193 | 73.7946 | 40
| Switchgear | > 66 kV & < = 132 kV ; Circuit Breaker | 2937.0615 | 26 | 0 | 1598.7572 | 2860.3625 | 2860.3625 | 0 | 14.1528 | 14.1528 | 14.1528 | 7.4098 | 112.9639 | 202.1056 | 202.1056 | 31.4171 | 68.1658 | 40
|  | > 132 kV ; Switch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | > 132 kV ; Circuit Breaker | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Luminaires ; Major Road | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Luminaires ; Minor Road | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Brackets ; Major Road | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Brackets ; Minor Road | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Lamps ; Major Road | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Lamps ; Minor Road | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Poles / Columns ; Major Road | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Poles / Columns ; Minor Road | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Field Devices | 14297.0341 | 536 | 26748.9669 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0
|  | Local Network Wiring Assets | 10586.4125 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Communications Network Assets | 4989.0508 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Master Station Assets | 1663.804 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Communications Site Infrastructure | 1.5118 | 1 | 869.8347 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0
|  | Communications Linear Assets | 9.7274 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | AFLC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UG cables | Pillar | 4485.8961 | 496 | 2558.371 | 7472.4168 | 5974.7019 | 7472.4168 | 353.7862 | 826.2159 | 826.2159 | 826.2159 | 826.2159 | 9.0441 | 7.2314 | 9.0441 | 40.6291 | 47.4334 | 40.6291
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Instrument Transformers | 1061.4621 | 80 | 225.2066 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0
|  | Voltage Regulators | 271.5966 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Switchgear | HV Switchboards | 0 | 0 | 0 | 1.5719e-05 | 1.5719e-05 | 1.5719e-05 | 0 | 0.015719 | 0.015719 | 0.015719 | 0.015719 | 0.001 | 0.001 | 0.001 | 77.2877 | 83.6593 | 77.2877
| Switchgear | Outdoor Bus | 0 | 0 | 0 | 1.0338e-05 | 1.0338e-05 | 1.0338e-05 | 0 | 0.010338 | 0.010338 | 0.010338 | 0.010338 | 0.001 | 0.001 | 0.001 | 81.0671 | 85.359 | 81.0671
| Switchgear | GIS | 0 | 0 | 0 | 2.0177e-05 | 2.0177e-05 | 2.0177e-05 | 0 | 0.020177 | 0.020177 | 0.020177 | 0.020177 | 0.001 | 0.001 | 0.001 | 55.3574 | 61.0272 | 55.3574
|  | Substation Auxiliary Plant (AC, Pumps) | 0 | 0 | 1616.7355 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0
|  | Battery Banks | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Auxiliary Transformers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Buildings | 27969.8214 | 38 | 4118.8017 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0
|  | Capacitor Banks | 2502.8593 | 10 | 651.8595 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0
|  | Fire Systems | 1714.3247 | 8 | 625.4132 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0
|  | Surge Arrestors | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Civil and Grounds | 15136.0654 | 13 | 3768.595 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Poles - unallocated | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Pole top structures - unallocated | 2713.3583 | 1988 | 7025.9506 | 0 | 0 | 0 | 2256.2241 | 0 | 0 | 0 | 0
|  | OH conductors - unallocated | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | UG cables - unallocated | 57.8645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Services - unallocated | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Transformers - unallocated | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Switchgear - unallocated | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Public lighting - unallocated | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | SCADA & protection - unallocated | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Other - unallocated | 3997.3225 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| subtotal |  | 201894.573 | 5313.2321 | 146178.2193 | 148069.234 | 127601.9952 | 144846.9313 | 7846.9743 | 3532.2468 | 3532.2468 | 3532.2468 | 6179.3049