{"text_format":"1","workbook":"xlsx","n_sheets":5,"sheets":["Contents","Cover","1. F-Factor summary","2. Individual fire start info","3. Systems and Audit"],"not_rendered":{"charts":0,"images":2,"macros":1,"external_links":2,"defined_names":97,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Contents","index":0,"n_rows":12,"n_cols":6,"rows_kept":12,"cut":false,"hidden":false,"merged":[[8,2,9,3],[2,1,2,10],[4,1,4,10]]}
[" "]
[]
[null,"Electricity Distribution Network Service Provider\nF-factor Reporting Template"]
[]
[null,"Table of contents"]
[]
[]
[null,null,"Cover sheet",null,null,"2. Fire start report"]
[]
[]
[]
[null,null,"1. F-factor summary",null,null,"3. Systems and Audit"]

{"sheet":"Cover","index":1,"n_rows":49,"n_cols":7,"rows_kept":49,"cut":false,"hidden":false,"merged":[[10,1,11,8],[13,1,13,8],[48,2,48,6],[42,2,42,3],[42,4,42,7],[46,2,46,6],[47,2,47,6],[38,2,38,3],[38,4,38,7],[41,2,41,3],[41,4,41,7],[37,2,37,3],[37,4,37,7],[32,3,32,8],[30,3,30,8],[15,1,15,8],[26,3,26,8],[28,3,28,8],[26,1,26,2],[31,3,31,5],[14,1,14,8],[16,1,16,8],[17,1,17,8],[21,1,21,8],[19,1,19,8]]}
[]
[]
[]
[]
[]
[]
[]
[null,"Distribution Network Service Provider"]
[null,"Fire start report"]
[]
[null,"This template is to be used by a DNSP to provide a fire start report to the AER in accordance with section 5 of the F-factor Order in Council.  "]
[]
[]
[null,"Colour coding of input sheets:"]
[null,"Dark blue = AER headings"]
[null,"Grey = AER instructions"]
[null,"Yellow = Input cells"]
[null,"Light orange = Automatically-generated cells"]
[]
[null,"Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so."]
[null,"The cells and structure of the spreadsheet is locked to prevent inadvertent interference with the automated settings."]
[null,"All dollar amounts are to be unrounded, and in nominal terms."]
[]
[]
[]
[]
[null,"DNSP:",null,"Powercor"]
[]
[null,"DNSP - trading name:",null,"Powercor Australia Ltd"]
[]
[null,"DNSP - Australian business number: ",null,"ACN 064 651 109"]
[]
[null,"Reporting year:",null,"2019/20"]
[]
[]
[]
[]
[null,"Business address","Address",null,"40 Market Street"]
[null,null,"Suburb",null,"Melbourne"]
[null,null,null,"State","Victoria","Postcode",3000]
[]
[null,"Postal address","Address",null,"Locked Bag 14090"]
[null,null,"Suburb",null,"Melbourne"]
[null,null,null,"State","Victoria","Postcode",8001]
[]
[]
[null,"Contact name/s","Mulitha De Silva"]
[null,"Contact phone/s","(03) 9683 4521"]
[null,"Contact email address/s","MUDESILVA@POWERCOR.COM.AU"]

{"sheet":"1. F-Factor summary","index":2,"n_rows":14,"n_cols":15,"rows_kept":14,"cut":false,"hidden":false,"merged":[[5,1,5,2],[3,6,3,8],[4,6,4,8],[5,6,5,8],[11,2,11,3],[12,2,12,3],[13,2,13,3],[6,2,6,3],[7,2,7,3],[8,2,8,3],[9,2,9,3],[10,2,10,3]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"Powercor"},"IRU target:",{"$f":"IF(SUM(K6:O6)=0,\"\",SUM(K6:O6))","v":412.8},null,null,null,null,null,null,"AusNet Services","CitiPower","Jemena","Powercor","United Energy"]
[null,"F-factor data reporting","IRU amount:",{"$f":"IF(SUM('2. Individual fire start info'!S38:S2000)=0,\"\",SUM('2. Individual fire start info'!S38:S2000))","v":309.5600000000004},null,null,null,null,null,"2016/17",247.7,3.4,9.6999999999999993,468,22.3]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2019/20"},"Revenue adjustment:",{"$f":"IF(OR(D1=\"\",D2=\"\"),\"\",15000*(D1-D2))","v":1548599.9999999942},null,null,null,null,null,"2017/18",247.7,3.4,9.6999999999999993,468,22.3]
[null,null,null,null,null,null,null,null,null,"2018/19",247.7,3.4,9.6999999999999993,468,22.3]
[null,"Table 2: Summary of total fire starts by F factor Order definition",null,null,null,null,null,null,null,"2019/20",221.1,3.4,9.6999999999999993,412.8,22.3]
[null,"This is a summary of data in worksheet \"2. Fire Start Report\"",null,null,null,null,null,null,null,null,{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>K1),\"\",LOOKUP($B3,$J2:$J5,K2:K5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>L1),\"\",LOOKUP($B3,$J2:$J5,L2:L5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>M1),\"\",LOOKUP($B3,$J2:$J5,M2:M5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>N1),\"\",LOOKUP($B3,$J2:$J5,N2:N5))","v":412.8},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>O1),\"\",LOOKUP($B3,$J2:$J5,O2:O5))","v":""}]
[null,"Kind of Fire Start by definition of fire start under clause 5 of F-factor Order","Total fires by cause"]
[null,"Started in or originated from a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B8)","v":231}]
[null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B9)","v":31}]
[null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B10)","v":21}]
[null,"Started by lightning striking a distribution system or a part of a distribution system ",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B11)","v":10}]
[null,"Started by any other thing forming part of or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B12)","v":12}]
[null,"Otherwise started by a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B13)","v":0}]
[null,"Total",{"$f":"SUM(C8:C13)","v":305}]

{"sheet":"2. Individual fire start info","index":3,"n_rows":347,"n_cols":25,"rows_kept":347,"cut":false,"hidden":false,"merged":[[25,1,25,18],[27,1,27,20],[26,1,26,21],[35,19,35,21],[33,1,33,4],[35,2,35,10],[28,1,28,18],[29,1,29,18],[35,11,35,13],[35,14,35,17],[13,1,13,11],[22,1,22,21],[24,1,24,21],[14,1,14,20],[15,1,15,18],[16,1,16,18],[18,1,18,18],[21,1,21,18],[19,1,19,18],[23,1,23,18],[20,1,20,18],[17,1,17,18],[3,22,3,24],[4,22,4,24],[5,22,5,24],[7,1,7,21],[11,1,11,2],[9,1,9,21]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"Powercor"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2019/20"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"\"Enter into this worksheet fire start data, from any IT system, which have been recorded by \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\". Note that fire starts must be in accordance with the definition of a fire start in the Order In Council.\"","v":"Enter into this worksheet fire start data, from any IT system, which have been recorded by Powercor. Note that fire starts must be in accordance with the definition of a fire start in the Order In Council."}]
[]
[null,"\"Fire\" should be interpreted using its common meaning and can be defined as a process in which substances combine chemically with oxygen from the air and typically give out bright light, heat and smoke. A fire should be recorded where there is evidence of smoking, charring, scorching, burning or any other evidence that a fire had occurred.  "]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"Powercor must provide:"}]
[]
[null,"Table 3 - Individual Fire Starts"]
[null,"   (1) Date - dd/mm/yyyy"]
[null,"   (2) Time - if known, the 24-hour time of the fire start hh:mm"]
[null,"   (3) Latitude and longitude of the fire start as decimal coordinates"]
[null,"   (4) Address of the property on which the incident occurred or closest to the incident"]
[null,"   (5) Asset number for the asset nearest the fire start"]
[null,{"$f":"\"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the \"&B1&\" network\"","v":"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the Powercor network"}]
[null,"   (7) Voltage on the line in which the fire start occurred (note: this may not be the nearest polyphase overhead line)"]
[null,"   (8) Network categorisation - CBD, Urban, Rural Long or Rural Short"]
[null,"   (9) Asset type of primary asset causing fire in accordance with OSIRIS asset categories"]
[null,"   (10) Where the asset involved in the fire is a transformer or an overhead or underground line, provide the phase, or phases, of the line or transformer"]
[null,"   (11) Kind of fire start in accordance with categories specified in Clause 5 of the F-factor Order-In-Council"]
[null,"   (12) Identify the location of the fire start in accordance with the categories specified in Clause 11(b) of the F-factor Order-In-Council"]
[null,"   (13) Provide the BOM fire danger rating applicable at the time of the fire start (data is available on the EM-COP website)"]
[null,{"$f":"\"   (14) \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\"'s record number for the incident\"","v":"   (14) Powercor's record number for the incident"}]
[null,"   (15) ESV's OSIRIS reference number for the incident"]
[null,"   (16) Free text description of the fault containing relevant comments from field reports "]
[]
[]
[]
[null,"Table 2: Individual Fire Starts"]
[]
[null,"Number","Fire starts",null,null,null,null,null,null,null,null,"Fire Type",null,null,"Risk Factors",null,null,null,"IRU \namount","Additional information"]
[null,null,"Date 1","Time 2","Latitude 3","Longitude 3","Address of incident 4","ID of \nnearest \nasset 5","ID of nearest \npolyphase \nline 6","Voltage of line in which \nfire start \noccurred 7","Network categorisation 8","Type of primary asset \ninvolved in fire start 9","Phase(s) of \nline or \ntransformer 10","Kind of fire start as per Clause 5\nof F-factor Order-In-Council 11","Location \narea 12","Location\nmultiplier","Fire \ndanger \nrating 13","Danger multiplier","Product of multipliers","DNSP record number 14","OSIRIS \n(ESV) reference \nnumber 15","Fault \ndescription 16"]
[{"$f":"COUNTA(C38:O38,Q38,T38:V38)","v":17},1,"2019-07-04","10:52:00",-37.5466537,143.91194200000001,"20 SPRINGS ROAD, BROWN HILL VIC 3350",32000612,"BAN015","22kV AC","Rural Short"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O38=\"\",\"\",IF(O38=\"LBRA only\",0.2,IF(O38=\"HBRA only\",1,IF(O38=\"within electric line construction area\",19.8,IF(O38=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"No forecast",{"$f":"IF(Q38=\"\",\"\",IF(Q38=\"No forecast\",0.1,IF(Q38=\"Low-moderate\",0.2,IF(Q38=\"High\",0.5,IF(Q38=\"Very high\",1,IF(Q38=\"Severe\",2,IF(Q38=\"Extreme\",3.5,5)))))))","v":0.1},{"$f":"IF(OR(P38=\"\",R38=\"\"),\"\",IF(AND(O38=\"within electric line construction area\",Q38=\"No forecast\"),1,P38*R38))","v":2.0000000000000004E-2},"INC-0007472","20190715PWA_08 ","A customer reported transformer and wire on fire at the incident location. The attended crew found that an insulated HV dropper on the substation pole ignited. There was no ground fire. The crew made the place safe and repairs arranged.   ",null,null,"Overhead conductors"]
[17,2,"2019-07-10","21:42:00",-38.076500000000003,144.369227,"292 -296 Princes Highway Corio 3214",30268929,"FNS021","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0007772","20190809PWA_01","Pole fire reported at incident location. There was no ground fire, no reported injuries or third party property damage.",null,null," - overhead conductor (bare; aluminium core steel reinforced)"]
[17,3,"2019-07-11","13:00:00",-36.272005,143.13717299999999,"1983 Borung Hwy, Jeffcott VIC 3480",31002530,"CTN006","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0007775","20190809PWA_02","During pole inspection pole fire damage to crossarm found. There was no ground fire, no reported injuries or third party damage.",null,null," - overhead conductor (bare; all aluminium conductor)"]
[17,4,"2019-07-16","15:24:00",-35.261975999999997,143.050568,"2375 Springfield Rd Chillingollah 3585",32155903,"SHL001","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0007569","20190724PWA_02 ","A customer reported a wire hanging low in the mid air and smoke coming from the pole at the incident location. The attended crew found that the angle cross arm burnt through on the pole. The crew made the place safe and repairs completed. ",null,null," - overhead conductor (bare; copper)"]
[17,5,"2019-07-16","11:38:00",-38.359223999999998,142.53905,"310 HORNE ROAD, WARRNAMBOOL VIC 3280",30241936,"WBL005","12.7kV AC (SWER)","Rural Short"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0007623","20190729PWA_01 ","A customer reported a smoking pole at the incident location. The attended crew found that the pole had been burnt through some time ago and at this time it was smoking. The place made safe and repairs done. There was no ground fire or injuries.\nThis insulator had been identified as P2 maintenance to replace it. However this pole fire which causes to damage the pole occurred in between the asset inspection date (P2 report) and this incident date. It believes the pole fire self-extinguished and no protection operations. It was not reported. \nThis incident was informed to the asset investigation team. This conductor was replaced and armour rod was fitted recently. These upgrades should have been done together with replacement of insulator per the asset investigation team.  The team will conduct a line patrol to check if there are more this type insulators on the line.\n",null,null," - overhead conductor (bare; steel)"]
[17,6,"2019-07-19","12:00:00",-34.213432439999998,142.14841960000001,"1 SPRINGFIELD DRIVE MILDURA 3500",30333970,"MDA034","22kV AC","Urban"," - overhead conductor (bare; steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0007537","20190722PWA_01 ","Call received from Vic Fire of pole fire at incident location. On arrival crew found a small burnt area of nature reserve adjacent to a concrete pole. CFA had extinguished the fire.\nThere were no reported injuries or third party property damage.",null,null," - overhead conductor (ABC)"]
[17,7,"2019-07-19","17:48:00",-38.259390969999998,144.53486720000001,"3 Lowe Street, Ocean Grove",33043236,"DDL011","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0007540","20190722PWA_02 ","A customer saw sparks coming from pole with streetlight on it, first pole in Lowe St. Power went off momentarily. A crew was dispatched to investigate. On arrival the crew identified a live HV conductor laying on the ground between P1 (LIS-7141) and P2 (LIS-787357), causing burns to the green grass.\nThe crew found a deceased bird believed to be the likely cause. It was suspected that the bird had bridged over two HV phases, causing 1 phase helical termination to fail and conductor to fall to ground. There were no reported injuries or third party property damage.\nThe fire brigade and police had the road blocked to keep the public away from the danger.",null,null," - overhead conductor (covered uninsulated)"]
[17,8,"2019-07-24","11:30:00",-35.231673530000002,143.4510234,"White Road 284 meters west of N S Rd Worrien North, 3585.",32161264,"SHL004","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0007571","20190724PWA_03 ","Vic Fire reported wires down and pole on fire reported at Intersection of White Rd and Nth Sth Rd Beverford. On arrival found that pole top had burnt thru and toppled over all insulators and phases still connected.\nThere was no ground fire, no reported injuries or third party property damage. Crew isolated the pole and all supply restored. One property will be off until pole replaced.",null,null," - overhead conductor (insulated)"]
[17,9,"2019-07-26","19:12:00",-36.403613,144.96138999999999,"43 Cowie Road, Girgarre VIC 3624",32189817,"SHP011","22kV AC","Rural Short"," - transformer (pole mounted)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0007728","20190809PWA_06","Customer reported pole fire at the incident location, customer also advised that a large Crow's nest was built on the structure in question & believe that to be the source of the fire. Upon arrival crew found that a birds nest was built on the termination substation structure, material within the nest was believed to be conductive & when a rain event commenced a flashover occurred that commenced combustion of the nesting materials. The fire soon self extinguished with the precipitation. No ground fire occurred, no damage to 3rd party.",null,null,"Service lines"]
[17,10,"2019-07-31","18:00:00",-37.968843990000003,144.6851144,"Opposite 668 Diggers Rd Werribee South 3030 (Melways 199 Ref E9)",32171115,"WBE034","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0007679","20190801PWA_03","MFB and local resident reported pole fire in Diggers Rd. that had now extinguished. Attending Powercor fault crew noted a burnt FOLCB. There were no shocks, injuries or ground fire.",null,null," - overhead service conductor (residential)"]
[17,11,"2019-08-08","07:53:00",-38.602023000000003,143.000879,"2549 C164, Port Campbell VIC 3269, Australia",32056249,"TRG003","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0007832","20190814PWA_02 ","A passer-by reported a pole on fire at the incident location. Upon arrival a Powercor crew found a melted fuse box on the pole. There was no ground fire, no reported injuries or third party property damage.",null,null," - overhead service conductor (commercial / industrial)"]
[17,12,"2019-08-11","04:18:00",-34.306538000000003,142.16424000000001,"6 Nealie St, Cardross VIC 3496, Australia",32145619,"RCT023","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0007850","20190815PWA_03 ","Pole fire reported by Vic Fire at incident location. On arrival crew found pole had burnt from below HV crossarm to stay position. There was no ground fire, no reported injuries or third party property damage.",null,null," - overhead service conductor (subdivision / construction)"]
[17,13,"2019-08-11","08:00:00",-34.221899000000001,142.16774000000001,"640 Sandilong Ave, Irymple VIC 3498, Australia",30095461,"MDA023","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0007852","20190815PWA_04 ","Report received of a pole fire at the incident location. On arrival crew found a crossarm had burnt in half. There was no HVI. There was no ground fire, no reported injuries or third party property damage.",null,null," - overhead service conductor (other)"]
[17,14,"2019-08-13","20:29:00",-36.353336300000002,145.4314,"133 GRAHAMVALE ROAD, GRAHAMVALE VIC 3631",30128968,"SHN024","Low voltage AC (<1kV)","Rural Short"," - fuse (any other type)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0007875","20190816PWA_03 ","Report received of a house fire at incident location. On arrival crew found fire extinguished and observed that the meter board had sustained fire damage. Crew was advised that customers gas heating had failed and they were running 4 x electric heaters in the house.\nThere was no ground fire, no reported injuries.",null,null," - underground service cable (residential)"]
[17,15,"2019-08-20","23:50:00",-37.736908,144.80950000000001,"UNIT1,11 LESLIE STREET, ST ALBANS, VIC 3021",30247361,"SA012","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0007914","20190821PWA_02 ","Emergency Services reported fire at POA at the incident location. On arrival the crew found that the FOLCB at the POA was completely melted, dropping hot debris to the ground, which started a small grass fire in the front of the property of less than 0.5 meter square. There were no reported injuries.",null,null," - underground service cable (commercial / industrial)"]
[17,16,"2019-08-27","09:26:00",-36.609057,143.94966400000001,"5 Cementry Rd, Bridgewater on Loddon",30028602,"BET001","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0007980","20190828PWA_03","A pole fire was reported by a customer. On arrival, A Powercor crew found that the LV fuse box on the pole caught fire. There was fallen debris but no ground fire. There was no ground fire, no reported injuries or third party property damage.",null,null," - underground service cable (subdivision / construction)"]
[17,17,"2019-08-31","00:11:00",-36.055349,145.69772,"Bourke Rd, Katamatite VIC 3649, Australia",32185775,"NKA001","22kV AC","Rural Long"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,{"$f":"IF(OR(P54=\"\",R54=\"\"),\"\",IF(AND(O54=\"within electric line construction area\",Q54=\"No forecast\"),1,P54*R54))","v":2.0000000000000004E-2},"INC-0008062","20190903PWA_03 ","Passer by reported sparking and hot debris being emitted from pole top at incident location. Upon arrival crew found that a Boric Acid fuse tube had candled and burnt through. No resultant ground fire.",null,null," - underground service cable (other)"]
[17,18,"2019-09-03","07:04:00",-35.342609000000003,143.55923300000001,"257 Beveridge st Swan Hill vic 3585",33070207,"SHL007","22kV AC","Urban"," - pole (concrete)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0008611","20191101PWA_01 ","Bird flashed over on pole top and caught fire. There was no ground fire or reported injuries.",null,null,"Underground cables"]
[17,19,"2019-09-04","09:51:00",-36.769953999999998,144.27774600000001,"10 Russell St Quarry Hill 3550",31008832,"BGO022","Low voltage AC (<1kV)","Urban"," - connector / termination","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0008074","20190905PWA_01 ","Customers reported supply issues at the incident location. Street light fire due to neutral fault.",null,null," - underground cable"]
[17,20,"2019-09-05","06:32:00",-35.885581000000002,144.23991000000001,"Leitchville-Kerang Rd, Horfield VIC 3567, Australia",33021753,"CHA005","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0008095","20190906PWA_02 ","Customer reported wires down and fire at incident location. Upon arrival the fault crew found that a swan had hit conductors nearest pole 17 of the Leitchville line, bringing 2 of the 3 conductors down. A ground fire was initiated due to downed conductors, approximately 3M x 10M of road verge was burnt. There was no injuries or third party property damage.",null,null," - underground communications cable"]
[17,21,"2019-09-07","15:02:00",-35.903891000000002,141.147527,"Unnamed Road, Telopea Downs VIC 3420",30087080,"NHL031","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0008612","20191101PWA_02 ","Pole replaced due to pole fire. No ground fire reported.",null,null,"Poles"]
[17,22,"2019-09-13","22:12:00",-38.548915999999998,143.97969900000001,"22 Francis Street, Lorne",30261511,"CLC005","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0008278","20190920PWA_01 ","Vicfire reported a pole fire at the incident location, on arrival the crew found a single phase FOLCB on the pole in front of the incident location address had overheated and caught fire. There was damage to wiring both up and down the pole, however there was no ground fire reported. \nThere were no injuries or third party damage reported.",null,null," - pole (concrete)"]
[17,23,"2019-09-14","06:07:00",-38.282772999999999,144.40116800000001,"291 BREAMLEA ROAD, CONNEWARRE VIC 3227",33045904,"WPD024","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0008193","20190916PWA_01 ","A swan contacted the HV conductors at the incident location, causing one of the HV conductors to fall to the ground alive via back-feed. This situation resulted in several small grassfires, totaling less than 1m2 in total. The CFA attended, however the grassfires self extinguished once the supply was isolated. \nThere were no reported injuries or third party damage.",null,null," - pole (steel)"]
[17,24,"2019-09-16","14:34:00",-34.238391999999997,142.19668999999999,"206 Ginquam Ave, Irymple VIC 3498, Australia",30097798,"RCT021","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0008221","20190918PWA_01 ","Report received from Vic Fire of a crossarm fire at incident location. There was no damage to the pole, the crossarm was burnt in half and HV conductors have fallen into LV below. There was suspected HVI effecting possibly 12 premises.\nThere was no ground fire, no reported injuries.",null,null," - pole (wood)"]
[17,25,"2019-09-16","13:00:00",-34.227977000000003,142.10046700000001,"3158 WALNUT AVENUE,MILDURA,VIC,3500  In front of this property.",31020923,"MBN032","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0008224","20190918PWA_02 ","Vic Fire reported pole fire at incident location. On arrival crew found crossarm on fire, part of crossarm burnt off and conductor hanging low. There was no ground fire, no reported injuries or third party property damage.",null,null,"Crossarms"]
[17,26,"2019-09-21","02:15:00",-36.131152,145.559237,"503 Drumanure Rd Invergordon",32184425,"NKA001","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0008318","20190923PWA_02 ","Customer called reporting wire down at back of his property which has caused a fire. On Arrival, crew found a tree had fallen across a slack span of conductor, breaking the wires mid span and bringing them to ground. A small burn section was found under the conductors approx. the size of a \"dinner plate\".  No injury or third party damage.",null,null," - crossarm (wood)"]
[17,27,"2019-09-23","14:49:00",-37.711061000000001,144.73253399999999,"58 Olsen Retreat, Caroline Springs VIC 3023, Australia",30322459,"SA011","Low voltage AC (<1kV)","Urban"," - underground service cable (other)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0008393","20191002PWA_06 ","Constable Alistair- Caroline Springs Police reports copper has been stolen out of pit on hume drive- between Infinity Dr and Lancefield Dr (thinks roughly at the back of 57 olsen retreat), pit lid is missing, wires pulled out of pit and exposed and burnt grass around the pit. Unsure of any other details of who has done this.\nOn arrival PAL crew have advised that the LV cables were laying on the ground adjacent to the affected pit and were found to be ALIVE. They further  advised that a pair of secatier cutters were found at the scene and the were burn marks around the service pit. No injuries have been reported to PAL.",null,null," - crossarm (steel)"]
[17,28,"2019-09-25","13:07:00",-36.364629999999998,145.47346999999999,"540 New Dookie Rd, Shepparton East 3631",33093102,"SHN024","22kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0008365","20190926PWA_01 ","A Lend Lease G&B Crew contracted to Powercor were attending a P1 fault on P71 Saleyards Spur (LIS-6304), where there was damage to an insulator and the aluminum conductor, believed to have been caused by a previous lightning strike. Whilst the crew were in the process of repairing the conductor, the conductor broke and fell to the ground. On contact with the ground, the conductor started a small grassfire of approx. 3m2. There were no injuries or third party damage.",null,null," - crossarm (other)"]
[17,29,"2019-10-01","17:35:00",-36.782407999999997,144.23053100000001,"105 NORELLE CRESCENT,KANGAROO FLAT,VIC,3555",33011824,"BET006","22kV AC","Rural Short"," - pole (concrete)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0008389","20191002PWA_03 ","A customer reported hearing loud bang, went outside and pole was sparking and cause fire in grass under pole. Supply not affected now but power did go off for a moment, fire is out now. Crew found a bird caused flashover on center phase HV bridge at pole 63 Norelle Cresent. There was a ground fire, no reported injuries or third party property damage.",null,null,"Overhead assets"]
[17,30,"2019-10-02","02:03:00",-35.500256999999998,143.679192,"320 Ridge Rd, Tresco VIC 3583",33068355,"KGT004","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0008390","20191002PWA_04 ","Report received of fallen conductor resulting in 100 x 200 square metres of stubble being burnt. On arrival crew found that HV conductor had parted about one metre from the pole. Protection operated. There was a ground fire, no reported injuries.",null,null," - capacity balancing units"]
[17,31,"2019-10-03","10:48:00",-34.738588999999997,142.65356800000001,"Staley Rd, Wemen",32143201,"WMN013","Low voltage AC (<1kV)","Rural Short"," - switch (disconnector/isolator)","single phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0008421","20191007PWA_02 ","A Customer reported that a few days ago when he started his pump, the nearby pole dropped a few large sparks that started a small grass fire. On arrival the crew found that a Low Voltage Isolator had overheated and caused hot debris to fall to the ground starting a small grassfire. The Customer told the crew that the initial grassfire was less than 1m2 in size, and the customer stamped it out with his feet. The customer subsequently burnt a larger area himself to create a fire break. There were no reported injuries or third party damage.",null,null," - connector / termination"]
[17,32,"2019-10-04","09:20:00",-38.53781,143.975188,"46B Mountjoy Parade, Lorne VIC 3232, Australia",30273992,"CLC005","Low voltage AC (<1kV)","Rural Short"," - luminaires (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0008550","20191023PWA_05 ","A customer called to report that on the previous night, the street light opposite No 50, was on fire, and that the lens fell on a truck, they also claim that they called 000 at the time, but no call was received by Powercor. On arrival the crew found the streetlight had overheated and was badly damaged and melted, the remains of the lens was on the ground. There was no ground fire, and no reported third party damage.",null,null," - dropper / bridge"]
[17,33,"2019-10-13","19:06:00",-37.529538000000002,143.86524,"10 Harrier Dr, Invermay Park VIC 3350, Australia",32011052,"BAN011","22kV AC","Rural Long"," - pole (wood)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0008470","20191014PWA_01 ","Vic fire reported a small ground fire ( 5 x 1 mts)  at the base of a pole at the incident location. On arrival the crew noticed that one HV crossarm strap had become loose, but was not in contact with conductors.\nThe fire start has been attributed to a bird contact although a bird was not found at the site. There was no injuries or third party property damage.",null,null," - guy wire"]
[17,34,"2019-10-25","07:00:00",-35.425516000000002,142.46101899999999,"2446 Sunraysia Hwy Turriff 3488",32159041,"OYN005","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0008566","20191028PWA_01","Customer reported loss of supply. On arrival crew found a deteriorated crossarm and one conductor had fallen to ground causing a small grass fire (30m x 20m). The fire self extinguished. There was no injuries.",null,null," - insulator tie wires / connections"]
[17,35,"2019-10-28","08:32:00",-35.972957000000001,144.39667499999999,"77 Lavender rd Gunbower 3566",32032440,"CHA005","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0010478","20200501PWA_01","Following a report of an outage at the incident location crew attended site. On arrival crew found an EDO fuse burnt in half. There was no ground fire, no reported injuries or thrid party property damage.",null,null," - insulators"]
[17,36,"2019-10-31","15:14:00",-38.037505000000003,144.356199,"520 BACCHUS MARSH ROAD, LARA VIC 3212",33044700,"FNS011","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0010479","20200501PWA_02 ","Following on from supply outage crew found hung up burnt edo fuse. There was no ground fire, no reported injuries or third party property damage.",null,null," - tower"]
[17,37,"2019-11-01","17:08:00",-37.926295000000003,144.647141,"215 Farm Road, Cocoroc, VIC, 3030",30304230,"WBE033","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0008621","20191104PWA_02 ","MMBW report grass fire possibly due to conductor clash between lis 799280 and 799276. PCA Faults Crew attended site and at first could not find any evidence of any grass fire within the span from Pole 2 LIS-799276 south west to Pole 3 LIS-799280. After further investigations the crew advised that they discovered a grass fire of approx. 30m x 30m,  some 20m south of the conductors.",null,null," - traction lines"]
[17,38,"2019-11-01","12:06:00",-36.533146000000002,145.05855299999999,"5 Waranga Drive Waranga Shores 3612",33089098,"SHP014","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Very high",1,{"$f":"IF(OR(P75=\"\",R75=\"\"),\"\",IF(AND(O75=\"within electric line construction area\",Q75=\"No forecast\"),1,P75*R75))","v":1},"INC-0008623","20191104PWA_04","Customer reported wire down hanging from pole and down onto grass, has caused fire, Fire brigade has just arrived to put fire out, at incident location. Crew found a customers tree had damaged an O/H HV conductor, starting a 800m2 ground fire, no property damage, no injuries, Vegetation Crew working nearby assisted with clean-up.",null,null,"Underground assets"]
[{"$f":"COUNTA(C76:O76,Q76,T76:V76)","v":17},39,"2019-11-01","02:04:00",-37.858640000000001,144.714935,"91 Grevillea Crescent, Hoppers Crossing, VIC, 3029",33073674,"LV009","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O76=\"\",\"\",IF(O76=\"LBRA only\",0.2,IF(O76=\"HBRA only\",1,IF(O76=\"within electric line construction area\",19.8,IF(O76=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"High",{"$f":"IF(Q76=\"\",\"\",IF(Q76=\"No forecast\",0.1,IF(Q76=\"Low-moderate\",0.2,IF(Q76=\"High\",0.5,IF(Q76=\"Very high\",1,IF(Q76=\"Severe\",2,IF(Q76=\"Extreme\",3.5,5)))))))","v":0.5},0.1,"INC-0008626","20191104PWA_05 ","VIC Fire reported  Service wire sparking and melted, started grass fire. Upon arrival the PCA Faults Crew have found that the POA/FOLCB at House No.91 Grevillea Crescent, Hoppers Crossing, VIC, 3029 has overheated, failed and melted and burnt away. The resultant hot melted plastic from the POA above has fallen onto the ground below causing a small grass fire of approximately 3m x4m, within the front yard of No.91 Grevillea Crescent, Hoppers Crossing, VIC, 3029. The MFB attended site and the grass fire was extinguished.",null,null," - LV pillar"]
[17,40,"2019-11-01","14:02:00",-36.326666000000003,143.468458,"Calder Hwy, Woosang 3518 (near Edwards Rd) (13km South of Charlton)",30229277,"BETS-CTN","66kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Severe",2,9.1999999999999993,"INC-0008627","20191104PWA_06 ","Crew were investigating an outage on BETS-CTN 66kV line and found a broken conductor and ground fire.",null,null," - services pit"]
[17,41,"2019-11-02","15:21:00",-36.583080000000002,145.01356699999999,"5 McDonald Street Rushworth 3612 ",30127619,"SHP014","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0008628","20191104PWA_07 ","Customer reported a pole fire out front of school on McDonald Street, wooden pole. Crew found that FSD had been consumed and required replacement.",null,null,"Transformers"]
[17,42,"2019-11-02","02:21:00",-34.200848000000001,142.153773,"276 San Mateo Avenue Mildura 3500",32147322,"MDA022","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0008629","20191104PWA_08 ","Vic Fire reported a Pole fire at intersection of Burrows Street and San Mateo Avenue, fire on HV cross arm. Crew found small fire on pole had started at king bolt.",null,null," - transformer (pole mounted)"]
[17,43,"2019-11-02","11:19:00",-37.870122000000002,144.70495700000001,"32 Macedon Street, Hoppers Crossing, VIC, 3029",32174345,"LV009","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0008638","20191106PWA_03","Customer advised that mains wire has come off insulator and is resting on the cross arm, making a sizzling sound. On arrival the PCA Faults Crew have advised that the HV cross arm has burnt.",null,null," - transformer (kiosk mounted)"]
[17,44,"2019-11-03","05:47:00",-35.996678000000003,144.47422599999999,"159 Patho Cemetery Road Patho 3564",33022125,"CHA005","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0008630","20191104PWA_09 ","Customer reports of supply failure.  Crew found wires down during line patrol due to pole fire, pole top assembly replaced.",null,null," - transformer (ground outdoor mounted)"]
[17,45,"2019-11-04","17:42:00",-36.613295000000001,145.30339699999999,"5475 GOULBURN VALLEY FREEWAY, MOORILIM, VIC, 3610",31027823,"MNA034","12.7kV AC (SWER)","Rural Long"," - fuse (EDO fuse)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0010508","20200515PWA_01 ","Customer called can see fuse down hanging down on substation. On arrival crew found fuse had candled and burnt in half. There was no ground fire, no reported injuries or third party property damage.",null,null," - transformer (indoor chamber mounted)"]
[17,46,"2019-11-05","21:04:00",-37.297151999999997,144.44109900000001,"455 CENTRAL ROAD, KYNETON SOUTH VIC 3444",33029664,"WND024","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within electric line construction area",19.8,"Low-moderate",0.2,3.9600000000000004,"INC-0010510","20200515PWA_02 ","Customer reports fuse arcing and sparking, sparks nor reaching the ground. On arrival crew found burnt hung up edo fuse. There was no ground fire, no reported injuries.",null,null," - transformer (any other type)"]
[17,47,"2019-11-08","22:43:00",-38.411115000000002,144.18316799999999,"31 MURRAY STREET, ANGLESEA VIC 3230",32072743,"WPD021","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0010513","20200515PWA_04 ","Calls received of supply failure at incident location. On arrival crew found EDO fuse burnt. There was no ground fire, no reported injuries or third party property damage.",null,null," - measurement transformer (current transformer)"]
[17,48,"2019-11-11","14:00:00",-36.352688000000001,145.433323,"130 Grahamvale Rd Grahamvale 3631",33096475,"SHN024","22kV AC","Rural Short"," - fuse (boric acid)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0008675","20191113PWA_03 ","A customer reported a loud bang and ground fire at the incident location. Upon arrival, a Powercor fault crew found that a bird flash over resulted in a small ground fire.",null,null," - measurement transformer (voltage transformer)"]
[17,49,"2019-11-12","07:17:00",-36.371496999999998,141.86018300000001," 5651 WESTERN HIGHWAY, GERANG GERUNG VIC 3418   (near Angle Road) Gerang Gerung 3418",30546090,"NHL015","22kV AC","Rural Long"," - automatic circuit recloser (ACR)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0008674","20191113PWA_02 ","Emergency services reported a crow on transformer causing sparks and small grass fire. Crew removed bird off ACR P205 Gerang.",null,null," - measurement transformer (capacitive voltage transformer)"]
[17,50,"2019-11-13","20:33:00",-34.169901000000003,142.0421,"30 YELTA RD MERBEIN (ACROSS THE ROAD).",33066091,"MBN031","22kV AC","Rural Short"," - fuse (boric acid)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0008684","20191115PWA_01","CFA reported a grassfire . Upon crew arrival found an extinguished grassfire near the base of the pole. A magpie had caused a flash over on HV fuse.",null,null,"Fuses and switchgear"]
[17,51,"2019-11-13","07:58:00",-38.496673000000001,143.240377,"276 TOMAHAWK CREEK ROAD, SIMPSON VIC 3266",33035709,"CDN001","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0010516","20200515PWA_05","Person advised fuse box half way up pole has caught on fire, fuse box may need replacing, pole is near the dairy, cust and dairy, access ok. On arrival crew found leads fuse box had burn damaging leads. There was no ground fire, no reported injuries or third party property damage.",null,null," - fuse (boric acid)"]
[17,52,"2019-11-21","13:25:00",-36.263627999999997,143.49520200000001,"379 Barrakee-Buckrabanyule Rd, Buckrabanyule VIC 3525",32027791,"CTN001","Low voltage AC (<1kV)","Rural Long"," - dropper / bridge","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Code Red",5,23,"INC-0008745","20191122PWA_01 ","A crew attended a fault on a SWER ACR BORUNG P81, no cause for the outage was located. The crew departed to site , but a short time later a grass fire was observed emanating from near the incident location. CFA extinguished fire, police attended. There was a ground fire of around 16.5 hectares. There was no injuries and potentially fencing and pasture burnt (unconfirmed).",null,null," - fuse (EDO fuse)"]
[17,53,"2019-11-21","11:57:00",-37.692286000000003,143.008737,"525 Glenelg Hwy, Streatham, 3351",30083878,"ART033","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0008747","20191122PWA_02 ","Vic fire reported wires down causing grass fire. On arrival crew found a broken strand of HV conductor had been intermittently brushing across  phases. The sparks from this started a grass fire, observed and extinguished by CFA personnel. There was a small fire, no reported injuries or third party property damage.",null,null," - fuse (Fault Tamer)"]
[17,54,"2019-11-21","14:30:00",-37.406649999999999,143.8938,"8 Geddes Rd, Creswick VIC 3363, Australia",33007412,"BAN009","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0008749","20191122PWA_03 ","Crew reports that a branch has broken of a gum tree and contacted the overhead line between  P1 and P2 Flem spur line. The branch caught fire and started a ground fire when it came to rest on the ground under the 22kV overhead line. There was a small ground fire, no reported injuries or third party property damage.",null,null," - fuse (powder filled)"]
[17,55,"2019-11-21","15:44:00",-37.876483,144.69520600000001,"18 Mossfiel drive.  Hoppers crossing 3029",32169859,"WBE013","Low voltage AC (<1kV)","Urban"," - dropper / bridge","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0008758","20191125PWA_02 ","A Customer reported a  Small Fire at base of Pole LIS-971870.  CFA attended, Fire extinguished.  Supply Off. On arrival the crew found that the  LV conductor line bridges had burnt at a substation LV bus fuse termination mounted on pole (LIS-208939).\nThere was a small  area of burnt grass at the base of the pole (LIS-208939) caused by fallen hot debris.  There was no reported injuries nor third party property damage.",null,null," - fuse (any other type)"]
[17,56,"2019-11-21","14:35:00",-37.874045000000002,144.78935200000001,"293 QUEEN STREET,ALTONA MEADOWS,VIC,3028",30118601,"LVN022","Low voltage AC (<1kV)","Urban"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0008760","20191125PWA_04 ","City West Water,  reported  pole to pole wire is broken, wire down, crossing over driveway and road. Fire is out and police is on site. On arrival the crew found that the  LV O/H service conductor between poles LIS-214017 and LIS-214018 was broken and lying on the ground over the driveway and on the grass.\nThere was a small area of burnt grass. There was no reported injuries nor third party property damage.",null,null," - circuit breaker"]
[17,57,"2019-11-25","19:06:00",-36.786182400000001,144.29092399999999,"11 ELIZABETH STREET -SPRING GULLY",32054109,"BET007","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0008768","20191126PWA_01 ","Report received from customer of service wire on ground and small patch of burnt grass in front yard. Service is still attached at pole end and draped across roadway. There was no injuries or third party property damage.",null,null," - switch (disconnector/isolator)"]
[17,58,"2019-11-25","17:52:00",-36.430197999999997,145.11375000000001,"515 Springvale Rd, Girgarre East VIC 3616, Australia",33097486,"SHP014","22kV AC","Rural Long"," - automatic circuit recloser (ACR)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0008769","20191126PWA_02 ","Vicfire called in event at the incident location advising that there had been a fire possibly causing damage to a  PCA asset. On arrival the crew found a small branch entangled in the ACR structure. The ACR had tripped, but the branch was on the supply side and still buzzing\nThere was a small fire started. There was no injuries and minor damage to fence posts.",null,null," - switch (earth)"]
[17,59,"2019-11-25","16:48:00",-36.647688000000002,141.26226600000001,"75 Barry Bulls Road, Minimay",30086961,"HSM004","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0008779","20191127PWA_01 ","Vic Fire reported that powerlines that started a grass fire at the incident location. On arrival the fault crew found that approx. 40cm had burned off the top of a SWER pole, allowing the conductor to drop into the scrub in the span below, igniting a fire in that scrub. The burned area was contained within the scrubland reserve on the southern fringe of the Little Desert National Park, and was estimated by CFA to be in the order of 1.6 hectares. There was no injuries.",null,null," - switch (FuseSaver)"]
[17,60,"2019-11-26","07:49:00",-36.427976000000001,145.11367200000001,"Springvale Rd, Cooma VIC 3616, Australia ( cnr midland hwy and springvale rd)",30566780,"SHP014","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0010519","20200515PWA_06 ","Customer advised Pole on Fire corner of  Midland Highway and Springvale rd, Shepparton.  Wires across the road. Emergency services have been called. On arrival crew found the top had been burnt off the pole. There was no ground fire, no reported injuries or third party property damage.",null,null," - switch (any other type)"]
[17,61,"2019-11-30","08:47:00",-35.905386999999997,144.301367,"28 King Albert Ave, Leitchville VIC 3567",30029109,"CHA005","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0008890","20191202PWA_02 ","Customer called reporting pole caught fire and smoldering. When crew arrived, they found that cross arm had burnt and outer phase (red phase) had dropped onto the LV cross arm. Crew called an LEI who attended and advised a HVI had occurred. No ground fire, no injuries that we have been made aware of.",null,null,"SCADA, network control and protection systems"]
[17,62,"2019-11-30","03:29:00",-34.272778000000002,142.198973,"151 Campbell Ave Irymple (Cnr Twenty Second St)",32151419,"RCT021","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0008891","20191202PWA_03 ","CFA called to advise pole fire and wire down at the incident location. Crew arrived and found HV cross arm was burning and part of cross arm had burnt out, dropping HV insulator and line to the ground.  CFA and Police in attendance.\nCable was still sparking due to backfeed. There was a small ground fire (1 mtr), no reported injuries or third party property damage.",null,null," - audio frequency load controller (AFLC)"]
[17,63,"2019-11-30","12:10:00",-36.347493999999998,145.41167300000001,"5 Shorthorn Ct (Ford Rd), Shepparton VIC 3630",33095210,"SHTSHN1","66kV AC","Unknown"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0008893","20191202PWA_04 ","CFA reported pole fire that caused grass fire at the incident location. When crew arrived they found an area of burnt grass approx.  4m x 18m in road reserve. Crew inspected pole and found evidence of a flash over from burn marks on east side of HV insulator but couldn't find any evidence of what had caused it or when.\nThere was no protection operations in the area.",null,null," - arc suppresion coil"]
[17,64,"2019-11-30","09:56:00",-35.283431999999998,143.56536199999999,"68 Woodgate Rd, Murraydale VIC 3586",32157209,"SHL004","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0008901","20191203PWA_03 ","Customer reported pole outside property was burnt at top of pole and wires were low.  On arrival crew found broken cross-arm that had snapped in two and burn damage around the king bolt.   CFA on site.  No ground fire, no injuries no third party damage.",null,null," - automatic circuit recloser (ACR)"]
[17,65,"2019-11-30","08:53:00",-34.290933000000003,142.17922999999999,"62 Moonah St, Red Cliffs VIC 3496",32153101,"RCT023","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0008907","20191204PWA_01 ","CFA reported pole fire at above address. When crew arrived, they found a cross arm that had burnt and conductors that had fallen onto LV.  Closer inspection showed damage to LV and HV insulators. LEI could find no evidence of property damage. There was no ground fire, no injuries or property damage.",null,null," - communications linear assets"]
[17,66,"2019-11-30","17:49:00",-35.319111999999997,141.363406,"410 Perkins Rd, Cowangie VIC 3506",32150598,"OYN001","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0008908","20191204PWA_02 ","Report from LSA Barry Gregg of pole fire at above address. Crew arrived and found pole that appeared to have been burning all day. There was  a lot of burnt debris from the pole but no ground fire had occurred and commented that site was very sandy.  \nNo third party damage or injuries.",null,null," - communications network assets"]
[17,67,"2019-11-30","03:00:00",-35.384452000000003,142.18768700000001,"88 CUMMINGS ROAD, PATCHEWOLLOCK VIC 3491",32151395,"OYN005","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0010521","20200515PWA_07 ","Report Received of cross-arm fire at incident location. On arrival crew found strain cross-arm had been burnt.",null,null," - communications site infrastructure"]
[17,68,"2019-12-01","11:54:00",-35.225188000000003,143.45411999999999,"North South Rd, Beverford VIC 3590",32160282,"SHL004","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0008898","20191203PWA_01 ","CFA reported lines down with small fire.  When crew arrived they found that the HV cross arm had burnt on one side and the conductor had dropped but was still in the air.  No injuries or third party damage.  No ground fire.",null,null," - field devices"]
[17,69,"2019-12-01","11:53:00",-35.248331,143.524033,"195 Tyntynder Central Rd, Tyntynder VIC 3586",32157266,"SHL004","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0008899","20191203PWA_02 ","CFA called advising pole fire at above address. When crew arrived, they found that the top of the pole had burnt and cross arm had broken.  Conductors were still on cross arm which was hanging on top of pole. No injuries, no ground fire, no third party damage.",null,null," - local network wiring assets"]
[17,70,"2019-12-01","12:57:00",-35.181064999999997,142.92250000000001,"Chinkapook-Mittyack rd Chinapook vic 3546",30304554,"OYN003","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,{"$f":"IF(OR(P107=\"\",R107=\"\"),\"\",IF(AND(O107=\"within electric line construction area\",Q107=\"No forecast\"),1,P107*R107))","v":0.5},"INC-0010509","20200515PWA_09","Crew reports burnt wooden HV crossarm on pole 238 - small ground fire",null,null," - master station assets"]
[17,71,"2019-12-01","18:06:00",-35.281793999999998,143.45478299999999,"507 LAKE ROAD, WOORINEN VIC 3589",50033988,"SHL004","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0010529","20200515PWA_08 ","Pole fire at incident location",null,null," - neutral earthing resistor"]
[17,72,"2019-12-02","14:21:00",-34.380707000000001,141.65517,"4 Millewa Road, Werrimull Vic 3496",30567057,"RCT023","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0010532","20200515PWA_10","Powercor received a report of a Pole fire at LIS 215, Just off Millewa Rd.",null,null," - oil-filled circuit recloser (OCR)"]
[17,73,"2019-12-03","05:00:00",-38.272516000000003,143.151567,"259 Count Boundary Rd East, Camperdown",30149131,"CDN002","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0008967","20191209PWA_02 ","Pole fire reported by Vicfire at incident location. Crew confirmed pole fire. Burn marks around crossarm straps only. There was no ground fire, no reported injuries or third party property damage.",null,null," - rapid earth fault current limiter (REFCL)"]
[17,74,"2019-12-04","14:28:00",-35.941648999999998,144.37706,"Cnr of Hipwell Rd and Gunbower Island Rd  Gunbower",33018378,"CHA005","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0008952","20191206PWA_01 ","CFA reported a fire under a pole last night at the incident location and CFA extinguished the fire. Crew replaced HV fuse and believed small grass fire was from some time ago (no CFA on site). On 5/12 following CFA advise crew re attended site and confirmed the fire area of  5*60m Sqm.\nThe crew also did not find the cause of fire or the fuse operation.",null,null," - surge diverter"]
[17,75,"2019-12-06","19:21:00",-37.745617000000003,144.605512,"11 Strathtulloh Circuit, Strathtulloh 3338",33105868,"MLN011","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0008966","20191209PWA_01 ","Report received of grass fire at incident location. On arrival crew found that a FOLCB had overheated and resultant sparks caused a small grass fire (5 x 30m). There was no injuries or third party property damage.",null,null," - voltage regulator"]
[17,76,"2019-12-07","13:59:00",-35.980879999999999,141.84196700000001,"1981 Rainbow-Nhill Rd, Rainbow 3424",32120528,"NHL015","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0008970","20191209PWA_04 ","A call was received from the CFA stating that a wire had come down at the above address and had caused a fire. Powercor crew arrived onsite they found that the HV SWER conductor between Pole 33 and 34 Lake Hindmarsh had broken mid span and caused a grass fire. At the point that the conductor broke, a extremely large cactus was growing and it appears that the cactus had made contact with the HV conductor causing the fire and conductor failure. The fire burnt approx. 15 acres of grass, bush and cactus plantation. CFA attended and extinguished the fire. THere was no reported injuries.",null,null,"Public lighting"]
[17,77,"2019-12-08","01:17:00",-37.627231000000002,144.51764499999999,"431 DIGGERS REST-COIMADAI ROAD, COIMADAI VIC 3340",32168128,"MLN022","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0010535","20200515PWA_11 ","Crew attending a fault found that  the end had burnt off edo fuse tube. No ground fire.",null,null," - brackets (major road)"]
[17,78,"2019-12-09","08:36:00",-35.899715,144.28644800000001,"Leitchville-Kerang Rd, Leitchville VIC 3567, Australia",33021956,"CHA005","22kV AC","Rural Long"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Extreme",3.5,0.70000000000000007,"INC-0008968","20191209PWA_03","CFA reported a ground fire at the incident location. On arrival, a Powercor crew found a 200 Sqm ground fire. They also observed a bird flashover on the pole top but\nno damage to pole top assets. There was no reported injuries or third party property damage.",null,null," - brackets (minor road)"]
[17,79,"2019-12-09","00:38:00",-37.072111999999997,144.20702700000001,"Corner Johnstone Street and Elizabeth Street Castlemaine 3450",32045518,"BETS-CMN","66kV AC","Unknown"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0009023","20191212PWA_01 ","Vic fire reported explosion and fire and incident location. On arrival crew found that a bat had caused a flashover on 66kv conductor resulting in 66kv conductors coming in contact with 22kv circuit below.\nThere was a small grass fire (30m x 30m) , no reported injuries or third party property damage.",null,null," - lamps (major road)"]
[17,80,"2019-12-09","13:35:00",-36.350878999999999,144.712975,"25 SULLIVAN ROAD, ROCHESTER VIC 3561",33083749,"KYM001","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (residential)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0010536","20200515PWA_12 ","Branch fell breaking service line and causing a small fire.",null,null," - lamps (minor road)"]
[17,81,"2019-12-10","11:13:00",-37.346024999999997,144.70277300000001,"1686 Romsey Road Romsey 3434",32042999,"WND012","22kV AC","Rural Long"," - earth / earthing","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0009030","20191212PWA_03 ","During a fault patrol a crew found a small ground fire (2 x 2 mtrs) at the incident location. The fault and fire was caused by a dislodged earth wire contacting an EDO fuse unit. There was no injuries or third party property damage. Fire was extinguished by fault crew.",null,null," - luminaires (major road)"]
[17,82,"2019-12-11","17:05:00",-37.067450000000001,142.79413099999999,"Cnr Centenary Crt and Jubilee Rd, Stawell (opposite 12 Jubilee Rd, Stawell)",33053400,"STL007","22kV AC","Rural Long"," - transformer (pole mounted)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0009028","20191212PWA_02 ","VicFire reported a fire at the incident location. On arrival the crew found that a bird had caused a flashover on a substation pole. The resultant fault current caused the feeder CB to reclose and the bird to fall to the ground, resulting in a ground fire (approx. 8m x 2m) on road reserve and a 2m section of a customer front yard at 12 Centenary Crt. There were no reported injuries or third party damage.",null,null," - luminaires (minor road)"]
[17,83,"2019-12-18","11:52:00",-37.534064999999998,143.88542899999999,"15 KIEWA STREET, NERRINA VIC 3350",30003432,"BAN011","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0010537","20200518PWA_01 ","Inspector reports burnt HV crossarm near HV fuse mount at incident location. No ground fire.",null,null," - poles / columns (major road)"]
[17,84,"2019-12-19","17:37:00",-35.436382000000002,143.62112999999999,"O/S SHAE STUD, 189 Lake Baker Rd, Lake Boga VIC 3584, Australia",32159504,"SHL005","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0009219","20191224PWA_01 ","Vicfire reported grassfire involving Powercor assets. Upon arrival crew  found that a small grassfire had occurred approximately 50m X 15m in area which had been extinguished by the CFA. The LV fuse box on the cross-arm had burnt out as was the LV cross-arm on the sub pole. There was also minor damage to the pole. There was no reported injuries.",null,null," - poles / columns (minor road)"]
[17,85,"2019-12-20","16:13:00",-37.774106000000003,143.06166400000001,"565 Trawalla East Rd, Nerrin Nerrin 3351",32057787,"CDN006","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Extreme",3.5,16.099999999999998,"INC-0009208","20191223PWA_01 ","SWER ACR Trawalla P10A tripped to Lock out at 16:13hrs. Shortly afterwards a report of a \"fire in the area - pole fire\" was recieved. Crews patrolled the line and found an extinguished paddock fire at the incident address together with 3 bays of SWER conductor down on the ground. Evidence  of a tree branch on the ground near Trawalla P22. On arrival crew found the fire had been extinguished by persons unknown. There was no reported injuries.",null,null,"Other "]
[17,86,"2019-12-20","21:37:00",-36.817228,144.343366,"20 Red Tank Road Strathfieldsaye 3551",33034128,"BGO013","22kV AC","Rural Short"," - automatic circuit recloser (ACR)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Severe",2,9.1999999999999993,"INC-0009209","20191223PWA_02 ","CFA reported a ground fire has burnt pole, check for damage. Crew found a Magpie had caused a flash over, starting a 20m x 10m grass fire. There was no reported injuries , no property damage.",null,null," - connection box"]
[17,87,"2019-12-20","13:36:00",-38.381374399999999,142.228058,"31 Villiers St, Port Fairy 3284",31028939,"KRT022","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (residential)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Extreme",3.5,0.70000000000000007,"INC-0009210","20191223PWA_03 ","Vic Fire reported wire down and sparking at incident address. When crews arrived they found a neutral screen Service wire had failed due to contact with a cust resp tree. A small ground  (lawn) fire 2m x 2m in size had started on the front lawn area and was extinguished by Vic Fire. No injuries or property damage reported.",null,null," - earth / earthing"]
[17,88,"2019-12-20","15:48:00",-36.989356999999998,144.06472299999999,"84 HIGH STREET MALDON 3463",32050537,"CMN004","Low voltage AC (<1kV)","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0009211","20191223PWA_04 ","Customer reported broken branch laying across mains wires at incident location, not reachable from ground, smallish branch. Crew found tree branch caused conductors to clash starting small 300mm x 300mm ground fire. There was no reported injuries or third party property damage."]
[17,89,"2019-12-20","20:38:00",-38.181750999999998,144.437895,"105 Whitehorse Rd, Moolap 3224",30064947,"GLE024","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"Severe",2,2,"INC-0009212","20191223PWA_05 ","Fire brigade reported pole fire and grass fire and incident address. When crews arrived confirmed a LV UG service cable on Transformer pole had failed at the connection box. There was a small 4 square spot fire at the base of the pole. There was no reported injuries or property damage."]
[17,90,"2019-12-20","20:11:00",-38.155113,144.31114700000001,"230 Scenic Rd, Highton 3216",32086978,"GL021","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0009213","20191223PWA_06 ","Fire Brigade reported pole fire at incident address. When crews arrived they found a small grass fire 4m2, had started due to a loose connection on a LV fused bus isol.  No injury or property damage was reported.",null,null,"Extra low voltage AC (<50V)"]
[17,91,"2019-12-20","14:28:00",-37.875346999999998,144.79530199999999,"QUEEN STREET, ALTONA VIC 3018",32178028,"LVN022","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0010538","20200518PWA_03","Report of pole fire at incident location. No ground fire.",null,null,"Low voltage AC (<1kV)"]
[17,92,"2019-12-20","15:27:00",-37.577635000000001,143.83962299999999,"804 TALBOT STREET S, REDAN VIC 3350",31001148,"BAS012","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0010539","20200518PWA_02","Service on the ground neutral screen service had burnt to the ground leaving some burns on some customer grass.",null,null,"2.2kV AC"]
[17,93,"2019-12-21","01:51:00",-37.069678000000003,142.79247100000001,"Lot 2 39 London Rd Stawell 3380",32095103,"STL007","22kV AC","Rural Long"," - insulators","three phase","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0009216","20191223PWA_09 ","Lightning has Struck the pole at incident location. There was damage to  two Disc Insulators, there was a ground fire approx. 2 x 4m. There was no injuries reported or third party property damage.",null,null,"6.6kV AC"]
[17,94,"2019-12-22","22:58:00",-35.471916,143.82603,"Murrabit W Rd, Benjeroop VIC 3579, Australia",30255066,"KGT003","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0009220","20191224PWA_02 ","Vicfire called to advise that PCA assets could have been the possible cause of a grassfire. On arrival crew found  a conductor had fallen and was on the ground at the incident location. CfA extinquished a small grass fire (100m x 5m) on roadside. There was no reported injuries.",null,null,"11kV AC"]
[17,95,"2019-12-22","12:37:00",-38.143940999999998,142.98533699999999,"120 CRUICKSHANKS ROAD, GLENORMISTON NORTH VIC 3265",30042218,"TRG001","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0010540","20200518PWA_07 ","Crew attending outage found burnt off edo fuse at incident location.",null,null,"12.7kV AC (SWER)"]
[17,96,"2019-12-23","07:25:00",-38.011526000000003,143.972782,"19 Tolson st, Shelford vic 3329",31034200,"GL012","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0010549","20200518PWA_08 ","Crew attending outage found burnt off edo fuse at incident location.",null,null,"22kV AC"]
[17,97,"2019-12-24","13:04:00",-37.443972000000002,143.98046600000001,"Ballarat-Daylesford Rd, Newlyn VIC 3364, Australia",33005282,"BAN008","Low voltage AC (<1kV)","Rural Long"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0009223","20191230PWA_01 ","Vic fire reported a ground fire at the incident location. Upon arrival, a Powercor crew found an overheated isolator connection had burnt out dropping molten particles on the the grass below. This resulted in a 120 sq section of roadside being burnt. There was no reported injuries or third party property damage.",null,null,"33kV AC"]
[17,98,"2019-12-24","16:22:00",-37.719732,141.962853,"204 Balkins Rd, Hamilton VIC 3300, Australia",30090118,"HTN006","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0009224","20191230PWA_02 ","Customer reported burnt out mains box. When crews arrived they found a failed FOLCB on Substation pole. There was small spots of burning amongst the long grass at the base of the pole. There was no reported injuries or third party property damage.",null,null,"66kV AC"]
[17,99,"2019-12-25","23:54:00",-38.186745000000002,143.18621300000001,"460 Chocolyn Rd, Camperdown 3260",30047237,"CDN004","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0009226","20191230PWA_04 ","Vic Fire reported a pole fire at the incident address. When crews arrived they found a FOLCB on substation pole had failed resulting in a equip fire and small (9x2m) grd fire. CFA crews extinguished the fire. No injuries or property damage was reported.",null,null,"132kV AC"]
[17,100,"2019-12-25","14:51:00",-36.722512000000002,144.26543000000001,"23 Bright St, California Gully VIC 3556, Australia",32032597,"EHK023","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0009228","20191230PWA_06 ","Vic fire reported an umbrella has blown onto HV line and wire down which started small grass fire. Crew found that an outdoor table umbrella had been caught by a gust of wind and had been thrown into the HV. The centre phase of the three phase line has as a result  burnt to the ground and started a grassfire in road reserve and creek reserve. There were no reported electrical injuries (Ambulance onsite were treating a resident for smoke inhalation.)",null,null,"220kV AC"]
[17,101,"2019-12-27","05:25:00",-38.315860000000001,144.031103,"155 WORMBETE STATION ROAD, WURDIBOLUC VIC 3241",33040998,"WIN022","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within electric line construction area",19.8,"High",0.5,9.9,"INC-0010552","20200518PWA_09 ","Following supply failure crew found an edo fuse had hung up and burnt in half.",null,null,"330kV AC"]
[17,102,"2019-12-28","19:00:00",-38.460420999999997,144.10540900000001,"12 Beach Rd, Aireys Inlet, 3231",31039147,"WPD014","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,{"$f":"IF(OR(P139=\"\",R139=\"\"),\"\",IF(AND(O139=\"within electric line construction area\",Q139=\"No forecast\"),1,P139*R139))","v":0.1},"INC-0009229","20191230PWA_07 ","Customer reported service down the side of pole on fire. On arrival the crew found a single phase fuse box had burnt and caused a small fire that was quickly extinguished by locals and CFA who were on site. There was no reported injuries or third party property damage.",null,null,"500kV AC"]
[{"$f":"COUNTA(C140:O140,Q140,T140:V140)","v":17},103,"2019-12-29","18:30:00",-37.064768000000001,142.79324500000001,"20 Oregan Street Stawell",31016235,"STL005","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O140=\"\",\"\",IF(O140=\"LBRA only\",0.2,IF(O140=\"HBRA only\",1,IF(O140=\"within electric line construction area\",19.8,IF(O140=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"Very high",{"$f":"IF(Q140=\"\",\"\",IF(Q140=\"No forecast\",0.1,IF(Q140=\"Low-moderate\",0.2,IF(Q140=\"High\",0.5,IF(Q140=\"Very high\",1,IF(Q140=\"Severe\",2,IF(Q140=\"Extreme\",3.5,5)))))))","v":1},4.5999999999999996,"INC-0009230","20191230PWA_08","Vic Fire reported a wire down and small fire at the incident location. On arrival the fault crew found that a branch had broken from a tree standing on the opposite side of the road from this property and had fallen onto the overhead distribution wires, bringing 3 bays of HV & LV conductors to the ground, and causing the small fire in the front yard of this residence. The fault crew also found evidence of High Voltage Injection damage to the electrical wiring and the switchboard at this residence. There was no reported injuries.",null,null,"Extra low voltage DC (<120V ripple free)"]
[17,104,"2019-12-29","17:53:00",-35.025393000000001,142.79354699999999,"Intersection of O'Toole Road and Sleep Road, Manangatang",32140525,"OYN003","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"Severe",2,2,"INC-0009231","20191230PWA_09 ","Lightning Strike Pole # 6 & Pole #5  Winnambool Spur OYN003 30-40 Hectares burnt. Fault tamer fuse destroyed, fire ignited at pole 6. There was no reported injuries.",null,null,"Low voltage DC (<1.5kV)"]
[17,105,"2019-12-30","11:00:00",-38.385854999999999,142.607767,"14 Grauers Rd, Allansford VIC 3277.",32198150,"WBL002","22kV AC","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Extreme",3.5,0.70000000000000007,"INC-0009232","20191231PWA_01 ","Vicfire reported  branch landed on conductors causing sparking and grass fire. On arrival crew reported small grass fire under line (1m*1m)  started by customer's tree branch contacting 22kV overhead conductors outside the incident address. Fire is out and branch has been pruned away form the line.",null,null,"600V DC"]
[17,106,"2019-12-30","13:15:00",-37.828589999999998,144.80781999999999,"38 Dohertys Road, Laverton North, 3026.  (Substation Dohertys 34-Cherry SStn)","PA0121380","LVN032","22kV AC","Urban"," - dropper / bridge","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Extreme",3.5,0.70000000000000007,"INC-0009233","20191231PWA_02 ","Vic fire requested  attendance required at factory fire. Some tin roof has blown onto HV conductors and caused a grassfire. Crew advise that a tin roofing sheet has come loose in strong winds and has been blown of the warehouse at 38 Dohertys Road onto its substation known as  Dohertys 34-Cherry.\nResulting in substation fire and a large grass fire in a vacant paddock to its east. Grass fire approximately 50m*300m. Grass fire has been extinguished by the CFA & MFB who were on site. There were no reported injuries.",null,null,"1500V DC"]
[17,107,"2019-12-30","19:31:00",-37.566833000000003,142.89770300000001,"1485 Delacombe Way, Mininera",30084285,"ART033","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Extreme",3.5,16.099999999999998,"INC-0009234","20191231PWA_03 ","Vic Fire reported a wire had come down from a pole and had started a grass fire at the incident location. On arrival the fault crew found that a tree had fallen from the other side of the road (outside clearance space) and had fallen across the overhead distribution wires, breaking a HV crossarm, and causing a grass fire below.\nThere was no reported injuries.",null,null,"Earthing cable"]
[17,108,"2019-12-30","13:35:00",-38.423059000000002,144.17686599999999,"2A SIXTH AVENUE,ANGLESEA,VIC,3230",33041664,"WPD021","Low voltage AC (<1kV)","Rural Short"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Extreme",3.5,0.70000000000000007,"INC-0009235","20191231PWA_04 ","Vicfire reported Transformer explosion - powerdown at this address. Crew attended to find ground fire under substation 5m*10m. The grass fire was extinguished by customer and CFA also attended. There was no reported injuries."]
[17,109,"2019-12-30","14:00:00",-37.677846000000002,144.57096799999999,"50 Quail Crescent, Melton,3337.",30300618,"MLN032","Low voltage AC (<1kV)","Rural Short"," - connector / termination","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Extreme",3.5,0.70000000000000007,"INC-0009236","20191231PWA_05 ","Following reports of outage crew found a burnt out copper to aluminium connection on north side transformer bus. Molten particles had caused a number of small spot fires in the grass below. There was no reported injuries or property damage."]
[17,110,"2019-12-30","22:51:00",-36.316204999999997,141.300366,"1004 Broughton Rd, Kaniva VIC 3419, Australia",32100682,"NHL031","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Extreme",3.5,3.5,"INC-0009237","20191231PWA_06","Vic Fire reported  a pole fire at the incident location. On arrival the fault crew found a HV crossarm had burned through at the kingbolt and had broken. There was no ground fire, no reported injuries or third party property damage.",null,null,"single wire earth return (SWER)"]
[17,111,"2019-12-30","23:04:00",-36.733454000000002,142.208439,"2 Apricot Street, Horsham 3400",32116250,"HOTS-HSM2","66kV AC","Unknown"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Extreme",3.5,0.70000000000000007,"INC-0009239","20191231PWA_09 ","Vic Fire reported a pole fire at the incident location. On arrival the fault crew found that a HV crossarm had been burning at a bridging insulator, but the fire had been extinguished before the crossarm burned through.\nCFA attended and extinguished the crossarm fire. There was no ground fire.",null,null,"single phase"]
[17,112,"2019-12-30","20:40:00",-36.739471000000002,141.05176499999999,"8576 Natimuk Frances Road, Neuarpurr 3413",32090113,"HSM004","22kV AC","Rural Long"," - surge diverter","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"Extreme",3.5,3.5,"INC-0009243","20200102PWA_01 ","Vic Fire reported  a grass fire at the incident location. On arrival the fault crew found that a surge diverter connected to the substation pole at the incident location had flashed over causing a small grass fire at the base of the pole. There was no reported injuries or third party property damage.",null,null,"two phase"]
[17,113,"2019-12-31","04:52:00",-37.795417,144.80494100000001,"12 Corella Rd, Sunshine West VIC 3020",32166103,"SU035","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009247","20200102PWA_03 ","Report received of Low conductors in Corella rd Sunshine West. Crew advise pole fire roadside phase strain cross-arm has burnt through. Roadside phase with insulators attached is hanging in midair. Possible high voltage injection, LEI on site Miles Tobias. No ground fire no person injured.",null,null,"three phase"]
[17,114,"2019-12-31","04:50:00",-37.722966999999997,144.827395," 42 Greengully Road, Keilor, 3036.",30114080,"SA002","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009248","20200102PWA_04","Crew advise pole fire intermediate arm has burnt through at kingbolt. No ground fire or reported injury."]
[17,115,"2019-12-31","06:41:00",-37.742404000000001,144.80921499999999," 36 Vincent Ave, St Albans, 3020.",32163794,"SA007","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009249","20200102PWA_05 ","Customer reports sparking and buzzing noise coming from pole in front of his home, believes it is coming from the conductors at the top of the pole. still on supply at site, sparks not reaching the ground. Crew advise pole fire. Cross-arm on roadside of pole has burnt through at strap bolt cross-arm is broken, insulator has shattered and fallen onto nature strip below. There was no ground fire, no reported injuries or third party property damage."]
[17,116,"2019-12-31","00:10:00",-36.704315999999999,142.21530899999999,"1 Pryors Road, Horsham 3400",30078377,"HSM009","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009250","20200102PWA_06","Vic Fire reported a pole fire at the incident location. On arrival the fault crew found a HV crossarm had burned through, dropping the outside conductor.  There was no ground fire.",null,null,"Negligible: no ground fire"]
[17,117,"2019-12-31","06:41:00",-37.724091000000001,144.836579,"2 Skyline Dr, Keilor VIC 3036",30108788,"SA002","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009251","20200102PWA_07 ","Vic fire reported crossarm on fire at incident location. Crew advise pole fire originating at pin of bridging insulator. Cross arm has lost integrity and insulators have broken away causing fault on feeder and ACR to trip. No ground fire and no reported injury.",null,null,"Localised: less than 10 sq.m"]
[17,118,"2019-12-31","07:00:00",-37.819772,144.80778699999999,"13 Raymond Road, Laverton North 3026.",30115647,"LVN032","22kV AC","Urban"," - pole (wood)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"High",0.5,0.1,"INC-0009252","20200102PWA_08 ","Customer reported lightning has struck the pole and its been smoking and there has been sparks coming out as well, also adv its burnt out black at some parts. Crew attended to find HV tee-off arm broken, conductors hanging with insulators attached. MFB attended to extinguish pole fire. Large chunks of  the wooden cross-arm on the ground. No ground fire, no reported injuries.",null,null,"Small: 10 - 1000 aq.m"]
[17,119,"2019-12-31","05:30:00",-37.764445000000002,144.81539000000001,"229 St Albans Rd, St Albans VIC 3021.",30112999,"SSE011","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009254","20200102PWA_10 ","Crew advise cross-arm burnt through on Red phase roadside HV isolator and fell into low voltage below, HV injection occurred. There was no ground fire or reported injuries.",null,null,"Medium: 1000 sq.m - 10 ha"]
[17,120,"2019-12-31","07:12:00",-37.764479999999999,144.839673,"68 Berkshire Road, Sunshine North VIC 3020",30102782,"SSE032","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009255","20200103PWA_01 ","Report received of pole fire at incident location. Crew advised a HV tee off crossarm has broken due to a pole fire. The conductors have come to rest across parked trucks at the premises. There was no ground fire or reported injuries.",null,null,"Large: more than 10 ha"]
[17,121,"2019-12-31","04:17:00",-37.800573999999997,144.81093899999999,"69 Cawood Dr, Sunshine West VIC 3020",31023754,"SSE033","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009257","20200103PWA_03 ","Crew reported pole fire at incident location. A high voltage isolator has broken off due to a crossarm fire and is now resting on the LV conductors below. There is reports of HVI. There was no ground fire or reported injuries."]
[17,122,"2019-12-31","11:04:00",-37.610190000000003,144.511436,"47 ANTIMONY MINE ROAD,COIMADAI,VIC,3340",30107875,"MLN022","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0009258","20200103PWA_04 ","Crew reported a hv crossarm fire at the incident location. CFA on site to extinguish the fire. There was no ground fire, no reported injuries or third party property damage."]
[17,123,"2019-12-31","02:20:00",-36.704317000000003,142.21530899999999,"3 Pryors Rd, Horsham VIC 3400",30078377,"HSM009","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009259","20200103PWA_05","Report received of a pole fire at the incident location. Crew advise cross-arm burnt on LIS 433, Pryors Lane P1. LEI confirmed no high voltage injection. There was no ground fire, no reported injuries or third party property damage.",null,null,"Started in or originated from a distribution system"]
[17,124,"2020-01-01","11:13:00",-37.783935999999997,144.81386499999999,"94 Forrest Street, Ardeer, 3022",31034122,"SSE033","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009260","20200103PWA_06","Customer reported HV lines on ground and has started a small fire at incident location. Crew attended site and found the incident was caused by balloons released by unknown persons coming in contact with the over head conductors. The resultant contact caused sparks to fall onto the nature strip and  adjacent reserve causing a small grass fire  (10x20mtrs). The incident cause the 22kv conductor to rupture and fall to ground. The fault current also caused the connections at Pole 19 lis 25672 ( in Forest st 600mts from original fault) to fail allowing the conductor to fall onto the roadway. There was suspected HVI. There was no reported injuries.",null,null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system"]
[17,125,"2020-01-02","17:53:00",-36.363154999999999,145.326052,"130 CORNISH ROAD, ARDMONA, VIC, 3629",33092737,"MNA014","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0009269","20200107PWA_03 ","CFA reported grass fire around our assets in road reserve.  On arrival crew found a fire approx. 80m x 15m along road reserve. Crew identified possible bird flashover and a bridge burnt through. Crew found bird at base of pole. There was a small grass fire, no reported injuries, minor damage to a fence.",null,null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system"]
[17,126,"2020-01-02","19:14:00",-35.346632,143.547167,"80 GRAY STREET, SWAN HILL, VIC, 3585",33070600,"SHL007","Low voltage AC (<1kV)","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009270","20200107PWA_04 ","Vic Fire reported ground fire at base of pole at above address. When crew arrived, they found that a cable between pole transformer and isolator had melted. Molten material had ignited the grass below. There was no injuries or third party property damage.",null,null,"Started by lightning striking a distribution system or a part of a distribution system "]
[17,127,"2020-01-02","20:54:00",-37.429437999999998,144.54821899999999,"67 ELLANDEE CRESCENT, MACEDON, VIC, 3440",32050356,"GSB014","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0009271","20200107PWA_05 ","Crew reported possible HVI from burnt cross-arm. Cross arm had burnt through on one side and HV conductor had landed on red phase of LV. There was no ground fire or reported injuries.",null,null,"Started by any other thing forming part of or coming into contact with a distribution system"]
[17,128,"2020-01-04","16:04:00",-36.648515000000003,144.31951100000001,"1 OLD MURRAY RD HUNTLY",32035322,"EHK031","12.7kV AC (SWER)","Rural Short"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Severe",2,9.1999999999999993,"INC-0009263","20200106PWA_01 ","Call received from Vic Fire reporting wires down and requesting urgent isolation of power. Crew were escorted by CFA to area where a SWER wire was down between Wallenjoe Pole 2 and Wallenjoe Pole 3 and found a tree had fallen on a SWER line.  Damage to rural fencing ,  no injuries reported.",null,null,"Otherwise started by a distribution system"]
[17,129,"2020-01-04","18:16:00",-36.695331000000003,144.33064200000001,"112 STRICKLAND STREET, ASCOT, VIC, 3551",33021191,"EHK033","Low voltage AC (<1kV)","Urban"," - overhead service conductor (other)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0009274","20200107PWA_07 ","Customer reported tree branch had come down & brought down service wire and a grass fire had occurred nearby. On arrival, crew found that a grey twisted wire road crossing had a tree branch on it and had been pulled at the junction box on the substation pole that it was coming from. There a patch of grass ignited (3x3mtr) around 10 metres from the pole. There was no injuries, no third party property damage."]
[17,130,"2020-01-04","14:12:00",-38.307361,142.34816000000001,"14 O'Gradys Lane, Koriot",33099459,"KRT013","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0009280","20200108PWA_05 ","CFA reported a ground fire at the above location. Powercor crew attended and found the ground fire had been started by faulted FOLCB. There was no reported injuries."]
[17,131,"2020-01-05","17:06:00",-35.444789999999998,143.79471000000001,"614 WEARNE ROAD, PENTAL ISLAND, VIC, 3586",30102272,"KGT003","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0009281","20200108PWA_06 ","Customer reports broken cross-arm, low wire and grass fire at incident location. When crew arrived, they found that cross-arm had burnt at the road side HV insulator and the wire had dropped to approx. 1m height. Crew found that the fire had been extinguished by the person reporting the incident. There was no reported injuries.",null,null,1]
[17,132,"2020-01-05","16:19:00",-35.075079000000002,142.31812099999999,"11 RAILWAY TERRACE, OUYEN, VIC, 3490",32150815,"OYN007","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009282","20200108PWA_07 ","Report from Vic Fire that pole on fire at above address. When crew arrived they found that the cross arm had burnt through from the cross arm strap bolt. The outer phase of the HV had fallen onto the LV cross-arm.  Crew confirmed no HVI had occurred.  There was no ground fire, no injury, no third party damage.",null,null,2]
[17,133,"2020-01-05","17:56:00",-36.330641,145.10360700000001,"365 DUNBAR ROAD, LANCASTER, VIC, 3620",30130749,"SHTS-KYM1","66kV AC","Unknown"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009286","20200109PWA_01 ","Passer by reported broken cross arm and low wires at incident location.  On arrival crew found that the cross arm had burn marks on it and had broken at the cross arm strap bolt. 66kV conductor had fallen and was hanging low.  No ground fire, no third party damage, no injuries.",null,null,3]
[17,134,"2020-01-05","07:53:00",-36.362831,144.79423299999999,"58 LETCHER ROAD, NANNEELLA, VIC, 3561",30120913,"KYM001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,{"$f":"IF(OR(P171=\"\",R171=\"\"),\"\",IF(AND(O171=\"within electric line construction area\",Q171=\"No forecast\"),1,P171*R171))","v":0.1},"INC-0009287","20200109PWA_02 ","Reports from customer of cross arm on fire.  Crew attended site and found that the wooden cross arm had burnt around the area of one of the EDO fuse arms and the fuse unit had fallen from the cross-arm.  No ground fire at site.  No injuries no third party damage.",null,null,4]
[17,135,"2020-01-05","15:39:00",-36.455992000000002,142.05085,"66 Horsham Rd, Dimboola VIC 3414, Australia",32121199,"HSM006","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0009288","20200109PWA_03 ","Report received report of pole fire at incident location. On arrival crew found a pole top burnt off and crossarm burnt. There was a small grass fire of 10 sq m, no injuries.",null,null,5]
[17,136,"2020-01-05","12:34:00",-36.734881999999999,141.14159000000001,"61 Hawkins Rd Minimay 3413",30139567,"HSM004","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0009289","20200109PWA_04 ","Vic fire reported Pole fire and grass fire. On arrival crew found a SWER pole burnt in half and a grass fire. There was no reported injuries.",null,null,6]
[17,137,"2020-01-05","09:09:00",-37.535915000000003,143.81932,"25 Learmonth Rd Wendouree 3355",32014213,"BAN004","22kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0009290","20200109PWA_05 ","Report received of pole on fire at incident location. On arrival crew found pole alight at king bolt position. There was no ground fire, no reported injuries or third party property damage.",null,null,7]
[17,138,"2020-01-05","18:15:00",-36.302883999999999,144.616636,"647 PRAIRIE-ROCHESTER RD BAMAWM",30120470,"SHP012","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009292","20200109PWA_06 ","Reports from customers of dim lights and broken cross arm with wire down. On arrival, crews found cross arm had burnt and broken at EDO holder and dropped to ground and a HV conductor was hanging over LV conductor. Crew identified possible HVI and inspector called to investigate. There was no ground fire, no reported injuries or third party property damage.",null,null,8]
[17,139,"2020-01-05","17:53:00",-35.462468999999999,143.63244499999999,"2 Lalbert Rd, Lake Boga VIC 3584",30101817,"KGT004","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009293","20200109PWA_07 ","CFA reported pole fire in Lalbert Rd near Station Street. When crew arrived they found that cross arm had burnt through at the cross arm strap. No ground fire confirmed by crew.  No injuries or third party damage.  CFA extinguished fire.",null,null,9]
[17,140,"2020-01-05","17:47:00",-36.055278999999999,144.11444900000001,"20 VICTORIA STREET, PYRAMID HILL, VIC, 3575",30567286,"CHA006","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009294","20200109PWA_08 ","Vic Fire reported pole fire and wire low at above address and crossing railway line. Concerned that train could hit line. On arrival crew found that cross-arm was burning from the King Bolt on both HV cross arms. No injury or third party damage.  No ground fire.",null,null,10]
[17,141,"2020-01-05","16:24:00",-36.181463000000001,144.031924,"201 Yarrawalla S Rd, Yarrawalla VIC 3575",32032629,"CHA006","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0009296","20200110PWA_01 ","Vic Fire reported ground fire started by our assets at incident location. When crew arrived, they found that the crossarm had burnt through at the roadside pin insulator and burnt grass underneath our assets in road reserve. There was no HVI. No injuries or third party damage.",null,null,{"$f":"Y177+1","v":11}]
[17,142,"2020-01-05","09:36:00",-36.323597999999997,141.87716,"575 Gerang-Glenlee Rd Gerang Gerung 3418",31015798,"NHL015","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0009297","20200110PWA_02 ","Report received of pole and ground fire at incident location. On arrival crew found Buck x arm fire and grass fire. There was no reported injuries or third party property damage.",null,null,{"$f":"Y178+1","v":12}]
[17,143,"2020-01-05","20:30:00",-36.403609000000003,145.39797899999999,"6 Murray St, Shepparton VIC 3630",32189142,"MNA024","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009298","20200110PWA_03 ","Vic Fire reported cross-arm burning through. On arrival, crew found cross arm burning at fuse holder bolt on HV cross-arm. Assets were still secure to cross arm. No injuries, no ground fire, no third party damage.",null,null,13]
[17,144,"2020-01-05","23:13:00",-34.636937000000003,142.744405,"289 Happy Valley Rd, Robinvale Irrigation District Section C VIC 3549",32145857,"RVL001","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0009299","20200110PWA_04 ","Report from Vic FIre of pole fire at 201 Shaggy Ridge Rd Robinvale. Crew attended and found cross arm had burnt and broke at the cross-arm strap bolt and the outer phase was being held up by the stays off the strain.  No ground fire, no injury, no third party damage.",null,null,14]
[17,145,"2020-01-05","21:21:00",-35.199140999999997,143.38259400000001,"50 DICKINSON ROAD, VINIFERA, VIC, 3591",32159107,"SHL002","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009300","20200110PWA_05 ","Vic Fire reported pole fire at above address. On arrival, crew found cross arm hanging from top of pole and still alight.  Burning appears to have occurred at Kingbolt.  No HVI suspected.  No ground fire, no injuries, no third party damage.",null,null,15]
[17,146,"2020-01-05","19:35:00",-34.284846000000002,142.21014500000001,"63 Johns Rd, Red Cliffs VIC 3496, Australia",32153003,"RCT023","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009301","20200110PWA_06 ","Reported as all supply fail, crew attended and found pole fire with cross arm burnt through at fuse holder and conductor hanging beside pole below transformer.  No ground fire.  No injuries or third party damage.  No reports of HVI.",null,null,16]
[17,147,"2020-01-05","17:45:00",-37.661551000000003,143.83006,"16 Sobeys Rd, Napoleons VIC 3352",32013707,"BAS022","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0009303","20200110PWA_07 ","Report received of pole fire and broken crossarm. There was no ground fire, no reported injuries or third party property damage.",null,null,17]
[17,148,"2020-01-05","20:55:00",-34.720098999999998,143.17305999999999,"8655 Murray Valley Highway, Boundary Bend, Vic. 3599",32148923,"BBD021","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0009304","20200110PWA_08 ","Vic fire reported pole fire.  Crew arrived to find one end of pole was burning.  Crew isolated and CFA extinguished fire. No ground fire, no reported injuries or third party property damage.",null,null,18]
[17,149,"2020-01-05","07:23:00",-38.437624999999997,143.81143,"685 Division Road, Murroon",30052618,"WIN011","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0009344","20200115PWA_04 ","CFA reported a pole fire in Division Road, Murroon. Crew attended and confirmed a crossarm fire on pole 2 Murroon Spur, no ground fire.",null,null,19]
[17,150,"2020-01-06","04:31:00",-35.786194000000002,144.029526,"8224 Murray Vally Hwy Kerang East 3579",32032025,"KGT003","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0009305","20200110PWA_09","A Powercor fault crew patrolling a faulted SWER line and found a pole fire at the incident location. The pole top ignited but no ground fire reported.",null,null,20]
[17,151,"2020-01-06","16:07:00",-34.207965000000002,142.06384,"66 Oak Ave, Birdwoodton VIC 3505",30096077,"MBN014","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009306","20200110PWA_10 ","Report from customer of Pole top/crossarm has caught fire and fallen to the ground. Fire is now out however wires/assets are still hanging off the pole. Crew arrived, they found that the cross arm had burnt from the king bolt. No ground fire, no injuries, no third party damage."]
[17,152,"2020-01-06","12:31:00",-34.661552,142.759477,"156 Madang Rd, Robinvale Irrigation District Section E VIC 3549",30097348,"RVL001","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009307","20200110PWA_11 ","Customer report of low wire at above address.  Crew attended site and found that a cross arm had burnt through at the cross arm strap bolt and one of the conductors was hanging at approx. 5m.  No ground fire at site.  No injuries or third party damage."]
[17,153,"2020-01-06","16:21:00",-34.794581000000001,142.56488300000001,"2862 Hattah-Robinvale Rd Liparoo Vic 3549",32140710,"WMN021","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0009308","20200110PWA_12 ","ZSS trip to lockout at Wemen Zone Substation. Crew arrived and found a pole fire on 66/22kV pole where 22kV crossarm had burnt through at the king bolt and dropped the top of the pole with the 66kV down to ground.  No ground fire, no injury, no third party damage."]
[17,154,"2020-01-06","21:00:00",-34.403222,142.28113500000001,"129 Kulkyne Way Iraak 3494",30097098,"RCT014","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",{"$f":"IF(Q191=\"\",\"\",IF(Q191=\"No forecast\",0.1,IF(Q191=\"Low-moderate\",0.2,IF(Q191=\"High\",0.5,IF(Q191=\"Very high\",1,IF(Q191=\"Severe\",2,IF(Q191=\"Extreme\",3.5,5)))))))","v":0.5},{"$f":"IF(OR(P191=\"\",R191=\"\"),\"\",IF(AND(O191=\"within electric line construction area\",Q191=\"No forecast\"),1,P191*R191))","v":0.1},"INC-0009310","20200110PWA_14","A Powercor fault crew attending a fault found that a pole fire at the incident location. There was no ground fire or third party damage."]
[17,155,"2020-01-06","11:23:00",-36.225769,143.85182399999999,"793 MYSIA EAST ROAD,MYSIA,VIC,3518",31002708,"CTN002","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0010031","20200228PWA_02","Customer reported wires low enough to touch. On arrival crew found a crossarm had burnt in half. There was no ground fire, no reported injuries or third party property damage."]
[17,156,"2020-01-09","15:18:00",-37.530054999999997,143.88803200000001,"60 Alkera Rd Invermay 3352",30003992,"BAN007","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0009316","20200113PWA_01 ","Vic Fire reported a ground fire at the incident location. A Powercor crew found that FOLCB on the pole (LIS 45326) overheated and fallen debris caused 6*30 grass fire. The fire damage to a customer's fence. There was no reported injuries."]
[17,157,"2020-01-09","16:45:00",-38.468463999999997,143.3075,"856 Coradjil Rd, Simpson VIC 3266",31032683,"CDN001","22kV AC","Rural Long"," - surge diverter","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0009317","20200113PWA_02 ","Crew were sectionalizing line to locate a feeder fault on CDN001. When restoring line, a lighting arrester failed on LIS-964946 \"HEYJILL 2\" S/S. The debris fell to the ground causing fire approximately 20m x 20m. The CFA and farmer assisted containing the fire. No damage to customer's property or assets identified. Fire burnt underneath wooden fence and around water tank. There was no reported injuries"]
[17,158,"2020-01-09","19:07:00",-36.751313000000003,144.27322000000001,"3 Milroy Street, Bendigo VIC 3550",32037243,"BET002","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009319","20200113PWA_03 ","Customer at incident address reported sparks dropping from pole and starting ground fire at base of pole.  Upon arrival fault crew found that white phase LV isolator at substation \"Milroy Valentine 8\" had failed and dropped molten material to ground, commencing small fire at base of pole. There was no reported injuries or third party property damage."]
[17,159,"2020-01-09","20:50:00",-36.842582999999998,143.87974,"3460 Bendigo -Maryborough Road, Laancoorie VIC 3463",30019863,"MRO007","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0009320","20200113PWA_04 ","CFA reported pole fire at incident address, Upon arrival crew found that ISO pole \"Waanyarra P4\" was burning internally. Crew isolated for CFA to extinguish internal burning. No ground fire, no injuries or 3rd party damage."]
[17,160,"2020-01-10","20:22:00",-36.520663999999996,145.01376999999999,"1050 Middle Rd, Rushworth VIC 3612, Australia",30127001,"SHP014","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Severe",2,2,"INC-0009321","20200113PWA_05 ","Rushworth P119 ACR tripped to lockout. Upon arrival fault crew found that P184 Rushworth had burnt through between HV x-arm kingbolt & stay eyebolt, the pole top assembly dislodged from pole and landed on roadway. No ground fire or 3rd party damage."]
[{"$f":"COUNTA(C198:O198,Q198,T198:V198)","v":17},161,"2020-01-10","20:59:00",-36.362198999999997,145.41174000000001,"6 Fitzgerald Street, Shepparton VIC 3630",30129783,"SHN022","22kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0009322","20200113PWA_06 ","Customer reported pole top sparking and smoking. Upon arrival crew found that intermediate HV/LV pole had ignited at the HV X-arm kingbolt position. No ground fire or 3rd party damage."]
[{"$f":"COUNTA(C199:O199,Q199,T199:V199)","v":17},162,"2020-01-10","15:27:00",-36.739181000000002,142.08514,"1230 Wimmera Hwy Qaontong 3401",32097564,"HSM004","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0009323","20200113PWA_07 ","Vic Fire reported a pole fire at the incident location. Upon arrival, a Powercor crew found that a cross arm bunt through and fallen apart.  There was no ground fire, no reported injuries or third party property damage."]
[17,163,"2020-01-10","23:00:00",-36.434514,145.43173999999999,"775 Doyles Road, Kialla VIC 3631",30130476,"STN021","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0009324","20200113PWA_08 ","CFA reported pole fire at incident location.  Upon arrival crew found that an intermediate X-arm on substation pole ( Doyles Lane South P45 ) had ignited and burnt through at the kingbolt position, conductors remained aloft held up by x-arm straps. No ground fire or 3rd party damage."]
[17,164,"2020-01-10","21:22:00",-36.295279999999998,144.56288000000001,"48 Vise Rd, Bamawm VIC 3561",30121008,"SHP012","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0009326","20200113PWA_09 ","CFA reported pole fire at the incident location.  Upon arrival crew found that an intermediate x-arm on a substation pole ( Hann 8 ) burnt through at the kingbolt position. Conductors remained aloft held up via x-arm straps. No ground fire or 3rd party damage."]
[17,165,"2020-01-11","16:30:00",-38.038311,144.41960399999999,"Outside 110 and 100 Coonawarra Drive, Avalon 3212",32085621,"FNS032","22kV AC","Rural Short"," - transformer (pole mounted)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0009327","20200114PWA_01 ","The crew were dispatched to a ground fire and blown transformer at the incident location. On arrival the crew found a 10kva transformer had failed causing debris to fall to the ground igniting grass below. Oil had also fallen to ground below. There was some damage to customers fencing and vegetation. No injuries were reported."]
[17,166,"2020-01-11","08:46:00",-36.106793000000003,141.40604300000001,"Cnr Nhill-Murrayville rd and E.Juss Rd, Yanac",32109482,"NHL031","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0009328","20200114PWA_02 ","Passing motorist reported broken Xarm and pole fire in paddock. Crew attended and found top of pole burnt off and Xarm burnt thru at king bolt. No CFA attended. No ground fire start. No shock or third party damage."]
[17,167,"2020-01-13","16:41:00",-37.024642999999998,143.74977999999999,"220 Parks Road, Maryborough VIC 3465",32020616,"MRO005","22kV AC","Rural Long"," - underground cable","three phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O204=\"\",\"\",IF(O204=\"LBRA only\",0.2,IF(O204=\"HBRA only\",1,IF(O204=\"within electric line construction area\",19.8,IF(O204=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"High",0.5,0.1,"INC-0009331","20200114PWA_05 ","CFA reported pole fire & ground fire at incident location. Upon arrival fault crew found that HV cable head had failed at termination ejecting molten material to ground and commencing a small ground fire of 3m x 8m in size, on the road verge extending slightly into an adjacent property. There was no reported injuries."]
[17,168,"2020-01-13","13:38:00",-37.880321000000002,144.78568799999999,"167 VICTORIA STREET, ALTONA MEADOWS VIC 3028",30118483,"LVN022","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0010033","20200228PWA_03 ","Asset inspector found HV crossarm straps burnt off at HV crossarm, resting on LV crossarm straps. There was no ground fire, no reported injuries or third party property damage."]
[17,169,"2020-01-14","13:00:00",-35.883845000000001,145.49469400000001,"468 Mywee Rd, Strathmerton 3641",30256137,"NKA003","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009341","20200115PWA_02 ","A customer called to say that wires were down and a fire had started, and he had called the CFA. On arrival the crew found that a tall gum tree located approx. 15m from the line had fallen over the HV conductors, causing one of the conductors to break and fall to the ground. This resulted in a grassfire of approx. 30m x 40m in size. There were no reported injuries."]
[17,170,"2020-01-14","11:30:00",-36.400998000000001,145.39940899999999,"7 Chuck Rd, Sheparton",33095419,"STN022","22kV AC","Urban"," - fuse (powder filled)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009345","20200115PWA_05 ","A Customer who wished to remain anonymous reported that a bird caused an \"explosion\" on the pole opposite 7 Chuck St and fell to the ground causing a small grassfire.  On arrival the crew found that a bird had caused a flashover on the HV fuses of the Substation at the incident location, and had fallen to the ground igniting a grassfire on the nature strip of approx. 2m x 4m. There were no reported injuries or third party damage."]
[{"$f":"COUNTA(C208:O208,Q208,T208:V208)","v":17},171,"2020-01-15","18:24:00",-37.874369000000002,143.765717,"Geggies Rd, Corindhap Vic. 3352",30005750,"BAS022","12.7kV AC (SWER)","Rural Long"," - surge diverter","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0009353","20200117PWA_03 ","A Powercor crew was called to an All Supply Failure report at the Dereel Sth SWER Isolating Substation. When the crew arrived onsite they discovered that a lightning strike had damage a surge diverter mounted on the pole and part of the damaged surge diverter had fallen to the ground causing a small grass fire. The fire burnt approx. 10 sq m of dry grass."]
[{"$f":"COUNTA(C209:O209,Q209,T209:V209)","v":17},172,"2020-01-15","19:07:00",-35.742140999999997,143.96174099999999,"491 Kerang-Koondrook Road, Kerang VIC 3579",32029954,"KGT003","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0009355","20200117PWA_04","CFA reported pole fire and ground fire at the incident location. Upon arrival crew found that strain/angle pole \"P50 Koondrook\" had burnt through between pole top assembly and centre phase strain insulator hardware. Conductors remained suspended aloft, burning material however fell to ground and ignited a grass fire along the road verge, approximately 20M x 100M in size. There was no reported injuries."]
[17,173,"2020-01-15","17:00:00",-37.330821999999998,144.51924700000001,"52 Bowyers Road, Woodend North, VIC 3442",33024345,"WND014","22kV AC","Rural Short"," - pole (concrete)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0009356","20200117PWA_05 ","CFA reported grass fire that commenced at base of pole. Upon arrival crew found evidence of lightning striking CHP \"kyneton 1\", a ground fire commenced from the base of the concrete pole and burnt 200M x 100M of grass, no 3rd party damage."]
[17,174,"2020-01-15","10:09:00",-37.333539999999999,144.13728399999999,"22 West Street Daylesford 3460",33004683,"BAN008","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0009992","20200224PWA_06 ","Customer reported a pole outside their property is making arching sounds and he can see smoke and small sparks near conductor(white/blue) on the mains wire. On arrival crew found a hung up EDO fuse, no ground fire or any other damage. There was no ground fire, no reported injuries or third party property damage."]
[17,175,"2020-01-15","18:11:00",-37.748066999999999,144.77210500000001,"48 PRESIDENT ROAD,ALBANVALE,VIC,3021",32163922,"SSE031","Low voltage AC (<1kV)","Urban"," - pole (wood)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"High",0.5,0.1,"INC-0010036","20200228PWA_05 ","Report received from vic fire of pole fire. There was no ground fire, no reported injuries or third party property damage. Possible lightning strike."]
[17,176,"2020-01-15","14:51:00",-35.103566000000001,143.34577300000001,"3571 Murray Valley Hwy Wood Wood 3596",32157058,"SHL002","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0010049","20200302PWA_05 ","Vic Roads reported tree branch falling on main power lines at incident location, heard a loud bang before noticing branch on wire and arcing causing a small fire which has been extinguished, no ground fire, no injuries, no property damage."]
[17,177,"2020-01-16","20:32:00",-38.293463000000003,142.849086,"772 Princes Hwy, Garvoc",33098550,"TRG004","22kV AC","Rural Short"," - guy wire","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0009359","20200120PWA_01","A crew patrolling following an outage found that at P1277 TRG-WBL Line (LIS-408458) the 66kV stay had parted at the helical termination. The stay contacted a HV conductor and the ground. A small grass fire of approx. 22m x 13m = 286m2 in size was found on the road reserve nearby. There was an  area of 1/2 m2  fire private property burnt, and no reported injuries."]
[17,178,"2020-01-18","15:00:00",-37.53049,143.83439999999999,"24 Elizabeth Street, Wendouree",75244598,"BAN004","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009366","20200120PWA_06 ","Vic Fire reported a wire down which had caused a grass fire at the incident location. On arrival crew found that a service line had ruptured at the house end roller clamp falling to ground and starting a small grass fire."]
[17,179,"2020-01-18","14:29:00",-37.564419999999998,143.76397700000001,"413 Ballarat -Carngham Road, Bunkers Hill",33007578,"BAS011","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0009370","20200121PWA_02","Vic Fire reported a grass fire at the incident location, evidently started by Powercor assets. On arrival crew found that a porcelain fuse box had overheated igniting grass below. There was no reported injuries or third party property damage."]
[17,180,"2020-01-19","19:19:00",-37.67324,144.418361,"5 Chicquita Crt Bacchus Marsh 3340","PA0054540","BMH004","22kV AC","Rural Short"," - transformer (kiosk mounted)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0009374","20200121PWA_03 ","While patrolling area following thunderstorms field crew were alerted by fore brigade of smoke emanating from kisok substation at incident location. On arrival crew of the substation it was established there was damaged HV cable and a possible damaged kiosk. There was no ground fire, no reported injuries or third party property damage."]
[17,181,"2020-01-19","17:26:00",-35.369889999999998,143.547526,"99 Back Boga Road Swan Hill 3585",32161148,"SHL005","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0009380","20200122PWA_01 ","Vic fire reported  wires down at incident location, caused grass fire. On arrival crew found a FMB had overheated debris ignited grass below. There was no reported injuries or third party property damage."]
[17,182,"2020-01-20","00:37:00",-36.705216,142.20501100000001,"57 Lynott Street, Horsham",32092095,"HSM009","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009386","20200122PWA_02 ","Vic Fire reported a pole fire at the incident location. On arrival the fault crew found that a HV crossarm had burned through, and dropped the end of the crossarm onto the LV circuit below. There was no HVI found at customers premises, although a number of smart meters were changed due to damage. There was no reported injuries or third party property damage."]
[17,183,"2020-01-20","00:00:00",-38.385917999999997,142.49158700000001,"74 Barkly St, Warrnambool 3280",30544142,"WBL008","22kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0009389","20200122PWA_03 ","A customer reported to the fire brigade that a pole fire had occurred at the incident location. On arrival the crew found that following misty rain, the pole had burnt through at the eye bolt for the centre phase HV discs. There was no ground fire, and there were no injuries or third party damage reported."]
[{"$f":"COUNTA(C221:O221,Q221,T221:V221)","v":17},184,"2020-01-20","10:00:00",-37.676845999999998,142.190673,"1 Worburtons Rd Mountajup 3294",33059281,"HTN005","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0009392","20200122PWA_04 ","Emergency services reported a pole fire at the incident location. A Powercor crew found that the LV fuse box on the pole ignited due to overheated connections. There were no injuries or ground fire."]
[{"$f":"COUNTA(C222:O222,Q222,T222:V222)","v":17},185,"2020-01-20","16:19:00",-34.623918000000003,142.76536100000001,"37 Happy Valley Road Robinvale Irrigation District Section D 3549",32143806,"RVL001","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009394","20200122PWA_05 ","Following a call from customers  Crew found a burnt cross-arm at incident location. There was a small ground fire  caused by fallen debris."]
[17,186,"2020-01-20","14:15:00",-36.287042999999997,141.30278100000001,"1256 Broughton Road, Kaniva",32100850,"NHL031","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0009396","20200122PWA_06 ","A customer reported a pole fire at the incident locaton. On arrival the fault crew found that a HV crossarm had burned through at the kingbolt, and had dropped down with the HV conductors remaining  attached to the crossarm. There was no ground fire, no reported injuries or third party property damage."]
[17,187,"2020-01-22","21:38:00",-36.091593000000003,145.44660999999999,"13 Gray Street Numurkah 3636 ",33078990,"NKA004","Low voltage AC (<1kV)","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0009463","20200129PWA_01","CFA reported wire stared grass fire at incident location, fire now out. On arrival crew found a small branch had contacted LV conductors. Burnt particles fell to ground starting a small grass fire. There was no injuries reported or third party property damage."]
[17,188,"2020-01-22","17:13:00",-35.624518000000002,144.091354,"365 Koondrook-Murrabit Road Koondrook 3580",33021888,"KGT003","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Extreme",3.5,0.70000000000000007,"INC-0009478","20200206PWA_02 ","Customer reported wire down, started small grass fire at incident location. There was no conductor damage. CFA on site. There was a small ground fire, no reported injuries or third party property damage."]
[17,189,"2020-01-22","10:53:00",-36.720443000000003,144.68812800000001,"44 Cornella-Toolleen Rd, Toolleen VIC 3551",30336794,"SHP021","22kV AC","Rural Long"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Severe",2,9.1999999999999993,"INC-0011150","20200710PWA_01","Edo candelling on swer iso. OMS incorrect was a boric acid fuse. Incident found during OMS data review. No ground fire."]
[17,190,"2020-01-23","02:38:00",-35.955289,144.35669300000001,"4475 Murray Valley Highway Gunbower 3566",30029617,"CHA005","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0009421","20200123PWA_01 ","VIC FIRE reported pole fire at incident location. Crew found Pole fire was put out by fire brigade at Leitchville P121, LIS 704306, burnt around centre phase tee off insulator eye bolt, pole OK, no ground fire. No reported injuries."]
[17,191,"2020-01-23","13:50:00",-34.517443999999998,142.37574599999999,"3188 Kulkyne Way, Colignan VIC 3494, Australia",31020287,"RCT013","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0009483","20200207PWA_09","HV 22Kv Wooden Crossarm burnt off HV Angle top circuit of HV Angle and Tee Off - small ground fire. There was no reported injuries or third party property damage."]
[17,192,"2020-01-23","12:38:00",-37.086159000000002,141.143518,"1279 Edenhope-Penola Road Langkoop 3318 ",30084121,"CHM011","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0009495","20200207PWA_10","Customer reported pole burning at the top of pole, dry grass at the base, was on fire, customer has put that out, he is calling fire brigade. On arrival crew found pole fire had occurred and debris had ignited grass. There was a 40 15 sq mtr fire, no reported injuries."]
[17,193,"2020-01-24","16:01:00",-38.754126999999997,143.667405,"27 Pascoe St, Apollo Bay VIC 3233",30051538,"CLC013","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0010039","20200228PWA_06 ","Crossarm fire reported by inspector. On arrival crew found bottom crossarm burnt off. There was no ground fire, no re[ported injuries or third party property damage."]
[17,194,"2020-01-25","15:53:00",-38.571359999999999,142.90297699999999,"Dairy -Dunbars Rd, Heytesbury Lower 3268 (approx 1km sth of Curdievale -Port Campbell Rd)",32056642,"TRG005","Low voltage AC (<1kV)","Rural Long"," - connector / termination","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0009501","20200207PWA_11 ","Fire emergency services reported a pole & ground fire at incident address. On arrival crew found a 20 x 30 mtr grass fire. On examination of substation it was determined that fire was caused by a \"hot\" joint on the substation 'b' phase.\nThere was no reported injuries."]
[17,195,"2020-01-29","12:30:00",-37.386285999999998,141.56390099999999,"1787 Nareen Road, Nareen, 3315. On property between between poles LIS 716498 & 716499. (Kilmuir 2 & Kilmuir 3)",32126181,"HTN006","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0009506","20200207PWA_08","Report received of a grassfire at the incident location. Crew were told that a tip truck with its carrier raised had contacted the overhead line which caused arcing and debris from this incident started the grass fire (10 by 10meters burnt). The truck and its owner had left the site and no details were forthcoming.\nCFA attended site. There was no reported injuries."]
[17,196,"2020-01-29","15:45:00",-38.171272000000002,144.14168000000001,"1781 Barrabool Rd, Gnarwarre 3221",33041740,"WPD011","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0009511","20200207PWA_07 ","Powercor received customer reports of no supply. Additional reports were also received of a fire at the incident location. When crews arrived they found a vehicle accident with a HV pole had occurred resulting in pole failure and coming to ground together with HV conductors.  The vehicle had come to rest on its roof and was engulfed in flames together with a 400m section of vegetation along the road side reserve. The fire area followed in the vicinity of the fallen HV conductors. Emergency services confirmed the driver had been killed in the accident"]
[{"$f":"COUNTA(C234:O234,Q234,T234:V234)","v":17},197,"2020-01-30","18:37:00",-37.764403000000001,144.768034,"10 Wandsworth Ave, Deer Park VIC 3023",30118460,"SU021","Low voltage AC (<1kV)","Urban"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O234=\"\",\"\",IF(O234=\"LBRA only\",0.2,IF(O234=\"HBRA only\",1,IF(O234=\"within electric line construction area\",19.8,IF(O234=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"Very high",{"$f":"IF(Q234=\"\",\"\",IF(Q234=\"No forecast\",0.1,IF(Q234=\"Low-moderate\",0.2,IF(Q234=\"High\",0.5,IF(Q234=\"Very high\",1,IF(Q234=\"Severe\",2,IF(Q234=\"Extreme\",3.5,5)))))))","v":1},{"$f":"IF(OR(P234=\"\",R234=\"\"),\"\",IF(AND(O234=\"within electric line construction area\",Q234=\"No forecast\"),1,P234*R234))","v":0.2},"INC-0009523","20200207PWA_06 ","Customer reported wire down and grass fire at incident location. MFB attended to control 0.5m x 0.5m grass fire. Attending crew found the fire was caused by a burnt out IPC on East bus fuse white phase hitting the ground after LV main cable broke at connection. No injuries or property damage."]
[{"$f":"COUNTA(C235:O235,Q235,T235:V235)","v":17},198,"2020-01-31","14:47:00",-36.794885000000001,144.34086300000001,"1 Woodlea Close Strathfieldsaye 3551 ",32051730,"BGO013","22kV AC","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",{"$f":"IF(O235=\"\",\"\",IF(O235=\"LBRA only\",0.2,IF(O235=\"HBRA only\",1,IF(O235=\"within electric line construction area\",19.8,IF(O235=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"Severe",{"$f":"IF(Q235=\"\",\"\",IF(Q235=\"No forecast\",0.1,IF(Q235=\"Low-moderate\",0.2,IF(Q235=\"High\",0.5,IF(Q235=\"Very high\",1,IF(Q235=\"Severe\",2,IF(Q235=\"Extreme\",3.5,5)))))))","v":2},{"$f":"IF(OR(P235=\"\",R235=\"\"),\"\",IF(AND(O235=\"within electric line construction area\",Q235=\"No forecast\"),1,P235*R235))","v":0.4},"INC-0009544","20200206PWA_01 ","Customer reported a large tree snapped in half now laying on conductors, wire sagging concerned wire could snap with weight. Crew found small ground fire roughly 1m2, where conductor had  arced along the fence before the feeder dropped out. There was a small ground fire, no reported injuries or third party property damage."]
[17,199,"2020-01-31","22:52:00",-35.316924,141.21514999999999,"1037 GUNAMALARY RD -MURRAYVILLE VIC 3512",32152937,"OYN001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Severe",2,2,"INC-0009549","20200205PWA_06 ","Vicfire advised they had just extinguished a small pole fire at the incident location. On arrival crew found there had been a crossarm fire. There was no ground fire, no reported injuries or third party property damage."]
[17,200,"2020-01-31","16:11:00",-37.655203999999998,143.67128700000001,"39 Bandys Road, Smythesdale 3351 ",33002842,"BAS021","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Severe",2,9.1999999999999993,"INC-0009587","20200205PWA_01 ","Vic fire reported a grass fire (8ha) at incident location. On arrival crew found a overheated FOLCB with one fuse base on the ground. There was no reported injuries. Damage sustained to pasture and fencing."]
[{"$f":"COUNTA(C238:O238,Q238,T238:V238)","v":17},201,"2020-02-01","11:19:00",-36.035654000000001,142.8997,"SUNRAYSIA HWY -BIRCHIP VIC 3483",32016825,"CTN001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O238=\"\",\"\",IF(O238=\"LBRA only\",0.2,IF(O238=\"HBRA only\",1,IF(O238=\"within electric line construction area\",19.8,IF(O238=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"Very high",{"$f":"IF(Q238=\"\",\"\",IF(Q238=\"No forecast\",0.1,IF(Q238=\"Low-moderate\",0.2,IF(Q238=\"High\",0.5,IF(Q238=\"Very high\",1,IF(Q238=\"Severe\",2,IF(Q238=\"Extreme\",3.5,5)))))))","v":1},{"$f":"IF(OR(P238=\"\",R238=\"\"),\"\",IF(AND(O238=\"within electric line construction area\",Q238=\"No forecast\"),1,P238*R238))","v":4.5999999999999996},"INC-0009546","20200205PWA_04 ","Vicfire attended to extinguish pole fire at the incident location. On arrival crew found crossarm burnt in half at king bolt position.  The railway side conductor was approx. 1m from the ground but was over rail reserve and as such not a threat to the general public. There was no ground fire, no reported injuries or third party property damage."]
[{"$f":"COUNTA(C239:O239,Q239,T239:V239)","v":17},202,"2020-02-01","08:15:00",-36.642009999999999,142.700579,"Wimmera Hwy, Rupanyup 3388",32107806,"STL006","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O239=\"\",\"\",IF(O239=\"LBRA only\",0.2,IF(O239=\"HBRA only\",1,IF(O239=\"within electric line construction area\",19.8,IF(O239=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"Low-moderate",{"$f":"IF(Q239=\"\",\"\",IF(Q239=\"No forecast\",0.1,IF(Q239=\"Low-moderate\",0.2,IF(Q239=\"High\",0.5,IF(Q239=\"Very high\",1,IF(Q239=\"Severe\",2,IF(Q239=\"Extreme\",3.5,5)))))))","v":0.2},{"$f":"IF(OR(P239=\"\",R239=\"\"),\"\",IF(AND(O239=\"within electric line construction area\",Q239=\"No forecast\"),1,P239*R239))","v":0.91999999999999993},"INC-0009585","20200204PWA_03","Vic fire reported a pole fire at the above location on a SWER intermediate pole. There was a small patch of stubble burnt, no reported injuries or third party property damage."]
[17,203,"2020-02-01","02:25:00",-37.283467999999999,142.91865200000001,"3 Spalding st Ararat 3377",32113387,"ART034","22kV AC","Rural Short"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0009586","20200204PWA_04 ","Report revived of smoke and sparks coming from top of pole at incident location. There was no ground fire, no reported injuries but report of third party damage due to HVI."]
[17,204,"2020-02-04","21:37:00",-35.207873999999997,143.40210999999999,"2267 MURRAY VALLEY HIGHWAY,VINIFERA,VIC,3591",33069333,"SHL002","22kV AC","Rural Long"," - capacity balancing units","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009687","20200210PWA_02 ","Customer reported fire on top of pole and sparking wires at incident location. Upon arrival crew found that the fire had been extinguished by the CFA. There appears to have been a HV capacitor fault, no damage to pole. There was no ground fire, no reported injuries or third party property damage."]
[17,205,"2020-02-06","10:20:00",-36.254154,144.98140000000001,"2094 Curr Rd, Tongala",33089386,"KYM004","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (other)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009690","20200210PWA_03 ","Customer rang to reported ground fire start at the incident address. A crew attended and found a customers tree had rubbed through the 2W grey service cable from pole to house. This resulted in the service breaking and falling to the ground starting a grass fire. Area burnt estimated at 160m2 ( 4mx40m ). There was no reported injuries."]
[17,206,"2020-02-06","18:25:00",-36.621665999999998,145.30956900000001,"1567 Longwood-Shepparton Rd Moorilim 3610",33088592,"MNA034","12.7kV AC (SWER)","Rural Long"," - insulator tie wires / connections","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0009694","20200210PWA_04 ","Following a call from customer, crew attended low wire at above address at Murchison pole 156. On arrival crew found a low conductor and burnt area underneath pole (4/10 sq mtr). There was no injuries, no third party property damage."]
[17,207,"2020-02-06","15:02:00",-37.755721000000001,144.738665," Western Hwy (8A Sherdley Green, Caroline Springs VIC 3023, Australia )",30110149,"SU035","22kV AC","Urban"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0009695","20200210PWA_05 ","Vic fire reported fire start at above incident location. On arrival crew found a following a transformer fault one HV BA fuse had ruptured, debris has started a small grass fire. There was a small oil leak. There was no reported injuries or third party property damage."]
[17,208,"2020-02-06","13:20:00",-36.371232999999997,145.49836999999999,"400 BOUNDARY ROAD, PINE LODGE VIC 3631",32192679,"STN024","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0010587","20200518PWA_10 ","Following report of supply failure crew found a burnt out EDO fuse unit."]
[17,209,"2020-02-07","18:54:00",-36.039901999999998,141.57612,"Hiscocks Track Netherby 3418",32099082,"NHL016","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0009709","20200211PWA_01 ","Report relieved of a pole fire at the incident location.  On arrival crew found pole top burnt , CFA attended and extinguished the fire. There was no ground fire, no reported injuries or third party property damage."]
[17,210,"2020-02-09","12:42:00",-38.152786999999996,144.16353100000001,"13 Nobles road Gnarwarre",33104059,"WPD011","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0009686","20200210PWA_01","Pine tree fell into during strong easterly wind, igniting trees and causing a small grass fire of approximately 10 by 6 metres. Some damage to 2 sections of farm fencing. No injuries"]
[17,211,"2020-02-09","07:34:00",-34.275928999999998,142.177571,"175 Belar Ave Ext, Red Cliffs VIC 3496",30098049,"RCT021","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009715","20200211PWA_02 ","Report received of pole fire at incident location. On arrival crew found crossarm burnt off and conductor down. There was no ground fire, no reported injuries or third party property damage."]
[17,212,"2020-02-09","07:34:00",-34.275824,142.17593099999999,"183 Belar Ave Ext, Red Cliffs VIC 3496",32148522,"RCT021","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009718","20200211PWA_05 ","Crew investigated area fault, on arrival found 2 poles consecutive poles that had cross arms burnt.  HV wire down. CFA in attendance. There was no ground fire, no reported injuries or third party property damage."]
[17,213,"2020-02-09","09:13:00",-34.233412000000001,142.15088299999999,"933 Sandilong Ave, Irymple VIC 3498",30095918,"MDA023","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009719","20200211PWA_08 ","Customer reported wire down at property. ON arrival crew found that a crossarm had burnt through. There was no ground fire, no reported injuries or third party property damage."]
[17,214,"2020-02-09","07:02:00",-34.242840999999999,142.20151000000001,"207 Belar Ave, Irymple VIC 3498",32141632,"RCT011","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009720","20200211PWA_11 ","Vic Fire reported pole fire at above location. When crew arrived they were able to isolate before HV cross arm collapsed. HV cross arm burnt through at king bolt. No injuries or third party damage.  No ground fire."]
[17,215,"2020-02-09","06:15:00",-34.224133999999999,142.174882,"798 Karadoc Ave, Irymple VIC 3498",32148297,"MDA023","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009722","20200211PWA_14 ","Vic Fire reported wires sparking at corner of Karadoc and Fourteenth St.  When crew arrived, they found a HV/LV wooden pole had burnt through at the LV king bolt, and the top of the pole had broken off and wires were low. Suspected HVI, inspector called to investigate. No ground fire, no third party damage or injuries."]
[17,216,"2020-02-10","08:14:00",-37.897486000000001,144.64825099999999,"26 Edgar St Werribee 3030",32167520,"WBE033","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0009725","20200211PWA_16","A passer-by reported a HV wire on LV wires at the incident location. Upon arrival a Powercor fault crew found that a cross arm bunt through and fallen HV conductor caused HVI. There was no ground fire and no reported injuries."]
[17,217,"2020-02-11","15:37:00",-37.647258000000001,141.02328900000001,"1491 Old Lindsay Road Strathdownie",32131144,"HTN002","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0009730","20200212PWA_01","Fire brigade advised of a pole fire possibly caused by a ground fire. The attending crew identified that a pole fire had occurred and spread into grassland. An area estimated to be several acres (1.5 Ha) of private pasture was burnt. No damage to fencing of nearby pine plantation. No injuries reported"]
[17,218,"2020-02-11","13:00:00",-38.152608000000001,143.237087,"1260 Camperdown-Lismore Rd, Camperdown (Kariah)",32059880,"CDN004","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0009755","20200212PWA_06 ","A customer called to report a pole fire and a wire down at the incident location. On arrival the crew found a HV wooden termination cross arm on the substation pole had burnt off. There was a small 5 sq m grass fire. There was no reported injuries or third party property damage."]
[17,219,"2020-02-11","21:34:00",-38.280985999999999,141.614754,"249 PRINCES HIGHWAY, BOLWARRA VIC 3305",32135413,"PLD001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0010588","20200520PWA_02 ","Customer reports fuse hanging off pole. On arrival crew found a cross-arm had burnt at the EDO mounting position"]
[17,220,"2020-02-12","23:01:00",-37.933064999999999,144.691316,"170 Diggers Road, Werribee South",30109960,"WBE034","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0009818","20200214PWA_02 ","MFB called to report a pole fire at LIS-203084. On arrival crew found that tracking had caused the dressing down crossarm to burn in half. There was no ground fire, no reported injuries or third party property damage."]
[17,221,"2020-02-13","20:31:00",-37.856225999999999,144.816667,"19 Deavey Ct, Altona VIC 3018, Australia",33073532,"AL006","11kV AC","Urban"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009848","20200217PWA_01 ","MFB reported Sparking wires at end of Jordan Close, Altona. Fire is out in a paddock. On arrival the crew found that metallic balloons had caused a flashover at the incident location. There was a 5 sq metre fire in the paddock. MFB attended. There was no reported injuries or third party property damage."]
[17,222,"2020-02-14","13:20:00",-37.822448999999999,144.83264700000001,"25 Paw Paw Road, Brooklyn, 3012.",30103015,"BLT016","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0009851","20200217PWA_02 ","Report received from customer of part supply.  There appears to be a fault with the box on pole and small grass fire started below. On arrival crew found that a FOLCB had burnt out and hot debris had fallen into grass below starting a small fire (0.2x0.2 sqm). There was no injuries or third party property damage."]
[17,223,"2020-02-14","16:18:00",-37.527934000000002,142.71705700000001,"218 Yarram Gap Rd, Willaura 3379",32098473,"ART033","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0009854","20200217PWA_03 ","A crew was responding to an area fault following a lightning storm.  A member of the public stopped the crew and reported a burning fuse tube at the above location. On arrival the crew found that the transformer had been struck by lightning and the EDO fuse tube had hung up and was candling. There was no ground fire or third party damage."]
[17,224,"2020-02-17","16:52:00",-37.635626000000002,142.51184000000001,"WINTOC, 5269 GLENELG HIGHWAY, GLENTHOMPSON",33055592,"HTN005","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0009971","20200220PWA_01 ","An  EDO HV Fuse hung up and a ground fire was found at the base of the pole type substation."]
[17,225,"2020-02-19","14:23:00",-37.847127,144.80981,"69 Horsburgh Dr, Altona North VIC 3018. ",30271646,"BLTS-AL","66kV AC","Rural Long"," - crossarm (steel)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009973","20200220PWA_02","Grass fire was reported near base of pole, attending crew  found center phase 66kV insulator has broken off its mount. The  conductor  was  resting on the 66kV steel cross-arm and evidence of current passing through the wooden pole  to earthed 11kV  bracket was found."]
[17,226,"2020-02-21","09:48:00",-38.266671000000002,144.66038699999999,"14 Hobson Street Queenscliff 3225",30288947,"DDL012","22kV AC","Rural Short"," - underground cable","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0010003","20200225PWA_05 ","MFB reported sparking wire. Crew found HV centre phase cable head termination failed at LA bracket, made safe, minimal fire damage on ground. No reported injuries or third party property damage."]
[17,227,"2020-02-21","10:35:00",-35.108161000000003,142.487225,"1255 COCAMBA ROAD, OUYEN VIC 3490",32147058,"OYN005","12.7kV AC (SWER)","Rural Long"," - fuse (EDO fuse)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0010589","20200520PWA_03 ","Customer reported fuse down. One arrival crew found EDO tube had  burnt in half."]
[17,228,"2020-02-23","23:55:00",-37.538905,143.88040899999999,"3 Norman St, Ballarat Nth",33006984,"BAN015","22kV AC","Rural Short"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0009997","20200225PWA_01 ","VICFIRE reported a ground fire start at the at the incident location.  A crew attended and found a possum had flashed over at Norman Mathoura P19.  The possum fell to the ground and started a grass fire on the road side of approx. 250m2 ( 25mx10m ). CFA was in attendance and extinguished fire. There was no injuries or third party property damage."]
[17,229,"2020-02-24","05:44:00",-35.806131000000001,144.20827,"44 Western Road, Cohuna VIC 3568",33022821,"CHA006","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0009999","20200225PWA_03 ","CFA reported pole fire at the incident location. Upon arrival fault crew found that a FOLCB had faulted and burnt the box. No ground fire or damage to concrete pole, CFA attended."]
[17,230,"2020-02-25","00:27:00",-37.769545000000001,144.60933499999999,"1753-1769 MOUNT COTTRELL ROAD, MOUNT COTTRELL VIC 3024",30106376,"MLN011","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0010591","20200520PWA_04 ","Crew responding to a report of power outage found an EDO fuse had burnt in half."]
[17,231,"2020-02-26","05:47:00",-38.136232,141.61884800000001,"Outside 58 Barclay St, Heywood",32125133,"PLD001","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0010041","20200302PWA_01 ","Customer reported seeing flames coming from top of pole and sparks falling to the ground into paddock. On arrival, the crew identified the centre phase bridging insulator has burnt through the pole. No ground fire was evident (wet ground), no damage to property, no shocks or injuries reported."]
[17,232,"2020-03-01","09:52:00",-38.136634999999998,141.67670000000001,"40  Prices lane. Homerton",30556949,"PLD001","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0010042","20200302PWA_02 ","Customers reported Low volts, motors not running properly, lights are dimming, attending crew found HV earth (ISO) damaged and pole base burnt. pole required replacement"]
[17,233,"2020-03-02","11:00:00",-36.728696999999997,142.198791,"34 McTavish Boulevard, Horsham, 3400.",30228434,"HSM009","Low voltage AC (<1kV)","Urban"," - LV pillar","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0010057","20200303PWA_01 ","MR BRIAN HARMER, REC Steve 0407 340 836 adv concrete truck has nudged pillar on nature strip in  front of property.  The Pillar was smoking and making noise. On arrival crew found that pillar had been dislodged causing shorting and overheating which scorched the ground underneath. There was no injuries or third party property damage."]
[17,234,"2020-03-03","14:30:00",-37.841541999999997,144.277458,"42-100 MCLEANS HIGHWAY, STAUGHTON VALE VIC 3340",30252610,"CRO013","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0010080","20200304PWA_01 ","Powercor received advice of wire broken and limited power. Attending crew found that tree had failed at ground level and brought down one HV conductor. Small ground fire had self extinguished. Residents had not been in attendance recently  so it unknown when fire occurred."]
[17,235,"2020-03-04","05:35:00",-34.310366000000002,142.18994499999999,"47 Heath Street Red Cliffs 3496",31019780,"RCT022","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0010093","20200305PWA_03 ","Customer advised pole outside is on fire. CFA attended and extinguished fire. On arrival crew found pole had been on fire near the king bolt position. There was no ground fire, no reported injuries or third party property damage."]
[17,236,"2020-03-04","08:50:00",-34.304454,142.185002,"91 Kauri St, Red Cliffs 3496",31020020,"RCT023","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0010094","20200305PWA_04 ","A customer reported a cross-arm fire at the incident location. On arrival the crew found that the HV cross-arm on Kauri Coorong P4 (LIS-4796) had burnt in half at the kingbolt, causing the two halves to fall onto the LV cross-arm below.\nThere were no reported ground fires, HVI or injuries."]
[17,237,"2020-03-04","13:33:00",-36.128179000000003,144.76201900000001,"133 GOULBURN ROAD, ECHUCA VIC 3564",30123584,"ECA003","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0010561","20200520PWA_06 ","Powercor crew responding to a report of a pole fire found  cross-arm had burnt"]
[17,238,"2020-03-04","15:11:00",-34.353028000000002,142.28350599999999,"228 JOHNS WAY, RED CLIFFS VIC 3496",32152209,"RCT014","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0010567","20200520PWA_05 ","Report of pole fire at incident location."]
[17,239,"2020-03-05","15:57:00",-36.490034999999999,144.970428,"Baker Cres, Stanhope, Vic 3623",30222928,"SHP021","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0010571","20200520PWA_07","Report of pole fire at incident location,  attending crew found pole burnt  above transformer."]
[17,240,"2020-03-08","13:33:00",-37.967869,144.30083099999999,"Poultry Farm, 415 Carrs Rd, Anakie 3213",30312074,"CRO013","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0010118","20200310PWA_02 ","Powercor received a call from Vic Fire advising of wires down and a fire start at the incident address. When crews arrived they found an excavator being driven on the property had contacted the HV overhead conductor resulting in conductor damage to all three phases and a 20m x 30m grass / paddock fire. No shock or injuries were experienced by the excavator operator who is also the property owner."]
[17,241,"2020-03-09","19:07:00",-37.685589,144.58626899999999,"Smith Street cnr Henry Street, Melton, 3337 (2-4 SMITH STREET, MELTON VIC 3337)",30322147,"MLN023","22kV AC","Rural Short"," - dropper / bridge","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0010123","20200310PWA_04 ","MFB reported sparking pole near 68 reserve road melton. On arrival crew advised that a dead-crow at the base of HVCHP P3 LIS-828102 appears to have caused a large -flashover across all 3 phases, resulting in damage to all 3 phases of the HVCHP terminations / HV UG cable. There was no reported grass-fire, HVI, injury or shocks as a result of this incident."]
[17,242,"2020-03-10","13:06:00",-37.947752999999999,141.368619,"Cnr of Johnsons Rd and Balds Rd Winnap 3304",30095338,"PLD003","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0010125","20200311PWA_01 ","A tree harvester cut down a tree branch on to SWER line. On arrival, a Powercor fault crew found that the tree branch on the conductors and small ground fire about 10 Sqm.  The crew made the place safe."]
[17,243,"2020-03-12","10:00:00",-37.143979000000002,144.18863099999999,"221 Kemps Bridge Rd, Guildford 3451",30038431,"CMN001","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0010146","20200313PWA_03 ","A farmer reported a tree took down mains wires at the incident location. On arrival the crew found that the farmer was cutting a tree approx. 15m from the HV Line, when it fell onto the 22kV 3 phase HV conductors. HV conductor broke and fell to the ground causing a small grassfire approx. 10m2 in size. There was no reported injuries or third party property damage."]
[17,244,"2020-03-13","20:02:00",-37.192869000000002,143.37272200000001,"1602 Pyrenees Hwy, Amphitheatre VIC 3468",32022861,"MRO008","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0010150","20200316PWA_01 ","Vic fire reported wires down and grass fire at incident location. On arrival found a large tree branch had fallen across HV conductors. Conductors still in the air and a ground fire started undermeath line. There was no injuries or third party property damage."]
[17,245,"2020-03-13","20:23:00",-37.551780999999998,143.86858000000001,"501 Sherrard St cnr Napier St Black Hill 3350",32012126,"BAN007","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0010153","20200316PWA_03 ","A crossarm  fire resulted in the high voltage conductor falling with the insulator coming to rest on the low voltage x arm. There was reported to be a HVI. There was no ground fire, no reported injuries."]
[17,246,"2020-03-14","13:18:00",-38.316899999999997,142.74682999999999,"8559 Princes Hwy, Panmure 3265",32058973,"TRG004","Low voltage AC (<1kV)","Rural Short"," - fuse (any other type)","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0010154","20200316PWA_04 ","A customer called to advise that what he described as a \"capacitor\" had caught fire on his meter board. On arrival the crew found that one of the meter board fuses had overheated causing minor damage to the wooden meter board. There was no ground fire, no reported injuries or third party property damage."]
[17,247,"2020-03-15","02:53:00",-38.465871999999997,144.06517299999999,"20 Old Neuk Rd Moggs Creek",32070006,"WPD014","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0010575","20200520PWA_08 ","Crew attending to an outage found   fuse carrier had burnt."]
[17,248,"2020-03-15","19:31:00",-36.343159,145.13234199999999,"1636 LILFORD ROAD, LANCASTER VIC 3620",32189439,"KYM003","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0010576","20200520PWA_09 ","Crew attending a report of part supply found arcing EDO fuse."]
[17,249,"2020-03-16","13:31:00",-38.009425,142.813616,"1513 Mortlake-Ararat Rd, Mortlake 3272",32061459,"TRG002","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0010161","20200317PWA_02 ","At 13:31 the Woorndoo P84 ACR went to lockout. While patrolling, the fault crew found that the HV conductors wrapped together between poles 140-140E Woorndo line. Line appears to have been struck by an unknown vehicle. The fault current at the ACR  caused molten metal to be ejected from the ACR connections igniting grass belo, resulting in 20x100m of roadside reserve being burnt. The fire site was approximately 7.5 km's from the conductor contact site. there were no reported injuries or third party property damage."]
[17,250,"2020-03-17","12:44:00",-36.323053999999999,145.06804199999999,"276 Bolitho Rd, Kyabram 3620",30130988,"SHTS-KYM1","66kV AC","Unknown"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0010169","20200318PWA_02 ","Vicfire reported a wire down and a grassfire at the incident location. On arrival the crew found that a large branch from a tree had fallen onto the 66kV OH HV conductors resulting in a ground fire of approx. 30m x 10m= 300m2 of road reserve. The HV conductors did not fall to the ground. There was no reported injuries or third party damage."]
[17,251,"2020-03-18","11:21:00",-37.156807999999998,142.52816799999999,"310 Grampians Road (corner Wattletree road) Halls Gap 3381",30333974,"STL005","Low voltage AC (<1kV)","Rural Long"," - overhead conductor (ABC)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0010176","20200319PWA_03 ","Vic Fire reported a tree has bought down wires across road and caused grass fire at incident location. Emergency services on site.  Crew found a tree damaged LV ABC between LIS: 840255 and LIS: 74877, bringing down 4 x bays of 95mm and 150mm cable, The transformer HV bushing also damaged,\nThere was a  a 8m x 6m grass fire, 2 x private vehicles damaged by falling cable. There was no reported injuries."]
[17,252,"2020-03-18","15:39:00",-37.938073000000003,144.59214800000001,"470 Wests Rd, Werribee VIC 3030",33071639,"WBE023","22kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0010199","20200320PWA_02 ","A Powercor fault crew attending a fault on WBE023 feeder found that the feeder HV overhead conductors contacted by an excavator at Werribee tip yard at the incident location. The conductor damaged and fell on to the ground. There was a small grass fire about one Sqm but no injures reported. The excavator works for the tip yard but no more details available. The crew made the place safe and all repairs have been completed. The protection operated."]
[17,253,"2020-03-19","13:55:00",-37.790818000000002,142.32396499999999,"Hamilton-Chatsworth Rd, Penshurst VIC 3289, Australia",31018721,"NRB-HTN","66kV AC","Unknown"," - pole (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0010200","20200320PWA_03 ","Call received from Vic Fire advising of a fire   Penshurst - approx 3k east Dunkeld-Penshurst rd. At this time NRB-HTN 66kv line operated to Lockout. On arrival crew advised that centre phase pole top assembly had dislodged resulting in a pole fire near the crossarm straps. Debris started a grass fire estimated to be 2000 sq m of roadside reserve. There was no reported injuries."]
[17,254,"2020-03-20","13:45:00",-37.923903000000003,141.27529899999999," 28 Ascot St, Dartmoor VIC 3304",30089487,"PLD003","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0010217","20200323PWA_02 ","Vic fire reported smoldering  pole at incident location. ON arrival crew found a crossarm has burnt through. The fire self extinguished. There was no ground fire, no reported injuries or third party property damage."]
[17,255,"2020-03-26","11:45:00",-37.826411999999998,144.85740000000001,"Opposite 65-69 Kyle Rd Altona North 3025",30569902,"BLT020","66kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0010245","20200327PWA_01 ","MFB reported powerlines down and wires were sparking. On arrival the crew found that multi circuit pole BLTS-NT Pole 6 (LIS-957045) had a pole fire mid way up the pole causing the top section to fall over but remain in the air. Two cars were reported as having damage caused by small pieces of molten aluminium and pieces of charcoal. There were no reported injuries, HVI or ground fire."]
[17,256,"2020-04-02","02:01:00",-35.928142999999999,144.36576500000001,"78 Gum Lagoon Road, Gunbower, VIC 3566",32033196,"CHA005","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0010289","20200406PWA_02 ","Following an all supply failure, a crew found a pole fire at incident location. NAO arranged for CFA to attend to extinguish fire. There was no ground fire, no reported injuries or third party property damage."]
[17,257,"2020-04-03","07:30:00",-38.123617000000003,141.637191,"14 Bell St Heywood",3026900,"PLD003","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0010288","20200406PWA_01 ","A powercor crew attending a fault located a pole fire at the incident location. The pole was half burnt through at the crossarm brace position. There was no ground fire, no reported injuries or third party property damage."]
[17,258,"2020-04-04","12:57:00",-35.186126999999999,143.316,"CHINKAPOOK-NYAH WEST ROAD, CHINKAPOOK VIC 3546",32157434,"SHL002","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0010602","20200520PWA_10 ","Crew responding to a report of a pole fire found found HV crossarm burnt."]
[17,259,"2020-04-05","18:15:00",-38.360140999999999,141.40561299999999," CA 8 Peacocks Road, Cape Bridgewater VIC 3305",30240886,"PLD006","66kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0010319","20200407PWA_01","Powercor crew attending to outage in area  became aware of a pole fire on shared pole."]
[17,260,"2020-04-09","18:58:00",-37.426628000000001,144.86268999999999,"1108 BOLINDA-DARRAWEIT ROAD, DARRAWEIT GUIM",33025397,"GSB012","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0010347","20200414PWA_01 ","Report received of pole and transformer on fire at incident location. On arrival the crew found that fire had been extinguished by CFA. There was no ground fire, no reported injuries or third party property damage."]
[17,261,"2020-04-09","08:03:00",-35.204146999999999,143.36317,"215 HOBSON ROAD,NYAH WEST,VIC,3595",33069006,"SHL002","22kV AC","Rural Long"," - transformer (pole mounted)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0010607","20200520PWA_12 ","Report received of a transformer struck by lighting. Transformer was on fire, now smoking"]
[17,262,"2020-04-09","11:05:00",-37.590631999999999,143.96546000000001,"2754 OLD MELBOURNE ROAD, DUNNSTOWN VIC 3352",30004990,"BAS023","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0010610","20200520PWA_11 ","Report received of a pole fire. On arrival crew found cross-arm burnt at EDO mounting position."]
[17,263,"2020-04-11","19:34:00",-36.343119999999999,145.17493999999999,"O/S 1230 LILFORD RD. MERRIGUM",30130456,"KYM003","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0010352","20200414PWA_02","Report received of small grass fire and wire down at the incident location. On arrival crew found that a conductor had fractured at the 22kv insulator and fallen to the ground starting a small grass fire. There was no reported injuries or third party property damage."]
[17,264,"2020-04-13","16:17:00",-37.703065000000002,144.80613199999999,"1017 Old Calder Hwy Service Rd, Keilor VIC 3036",26810509,"SA006","Low voltage AC (<1kV)","Rural Short"," - LV pillar","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0010361","20200415PWA_02 ","Customer advised that pillar at front of his property had caught fire. Crew attended onsite the fire brigade was at the incident location with the paralleling pillar taped off. A vehicle had ran the pillar over but no one had any details.  The flashover caused a small fire on the nature strip. There was no reported injuries or third party property damage."]
[17,265,"2020-04-14","14:45:00",-38.013269999999999,143.481988,"3200 Foxhow Rd, Berrybank.",30049834,"CDN004","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0010382","20200416PWA_01","A customer called to report a service wire broken mid-span and a small grass fire. On arrival the crew found that a grey service cable had ruptured mid span and fallen to the ground. The live end of the service cable ignited a small grass fire of around 40 sq metres. There was no injuries or third party property damage reported."]
[{"$f":"COUNTA(C303:O303,Q303,T303:V303)","v":17},266,"2020-04-18","17:59:00",-36.148533999999998,144.822723,"411 Brown Rd, Echuca Village VIC 3564",30125952,"ECA005","22kV AC","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",{"$f":"IF(O303=\"\",\"\",IF(O303=\"LBRA only\",0.2,IF(O303=\"HBRA only\",1,IF(O303=\"within electric line construction area\",19.8,IF(O303=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"Low-moderate",{"$f":"IF(Q303=\"\",\"\",IF(Q303=\"No forecast\",0.1,IF(Q303=\"Low-moderate\",0.2,IF(Q303=\"High\",0.5,IF(Q303=\"Very high\",1,IF(Q303=\"Severe\",2,IF(Q303=\"Extreme\",3.5,5)))))))","v":0.2},{"$f":"IF(OR(P303=\"\",R303=\"\"),\"\",IF(AND(O303=\"within electric line construction area\",Q303=\"No forecast\"),1,P303*R303))","v":4.0000000000000008E-2},"INC-0010407","20200420PWA_02 ","Call from customer advising tree down on mains wires, sparking and starting to catch fire and CFA had been called.  On arrival crew found a large branch had fallen.  The tree is located on private property on the opposite side of the road from the HV line.   HV conductor was down but no ground fire was evident.  Burn marks identified on branch. No ground fire, no injuries, no third party damage."]
[17,267,"2020-04-20","22:46:00",-38.260407999999998,144.200121,"MUNGARA, 475 HUNTS ROAD, PARAPARAP VIC 3240",33045623,"WPD014","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0010621","20200520PWA_13 ","Crew responding to an outage  found that a fuse had hung up and burnt."]
[17,268,"2020-04-23","17:57:00",-34.292704999999998,142.19873200000001,"121 Azolia Street Red Cliffs 3496",32152465,"RCT023","Low voltage AC (<1kV)","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0010443","20200424PWA_01 ","Customer reported wooden x-arm on power pole has caught fire, wires do not look damaged yet, burning into pole. OK, customer will call Emergency Services. On arrival crew found pole fire was at king bolt of LV Xarm. Made safe, no ground fire, CFA attended. No reported injuries or third party property damage."]
[17,269,"2020-04-23","18:57:00",-34.206091000000001,142.17703,"2 Eleventh Street (corner Cowra Avenue)Mildura 3500",32155128,"MDA024","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0010450","20200424PWA_02","CFA reported a pole fire at incident location. Crew found that the top position HV xarm had burnt allowing the white phase insulator to drop down on the lower HV conductors. CFA attended and put out the fire. There was no ground fire, no reported injuries or third party property damage."]
[17,270,"2020-04-29","11:00:00",-38.307220000000001,144.32980000000001,"240 Fischer Street, Torquay, 3228. (rear of property).",30346842,"WPD022","Low voltage AC (<1kV)","Rural Short"," - LV pillar","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0010468","20200430PWA_01 ","Report received of pillar fire at incident  location. On arrival crew found an lv pillar had been destroyed and small patch of burnt ground. There was no reported injuries or third party property damage."]
[17,271,"2020-04-30","21:50:00",-35.065241999999998,142.31519399999999,"9 Martin avenue, Ouyen VIC 3496",32148103,"OYN007","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0010485","20200504PWA_01 ","CFA reported a pole fire at the incident location. Upon arrival the fault crew found that a 3 phase LV FOLCB had burnt resulting in an all supply fail. There was no ground fire or 3rd party damage."]
[17,272,"2020-05-01","10:25:00",-37.345790000000001,144.44040000000001,"2 CADDYS LANE, TYLDEN VIC 3444",30342390,"WND024","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","within electric line construction area",19.8,"Low-moderate",0.2,3.9600000000000004,"INC-0010481","20200505PWA_01","Fault crew investigating an outage found substation pole burning at ground level. Crew  was  preparing to isolate supply at tee off further up the line when burnt pole fell."]
[17,273,"2020-05-12","17:25:00",-38.387895999999998,142.48379,"2 Banyan Street, Warrnambool",30135617,"WBL008","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0010595","20200513PWA_02 ","Report received of pole fire at incident location. On arrival a crew found a Krone box on fire. THere was no ground fire, no reported injuries or third party property damage."]
[17,274,"2020-05-13","14:10:00",-36.439127999999997,145.241015,"305 Dhurringile Rd, Tatura VIC 3616, Australia (6-7 Rose Court Tatura 3616)",33093071,"MNA013","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0010686","20200520PWA_01 ","MNA013 Feeder went to lockout. On arrival crew found a small branch (200mm long) had blown onto the line on the west side of pole 65 Tatura line. There was signs of a flashover to crossarm and small burn marks on the branch.\nThere was no ground fire , no reported injuries or third party property damage."]
[17,275,"2020-05-15","22:38:00",-38.282533999999998,144.61233200000001,"23 Albert St, Point Lonsdale",30071219,"DDL012","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0010657","20200518PWA_05","Report received of a pole fire in Albert st Point Lonsdale. On arrival the crew found  that an overheated FOLCB had resulted in a pole fire. Falling debris also resulted in a small ground fire."]
[17,276,"2020-05-17","19:50:00",-38.073999999999998,144.3587,"120 Bacchus Marsh Rd, Corio VIC 3214, Australia",35207919,"FNS011","Low voltage AC (<1kV)","Rural Short"," - lamps (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011069","20200703PWA_03","Public light fire. No gorund fire."]
[17,277,"2020-05-18","15:38:00",-36.965266,143.51325,"Maryborough-st Arnaud Rd, Rathscar VIC 3465, Australia ",32024807,"MRO005","22kV AC","Rural Long"," - pole (wood)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0010683","20200519PWA_03 ","Vicfire advised of fire caused by tractor operator hitting pole and bringing it and the overhead conductors to the ground. Tractor operator advised to remain in tractor until PCA crew onsite. On arrival crew found that a tractor/sprayer had collided with a pole .\nPolice and CFA on site. There was a small grass fire , no reported in juries or third party proper try damage."]
[17,278,"2020-05-19","19:00:00",-38.195132000000001,144.356697,"30 Grove Rd, Marshall VIC 3216, Australia",31013080,"GLE013","22kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0010697","20200521PWA_01 ","Customers called in to report a conductor brought down by tree branch. The crew attended and confirmed all 3 phases had been brought down by a tree branch. There was a small burn mark on the ground next to the conductors. There was no reported injuries or third party property damage."]
[17,279,"2020-05-22","16:10:00",-38.281337999999998,141.61550399999999,"249 Princes Hwy, Bolwarra 3305",31033424,"PLD001","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0010743","20200525PWA_02","A tree clearing crew reported that a PTA (pole top assembly) had burnt off the pole at the incident location, P519X KRT-PLD No2 R. On arrival the crew found that a bridging insulator had caused a section of the top of the pole to be burnt. There was no ground fire, and no other reported damage or injuries."]
[17,280,"2020-05-22","17:07:00",-36.773772000000001,144.31141500000001,"27 Plante Court Strathdale",60349574,"BGO022","Low voltage AC (<1kV)","Urban"," - services pit","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0010744","20200525PWA_03 ","Customer reported electricity pit out front of property was on fire but had been extinguished.  Customer reported a number of neighbors with no power and partial power. When crew arrive they found that there had been evidence of a fire in the service pit with melted assets inside. No injuries or third party damage."]
[{"$f":"COUNTA(C318:O318,Q318,T318:V318)","v":17},281,"2020-05-22","10:37:00",-38.314999999999998,144.16990000000001,"370 FLAXBOURNE ROAD,PARAPARAP,VIC,3240",32084233,"WPD014","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within electric line construction area",{"$f":"IF(O318=\"\",\"\",IF(O318=\"LBRA only\",0.2,IF(O318=\"HBRA only\",1,IF(O318=\"within electric line construction area\",19.8,IF(O318=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":19.8},"No forecast",{"$f":"IF(Q318=\"\",\"\",IF(Q318=\"No forecast\",0.1,IF(Q318=\"Low-moderate\",0.2,IF(Q318=\"High\",0.5,IF(Q318=\"Very high\",1,IF(Q318=\"Severe\",2,IF(Q318=\"Extreme\",3.5,5)))))))","v":0.1},{"$f":"IF(OR(P318=\"\",R318=\"\"),\"\",IF(AND(O318=\"within electric line construction area\",Q318=\"No forecast\"),1,P318*R318))","v":1},"INC-0011070","20200703PWA_04","EDO found burnt in half on ground. No ground fire."]
[{"$f":"COUNTA(C319:O319,Q319,T319:V319)","v":17},282,"2020-05-23","15:30:00",-37.806333000000002,142.80228099999999,"3174 Mortlake-Ararat Rd, Woorndoo.",32060550,"TRG002","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O319=\"\",\"\",IF(O319=\"LBRA only\",0.2,IF(O319=\"HBRA only\",1,IF(O319=\"within electric line construction area\",19.8,IF(O319=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"No forecast",{"$f":"IF(Q319=\"\",\"\",IF(Q319=\"No forecast\",0.1,IF(Q319=\"Low-moderate\",0.2,IF(Q319=\"High\",0.5,IF(Q319=\"Very high\",1,IF(Q319=\"Severe\",2,IF(Q319=\"Extreme\",3.5,5)))))))","v":0.1},{"$f":"IF(OR(P319=\"\",R319=\"\"),\"\",IF(AND(O319=\"within electric line construction area\",Q319=\"No forecast\"),1,P319*R319))","v":0.45999999999999996},"INC-0010747","20200525PWA_05 ","Powercor Employee was driving on the road at the incident location, when he noticed a burn mark on the cross-arm of P263 Woorndoo Line.\nOn closer inspection, it was found that the crossarm had burnt most of the way through at the strap bolt. All of the conductors were still in position, and there was no ground fire."]
[17,283,"2020-05-24","08:08:00",-38.098956999999999,144.32289,"UNIT 3 89 ROLLINS ROAD, BELL POST HILL VIC 3215",30070328,"GL015","Low voltage AC (<1kV)","Rural Long"," - fuse (any other type)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0010749","20200525PWA_07 ","A fault crew attended an all supply failure at the incident location. On arrival the crew found that a meter board fuse had overheated and burnt a small area of the meter board. There was no other fire or damage reported."]
[17,284,"2020-05-25","15:43:00",-36.055300000000003,144.11930000000001,"74 VICTORIA STREET,PYRAMID HILL,VIC,3575",32031168,"CHA006","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011071","20200703PWA_05","Cross arm fire reported."]
[17,285,"2020-05-26","19:31:00",-38.411727999999997,144.166923,"55A Belton St, Anglesea 3230",30066251,"WPD021","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0010777","20200527PWA_02 ","Vicfire reported a pole fire at the incident location. On arrival the crew found that an LV fused mains box had overheated and failed.  The box dropped debris and melted plastic to the ground, but there was no ground fire. here was no other damage or injuries reported."]
[17,286,"2020-05-26","18:03:00",-38.114910000000002,144.32240899999999,"1 Rowe St, Hamlyn Heights 3215",32069696,"GL013","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0010778","20200527PWA_03 ","A customer and Vicfire both reported a fire on a pole at the incident location. On arrival the crew found that an LV FSD isolator had overheated and caught fire.  There was no ground fire, other damage or injuries reported."]
[17,287,"2020-05-26","17:54:00",-38.257927000000002,144.52142900000001,"29 Field St N, Ocean Grove 3226",32076059,"DDL011","Low voltage AC (<1kV)","Rural Short"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0010779","20200527PWA_04 ","MFB Communications reported a pole fire at the incident location. On arrival the crew found that a transformer LV isolator overheated, causing the attached lead insulation to catch fire, melt and fall to the ground.  There were no reported injuries, ground fire or other damage."]
[17,288,"2020-05-29","19:34:00",-37.739589000000002,144.63951900000001,"463-467 Paynes Rd, Rockbank 3335",33076291,"MLN021","22kV AC","Rural Short"," - transformer (pole mounted)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"No forecast",0.1,0.1,"INC-0010856","20200602PWA_01 ","MFB reported a pole fire at incident location. On arrival crew found a transformer had failed and caught fire briefly. There was no ground fire, no reported injuries or third party property damage. Possible lightning strike."]
[17,289,"2020-05-30","15:20:00",-38.295487999999999,142.36869999999999,"Stadium, High Street, KOROIT 3282 (76 High St, Koroit VIC 3282, Australia)",30271815,"KRT013","22kV AC","Rural Long"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0010857","20200602PWA_02 ","Emergency services reported a pole fire at incident location. When crews arrived they found a HV insulated dropper lead to Pole type S/S \"High-King 42\" had failed and required replacement. No evidence or reports received of ground fire starts, injuries or third party property damage"]
[17,290,"2020-06-05","11:29:00",-36.048642999999998,144.11450099999999,"86 Kelly St, Pyramid Hill VIC 3575",30024621,"CHA006","Low voltage AC (<1kV)","Rural Long"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011176","20200714PWA_03","FSD fire - no ground fire. Found during OMS data review."]
[17,291,"2020-06-08","13:26:00",-36.180103000000003,145.354761,"208 McPhersons Rd, Mundoona VIC 3635",33080324,"SHN011","22kV AC","Rural Long"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0011178","20200714PWA_04","Following fault call, Boric acid fuse found hung up and burnt as switch pole. No ground fire. Incident found during OMS data review"]
[17,292,"2020-06-12","06:28:00",-38.277434999999997,144.48984799999999,"11 Jasper Ave, Barwon Heads 3227",30072968,"GLE013","Low voltage AC (<1kV)","Rural Short"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0010952","20200612PWA_02 ","Vicfire called to report a pole fire at the incident location. On arrival the crew found that the red phase connection of an FSD Krone box on the substation pole had overheated and burnt out. There was no ground fire or any reported injuries or other damage."]
[17,293,"2020-06-14","15:32:00",-34.978769,142.365388,"196 Vallance Road OUYEN",32151770,"OYN003","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0010975","20200616PWA_01 ","Report received of pole fire at incident location. On arrival crew found top burnt off SWER pole. Fire extinguished. There was no ground fire, no reported injuries or third party property damage."]
[17,294,"2020-06-17","08:43:00",-37.983446000000001,143.49082200000001,"3538 Foxhow-Berrybank Road Berrybank 3323",30049762,"CDN004","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0010991","20200618PWA_01 ","GRAINCORP OPERATIONS reported pole on fire and wire down. Crew found a damaged pole due to a pole fire, needs to be replaced, There was no ground fire, no reported injuries or third party property damage."]
[17,295,"2020-06-20","23:48:00",-38.338994,141.59889999999999,"120 Blair Street, Portland",33060158,"PLD004","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011011","20200622PWA_03 ","CFA reported a pole fire at the above address. The crew attended and found a faulted Krone box on the sub pole.  It had overheated and melted. No ground fire was involved.  CFA attended the incident. There was no ground fire, no reported injuries or third party property damage."]
[17,296,"2020-06-22","23:49:00",-36.252603000000001,144.82432,"1768 ODEA ROAD, STRATHALLAN VIC 3622",31025963,"ECA005","22kV AC","Rural Short"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011040","20200624PWA_04 ","Powercor crew responded to  advice of a pole that was on fire. On arrival the crew identified that the high voltage transformer leads have malfunctioned."]
[17,297,"2020-06-24","19:31:00",-38.181750000000001,144.43371200000001,"455 Bellarine Highway, Moolap.",31011250,"GLE024","Low voltage AC (<1kV)","Rural Short"," - fuse (any other type)","single phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0011045","20200625PWA_01","Customer reported smoldering meterboard, no visible flames. On arrival crew found a powercor fuse on the meter board had overheated and caught fire. Meter board slightly burnt and fuse melted. There was no ground fire, no reported injuries or third party property damage."]
[17,298,"2020-06-25","15:30:00",-38.277723999999999,141.641718,"8582 Princes Hwy, Allestree VIC 3305",30308761,"PLD001","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0011053","20200629PWA_01 ","Customer reporting was driving and noticed asset on powerpole was on fire. On arrival crew advised  junction box has caused small fire which has self extinguished. There was no ground fire, no reported injuries or third party property damage"]
[17,299,"2020-06-25","22:11:00",-36.092419,145.442972,"101 Melville St, Numurkah VIC 3636",30304093,"NKA004","22kV AC","Rural Short"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011054","20200629PWA_02 ","Vic Fire reported sparking and arcing at transformer at above address. On arrival, crew found failed insulated HV lead.  HV fuse had operated. Evidence of arcing between two leads. No ground fire, no injuries, no third party damage."]
[17,300,"2020-06-26","23:05:00",-38.554850000000002,143.214877,"590 or 712 CENTRE ROAD, COORIEMUNGLE 3268",30256933,"COB011","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0011058","20200629PWA_03 ","CFA Reported fire. Crew attended and found customer pole mounted krone fuse box had burnt out, causing pole fire. No ground fire, shocks or injuries reported."]
[17,301,"2020-06-27","19:53:00",-38.407395000000001,144.18488300000001,"4 Noble St, Anglesea",30289267,"WPD021","Low voltage AC (<1kV)","Rural Short"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011061","20200629PWA_05 ","Vicfire Reported crossarm fire.  Crew attended and found pole mounted FSD glowing hot and melting, no pole fire. There was no ground fire, no reported injuries or third party property damage."]
[17,302,"2020-06-28","11:44:00",-37.955751999999997,144.30309399999999,"415 CARRS ROAD,ANAKIE,VIC,3213",30312072,"CRO013","22kV AC","Rural Short"," - dropper / bridge","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0011060","20200629PWA_06 ","Customer reported flames and smoke coming from pole on his property, farm has lost supply. Crew found a HV lead on the sub pole had burnt out and required replacing."]
[17,303,"2020-06-30","17:49:00",-38.336167000000003,143.17613600000001,"190 Thorntons Rd E, South Purrumbete VIC 3260",30046394,"CDN001","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0011182","20200715PWA_01","Following reports of no supply an EDO fuse was found burnt but hung up. There was no ground fire. Found during OMS data review."]
[17,304,"2019-12-18","17:47:00",-36.761336999999997,144.29545400000001,"2 MICHAEL STREET,  BENDIGO,VIC,3550",32052992,"BGO022","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0011587","20200908PWA_02","Customer advised half of a tree has fallen onto swire , wire is sparking with sparks reaching the ground, the sparks have already caused 2 lawn fires.\nAttending crew replaced aerial service cable."]
[17,305,"2020-06-05","19:05:00",-38.253993000000001,144.55918199999999,"21-29 Ocean Grand Dr, Ocean Grove VIC 3226, Australia",32080289,"DDL024","22kV AC","Rural Short"," - fuse (powder filled)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011183","20200715PWA_02","Report of pole top fire. On arrival crew found a PF fuse has candled. There was no ground fire. Incident found during oms data review."]
[0,306,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,307,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,308,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,309,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,310,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]

{"sheet":"3. Systems and Audit","index":4,"n_rows":29,"n_cols":5,"rows_kept":29,"cut":false,"hidden":false,"merged":[[28,1,29,4],[3,5,3,6],[4,5,4,6],[5,5,5,6],[6,1,6,4],[9,1,9,4],[14,1,14,4],[10,1,10,4],[13,1,13,4],[12,1,12,4],[11,1,11,4]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"Powercor"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2019/20"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"Powercor must provide:"}]
[]
[null,"Table 4 - Information or reporting systems"]
[null,"   (1) Name of any IT system used to collect fire start data or fault event data - i.e. SCADA system, or fault reporting system"]
[null,"   (2) Whether the fire recording or fault recording process has been audited or complies with a relevant Australian or industry standard - Yes or No"]
[null,"   (3) List any relevant Australian or industry standards that the fire recording or fault recording process complies with"]
[null,"   (4) Whether the data entered into or removed from the IT system has been audited - Yes or No"]
[]
[]
[null,"Table 4: Information or reporting systems"]
[]
[null,"Information or reporting systems","Name","System Audited","Relevant Standards"]
[null,"System 1","Network Incidents Database","Yes","None applicable"]
[null,"System 2","Outage Management System (OMS)","Yes","None applicable"]
[null,"System 3 ","Smallworld GIS (Graphical Information System)","Yes","None applicable"]
[null,"System 4"]
[null,"System 5"]
[null,"System 6"]
[null,"System 7"]
[null,"System 8"]
[]
[null,"The SGSPAA Internal Audit function undertakes a programme of work in accordance with the SGSPAA Group Internal Audit Plan. This internal audit activity covers elements of the systems and process used for capturing, recording and maintaining fire start data."]