{"text_format":"1","workbook":"xlsx","n_sheets":5,"sheets":["Contents","Cover","1. F-Factor summary","2. Individual fire start info","3. Systems and Audit"],"not_rendered":{"charts":0,"images":2,"macros":1,"external_links":2,"defined_names":97,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Contents","index":0,"n_rows":19,"n_cols":6,"rows_kept":19,"cut":false,"hidden":false,"merged":[[8,2,9,3],[2,1,2,10],[4,1,4,10]]}
[" "]
[]
[null,"Electricity Distribution Network Service Provider\nF-factor Reporting Template"]
[]
[null,"Table of contents"]
[]
[]
[null,null,"Cover sheet",null,null,"2. Fire start report"]
[]
[]
[]
[null,null,"1. F-factor summary",null,null,"3. Systems and Audit"]
[]
[]
[]
[]
[]
[]
[null,null,{"$f":"\"NOTE: This spreadsheet includes IRU targets up to and including FY\"&'1. F-Factor summary'!J6","v":"NOTE: This spreadsheet includes IRU targets up to and including FY2020/21"}]

{"sheet":"Cover","index":1,"n_rows":49,"n_cols":6,"rows_kept":49,"cut":false,"hidden":false,"merged":[[26,3,26,8],[28,3,28,8],[26,1,26,2],[31,3,31,5],[14,1,14,8],[16,1,16,8],[17,1,17,8],[21,1,21,8],[19,1,19,8],[10,1,11,8],[13,1,13,8],[48,2,48,6],[42,2,42,3],[42,4,42,7],[46,2,46,6],[47,2,47,6],[38,2,38,3],[38,4,38,7],[41,2,41,3],[41,4,41,7],[37,2,37,3],[37,4,37,7],[32,3,32,8],[30,3,30,8],[15,1,15,8]]}
[]
[]
[]
[]
[]
[]
[]
[null,"Distribution Network Service Provider"]
[null,"Fire start report"]
[]
[null,"This template is to be used by a DNSP to provide a fire start report to the AER in accordance with section 5 of the F-factor Order in Council.  "]
[]
[]
[null,"Colour coding of input sheets:"]
[null,"Dark blue = AER headings"]
[null,"Grey = AER instructions"]
[null,"Yellow = Input cells"]
[null,"Light orange = Automatically-generated cells"]
[]
[null,"Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so."]
[null,"The cells and structure of the spreadsheet is locked to prevent inadvertent interference with the automated settings."]
[null,"All dollar amounts are to be unrounded, and in nominal terms."]
[]
[]
[]
[]
[null,"DNSP:",null,"Powercor"]
[]
[null,"DNSP - trading name:",null,"Powercor Australia Ltd"]
[]
[null,"DNSP - Australian business number: ",null,"ACN 064 651 109"]
[]
[null,"Reporting year:",null,"2020/21"]
[]
[]
[]
[]
[null,"Business address","Address",null,"40 Market Street"]
[null,null,"Suburb",null,"Melbourne"]
[null,null,null,"State","Victoria","Postcode"]
[]
[null,"Postal address","Address",null,"Locked Bag 14090"]
[null,null,"Suburb",null,"Melbourne"]
[null,null,null,"State","Victoria","Postcode"]
[]
[]
[null,"Contact name/s","Rachel Perlaki"]
[null,"Contact phone/s","(03) 9683 4872"]
[null,"Contact email address/s","RPERLAKI@POWERCOR.COM.AU"]

{"sheet":"1. F-Factor summary","index":2,"n_rows":14,"n_cols":15,"rows_kept":14,"cut":false,"hidden":false,"merged":[[12,2,12,3],[13,2,13,3],[6,2,6,3],[7,2,7,3],[8,2,8,3],[9,2,9,3],[10,2,10,3],[5,1,5,2],[3,6,3,8],[4,6,4,8],[5,6,5,8],[11,2,11,3]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"Powercor"},"IRU target:",{"$f":"IF(SUM(K7:O7)=0,\"\",SUM(K7:O7))","v":277.60000000000002},null,null,null,null,null,null,"AusNet Services","CitiPower","Jemena","Powercor","United Energy"]
[null,"F-factor data reporting","IRU amount:",{"$f":"IF(SUM('2. Individual fire start info'!S38:S2000)=0,\"\",SUM('2. Individual fire start info'!S38:S2000))","v":112.27999999999999},null,null,null,null,null,"2016/17",247.7,3.4,9.6999999999999993,468,22.3]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2020/21"},"Revenue adjustment:",{"$f":"IF(OR(D1=\"\",D2=\"\"),\"\",15000*(D1-D2))","v":2479800.0000000009},null,null,null,null,null,"2017/18",247.7,3.4,9.6999999999999993,468,22.3]
[null,null,null,null,null,null,null,null,null,"2018/19",247.7,3.4,9.6999999999999993,468,22.3]
[null,"Table 2: Summary of total fire starts by F factor Order definition",null,null,null,null,null,null,null,"2019/20",221.1,3.4,9.6999999999999993,412.8,22.3]
[null,"This is a summary of data in worksheet \"2. Fire Start Report\"",null,null,null,null,null,null,null,"2020/21",177.5,1.3,4.2,277.60000000000002,18.7]
[null,"Kind of Fire Start by definition of fire start under clause 5 of F-factor Order","Total fires by cause",null,null,null,null,null,null,null,{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>K1),\"\",LOOKUP($B3,$J2:$J6,K2:K6))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>L1),\"\",LOOKUP($B3,$J2:$J6,L2:L6))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>M1),\"\",LOOKUP($B3,$J2:$J6,M2:M6))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>N1),\"\",LOOKUP($B3,$J2:$J6,N2:N6))","v":277.60000000000002},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>O1),\"\",LOOKUP($B3,$J2:$J6,O2:O6))","v":""}]
[null,"Started in or originated from a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B8)","v":168}]
[null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B9)","v":32}]
[null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B10)","v":20}]
[null,"Started by lightning striking a distribution system or a part of a distribution system ",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B11)","v":3}]
[null,"Started by any other thing forming part of or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B12)","v":18}]
[null,"Otherwise started by a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B13)","v":0}]
[null,"Total",{"$f":"SUM(C8:C13)","v":241}]

{"sheet":"2. Individual fire start info","index":3,"n_rows":312,"n_cols":25,"rows_kept":312,"cut":false,"hidden":false,"merged":[[3,22,3,24],[4,22,4,24],[5,22,5,24],[7,1,7,21],[11,1,11,2],[9,1,9,21],[13,1,13,11],[22,1,22,21],[24,1,24,21],[14,1,14,20],[15,1,15,18],[16,1,16,18],[18,1,18,18],[21,1,21,18],[19,1,19,18],[23,1,23,18],[20,1,20,18],[17,1,17,18],[25,1,25,18],[27,1,27,20],[26,1,26,21],[35,19,35,21],[33,1,33,4],[35,2,35,10],[28,1,28,18],[29,1,29,18],[35,11,35,13],[35,14,35,17]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"Powercor"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2020/21"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"\"Enter into this worksheet fire start data, from any IT system, which have been recorded by \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\". Note that fire starts must be in accordance with the definition of a fire start in the Order In Council.\"","v":"Enter into this worksheet fire start data, from any IT system, which have been recorded by Powercor. Note that fire starts must be in accordance with the definition of a fire start in the Order In Council."}]
[]
[null,"\"Fire\" should be interpreted using its common meaning and can be defined as a process in which substances combine chemically with oxygen from the air and typically give out bright light, heat and smoke. A fire should be recorded where there is evidence of smoking, charring, scorching, burning or any other evidence that a fire had occurred.  "]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"Powercor must provide:"}]
[]
[null,"Table 3 - Individual Fire Starts"]
[null,"   (1) Date - dd/mm/yyyy"]
[null,"   (2) Time - if known, the 24-hour time of the fire start hh:mm"]
[null,"   (3) Latitude and longitude of the fire start as decimal coordinates"]
[null,"   (4) Address of the property on which the incident occurred or closest to the incident"]
[null,"   (5) Asset number for the asset nearest the fire start"]
[null,{"$f":"\"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the \"&B1&\" network\"","v":"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the Powercor network"}]
[null,"   (7) Voltage on the line in which the fire start occurred (note: this may not be the nearest polyphase overhead line)"]
[null,"   (8) Network categorisation - CBD, Urban, Rural Long or Rural Short"]
[null,"   (9) Asset type of primary asset causing fire in accordance with OSIRIS asset categories"]
[null,"   (10) Where the asset involved in the fire is a transformer or an overhead or underground line, provide the phase, or phases, of the line or transformer"]
[null,"   (11) Kind of fire start in accordance with categories specified in Clause 5 of the F-factor Order-In-Council"]
[null,"   (12) Identify the location of the fire start in accordance with the categories specified in Clause 11(b) of the F-factor Order-In-Council"]
[null,"   (13) Provide the BOM fire danger rating applicable at the time of the fire start (data is available on the EM-COP website)"]
[null,{"$f":"\"   (14) \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\"'s record number for the incident\"","v":"   (14) Powercor's record number for the incident"}]
[null,"   (15) ESV's OSIRIS reference number for the incident"]
[null,"   (16) Free text description of the fault containing relevant comments from field reports "]
[]
[]
[]
[null,"Table 2: Individual Fire Starts"]
[]
[null,"Number","Fire starts",null,null,null,null,null,null,null,null,"Fire Type",null,null,"Risk Factors",null,null,null,"IRU \namount","Additional information"]
[null,null,"Date 1","Time 2","Latitude 3","Longitude 3","Address of incident 4","ID of \nnearest \nasset 5","ID of nearest \npolyphase \nline 6","Voltage of line in which \nfire start \noccurred 7","Network categorisation 8","Type of primary asset \ninvolved in fire start 9","Phase(s) of \nline or \ntransformer 10","Kind of fire start as per Clause 5\nof F-factor Order-In-Council 11","Location \narea 12","Location\nmultiplier","Fire \ndanger \nrating 13","Danger multiplier","Product of multipliers","DNSP record number 14","OSIRIS \n(ESV) reference \nnumber 15","Fault \ndescription 16"]
[{"$f":"COUNTA(C38:O38,Q38,T38:V38)","v":17},1,"2020-07-01","13:00",-37.872101000000001,143.56879699999999,"469 Burgers Road / Quarrells Road, Wallinduc","33006028","BAS021","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O38=\"\",\"\",IF(O38=\"LBRA only\",0.2,IF(O38=\"HBRA only\",1,IF(O38=\"within electric line construction area\",19.8,IF(O38=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"No forecast",{"$f":"IF(Q38=\"\",\"\",IF(Q38=\"No forecast\",0.1,IF(Q38=\"Low-moderate\",0.2,IF(Q38=\"High\",0.5,IF(Q38=\"Very high\",1,IF(Q38=\"Severe\",2,IF(Q38=\"Extreme\",3.5,5)))))))","v":0.1},{"$f":"IF(OR(P38=\"\",R38=\"\"),\"\",IF(AND(O38=\"within electric line construction area\",Q38=\"No forecast\"),1,P38*R38))","v":0.45999999999999996},"INC-0011096","20210908PWA_01","Customer advised Fuse box on pole Glenfine 19 has burnt out and fallen onto ground. \n Burnt grass at base of pole.\nThere was no reported injuries or third party property damage.",null,null,"Overhead conductors"]
[17,2,"2020-07-02","18:11",-36.416213999999997,145.20915400000001,"5735 Midland Highway Tatura 3616 (A300, Tatura VIC 3616, Australia)","30138784","MNA014","22kV AC","Rural Long"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011197","20200716PWA_07","Customer reported equipment on pole is arcing and glowing, no sparks reaching the ground.\nCrew found a Candling/arcing fuse associated with a line fault caused by a Pelican\nThere was no ground fire, no reported injuries or third party property damage.\n",null,null," - overhead conductor (bare; aluminium core steel reinforced)"]
[17,3,"2020-07-02","18:29",-35.479475999999998,143.76900800000001,"1611 Winlaton Road Fish Point 3585","33067945","KGT004","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0011198","20200716PWA_08","CFA reported pole fire at incident location.\nOn arrival crew found a FOLCB had melted and caught fire.\nDebris on ground but no ground fire.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - overhead conductor (bare; all aluminium conductor)"]
[17,4,"2020-07-05","14:26",-37.052788999999997,143.70975999999999,"4899 Pyrenees Highway Maryborough 3465","33009623","MRO008","22kV AC","Rural Long"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0011213","20200717PWA_05","During patrol of line following outage report, crew found a boric acid fuse had candled and broken.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - overhead conductor (bare; copper)"]
[17,5,"2020-07-07","16:45",-38.231482999999997,143.145802,"202 Manifold St, Camperdown 3260","31008966","CDN003","Low voltage AC (<1kV)","Urban"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011155","20200713PWA_02","The customer reported that a fuse had burnt down and melted on junction box, attached to the side of the building, and the power was still on. \nOn arrival the crew found that the Red phase fuse of the POA mounted fuse box had overheated and fallen to the ground, there was other melting of the box evident also. \nThere were no reported injuries, ground fire or other damage.",null,null," - overhead conductor (bare; steel)"]
[17,6,"2020-07-08","23:34",-37.584989,143.84116800000001,"37 Albert Street Sebastopol 3356","41089865","BAS034","22kV AC","Urban"," - transformer (kiosk mounted)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011228","20200720PWA_03","A Car has collided and damaged 315kVA kiosk substation.\nThe kiosk was moved off its pad, there was a flashover and evidence of burning.\nThere was oil leaking.\n",null,null," - overhead conductor (ABC)"]
[17,7,"2020-07-09","09:38",-36.748848000000002,141.22971000000001,"Minimay Frances rd Minimay 3413 (C213, Minimay VIC 3413, Australia)","31033672","HSM004","22kV AC","Rural Long"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0011237","20200720PWA_04","A work crew were dispatched a supply outage traced back to switch pole 672 on the Natimuk line.\nOn arrival the crew found a 12k B/A HV fuse south side of the switch had operated but had failed to drop down to an isolated position, the tube has then burnt in half and caused the outage.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - overhead conductor (covered uninsulated)"]
[17,8,"2020-07-09","21:33",-38.428033999999997,144.17577900000001,"114 Melba Pde ANGLESEA 3230","30068325","WPD021","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0011158","20200713PWA_03","Powercor received a report from Vic Fire of a glowing / smoldering pole at incident address.\nWhen crews arrived they found a three phase FOLCB on the pole had failed resulting in a equipment fire.\nNo ground fire, injuries or third party damage was reported. ",null,null," - overhead conductor (insulated)"]
[17,9,"2020-07-10","13:09",-38.289422999999999,144.61024399999999,"Ocean Rd, cnr Baillieu St, Point Lonsdale 3225 (35 Baillieu St, Point Lonsdale VIC 3225, Australia)","30281421","DDL012","Low voltage AC (<1kV)","Rural Short"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0011159","20200713PWA_04","Powercor received customer calls advising of no & part supply in incident address area. \n When crews arrived they found the red phase LV bus fuse holder was damaged with evidence of burning. \nNo ground fire, injuries or third party property damage was reported.",null,null,"Service lines"]
[17,10,"2020-07-13","19:22",-36.807141000000001,144.36299500000001,"2 Swanson Boulevard, Strathfieldsaye VIC 3551","30318665","BGO013","22kV AC","Rural Short"," - connector / termination","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0011173","20200714PWA_01","Customer reported pole fire and dim lights at the incident address.\nUpon arrival crew found that the white phase of HV insulated transformer leads had failed and had arced during its failure, this resulted in a brown out situation to approximated 2/3 of the customers supplied by the substation.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - overhead service conductor (residential)"]
[17,11,"2020-07-13","17:27",-37.254353000000002,144.464451,"19 Warren Street, Kyneton VIC 3444","33024546","WND023","Low voltage AC (<1kV)","Rural Long"," - overhead conductor (ABC)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011192","20200716PWA_04","Customer reported, sparks, arcing and fire coming from pole top at the incident location\nupon arrival crew found that an IPC on the LV ABC had burnt off\n The fire had self extinguished.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - overhead service conductor (commercial / industrial)"]
[17,12,"2020-07-15","22:30",-37.136445000000002,143.50853499999999,"20 Lamplough - Greenhill Creek Road, Lamplough VIC 3352","30017197","MRO008","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0011220","20200717PWA_08","Customer reported intermittent supply at the incident address. Upon arrival fault crew found that a 22kV side EDO fuse tube on the Lamplough ISO P34 had candled and burnt through.\nThere was no ground fire, no reported injuries or third party property damage",null,null," - overhead service conductor (subdivision / construction)"]
[17,13,"2020-07-17","07:00",-38.137352,144.70929799999999,"19 Cairnes Street, Indented Head 3223","30064333","DDL013","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (residential)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011227","20200720PWA_02","Neighbors reported sparks and what looked like fireworks coming from the service cable where it went through a tree at the incident location. \nOn arrival the crew found that the service cable to had rubbed through the insulation on a tree in the front yard of the house, this resulted in the service cable burning on a branch of the tree\nThere were no reported injuries or ground fire.",null,null," - overhead service conductor (other)"]
[17,14,"2020-07-17","09:10",-37.540733000000003,143.836386,"1032 Howitt St, Wendouree 3355 (1032 C287, Wendouree VIC 3355, Australia)","30013528","BAN002","Low voltage AC (<1kV)","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011224","20200720PWA_01","A customer called and said the following: Pole across the road on fire, something has fallen and smoldering on grass below. Grass wet.\nOn arrival the crew found that an LV ABC IPC had overheated and burnt out, falling to the ground. \nThe IPC fell on wet green grass, so there was no ground fire. \nThere were no injuries or third party damage reported.",null,null," - underground service cable (residential)"]
[17,15,"2020-07-17","13:45",-34.423172999999998,142.306308,"Westridge, 16 Robinson Rd, Iraak VIC 3494, Australia","32145382","RCT013","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0011244","20200721PWA_01","An unknown vehicle [believed to be a tractor fro Gill Farms collided with substation pole # 160 Colignan, the shock load broke all three insulator ties, snapped one insulator off the end of the crossarm. \nThe other two conductors were on the wood crossarm on a wood pole. \nThere was evidence of smoldering on the crossarm but no ground fire evidence.\nThird party had left the scene. \nThere was no ground fire, no reported injuries or third party property damage.",null,null," - underground service cable (commercial / industrial)"]
[17,16,"2020-07-20","05:01",-36.775148999999999,144.30753999999999,"150 CONDON STREET  KENNINGTON 3550 ","30319893","BGO012","22kV AC","Urban"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011269","20200723PWA_01","Vic fire reported pole fire at incident location.\nOn arrival crew found that a Red Phase HV Insulated Dropper Lead failed on Substation.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - underground service cable (subdivision / construction)"]
[17,17,"2020-07-22","10:17",-38.349412999999998,143.81224399999999,"290 Birregurra-Deans Marsh Rd, Whoorel VIC 3243, Australia","30054881","WIN011","22kV AC","Rural Long"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,{"$f":"IF(OR(P54=\"\",R54=\"\"),\"\",IF(AND(O54=\"within electric line construction area\",Q54=\"No forecast\"),1,P54*R54))","v":0.45999999999999996},"INC-0011265","20200722PWA_01","A passer-by reported a sparking pole at the incident location.\nUpon arrival, a Powercor fault crew found that a Boric Acid fuse candled.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - underground service cable (other)"]
[17,18,"2020-07-23","21:00",-38.338562000000003,141.59439699999999,"5 Pile Ct, Portland 3305","33060221","PLD004","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011288","20200727PWA_01","CFA reported pole fire at incident location. \n On arrival the crew found an FOLCB had caught fire and fallen to the ground. Wet grass at the base of pole was not burnt.\nThere was no ground fire, no reported injuries or third party property damage.",null,null,"Underground cables"]
[17,19,"2020-07-24","23:44",-37.678049999999999,144.532287,"531-555 Harkness Rd, Melton West VIC 3337, Australia","30111468","MLN022","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0011322","20200729PWA_05","Report received to advise of a tree branch falling onto wires and that branch caught fire.\nUpon arrival the crew didn’t find any evidence of a branch falling onto wires, however they did find a burnt out FOLCB at transformer pole “Harkness Rd P5” \nThere was no ground fire, no reported injuries or third party property damage",null,null," - underground cable"]
[17,20,"2020-07-28","09:45",-38.343220000000002,143.78126700000001,"26 Murrell St, Birregurra VIC 3242, Australia","30348990","WIN011","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011314","20200729PWA_01","Vicfire reported a pole fire at the incident location.\nOn arrival the crew found that a 240V single phase FOLCB on the pole that supplies both No28 & No30 Murrell St, had overheated and caught fire. \ndebris had fallen to the ground, however there was no ground fire, and no other damage reported.",null,null," - underground communications cable"]
[17,21,"2020-07-31","16:03",-37.926402000000003,144.464529,"Little River-Ripley Rd, Little River VIC 3211","30075607","FNS022","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0011864","20201013PWA_01","Report of part supply.\nOn arrival crew found a white phase EDO fuse had candled\nThere was no ground fire, no reported injuries or third party property damage.\nEvent found during OMS data review.",null,null,"Poles"]
[17,22,"2020-08-05","10:12",-38.281599999999997,144.60123200000001,"73 Gill Rd, Point Lonsdale VIC 3225","30244054","DDL012","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0011867","20201013PWA_02","Following review of outage data, report of Candled HV fuse found.\nNo ground fire, no reported injuries or third party property damage",null,null," - pole (concrete)"]
[17,23,"2020-08-09","13:31",-38.172035000000001,144.71299500000001,"40 Coatsworth Ave, St Leonards VIC 3223","32087670","DDL013","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011869","20201013PWA_03","Candled EDO fuse reported\nNo ground fire, no reported injuries or third party property damage\nFound during outage data review",null,null," - pole (steel)"]
[17,24,"2020-08-10","04:16",-38.343063000000001,142.34720100000001,"306 Survey Lane, Killarney VIC 3283","31030092","KRT022","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0011496","20200820PWA_01","A customer reported 2 fuses open at front of her property.\nCrew patrolled line and confirmed the report at Pole 17 (. \nCrew identified the pole smoking/smoldering near center phase EDO position.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - pole (wood)"]
[17,25,"2020-08-10","09:30",-38.205868000000002,144.29099199999999,"115 Waurn Ponds Drive, Waurn Ponds, 3216.","30244874","GTS-WIN","66kV AC","Unknown"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0011401","20200811PWA_01","A 66kv conductor dislodged from insulator, coming to rest on HV crossarm.\nThere was a pole fire and suspected HVI damage.\nThere was no ground fire and no reported injuries.",null,null,"Crossarms"]
[17,26,"2020-08-11","11:30",-37.894826000000002,144.61923300000001,"4 Greenhill Cres, Wyndham Vale VIC 3024","31022675","WBE031","Low voltage AC (<1kV)","Urban"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011430","20200813PWA_02","Vicfire reported a pole fire at the incident location, on arrival the crew found that the connections in a service cable junction box on the pole had overheated causing the box to catch fire. \nThere were no reported injuries, ground fire, or any other damage.",null,null," - crossarm (wood)"]
[17,27,"2020-08-13","18:22",-38.242483999999997,142.459271,"14 Church St, Winslow 3281","33100025","KRT012","22kV AC","Rural Long"," - insulators","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011447","20200814PWA_03","Vicfire reported a transformer on fire at the incident location.\nOn arrival the crew found that a stick from a nearby tree had fallen onto the top of the three phase transformer. The stick bridged out one of the HV bushings to the earthed tank of the transformer, light rain at the time caused the stick to track and catch fire. \nThere was only minor damage to one of the HV bushing covers, and there was no ground fire, and no other damage reported.",null,null," - crossarm (steel)"]
[17,28,"2020-08-13","18:43",-38.339576000000001,144.286405,"1A Bells Boulevard, Jan Juc","33045102","WPD021","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0011445","20200814PWA_02","Vicfire reported a pole fire at the incident location. \nOn arrival the crew found that a single phase FOLCB on the substation, had burnt when the connections had over heated.\nThe box was totally destroyed by the fire.\nDebris had dropped to the wet ground, but there was no ground fire, and no other damage reported.",null,null," - crossarm (other)"]
[17,29,"2020-08-16","20:30",-38.148491999999997,144.35901100000001,"Minns Place, Geelong CBD (15 James St, Geelong VIC 3220, Australia)","PA0088549","GCY021","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011461","20200817PWA_02","Vicfire called and reported a Substation on fire at the incident location.\nOn arrival the crew found a large circuit board at the Minns-Little Malop Indoor Substation had caught fire. \nThe circuit board which controls four LV underground circuits, was almost completely destroyed by the fire, an adjoining circuit board also suffered minor damage. \nA dead rat was found partially burnt on one of the adjoining circuits, however it could not be determined if the rat was the cause of the fire. \nThe fire has resulted in a large outage to the CBD area of Geelong. There were no reported injuries or third party damage. ",null,null,"Overhead assets"]
[17,30,"2020-08-20","12:42",-37.774467000000001,144.84124,"40 Northumberland Road, Sunshine North 3020 (Sunshine Sec Col, Sunshine North VIC 3020, Australia)","33077940","SSE032","22kV AC","Urban"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011497","20200821PWA_01","Vic Emergency reported a pole fire at this incident location. \nOn arrival the crew found that the blue phase HV Boric Acid fuse had operated and candled. \nThere was no ground fire, and no reported third party damage.",null,null," - capacity balancing units"]
[17,31,"2020-08-22","04:44",-38.20458,144.198714,"95 Simmonds Rd, Mount Moriac VIC 3240, Australia","30073999","WPD011","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0011874","20201014PWA_01","Crew reported EDO fuse hung up and candled\nreport found during outage data review\nno photos found\nNo ground fire, no reported injuries or third party property damage.",null,null," - connector / termination"]
[17,32,"2020-08-23","07:28",-36.965176999999997,144.24907200000001,"5 McIvor Road Harcourt VIC","32041806","CMN003","22kV AC","Rural Long"," - fuse (powder filled)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0011527","20200826PWA_02","Large tree on opposite side of the road to the HV Harcourt Reservoir Line fell [failure at roots] causing a HV phase to phase fault. Pole 6A switch pole was in the same span. Centre phase HV fuse operated and Road side fuse hung up and burnt off at bottom of the fuse holder. HV crossarm broke at Pole 7 LIS 506616 with broken ties and cable was against the side of the pole",null,null," - dropper / bridge"]
[17,33,"2020-08-24","16:54",-37.875014999999998,144.71932000000001,"234 OLD GEELONG ROAD,HOPPERS CROSSING,VIC,3029","32170402","LV008","Low voltage AC (<1kV)","Urban"," - fuse (any other type)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011513","20200825PWA_01","customer reported can smell burning  , from meter box  no flames or smoke- Meter panel is scorched. No self isolation\n\nOn arrival the PCA Faults Crew have advised that Meter Box Panel (Backing Board /Chip Board) has sustained some very minor charring/scorching approx. 0.05m x 0.1m (5cm x10cm) due to an overheated connection on the Red-Phase Fuse /Service Cartridge.\n",null,null," - guy wire"]
[17,34,"2020-08-24","09:02",-38.148932000000002,144.36046300000001,"Indoor Substation \"Rock - Lt Malop\" Rock O'Cashel Lane, Geelong 3220","41067447","GCY013","Low voltage AC (<1kV)","Urban"," - transformer (indoor chamber mounted)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011514","20200825PWA_02","Powercor initially received a customer report of a substation \"smoking & having a burned plastic smell\" outside of his premises in Rock O'Cashel Lane, Geelong. When crews arrived at the incident site they found the LV Distribution Fuse panel at \"Rock - Lt Malop\" Indoor Substation had been damaged by a fire on one of the LV Circuits.",null,null," - insulator tie wires / connections"]
[17,35,"2020-08-27","16:38",-38.346133000000002,143.61018899999999,"38 HUGH MURRAY DRIVE, COLAC,VIC,3250","30246621","CLC004","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0011618","20200915PWA_02","Multiple report of tree and wires down . \nAttending crew found trees brought down by storm  in multiple locations in immediate area\nUpon review of Images, burns on branch were apparent",null,null," - insulators"]
[17,36,"2020-08-28","14:33",-37.722926000000001,144.790705,"13 Gunsynd Ct, Keilor Downs VIC 3038","30243671","SA011","22kV AC","Urban"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011546","20200830PWA_04","MFB reported a pole fire at incident location. \nCrew found that a pole fire had occurred \nThe top position HV Xarm had dropped down on the lower HV conductors.\nfire  attended and put out the fire, no HVI, resulted in 10m x 5m ground fire.",null,null," - tower"]
[17,37,"2020-08-28","08:37",-35.343418999999997,141.07252,"Ngallo S Rd, Panitya VIC 3512","32139302","OYN001","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0011884","20201014PWA_03","Report of part supply.\nCrew found a candled EDO fuse\nNo ground fire\nIncident found when doing outage data review - no photos",null,null," - traction lines"]
[17,38,"2020-08-28","06:57",-36.164665999999997,144.83175800000001,"594 Looker Rd, Echuca Village VIC 3564","32179732","ECA005","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,{"$f":"IF(OR(P75=\"\",R75=\"\"),\"\",IF(AND(O75=\"within electric line construction area\",Q75=\"No forecast\"),1,P75*R75))","v":0.1},"INC-0011880","20201014PWA_02","Report received of pole fire \nOn arrival crew found a FOLCB burnt\nThere was no ground fire, no reported injuries or third party property damage.\n\nIncident found during outage data review",null,null,"Underground assets"]
[{"$f":"COUNTA(C76:O76,Q76,T76:V76)","v":17},39,"2020-09-01","21:56",-37.442866000000002,144.67508799999999,"O/S 156 SANDY CREEK RD - RIDDELLS CREEK","33028928","GSB012","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O76=\"\",\"\",IF(O76=\"LBRA only\",0.2,IF(O76=\"HBRA only\",1,IF(O76=\"within electric line construction area\",19.8,IF(O76=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"No forecast",{"$f":"IF(Q76=\"\",\"\",IF(Q76=\"No forecast\",0.1,IF(Q76=\"Low-moderate\",0.2,IF(Q76=\"High\",0.5,IF(Q76=\"Very high\",1,IF(Q76=\"Severe\",2,IF(Q76=\"Extreme\",3.5,5)))))))","v":0.1},0.45999999999999996,"INC-0011565","20200902PWA_02","Vicfire reported wires down and sparking. intersection of sandy creek road and cutevan cres\n\nUpon arrival crew found that a large tree had fallen across the HV conductors. One of the conductors had come to ground",null,null," - LV pillar"]
[17,40,"2020-09-01","23:53",-37.457191000000002,144.68293700000001,"5 Gap Rd, Riddells Creek VIC 3431",30551148,"GSB012","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011911","20201019PWA_04","Report of section fuses operated , crew found branch blown, burnt and hung up on line\nno ground fire\nFound during outage data review",null,null," - services pit"]
[17,41,"2020-09-01","17:24",-37.274374000000002,144.03224700000001,"5 Robinson Rd, Werona VIC 3364","30004525","BAN009","12.7kV AC (SWER)","Rural Long"," - fuse (EDO fuse)","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0011909","20201019PWA_01","Crew attended found candled EDO fuse \nNo ground fire\nIncident found during outage data review",null,null,"Transformers"]
[17,42,"2020-09-02","00:43",-38.336494000000002,144.30411899999999,"175 Duffields Rd, Torquay VIC 3228 ","33045018","WPD032","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0011912","20201019PWA_05","Following reports of outage on arrival crew found that an EDO fuse unit had candled.\nThere was no ground fire\nincident found during outage data review",null,null," - transformer (pole mounted)"]
[17,43,"2020-09-02","15:52",-36.401339,144.956199," 689 Winter Rd, Girgarre VIC 3624","33108461","SHP011","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011914","20201019PWA_06","Following supply failure crew found an EDO had candled and fallen to ground.\nThere was no ground fire\nFound during outage data review  photos taken",null,null," - transformer (kiosk mounted)"]
[17,44,"2020-09-07","19:01",-37.444398,144.66731999999999,"200 Gaps Rd, Riddells Creek Vic 3431",32046805,"GSB012","22kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0011586","20200908PWA_01","Crew attended supply outage at above address.  When crew arrived, they found that a tree branch had fallen onto HV  breaking Blue and Red phase while resting on White phase. Base of tree approx. 6m from centre of span.",null,null," - transformer (ground outdoor mounted)"]
[17,45,"2020-09-07","08:52",-37.825837,144.75807699999999,"441 Dohertys Rd, Truganina 3029","31024574","LVN021","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0011589","20200908PWA_04","A foil  balloon flew into the HV causing a flashover, resulting in a small grassfire, 441 Dohertys Rd, Truganina 3029\nThe flashover caused damage to the Boric Acid fuse units, and caused the 22kV conductors to fall to the ground, resulting in a grassfire of approx 20m x 10m= 200m2. The conductors fell onto a worksite, however it was not known if there were any workers in the area at the time.",null,null," - transformer (indoor chamber mounted)"]
[17,46,"2020-09-11","18:26",-38.336494000000002,144.30411899999999,"175 Duffields Rd, Torquay VIC 3228","33045018","WPD032","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0011921","20201019PWA_07 ","Crew investigating part supply found EDO fuse candled\nno ground fire\nno photos provided found during outage data review data review\nNote osiris 20201019PWA_05 on 2/9/20 same structure",null,null," - transformer (any other type)"]
[17,47,"2020-09-13","22:00",-38.158763,144.32695899999999,"16 Holyrood Avenue, Newtown 3220","32086105","GL021","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011610","20200915PWA_01","ESTA reported a fire at the incident location. On arrival the crew found an LV FSD isolator had overheated and burnt out on Substation Holyrood-Buckingham. melted debris fell to the ground",null,null," - measurement transformer (current transformer)"]
[17,48,"2020-09-19","16:03",-34.249842000000001,142.18313000000001,"9320 Calder Hwy, Irymple, VIC 3498","32141581","RCT021","Low voltage AC (<1kV)","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011673","20200921PWA_01","Customer report of a pole fire at the incident address. \nUpon arrival Powercor fault crew found that a LV crossarm  had burnt through at the kingbolt, all conductors remained aloft.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - measurement transformer (voltage transformer)"]
[17,49,"2020-09-21","10:38",-38.159193999999999,144.33660499999999,"1 Bridge St, Newtown VIC 3220","30061272","GCY014","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011928","20201020PWA_01","Asset inspector found badly burnt crossarm that has occurred at some time prior to inspection.\nno ground fire\nincident found during outage data review",null,null," - measurement transformer (capacitive voltage transformer)"]
[17,50,"2020-09-24","06:10",-37.931328000000001,144.402072,"390 SANDY CREEK ROAD,LARA,VIC,3212","32068295","FNS021","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0011933","20201020PWA_02","Fuse had blown after bird contact but had candled causing edo barrel to burn and fall\nNo ground fire\nfound during outage data review no photos found",null,null,"Fuses and switchgear"]
[17,51,"2020-09-27","10:46",-38.391283999999999,142.48453900000001,"120 Pertobe Road, Warrnambool 3280","31032482","WBL008","22kV AC","Urban"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0011732","20200929PWA_01","A customer called and reported a transformer on pole in Caravan park, buzzing and smoking.\nOn arrival the crew found that one of the HV Boric acid fuses on the substation had blown, and the other two HV Boric acid fuses had candled and burnt and remained in place. \nhe crew stated that there was flashover damage to the Surge Diverters on the transformer, possibly caused by an animal or bird, however no carcass was found.\nThere was no reported ground fire, injuries, or other damage.",null,null," - fuse (boric acid)"]
[17,52,"2020-10-02","08:38",-35.322823,143.553033,"188 Murray Valley Highway, Swan Hill 3585","32156183","SHL004","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0011804","20201005PWA_02","A customer called and said: Fuse has blown at top of powerpole and is now smoking, made a loud bang.\nOn arrival the crew found that a HV fuse had operated but not cleared properly, causing the fuse barrel to candle.\nThere were no reported injuries or ground fires.",null,null," - fuse (EDO fuse)"]
[17,53,"2020-10-03","16:29",-35.914485999999997,144.10029399999999,"Mincha West-Cohuna Rd -Mincha"," 30229009","CHA006","22kV AC","Rural Long"," - automatic circuit recloser (ACR)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0011802","20201005PWA_01","ACR operational fault at PYRAMID P135 ACR LIS-986864 reported by control room. \nACR didn't operate alarm. \n Upon arrival crew found 200mx10m grassfire had burnt itself out mainly in road reserve and approximately 1m into private paddock.\n CFA were not onsite, fire burnt itself out, grass was quite green. \nThere was no reported injuries",null,null," - fuse (Fault Tamer)"]
[17,54,"2020-10-08","20:32",-38.125194999999998,144.32142200000001,"49 HAMLYN AVENUE,NORTH GEELONG,VIC,3215","32067684","GL013","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0011846","20201009PWA_01","customer reported that  POA exploded there were a lot of sparks and smoke and glowing from mains box",null,null," - fuse (powder filled)"]
[17,55,"2020-10-12","08:48",-37.925502000000002,144.163355,"482 Maude-She Oaks Rd, Maude VIC 3331","33105571","GL015","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0012077","20201106PWA_02","Following on from supply problem crew found EDO fuse candled.\nNo Ground fire, no reported injuries or third party property damage.\nNo photos taken\nIncident found during outage data review. ",null,null," - fuse (any other type)"]
[17,56,"2020-10-13","19:56",-37.677135999999997,144.565214,"26 West Melton Drive, Melton West","60069344","MLN032","Low voltage AC (<1kV)","Rural Short"," - LV pillar","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0011901","20201015PWA_04","Several customers reported hearing an explosion and seeing a fire at the incident location.\nA Powercor crew attended the site and identified that an LV cable had incurred insulation failure below ground level within an LV service pillar inside the property at No. 26\nThe crew indicated that the internals of the pillar had sustained sooting and that weeds around the ground edge of the pillar cover had sustained burning.\n",null,null," - circuit breaker"]
[17,57,"2020-10-14","15:56",-36.363157999999999,145.31155699999999,"237 Cornish Rd, Ardmona VIC 3629","33092828","MNA014","22kV AC","Rural Long"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0011898","20201015PWA_03","Customer reported ground fire at the base of a pole.  On arrival crew found damage to an insulator at the top of the pole and noticed that a bird cover on the cross-arm had moved towards the pole.   Crew also found a dead bird at the base of the pole and a ground fire",null,null," - switch (disconnector/isolator)"]
[17,58,"2020-10-17","15:40",-36.786656000000001,144.354534,"115 Junortoun Road Strathfieldsaye 3551","32051363","BGO013","22kV AC","Rural Short"," - dropper / bridge","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0011977","20201026PWA_03","Customer reported a transformer across the road has caught on fire, fire is now out but there is still a burning smell and smoke.\nsupply is out, CFA attended. \nOn arrival crew found HV leads had failed\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - switch (earth)"]
[17,59,"2020-10-19","10:00",-38.355761000000001,144.28825599999999,"21 BROADBEACH ROAD,JAN JUC,VIC,3228","30074968","WPD021","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0011991","20201027PWA_01","Emergency Services reported a fire on black box on pole at the incident location. \nUpon arrival a Powercor crew found the melted fuse box on the pole that was smoking.\nhere were no injuries or ground fire.",null,null," - switch (FuseSaver)"]
[17,60,"2020-10-20","16:45",-37.38843,143.33548999999999,"354 Eurambeen - Raglan Road Raglan","32001351","BAS011","22kV AC","Rural Long"," - transformer (pole mounted)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0011942","20201021PWA_01","Following Feeder operation , fault crew advise that a transformer failed at incident location\nThe EDO fuses did not operate allowing the earthing system on the Substation to short the 22kV to ground.\nSparks dropped from above as attempts were made to energise BAS011 feeder started a small fire - approx. 1.5m x 6m in size - to start smoldering in the wet grass at the base of the pole.\nThe transformer failure  occurred whilst REFCL stress testing was being undertaken.\nThere was no injuries reported or third party property damage.\n\nThe small fire extinguished in the wet grass.  \n\nThere was no other damage, and no injuries caused by this incident.",null,null," - switch (any other type)"]
[17,61,"2020-10-20","10:40",-38.170746999999999,144.380064,"10 Winstanley Rd, Thomson VIC 3219","32068904","GLE031","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012122","20201112PWA_01","Service failure customer stated :\n\"Elisa calling for neighbor, Service wire has come down with a bang and sparks and is on front lawn, burn marks around wire. Lost supply. \n VicFire - Sparking conductors, fireys en route.\nFound during outage data review - no photos",null,null,"SCADA, network control and protection systems"]
[17,62,"2020-10-22","17:00",-35.813768000000003,141.99784600000001,"Albacutcha rd Rainbow 3424 (near Wembulin track)","32090895","NHL015","22kV AC","Rural Long"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0011969","20201026PWA_01","CFA reported fire at base of pole at the incident location.\nOn arrival the fault crew found a Boric Acid fuse had operated , the tube burnt through and dropped to the ground causing a ground fire of approx 1.2 HA on a road reserve.\nThere was no reported injuries of property damage.",null,null," - audio frequency load controller (AFLC)"]
[17,63,"2020-10-31","07:09",-34.212679000000001,142.017382,"960 Paschendale Ave, Merbein South VIC 3505","33106721","MBN014","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012123","20201112PWA_02","Report of pole with Transformer on it outside *** 960 Paschendale av. *** active cable was on fire. and arcing.\nfire now out. \nOn arrival crew found an EDO had hung up and burnt\nNo ground fire\nIncident found during outage data review no photos taken\nFound during outage data review - no photos of incident",null,null," - arc suppresion coil"]
[17,64,"2020-11-05","11:40",-35.984544999999997,145.67148599999999,"381 McIntyre Road Muckatah 3644","33085644","CME015","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012076","20201106PWA_01","CME015 feeder fault with report of a grass fire at incident location per ESTA.\nOn arrival crew found a tree had made contact with a HV 3/12 conductor damaging 2 strands.\nGrass fire was estimated to be 4 to 6HA, no property damage or reported injuries.",null,null," - automatic circuit recloser (ACR)"]
[17,65,"2020-11-06","19:49",-35.697153999999998,144.162926,"24 SAFES RD, GANNAWARRA VIC 3568","32033009","CHA006","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012089","20201109PWA_01","CFA called reported incident. \nUpon arrival crew made area safe and found that an HV termination arm had broken causing the  3/12 steel conductor to fall on a adjacent electric fence sparking a small grassfire 10mx2m in area along a channel bank.\nThere was no reported injuries or third party property damage.",null,null," - communications linear assets"]
[17,66,"2020-11-10","12:59",-36.298867000000001,144.64998499999999,"Behind 53 Waterman Lane, Ballendella 3561","30124238","SHP011","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012112","20201111PWA_01","Customers called to report a fallen tree over mains wire at the incident location. On arrival the crew found that a large gum tree from outside the clearance space, had suffered root plate failure on the far bank of an irrigation channel. The tree fell on the 22kV 3 phase HV conductors. There was slight charring to some of the tree branches, but no ground fire",null,null," - communications network assets"]
[17,67,"2020-11-11","21:59",-37.909669999999998,144.67725899999999,"119 Duncans Rd Service Rd, Werribee VIC 3030","30576479","WBE034","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012536","20210112PWA_05","Report of pole fire on corner of Edwards rd and Duncans rd werribee\nNo photos of incident found.\nFound during outage data review\nNo ground fire, no reported injuries or third party property damage.",null,null," - communications site infrastructure"]
[17,68,"2020-11-11","12:28",-36.156362999999999,142.245396,"74 Agip Lane, Crymelon 3393","32113024","HSM003","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"High",0.5,0.5,"INC-0012125","20201113PWA_01","Vic Emergency reported a wire down had started a grassfire at the incident location.\nOn arrival the crew found that the steel SWER conductor had been hit by lightning mid span between P60 Yellangip & Luther P1.\nThe lightning strike caused the conductor to break and fall to the ground, resulting in a grassfire of approx 300m2 in size on private property. \nThere were no reported injuries.",null,null," - field devices"]
[17,69,"2020-11-12","15:12",-36.374070000000003,141.914255,"277 Albrecht Rd Gerang Gerung, VIC 3414","32113624","NHL015","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0012135","20201113PWA_02","A \"telehandler\" had contacted HV conductors.\nPowercor is assisting ESV and Worksafe investigations.",null,null," - local network wiring assets"]
[17,70,"2020-11-13","21:07",-38.322898000000002,143.670647,"5855 Princes Hwy, Irrewarra","30056442","CLC003","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,{"$f":"IF(OR(P107=\"\",R107=\"\"),\"\",IF(AND(O107=\"within electric line construction area\",Q107=\"No forecast\"),1,P107*R107))","v":0.91999999999999993},"INC-0012144","20201126PWA_01","Customer report of a tree branch onto wires at incident location. No loss of supply had occurred.   Large private owned cypress tree has failed at root / ground level and branches were in contact with HV conductors. The following morning conductor failure had occurred with evidence of minor burning found on branch. No ground fire occurred. Controlling spur fuse operated as expected. No reports of injuries or third party property damage were received .",null,null," - master station assets"]
[17,71,"2020-11-15","13:54",-37.971665000000002,144.503252,"101-121 Rothwell Rd, Little River VIC 3211","30059454","FNS022","22kV AC","Rural Short"," - overhead conductor (bare; copper)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0012147","20201116PWA_02","At the incident time the \"Little River P5\" ACR tripped to lockout interrupting supply to 578 accounts. \nPowercor received a call advising of a wire down and fire brigade attending a grass fire at the incident site.\n When crews arrived they found a tree branch had blown from a tree located in the road reserve into the HV overhead conductors.\nThe branch caused conductor clash and started a grass fire on a rural property.\n Fire brigade contained the fire to a 40m x 60m area. \nNo injuries or third property damage was reported",null,null," - neutral earthing resistor"]
[17,72,"2020-11-16","11:30",-38.219942000000003,144.53098800000001,"1437 Bellarine Hwy, Wallington VIC 3222","33041110","DDL011","22kV AC","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0014203","20210629PWA_08","Emergency services report tree on wires has caught fire. fire brigade on site. \nCrew found large tree  had fallen and hit line (aerial vegetation fire)",null,null," - oil-filled circuit recloser (OCR)"]
[17,73,"2020-11-16","02:19",-37.091818000000004,141.052436,"18 Millards Rd, Langkoop VIC 3318","32111772","CHM011","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0012538","20210112PWA_07","Following supply failures candled fuse found at incident location\nno ground fire\nFound during OMS data review\nNo photos located",null,null," - rapid earth fault current limiter (REFCL)"]
[17,74,"2020-11-16","13:32",-38.546672000000001,143.97491400000001,"12 John St, Lorne VIC 3232",33040848,"CLC014","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0012540","20210113PWA_01","Following report of supply failure, on arrival crew found EDO fuse unit burnt.\nThere was no ground fire, no reported injuries or third party property damage.\nIncident found during OMS data review, no photos found.",null,null," - surge diverter"]
[17,75,"2020-11-16","16:23",-36.474403000000002,145.241469,"695 Dhurringile Rd, Toolamba West VIC 3614",30266285,"MNA021","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012168","20201117PWA_02","Vic Fire reported wires down and grass fire.\nWhen crew arrived, they found a large tree had fallen across all 3 HV conductors, snapping them midspan between LIS 747441 and LIS 1633.  \nA ground fire had started in area, approx 40m x 80m.   \nMinimal damage to fencing, largely caused by the tree.   Base of fallen tree approx 8m from conductor.  CFA extinguished fire.  No injuries.\n",null,null," - voltage regulator"]
[17,76,"2020-11-16","03:22",-35.624518000000002,144.091354,"365 Koondrook-Murrabit Rd, Koondrook VIC 3580",33021888,"KGT003","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0012166","20201117PWA_01","Wires down, tree branch on wire, ground fire.\nCrew found HV conductors down on a patrol between poles 45 and 46. \nCrew reported large tree branch  snapped 2 conductors, resting on third. \nSmall grass fire, no reported injuries or third party property damage.",null,null,"Public lighting"]
[17,77,"2020-11-16","04:44",-36.187134,145.115306,"Murray Valley Hwy Wyuna","31028501","KYM004","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0012146","20201116PWA_01","Report from ESTA of wires down 100m south of Bunyip Road Wyuna. \n On arrival, crew found a pole that was on fire and burnt area on the ground around the pole. \nThe top of the pole was mostly gone with the remains of the cross-arm and pole top on the ground with the conductors suspended just above ground level. \nThere was lightning activity overnight with high winds.  No injuries.  Minor damage to fence.",null,null," - brackets (major road)"]
[17,78,"2020-11-19","15:34",-37.847175999999997,144.810125,"69 Horsburgh Dr, Altona North VIC 3018","30271645","AL014","22kV AC","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012221","20201123PWA_01","Reported of grass fire, MFB on site.\nUpon arrival the crew have found that the melted HV isolator causing a grass fire approximately 18 x 4m at the base of the pole.\nThere was no reported injury or shocks as a result of this incident",null,null," - brackets (minor road)"]
[17,79,"2020-11-20","21:21",-34.486454999999999,142.36218299999999,"2770 Kulkyne Way Nangiloc 3494","32150742","RCT013","Low voltage AC (<1kV)","Rural Short"," - fuse (any other type)","two phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0012235","20201124PWA_01","Vicfire reported fuse-box on pole, NANGILOC 15, sparking arcing, started a small fire, brigade onsite, on Kulkyne Way Nangiloc.\nOn arrival crew found customers river pump on startup had blown 2 x 160A krone fuses on sub pole.\nThere was a 4m x 10m grass fire at base of substation pole.",null,null," - lamps (major road)"]
[17,80,"2020-11-20","17:52",-35.956612999999997,145.65992299999999,"428 Campbell Road Cobram 3644","33087561","CME015","22kV AC","Rural Short"," - fuse (boric acid)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012230","20201123PWA_04","Report of bird flashing over on HV fuse unit to concrete pole at incident location. \nFeeder CB reclosed.\nThe HV earth fault injected into customers fence and shed starting small fire in some dried leaves between fence and shed. \nThere was signs of arcing between shed and fence, with some minor damage to shed.\n\n\n\n",null,null," - lamps (minor road)"]
[17,81,"2020-11-21","22:06",-38.256157999999999,144.24034800000001,"495 PETTAVEL ROAD,FRESHWATER CREEK,VIC,3216","32078771","WPD014","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0012545","20210113PWA_02","Following report of supply failure, on arrival crew found a HV EDO fuse had candled.\nThere was no ground fire, no reported injuries or third party property damage.\nFound during OMS data review, no photos located.",null,null," - luminaires (major road)"]
[17,82,"2020-11-21","08:41",-35.517696000000001,143.72969000000001,"Murray Valley Highway Tresco VIC 3583 (near corner Bailey Road)","32038663","KGT004","22kV AC","Rural Long"," - pole (concrete)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0012232","20201123PWA_07","Vic Fire reported, on Murray Valley highway between near Bailey Road, base of pole on fire, caused grass fire, brigade en-route.\nOn arrival crew found a Magpie has caused grass-fire, extinguished by CFA prior to our arrival, approximately 50m2, no damage on ground or ACR on visual inspection.",null,null," - luminaires (minor road)"]
[17,83,"2020-11-22","14:47",-34.206972,142.14640800000001,"374 San Mateo Avenue Mildura 3500","33063519","MDA034","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0012238","20201124PWA_03","Customer reported truck coming into farm has clipped service line and another line, so 2 wires broken in middle, one lying on footpath, the other in grass with has caused a small fire.\nThere was no reported injuries.",null,null," - poles / columns (major road)"]
[17,84,"2020-11-22","19:57",-36.388795999999999,142.66610700000001,"362 Woods Rd, Boolite Vic 3392","32101708","STL006","12.7kV AC (SWER)","Rural Long"," - insulators","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0012237","20201124PWA_02","CFA reported pole fire.\nCrew attended and found SWER pole alight.\nCrew isolated supply and CFA extinguished fire.\nNo shocks, injuries or ground fire starts.",null,null," - poles / columns (minor road)"]
[17,85,"2020-11-22","20:50",-37.765360000000001,144.84197399999999,"42b Berkshire Rd, Sunshine North VIC 3020","32163537","SSE032","22kV AC","Urban"," - pole (wood)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012239","20201124PWA_04","MFB reported pole fire, upon arrival crew found pole top fire due to lighting strike. No HVI or ground fire.",null,null,"Other "]
[17,86,"2020-11-23","20:11",-37.839033000000001,144.661349,"120 HAMISH DRIVE,TARNEIT,VIC,3029","60183412","TNA013","Low voltage AC (<1kV)","Rural Short"," - services pit","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012254","20201125PWA_02","Customer reported electricity pit out front of property has smoke coming out of it, heard a loud bang, saw a flash from pit & pit lid has popped out. Customer also reported has no supply.  When crew arrive they found that there had been evidence of a fire in the service pit with 16mm 4 core underground service cable burnt in conduit. The crew dug faulty service cable, cut and extended the cable. No injuries or third party damage.",null,null," - connection box"]
[17,87,"2020-11-23","08:25",-37.700119999999998,143.16069899999999,"6675 Darlington-Carranballac Rd, Carranballac VIC 3361.","31016459","ART033","22kV AC","Rural Long"," - pole (wood)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0012244","20201124PWA_06","CFA member driving past, mains wire down, struck by lightening, X-arm broken, smoke, sparks, unsure if supply still on, access around okay.\nOn arrival crew advise pole has been struck by lightning and requires replacement.\nThere was no ground fire, reported injuries or third party property damage.\n\nNo ground fire. CFA report pole was on fire.",null,null," - earth / earthing"]
[17,88,"2020-11-23","06:40:00",-34.251800000000003,142.17089999999999,"3090 Sixteenth Street Irymple 3498",32140515,"MDA023","22kV AC","Rural Short"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0012288","20201127PWA_03","Vicfire reported pole fire at incident location, brigade onroute.\nCrew found insulated HV transformer leads had Burnt\nThere was no ground fire, no reported injuries or third party property damage."]
[17,89,"2020-11-26","03:59",-37.102494,144.88179299999999,"210 Panyule Rd, Pyalong VIC 3521","32044811","WND013","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0012546","20210113PWA_03","Following report of supply failure, on arrival crew found a burnt EDO fuse .\nThere was no ground fire, no reported injuries or third party property damage.\nIncident found during OMS data review ."]
[17,90,"2020-11-27","19:58",-37.280431999999998,142.95978199999999,"13 Heath St, Ararat VIC 3377","32118861","ART023","22kV AC","Rural Long"," - fuse (powder filled)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012547","20210113PWA_04","Report of supply failure, on arrival crew found a candled power filled fuse.\nThere was no ground fire, no reported injuries or third party property damage.\nFound during OMS data review\nNo photos found",null,null,"Extra low voltage AC (<50V)"]
[17,91,"2020-11-28","16:30",-35.441079999999999,143.614791,"Murray Valley, Lake Boga VIC 3584 ( near intersection Long Lake Rd ","30100938","SHL005","22kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Extreme",3.5,0.70000000000000007,"INC-0012300","20201130PWA_02","VicFire reported wire down and ground fire at incident location. \nUpon arrival fault crew found that a HV  conductor had fallen and ignited a ground fire of approximately 250M x 100M in size, possible damage to farm machinery, bailed hay burnt, \nCFA managed to extinguish fire before it reached structures.\nThere were no reported injuries\nNAO requested crew to mark further repairs to other phases if not rectified during repairs, all 3 phases of slack span have joins using splices.\nNAO also requested failed conductor be quarantined for failed asset investigation.",null,null,"Low voltage AC (<1kV)"]
[17,92,"2020-11-28","08:00",-35.782010999999997,144.227001,"70 Mathers Road, Cohuna VIC 3568 ( 200M south of Weymouths Rd )","30025562","CHA006","22kV AC","Rural Short"," - surge diverter","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Extreme",3.5,0.70000000000000007,"INC-0012301","20201130PWA_03","VicFire reported fire associated with electricity assets, upon arrival crew found that a crow had flashed over on substation pole \"Mates 1\", the deceased bird fell to ground igniting the grass.\nA ground fire of approximately 100m x 30m resulted, CFA attended and extinguished fire.\nThere was no reported injuries",null,null,"2.2kV AC"]
[17,93,"2020-12-01","08:40",-38.127887000000001,144.34573,"44 Weddell Road North Geelong 3215","32071840","GL011","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012326","20201202PWA_02","Energy Safe reported a customer called, stating a neighbors service line down across the yard, was arcing and sparking at incident location. \nOn arrival crew found neutral screen service burnt down at P.O.A.\nsmall burnt area on front lawn.\nThere was no injuries or third party property damage.",null,null,"6.6kV AC"]
[17,94,"2020-12-01","15:19",-37.950453000000003,141.62558999999999,"517 Condah-Hotspur Lower Rd, Condah VIC 3303","32125483","HYT011","12.7kV AC (SWER)","Rural Short"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0012320","20201202PWA_01","Vicfire reported wire down and caused grass fire.\nOn arrival the crew found a blue gum tree in a plantation had fallen onto the SWER line bringing down conductor from P39 to P41 starting a fire. \nArea burnt was roughly 100x10m.\nNo reported injuries",null,null,"11kV AC"]
[17,95,"2020-12-05","13:48",-36.004238999999998,146.02732900000001,"LOT-28,22 LAKEVIEWS CIRCUIT,YARRAWONGA,VIC,3730","30247812","CME014","Low voltage AC (<1kV)","Rural Short"," - fuse (any other type)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0014197","20210629PWA_05","customer reported  fire in meter box at fuse location and fu se melted. fire out now.\nattending crew found melted fuse\nfound during record check no images, reported as fire on balance of probability",null,null,"12.7kV AC (SWER)"]
[17,96,"2020-12-05","13:38",-36.305700999999999,145.42922200000001,"910 Goulburn Valley Highway CONGUPNA","33093652","SHN011","66kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0012347","20201207PWA_04","High winds caused tree branch to break and fall across conductors Pole # 38 SHT-NSF 66KV LINE no fire on the ground and tree branch showed signs of smoldering.\nThere was no ground fire, no reported injuries or third party property damage.\n",null,null,"22kV AC"]
[17,97,"2020-12-05","14:28",-37.797638999999997,144.83542,"32 Central Avenue, Sunshine 3020.","30107037","SSE034","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012342","20201207PWA_01","Fire brigade reported a grass fire .  \nOn arrival the crew found that the white phase HV conductor had broken and was laying on the top of 2  LV conductors. \nThere was a small fire on the nature strip and on the grass inside the front yard of #32 Central Avenue.  \nLEI was on site inspecting LV for possible HV injections, at the time of this report all supply was ok and no HV injection found.\nThere were no shocks or injuries reported.\n",null,null,"33kV AC"]
[17,98,"2020-12-05","13:01",-37.692259,142.99471199999999,"728 Glenelg Hwy, Westmere 3351",30083861,"ART033","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0012344","20201207PWA_03","Fire Comm reported a fire at the incident location. \nOn arrival, the crew found that a tree branch (from outside the clearance space) had fallen across an adjacent 22kV line causing the line to break and fall to the ground resulting in a ground fire (Approx. 600 sqm) on the road reserve and adjacent paddock.\nThere were no reported injuries.",null,null,"66kV AC"]
[17,99,"2020-12-06","19:58",-36.293201000000003,145.439695,"3490 Katamatite-Shepparton Main Rd, Congupna VIC 3633","32188601","SHN011","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012578","20210118PWA_01","On arrival crew found EDO fuse burnt in half.\nNo ground fire\nIncident found during OMS data review, no photos",null,null,"132kV AC"]
[17,100,"2020-12-07","02:42",-38.167313999999998,144.51279299999999,"21 Manresa Rd, Curlewis VIC 3222","32081619","DDL014","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0012580","20210118PWA_02","Following report of supply failure , crew found a candled EDO fuse.\nNo ground fire\nincident found during OMS data review, no photos found",null,null,"220kV AC"]
[17,101,"2020-12-07","12:21",-35.118124999999999,142.89373499999999,"913 Robinvale-Sea Lake Road Cocamba 3546","32146169","OYN003","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0012355","20201209PWA_01","VicFire reported a pole fire, Robinvale-Sea Lake Road Cocamba, near silos, fire brigade enroute.\nCrew found pole burnt off near top of pole and small burnt grass area of approximately 10m2.\nThere was no injuries or third party damage.",null,null,"330kV AC"]
[17,102,"2020-12-07","05:03",-36.134650000000001,141.43476799999999,"16 Maude St, Yanac VIC 3418, Australia","32108983","NHL031","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,{"$f":"IF(OR(P139=\"\",R139=\"\"),\"\",IF(AND(O139=\"within electric line construction area\",Q139=\"No forecast\"),1,P139*R139))","v":1},"INC-0012343","20201207PWA_02","Fire comm reported a fire on a pole at the incident location. \nOn arrival the crew found that a pole fire had occurred on a three phase pole which burnt the top of the pole and cross arm. \nThere was no ground fire. \nThere were no reported injuries shocks or third party property damages. ",null,null,"500kV AC"]
[{"$f":"COUNTA(C140:O140,Q140,T140:V140)","v":17},103,"2020-12-09","07:56",-35.042563000000001,143.32427200000001,"4318 Murray Valley Hwy, Piangil VIC 3597","30268957","SHL002","22kV AC","Rural Long"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O140=\"\",\"\",IF(O140=\"LBRA only\",0.2,IF(O140=\"HBRA only\",1,IF(O140=\"within electric line construction area\",19.8,IF(O140=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"Low-moderate",{"$f":"IF(Q140=\"\",\"\",IF(Q140=\"No forecast\",0.1,IF(Q140=\"Low-moderate\",0.2,IF(Q140=\"High\",0.5,IF(Q140=\"Very high\",1,IF(Q140=\"Severe\",2,IF(Q140=\"Extreme\",3.5,5)))))))","v":0.2},4.0000000000000008E-2,"INC-0012581","20210118PWA_03","Report of HV leads sparking and catching fire.\nNo ground fire\nfound during OMS data review\nno photos found",null,null,"Extra low voltage DC (<120V ripple free)"]
[17,104,"2020-12-10","17:44",-36.454740999999999,145.204465,"420 Winter Rd, Tatura VIC 3616, Australia","33089564","MNA021","22kV AC","Rural Short"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012412","20201216PWA_02","Report r3ecieved of grass fire, CFA onsite\nUpon arrival crew found that a Boric Acid fuse had candled and started a small fire (30sqm) at the base of the pole. There was no reported injuries , a few fence posts burnt along driveway.",null,null,"Low voltage DC (<1.5kV)"]
[17,105,"2020-12-10","10:21",-37.838272000000003,144.81817699999999,"29 Pinnacle Rd, Altona Nth 3025","30257571","BLT017","22kV AC","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012375","20201211PWA_01","Emergency Services reported a wire down and sparking at the incident location. \nOn arrival the crew found that a HV Ampac connection had failed on the east side of pole at incident location.\nThe helical termination was damaged, resulting in the HV conductor falling to the ground and starting a small grassfire approx 0.2m2 in size. \nA HVI was suspected.\nThere were no reported injuries or third party damage.",null,null,"600V DC"]
[17,106,"2020-12-11","15:00",-34.744027000000003,143.03401199999999," Ferry Rd cnr of Paul Ln  Boundary Bend 3599",30317071,"BBD014","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012382","20201214PWA_02","A Powercor crew attending a fault found a dead bird contacted the load side of ACR at the incident location. \nThere was a ground fire approx. 30*10 Sqm .\nNo other damage found. A black mark on a conductor found.\nThere was no reported injuries\n\n85424-29 22kV PIAMBIE P198 ACR operated.",null,null,"1500V DC"]
[17,107,"2020-12-13","21:41",-37.684488000000002,144.56691499999999,"Roadside Lighting pole in front of 523-531 High St Melton, VIC 3337, Australia","30153816","MLN023","Low voltage AC (<1kV)","Rural Short"," - luminaires (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012409","20201216PWA_03","MFB reported flames on top of a pole at incident location.\nAn attending Powercor Fault crew  identified a burning public lighting lantern head on a roadside lighting pole.\nThere was no ground fire, no reported injuries or third party property damage.",null,null,"Earthing cable"]
[17,108,"2020-12-13","16:00",-37.442027000000003,143.37844000000001,"140 Skipton Rd, Beaufort VIC 3373","32008382","BAS011","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0012399","20201215PWA_01","FireComms, tree down and wires down - grass fire started was reported\nOn arrival crew found an Excavator had made contact with the 3 phase Hv line causing 2 conductors to break and contact the ground. \nThis resulted in a ground fire\nThere was no reported injuries"]
[17,109,"2020-12-14","16:38",-34.450313000000001,142.28082900000001,"749 BROWNPORT RD - IRAAK VIC 3494","30142455","RCT013","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0012459","20201223PWA_02","VicFire - reported fire near Powercor assets at incident location.\nCustomer advised of fire around pole when power went out.\nUpon arrival crew found one EDO fuse had hung up and candled, there was a small grassfire (10mx20m).\nCrew suspects damage from prior lightning strike was the main cause of fuse failure.\nCFA no longer on site.\nThere were no reported injuries. \n"]
[17,110,"2020-12-15","20:27",-35.929366000000002,145.47853900000001,"12 NUMURKAH ROAD,STRATHMERTON,VIC,3641","33083429","NKA003","22kV AC","Rural Short"," - switch (any other type)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012414","20201217PWA_01","Report received of small grass fire at base of pole at incident location.\nOn arrival crew found a bird has flashed over on switch structure igniting grass below.\nThere was no reported injuries",null,null,"single wire earth return (SWER)"]
[17,111,"2020-12-15","20:40",-38.261387999999997,141.616546,"5 Denhill Ct, Bolwarra VIC 3305","33056973","PLD001","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0012584","20210119PWA_01","Report of supply failure.\nOn arrival crew found EDO barrel burnt and broken and dead possum at base of pole.\nThere was no ground fire.\nIncident found during oms checks, no photos found.\n",null,null,"single phase"]
[17,112,"2020-12-16","01:22",-37.794094999999999,141.53094400000001,"3362 Portland-Casterton Rd, Digby 3309","32123265","HTN002","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0012419","20201217PWA_04","Vicfire reported a pole fire at the incident location. On arrival the crew found that the very top section of P4 Digby West Spur (LIS-716240) had burnt off, at around the location of the HV disc insulators of the type 3 angle. The conductor fell to the ground, and the protection operated. There were no reported injuries, third party damage or ground fires.",null,null,"two phase"]
[17,113,"2020-12-16","10:00",-38.000176000000003,141.43964399999999,"4321 PRINCES HIGHWAY, Greenwald, VIC, 3304  (HVTee of pole 50m north of this address)","32132008","PLD003","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0012420","20201217PWA_05","Call recieved that on A1 Princess hwy, between Lions and Greenwald truck drivers report wire down low enough trucks cant get under, and cars are just clearing it, 10 mtrs high, location is 50 meters off Cowlands rd on the A1 hwy. calling ses, \nTraffic banked up as unable to get through. \nOn arrival crew reported pole fire started at eye bolts, has burnt thru pole and center phase conductor and insulator assembly have broken away from pole.\nConductor has presented a hazard as low clearance across the Princess Highway and trucks cannot pass under. The low conductor is alive at 22kV. \nPrincess highway closed. Significant delays for motorists using the Highway.\n\nNo ground fire, no reported injury.",null,null,"three phase"]
[17,114,"2020-12-16","06:30",-38.728952999999997,143.697677,"6080 Great Ocean Road, Apollo Bay 3233","32064807","CLC007","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0012418","20201217PWA_03","A customer called to report a pole fire at the incident location. On arrival the crew found that P584 Gellibrand Line (LIS-16721) had partly burnt around the top metre of the pole, from suspected salt build up due to the proximity to the sea (approx 200m), combined with light rain. The conductors and crossarm remained aloft, and there was no reported ground fire or other damage."]
[17,115,"2020-12-18","09:00",-37.817557000000001,144.81758400000001,"43 Little Boundary Rd, Laverton North VIC 3026","30115780","BLT016","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012432","20201218PWA_01","A customer called to report loud explosion sound on pole out front of unit block, street light and wires now hanging down over the street and may hit passing trucks. \nCrew advise pole fire at incident location, a high voltage cross-arm has burnt thru at strap bolt and broken away from pole. \nPole fire self extinguished.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,116,"2020-12-19","06:59",-36.430197999999997,145.11371700000001,"515 Springvale Road, Grigarre East VIC 3616","33097486","SHP014","22kV AC","Rural Long"," - switch (disconnector/isolator)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012446","20201221PWA_03","Vic emergency reported a fire commenced by Powercor assets.\nUpon arrival fault crew found that a bird had flashed over on a isolator resulting in burning material falling to ground and commencing a ground fire of 4m x 11m in size.\nThere was no reported injuries or third party property damage.",null,null,"Negligible: no ground fire"]
[17,117,"2020-12-19","11:17",-37.048822000000001,144.14761799999999,"514 Muckleford - Walmer Road, Muckleford VIC 3451","33026570","CMN004","22kV AC","Rural Long"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","within electric line construction area",19.8,"Low-moderate",0.2,3.9600000000000004,"INC-0012444","20201221PWA_04","A customer reported sparking insulator and ground fire at the incident location.\nUpon arrival fault crew found that a Boric Acid fuse had candled and dropped burning material to ground resulting in a ground fire of approximately 40M x 120M in size.\nCFA attended and extinguished fire, no damage to 3rd party property.",null,null,"Localised: less than 10 sq.m"]
[17,118,"2020-12-20","17:36",-34.194923000000003,142.07947100000001,"18 Mena Road, Birdwoodton VIC 3505","33061867","MBN032","22kV AC","Rural Short"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012447","20201221PWA_05","VicFire reported fire associated with Powercor assets at incident location.\nUpon arrival crew found that a crow had flashed over on a 5 shed bridging insulator on concrete strain pole. Material ejected due to electrical arc commenced ground fire at base of pole burning approximately  4m x 10m of grass at road verge.\nNo 3rd party damage or injuries.",null,null,"Small: 10 - 1000 aq.m"]
[17,119,"2020-12-21","19:10",-37.104537000000001,142.73980900000001,"52 Ganawarra Rd, Black Range 3381","32114974","STL007","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0012449","20201222PWA_02","A report was received from the CFA that a power lines was down and a pole fire had occurred at the above location. \nA Powercor crew attended and determined that a X-arm fire occurred on Burrong Basin Pole 4.\nThe x-arm had burnt through at the x-arm strap bolt on the road side. \nThere was no ground fire start, no reported injuries or third party property damage.",null,null,"Medium: 1000 sq.m - 10 ha"]
[17,120,"2020-12-27","15:27",-36.271154000000003,144.53571099999999,"7 SINGER ROAD,LOCKINGTON,VIC,3563","30349248","SHP012","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0014200","20210629PWA_06","vic fire reported a  tree over conductors which is on fire, - cnr lockington and singer roads \nattending crew  found minor damage to steel conductor\n\nfound during record check no images, reported as fire on balance of probability / customer report information ",null,null,"Large: more than 10 ha"]
[17,121,"2020-12-27","20:00",-37.830748999999997,144.84322800000001,"423 Blackshaws Road, Altona North, 3025","30114530","BLTS-TYA","66kV AC","Unknown"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0012472","20201231PWA_01","FireComms, pole fire - MFB attending, stating pole is still sparking\n\nOn arrival the PCA Faults Crew have advised that there was Sparking / Pole fire on 66kV Pole 40 LIS-4485.  \n\nThe Sparking/Pole fire was contained to the top 66kV Vertical Anchor Eye-bolt connection onto the Pole on the BLTS-AL 66kV Circuit, which may have resulted from the drizzling rain in the evening and tracking across the 66kV disc insulators."]
[17,122,"2020-12-27","17:40",-38.267570999999997,144.49337199999999,"9 Fishermans Walk (cnr Taits Rd) Barwon Heads",30071999,"GLE013","22kV AC","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0012476","20201231PWA_04","Vic Fire notified Powercor of a pole fire caused by a branch on wires at the incident address. Powercor also started to receive a number of calls from customers advising of loss of supply in the area. When crews arrived on site they found a branch from a very large gum tree  had fallen across the HV conductors, mid span between P6 & P7 Taits Rd"]
[17,123,"2020-12-28","10:31",-37.830748999999997,144.84322800000001,"421 Blackshaws Rd, Altona North VIC 3025","30114530","BLTS-TYA","66kV AC","Unknown"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012585","20210119PWA_02","Report of pole fire at incident location.\nNo ground fire\nIncident found during oms data review",null,null,"Started in or originated from a distribution system"]
[17,124,"2020-12-28","13:31",-37.700223999999999,144.57546199999999,"57 STATION ROAD,MELTON SOUTH,VIC,3338","32174272","MLN011","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012473","20201231PWA_02","GREG ESV, FIRE AT POA PER CUST REPORT TO ESV   \n\nOn arrival the PCA Faults Crew have advised that the 2/C Neutral Screened Service Cable had burnt out where it was crutched.  \n\nThe PCA Faults Crew, then preceded to replace the burnt out n/s s/c, however they had detected illegal wiring and found bypass cables at the meter/switchboard.  As a result of this a customer defect notice was issued.",null,null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system"]
[17,125,"2021-01-01","13:35",-36.348281999999998,145.06795,"265 Kyabram-Cooma Rd, Kyabram VIC 3620","30129002","KYM003","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012483","20210104PWA_01","CFA reported tree branch over HV conductors and fire at the incident location. Upon arrival fault crew found that reported branch had burnt through and fallen clear of the line, no ground fire commenced as ground conditions were wet due to heavy rain.\nTree branch came from trees in adjacent span P18 > P19 Anderson spur line, which fell onto line in strong winds associated with thunderstorm activity, tree was outside clearance space.\n",null,null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system"]
[17,126,"2021-01-02","16:27",-34.222292000000003,142.10739100000001,"3041 Walnut Ave, Mildura VIC 3500","30098922","MBN031","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012485","20210104PWA_03","PAL employee reported pole fire at the incident location. Upon arrival found that a HV intermediate x-arm had burnt though at the x-arm King bolt, HV conductors resting on the LV subsidiary x-arm beneath.",null,null,"Started by lightning striking a distribution system or a part of a distribution system "]
[17,127,"2021-01-02","11:10",-34.199007000000002,142.14810399999999,"816 Fourteenth St, Mildura VIC 3500","31021407","MDA032","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012486","20210104PWA_04","Customers reported smoke and flames from a Powercor pole at the incident location. Upon arrival fault crew found that a HV strain x-arm on switch pole 19404 had burnt off at the footpath side strain insulator eye bolt, the HV conductor remained aloft but may have made contact with LV subsidiary circuit below (MDA32 reclose ), LEI arranged to check installations for HVI",null,null,"Started by any other thing forming part of or coming into contact with a distribution system"]
[17,128,"2021-01-02","12:04",-34.198256999999998,142.16976,"9 Scott Cres, Mildura VIC 3500","31021144","MDA024","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012487","20210104PWA_05","SCADA alarm advised MDA24 tripped to lockout, fault crew found cause at incident address being pole top fire at LIS 10405 \"Scott Etiwanda Sub 4\"\nPole top assembly had burnt off including x-arm at kingbolt position, causing HV conductors to fall onto the LV subsidiary x-arm below,\n",null,null,"Otherwise started by a distribution system"]
[17,129,"2021-01-03","14:07",-36.397602999999997,145.33153100000001,"20 Excelsior Ave, Mooroopna VIC 3629","33093873","MNA021","22kV AC","Rural Short"," - surge diverter","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012484","20211008PWA_01","CFA reported a ground fire that commenced due to fault related with PAL assets at the incident address. Upon arrival crew found that a bird had flashed over on the surge diverter on a gas switch structure ( concrete pole ).\nDeceased bird fell to base of pole igniting a ground fire of approximately 10M x 30M in size. \nCFA extinguished the grass fire on the road verge.\nNOTE: Old record 20210104PWA_02  in OSIRIS was corrupted. New record 20211008PWA_01 had to be created in OSIRIS. Refer to emails. Updated OSIRIS number in RIN."]
[17,130,"2021-01-06","23:34",-36.087139000000001,145.69425000000001,"4824 Bennalla Tocumwal Road, Katamatite VIC 3649","33078550","NKA001","22kV AC","Rural Long"," - switch (disconnector/isolator)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0012526","20210108PWA_02","Passer by reported ground fire in vicinity of PAL assets at the incident location. Crew could not find damage during initial inspection, \nDaytime inspection revealed flashover had occurred on center phase line side isolator, most likely caused by possum."]
[17,131,"2021-01-07","12:19",-36.937942999999997,141.450579,"7409 Wimmera Highway, Edenhope 3318","30319123","CHM011","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0012525","20210108PWA_01","A customer reported mains wire brought down by a tree branch at the incident location. On arrival the crew found that an excavator being operated by the land owner, had knocked down a tree resulting in the tree hitting the single phase HV conductor between P2 Oak Park Spur (LIS-21540) & P3 Oak Park Spur (LIS-825149). One of the HV conductors fell to the ground, starting two small grassfires approx 600m2 total in size on private property",null,null,1]
[17,132,"2021-01-08","10:00",-34.728422999999999,142.953497,"Berg Lane Lake Powell 3597","30245599","BBD013","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012531","20210112PWA_01","REC reported supply issue , pump has been tripping, HV Fuse is blown. Crew found a bird had caused a flashover and started a small 4m2 grass fire",null,null,2]
[17,133,"2021-01-08","12:58",-37.863478000000001,144.73133300000001,"77 Forsyth Road Hoppers Crossing 3029","30115817","LV008","Low voltage AC (<1kV)","Urban"," - overhead service conductor (commercial / industrial)","single phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012533","20210112PWA_02","VIC EMERGENCY reported a truck has brought down O/H wire and resting on top of truck smoking, truck driver clear of vehicle, emergency services en-route, REF: 2916. Crew found a container crane Truck bought down 4 core service to 83 Forsyth Road Truganina, CFA put out small grass fire 5m x 1m, customer defect issued for broken POA.",null,null,3]
[17,134,"2021-01-09","19:49",-37.368245999999999,144.00188399999999,"324 Daylesford-Clunes Road, Blampied","33001613","BAN009","Low voltage AC (<1kV)","Rural Long"," - dropper / bridge","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,{"$f":"IF(OR(P171=\"\",R171=\"\"),\"\",IF(AND(O171=\"within electric line construction area\",Q171=\"No forecast\"),1,P171*R171))","v":0.91999999999999993},"INC-0012527","20210111PWA_01","Vicfire reported a fire start at this location. CFA attended and extinguished ground fire. A crew attended and found a over heated LV isolator lead had dropped hot materials to he ground, starting a ground of 5mx5m at the base of the pole",null,null,4]
[17,135,"2021-01-10","17:19",-36.342021000000003,144.75248400000001,"304 Zegelin Road Fairy Dell 3561","33079887","KYM001","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012529","20210111PWA_02","Customer reported box on the pole is completely burnt out, approximately 100m burnt, CFA have attended, pole is on the road, lost power at both house and shed. Crew found fire burnt area on road side, ",null,null,5]
[17,136,"2021-01-11","13:00",-37.762805999999998,144.8339,"20 Ayton St, Sunshine Nth 3020",30118234,"SSE012","Low voltage AC (<1kV)","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0012534","20210112PWA_03","Customers reported that a truck hit the mains wire at the incident location. On arrival the crew found that an unknown truck contacted a communications cable, knocking it up into the LV mains above. The catenary wire of the communications cable appears to have contacted the Live LV overhead above it, resulting in a small grassfire on the nature strip of approx 10m2 in size. All conductors remained aloft. ",null,null,6]
[17,137,"2021-01-11","12:26",-38.109831999999997,144.261638,"431 Fyansford-Gheringhap Rd, Stonehaven 3218","33042631","GL012","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0012537","20210112PWA_06","everal reports were received by Powercor, including the following: 11-JAN-2021 13:09:52, Sam from ESV, Sam from ESV recd report from Dean 0409158082 stating mobile crane has hit o/h CNR Friend In Hand rd.   no report of injuries or wires down.\n\nSubsequent investigations found small fire at foot of  the crane stabiliser had been extinguished.\nOn arrival at the incident location the crew found that a crane unloading concrete culverts on the side of the road  had contacted the roadside single phase HV conductor of Ballarat Dogrocks Spur between P1 (LIS-15762) & P2 (LIS-62466).",null,null,7]
[17,138,"2021-01-11","23:56",-38.174525000000003,142.921177,"2073 Darlington-Terang Rd, Noorat, 3265",31018467,"TRG022","22kV AC","Rural Long"," - dropper / bridge","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0012535","20210112PWA_04","VIC Fire reported wires arcing and sparking, started a grass fire. Fire brigade en route. On arrival the crew found a bridge had broken and was arcing across the gap causing sparks which had started a grass fire approx. 50m x 50m",null,null,8]
[17,139,"2021-01-13","10:18",-37.412609000000003,142.771367,"Andrews Lane Willaura North 3379","30086557","ART033","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0012558","20210113PWA_05"," fire reported at incident location. \nCrew found a bird (ibis) had contacted the HV conductors between MOSTON 63 and 64, causing a HV ph-ph fault, starting a grass fire when it fell to ground,",null,null,9]
[17,140,"2021-01-14","01:20",-36.148687000000002,144.79564500000001,"Corner Lady Augusta Road and Brown Road Echuca Village 3564","33087169","ECA005","22kV AC","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012567","20210115PWA_01","FireComms reported a tree has brought down lines, grass fire spreading, CFA enroute. Crew found a large tree from the opposite side of the road had brought down  1 HV conductor.",null,null,10]
[17,141,"2021-01-15","17:20",-36.600411000000001,144.41196500000001,"383 Clays Rd, Bagshot North VIC 3551, Australia (Cnr willmans rd and clays rd - bagshot)","30570325","EHK031","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0012600","20210121PWA_01","Report received of Tree falling across line starting a fire.\nOn arrival crew found that a tree from outside clearance space had fallen across conductors.\nA grass fire of around 0.4 HA occurred.\nThere was no reported injuries.",null,null,{"$f":"Y177+1","v":11}]
[17,142,"2021-01-20","23:21",-34.182341000000001,142.15588500000001,"83 Walnut Ave, Mildura VIC 3500, Australia","34005248","MDA032","Low voltage AC (<1kV)","Urban"," - underground service cable (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012606","20210121PWA_02","Report received of pole smoking and sizzling sound.\nCFA attended and extinguished small fire at base of pole.\nOn arrival crew found burnt out connection at base of roundabout steel public lighting pole\nThere was no injuries or third party property damage.\n ",null,null,{"$f":"Y178+1","v":12}]
[17,143,"2021-01-22","10:42",-36.433742000000002,145.01329999999999,"56 Baldwin Rd, Stanhope VIC 3623",30233398,"SHP012","22kV AC","Rural Long"," - dropper / bridge","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0012620","20210125PWA_01","Two G&B crews had installed a new HV switch on a strain pole and were in the process of removing the 22KV bridges.\nOne of the G&B Lineworkers was holding the bridge and the other Lineworker was to cut the bridge.\nin the process of cutting motion the cutters were moved downwards causing the bottom of the cutters to make contact with an eye bolt on the cross arm.\nA loud bang and spark was observed, this also started a small fire at the base of the pole (approx 4 square meters) and was extinguished quickly by the safety observer.\nFeeder tripped.\nNo injuries",null,null,13]
[17,144,"2021-01-22","22:59",-37.602277999999998,141.71767600000001,"227 Racecourse Rd Coleraine","32132629","HTN006","22kV AC","Rural Long"," - dropper / bridge","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0012623","20210125PWA_04","A customer reported loss of power.\nA crew was dispatched to investigate. \nOn arrival the crew found that the fault was at fused tee off pole 305.\nA tee off tee-off flex had broken loose and made contact with the steel tee-off crossarm and possibly the stay king bolt. \nThis was causing an internal pole fire/smoldering.\nThere was no ground fire, no reported injuries or third party property damage.\n\nThe crew reported the pole fire to CFA who attended the site to put out.\n\nThe crew made necessary repairs to make safe.\n\nNo ground fire, injuries, shocks or 3rd party property damage reported.",null,null,14]
[17,145,"2021-01-23","11:47",-36.466377000000001,145.22276099999999,"1450 Murchison-Tatura Rd, Tatura VIC 3616",33094267,"MNA021","22kV AC","Rural Short"," - insulators","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0012622","20210125PWA_03","Vic Fire reported grass fire at above address.   On arrival, crews found that what appears to be a \"bathurst burr\" (weed) was stuck on HV conductor at insulator and evidence of HV flashover marks on the crossarm",null,null,15]
[17,146,"2021-01-25","12:20",-36.347200999999998,145.238158,"63 Hooper Rd, Mooroopna North West VIC 3616.",30242248,"MNA014","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0012637","20210125PWA_06","VIC EMERGENCY, Tree on wire - started fire \nCrew advise gum tree down over high voltage line MNA014, feeder tripped to lockout. \nWires down.\nSmall fire started underneath line extinguished by the fire brigade.\nNo injuries caused by this incident.",null,null,16]
[17,147,"2021-01-25","10:35",-37.414091999999997,143.89562900000001,"3 Alexander Court, Creswick, 3363.","60071837","BAN009","Low voltage AC (<1kV)","Rural Long"," - LV pillar","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0012636","20210125PWA_05","Crew advise a connection in a pillar overheated. \nDry material near the pillar ignited causing a small fire about 1m2 in area.\nLow voltage fuse blown due to the fault in the pillar.\nFire extinguished using a nearby garden hose.\nNo injuries resulted.\n",null,null,17]
[17,148,"2021-01-25","21:14",-34.290486000000001,142.236368,"728 Woomera Ave, Red Cliffs VIC 3496","30098458","RCT023","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Severe",2,2,"INC-0012642","20210127PWA_02","Report from firecom of explosion at transformer.  \nOn arrival, crew found HV cross-arm had burnt through at centre phase pin insulator. \nThere was no ground fire, no injuries or third party damage.",null,null,18]
[17,149,"2021-01-25","23:51",-37.044096000000003,143.73277400000001,"32 Barkly St, Maryborough VIC 3465","30017423","MRO004","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0012647","20210127PWA_05","Fire com reported pole fire. \nOn arrival crew found burnt end of crossarm on HV strain and HV conductor into LV conductor.\nPossible HVI.  \nNo known injuries or ground fire.\n",null,null,19]
[17,150,"2021-01-25","19:09",-38.370334999999997,142.47071099999999,"904 Raglan Parade, Warrnambool","30134951","WBL006","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012641","20210127PWA_01","CFA reported pole at the incident location.\nOn arrival crew found an LV krone box and junction box had caught fire.\nFSD and junction box replaced and repairs made.\nThere was no ground fire, no reported injuries or third party property damage.",null,null,20]
[17,151,"2021-01-26","02:43",-35.378135,143.454466,"Woorinen-Goschen Rd, Swan Hill West VIC 3585","32160374","SHL001","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0012644","20210127PWA_04","Report of pole fire at incident location.\nOn arrival crew found top of pole burnt through, HV centre phase had fallen to ground with insulator. \n No ground fire, no injuries, no third party damage."]
[17,152,"2021-01-26","04:27",-35.400775000000003,142.45447999999999,"Corner of Faulkner Rd and Patchewollock-Sea Lake Rd, Speed East 3488 ( Patchewollock-Sea Lake Rd, Speed VIC 3488, Australia)","32160418","OYN005","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0012643","20210127PWA_03","Pole fire was reported at the incident location.\nOn arrival crew found HV tee pole on fire.\nCFA attended to extinguish the fire. \nSome embers had fallen to ground however the ground was wet due to overnight rain - there was no ground fire.\nThere was no reported injuries or third party property damage.\n\nThe pole was to be replaced and repairs made. The site was made safe.\n\nNo 3rd party damage, shocks or injuries reported.\n"]
[17,153,"2021-01-28","09:40",-34.128861000000001,141.89324099999999,"Lot 1 Lock 10 Road, Wargan VIC 3505.  (WAKEFIELD FILTER 2 25kVA sstn)","33061714","MBN031","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0012666","20210129PWA_01","Customer reported fuse is down, fuse was on fire, was shooting flames 5 mins ago.  \nOn arrival crew advise high voltage fuse has candled causing small fire which self extinguished after about five minutes.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,154,"2021-01-29","06:00",-38.094870999999998,144.324805,"99 Kansas Ave, Bell Post Hill VIC 3215.    LIS 48600.","30067959","CRO022","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",{"$f":"IF(Q191=\"\",\"\",IF(Q191=\"No forecast\",0.1,IF(Q191=\"Low-moderate\",0.2,IF(Q191=\"High\",0.5,IF(Q191=\"Very high\",1,IF(Q191=\"Severe\",2,IF(Q191=\"Extreme\",3.5,5)))))))","v":0.2},{"$f":"IF(OR(P191=\"\",R191=\"\"),\"\",IF(AND(O191=\"within electric line construction area\",Q191=\"No forecast\"),1,P191*R191))","v":4.0000000000000008E-2},"INC-0012668","20210129PWA_02","As per brigade pole fire outside address HV cross-arm burning.\nLarge bang and flash of light from pole LIS 48600. Pole now has orange embers falling from it, reaching the ground. \n Currently raining. Assets on the pole are now glowing red.\n HV cross-arm has burnt through, broken arm resting on LV cross-arm with conductor still tied in. Could be  HV injection.\nCrew advise high voltage cross-arm has burnt through at the cross-arm strap, \nThere is no ground fire and no reported injuries due to this incident."]
[17,155,"2021-01-29","07:43",-37.602102000000002,143.69465700000001,"80 Kent Drive, Haddon 3351","33001899","BAS033","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0012702","20210201PWA_01","A customer reported the following: Black boxes on pole below transformer are currently on fire. Flames close to transformer. Raining and wet conditions outside. Access ok. Supply off.\n\nOn arrival the crew found that connections in a 3 phase FOLCB on the Substation had overheated, and the box had caught fire and dropped debris to the ground. \nThere was no ground fire due to heavy rain at the time of the incident. There were no reported injuries or third party damage."]
[17,156,"2021-02-02","13:07",-36.263781000000002,143.07212000000001,"Banyenong-Jeffcott Road Jeffcott North 3480 (between Old Bus Road and A Campbells Road)","33009579","CTN006","12.7kV AC (SWER)","Rural Long"," - fuse (boric acid)","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0012740","20210204PWA_01","Report received of sparking wire on concrete pole, started a small grass fire.\nCrew found candling Boric Acid fuse has caused small ground fire approx 150m2.\nCFA attended\nThere was no injuries or third party damage reported."]
[17,157,"2021-02-02","01:41",-38.313737000000003,142.21475599999999,"138 Toolong West Rd, Toolong 3285","30135821","KRT013","22kV AC","Rural Long"," - transformer (pole mounted)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0012734","20210202PWA_03","During REFCL testing of HV feeders fed from Koroit Zone Substation, the 25kVA single phase transformer of P45 Toolong Rd caught fire. \nCrews reported that there was no ground fire, however there may have been some oil leakage to the ground. \nThe CFA had been called.\nThere was no reported injuries or third party property damage."]
[17,158,"2021-02-04","13:50",-35.337637999999998,143.53253699999999,"18 Boree Drive, Swanhill, 3585.","60077424","SHL004","Low voltage AC (<1kV)","Rural Short"," - LV pillar","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0012752","20210205PWA_03","Some-one has backed over a underground power box/ distribution box - burning the grass. Trevor REC called it in.\nCrew advise vehicle being used by the local concreting company has contacted and damaged a low voltage pillar installed in front of the incident location.\nDamage resulted in a short circuit on Blue phase which ignited a small grass fire on the nature strip. \nThe Blue phase fuse operated. The grass fire was extinguished by workers on site.\nThere was no reported injuries or third party property damage."]
[17,159,"2021-02-05","17:55",-35.984544999999997,145.67148499999999,"381 McIntyre Roa, Mucktah VIC 3649","33085644","CME015","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012757","20210208PWA_01","Customers reported brown out & flickering lights at the incident location, upon arrival fault crew found that a tree from outside clearance space had been brought down during a thunderstorm event.\nFallen conductors ( 2 phases ) commenced a small grass fire where they made contact with vegetation.\nThere was no reported injuries or third party property damage."]
[17,160,"2021-02-06","09:35",-35.319251000000001,141.10679999999999,"901 Carina South Road, Carina VIC 3512","31021403","OYN001","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0012761","20210208PWA_02","Fire comms reported pole fire at the incident location.\nUpon arrival fault crew found that a 3 phase intermediate pole had a pole top fire believed to have commenced at the PTA, also burning wooden crossarm through at the king bolt, centre phase fell to ground whilst the outer phases remained aloft held up by the crossarm straps.\nA small ground fire of approximately 0.5m square occurred at pole base, no 3rd party damage.\n"]
[{"$f":"COUNTA(C198:O198,Q198,T198:V198)","v":17},161,"2021-02-09","15:41",-36.020386000000002,145.50546800000001,"1056 Lorenzs Road, Katunga VIC 3640","33080360","NKA003","Low voltage AC (<1kV)","Rural Short"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012765","20210210PWA_01","FireComms reported wires sparking and ground fire at the incident address.\nUpon arrival crew found that a single phase FSD had overheated and dropped molten material on the ground commencing a 40m x 5m ground fire, CFA on scene to extinguish the fire.\nThere was no reported injuries or third party property damage"]
[{"$f":"COUNTA(C199:O199,Q199,T199:V199)","v":17},162,"2021-02-10","10:14",-36.164178999999997,145.46797000000001,"Cnr of Kelly Rd and Wunghnu Rd DRUMANURE 3636",33084754,"SHTSNSF","66kV AC","Unknown"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0012767","20210210PWA_02","Vic Fire reported the company asset caused a ground fire at the incident location. \nUpon arrival a Powercor crew found a grass fire covering 100*400 Sqm area. \nThe exact cause could not be established, A chipped 66kV insulator was observed\nThere were no reported injuries. \n"]
[17,163,"2021-02-10","09:20",-37.562013999999998,143.85756599999999,"SHOP2,201 STURT STREET,BALLARAT,VIC,3350","34027327","BAS012","Low voltage AC (<1kV)","Urban"," - luminaires (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0014201","20210629PWA_07","Powercor received a report of a Pole fire on streetlight pole and REC had extinguished fire"]
[17,164,"2021-02-11","03:47",-38.129376999999998,144.33989,"7 Ebden St, Hamlyn Heights 3215","32078592","GL012","22kV AC","Rural Long"," - insulator tie wires / connections","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012797","20210212PWA_01","At 03:47hrs the GL012 Feeder experienced a successful reclose. Later that morning Powercor received a call from the Police advising of a dead possum at the base of a pole at the incident site. When crews arrived they found an apparent possum fault on the footpath side strain poly insulator on a HV Switch pole had resulted in fault current starting a small ground fire at the base of the pole.  The fire had self extinguished. "]
[17,165,"2021-02-16","13:25",-35.998238999999998,144.498051,"292 Heppell Rd, Torrumbarry VIC 3562","33106407","CHA005","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012816","20210217PWA_03","Tree clearing crew using a large mechanical equipment  inadvertently cut a large branch  causing it to contact HV conductor. A grass fire ensued."]
[17,166,"2021-02-16","13:11",-38.279738000000002,142.00352599999999,"5015 PRINCES HIGHWAY YAMBUK 3285 (4978 Princes Hwy, Codrington VIC 3285, Australia)","31029075","KRT013","22kV AC","Rural Long"," - surge diverter","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0012820","20210217PWA_02","Crew  attending to  outage  found HV fuse had operated and small ground fire at base of pole. \nSurge divertor  earth disconnect device had also operated.\nCrew advised that REFCL testing was occurring in area.\nThere was no injuries or third party property damage."]
[17,167,"2021-02-17","12:46",-38.124698000000002,144.664458,"122-132 Simson St, Portarlington VIC 3223","32070815","DDL013","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",{"$f":"IF(O204=\"\",\"\",IF(O204=\"LBRA only\",0.2,IF(O204=\"HBRA only\",1,IF(O204=\"within electric line construction area\",19.8,IF(O204=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":1},"Low-moderate",0.2,0.2,"INC-0012932","20210305PWA_02","EDO fuse operated \nOn arrival crew found fuse had candled\nThere was no ground fire, no reported injuries or third party property damage.\nIncident found during Outage data review.\nNo photos found\n"]
[17,168,"2021-02-18","14:53",-38.368670000000002,144.235164,"49 Minter Dr, Bells Beach VIC 3228","30072500","WPD021","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0012938","20210309PWA_01","Following supply interruption, crew found candled EDO fuse .\nThere was no ground fire, no reported injuries or third party property damage\nIncident found during Outage data review\nNo photos found"]
[17,169,"2021-02-20","14:00",-37.622020999999997,144.09743599999999,"14 Malones road west, Mount Edgerton 3352","33000127","BAN003","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0012854","20210223PWA_01","Customer reported a burnt patch of ground at the base of pole at the above address, the fault crew on arrival found a overheated neutral connection on the substation pole which has dropped to the ground and burnt a small patch of grass. "]
[17,170,"2021-02-21","16:58",-36.391221000000002,145.36342999999999,"OUTSIDE 14 PARK STREET,MOOROOPNA,VIC,3629","33088811","MNA024","22kV AC","Rural Short"," - fuse (powder filled)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0012898","20210303PWA_01","Crew found  a dead bird was at the base of substation pole and HV fuse had operated.  Further investigation found a small burnt patch of ground where the bird was found."]
[{"$f":"COUNTA(C208:O208,Q208,T208:V208)","v":17},171,"2021-02-21","10:51",-37.907066999999998,144.67598899999999,"120 Tower Road, Werribee","30115121","WBE034","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012846","20210222PWA_01","Reports received to advise of a pole fire and wires dangling.\n Upon arrival the fault crew found that the wooden HV cross-arm had burnt through at the road side insulator and  the HV conductor has fallen and contacted  LV overhead services.\n\n"]
[{"$f":"COUNTA(C209:O209,Q209,T209:V209)","v":17},172,"2021-02-23","14:35",-37.704895999999998,144.81412499999999,"891 Old Calder Hwy Service Rd, Keilor VIC 3036","30115590, 30114706","SA006","22kV AC","Urban"," - switch (disconnector/isolator)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012861","20210224PWA_01","A ground fire was reported at 967 Old Calder Hwy, Keilor.\n Upon arrival, a Powercor crew found  a  HV Isolator had ruptured  and there had been a small ground fire. (secondary fault)\nThe initiating fault  was found to be that the vehicle hit a comm (Optus) cable  and catenary wire at the incident location (Between LIS 15382 and LIS 4761) involving HV clashing from the impact"]
[17,173,"2021-02-26","09:49",-35.064411,142.59429900000001,"Boland Rd, Kulwin VIC 3490","30580656","OYN003","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0012939","20210309PWA_02","Report of pole fire at incident location\nNo ground fire\nIncident found during outage data review\nNo photos found"]
[17,174,"2021-03-04","16:30",-37.908963,144.65641600000001,"43-45 Greaves St S, Werribee VIC 3030",30102876,"WBE024","Low voltage AC (<1kV)","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012946","20210309PWA_03"," A vehicle travelling along Greaves St South has struck and damaged an overhead Optus cable crossing from  Greaves St South. into Hodge St.\nThe Optus cable appears to have been flicked into the electrical conductors above causing hot metal droplets to fall to the ground igniting dry lawn.\nThere was no reported injuries or third party property damage."]
[17,175,"2021-03-06","22:05",-37.815534999999997,144.657546,"560 Davis Rd, Tarneit VIC 3029, Australia","30104219","TNA021","Low voltage AC (<1kV)","Urban"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0012957","20210310PWA_01","Firecomms reported a pole on fire at the incident address. \nThe report indicated flames were coming down the pole.\nOn arrival the crew identified that a FOLCB had overheated and melted.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,176,"2021-03-07","22:10",-37.855038999999998,144.757803,"51-64 Sayers Road, Laverton (Outside Rear of Laverton RAAF base)","31030622","LV006","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0012960","20210310PWA_02","Passerby, and Firecomms reported sparks, pole fires and multiple ground fire starts along road reserve in Sayers Road at the rear of the Laverton RAAF base.\nAn inspection of the overhead lines noted some damage to conductor stranding and possible conductor clashing.\nThere were two fire sites adjacent (2 x 15 sqm)\nAn inspection of the affected area by Powercor and the Fire brigade noted several burnt, metallic-coated balloons on the ground.\nA Bureau of Meterology weather station is located adjacent to the ground fire sites. \nIt was not confirmed if the balloons are related to Bureau of Meterology work activity.\nThere was no injuries or third party property damage"]
[17,177,"2021-03-08","10:02",-36.773060999999998,141.46836500000001,"216 Edenhope Goroke Road, Karnak (Edenhope-Goroke Rd, Goroke VIC 3412, Australia)","30299343","HSM004","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0012962","20210310PWA_03","A Fire Brigade member -while passing - noticed the cross arm at the incident location was smoking and burning on the pole.\n\nThere was no ground fire, and no other damage"]
[17,178,"2021-03-11","09:30",-36.178852999999997,144.84422900000001,"8510 Murray Valley Hwy, Echuca Village VIC 3564.","33078770","ECA005","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0012985","20210311PWA_01","Vic Fire  reported pole on fire has caused small grass fire at incident location.\nOn arrival crew reported a flashover across fuse unit has occurred, two dead magpies at base of pole and small grass fire (1sqm).\nThere was no reported injuries or third party property damage.\n"]
[17,179,"2021-03-12","16:00",-37.52722,143.82777999999999,"1151 Grevillea Rd Wendouree","32007419","BAN006","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0013008","20210315PWA_04","Fault crew reported hv crossarm had burnt through and blue phase conductor fell and landed on lv x/arm.\nThere was no hv injection, ground fire or injuries as a result of this fire incident."]
[17,180,"2021-03-13","22:19",-36.291370000000001,145.04471799999999,"76 C359, Kyabram VIC 3620","30149948","KYM004","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0013006","20210315PWA_02","Customer has reported a wire down over lane way at the incident location.\nUpon arrival fault crew found that a termination substation pole had burnt off just above the transformer, resulting in the pole top falling to ground.\nCFA attended an extinguished the pole fire after PAL crew confirmed isolation's.\nNo ground fire, no reported injuries or third party property damage."]
[17,181,"2021-03-13","17:37",-36.377650000000003,145.44918200000001,"290 Old Dookie Rd, Shepparton East VIC 3631","30127303","STN024","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0013004","20210315PWA_01","Customer ( PAL employee ) reported a broken crossarm due to a pole fire and possible HVI. \nUpon arrival fault crew found that an intermediate substation crossarm had burnt through at fuse unit mounting location, causing the white phase HV conductor to fall onto the LV subsidiary circuit below.\nNo ground fire resulted, STN24 CB tripped to LO for the incident.\n"]
[17,182,"2021-03-13","18:39",-36.371144999999999,144.21839,"111 Dingee Rd, Dingee VIC 3571","32039171","EHK024","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (residential)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0013007","20210315PWA_03","Customer reported that service wire in contact with tree had faulted and the vegetation ignited briefly before supply was interrupted.\nUpon arrival crew found that grey LV twisted service had failed, finding evidence of burnt vegetation at the contact point substantiating customers account of a brief fire.\nNo ground fire or 3rd party damage."]
[17,183,"2021-03-13","16:14",-36.826349999999998,141.47217699999999,"888 Edenhope-Goroke Rd, Karnak VIC 3401","32099901","HSM004","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0013694","20210512PWA_02","Following Fdr interruption Crossarm fire found at incident location.\nThere was no ground fire, no reported injuries or third party property damage.\n(Incident found during outage data review)"]
[{"$f":"COUNTA(C221:O221,Q221,T221:V221)","v":17},184,"2021-03-13","17:40",-37.245592000000002,144.43541999999999,"60 FLYNNS ROAD,KYNETON,VIC,3444","33029402","WND024","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0013030","20210318PWA_02","Customer reported service cable arcing and dropping sparks  & smoking, without any visible fire. \nUpon arrival fault crew found that a 3 Phase grey twisted service had failed at the dogbone, customer POA end. The arcing had caused blackening of the area immediately where the failure had occurred.\nNo ground fire, no shock or 3rd party damage"]
[{"$f":"COUNTA(C222:O222,Q222,T222:V222)","v":17},185,"2021-03-15","08:46",-38.16019,144.57057399999999,"37 Barongarook Drive Clifton Springs 3222","32070010","DDL022","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0013009","20210316PWA_01","Vic Fire reported, service wire on fire causing to burn down part of house.\nCrew found fire damaged to P.O.A. and customer mains.\nThere was no ground fire or reported injuries"]
[17,186,"2021-03-15","12:52",-36.243374000000003,142.391989,"120 Craig Avenue Warracknabeal 3393","30352094","HSM005","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0013033","20210318PWA_03","Employee reported pole box has caught on fire and burnt.\nThere was debris on ground but no ground fire.\nNo reported injuries or third party property damage.\n"]
[17,187,"2021-03-18","15:35",-38.173391000000002,144.26728,"605 Barrabool Road, Ceres ","32084859","WPD011","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0013040","20210319PWA_02","Customer advised fire at the top of the pole in front of the Primary School. \nCrews attended and confirmed a three phase polebox had faulted and had caught fire.\nNo ground fire was evident, there was no reported injuries or third party property damage."]
[17,188,"2021-03-20","01:00",-36.347577000000001,145.456457,"490 Ford Road LEMNOS VIC 3631","33096699","SHN024","22kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0013058","20210322PWA_03","Customer reported at 1.00am in the morning a bat caused a flashover and a small ground fire resulted ACR interrupted supply momentarily and came back on customer did not report till next morning.\nThere was a small ground fire( 2 sqm) no reported injuries or third party property damage."]
[17,189,"2021-03-20","10:40",-36.353943000000001,145.412384,"3 Merrno Drive SHEPPARTON VIC 3630 ",60231266,"SHN022","Low voltage AC (<1kV)","Urban"," - services pit","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0013064","20210323PWA_01","Report of fire in Pit at incident location.\nOn arrival crew found pit connections had been on fire and melted.\nThere was no reported injuries\n"]
[17,190,"2021-03-20","21:45",-37.771442,144.758219,"UNIT1, 7 LEE STREET, DEER PARK, VIC, 3023 (8 Lee St, Deer Park VIC 3023, Australia)","33073656","SU035","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0013055","20210322PWA_01","Vic Fire reported sparking at poa - brigade on site.\nOn arrival the PCA Faults Crew have advised that the Red-Phase Connection at the POA was Vhad burnt out \nThere was no ground fire, no reported injuries or third party property damage.\n"]
[17,191,"2021-03-21","18:55",-36.325583000000002,144.23229599999999,"Bendigo-Pyramid Rd, Dingee VIC 3571, Australia","31006153","EHK024","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0013066","20210323PWA_02","Report of pole fire at incident location.\non arrival crew found top burnt off pole.\nThere was no ground fire, no injuries or third party property damage."]
[17,192,"2021-03-22","12:58",-38.744942999999999,143.671505,"58 Casino Ave, Apollo Bay VIC 3233",32064587,"CLC013","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0014319","20210708PWA_02","Gardener Angela for 56 Casino Av reporting that insulator on pole in front of this property has fallen, now hanging down resting on xarm of lower wires. Angela can hear arcing noise. No sparks. She was unsure if anyone had lost power. Wire still attached to insulator, doesnt look to have touched any other wires.\nCrew found crossarm had burnt off at strap bolt.\nThere was no ground fire, no reported injuries or third party property damage.\n\nIncident found during outage data review."]
[17,193,"2021-03-23","17:04",-36.738430000000001,144.218119,"68 MAIDEN GULLY ROAD, MAIDEN GULLY, VIC 3551","32040751","BET001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0013077","20210324PWA_02","Report of broken crossarm, crossarm fallen into LV.\nThere was no HVI\nSmall ground fire (4sqm), no reported injuries or third party property damage"]
[17,194,"2021-03-23","15:46",-38.158213000000003,144.57758999999999,"12 Turana Avenue, Clifton Springs. ","30076381","DDL022","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0013072","20210324PWA_01","Report of pole fire at incident location.\nOn arrival crew found HV crossarm burnt through.\nNo HVI, No ground fire.\nThere was no reported injuries or third party property damage."]
[17,195,"2021-03-24","15:09",-38.163457000000001,144.395205,"17 Lucas St, Newcomb VIC 3219","32068758","GLE031","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0013704","20210512PWA_03","During pole inspection works a burnt HV crossarm was found.\nthere was no ground fire, no reported injuries or third party property damage.\n(incident found during outage data review)"]
[17,196,"2021-03-27","12:02",-36.308745000000002,143.20247900000001,"3469 St Arnaud-Wycheproof Road Jeffcott 3480 (near Conlans road)","32016809","CTN006","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0013123","20210329PWA_02","Crew patrolling fault on CTN006 found that a tipper truck had made contact with the SWER conductor.\nThere was one broken SWER pole, 4 x bays of conductor on ground, conductor broken.\nThere was a small ground fire (small burn mark), no reported injuries, no reported property damage."]
[{"$f":"COUNTA(C234:O234,Q234,T234:V234)","v":17},197,"2021-04-01","19:11",-35.432924999999997,143.65043,"351 Lakeside Dr, Lake Boga VIC 3584","30149711","SHL005","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O234=\"\",\"\",IF(O234=\"LBRA only\",0.2,IF(O234=\"HBRA only\",1,IF(O234=\"within electric line construction area\",19.8,IF(O234=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"Low-moderate",{"$f":"IF(Q234=\"\",\"\",IF(Q234=\"No forecast\",0.1,IF(Q234=\"Low-moderate\",0.2,IF(Q234=\"High\",0.5,IF(Q234=\"Very high\",1,IF(Q234=\"Severe\",2,IF(Q234=\"Extreme\",3.5,5)))))))","v":0.2},{"$f":"IF(OR(P234=\"\",R234=\"\"),\"\",IF(AND(O234=\"within electric line construction area\",Q234=\"No forecast\"),1,P234*R234))","v":4.0000000000000008E-2},"INC-0013178","20210406PWA_01","Report received of pole fire at incident location.\nOn arrival crew found burnt out Krone box.\nThere was a small ground fire(1sqm), no reported injuries or third party property damage.\n"]
[{"$f":"COUNTA(C235:O235,Q235,T235:V235)","v":17},198,"2021-04-01","00:54",-38.344236000000002,144.296392,"50 DOMAIN ROAD,JAN JUC,VIC,3228","33047244","WPD032","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O235=\"\",\"\",IF(O235=\"LBRA only\",0.2,IF(O235=\"HBRA only\",1,IF(O235=\"within electric line construction area\",19.8,IF(O235=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"Low-moderate",{"$f":"IF(Q235=\"\",\"\",IF(Q235=\"No forecast\",0.1,IF(Q235=\"Low-moderate\",0.2,IF(Q235=\"High\",0.5,IF(Q235=\"Very high\",1,IF(Q235=\"Severe\",2,IF(Q235=\"Extreme\",3.5,5)))))))","v":0.2},{"$f":"IF(OR(P235=\"\",R235=\"\"),\"\",IF(AND(O235=\"within electric line construction area\",Q235=\"No forecast\"),1,P235*R235))","v":4.0000000000000008E-2},"INC-0013155","20210401PWA_02","Fire brigade reported pole top  fire. On arrival the crew found a EDO fuse had malfunctioned and hung up.\nThere was no ground fire, no reported injuries or third party property damage"]
[17,199,"2021-04-02","18:34",-38.290084,142.309234,"647 Penshurst-Port Fairy Rd, Kirkstall VIC 3283","33102336","KRT013","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0014214","20210701PWA_01","Report received of pole fire at incident location.\nOn arrival crew found a FOLCB has melted and caught fire, fire now out.\nThere was no ground fire, no reported injuries or third party property damage.\nIncident found during outage data review."]
[17,200,"2021-04-07","12:19:00",-37.443668000000002,144.76658900000001,"128 MCINTYRE LANE,BOLINDA,VIC,3432",30298101,"GSB012","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0013193","20210408PWA_01","Report from CFA of Pole and ground fire at incident location.\nOn arrival crew found a FOLCB Had overheated molten particles fell to ground causing a small grass fire.\nThere was no reported injuries or third party property damage."]
[{"$f":"COUNTA(C238:O238,Q238,T238:V238)","v":17},201,"2021-04-10","12:03",-37.822248999999999,144.117526,"662 SLATE QUARRY ROAD,MEREDITH,VIC,3333","30060403","GL015","12.7kV AC (SWER)","Rural Long"," - fuse (EDO fuse)","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O238=\"\",\"\",IF(O238=\"LBRA only\",0.2,IF(O238=\"HBRA only\",1,IF(O238=\"within electric line construction area\",19.8,IF(O238=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"High",{"$f":"IF(Q238=\"\",\"\",IF(Q238=\"No forecast\",0.1,IF(Q238=\"Low-moderate\",0.2,IF(Q238=\"High\",0.5,IF(Q238=\"Very high\",1,IF(Q238=\"Severe\",2,IF(Q238=\"Extreme\",3.5,5)))))))","v":0.5},{"$f":"IF(OR(P238=\"\",R238=\"\"),\"\",IF(AND(O238=\"within electric line construction area\",Q238=\"No forecast\"),1,P238*R238))","v":2.2999999999999998},"INC-0013785","20210519PWA_01","Crew attending to report of sparking pole found EDO unit had malfunctioned \nFound during outage data review\nNo ground fire, no reported injuries, no third party property damage\n"]
[{"$f":"COUNTA(C239:O239,Q239,T239:V239)","v":17},202,"2021-04-12","12:10",-38.620634000000003,143.03918100000001,"Rounds Road, Port Campbell",30235731,"TRG013","12.7kV AC (SWER)","Rural Long"," - insulators","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O239=\"\",\"\",IF(O239=\"LBRA only\",0.2,IF(O239=\"HBRA only\",1,IF(O239=\"within electric line construction area\",19.8,IF(O239=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"Low-moderate",{"$f":"IF(Q239=\"\",\"\",IF(Q239=\"No forecast\",0.1,IF(Q239=\"Low-moderate\",0.2,IF(Q239=\"High\",0.5,IF(Q239=\"Very high\",1,IF(Q239=\"Severe\",2,IF(Q239=\"Extreme\",3.5,5)))))))","v":0.2},{"$f":"IF(OR(P239=\"\",R239=\"\"),\"\",IF(AND(O239=\"within electric line construction area\",Q239=\"No forecast\"),1,P239*R239))","v":0.91999999999999993},"INC-0013225","20210413PWA_01","Powercor was advised of a pole fire. the attending crew found  a pole top insulator had burnt"]
[17,203,"2021-04-18","16:30",-37.733370000000001,141.814502,"303 Schullers Rd, Tahara VIC 3301","32128099","HTN002","12.7kV AC (SWER)","Rural Long"," - fuse (boric acid)","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0013312","20210422PWA_02","After patrolling a line, the crew were restoring power to and reclosing the HV fusing at a nearby switch pole. \nWhen it was closed the HV Boric Acid fuse activated and got hung up, causing the bottom hinge below the fuse tube to burn away. This caused a ground fire of approximately 120m2. The crew extinguished the blaze.\nThere was no reported injuries."]
[17,204,"2021-04-20","18:05",-35.207009999999997,143.40087700000001,"2267 Murray Valley Hwy, Vinifera VIC 3591","32158966","SHL002","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0013309","20210422PWA_01","Firecomms reported a pole fire at the incident location, Upon arrival fault crew found P188 Nyah had a pole fire affecting the t/off crossarm, which had burnt through at the crossarm kingbolt, causing conductors to hang low over Murray Valley highway. conductors remained suspended by the bridging flex's, supply remained on until supply was switched & isolated for access permit.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,205,"2021-04-24","16:29",-38.167960999999998,144.506933,"21-29 Pax Parade, Curlewis VIC 3222, Australia","32081493","DDL014","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0013787","20210519PWA_02","Crew attending to outage  found EDO tube malfunctioned \nFound during outage data review.\nThere was no ground fire, no reported injuries or third party property damage"]
[17,206,"2021-05-01","20:44",-36.015129999999999,144.99558200000001,"108 Barmah East Road Barmah 3639","33082651","NKA002","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0013519","20210503PWA_01","Customer reported  tree has brought down wire off to side of road,.\nSmall grass fire is now out. \nOn arrival crew found 3 phase line, West side 3/12 steel conductor damaged by customers tree (outside clearance space)  fallen tree & grass burnt, 5 x 5m or 25m2\nAt LIS: 5479, BARMAH 110, 1 x candled fuse, South side, no grass fire.\nThere was no reported injuries or third party property damage."]
[17,207,"2021-05-02","13:36",-37.685310999999999,144.55020500000001,"721 High Street Service Rd, Melton West VIC 3337","30352515","MLN022","22kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0013523","20210503PWA_02","Vic Fire, Reports of wires on fire and caused a grass fire at base of pole at intersection of Bulmans Rd and High St Melton West.\nUpon arrival the PCA Operator and PCA Faults Crew have advised that party balloons had contacted, tangled and wrapped around the HV OH Line near HV Pole LIS-858339. \nhe 22kV Feeder MLN022 had a reclose on it, which would have resulted in the tangled balloons becoming free from the HV OH Line . As a result of this, sparks have fallen onto the grassed area below resulting in a very minor grass-fire of approximately 1m².\n\nThe Fire brigade attended site and the grass fire was extinguished.\n\nThere was no reported, HVI, injury or shocks as a result of this incident. "]
[17,208,"2021-05-06","23:38",-35.927872000000001,145.231897,"2220A MURRAY VALLEY HIGHWAY  YALCA 3637","30120818","NKA006","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0013626","20210507PWA_01","Vicfire comms reported pole fire. sparks falling to ground. burn marks on the grass.  \nOn arrival crew found burnt out LV junction box on pole in Browns Bridge road \n Ground fire approx. 12m x 12m at base of the pole."]
[17,209,"2021-05-07","15:17",-36.486558000000002,145.106426,"240 Heath Rd, Harston VIC 3616","30295497","SHP014","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0014148","20210623PWA_02","Crew found EDO fuse barrel burnt in half.\nNo ground fire.\n\nIncident found during OMS data review\nNo photos located"]
[17,210,"2021-05-07","08:48",-36.182544999999998,141.36031199999999,"Unnamed Road, Broughton VIC 3418","32118496","NHL031","12.7kV AC (SWER)","Rural Long"," - insulators","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0013645","20210507PWA_02","Customer reports Wire down in paddock.\nAttending crew found top burnt off pole  and cracked HV insulator."]
[17,211,"2021-05-12","08:18",-37.599907999999999,144.217535,"381 Old Melbourne Rd, Ballan VIC 3342","30105719","BMH003","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0013707","20210512PWA_05","Overhead service caught fire mid span between poles LIS # 105145 and 104261. Service remained intact across road. No ground fire reported. No damage to premises.\n"]
[17,212,"2021-05-17","12:47",-38.404496000000002,144.19154399999999,"1a McDougall Rd, Anglesea VIC 3230","32072343","WPD021","Low voltage AC (<1kV)","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0014150","20210623PWA_03","During maintenance inspection LV Crossarm found burnt around kingbolt area.\nThere was no ground fire\n\nFound during Outage Data review "]
[17,213,"2021-05-18","20:25",-35.264536,141.185732,"7 Sharrock St, Murrayville VIC 3512","30319312","OYN001","22kV AC","Rural Long"," - dropper / bridge","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0013844","20210525PWA_02","CFA reported smouldering HV leads on pole at incident location.\nOn arrival crew found HV lead had been on fire.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,214,"2021-05-20","09:30",-36.357070999999998,144.78058200000001,"2228 Webb Rd, Nanneella 3561 ( Rochester P219 lis 890184 2228) ","30567753","KYM001","22kV AC","Rural Long"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0013807","20210521PWA_01","During planned switching the regulator Tap change mis-operated resulted in a burning bushing cover and debris falling to the ground.\nNo ground fire, no reported injuries or third party property damage."]
[17,215,"2021-05-21","11:00",-37.035798999999997,141.31279799999999,"397 Scrubby Lake Rd, Edenhope VIC 3318","33053052","CHM011","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0014151","20210623PWA_04","2x candled fuses required shutdown to replace safely\nno ground fire.\n\nIncident found during outage data review"]
[17,216,"2021-05-23","20:41",-38.249434999999998,144.510381,"5 Boulevard Court, Ocean Grove ","33044300","DDL011","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0013835","20210524PWA_05","Report recieved of pole fire at incident location.\nOn arrival crew found that a FOLCB had caught fire, dropping debris to ground causeing a small ground fire (0.5 X 0.5 sqm mtr approx)\nThere was no injuries or third party property damage.\n0\nThere was no injuries"]
[17,217,"2021-05-24","14:43",-37.793382999999999,144.72153399999999,"314 Middle Rd, Ravenhall VIC 3023","30573681","TNA021","22kV AC","Urban"," - pole (wood)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0013842","20210525PWA_01","CFA reported of pole fire.\nIt was reported that top HV X-arm fallen into bottom wires and sparking. \nOn arrival the crew found that a vehicle had impacted the pole resulting in top cross-arm to be dislodges and falling onto the bottom HV circuit. \nPole caught fire and small ground fire was also reported. \nThe vehicle had left the scene prior to crew attending site."]
[17,218,"2021-05-25","08:21",-37.125110999999997,141.04243199999999,"6737 C211, Langkoop VIC 3318","32109370","CHM011","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0014165","20210625PWA_01","During asset inspection, burnt EDO fuse found.\nThere was no ground fire\n\nincident found during Outage Data review."]
[17,219,"2021-05-26","20:26",-37.667727999999997,144.58803499999999,"7 OUTLOOK RIDE,KURUNJANG,VIC,3337","31025459","MLN012","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0013893","20210528PWA_01","Following report of pole fire On arrival, the crew found that the 3 FOLCB’s and the FSD box on the substation pole  had caught fire. \nAll of the fuse boxes were partially melted, and burnt debris fell to the pavement and wet grass below. \nThe crew advised that the underground cable guard on the pole was damaged and the HV ties were broken, seemingly like a car had hit the pole.\nNeighbours confirmed that unknown vehicle had hit pole a week ago.\nThere was no ground fire nor third party damaged. No reported injuries. \n"]
[17,220,"2021-05-26","05:49",-37.664582000000003,144.581627,"11 Greenstead Amble, Kurunjang VIC 3337","30258026","MLN012","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0013875","20210527PWA_01","Crew on site found FOLCB on pole had evidence of fire"]
[17,221,"2021-05-28","12:35",-34.227423999999999,142.18166199999999,"2937 Fourteenth St, Irymple VIC 3498","30098668","RCTS-MDA2","66kV AC","Unknown"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0013899","20210528PWA_04","Customer reported large bang came from pole some smoke and sparking.\nOn arrival crew found pole top burnt off allowing 66kv conductors to fall onto 22kv below.\nPossibility of HVI\nThere was no ground fire, no reported injuries."]
[17,222,"2021-05-30","10:39",-36.80133,144.16036199999999,"1174 Calder Alternative Hwy, Lockwood VIC 3551","30019244","BET004","12.7kV AC (SWER)","Rural Short"," - fuse (Fault Tamer)","single wire earth return (SWER)","Started in or originated from a distribution system","within electric line construction area",19.8,"No forecast",0.1,1,"INC-0014167","20210625PWA_02","Following report of supply failure, crew arrived and found a Fault Tamer fuse burnt out.\nThere was no ground fire.\n\nIncident found during Outage data review"]
[17,223,"2021-06-02","16:59",-37.640366999999998,143.72236799999999,"330 Sebastopol-Smythesdale Rd, Ross Creek VIC 3351",30002446,"BAS033","12.7kV AC (SWER)","Rural Short"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0014465","20210719PWA_01","Report received of car into tree, tree on conductors has caught fire.\nEmergency services on route, passengers out of vehicle.\nThere was no gound fire\nIncident found during Outage data review\nNo photos found"]
[17,224,"2021-06-03","09:36",-37.806555000000003,144.83155500000001,"21 Vella Dr, Sunshine West VIC 3020","30104049","SSE033","Low voltage AC (<1kV)","Urban"," - overhead conductor (ABC)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0014006","20210607PWA_01","Emergency services report transformer fire o/s 534 Somerville rd Sunshine West\nOn arrival crew found pole burnt due to ABC connection burning out.\nThere had been some rubbing of insulation against a metal stay  out reach bracket.\nThere was no \n"]
[17,225,"2021-06-06","09:05",-36.383004,145.41266999999999,"352 High St, Shepparton VIC 3630","33089701","STN014","Low voltage AC (<1kV)","Urban"," - lamps (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0014466","20210719PWA_02","Street Light PE Cell Base Caught Fire in Rain\nThere was no ground fire.\nNo photos found\nFound during OMS data review"]
[17,226,"2021-06-07","15:34",-38.199751999999997,144.49244400000001,"1025 Bellarine Highway, Wallington 3222","32070269","DDL014","22kV AC","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0014016","20210608PWA_01","A customer reported wires down and a fire started in front of his property at the incident location.\nOn arrival, the crew found that a large tree from outside the clearance space had fallen on the HV conductors adjacent to Substation pole 167 Bellarine Hwy LIS-6200. \nThe tree caused the conductors to burn on a tree branch and break falling to the ground, starting small grassfires along the conductor of less than 1 square metre total in size. \nThere were no reported injuries or third party damage."]
[17,227,"2021-06-09","06:20",-38.288465000000002,142.335407,"Cypress Lodge, 278 Penshurst-Warrnambool Rd, Koroit","33100095","KRT013","22kV AC","Rural Long"," - dropper / bridge","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0014467","20210719PWA_03","Report of pole fire at incident location.\nOn arrival crew found burnt out HV dropper leads\nThere was no ground fire\nFound during outage data review.\nNo photos taken"]
[17,228,"2021-06-10","16:53",-37.353143000000003,144.05263099999999,"89 Richards Rd, Blampied VIC 3364","30011729","BAN008","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0014468","20210719PWA_04","On arrival crew found burnt out edo barrel. \nNo ground fire\nfound during Outage data review\nno photos found"]
[17,229,"2021-06-11","19:39",-34.208961000000002,142.11972,"22 Bozzi Ct, Mildura VIC 3500","60075407","MBN032","Low voltage AC (<1kV)","Rural Short"," - LV pillar","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0014056","20210615PWA_05","Customer report of pillar on fire out front of above address. \nOn arrival, crew found P/P on fire.\nFire limited to pillar location.\nThere was no injuries or third party property damage."]
[17,230,"2021-06-11","17:21",-37.267918999999999,141.4179,"Mooree Road, Chetwynd","32105357","CHM011","12.7kV AC (SWER)","Rural Long"," - insulators","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0014057","20210615PWA_06","Crew attending to outage advised top section of Angle type 3 pole burned off below insulators.  "]
[17,231,"2021-06-11","02:30",-37.713270000000001,144.83103800000001,"34 Borrell St, Keilor VIC 3036",30111402,"SA002","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (residential)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0014513","20210722PWA_01","Fire brigade has attended overnight due to service sparking and flames on wire.\nThere was no ground fire \nIncident found during outage data review"]
[17,232,"2021-06-11","17:36",-37.362873999999998,144.636787,"114 Hesket Boundary Rd, Hesket VIC 3442","32050056","WND012","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0014515","20210722PWA_02","Report of tree on fire under line\nTree on SWER conductors\nNo ground fire\nFound during outage data review\nNo photos found"]
[17,233,"2021-06-12","15:23",-37.671241999999999,143.65441999999999,"74 Scarsdale-Pitfield Road, Scarsdale","30005662","BAS033","Low voltage AC (<1kV)","Rural Long"," - earth / earthing","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0014061","20210615PWA_08","Emergency Services reported to Powercor a pole fire at the incident location.\n\nCrew attended and found the High Voltage earth had detached at the pole top and was making contact with the Low Voltage conductors below, causing a Low Voltage short to earth, generating heat I the HV Earth, and causing a small grass fire at the base of the pole."]
[17,234,"2021-06-21","06:55",-36.776972999999998,144.258691,"8 Hunter St, Golden Square VIC 3555","30039172","BET005","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0014516","20210722PWA_03","PAL fuse box had flames coming from it\nNo ground fire\nfound during Outage data review\nno photos found"]
[17,235,"2021-06-24","16:02",-37.344059000000001,144.14060000000001,"34A Bridport St Daylesford 3460","30305792","BAN008","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0014177","20210628PWA_01","A pole fire was reported at the incident address.\nOn arrival the fault crew found that a single phase FOLCB controlling an underground service line to a house had caught fire and melted. \nThere was no ground fire, no reported injuries or third party property damage. "]
[17,236,"2021-06-24","09:24",-38.541037000000003,143.97472200000001,"130 Mountjoy Parade, Lorne VIC 3232",33040905,"CLC014","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0014179","20210628PWA_02","FOLCB fire on pole. Fire brigade and police on site. No ground fire."]
[17,237,"2021-06-28","17:10",-38.335804000000003,143.68744899999999,"255 Trasks Rd, Warncoort, 3243","32064553","WIN011","Low voltage AC (<1kV)","Rural Long"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0014196","20210629PWA_04","Customer reported junction box on pole on fire outside incident location.\nOn arrival the crew found an LV FSD had caught fire and melted insulation. Some hot insulation also dripped onto a lower FOLCB.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,238,"2021-06-29","15:03",-38.114552000000003,143.63377299999999,"2360 Colac-Ballarat Rd, Weering VIC 3251","30052577","CLC006","22kV AC","Rural Long"," - pole (wood)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0014217","20210701PWA_02","emergency services reported wire down. \nattending crew found vehicle has struck and destroyed pole 237 and fallen conductors had left burns on the ground "]
[17,239,"2021-02-18","01:30:00",-37.548971000000002,143.90828999999999,"4 Moneill Cl, Brown Hill VIC 3350. trees west of this address.",33005885,"BAN003","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0012831","20210302PWA_01","Report of tree on fire near incident location.\nCrew advise trees contacting line from below at the incident location require immediate pruning."]
[17,240,"2020-10-27","06:30:00",-37.601106999999999,143.682435,"CADENZA ARABIANS, 40 LOUISE COURT, HADDON VIC 3351",33001840,"BAS033","Low voltage AC (<1kV)","Rural Short"," - connection box","two phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0012009","20201028PWA_02","CFA reported a pole fire at the above location, on arrival the fault crew found a pole fuse box had burnt and melted dropping onto green grass at the base of the pole. There was small patch of grass scorched , no reported injuries or third party property damage."]
[17,241,"2021-03-26","19:04:00",-36.949367000000002,144.736715,"6308 Northern Highway Heathcote 3523",33032795,"BGO023","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0013136","20210330PWA_01","Vic Fire reported a pole fire at incident location, pole fuse box on fire. On arrival crew found a LV pole mounted fuse box had failed. There was a small ( < 0.5m2) ground fire at base of pole. There was no reported injuries."]
[0,242,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,243,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,244,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,245,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,246,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,247,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,248,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,249,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,250,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,251,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,252,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,253,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,254,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,255,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,256,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,257,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,258,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,259,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,260,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,261,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,262,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,263,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,264,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,265,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[{"$f":"COUNTA(C303:O303,Q303,T303:V303)","v":0},266,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(O303=\"\",\"\",IF(O303=\"LBRA only\",0.2,IF(O303=\"HBRA only\",1,IF(O303=\"within electric line construction area\",19.8,IF(O303=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":""},null,{"$f":"IF(Q303=\"\",\"\",IF(Q303=\"No forecast\",0.1,IF(Q303=\"Low-moderate\",0.2,IF(Q303=\"High\",0.5,IF(Q303=\"Very high\",1,IF(Q303=\"Severe\",2,IF(Q303=\"Extreme\",3.5,5)))))))","v":""},{"$f":"IF(OR(P303=\"\",R303=\"\"),\"\",IF(AND(O303=\"within electric line construction area\",Q303=\"No forecast\"),1,P303*R303))","v":""}]
[0,267,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,268,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,269,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,270,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,271,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,272,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,273,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,274,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,275,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]

{"sheet":"3. Systems and Audit","index":4,"n_rows":29,"n_cols":5,"rows_kept":29,"cut":false,"hidden":false,"merged":[[28,1,29,4],[3,5,3,6],[4,5,4,6],[5,5,5,6],[6,1,6,4],[9,1,9,4],[14,1,14,4],[10,1,10,4],[13,1,13,4],[12,1,12,4],[11,1,11,4]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"Powercor"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2020/21"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"Powercor must provide:"}]
[]
[null,"Table 4 - Information or reporting systems"]
[null,"   (1) Name of any IT system used to collect fire start data or fault event data - i.e. SCADA system, or fault reporting system"]
[null,"   (2) Whether the fire recording or fault recording process has been audited or complies with a relevant Australian or industry standard - Yes or No"]
[null,"   (3) List any relevant Australian or industry standards that the fire recording or fault recording process complies with"]
[null,"   (4) Whether the data entered into or removed from the IT system has been audited - Yes or No"]
[]
[]
[null,"Table 4: Information or reporting systems"]
[]
[null,"Information or reporting systems","Name","System Audited","Relevant Standards"]
[null,"System 1","Network Incidents Database","Yes","None applicable"]
[null,"System 2","Outage Management System (OMS)","Yes","None applicable"]
[null,"System 3 ","Smallworld GIS (Graphical Information System)","Yes","None applicable"]
[null,"System 4"]
[null,"System 5"]
[null,"System 6"]
[null,"System 7"]
[null,"System 8"]
[]
[null,"The SGSPAA Internal Audit function undertakes a programme of work in accordance with the SGSPAA Group Internal Audit Plan. This internal audit activity covers elements of the systems and process used for capturing, recording and maintaining fire start data."]