{"text_format":"1","workbook":"xlsx","n_sheets":5,"sheets":["Contents","Cover","1. F-Factor summary","2. Individual fire start info","3. Systems and Audit"],"not_rendered":{"charts":0,"images":2,"macros":1,"external_links":2,"defined_names":97,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Contents","index":0,"n_rows":19,"n_cols":6,"rows_kept":19,"cut":false,"hidden":false,"merged":[[8,2,9,3],[2,1,2,10],[4,1,4,10]]}
[" "]
[]
[null,"Electricity Distribution Network Service Provider\nF-factor Reporting Template"]
[]
[null,"Table of contents"]
[]
[]
[null,null,"Cover sheet",null,null,"2. Fire start report"]
[]
[]
[]
[null,null,"1. F-factor summary",null,null,"3. Systems and Audit"]
[]
[]
[]
[]
[]
[]
[null,null,{"$f":"\"NOTE: This spreadsheet includes IRU targets up to and including FY\"&'1. F-Factor summary'!J8","v":"NOTE: This spreadsheet includes IRU targets up to and including FY2021/22"}]

{"sheet":"Cover","index":1,"n_rows":49,"n_cols":6,"rows_kept":49,"cut":false,"hidden":false,"merged":[[26,3,26,8],[28,3,28,8],[26,1,26,2],[31,3,31,5],[14,1,14,8],[16,1,16,8],[17,1,17,8],[21,1,21,8],[19,1,19,8],[10,1,11,8],[13,1,13,8],[48,2,48,6],[42,2,42,3],[42,4,42,7],[46,2,46,6],[47,2,47,6],[38,2,38,3],[38,4,38,7],[41,2,41,3],[41,4,41,7],[37,2,37,3],[37,4,37,7],[32,3,32,8],[30,3,30,8],[15,1,15,8]]}
[]
[]
[]
[]
[]
[]
[]
[null,"Distribution Network Service Provider"]
[null,"Fire start report"]
[]
[null,"This template is to be used by a DNSP to provide a fire start report to the AER in accordance with section 5 of the F-factor Order in Council.  "]
[]
[]
[null,"Colour coding of input sheets:"]
[null,"Dark blue = AER headings"]
[null,"Grey = AER instructions"]
[null,"Yellow = Input cells"]
[null,"Light orange = Automatically-generated cells"]
[]
[null,"Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so."]
[null,"The cells and structure of the spreadsheet is locked to prevent inadvertent interference with the automated settings."]
[null,"All dollar amounts are to be unrounded, and in nominal terms."]
[]
[]
[]
[]
[null,"DNSP:",null,"Powercor"]
[]
[null,"DNSP - trading name:",null,"Powercor Australia Ltd"]
[]
[null,"DNSP - Australian business number: ",null,"ACN 064 651 109"]
[]
[null,"Reporting year:",null,"2021/22"]
[]
[]
[]
[]
[null,"Business address","Address",null,"40 Market Street"]
[null,null,"Suburb",null,"Melbourne"]
[null,null,null,"State","Victoria","Postcode"]
[]
[null,"Postal address","Address",null,"Locked Bag 14090"]
[null,null,"Suburb",null,"Melbourne"]
[null,null,null,"State","Victoria","Postcode"]
[]
[]
[null,"Contact name/s"]
[null,"Contact phone/s"]
[null,"Contact email address/s"]

{"sheet":"1. F-Factor summary","index":2,"n_rows":14,"n_cols":15,"rows_kept":14,"cut":false,"hidden":false,"merged":[[12,2,12,3],[13,2,13,3],[6,2,6,3],[7,2,7,3],[8,2,8,3],[9,2,9,3],[10,2,10,3],[5,1,5,2],[3,6,3,8],[4,6,4,8],[5,6,5,8],[11,2,11,3]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"Powercor"},"IRU target:",{"$f":"IF(SUM(K2:O2)=0,\"\",SUM(K2:O2))","v":235.2},null,null,null,null,null,null,"AusNet Services","CitiPower","Jemena","Powercor","United Energy"]
[null,"F-factor data reporting","IRU amount:",{"$f":"IF(SUM('2. Individual fire start info'!S38:S2000)=0,\"\",SUM('2. Individual fire start info'!S38:S2000))","v":156.01999999999984},null,null,null,null,null,"current",{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>K1),\"\",LOOKUP($B3,$J3:$J100,K3:K100))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>L1),\"\",LOOKUP($B3,$J3:$J100,L3:L100))","v":""},"",235.2,""]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2021/22"},"Revenue adjustment:",{"$f":"IF(OR(D1=\"\",D2=\"\"),\"\",15000*(D1-D2))","v":1187700.0000000023},null,null,null,null,null,"2016/17",247.7,3.4,9.6999999999999993,468,22.3]
[null,null,null,null,null,null,null,null,null,"2017/18",247.7,3.4,9.6999999999999993,468,22.3]
[null,"Table 2: Summary of total fire starts by F factor Order definition",null,null,null,null,null,null,null,"2018/19",247.7,3.4,9.6999999999999993,468,22.3]
[null,"This is a summary of data in worksheet \"2. Fire Start Report\"",null,null,null,null,null,null,null,"2019/20",221.1,3.4,9.6999999999999993,412.8,22.3]
[null,"Kind of Fire Start by definition of fire start under clause 5 of F-factor Order","Total fires by cause",null,null,null,null,null,null,"2020/21",177.5,1.3,4.2,277.60000000000002,18.7]
[null,"Started in or originated from a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B8)","v":162},null,null,null,null,null,null,"2021/22",164.3,1.9,3.7,235.2,19]
[null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B9)","v":21}]
[null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B10)","v":15}]
[null,"Started by lightning striking a distribution system or a part of a distribution system ",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B11)","v":12}]
[null,"Started by any other thing forming part of or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B12)","v":18}]
[null,"Otherwise started by a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B13)","v":0}]
[null,"Total",{"$f":"SUM(C8:C13)","v":228}]

{"sheet":"2. Individual fire start info","index":3,"n_rows":287,"n_cols":25,"rows_kept":287,"cut":false,"hidden":false,"merged":[[3,22,3,24],[4,22,4,24],[5,22,5,24],[7,1,7,21],[11,1,11,2],[9,1,9,21],[13,1,13,11],[22,1,22,21],[24,1,24,21],[14,1,14,20],[15,1,15,18],[16,1,16,18],[18,1,18,18],[21,1,21,18],[19,1,19,18],[23,1,23,18],[20,1,20,18],[17,1,17,18],[25,1,25,18],[27,1,27,20],[26,1,26,21],[35,19,35,21],[33,1,33,4],[35,2,35,10],[28,1,28,18],[29,1,29,18],[35,11,35,13],[35,14,35,17]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"Powercor"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2021/22"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"\"Enter into this worksheet fire start data, from any IT system, which have been recorded by \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\". Note that fire starts must be in accordance with the definition of a fire start in the Order In Council.\"","v":"Enter into this worksheet fire start data, from any IT system, which have been recorded by Powercor. Note that fire starts must be in accordance with the definition of a fire start in the Order In Council."}]
[]
[null,"\"Fire\" should be interpreted using its common meaning and can be defined as a process in which substances combine chemically with oxygen from the air and typically give out bright light, heat and smoke. A fire should be recorded where there is evidence of smoking, charring, scorching, burning or any other evidence that a fire had occurred.  "]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"Powercor must provide:"}]
[]
[null,"Table 3 - Individual Fire Starts"]
[null,"   (1) Date - dd/mm/yyyy"]
[null,"   (2) Time - if known, the 24-hour time of the fire start hh:mm"]
[null,"   (3) Latitude and longitude of the fire start as decimal coordinates"]
[null,"   (4) Address of the property on which the incident occurred or closest to the incident"]
[null,"   (5) Asset number for the asset nearest the fire start"]
[null,{"$f":"\"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the \"&B1&\" network\"","v":"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the Powercor network"}]
[null,"   (7) Voltage on the line in which the fire start occurred (note: this may not be the nearest polyphase overhead line)"]
[null,"   (8) Network categorisation - CBD, Urban, Rural Long or Rural Short"]
[null,"   (9) Asset type of primary asset causing fire in accordance with OSIRIS asset categories"]
[null,"   (10) Where the asset involved in the fire is a transformer or an overhead or underground line, provide the phase, or phases, of the line or transformer"]
[null,"   (11) Kind of fire start in accordance with categories specified in Clause 5 of the F-factor Order-In-Council"]
[null,"   (12) Identify the location of the fire start in accordance with the categories specified in Clause 11(b) of the F-factor Order-In-Council"]
[null,"   (13) Provide the BOM fire danger rating applicable at the time of the fire start (data is available on the EM-COP website)"]
[null,{"$f":"\"   (14) \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\"'s record number for the incident\"","v":"   (14) Powercor's record number for the incident"}]
[null,"   (15) ESV's OSIRIS reference number for the incident"]
[null,"   (16) Free text description of the fault containing relevant comments from field reports "]
[]
[]
[]
[null,"Table 2: Individual Fire Starts"]
[]
[null,"Number","Fire starts",null,null,null,null,null,null,null,null,"Fire Type",null,null,"Risk Factors",null,null,null,"IRU \namount","Additional information"]
[null,null,"Date 1","Time 2","Latitude 3","Longitude 3","Address of incident 4","ID of \nnearest \nasset 5","ID of nearest \npolyphase \nline 6","Voltage of line in which \nfire start \noccurred 7","Network categorisation 8","Type of primary asset \ninvolved in fire start 9","Phase(s) of \nline or \ntransformer 10","Kind of fire start as per Clause 5\nof F-factor Order-In-Council 11","Location \narea 12","Location\nmultiplier","Fire \ndanger \nrating 13","Danger multiplier","Product of multipliers","DNSP record number 14","OSIRIS \n(ESV) reference \nnumber 15","Fault \ndescription 16"]
[{"$f":"COUNTA(C38:O38,Q38,T38:V38)","v":17},1,"2021-07-02","00:31",-38.378557000000001,142.55392000000001,"9 Drylakes Rd, Allansford VIC 3277, Australia",30136044,"WBL002","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",{"$f":"IF(O38=\"\",\"\",IF(O38=\"LBRA only\",0.2,IF(O38=\"HBRA only\",1,IF(O38=\"within electric line construction area\",19.8,IF(O38=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":1},"No forecast",{"$f":"IF(Q38=\"\",\"\",IF(Q38=\"No forecast\",0.1,IF(Q38=\"Low-moderate\",0.2,IF(Q38=\"High\",0.5,IF(Q38=\"Very high\",1,IF(Q38=\"Severe\",2,IF(Q38=\"Extreme\",3.5,5)))))))","v":0.1},{"$f":"IF(OR(P38=\"\",R38=\"\"),\"\",IF(AND(O38=\"within electric line construction area\",Q38=\"No forecast\"),1,P38*R38))","v":0.1},"INC-0014227","20210702PWA_01","Pole box faulted and caught fire. No ground Fire. ",null,null,"Overhead conductors"]
[17,2,"2021-07-02","19:55",-37.556676000000003,143.86255600000001,"211A HAVELOCK STREET,BALLARAT,VIC,3350",30260812,"BAN007","Low voltage AC (<1kV)","Rural Short"," - connector / termination","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0016307","20211209PWA_03","POA was on fire, still sparking a little after cust put it out with a fire extinguisher. Power was flicking on and off\nFound during OMS data review.\nNo photos provided.\nNo ground fire",null,null," - overhead conductor (bare; aluminium core steel reinforced)"]
[17,3,"2021-07-03","00:55",-37.867685000000002,144.82983200000001,"84 Railway St S, Altona VIC 3018",34027056,"AL012","Low voltage AC (<1kV)","Urban"," - luminaires (minor road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0016310","20211209PWA_04","Street light Pole number 964257 has been arcing with flame coming out the top. Light failed while caller talking (Ishan 0421739735). Arcing stopped after light went out.\nNo ground fire\nno useful photos supplied\nFound during outage data review",null,null," - overhead conductor (bare; all aluminium conductor)"]
[17,4,"2021-07-06","07:17",-35.817579000000002,144.23230599999999,"6342 Murray Valley Hwy, Cohuna VIC 3568",30302744,"CHA003","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0016314","20211210PWA_01","3 phase Junction box has melted and burnt beyond recognition \nNo ground fire\nFound during outage data review",null,null," - overhead conductor (bare; copper)"]
[17,5,"2021-07-10","09:18",-38.370206000000003,144.25910099999999,"150 Jarosite Rd, BELLS BEACH 3228",32073555,"WPD021","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0014379","20210712PWA_03","A customer contacted Powercor advising of a pole out front of property was on fire at the incident address.\nWhen crews arrived they found a FOLCB had failed and was significantly fire damaged.\nThe FOLCB had been attached to the LV crossarm and this asset also experienced significant fire damage, however the crossarm did not break.\nDebris from the damaged FOLCB had fallen to ground at the base of the pole, however due to the damp conditions and green vegetation no ground fire was started.\n No shock, injuries or 3rd party property damage was reported. ",null,null," - overhead conductor (bare; steel)"]
[17,6,"2021-07-13","17:59",-38.555821999999999,142.82038800000001,"Dairy Farm; 2249 Great Ocean Road, NIRRANDA SOUTH 3268",33103074,"WBL012","Low voltage AC (<1kV)","Rural Long"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0014424","20210714PWA_01","Powercor received a customer report of \"flame/fire on the wire\" at the incident address.\n When crews arrived they found a KRONE box on transformer pole \"NIRVINE 11\" had failed and was partially damaged by fire.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - overhead conductor (ABC)"]
[17,7,"2021-07-20","06:59",-38.585718999999997,143.04477800000001,"140 Waarre Rd, Waarre VIC 3269",32058987,"TRG013","12.7kV AC (SWER)","Rural Long"," - transformer (pole mounted)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0014497","20210721PWA_01","Customer reported that a pole mounted transformer has exploded and was on fire.\nOn arrival crew found that transformer was hit by lightning, causing it to rapture and leak oil. \nFire extinguished due to rain. \nNo ground fire.",null,null," - overhead conductor (covered uninsulated)"]
[17,8,"2021-07-22","20:56",-38.004635999999998,144.362899,"515 Windermere Rd, Lara VIC 3212",33042307,"FNS011","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0014519","20210723PWA_01","The fire brigade reported a pole fire at the incident location.\nCrew attended and found an FOLCB supplying a service CHP to a house had caught fire.\nThe FOLCB support arm was charred but the crew believed was OK to re-use. A melted fuse cover was found on the grass below.\nNo ground fire, no injuries/shocks and no third party damage identified. ",null,null," - overhead conductor (insulated)"]
[17,9,"2021-07-25","17:15",-38.080429000000002,144.49691899999999,"Twentynine Mile Rd, Point Wilson VIC 3212",30059431,"FNS032","22kV AC","Rural Short"," - overhead conductor (bare; copper)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0014594","20210729PWA_03","Customer reported no power at their site.\nThe crew were dispatched and found the spur fuses had operated, after a patrol of the line they identified 1 phase in a span of 22kV conductor had snapped and fallen to the ground between pole 81 (LIS-61428) and pole 82 (LIS-47840).\nThe fallen conductor was not alive, however a back feed from the spur substations caused minor burn marks to the wet ground.\nThere was no , shocks/injuries or third party damage reported.",null,null,"Service lines"]
[17,10,"2021-07-26","17:36",-38.476874000000002,143.14594700000001,"549 Bucks Rd, Simpson VIC 3266",32057848,"COB011","Low voltage AC (<1kV)","Rural Long"," - fuse (any other type)","single phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0014561","20210728PWA_01","A customer reported their meter panel had caught fire, a meter ping showed all phases were still on supply.\nThe crew attended and found evidence of a small fire on the fuse box Powercor side of the meter.\nThere was no gropund fire, no reported injuries or third party property damage.",null,null," - overhead service conductor (residential)"]
[17,11,"2021-07-27","19:31",-37.926786,144.72630799999999,"830 Aviation Rd, Werribee South VIC 3030, Australia",30108477,"WBE034","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0014562","20210728PWA_02","MFB reported pole fire at incident location.\nOn arrival the PCA Faults Crew have advised that there was a Pole fire on 22kV HV Inter Pole P14E 113 LIS-202696.\nThe Pole fire caused the HV X-arm to snap at the king-bolt , suspected HVI>\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - overhead service conductor (commercial / industrial)"]
[17,12,"2021-07-29","16:41",-37.490859,144.56685400000001,"171 Bacchus Marsh Rd, Gisborne VIC 3437",30031751,"GSB011","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0014601","20210730PWA_01","Vic fire advised of pole on fire outside at incident location\nOn arrival crew found a tall pine tree had fallen over and was resting on the red phase conductor and was smoke coming from tree.\nCrew advised base of tree was some 20m from conductor.\nBurn marks at point of contact on the tree.\nNo injuries or third party damage.",null,null," - overhead service conductor (subdivision / construction)"]
[17,13,"2021-07-31","03:46",-37.955958000000003,143.34239500000001,"13 Heriot Street, Lismore",30047097,"CDN004","Low voltage AC (<1kV)","Rural Long","Other","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0014637","20210802PWA_01","CFA reported fuse box fire.\nThe Crew attended and found a fire at the group metering position\nMeter position totally destroyed.\nThere was no reported injuries. ",null,null," - overhead service conductor (other)"]
[17,14,"2021-07-31","06:23",-38.596159,143.10699,"851 Melrose Rd, Princetown VIC 3269, Australia",32057588,"TRG002","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0014639","20210802PWA_02","Customer reported no supply and pole box on fire at incident location.\nOn arrival crew found a pole box had been on fire.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - underground service cable (residential)"]
[17,15,"2021-08-01","17:02",-37.78,144.736896,"210 Riding Boundary Rd, Ravenhall VIC 3023 (corner of Christies Road and Riding Boundary Road)",30350901,"TNA021","22kV AC","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0014640","20210802PWA_03","Crew reported that during a planned switching an isolator (MSI) appears have been incorrectly latched faulted.\nMolten material dropped into grass below.\nThere was a small patch of burnt grass around 1 sq mtr.\nThere was no reported injuries or third party property damage, ",null,null," - underground service cable (commercial / industrial)"]
[17,16,"2021-08-02","07:24",-38.308146999999998,142.30269100000001,"Penshurst-Port Fairy Rd, Kirkstall VIC 3283",32198314,"KRT013","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0014644","20210802PWA_04","Following reports of part supply a crew found a pole fire at incident location.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - underground service cable (subdivision / construction)"]
[17,17,"2021-08-07","23:50",-37.251491000000001,144.76409100000001,"123 Parkview Dr, Lancefield VIC 3435",33026352,"WND013","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,{"$f":"IF(OR(P54=\"\",R54=\"\"),\"\",IF(AND(O54=\"within electric line construction area\",Q54=\"No forecast\"),1,P54*R54))","v":0.45999999999999996},"INC-0014687","20210809PWA_02","Vic Emergency reported pole file. \nUpon arrival crew found that an FOLCB had completely burnt.\nHV fuse on road side of VIEW PARK 2 S/S had operated.  Concrete pole not damaged, adjacent FOLCB and crossarm charred. \nNo injury reported, no ground file reported.",null,null," - underground service cable (other)"]
[17,18,"2021-08-09","08:13",-37.853740999999999,144.85696300000001,"223 KOROROIT CREEK ROAD,WILLIAMSTOWN,VIC,3016",33074656,"BLT022","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0014700","20210810PWA_03","Customer advised of lost power and noted equipment at top of pole on fire.\nUpon arrival crew found that the LV switch (Krone box) had overheated & melted.  \nThere was no ground fire, no reported injuries or third party property damage",null,null,"Underground cables"]
[17,19,"2021-08-12","20:08",-38.202289999999998,144.26935,"402 Cochranes Road, Waurn Ponds",33045081,"WPD011","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0014732","20210813PWA_02","Report of pole fire at incident location.\nOn arrival crew found that a FOLCB had caught fire and burnt.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - underground cable"]
[17,20,"2021-08-13","17:08",-36.155337000000003,144.67687699999999,"668 Muller Rd Echuca West VIC 3564, Australia ",30265274,"ECA012","22kV AC","Rural Long"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0014771","20210817PWA_02","Emergency services advised pole fire at incident location.\nOn arrival crew found that a birds nest on a transformer had flashed over and caught fire.\nTransformer damaged.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - underground communications cable"]
[17,21,"2021-08-17","07:44",-37.739705000000001,140.98195000000001,"Border Rd, Strathdownie VIC 3312",32128340,"HTN002","12.7kV AC (SWER)","Rural Long"," - insulators","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0014775","20210818PWA_01","Following supply interruption a patroling field crew found a pole fire at incident location.\nThe top of Swer pole found burnt off.\nThere was no ground fire, no reported injuries or third party property damage.",null,null,"Poles"]
[17,22,"2021-08-17","14:08",-38.642899,143.10856999999999,"234 BOORINGA ROAD,PRINCETOWN,VIC,3269",32055280,"COB011","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0014778","20210818PWA_03","Report was received from fire comms regarding a pole fire at incident location.\nUpon arrival the crew found that the LV fuse box had overheated & caught fire. \nThere was no report that the fire got to the ground.\nThere was no injuries or third party property damage.",null,null," - pole (concrete)"]
[17,23,"2021-08-18","10:22",-38.358823000000001,142.290424,"211 Skenes Rd, Rosebrook VIC 3285",31031815,"KRT022","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0014784","20210819PWA_01","Report received of pole fire at incident location.\nOn arrival crew found a Junction box on fire.\nSome damage to pole found.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - pole (steel)"]
[17,24,"2021-08-24","09:17",-37.351768999999997,144.589992,"TREVETHAN 25 LAVENDER FARM ROAD WOODEND VIC 3442",32045791,"WND012","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0014853","20210825PWA_01","Emergency services reported tree on conductors smoking.\nOn arrival crew found that tree branch from outside clearance space had fallen and brought conductor to ground.\nThere was burn marks evident on tree branch\nThere was no ground fire, no reported injuries or third party property damage.\n",null,null," - pole (wood)"]
[17,25,"2021-08-27","09:44",-37.805548000000002,144.826786,"76-80 Vella Dr, Sunshine West VIC 3020, Australia",33106650,"SSE033","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0014905","20210827PWA_02","Report received of pole fire and small ground fire at incident location.\nOn arrival crew found a burnt out FSD at incident location.\nMolten material had fallen to ground and ignited a small patch of grass below.\nThere was no reported injuries or third party property damage.",null,null,"Crossarms"]
[17,26,"2021-09-01","18:43",-36.767282000000002,144.28799599999999,"UNIT1,5 YORK STREET,BENDIGO,VIC,3550",60269983,"BGO022","Low voltage AC (<1kV)","Urban"," - fuse (any other type)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0016326","20211213PWA_01","Request by REC to isolate supply after fire in meter enclosure.\nIsolated at pit for REC repairs\nRefer photos, damage to meter, meter board and customers switchboard.\nThere were no injuries\nFound during outage data review",null,null," - crossarm (wood)"]
[17,27,"2021-09-02","13:39",-37.641081,141.44734299999999,"187 Six Chain Rd, Sandford VIC 3312",31018121,"HTN002","12.7kV AC (SWER)","Rural Long"," - fuse (boric acid)","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0015006","20210909PWA_02","Customer advised of Insulator on pole on fire with smoke.\nOn arrival the crew found that a HV boric acid fuse had hung up. \nThe fire had self extinguished.\nThere was no injuries or third party property damage.",null,null," - crossarm (steel)"]
[17,28,"2021-09-02","15:46",-38.200749000000002,144.334191,"14 MANDAMA AVENUE,GROVEDALE,VIC,3216",32086941,"WPD012","Low voltage AC (<1kV)","Urban","Overhead conductors","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0016328","20211213PWA_03","Report received from customer of possible powerlines clashing in high wind.\nCraig 0410211386, (did not witness incident)\nSmall spot fire which self extinguished.\nThere was no reported injuries or third party property damage.\nLBRA area\nFound during outage data review\nNo photos of incident",null,null," - crossarm (other)"]
[17,29,"2021-09-06","12:19",-37.599805000000003,144.587346,"861 Gisborne-Melton Rd, Toolern Vale VIC 3337",30114142,"MLN012","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0016329","20211213PWA_04","Report received of an EDO fuse unit burnt in half.\nThere was no ground fire.\nFound during outage data review\nNo photos taken",null,null,"Overhead assets"]
[17,30,"2021-09-08","01:33",-38.164627000000003,144.392515,"68 Wilsons Rd, Newcomb VIC 3219",30060323,"GLE031","22kV AC","Rural Short"," - dropper / bridge","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0015008","20210909PWA_04","Following supply interruption crew found a possum had flashed over on Portarlington P66 ACR.\nFlash marks on isolators, damage to switch.\nFault current caused a HV dropper to rupture at HV switch P14 causing a small spot fire from debris that fell to ground.\nThere was no reported injuries or third party property damage.",null,null," - capacity balancing units"]
[17,31,"2021-09-11","18:28",-37.988351999999999,144.254042,"635-655 Sutherlands Creek Rd, Anakie VIC 3213",32082804,"CRO013","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0016330","20211213PWA_05","Following report of supply issue EDO fuse found burnt in half.\nNo ground fire or injuries.\nFound during outage data review",null,null," - connector / termination"]
[17,32,"2021-09-14","19:26",-37.728169999999999,144.70099500000001,"84 Reed Ct, Plumpton VIC 3335",30333222,"MLN021","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0015065","20210916PWA_01","Vic Fire reported a wire sparking at the incident location. Upon arrival, the crew found that the LV junction box on the pole caught fire. \nThere was no ground fire, no reported injuries or third party property damage.",null,null," - dropper / bridge"]
[17,33,"2021-09-16","14:50",-37.772258999999998,144.80966100000001,"10 Carrington Dr, Albion VIC 3020",30116091,"SU022","Low voltage AC (<1kV)","Urban"," - connector / termination","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0015082","20210917PWA_01","Fire brigade reported power line of fire.\nOn arrival crew found that an IPC connection had failed, dropping burnt material and starting a small grass fire approx. 0.2m square in area.\nThere was no injuries or third party property damage.",null,null," - guy wire"]
[17,34,"2021-09-17","15:43",-37.373756,144.508658,"220 Ashbourne Road Woodend 3442",30586869,"WND021","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0015127","20210920PWA_03","CFA advised powercor that a tree had contacted conductors and a small grass fire  of  1 sq m ensued.\n",null,null," - insulator tie wires / connections"]
[17,35,"2021-09-20","18:30",-35.12135,142.02168499999999,"Nestor Road Walpeup 3507",32147516,"OYN001","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0015160","20210923PWA_01","Powercor received a report of a pole fire , attending crew found Pole fire at LIS: 20402, CFA attended, minimal ground fire in green crop, burning material on ground",null,null," - insulators"]
[17,36,"2021-09-20","16:55",-36.822777000000002,144.24432100000001,"68 Phillis Street Kangaroo Flat 3555",33009115,"BET004","22kV AC","Rural Short"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0015220","20211001PWA_01","Customer reported a pole fire and CFA attended. Crew found that the HV insulated transformer leads had failed, no ground fire.",null,null," - tower"]
[17,37,"2021-09-21","00:27",-37.987596000000003,143.039749,"136 Darlington-Carranballac Rd, Darlington VIC 3271",30047412,"CDN006","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0015132","20210921PWA_01","Crew patrolling line after protection activity found a large branch had detached from a  tree  and  contacted line and a small grass fire was present.\nest fire size 2 sq meters ",null,null," - traction lines"]
[17,38,"2021-09-21","17:38",-38.355688000000001,144.29096999999999,"8 Broadbeach Rd, Jan Juc VIC 3228",30074993,"WPD021","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,{"$f":"IF(OR(P75=\"\",R75=\"\"),\"\",IF(AND(O75=\"within electric line construction area\",Q75=\"No forecast\"),1,P75*R75))","v":0.45999999999999996},"INC-0016333","20211213PWA_07","EDO fuse candled and burnt in half\nno ground fire.\nFound during ouitage data review",null,null,"Underground assets"]
[{"$f":"COUNTA(C76:O76,Q76,T76:V76)","v":17},39,"2021-09-26","01:17",-37.637397999999997,144.35307399999999,"44 DUNBAR ROAD,MYRNIONG,VIC,3341",30104034,"BMH003","Low voltage AC (<1kV)","Rural Long"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",{"$f":"IF(O76=\"\",\"\",IF(O76=\"LBRA only\",0.2,IF(O76=\"HBRA only\",1,IF(O76=\"within electric line construction area\",19.8,IF(O76=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":1},"No forecast",{"$f":"IF(Q76=\"\",\"\",IF(Q76=\"No forecast\",0.1,IF(Q76=\"Low-moderate\",0.2,IF(Q76=\"High\",0.5,IF(Q76=\"Very high\",1,IF(Q76=\"Severe\",2,IF(Q76=\"Extreme\",3.5,5)))))))","v":0.1},0.1,"INC-0015172","20210927PWA_01","Customer reported top of pole across the road is on fire, sparking to the ground.\n\nOn arrival, the crew found that the 2 FOLCB’s and the FSD box (transformer isolator) on the substation pole LIS 100536 (POOLE 3 S/S) have caught fire. ",null,null," - LV pillar"]
[17,40,"2021-10-02","19:06",-38.345498999999997,141.606292,"CHRISTIAN COMMUNITY COLLEGE, 119 BENTINCK STREET, PORTLAND, VIC, 3305",35108765,"PLD004","Low voltage AC (<1kV)","Rural Short"," - luminaires (minor road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0015230","20211004PWA_02","Powercor received a customer call advising that a street light was on fire and smoke still coming from light in front of the incident address. When crews arrived they found a public light lantern head (HP Sodium 150W) had failed internally and required replacement. Previous days had experienced significant rain.  Lantern head fire was internal and very small and self extinguished before crews attended. No ground fire ",null,null," - services pit"]
[17,41,"2021-10-03","18:24",-36.763353000000002,142.18928399999999,"4298 Henty Hwy, Haven",30242728,"HSM002","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0015232","20211004PWA_03","Vicfire reports fire start at above location. ACR P24 Toolondo tripped to LO. Crew attended. Found small branch on line. Residents report mini tornado had occurred at time of outage. Branch had contacted both HV and LV conductors. CFA had extinguished fire but not onsite when crew arrived. Crew cleared branch from line and inspected conductors. No damage obvious",null,null,"Transformers"]
[17,42,"2021-10-05","18:21",-37.434899000000001,143.39736400000001,"72 High St, Beaufort",31001108,"BAS011","22kV AC","Rural Long"," - dropper / bridge","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0015281","20211007PWA_03","Customer called to advise flickering lights and sparking/arching at power pole. CFA was in attendance. Crew attended and found one HV lead on 1ph TX had melted ",null,null," - transformer (pole mounted)"]
[17,43,"2021-10-06","07:33",-38.417471999999997,142.874313,"144 Missens Rd, Ecklin South VIC 3265",33035345,"TRG024","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0015269","20211007PWA_02","Received notification of pole fire. Upon arrival crew noted that FOLCB caught fire on pole LIS 407887",null,null," - transformer (kiosk mounted)"]
[17,44,"2021-10-10","15:40",-35.984290999999999,142.9127,"2 Johnson St S, Birchip VIC 3483",30139353,"CTN001","Low voltage AC (<1kV)","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0015314","20211011PWA_01","VicFire reported pole fire at the incident address.\nUpon arrival Charlton LSA fault crew found that a piece of foil insulation had been blown onto LV conductors nearest to pole LIS 928446.\nThis resulted in a flash over resulting in insulation falling to ground alight, subsequently igniting grass below, a fire of 1m x 1m resulted.\nThere was no injuries or third party property damage.",null,null," - transformer (ground outdoor mounted)"]
[17,45,"2021-10-11","19:30",-38.657161000000002,143.20590300000001,"320 Wiridjil Rd, Princetown 3269",33035943,"COB011","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0015335","20211012PWA_01","A customer called to report a pole fire at the incident location.\nOn arrival the crew found that a 3 phase fused mains box on the concrete substation pole had caught fire. \nThe box was totally destroyed, and hot debris had fallen to the ground, however there was no ground fire due to wet green grass. \nThere was no ground fire, no injuries or third party property damage.",null,null," - transformer (indoor chamber mounted)"]
[17,46,"2021-10-12","14:31",-38.297559,142.81847500000001,"7721 Princes Hwy, Garvoc 3265",33098566,"TRG-WBL1","66kV AC","Unknown"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0015362","20211014PWA_03","Firecoms reported a small grassfire caused by Powercor Assets at the incident location.\nOn arrival the crew found that a crow had caused a flashover on the top insulator of the TRG-WBL No1 66kV Line Pole 1298 (LIS-408468). \nThe crow fell to the ground igniting a grassfire of approx 50m x 50m= 2500m2 in size. \nThe CFA extinguished the fire. \nThere was no injuries or third party property damage.",null,null," - transformer (any other type)"]
[17,47,"2021-10-13","10:30",-35.887618000000003,142.00403900000001,"4583 Hopetoun-Rainbow Rd, Rainbow VIC 3424",32092107,"NHL015","22kV AC","Rural Long"," - fuse (boric acid)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0015361","20211014PWA_02","During outage works crew found burnt grass and dead magpie under SWER ISO pole LIS 18675.\nUpon further investigation crew noted burn marks on Boric Acid fuse. \nBurnt grass area was 2m square. \nThere was no injuries, no third party property damage.\n",null,null," - measurement transformer (current transformer)"]
[17,48,"2021-10-13","19:28",-35.185499999999998,143.348116,"45 MONASH AVENUE,NYAH WEST,VIC,3595",32156161,"SHL002","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0015373","20211015PWA_01","Vic Emergency reported pole fire at the incident address,\nUpon arrival fault crew found that an intermediate crossarm on pole 35 Managatang burnt through at the kingbolt position.\nConductors remained alloft, suspended by the crossarm straps and the t/off subsidary circuit below.\nManagatang P1 ACR tripped to lockout for the incident.\nNo ground fire or third party damage.",null,null," - measurement transformer (voltage transformer)"]
[17,49,"2021-10-15","18:32",-38.762529000000001,143.62989999999999,"400 Barham River Road, APOLLO BAY 3233",31032580,"CLC003","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0015383","20211019PWA_02","Powercor received a report of sparking wire from Fire Comms with brigade enroute to the incident address. When crews arrived on site in the dark, the weather conditions had deteriorated with heavy rain and strong winds in the area. Through the rain, the crews observed a large tree branch had broken from the main tree trunk and was resting against a HV conductor, mid span between P1 & P2 Buncle Spur.  The top foliage of the branch was arcing and small flames were observed. The Barham River runs adjacent the Buncle Spur at this point and was starting to flood with the heavy rain in the area. The flooded river had extended under the HV OH conductors and restricted access to the HV Conductor  / branch contact point for both the crews and the attending Fire Services.",null,null," - measurement transformer (capacitive voltage transformer)"]
[17,50,"2021-10-20","17:14",-37.654443999999998,143.96178,"172 Triggs Rd, Yendon VIC 3352, Australia",30543611,"BAS023","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0015437","20211021PWA_01","Vicfire reported a grass fire at the above address.\nCFA attended. \nCrew attended and found fuse box on pole had melted, dropping hot debris to the ground, starting grass fire of 25m x 2m in area on road reserve. \nAdjacent tree and  fence posts burnt. No other private property damaged. No shocks or injuries.",null,null,"Fuses and switchgear"]
[17,51,"2021-10-26","13:35",-34.540816,142.33012099999999,"58 Valencia Grove Colignan 3494",30097950,"RCT013","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0015509","20211214PWA_03","Customer reported phase has dropped, can see fuse has dropped from power pole clear access.\nCrew found a candled EDO fuse.\nno ground fire.\nFound during outage data review\nNo photo taken",null,null," - fuse (boric acid)"]
[17,52,"2021-10-27","16:45",-38.572028000000003,143.047068,"305 WAARRE ROAD,WAARRE,VIC,3269",30293189,"COB021","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0015520","20211028PWA_03","FireComms reporting pole fire which has spread to grass at incident location.\nCFA attended.\nOtway Gas plant reported ground fire has started from PAL asset and spread to grass.\nThere was no reported injuries.",null,null," - fuse (EDO fuse)"]
[17,53,"2021-10-29","00:00",-38.306910000000002,143.31438399999999,"M8V7+6Q Pomborneit VIC (Princes hwy Stonyford)",32058611,"CLC-CDN","66kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","within electric line construction area",19.8,"Low-moderate",0.2,3.9600000000000004,"INC-0015538","20211101PWA_03","Report received of a pole being blown over during wind storm conditions (Princes hwy Stonyford)\nOn arrival crew found that pole CLC-CDN 850 had fallen over.\n\n\n",null,null," - fuse (Fault Tamer)"]
[17,54,"2021-10-30","15:59",-37.58746,144.45905200000001,"2043 Gisborne Rd, Coimadai VIC 3340",32168991,"MLN022","22kV AC","Rural Short"," - transformer (indoor chamber mounted)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0016342","20211214PWA_02","pole fire at LIS 933924, green conditions for grass. customer not on site, advised he may contact neighbour to see if they can call CFA\nTransformer on pole is on fire. called in by Alan 0438796333\nNo photos\nFound during outage data review\nNo Ground fire",null,null," - fuse (powder filled)"]
[17,55,"2021-11-01","15:45",-38.005164000000001,143.85863699999999,"CRAIGWOOD,1944 WINGEEL ROAD,SHELFORD,VIC,3329",32071929,"GL012","12.7kV AC (SWER)","Rural Long"," - insulators","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016359","20211216PWA_03","P52 Messy swer conductor on deck, pole still burning, conductor came off insulator and resting against pole, until it burnt through and let go.\nCrew to make safe and repair tomorrow.\nPole in middle of paddock access is not clear, quite muddy.\nNo ground fire, no reported injuries or third party property damage\nFound during outage data review",null,null," - fuse (any other type)"]
[17,56,"2021-11-02","17:30",-36.703982000000003,144.21775299999999,"4 Dempsey Street, Sailors Gully",33023096,"BET001","Low voltage AC (<1kV)","Rural Long"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","within electric line construction area",19.8,"Low-moderate",0.2,3.9600000000000004,"INC-0015563","20211103PWA_02","Crew attended and found that a FSD had overheated, igniting grass at base of pole.\nThere was approx 2 sq mtrs of grass burnt.\nThere was no injuries or third party property damage.",null,null," - circuit breaker"]
[17,57,"2021-11-05","15:49",-37.674028999999997,144.56182899999999,"10 Argyll CIRCUIT, MELTON WEST, VIC 3337",34006906,"MLN023","Low voltage AC (<1kV)","Urban"," - LV pillar","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0015684","20211108PWA_01","Few customers reported a Pillar box on fire. Pillar located inside customer’s property at 10 Argyll circuit.\nOn arrival, the Powercor crew found that the service pillar at 10 Argyll circuit  have sustained internal heat & fire damage. \nThe grass surrounding the Pillar, approximately 200mm wide, had burnt but the fire extinguished by itself.",null,null," - switch (disconnector/isolator)"]
[17,58,"2021-11-06","07:16",-36.220841,143.29660699999999,"491 Bennetts Rd, Teddywaddy VIC 3527",32028634,"CTN006","12.7kV AC (SWER)","Rural Long"," - fuse (EDO fuse)","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0016362","20211216PWA_04","Customer reports fuse down at substation.\nOn arrival crew found an EDO had hung up and subsequently burnt in half.\nThere was no ground fire.\nFound during outage data review\nNo photos taken",null,null," - switch (earth)"]
[17,59,"2021-11-18","17:20",-35.048479,142.250091,"332 Trimble Road Ouyen",32143893,"OYN001","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"Severe",2,2,"INC-0016070","20211119PWA_01","Report received of large grass fire at incident location.\nOn arrival crew found a fallen pole and a large crop fire in progress.\nThere was no reported injuries, possible crop loss and fence damage.\n",null,null," - switch (FuseSaver)"]
[17,60,"2021-11-19","07:17",-37.652078000000003,143.01644300000001,"218 Tara Rd, Westmere VIC 3351",32111553,"ART033","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016364","20211216PWA_05","Following report of supply issues crew found an edo fuse had hung up and burnt in half\nThere was no ground fire\nFound during outage data review\nNo photos",null,null," - switch (any other type)"]
[17,61,"2021-11-20","15:30",-38.774537000000002,143.42730399999999,"3360 Great Ocean Rd, Glenaire 3238",33039195,"CLC003","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016082","20211122PWA_01","Following a feeder outage, Fire comms reported wires down at the incident location. \nOn arrival the crew found that the customer had felled a tree onto the single phase HV conductors between P45A Hordern Vale LIS-18844 & P46 Hordern Vale LIS-20685. \nThe CLC003 feeder CB went to lockout, and one HV conductor broke and fell to the ground. \nA small burn mark approx 30cm long was found on one of the tree branches, but no ground fire was reported. There were no injuries or other damage reported.",null,null,"SCADA, network control and protection systems"]
[17,62,"2021-11-23","08:27",-34.799073,142.68358699999999,"adjacent to 1813 ANNUELLO-WEMEN ROAD WEMEN VIC 3549",30278135,"WMN021","22kV AC","Rural Short"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0016110","20211123PWA_02","Vic fire reported fire at incident location.\nOn arrival crew found that a magpie had flashed over on structure, falling to ground and igniting grass stubble.\nThere was no reported injuries.",null,null," - audio frequency load controller (AFLC)"]
[17,63,"2021-11-26","16:13",-36.309131999999998,144.431949,"697 TENNYSON SOUTH RD - TENNYSON VIC 3572",30121921,"SHP012","22kV AC","Rural Long"," - guy wire","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0016173","20211129PWA_01","Call received from Vic fire of grass fire at incident location,.\nOn arrival crew found that a Ground stay had dislodged allowing pole to lean, the disturbance to conductors ignited a grass fire.\nThere was no reported injuries.",null,null," - arc suppresion coil"]
[17,64,"2021-11-27","11:17",-35.764902999999997,143.908536,"204 Taverner Rd, Kerang VIC 3579",30353960,"KGT004","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"High",0.5,0.5,"INC-0016175","20211129PWA_02","Report received of conductor down and grass fire at incident location.\nOn arrival crew found 22kv conductor on ground.\nCrew observed insulator and conductor damage consistent with a potential lightning strike.\nThere was an approx .7 HA grass fire, no reported injuries.\n",null,null," - automatic circuit recloser (ACR)"]
[17,65,"2021-11-27","10:51",-35.729958000000003,143.89150100000001,"54 Lindsay Rd, Kerang VIC 3579",33021310,"KGT004","22kV AC","Rural Long"," - automatic circuit recloser (ACR)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0016180","20211129PWA_03","Report from vic fire of smoking pole and fire at incident location.\nOn arrival crew found that a bird had flashed over on ACR structure, falling to ground and burning small area of grass.\nThere was no reported injuries or third party property damage.",null,null," - communications linear assets"]
[17,66,"2021-11-30","19:30",-36.334882999999998,141.69132200000001,"Off Western Hwy Nhill - 800 East of Jeparit-Nhill Rd",32097874,"NHL015","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0016248","20211201PWA_01","At 17:30 hrs a header operating in a wheat paddock made contact with the HV conductor between Pole 1 and Pole 2 Balrootan Spur. \nThe contacted caused the NHL015 feeder CB to trip to Lockout. \nThe contact caused a grass fire in the wheat paddock which burnt an area approx. 100 x 150 metres.\nHeader operator felt tingle in driver seat when header hit HV. Spent night in hospital under observation. Discharged 1/12 following being given all clear.\n",null,null," - communications network assets"]
[17,67,"2021-11-30","20:58",-38.110411999999997,144.34357399999999,"246 C136 Thompson Road, North Geelong VIC 3215",35093754,"GL024","Low voltage AC (<1kV)","Urban"," - luminaires (minor road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016269","20211202PWA_01","Report received from FRV of pole fire at incident location.\nOn arrival crew found that a HPS lantern had caught fire\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - communications site infrastructure"]
[17,68,"2021-11-30","13:27",-38.195041000000003,144.63083800000001,"720 Andersons Rd, Mannerim VIC 3222",32083747,"DDL012","22kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0016273","20211203PWA_02","Passer-by noticed tree branches contacting overhead high voltage conductor causing smoke.\nOn arrival crew found trees in contact with HV conductors.\nEvidence of arcing and burning.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - field devices"]
[17,69,"2021-12-02","08:20",-37.780211000000001,143.37037699999999,"120 SMITHS ROAD,BRADVALE,VIC,3361",30045523,"CDN004","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016281","20211204PWA_03","Customer reports tree branch is touching mains wire and sparking including making arching noises, line connected at both ends, possibly happened overnight, cust still has supply.\nAttending crew/s  found branch contacted 1 Hv conductor and had burnt through, conductor down & upon follow up crew indicated branch had burnt through. No Images taken\nLarge  EUC tree from far side of shelter belt fell through shelter belt and contacted line ",null,null," - local network wiring assets"]
[17,70,"2021-12-03","16:41",-36.154310000000002,144.18591799999999,"14 JONES LANE, MOLOGA, VIC, 3575",30025785,"CHA006","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (residential)","single phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"High",0.5,{"$f":"IF(OR(P107=\"\",R107=\"\"),\"\",IF(AND(O107=\"within electric line construction area\",Q107=\"No forecast\"),1,P107*R107))","v":0.5},"INC-0016284","20211206PWA_02","Vic emergency reported wire brought down by truck and customer reported wire sparking.\nOn arrival, crew found service cable that had broken away from house come down near road.  \nCustomers raiser bracket had also been pulled from house.  \nCustomer reported a tipper truck leaving adjacent property had tipper up still and had collected wire. \nSmall grass fire less than 1m sq.  No injuries.",null,null," - master station assets"]
[17,71,"2021-12-03","22:13",-36.141911,145.13986299999999,"10 HANCOCKS BRIDGE ROAD, KOTUPNA VIC 3638",32193593,"KYM004","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0016287","20211206PWA_03","Vic Fire reported wires down at the above location.  \nOn arrival, crew found a large tree approx 120ft high had fallen across the powerlines and the lines were just off the ground.  \nCrew advised tree was outside clearance zone.  \nNo asset damage.\nCFA in attendance.  \nGrass fire approx 15m x 30m.  No injuries or third party damage.  ",null,null," - neutral earthing resistor"]
[17,72,"2021-12-05","12:41",-38.223016999999999,144.58855800000001,"395 BANKS ROAD  MANNERIM 3222 ",33044293,"DDL024","22kV AC","Rural Short"," - fuse (powder filled)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0016289","20211206PWA_05","MFB reported Xrm fire.\nHV fuse unit on concrete pole had flashed over causing a small ground fire \nFlashover due to bird contact\nThere was a small ground fire, no reported injuries or third party property damage",null,null," - oil-filled circuit recloser (OCR)"]
[17,73,"2021-12-06","10:15",-36.677185000000001,144.36464799999999,"349 Huntly-Fosterville Rd, Bagshot VIC 3551",33018499,"EHK031","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016588","20220117PWA_02","Following lightning strike, EDO fuse found hung up and burnt.\nThere was no ground fire, no reported injuries or third party property damage\nFound during outage data review",null,null," - rapid earth fault current limiter (REFCL)"]
[17,74,"2021-12-08","14:12",-37.940061,144.16916900000001,"1921 Steiglitz Rd, Maude VIC 3331, Australia",32070162,"GL015","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016591","20220117PWA_03","Evidence of burnt crossarm found during inspection, exact data of event unknown.\nNo ground fire\nFound during outage data review",null,null," - surge diverter"]
[17,75,"2021-12-14","14:41",-37.199114000000002,143.75150300000001,"105 Cobbs Rd, Mount Glasgow VIC 3371, Australia",32026010,"MRO007","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016354","20211216PWA_01","Firecom advised of Fire in paddock near pole .  \nAttending crew  found LV service termination (dog bone) had burnt and  small grass fire at base of pole",null,null," - voltage regulator"]
[17,76,"2021-12-15","07:39",-36.146667999999998,141.68896699999999," 2060 NHILL-NETHERBY ROAD,NHILL,VIC,3418",32097944,"NHL016","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0016357","20211216PWA_02","Powercor received a report of a Cross arm fire at Pole 103 Nhill Netherby Rd just north of intersection of Lorquon Road.\nAttending crew found HV cross-arm had burnt",null,null,"Public lighting"]
[17,77,"2021-12-16","07:25",-37.463303000000003,144.00275600000001,"Loatta, 200 Dean-Mollongghip Rd, Dean VIC 3363, Australia",32006849,"BAN008","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016878","20220218PWA_04","Fuse hanging did start fire but now out. \n4 wheel drive and ladder required due to canola crop and creek.\nno ground fire\nFound during outage  data review, no photos",null,null," - brackets (major road)"]
[17,78,"2021-12-17","13:25",-36.542917000000003,145.243257,"520 Langham Rd, Dhurringile VIC 3610, Australia",32192493,"MNA034","Low voltage AC (<1kV)","Rural Long"," - fuse (any other type)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0016391","20211220PWA_01","Customer reported power pole is on fire currently and All supply lost at pump. Meter box is burnt out. Wires crackling that come from Langham RD\n\nCrew found  melting and burning  on meter, Meter panel and heat damage to customers switchboard occurred when customer was starting irrigation pump.",null,null," - brackets (minor road)"]
[17,79,"2021-12-19","13:55",-36.148451999999999,144.00103899999999,"948 Mologa-Durham Ox Rd, Yarrawalla VIC 3575, Australia",30026112,"CHA006","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"Very high",1,1,"INC-0016394","20211220PWA_02","Member of the public reported pole being struck by lightning and evidence of ground fire at the incident location.\n Upon arrival fault crew confirmed that pole had been struck by lightning, crew used their available water to douse the ground as there was still residual heat in smoldering material. Approximately 3M x 3M area around pole burnt.\nPole had largely lost sap wood and remained in service, crew marked  to be replaced in next 24 hours.\nAppears  the lightning struck below the pole top not conductor\n\nESV ref ?? 1789589 ( digit missing)",null,null," - lamps (major road)"]
[17,80,"2021-12-19","10:41",-38.210475000000002,143.33615,"920 Pomborneit - Foxhow Road, Pomborneit North",30042480,"CDN002","12.7kV AC (SWER)","Rural Long"," - insulators","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016396","20211220PWA_03","Vic Emergency reported a pole fire at the above address. \nCrew attended and confirmed the top of the pole had burnt off at P50 Lucas Spur.\n No ground fire. ",null,null," - lamps (minor road)"]
[17,81,"2021-12-21","13:16",-36.494210000000002,144.98482200000001,"1086 GIRGARRE-RUSHWORTH ROAD,STANHOPE,VIC,3623",32191746,"SHP021","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0016410","20211221PWA_05","Customer  reported an excavator has pulled down some wires out the front of Jacobs property. a grass fire started but they were able to control. adv Jacob to call SES if he thinks they are needed\nAttending crew found  excavator was no longer present,\n HV conductor down between poles 17 & 18  and an area of burnt ground of some 5 by 50 M in private property.\nexcavator had apparently  been clearing  irrigation channel ",null,null," - luminaires (major road)"]
[17,82,"2021-12-23","11:50",-37.685099000000001,143.35851,"62 MONTGOMERY STREET,SKIPTON,VIC,3361",30001813,"BAS033","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016425","20211223PWA_01","Contractor worker driving past identified cross arm had severe burn damage  and provided image.\nunknown when damage occurred.\nThere was no ground fire, no reported injuries or third party property damage",null,null," - luminaires (minor road)"]
[17,83,"2021-12-23","08:37",-36.251330000000003,145.548655,"963 JUBILEE ROAD,KATANDRA WEST,VIC,3634",30261786,"SHN024","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0016426","20211224PWA_01","Crew  attending fault found EDO fuse had hung up and  Burnt.\nNo ground fire",null,null," - poles / columns (major road)"]
[17,84,"2021-12-24","09:27",-36.250681,145.55047200000001,"963 Jubilee Rd, Katandra West VIC 3634",33107574,"SHN024","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0016597","20220118PWA_01","Following customer report of supply issues an EDO fuse barrel was found to have hung up and subsequently burnt in half.\nThere was no ground fire, no reported injuries or third party property damage.\nFound during outage data review\nNo photos found",null,null," - poles / columns (minor road)"]
[17,85,"2021-12-26","21:44",-37.421380999999997,143.37262999999999,"29 Back Raglan Road Beaufort 3373",33005477,"BAS011","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016457","20211230PWA_05","Customer reported a sparking wire started a grass fire.\nUpon arrival the fault crew found that an edo fuse had been candling on BACKRAGLAN 11 s/s, LIS: 59321 and this had caused a ground fire with the area burnt being 4mx2m.\nThere was no reported injuries or third party property damage.",null,null,"Other "]
[17,86,"2021-12-29","09:48",-38.269558000000004,144.65652800000001,"60 MERCER STREET, QUEENSCLIFF",30059603,"DDL012","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016448","20211230PWA_01","The fire brigade reported a sparking wire on the ground.\nCrew were dispatched to investigate. \nOn arrival they found a neutral screened service wire sparking on the ground and burnt around 1 sq metre . \nThere were no reported injuries",null,null," - connection box"]
[17,87,"2021-12-30","15:45",-36.680852000000002,143.928417,"O/S #ALLOT. 144 BRIDGEWATER-MALDON RD - BRIDGEWATER (104 MORSES RD - BRIDGEWATER)",30260114,"BET001","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0016481","20220104PWA_04"," Fire brigade report grass fire has burnt pole 73.\n\nUpon arrival crew made the area safe and CFA had noted that they had found a piece of burnt off fencing wire at the base of pole 72 (LIS-741338) which they believe had started the fire of approximately 20 hectares (200, 000m²) beginning in road reserve and blowing into private property,\nCrew noted that there was still a piece of the same wire across the centre phase insulator (most likely left there by a bird) ",null,null," - earth / earthing"]
[17,88,"2021-12-30","20:42",-36.539332000000002,145.42057,"95 Kays Rd, Arcadia VIC 3631, Australia",32193018,"STN021","12.7kV AC (SWER)","Rural Short"," - fuse (EDO fuse)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0016482","20220104PWA_05","Customer reported fire at base of pole.\nAttending crew found evidence of a small ground fire at the base of the pole"]
[17,89,"2021-12-31","14:41",-37.869562999999999,144.81763100000001,"142 Blyth Street Altona  VIC  3018",31023129,"AL006","Low voltage AC (<1kV)","Urban"," - connector / termination","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0016480","20220104PWA_03","Melted D clamp resulted in small ground fire on nature strip at transformer pole. "]
[17,90,"2022-01-01","06:42",-36.607047999999999,142.124863,"1611 WESTERN HIGHWAY - PIMPINIO VIC 3401",33048855,"HSM006","22kV AC","Rural Long"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"Very high",1,1,"INC-0016484","20220104PWA_07","fire comms reported Wires sparking and grass fire.\nAttending crew found that a grass fire of some 1/4 acre had occurred  around the base of pole 132. ",null,null,"Extra low voltage AC (<50V)"]
[17,91,"2022-01-01","14:22",-37.606428000000001,141.39721599999999,"92 Gilmores Rd, Casterton 3311",30141084,"HTN002","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0016492","20220105PWA_01","Vicfire reported a grassfire at the incident location, on arrival the crew found that a HV fuse had candled and fallen to the ground starting a grassfire. ",null,null,"Low voltage AC (<1kV)"]
[17,92,"2022-01-02","13:20",-35.398257000000001,143.11379199999999,"324 McCLELLAND ROAD - WAITCHIE VIC 3544",33069750,"SHL001","Low voltage AC (<1kV)","Rural Long"," - fuse (any other type)","single phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0016488","20220104PWA_09","customer reported that at the switch board main fuse had caught fire. looks like not on fire anymore. \nattending crew found  hole burnt in wooden meter board ",null,null,"2.2kV AC"]
[17,93,"2022-01-04","09:06",-35.927563999999997,143.226551,"23 Blacks Ln, Dumosa VIC 3527",30144686,"CTN003","22kV AC","Rural Long"," - pole (concrete)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0016493","20220105PWA_02","Fire authority advised of wire down with grass fire.\n\nUpon arrival the crew found that a road works truck trailer had hit the concrete pole & snapped it. There was approximately 40 x 5 meters grass fire.",null,null,"6.6kV AC"]
[17,94,"2022-01-04","20:24",-37.566343000000003,143.93432100000001,"Ex Govt Truck Centre, 3196 Old Melbourne Rd, Warrenheip VIC 3352",31002028,"BAN003","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016497","20220106PWA_01","Vic Fire reported pole fire at the above location.\nOn arrival crew found Blue centre phase EDO bracket had tracked due to light rain and pole was burnt at this position on the pole. ",null,null,"11kV AC"]
[17,95,"2022-01-04","23:06",-37.581966999999999,143.820369,"13 Warratta Ave, Delacombe VIC 3356",32002002,"BAS033","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016498","20220106PWA_02","Vic fire reported a pole fire at the above location, crew on arrival found a hv cross arm burnt off and had dropped onto the LV circuit below, HVI.",null,null,"12.7kV AC (SWER)"]
[17,96,"2022-01-04","23:31",-37.563209000000001,143.848377,"759 Dana St Ballarat 3350",32005173,"BAS014","22kV AC","Urban"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016499","20220106PWA_03","Vic Fire reports a cross arm at the above location, on arrival the crew found the HV Cross arm was partially burnt and will require replacement",null,null,"22kV AC"]
[17,97,"2022-01-04","21:05",-37.531638999999998,143.826134,"59 hastings st Wendouree 3355",30013263,"BAN004","22kV AC","Urban"," - fuse (powder filled)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016500","20220106PWA_04","Vic Fire reported a pole fire at the above location, on arrival crew found one powder filled fuse had become disconnected from the cross arm after the arm had partially burnt.",null,null,"33kV AC"]
[17,98,"2022-01-05","02:45",-37.564726999999998,143.866062,"13 Porter St, Bakery Hill VIC 3350, Australia",32002214,"BAS012","22kV AC","Urban"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016495","20220105PWA_04","Vic Fire reported a cross-arm fire at the above location, on arrival the crew found a HV cross-arm had burnt through and dropped down onto the LV circuits",null,null,"66kV AC"]
[17,99,"2022-01-05","03:05",-37.285100999999997,142.92624699999999,"47A View Point St, Ararat VIC 3377",30085258,"ART034","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016501","20220106PWA_05","Vic fire reported a pole fire at the above location, on arrival the crew found the HV cross arm burning and had broken but not dropped down into the LV.",null,null,"132kV AC"]
[17,100,"2022-01-05","05:03",-37.299598000000003,142.933941,"110 BRYANT ROAD,ARARAT,VIC,3377",32102112,"ART034","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016502","20220106PWA_06","Vic fire reported pole fire \nattending crew found cross-arm had burnt and required replacement ",null,null,"220kV AC"]
[17,101,"2022-01-05","14:27",-38.074573000000001,142.407871,"800 HAWKESDALE-MINJAH ROAD,MINJAH,VIC,3276",33099942,"KRT012","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016503","20220106PWA_07","Powercor received report that a tree trimmer cut through wire, has caused a fire. fire truck on its way.\nAttending crew found that HV conductor had been severed by rotating saw  and several small burns on the ground observed.",null,null,"330kV AC"]
[17,102,"2022-01-05","09:34",-38.365732999999999,141.592848,"151 Fawthrop St, Portland VIC 3305",30088915,"PLD006","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,{"$f":"IF(OR(P139=\"\",R139=\"\"),\"\",IF(AND(O139=\"within electric line construction area\",Q139=\"No forecast\"),1,P139*R139))","v":4.0000000000000008E-2},"INC-0016504","20220106PWA_08","Customer reports loud bang came from the pole/transformer outside his property; and that also his neighbours wall has become singed since then. Power also went off.\n Upon arrival crew found that HV Crossarm burnt and HV fell in to service lines",null,null,"500kV AC"]
[{"$f":"COUNTA(C140:O140,Q140,T140:V140)","v":17},103,"2022-01-05","02:08",-37.644618999999999,141.015747,"1584 Old Lindsay Rd, Strathdownie 3312",32131166,"HTN002","12.7kV AC (SWER)","Rural Long"," - insulators","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O140=\"\",\"\",IF(O140=\"LBRA only\",0.2,IF(O140=\"HBRA only\",1,IF(O140=\"within electric line construction area\",19.8,IF(O140=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"Low-moderate",{"$f":"IF(Q140=\"\",\"\",IF(Q140=\"No forecast\",0.1,IF(Q140=\"Low-moderate\",0.2,IF(Q140=\"High\",0.5,IF(Q140=\"Very high\",1,IF(Q140=\"Severe\",2,IF(Q140=\"Extreme\",3.5,5)))))))","v":0.2},0.91999999999999993,"INC-0016505","20220106PWA_09","Vicfire reported a wire down and a grassfire at the incident location. On arrival the crew found that the SWER tee-off pole 135 Strathlin (LIS-719522) had caught fire and burnt off. This caused a grassfire of approx 60m x 40m in size. No other damage or injuries were reported.",null,null,"Extra low voltage DC (<120V ripple free)"]
[17,104,"2022-01-05","06:18",-37.742288000000002,142.03966800000001,"208 Rippon Rd, Hamilton VIC 3300",30090134,"HTN005","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016506","20220106PWA_10","As per vic fire - intersection rippon rd and balllarat rd- near lawn tennis club - pole top on fire. \nUpon Arrival, crew found a Burnt 22kV cross-arm and arc mark where the HV conductors came down to LV conductors. No HV injection found.",null,null,"Low voltage DC (<1.5kV)"]
[17,105,"2022-01-05","04:55",-38.389150999999998,142.62947800000001,"4412 Cobden-Warrnambool Rd, Allansford 3277",32194352,"WBL002","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0016507","20220106PWA_11","Vicfire reported a crossarm fire and a grassfire at the incident location. On arrival the crew found that the strain cross-arm had caught fire and burnt off on the north side conductor. This a grassfire of approx 30m x 10m in size occurred",null,null,"600V DC"]
[17,106,"2022-01-05","21:13",-38.165835999999999,144.71162899999999,"62 Harvey Rd, St Leonards 3223",32087896,"DDL013","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016518","20220107PWA_01","A customer called to report a cross-arm on fire. On arrival the crew found the top section of a 3 phase 22kV termination pole was on fire, and the centre phase conductor and disc insulators had fallen to the ground. There were a couple of small patches of burnt grass where the conductor had landed on the ground, totalling no more than 2 square metres in size.",null,null,"1500V DC"]
[17,107,"2022-01-05","04:09",-38.225126000000003,143.47793999999999," 70 Mahoods rd Alvie Vic 3249",32066991,"CLC004","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016818","20220214PWA_02","Report of broken crossarm\nOn arrival crew found strain crossarm burnt off.\nNo ground fire, no reported injuries or third party property damage.\nFound during Outage data review",null,null,"Earthing cable"]
[17,108,"2022-01-05","11:05",-37.733252,144.380943,"619 Glenmore Rd, Rowsley VIC 3340",32176954,"BMH005","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0016879","20220214PWA_03","Report of low conductors.\nOn arrival crew found burnt HV crossarm\nThere was no ground fire, no reported injuries or third party property damage.\nFound during outage data review, no photos of damage"]
[17,109,"2022-01-06","04:23",-38.122064000000002,144.692453,"5 Grassy Point Rd, Indented Head VIC 3223",32073573,"DDL013","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0016508","20220106PWA_12","Meters indicated low voltage conditions \n\nCrew was dispatched to investigate., Upon arrival the crew found that a cross arm fire had occurred. "]
[17,110,"2022-01-06","21:10",-38.177238000000003,144.56994399999999,"68-70 Newcombe St, Drysdale VIC 3222",32077430,"DDL021","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016534","20220107PWA_02","Customer reported sparking at low voltage pole LIS 14773, Princess Street, corner of Newcombe Street, Drysdale, which caused a small grass fire at the base of pole. Powercor crew attended site and replaced damaged low voltage service cable.",null,null,"single wire earth return (SWER)"]
[17,111,"2022-01-06","15:30",-37.787472000000001,142.09418600000001,"607 Pierrepoint Rd, Tarrington VIC 3301",30090023,"HTN003","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016892","20220214PWA_06","Customer reported low conductors and broken crossarm.\nOn arrival crew found burnt, broken HV crossarm.\nThere was no ground fire, no reported injuries or third party property damage\nFound during outage data review, no photos of damage",null,null,"single phase"]
[17,112,"2022-01-07","14:36",-38.373474000000002,142.744744,"230 Wrights Rd, Panmure VIC 3265",32194488,"WBL002","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0016535","20220107PWA_03","Customer advised he was \"moving trees with excavator\" and a branch has come in contact with overhead 22kV. Upon arrival crew noted that a tree was still contact with the conductor. \nTree in contact with the conductor has caught fire (no ground fire).\nThe excavator was not in contact with the conductor and the conductor did not fall to the ground.",null,null,"two phase"]
[17,113,"2022-01-07","15:07",-37.444670000000002,142.75543999999999,"841 Watgania Rd, Willaura VIC 3379, Australia",30077011,"ART033","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016894","20220214PWA_10","Fire com reported low conductors at incident location.\nOn arrival crew found a burnt crossarm\nthere was no ground fire, no reported injuries or third party property damage.\nFound during outage  data review no photos provided",null,null,"three phase"]
[17,114,"2022-01-09","14:30",-36.616967000000002,141.94445200000001,"560 Duchembegarra Rd, Duchembegarra VIC 3409, Australia",32111375,"HSM004","12.7kV AC (SWER)","Rural Long"," - insulators","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0016547","20220111PWA_02","Vic fire reported a pole fire at the above location, om arrival crew found the top of pole 79 Lake Natimuk was burning and the tee-off eyebolt had disconnected from the pole, the conductor on the bay from pole 79 to 79e was touching the ground with supply still connected.\n\nSubmission delayed by Osiris Issues"]
[17,115,"2022-01-09","14:55",-38.270989,144.522109,"1 Lookout Rd, Ocean Grove VIC 3226",30062020,"DDL023","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016552","20220112PWA_01","Fire Brigade called in fire at low voltage fuse box at pole\nattending crew found  heating at FOLCB  on pole top \n\nsubmission delayed by OSIRIS issues"]
[17,116,"2022-01-09","23:42",-38.168022999999998,144.313851,"18 Marcus St, Highton VIC 3216",30295565,"WPD033","22kV AC","Urban"," - automatic circuit recloser (ACR)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016568","20220113PWA_01"," Flashover caused by possum caused flashover on pole mounted ACR which left visible burn mark on pole.",null,null,"Negligible: no ground fire"]
[17,117,"2022-01-10","06:35",-38.313087000000003,144.333156,"6 Onshore Dr, Torquay VIC 3228, Australia",30240916,"WPD024","Low voltage AC (<1kV)","Rural Short"," - LV pillar","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016569","20220113PWA_02","Customers reported intermittent supply. \nAttending crew found LV pillar had burnt and was arcing. Entire pillar burnt to ground",null,null,"Localised: less than 10 sq.m"]
[17,118,"2022-01-10","22:17",-37.572783999999999,143.84537800000001,"519 Drummond St S, Redan VIC 3350",30011169,"BAS032","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016899","20220215PWA_01","Report of broken crossarm.\nOn arrival crew found burnt off crossarm\nThere was no ground fire, no reported injuries or third party property damage.\nFound during outage data review no photos found",null,null,"Small: 10 - 1000 aq.m"]
[17,119,"2022-01-11","03:51",-36.773916,144.43090900000001,"1535 McIvor Highway, Longlea ",30268259,"BET005","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0016570","20220113PWA_03","Vic fire attended grass fire at the scene, reported fire started a pole.  Upon arrival the crew noticed centre phase EDO unit broken, suspected lightning strike",null,null,"Medium: 1000 sq.m - 10 ha"]
[17,120,"2022-01-11","16:28",-36.518188000000002,144.76448500000001,"3481 Heathcote-Rochester Rd, Burramboot",30122673,"SHP021","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0016571","20220113PWA_04","quarry operator advised that the Quarry had a blast which has knocked out Powerlines. Powerline laying on the ground Inside quarry.\nAttending crew found  HV conductor had been brought down and ignited a tyre  that it fell on to.",null,null,"Large: more than 10 ha"]
[17,121,"2022-01-11","21:41",-36.061717999999999,143.134815,"2471 Birchip-Wycheproof Rd Narraport",32027624,"CTN001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0016572","20220113PWA_05","Vic fire reported fire on Birchip-Wycheproof Rd.  \nUpon arrival crew found that a crossarm had broken due to termite damage and conductor had fallen to ground. "]
[17,122,"2022-01-13","13:39",-36.00517,142.41021499999999,"2828 Henty Hwy, Beulah",32107714,"HSM003","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"Very high",1,1,"INC-0016575","20220114PWA_01","Customer rang with an all supply failure. \nA crew attended and found that P2 Galaquil East S/L had been struck by lightning and started a ground fire"]
[17,123,"2022-01-13","19:23",-38.219504000000001,143.57226399999999,"15 Melrose Rd, Warrion VIC 3249",32065806,"CLC006","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0016900","20220215PWA_02","Crew found burnt  HV crossarm\nNo ground fire, no reported injuries or third party property damage.\nfound during outage data review ",null,null,"Started in or originated from a distribution system"]
[17,124,"2022-01-14","06:43",-34.204059999999998,142.149934,"326 San Mateo Ave, Mildura VIC 3500",30294810,"MDA034","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0016576","20220114PWA_02","FSD fire reported fire brigade reported they had extinguished fire on FSD \n",null,null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system"]
[17,125,"2022-01-14","03:56",-37.790427999999999,144.831763,"94-98 Hampshire Rd, Sunshine VIC 3020",32178129,"SSE034","Low voltage AC (<1kV)","Urban"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016587","20220117PWA_01","Vic fire reported pole file.  \nUpon arrival crew found burnt fuse box and under ground cable.",null,null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system"]
[17,126,"2022-01-18","23:15",-36.391432999999999,145.36775800000001,"7147 Midland Highway Mooroopna 3629",33093754,"MNA024","22kV AC","Rural Short"," - pole (concrete)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0016607","20220119PWA_01","A bird flashover caused a small fire at the base of the pole at the incident location.\nThe feeder successfully reclosed.\nThere was no injuries or third party propwerty damage.",null,null,"Started by lightning striking a distribution system or a part of a distribution system "]
[17,127,"2022-01-20","11:17",-37.806671999999999,144.82485600000001,"561 Somerville Rd, Sunshine West VIC 3020",30317869,"SSE033","22kV AC","Urban"," - dropper / bridge","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0016617","20220121PWA_01","Report received of pole fire at incident location.\nOn arrival crew found a birds nest  or bird activity had caused flashover and burning on transformer.\nDebris fell to ground and caused a small grass fire.",null,null,"Started by any other thing forming part of or coming into contact with a distribution system"]
[17,128,"2022-01-21","22:15",-38.381185000000002,142.72270700000001,"792 Swans Ln, Naringal, 3277",30308788,"WBL002","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Very high",1,1,"INC-0016631","20220124PWA_01","Vicfire reported wires down and had caused a grass fire.\nOn arrival crew found a large broken branch had fallen on the 22kV OH conductors.\nThe tree was resting on the outer 2 phases and a grass fire had been extinguished by CFA. \nTree approx 20m from line prior to falling.\nThere was no injuries",null,null,"Otherwise started by a distribution system"]
[17,129,"2022-01-21","16:25",-36.307248999999999,145.044532,"3 Mellis St, Kyabram VIC 3620",32186714,"KYM002","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0016904","20220218PWA_08","Asset inspector found crossarm with burn damage and termite activity\nThere was no ground fire\nfound during outage data review"]
[17,130,"2022-01-22","01:37",-38.083849999999998,143.94513499999999,"3839 Hamilton Highway, Inverleigh, 3321 (B140, Inverleigh VIC 3321, Australia)",30052101,"WIN013","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0016632","20220124PWA_02","Vicfire reported pole fire. \nOn arrival crew found a LV FOLCB had overheated and melted,\nThere was no ground fire, no injuries or third party property damage."]
[17,131,"2022-01-23","09:46",-37.784035000000003,144.809057,"49 Ridgeway Parade, Sunshine West",32164939,"SU035","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0016633","20220124PWA_03","Customer called to report a broken service to their property which in turn has caused a small (1m2) grass fire within their front lawn. \nUpon arrival the fault crew found that the old neutral screen service between the house at #49 and LIS-19320 had failed at the reel/roller near the POA.\nNo injury, shock or third party damage to report.",null,null,1]
[17,132,"2022-01-24","13:05",-37.764477999999997,144.83199500000001,"131 Berkshire Rd, Sunshine North VIC 3020",30314549,"SSE012","Low voltage AC (<1kV)","Urban"," - pole (steel)","single phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0016646","20220125PWA_02","Following collision, car hit public lighting pole,  pole fell. A small grass fire occurred (approximately 3 square mtrs). \nUnable to determine if pole lantern head or vehicle ignited fire.\n\n\n ",null,null,2]
[17,133,"2022-01-26","19:32",-38.554769999999998,143.39810199999999,"2600 Carlisle Rd, Carlisle River, 3239",33039641,"CLC003","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within electric line construction area",19.8,"High",0.5,9.9,"INC-0016658","20220127PWA_01","Customer advised wires down and possibly cause of grass fire. On arrival crew found a tree had fallen a grass fire had started between CARLISLE RIVER P95 & P96. ",null,null,3]
[17,134,"2022-01-26","12:20",-35.291578999999999,141.105704,"Carina Rd, 500M south of Ngallo Rd, Carina VIC 3512",32154670,"OYN001","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,{"$f":"IF(OR(P171=\"\",R171=\"\"),\"\",IF(AND(O171=\"within electric line construction area\",Q171=\"No forecast\"),1,P171*R171))","v":0.5},"INC-0016662","20220128PWA_01","fault crew found that a crossarm fire had occurred at Ngallo P3, crossarm burnt off at the strap position, conductor fell and made contact with ground igniting a small grass fire of approximately 20M square.",null,null,4]
[17,135,"2022-01-26","18:43",-37.056178000000003,142.34327200000001,"75 Snells Rd, Wartook VIC 3401",30591611,"HSM001","12.7kV AC (SWER)","Rural Long"," - insulators","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0016915","20220215PWA_03","Report of pole fire at incident location.\nNo ground fire, no reported injuries or third party property damage\nFound during outage data review, no photos",null,null,5]
[17,136,"2022-01-27","15:41",-38.236612000000001,144.03961000000001,"2445 Princes Hwy, Winchelsea VIC 3241, Australia",30076064,"WIN022","22kV AC","Rural Long"," - surge diverter","three phase","Started in or originated from a distribution system","within electric line construction area",19.8,"High",0.5,9.9,"INC-0016663","20220128PWA_03","CFA reported a pole fire. \nCrews attended and an LA had faulted causing a ground fire of approximately 100 m X 200 m.\n\nDarcy @ ESV notified @ 17:10. ED from ESV called back at 17:20 (no ref)",null,null,6]
[17,137,"2022-01-27","20:34",-36.701228999999998,144.70430500000001,"165 MYOLA EAST ROAD TOOLLEEN 3551",30030981,"SHP021","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0016669","20220131PWA_01","Vic Emergency reported wire down, 165 Myola East Road, started a grass fire, emergency services enroute. \nCrew found a tree had damaged 1 x 3/12 steel conductor on East side between P21 & P22, CFA on site, grass fire approximately 10 to 20m wide & 50m long, no property damage, no injuries.\n",null,null,7]
[17,138,"2022-01-27","07:45",-34.358547999999999,142.28287599999999,"117 Swamp Road Red Cliffs 3496 ",30099272,"RCT014","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0016672","20220131PWA_02","Report received that crossarm broken and pole smoking at incident location.\nOn arrival crew found pole fire.\nThere was no ground fire, no reported injuries or third party property damage.",null,null,8]
[17,139,"2022-01-28","23:47",-35.058031999999997,143.33151699999999,"4149 Murray Valley Highway Piangil 3597",32157132,"SHL002","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0016673","20220131PWA_03","VIC Fire reported a pole fire with Fire brigade en route. Crew found a pole damaged by pole fire\nThere was no ground fire, no reported injuries or third party property damage.",null,null,9]
[17,140,"2022-01-28","20:00",-37.718747,140.97408999999999,"530 Border Road, Strathdownie.",32128386,"HTN002","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016679","20220131PWA_07","CFA reported pole fire at the above address. \nThe Crew attended and found a faulted service cable that had come to ground causing a ground fire.\nThe ground fire was approximately 200 sq metres.\n",null,null,10]
[17,141,"2022-01-28","14:17",-37.577767000000001,142.68751800000001,"302 Lalkaldarno Rd, Willaura VIC 3379, Australia",30151633,"ART033","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016924","20220218PWA_07","Report of lightning strike and pole fire.\nON arrival crew found an edo fuse hung up and fire damage.\nno ground fire\nfound during outage data review no photos",null,null,{"$f":"Y177+1","v":11}]
[17,142,"2022-01-28","07:30",-37.376632999999998,141.806791,"2920 Coleraine-Balmoral Rd, Gringegalgona VIC 3315",32105698,"HSM002","22kV AC","Rural Long"," - transformer (pole mounted)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0016927","20220218PWA_06","Following lightning strike report of transformer fire cfa put it out. \nThere was no ground fire\nFound during outage data review ",null,null,{"$f":"Y178+1","v":12}]
[17,143,"2022-01-28","15:40",-38.735970999999999,143.304451,"5835 Great Ocean Rd, Yuulong VIC 3237",30245361,"CLC003","22kV AC","Rural Long"," - pole (wood)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016930","20220215PWA_04","Pole struck by lightning caused pole fire.\nThere was no ground fire.\nfound during outage data review ",null,null,13]
[17,144,"2022-01-30","15:15",-36.420032999999997,142.64908,"Private property located near the corner of Heintze Road and Dunmunkle School Road Minyip 3392",32118039,"STL006","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0016676","20220131PWA_06","Report received CFA on way to report of grass fire and wire down at incident location. \nOn arrival crew found a swer pole had been totally destroyed by lightning (lightning storms previous 2 days).\nThe high voltage conductor came to rest approximately 600mm above the ground and remained alive.\nA sheep subsequently made contact with the line, was electrocuted and a grass fire ignited.\nThere were no other injuries, ground fire approx 12 ha of stubble",null,null,14]
[17,145,"2022-01-31","11:22",-37.825834999999998,143.74695800000001,"85 Swanson Rd, Dereel VIC 3352",30005685,"BAS022","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0016683","20220201PWA_03","Emergency services reported a pole fire.\nAttending crew found LV fuse box had overheated\nThere was a small grass fire, no reported injuries or third party property damage.",null,null,15]
[17,146,"2022-01-31","21:07",-38.386938999999998,142.604972,"119 Ziegler Parade, Allansford VIC 3277",33100532,"WBL002","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0016934","20220215PWA_05","Report of pole fire.\nOn arrival crew found that an EDO fuse had hung up and burnt in half.\nThere was no ground fire.\nNo photos taken\nfound during outage data review",null,null,16]
[17,147,"2022-02-01","04:42",-36.614716999999999,142.49698900000001,"Konigs Rd, Murtoa VIC 3390, Australia",30548901,"HSM001","12.7kV AC (SWER)","Rural Long"," - fuse (Fault Tamer)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0017172","20220322PWA_01","Following report of supply failure, on arrival crew found that a fault tamer unit had burnt out and fallen to ground.\nThere was no ground fire, no reported injuries or third party property damage.\nFound during outage data review.",null,null,17]
[17,148,"2022-02-02","02:30",-38.197859999999999,144.46539000000001,"16 Hazelwood Crescent, Leopold ",32077395,"DDL014","Low voltage AC (<1kV)","Rural Short"," - connector / termination","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016703","20220202PWA_02","Customer reported  POA on Fire. The Crew attended and confirmed a Fire at the POA (No ground fire). CFA also attended the scene.  \nThere were no injuries",null,null,18]
[17,149,"2022-02-05","07:09",-38.228340000000003,143.44673700000001,"650 Wool Wool Rd, Wool Wool VIC 3249",30056328,"CLC004","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0016756","20220207PWA_02","The CFA reports pole and grass fire at WOOL WOOL 31 transformer pole, a customer also reported the incident. A crew was dispatched to investigate.\nOn arrival crew found found both transformer folcb and fuse box had been burnt.\nThere was a 1x1 mtr grass fire at base of pole.\nThere was no injuries or third party property damage. ",null,null,19]
[17,150,"2022-02-06","18:01",-38.493969999999997,143.26213999999999,"511 TOMAHAWK CREEK ROAD, SIMPSON",30046488,"COB011","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0016758","20220207PWA_03","The fire authority reported a grass fire had occurred due to pole fire, a crew was dispatched to investigate. \nOn arrival the crew confirmed a pole fire had occurred, damage to LV fuse box on the pole. The CFA were still onsite putting out the fire, and the crew isolated the Tx until it was safe to make repairs.\nThere was a around a 400sqm grass fire.\nNo injuries or third party property damage.",null,null,20]
[17,151,"2022-02-08","19:37",-37.747414999999997,144.76552699999999,"56 Wintersun Drive, Albanvale 3021, corner with Woodland Drive",32178796,"SSE031","Low voltage AC (<1kV)","Urban"," - connector / termination","single phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0016780","20220209PWA_01","Customer reported sparking on pole and fire on lawn beneath.\nA Powercor crew attended  and noted a burnt Copper to Aluminium Tee connector on one end of the White phase LV Substation Bus fuse assembly.\nMolten metal particles had fallen to the grassed nature strip below. \nThere was no reported injuries or third party property damage.\nApprox 150mm wide ring of dried grass had been burnt around the pole."]
[17,152,"2022-02-12","08:05",-38.629572000000003,143.57423900000001,"1485 Old Beech Forest Rd, Beech Forest 3237",30267836,"CLC003","Low voltage AC (<1kV)","Rural Long"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0016945","20220214PWA_07","A customer called to report the pole had been on fire, but had now died down. On arrival the crew found that a 160A FSD fused isolator had failed and caught fire. The failed isolator had caused debris to fall to the ground, however the pole was not burnt, and there was no ground fire "]
[17,153,"2022-02-13","13:06",-37.881965000000001,144.629706,"13 Bellinger Crescent, Wyndhan Vale, 3024",30228021,"WBE014","Low voltage AC (<1kV)","Rural Short"," - LV pillar","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0016823","20220214PWA_09","Vicfire have advised pillar arcing and sparking - was on fire - fire now out but still arcing\n\nOn arrival the PCA Faults Crew  found that that an unknown vehicle has made contact with the LV Pillar.\nUpon closer inspection, this is evident by the bent pillar frame, this has then caused the pillar to arc, spark, catch fire and melt.\n"]
[17,154,"2022-02-15","15:00",-36.757105000000003,144.282241,"116 PALL MALL,BENDIGO,VIC,3550",34022850,"BGO024","Low voltage AC (<1kV)","Urban"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"High",{"$f":"IF(Q191=\"\",\"\",IF(Q191=\"No forecast\",0.1,IF(Q191=\"Low-moderate\",0.2,IF(Q191=\"High\",0.5,IF(Q191=\"Very high\",1,IF(Q191=\"Severe\",2,IF(Q191=\"Extreme\",3.5,5)))))))","v":0.5},{"$f":"IF(OR(P191=\"\",R191=\"\"),\"\",IF(AND(O191=\"within electric line construction area\",Q191=\"No forecast\"),1,P191*R191))","v":0.1},"INC-0016948","20220216PWA_02","Fire authorities reported junction box fire out the front of incident location"]
[17,155,"2022-02-15","15:54",-34.189912999999997,142.031901,"35 Addison Ln, Merbein VIC 3505",30095871,"MBN014","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0017173","20220322PWA_02","Following supply failure on arrival crew found an EDO fuse unit had candled and burnt.\nThere was no ground fire, no reported injuries or third party property damage.\nFound during outage data review, no photos supplied."]
[17,156,"2022-02-16","08:55",-37.18486,144.02806100000001,"1031 Creswick-Newstead Rd, Sandon VIC 3462",32044382,"CMN002","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within electric line construction area",19.8,"Very high",1,19.8,"INC-0016950","20220216PWA_03","Dispatch reported on a small grass fire that started from Penrose Pole 40 due to a wire down. \nUpon Arrival, crew found that the ACR had tripped and the wire down had started a grass fire. \nCFA attended to extinguish fire. \nThe area burnt was approximately 70mx20m (1400 m2).\nCrew indicated tree down on conductor.\nThere was no reported injuries. "]
[17,157,"2022-02-17","05:50",-37.741953000000002,142.03527600000001,"Riley St &, Ballarat Rd, Hamilton VIC 3300, Australia",32134992,"HTN005","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0016937","20220217PWA_02","A passerby reported insulators sparking and glowing bright red at the incident location. \nOn arrival the crew found that a crossarm fire had occurred on Ballarat Rd Pole 10, LIS-722333. \nThe crew isolated the supply to the area, and the fire self extinguished. \nThe crossarm had burnt through near the strap bolt.\nThere were no reported ground fires, HVIs or injuries."]
[17,158,"2022-02-17","18:01",-36.032128,145.191215,"130 Peter Hawkey Rd, Nathalia VIC 3638, Australia",33079443,"NKA002","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0016940","20220218PWA_03","Reports of vehicle contacting wires.\n On arrival, crew found evidence of approx. 2 hectares of burnt grass and burn marks on overhead conductor between LIS 307 and LIS 308. \nOwner of property advised that a fertiliser with a tipper had struck the overhead conductors.  \nOwner reported to us that driver was uninjured and CFA attended and extinguished fire.  \nDriver and CFA not on site when crew arrived.  No third party damage."]
[17,159,"2022-02-17","05:53",-38.521411999999998,142.795783,"2709 B100, Nirranda South VIC 3268",30136055,"WBL012","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0017174","20220322PWA_03","Report recieved of pole fire at incident location.\nOn arrival crew found a FOLCB had burnt out.\nThere was no ground fire\nFound during outage data review, no photos supplied."]
[17,160,"2022-02-20","19:48",-36.018768999999999,145.463189,"278 Hays Road Katunga",33078570,"NKA006","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0016925","20220221PWA_02","Vic fire reported wire down and ground fire.\nOn arrival, crew found a steel HV conductor had broken.\nGround fire at area approx 200m x 4m with potential damage to fence.  \nNo injuries."]
[{"$f":"COUNTA(C198:O198,Q198,T198:V198)","v":17},161,"2022-02-20","18:20",-37.703693999999999,144.81002000000001,"862 OLD CALDER HIGHWAY, C, VIC, 3036",30102907,"SA006","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0016928","20220221PWA_01","Brett from brimbank council ph 0447108107 Palm tree has been on fire due to touching the lines.\nFire brigade put out the fire.\nOn arrival the PCA Faults Crew have advised that the Customers Private Palm Tree , located directly underneath the existing 22kV OH Bare Conductor have appeared to have been smouldering / scorched / charring due to the palm tree tips growing into and contacting the existing 22kV OH Bare Conductors above. \nThere was no ground fire, no reported injuries or third party property damage,"]
[{"$f":"COUNTA(C199:O199,Q199,T199:V199)","v":17},162,"2022-02-20","21:00",-36.356698000000002,141.07936799999999,"Western Hwy near corner of Leeor rd Serviceton",32102855,"NHL031","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0016935","20220228PWA_04","Vic fire reported a fire on a pole at the above location, on arrival the crew found a partial burnt cross arm at the king bolt with the cross arm still intact. their was no ground fire. the crew organised to return the next day to replace the cross arm."]
[17,163,"2022-02-21","12:42",-37.171722000000003,143.55033800000001,"1075 Lillicur Rd, Lillicur VIC 3371, Australia",33009356,"MRO008","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0016916","20220222PWA_02","Report received from Vic fire of a fallen SWER conductor starting grass fire.\nReport recieved that a large tree from outside the clearance space had fallen across line.\nThere was a ground fire (area estimated), there was no injuries."]
[17,164,"2022-02-21","12:33",-37.761904000000001,144.838537,"14-24 Burwood Avenue, Sunshine North, 3020 ",30118198,"SSE032","22kV AC","Urban"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016919","20220222PWA_01","Report received of pole fire at incident location.\nOn arrival the PCA Faults Crew have advised that Top HV X-arm on HV Anchor Pole has burnt through the outer phase.\nThere was no HVI, No ground fire, no reported injuries or third party property damage."]
[17,165,"2022-02-23","20:43",-37.704137000000003,142.06886,"81 Rogers Rd, Hamilton VIC 3300",30087339,"HTN005","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0016890","20220228PWA_02","Customer reported SWER conductor had come away from ceramic insulator at pole 14 Lake Doling line (LIS 702990).  Sparks observed and burn mark on pole. No fire at ground level.   SWER conductor was low but was out of reach from ground level."]
[17,166,"2022-02-24","11:50",-38.384245999999997,142.489497,"80 KELP STREET,WARRNAMBOOL,VIC,3280",32196313,"WBL008","22kV AC","Urban"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0016898","20220225PWA_02","Vicfire reported pole fire. intersection of lava and kelp st\nAttending crew found HV termination cross-arm had burnt\nThere was no ground fire"]
[17,167,"2022-02-26","16:35",-37.861665000000002,144.71167299999999,"112 Birchwood Boulevard, Hoppers Crossing Vic 3029. ",30103619,"LV009","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",{"$f":"IF(O204=\"\",\"\",IF(O204=\"LBRA only\",0.2,IF(O204=\"HBRA only\",1,IF(O204=\"within electric line construction area\",19.8,IF(O204=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"High",0.5,0.1,"INC-0016882","20220228PWA_01","Vic emergency reported that line arcing in tree has caused a garden fire. Fire put out by brigade who are onsite at the incident location.\nOn arrival, crew found there was a small grass fire caused by twisted service line burnt from rubbing on council tree and the sparks dropped to the ground which resulted small grass fire at the customers front garden area."]
[17,168,"2022-02-27","16:59",-36.304481000000003,141.29992999999999,"1135 Broughton Rd, Kaniva VIC 3419",32100750,"NHL031","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0017175","20220322PWA_04","Report received of pole fire at incident location.\non arrival crew found tee off crossarm burnt through.\nthere was no ground fire\nno photos supplied\nfound during outage data review"]
[17,169,"2022-02-28","02:40",-34.237307999999999,142.10834199999999," 3147 San Mateo Ave, Mildura VIC 3500",32151327,"MBN032","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0016964","20220301PWA_02","Police Comms reported Powerline down at the intersection of San Mateo Avenue and Gordon Avenue.\nPole had burnt through and resting on the powerline. \nUpon arrival, crew found that the Centre phase  had burnt off. \nConductor had dropped on the HV angle and HV tee off. \nThe burnt section is between Top and tee off structure.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,170,"2022-02-28","12:53",-36.136172999999999,144.13130200000001,"7541 Bendigo-Pyramid Rd, Mologa VIC 3575, Australia",30025424,"CHA006","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0017003","20220302PWA_01","Following lighning activity conductor found resting on crossarm, slight burn marks on crossarm.\nThere was no ground fire, no reported injuries or third party property damage."]
[{"$f":"COUNTA(C208:O208,Q208,T208:V208)","v":17},171,"2022-02-28","17:21",-35.286690999999998,141.09567300000001,"905 Ngallo Rd, Carina VIC 3512 (800M west of Carina Rd intersection)",32154413,"OYN001","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0017015","20220303PWA_01","All supply fail resulted in Ouyen LSA fault crew patrolling line past fuses ex P928 OYN001 feeder.\nCrew found pole fire occurring at the incident location.\nCFA were called to extinguish fire which had taken hold on the pole top. e cross arm king bolt position.\nConductors remained aloft, held up by the cross arm straps.\nNo ground fire or third party damage."]
[{"$f":"COUNTA(C209:O209,Q209,T209:V209)","v":17},172,"2022-03-02","15:49",-38.396473999999998,142.65736100000001,"4161 Cobden-Warrnambool Rd, Allansford VIC 3277",31034720,"WBL002","Low voltage AC (<1kV)","Rural Short"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0017018","20220303PWA_03","Customer reported main pole with the transformer on it - the fire was in the first fuse closest to the pole - still smoking but it has stopped with the fire and sparking - no one iso - he shut down the meter, few lights at the property but nothing else - over cast weather\nCrew found overheated terminal on FSD on substation pole supplying milking shed on pole 2E"]
[17,173,"2022-03-03","12:38",-37.701410000000003,144.799306,"3 Melton Hwy, Taylors Lakes VIC 3038",33076955,"SA010","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0017022","20220304PWA_01","Truck hit substation pole (KEILOR MLN-HOTEL) LIS 30685. \nThis caused a connection fault at the FSD resulting in FSD fire and scorching of grass below. \nThere was no reported injuries or third party property damage. "]
[17,174,"2022-03-09","07:08",-38.178896999999999,144.71436700000001,"Holiday Lifestyle St Leonards Caravan Park, 99 Leviens Rd, St Leonards VIC 3223, Australia",32071215,"DDL013","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0017076","20220310PWA_01","Report of pole fire at incident location.\nOn arrival crew found top burnt off pole fire now out.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,175,"2022-03-10","14:24",-37.911481000000002,143.91483700000001,"1190 Shelford-mt Mercer Rd, Shelford VIC 3329, Australia",32003832,"BAS022","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0017095","20220311PWA_03","Tractor has impacted pole resulting in fallen SWER conductor, causing a small grass fire. \nProtection operated.\n No shock resulted from the incident.  "]
[17,176,"2022-03-12","16:54",-36.368259000000002,145.40195499999999,"Outside of 16 Wyndham St, Shepparton VIC 3630",34010077,"SHN012","Low voltage AC (<1kV)","Urban"," - luminaires (minor road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0017117","20220315PWA_07"," Vic fire - street light pole on fire - pca attendance required - brigade currently on site.\nOn arrival crew found a streetlight lantern had caught fire\nThere was no ground fire, no reported injuries or third party property damage."]
[17,177,"2022-03-14","00:06",-38.256872999999999,143.21717000000001,"3650 Princes Highway, Weerite ",32055668,"CDN002","66kV AC","Rural Long"," - insulators","three phase","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0017112","20220315PWA_05","TMC case 1849653?\nVic fire reported a pole fire. The crew attended and confirmed a pole fire at LIS 414680.\nThe top of the pole was charred and there was no ground fire."]
[17,178,"2022-03-15","16:33",-37.967705000000002,142.51590999999999,"4810 Warrnambool-Caramut Rd, Caramut VIC 3274, Australia",30265063,"TRG022","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (commercial / industrial)","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0017211","20220317PWA_01","Firecomms - Reported There was a small bushfire in this location, all under control now - Possible damage to Powercor assets pole & line near the LIS 746226 and out the front of the golf course gate.\n\nRefer follow up from D Clarke ESV "]
[17,179,"2022-03-21","17:34",-37.808604000000003,144.81809200000001,"133-169 Fairbairn Road, Sunshine West 3020 - Along the front boundary of Australia Post Mail handling facility. ",30120016,"SSE014","22kV AC","Urban"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0017180","20220323PWA_01","A passing Jemena electrical operator noticed a lower than normal HV phase conductor at the incident location.\nA Powercor crew attended and observed that the southern end of a HV -tee off arm on LIS 17689 had burnt and broken free of the rest of the arm fixed to the pole.\nhe broken crossarm ends appeared cold, suggesting that the crossarm fire may not have occurred immediately prior.\nThere was no fire brigade in attendance.\nThe was no evidence of a fire at ground level."]
[17,180,"2022-03-24","15:38",-36.537075000000002,144.99664000000001,"Corner Girgarre-Rushworth Road and Home Road, Rushworth 3612",32190817,"SHP014","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0017212","20220328PWA_01","Firecom reported small grassfire caused by low wires at Home Rd Rushworth 500m East of Girgarre - Rushworth Rd Rushworth near LIS 885234. \nFarmer working for property owner cut down a tree which damaged HV 3/12 conductor starting approximately 200m2 grass fire, CFA attended.\nThere was no reported injuries"]
[17,181,"2022-03-26","08:45",-37.762791999999997,144.832674,"Steers St Sunshine, 1 pole south of corner with Ayton St. (Along the side of 82-86 Berkshire Road), Sunshine North 3020",30592317,"SSE012","22kV AC","Urban"," - pole (wood)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0017217","20220328PWA_02","A Truck with an extended semi-trailer carrying steel, was travelling south from Ayton St into Steers St. \nAs the driver negotiated the turn he indicated that he was confronted by an oncoming car and he pulled into the kerb to provide clearance. \nIn so doing his trailer snagged a recently replaced HV/LV pole LIS 132080\nThe force of impact caused severe damage to the pole, pole displacement in the ground, the HV king-bolt to shear, HV insulator collars to break releasing the conductors into the air. \nThe red phase property side HV conductor swung significantly sideways and welded itself to the steel re-inforcement of an adjacent concrete water tank.\nThere was a pole top fire and small vegetation fire near the concrete water tank.\nThere was no reported injuries"]
[17,182,"2022-03-28","04:57",-36.350445999999998,145.43173999999999,"139 Grahamvale Road Grahamvale 3631",33096489,"SHN024","22kV AC","Rural Short"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0017222","20220329PWA_01","Bats flashed over at Pole 37.\nThere was a small grass fire 8m x 8m.\nThere was no reported injuries or third party property damage.\nProtection operated as expected "]
[17,183,"2022-03-29","12:54",-37.460712999999998,144.02213800000001,"1050 Blampied-Mollongghip Rd, Mollongghip VIC 3352, Australia",33007352,"BAN008","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0017454","20220505PWA_02","EDO fuse unit found hung up and burnt in half.\nThere was no ground fire\nfound during Outage data review\n"]
[{"$f":"COUNTA(C221:O221,Q221,T221:V221)","v":17},184,"2022-03-30","07:16",-38.335557999999999,141.595057,"97 Kennedy St, Portland - 1736547-1",33060131,"PLD004","Low voltage AC (<1kV)","Rural Short"," - connector / termination","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0017236","20220331PWA_01","Vic fire reported a service line on was fire. \nThe crew attended and confirmed an IPC on pole 11 (LIS-901496) had caught fire. \nThere was no ground fire, no reported injuries or third party property damage."]
[{"$f":"COUNTA(C222:O222,Q222,T222:V222)","v":17},185,"2022-04-02","18:43",-37.831775999999998,144.85626400000001,"300 Blackshaws Rd, Altona North VIC 3025, Australia",32174798,"BLTS-SCI","66kV AC","Unknown"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0017253","20220404PWA_01","Report of pole fire at incident location.\nOn arrival crew found that a pole fire had burnt through Bottom crossarm position allowing all three crossarms to break away from double circuit pole\nThere was no ground fire, no reported injuries or third party property damage. "]
[17,186,"2022-04-07","17:12",-38.372073999999998,144.243865,"915 GREAT OCEAN ROAD,BELLBRAE,VIC,3228",32073674,"WPD021","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0017295","20220408PWA_02","Fire Brigade attended pole fire and small grass fire at pole 6 \n\n Powercor crew attended and replaced burnt pole and single phase pole type transformer"]
[17,187,"2022-04-08","18:43",-36.140633000000001,144.757474,"131-159 Ogilvie Avenue, Echuca ",30121470,"ECA001","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0017301","20220411PWA_01","Report received of a pole fire at incident location.\nOn arrival crew found that a HV crossarm had caught fire and burnt through at the king bolt, the crossarm had failed and HV conductor was hanging.\nBottom HV crossarm of a 2 x HV circuit, 1 x LV circuit structure.\nAppears as though HV has not contacted LV conductors.\nCFA on scene but not required.  \nNo reported injuries, fire did not spread beyond crossarm. No signs of HVI."]
[17,188,"2022-04-09","01:13",-36.312902999999999,145.26490100000001,"1080 Starritt Road, Undera",30128240,"KYM003","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0017300","20220422PWA_01","HV conductor down - Crew arrived to find that a tree branch had fallen and struck the HV line. "]
[17,189,"2022-04-11","08:02",-37.820563999999997,144.80092200000001,"32 Agosta Dr, Laverton North VIC 3026",30229063,"LVN032","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0017306","20220411PWA_04","Dispatch reported of a pole fire in Laverton North.\nUpon Arrival, crew found that the 3 phase isolation box was burnt out.\nThere was no ground fire or reported injuries."]
[17,190,"2022-04-11","04:55",-37.821820000000002,144.822227,"18 Little Boundary Rd, Laverton North VIC 3026",30120109,"BLT016","22kV AC","Urban"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0017310","20220412PWA_01","Vic Fire, reports of wires sparking outside 18 Little Boundary Rd, Laverton North VIC 3026. \nOn arrival, crew found HV X-arm fire on LIS 17737. \nNo ground fire, no injuries, no HVI."]
[17,191,"2022-04-11","06:00",-38.5745,143.189593,"1120 Princetown Rd, Cooriemungle VIC 3268",30048887,"COB011","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0017312","20220412PWA_03","Customer called in fire at low voltage service pole at incident location.\nPowercor crew attended site and replaced damaged low voltage FOLCB.\nSmall grass fire at base of low voltage service pole\nThere was no reported injuries or third party property damage."]
[17,192,"2022-04-11","05:46",-38.502581999999997,142.76000099999999,"3227 Great Ocean Rd, Nirranda VIC 3268",30135113,"WBL012","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0017313","20220412PWA_04","Fire Brigade reported fire at pole LIS 4274.\nPowercor crew attended site, connection box found burnt.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,193,"2022-04-16","07:32",-35.234127000000001,141.18724,"Murrayville North Rd, Murrayville VIC 3512, Australia",32146489,"OYN001","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0017535","20220518PWA_01","Customer reported broken crossarm.\nOn arrival crew found burnt crossarm.\nThere was no ground fire.\nFound during outage data review"]
[17,194,"2022-04-17","15:20",-36.285783000000002,144.61847599999999,"(675 - 731) Hansen Road Bamawm 3561 (corner Bamawm Road)",32184597,"SHP012","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0017340","20220419PWA_01","Vic Fire reported, corner Bamawm and Hansen Roads, grass fire caused by arcing and sparking from PCA assets.\n\nCrew found grass fire  ignited in vicinity of candled HV fuse"]
[17,195,"2022-04-18","13:34",-35.745897999999997,143.99073899999999,"243 Tuck Road Kerang 3579 ",32031556,"KGT003","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0017350","20220419PWA_03","Customer reported brownout affecting house and shed.\nCrew found pole  had caught fire and some high voltage injection damage was detected."]
[17,196,"2022-04-18","02:24",-37.640751000000002,144.46467200000001,"2677 Gisborne Rd, Merrimu VIC 3340",32167433,"MLN022","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0017536","20220518PWA_02","Pole on property caught fire.\nOn arrival crew found that a FOLCB had caught fire\nInsufficient remains to determine a cause of the incident.\nThere was no ground fire\nFound during outage data review "]
[{"$f":"COUNTA(C234:O234,Q234,T234:V234)","v":17},197,"2022-04-23","22:00",-38.356335999999999,142.49743000000001,"29 Grange Rd, Warrnambool VIC 3280, Australia",30134667,"WBL005","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O234=\"\",\"\",IF(O234=\"LBRA only\",0.2,IF(O234=\"HBRA only\",1,IF(O234=\"within electric line construction area\",19.8,IF(O234=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"Low-moderate",{"$f":"IF(Q234=\"\",\"\",IF(Q234=\"No forecast\",0.1,IF(Q234=\"Low-moderate\",0.2,IF(Q234=\"High\",0.5,IF(Q234=\"Very high\",1,IF(Q234=\"Severe\",2,IF(Q234=\"Extreme\",3.5,5)))))))","v":0.2},{"$f":"IF(OR(P234=\"\",R234=\"\"),\"\",IF(AND(O234=\"within electric line construction area\",Q234=\"No forecast\"),1,P234*R234))","v":4.0000000000000008E-2},"INC-0017392","20220426PWA_02","CFA reported a pole fire. Crew attended and confirmed a pole box fire at James Street P3"]
[{"$f":"COUNTA(C235:O235,Q235,T235:V235)","v":17},198,"2022-04-24","04:00",-38.298344,141.58839,"119 Crowes Road, Bolwarra",33057221,"PLD003","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",{"$f":"IF(O235=\"\",\"\",IF(O235=\"LBRA only\",0.2,IF(O235=\"HBRA only\",1,IF(O235=\"within electric line construction area\",19.8,IF(O235=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":1},"Low-moderate",{"$f":"IF(Q235=\"\",\"\",IF(Q235=\"No forecast\",0.1,IF(Q235=\"Low-moderate\",0.2,IF(Q235=\"High\",0.5,IF(Q235=\"Very high\",1,IF(Q235=\"Severe\",2,IF(Q235=\"Extreme\",3.5,5)))))))","v":0.2},{"$f":"IF(OR(P235=\"\",R235=\"\"),\"\",IF(AND(O235=\"within electric line construction area\",Q235=\"No forecast\"),1,P235*R235))","v":0.2},"INC-0017394","20220426PWA_03","CFA reported a pole fire. Powercor dispatch confirmed it was a pole box fire."]
[17,199,"2022-05-04","19:43",-37.734063999999996,144.81421,"25-27 Fox St, St Albans VIC 3021",30114819,"SA010","Low voltage AC (<1kV)","Urban"," - connection box","single phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0017872","20220628PWA_01","MFB reported pole fire.\nCrew found box had overheated due to birds nest\nno ground fire\nfound during outage data review"]
[17,200,"2022-05-05","17:44",-37.729191999999998,143.80864199999999,"5 Forest Ct, Enfield VIC 3352",33008511,"BAS022","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0017876","20220628PWA_02","Report of pole fire\ncrew found FOLCB burnt out\nno ground fire\nfound during outage data review"]
[{"$f":"COUNTA(C238:O238,Q238,T238:V238)","v":17},201,"2022-05-06","12:33",-38.315713000000002,142.44808900000001,"542 Tower Hill Rd, Yangery VIC 3283",30134220,"KRT023","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O238=\"\",\"\",IF(O238=\"LBRA only\",0.2,IF(O238=\"HBRA only\",1,IF(O238=\"within electric line construction area\",19.8,IF(O238=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"No forecast",{"$f":"IF(Q238=\"\",\"\",IF(Q238=\"No forecast\",0.1,IF(Q238=\"Low-moderate\",0.2,IF(Q238=\"High\",0.5,IF(Q238=\"Very high\",1,IF(Q238=\"Severe\",2,IF(Q238=\"Extreme\",3.5,5)))))))","v":0.1},{"$f":"IF(OR(P238=\"\",R238=\"\"),\"\",IF(AND(O238=\"within electric line construction area\",Q238=\"No forecast\"),1,P238*R238))","v":0.45999999999999996},"INC-0017470","20220509PWA_01","Vic fire reported pole mounted junction box fire. \nUpon arrival crew noted  the junction  box had burnt bird nest on the box which could have been the cause of fire."]
[{"$f":"COUNTA(C239:O239,Q239,T239:V239)","v":17},202,"2022-05-09","15:10",-38.246378999999997,142.92361099999999,"62 Dow St, Terang VIC 3264",30046107,"TRG024","22kV AC","Rural Long"," - underground cable","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O239=\"\",\"\",IF(O239=\"LBRA only\",0.2,IF(O239=\"HBRA only\",1,IF(O239=\"within electric line construction area\",19.8,IF(O239=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"No forecast",{"$f":"IF(Q239=\"\",\"\",IF(Q239=\"No forecast\",0.1,IF(Q239=\"Low-moderate\",0.2,IF(Q239=\"High\",0.5,IF(Q239=\"Very high\",1,IF(Q239=\"Severe\",2,IF(Q239=\"Extreme\",3.5,5)))))))","v":0.1},{"$f":"IF(OR(P239=\"\",R239=\"\"),\"\",IF(AND(O239=\"within electric line construction area\",Q239=\"No forecast\"),1,P239*R239))","v":0.45999999999999996},"INC-0017490","20220510PWA_01","Report was received of tractor reversing into pole. It was also reported as fire start. Upon arrival the crew found that a HV cable had ruptured resulted in fault. The cable & pole was burnt. There was no ground fire, no reported injuries or third party property damage."]
[17,203,"2022-05-10","18:18",-37.619982999999998,144.34742,"21 Muddy Ln, Myrniong VIC 3341",32164665,"BMH003","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0017879","20220628PWA_03","Fire brigade reported pole fire\nOn arrival crew found krone box destroyed by fire\nthere was no ground fire\nFound during outage data review"]
[17,204,"2022-05-11","18:17",-37.876871999999999,144.78129200000001,"1B Tyrell Court Altona Meadows, 3028",33074981,"TNA023","Low voltage AC (<1kV)","Rural Short"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0017503","20220512PWA_01","A Powercor Fault crew attended the scene but VicFire had already departed the site.\nThere was evidence that VicFire had doused the pole with water.\nAn inspection of the pole top showed that a ganged, pole-top, low voltage FSD had shorted across two LV phases. \nThere was no ground fire"]
[17,205,"2022-05-13","18:12",-37.757896000000002,144.803845,"11 Austin Street, St Albans 3021",32173507,"SU012","Low voltage AC (<1kV)","Urban"," - overhead conductor (insulated)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0017512","20220516PWA_01","Report received of transformer sparking corner of Austin and Lima Street St Albans.\nOn arrival to site the PCA Faults Crew have advised that the 185mm 1/c cu LV Neutral at \"Austin-Lima\" 300kVA Pole Sub and LV earth has burnt through resulting in customers connected to this Pole Sub experiencing voltages approaching 320V.\nMinor shock reported from customer unit 3 bent st.\nThere was no reported fire."]
[17,206,"2022-05-13","18:02",-37.265068999999997,144.51256900000001,"138 Williatts Ln, Carlsruhe VIC 3442",30150732,"WND023","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0017513","20220516PWA_02","Emergency Vic reported a pole fire.  \nUpon arrival the crew found an FOLCB had been completely burnt. \nThe fire did not spread any further, minor charring on crossarm. \nThe fire was extinguished by the time the crew arrived. \nThere was no reported injuries or third party property damage."]
[17,207,"2022-05-14","19:28",-38.755830000000003,143.66916800000001,"131 Great Ocean Rd, Apollo Bay VIC 3233",34026664,"CLC003","Low voltage AC (<1kV)","Rural Long"," - luminaires (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0017880","20220628PWA_04","Report of pole fire\non arrival crew found lantern fire\nno ground fire\nfound during outage data review "]
[17,208,"2022-05-17","13:39",-38.247145000000003,142.37735499999999,"266 Depot road KOROIT ( BEGA CHEESE LIMITED KOROIT 1 NMI-6203639735)",30150185,"KRT013","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0017537","20220519PWA_02","Report recieved of pole on fire and about to collapse.\nOn arrival crew found that centre phase EDO unit had fractured dropping live backfed lead onto pole.\nThere was no ground fire, no reported injuries or third party property damage.\n"]
[17,209,"2022-05-17","20:39",-38.192374000000001,144.47278,"4 Clarmeont Drive, Leopold 3224",32077238,"DDL014","Low voltage AC (<1kV)","Rural Short"," - fuse (any other type)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0017539","20220519PWA_03","Fuse fire at switchboard ( & meter panel fuse) at 4 Claremont Drive, Leopold 3224. \n Main switch has no overcurrent protection. \n "]
[17,210,"2022-05-20","09:15",-37.668424999999999,143.873649,"286 MT MERCER ROAD,BUNINYONG,VIC,3357",30002733,"BAS022","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0017882","20220628PWA_05","Remains of crossarm fire found by line inspector, occurred some time previous\nThere was no ground fire\nFound during outage data review"]
[17,211,"2022-05-24","08:02",-38.007240000000003,144.35668100000001,"25 WEST GATEWAY LARA,VIC,3212",33044284,"FNS011","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0017582","20220525PWA_01","Passer by reported fire on pole.\nAttending crew found  powercor FOLCB on cross-arm had ignited\nThere was no ground fire, no reported injuries or third party property damage."]
[17,212,"2022-05-25","22:42",-37.766952000000003,144.609658,"1717-1733 Mount Cottrell Rd, Mount Cottrell VIC 3024",30597411,"MLN011","22kV AC","Rural Short"," - pole (wood)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0017647","20220601PWA_01","Vic fire, reported pole and wires down - Car into pole - arking and sparking - Brigade and police onsite. \nUpon arrival, crew found car had hit and damaged the wooden pole and had brought down the HV and LV conductors and resulting in arching which caused patches of grass fires along the whole 50m strip and no HVI. \nPole and fallen conductors all blocking access to car/injured occupant.\n"]
[17,213,"2022-05-25","21:23",-38.173858000000003,144.29989900000001,"CERES LOOKOUT, 37 Cityview Dr, Wandana Heights VIC 3216",32073384,"WPD033","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0017649","20220601PWA_03","Reports of electrical fire at base of comms tower on Cityview drive ..Called in by Vic Fire\nCrew found  FSD had overheated and caught fire, significant public and emergency servcies communications operate from this site\nThere was no reported injuries or third party property damage"]
[17,214,"2022-05-29","20:02",-38.299135999999997,142.02709899999999,"5 Henshaws Rd, Yambuk VIC 3285",30227206,"KRTPLD2","66kV AC","Unknown"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0017657","20220601PWA_06","Following 66KV feeder lockout a patrol found a damaged burnt pole adjacent to YWF switchyard.\nThe pole had burnt in half, top part of structure landing adjacent.\nThere was no ground fire, no reported injuries or third party property damage.\n"]
[17,215,"2022-05-30","07:47",-35.730035000000001,143.18299099999999,"595 Hayes Rd, Culgoa VIC 3530",30020619,"CTN003","Low voltage AC (<1kV)","Rural Long"," - dropper / bridge","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0017695","20220606PWA_05","Dispatch reported on burnt out Transformer leads. \nUpon arrival, crew reported on sparked and burnt off two active LV leads. \nThere was evidence of burning on the pole\nThere was no injuries or third party property damage."]
[17,216,"2022-05-31","14:19",-35.957180999999999,145.50538900000001,"352 Lorenzs Rd, Strathmerton VIC 3641",30551934,"NKA005","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0017885","20220629PWA_01","CFA - Outside of 326 Lorenz rd , Tree branch has fallen on to lines is currently on fire/ lines also appear to be on fire. CFA not on route yet\nNo ground fire\nFound during outage data review"]
[17,217,"2022-06-02","13:33",-37.696067999999997,144.51050699999999,"22 View Gully Rd, Hopetoun Park VIC 3340",30116512,"MLN022","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0017672","20220603PWA_03","Vic fire reported of pole fire at the corner of Hopetoun Park RD and View Gully Rd.\nUpon arrival the crew found that FOLCB had burnt. \nThere was no reported ground fire."]
[17,218,"2022-06-02","09:12",-37.559068000000003,143.85308900000001,"516 Mair St, Ballarat Central VIC 3350",30007359,"BAN005","Low voltage AC (<1kV)","Urban"," - connector / termination","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0017673","20220603PWA_04","Customer advised that wire has come down & is on fire. Fire brigade was on scene.\nUpon arrival the crew found that an IPC had burnt & dislodged.\nConnector landed on ground still burning\nThere was no reported injuries or third party damage."]
[17,219,"2022-06-03","01:20",-37.760857999999999,144.80288200000001,"8 MYTTON CLOSE, ST ALBANS VIC,3021",30114445,"SU012","Low voltage AC (<1kV)","Urban"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0017680","20220606PWA_01"," A crew was attending a LV switch outage incident at pole LIS-15637 on Wangaratta crescent, St Albans, when suddenly the wires on pole LIS-25737 70 metres east started sparking and the junction box on pole  caught fire. The Junction Box melted and the 4 service wires were burnt and damaged.\nThe sparks and hot debris fell onto the wet grass and the road, the fire extinguished by itself, no ground fire was reported.\nThere was no reported injuries or third party property damage."]
[17,220,"2022-06-05","06:20",-36.801248999999999,144.34659500000001,"65C Ryalls Lane Strathfieldsaye 3551",30142804,"BGO013","22kV AC","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0017722","20220608PWA_01","Firecom reported a pole fire, Ryalls Lane corner Strathfieldsaye Road.\nOn arrival crew found that a vehicle had struck pole.\nHV cable was dislodged which in turn ignited a pole fire.\nThere was no ground fire."]
[17,221,"2022-06-10","03:23",-38.294361000000002,141.605671,"87 Princes Highway, Bolwarra 3305",32138786,"PLD001","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0017763","20220614PWA_02","Firecom reported a pole fire at the incident location, on arrival the crew found that a 3 phase FOLCB had overheated and caught fire.\nThere was no ground fire, and only minor charring to the pole. There were no injuries or third party damage."]
[17,222,"2022-06-16","22:39",-37.634399000000002,143.88076599999999,"2108 GEELONG ROAD,MOUNT HELEN,VIC,3350",30230279,"BAS022","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0017790","20220617PWA_02","MFB reported pole fire. intersection of moss ave and geelong road. \nAttending crew found lv box on pole had overheated. \nBurnt debris on ground and some damage to Telstra assets on pole "]
[17,223,"2022-06-22","22:06",-38.209552000000002,142.12969000000001,"32 McGraths Road, Orford 3284",30135525,"KRT013","22kV AC","Rural Long"," - transformer (pole mounted)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0017829","20220623PWA_01","An REC called to report a transformer on the ground and exposed wires at the incident location. Shortly afterwards, while the crew were still enroute, a further call was received from Firecom reporting that the REC had called them and reported a small fire had started from the downed assets at the incident location. \n\nOn arrival the crew found that the 200kVA transformer on the pole had been dislodged by the impact of a car striking P82 Orford Line , 510m away earlier in the night. Wiring from the dislodged transformer made contact with the wood pole and resulted in a small burnt area on the pole. \n"]
[17,224,"2022-06-24","10:22",-37.398282999999999,144.59241900000001,"35 ANZAC ROAD MOUNT MACEDON VIC 3441",30032407,"GSB014","12.7kV AC (SWER)","Rural Short"," - overhead conductor (bare; all aluminium conductor)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0017855","20220627PWA_03","Fire agency reported Tree branch fell on lines out the front of 36 Anzac - Tree branch on fire\nAttending crew found dead limb had blown in from outside the clearance area, contacted  line and had burnt"]
[17,225,"2022-06-30","21:39",-36.458154,143.598793,"opposite 407 Logan-Wedderburn Rd, Wedderburn VIC 3518, Australia",32020947,"CTN002","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0017898","20220701PWA_01","Report of pole fire opposite above address.\nOn arrival, crew found a burnt out FOLCB at the 4m point of the pole substation.   \nNo ground fire, no injuries or third party damage.  "]
[17,226,"2022-06-18","22:52",-38.69415,143.15804800000001,"53 Old Post Office Rd, Princetown VIC 3269",30049477,"COB011","Low voltage AC (<1kV)","Rural Long"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0017975","20220713PWA_02","Report of pole on fire\nCrew found FOLCB had burnt out\nNo ground fire\nFound during OMS data review\nNo photos taken"]
[17,227,"2022-06-12","15:11",-36.776189000000002,144.44500600000001,"1636 McIvor Hwy, Longlea VIC 3551",30255302,"BET005","22kV AC","Rural Long"," - fuse (Fault Tamer)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0017971","20220713PWA_01","Following Report of supply failure crew attended site.\nOn arrival crew found a fault tamer unit burnt in half.\nThere was no ground fire, no reported injuries or third party property damage.\nIncident found during OMS data review"]
[17,228,"2021-09-08","04:28:00",-38.163161000000002,142.98914199999999,"765 Glenormiston Rd, Glenormiston North VIC 3265",32054382,"TRG011","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0018507","20220912PWA_01","Report of pole fire at incident location. On arrival crew found a burnt out Krone box There was no ground fire, no reported injuries or third party property damage found during outage data review."]
[0,229,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,230,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,231,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,232,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,233,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,234,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,235,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,236,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,237,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,238,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,239,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,240,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,241,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,242,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,243,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,244,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,245,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,246,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,247,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,248,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,249,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,250,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]

{"sheet":"3. Systems and Audit","index":4,"n_rows":29,"n_cols":5,"rows_kept":29,"cut":false,"hidden":false,"merged":[[28,1,29,4],[3,5,3,6],[4,5,4,6],[5,5,5,6],[6,1,6,4],[9,1,9,4],[14,1,14,4],[10,1,10,4],[13,1,13,4],[12,1,12,4],[11,1,11,4]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"Powercor"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2021/22"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"Powercor must provide:"}]
[]
[null,"Table 4 - Information or reporting systems"]
[null,"   (1) Name of any IT system used to collect fire start data or fault event data - i.e. SCADA system, or fault reporting system"]
[null,"   (2) Whether the fire recording or fault recording process has been audited or complies with a relevant Australian or industry standard - Yes or No"]
[null,"   (3) List any relevant Australian or industry standards that the fire recording or fault recording process complies with"]
[null,"   (4) Whether the data entered into or removed from the IT system has been audited - Yes or No"]
[]
[]
[null,"Table 4: Information or reporting systems"]
[]
[null,"Information or reporting systems","Name","System Audited","Relevant Standards"]
[null,"System 1","Network Incidents Database","Yes","None applicable"]
[null,"System 2","Outage Management System (OMS)","Yes","None applicable"]
[null,"System 3 ","Smallworld GIS (Graphical Information System)","Yes","None applicable"]
[null,"System 4"]
[null,"System 5"]
[null,"System 6"]
[null,"System 7"]
[null,"System 8"]
[]
[null,"The SGSPAA Internal Audit function undertakes a programme of work in accordance with the SGSPAA Group Internal Audit Plan. This internal audit activity covers elements of the systems and process used for capturing, recording and maintaining fire start data."]