{"text_format":"1","workbook":"xlsx","n_sheets":5,"sheets":["Cover","Contents","1. F-Factor summary","2. Individual fire start info","3. Systems and Audit"],"not_rendered":{"charts":0,"images":2,"macros":1,"external_links":2,"defined_names":97,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Cover","index":0,"n_rows":47,"n_cols":6,"rows_kept":47,"cut":false,"hidden":false,"merged":[[10,0,11,8],[12,0,12,8],[15,0,15,8],[14,0,14,8],[13,0,13,8],[46,1,46,5],[40,1,40,2],[40,3,40,6],[44,1,44,5],[45,1,45,5],[36,1,36,2],[36,3,36,6],[39,1,39,2],[39,3,39,6],[17,0,17,8],[35,1,35,2],[35,3,35,6],[30,2,30,4],[28,2,28,4],[24,2,24,4],[24,0,24,1],[26,2,26,4],[29,2,29,4],[18,0,18,8],[19,0,19,8],[20,0,23,8]]}
[]
[]
[]
[]
[]
[]
[]
["Distribution Network Service Provider"]
["Fire start report"]
[]
["This template is to be used by a DNSP to provide a fire start report to the AER in accordance with section 5 of the F-factor Order in Council.  "]
[]
["Colour coding of input sheets:"]
["Dark blue = AER headings"]
["Grey = AER instructions"]
["Yellow = Input cells"]
["Light orange = Automatically-generated cells"]
[]
["Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so."]
["All dollar amounts are to be unrounded, and in nominal terms."]
[]
[]
[]
[]
["DNSP:",null,"Powercor"]
[]
["DNSP - trading name:",null,"Powercor Australia Ltd"]
[]
["DNSP - Australian business number: ",null,"89 064 651 109"]
[]
["Reporting year:",null,"2016/17"]
[]
[]
[]
[]
["Business address","Address",null,"40 Market Street"]
[null,"Suburb",null,"Melbourne"]
[null,null,"State","Victoria","Postcode",3000]
[]
["Postal address","Address"]
[null,"Suburb"]
[null,null,"State","Victoria","Postcode"]
[]
[]
["Contact name/s","Mark de Villiers"]
["Contact phone/s",396834907]
["Contact email address/s","mdevilliers@powercor.com.au"]

{"sheet":"Contents","index":1,"n_rows":12,"n_cols":8,"rows_kept":12,"cut":false,"hidden":false,"merged":[[2,4,2,10]]}
[" "]
[]
[null,null,null,null,"Electricity Distribution Network Service Provider    F-factor Reporting Template"]
[]
[null,null,null,null,null,null,null,"Table of contents"]
[]
[]
[null,null,"Cover sheet",null,null,"2. Fire start report"]
[]
[]
[]
[null,null,"1. F-factor summary",null,null,"3. Systems and Audit"]

{"sheet":"1. F-Factor summary","index":2,"n_rows":147,"n_cols":15,"rows_kept":147,"cut":false,"hidden":false,"merged":[[26,1,26,2],[8,1,12,1],[16,1,20,1],[5,1,5,2],[3,6,3,8],[4,6,4,8],[5,6,5,8],[13,1,15,1],[6,3,7,3]]}
[null,{"$f":"IF(Cover!C25=\"\",\"[DNSP Name]\", Cover!C25)","v":"Powercor"},"IRU target:",{"$f":"IF(SUM(K6:O6)=0,\"\",SUM(K6:O6))","v":468},null,null,null,null,null,null,"AusNet Services","CitiPower","Jemena","Powercor","United Energy"]
[null,"F-factor data reporting","IRU amount:",{"$f":"IF(SUM('2. Individual fire start info'!U40:U251)=0,\"\",SUM('2. Individual fire start info'!U40:U251))","v":156.61999999999981},null,null,null,null,null,"2016/17",247.7,3.4,9.6999999999999993,468,22.3]
[null,{"$f":"IF(Cover!C31=\"\",\"[Year]\",Cover!C31)","v":"2016/17"},"Revenue adjustment:",{"$f":"IF(OR(D1=\"\",D2=\"\"),\"\",15000*(D1-D2))","v":4670700.0000000037},null,null,null,null,null,"2017/18",247.7,3.4,9.6999999999999993,468,22.3]
[null,null,null,null,null,null,null,null,null,"2018/19",247.7,3.4,9.6999999999999993,468,22.3]
[null,"Table 1: Summary of total fire starts",null,null,null,null,null,null,null,"2019/20",221.1,3.4,9.6999999999999993,412.8,22.3]
[null,"This is a summary of data in worksheet \"2. Fire Start Report\"",null,null,null,null,null,null,null,null,{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>K1),\"\",LOOKUP($B3,$J2:$J5,K2:K5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>L1),\"\",LOOKUP($B3,$J2:$J5,L2:L5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>M1),\"\",LOOKUP($B3,$J2:$J5,M2:M5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>N1),\"\",LOOKUP($B3,$J2:$J5,N2:N5))","v":468},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>O1),\"\",LOOKUP($B3,$J2:$J5,O2:O5))","v":""}]
[null,null,null,"Total fires by category"]
[null,"Fire Start by Category","Fire Start by Asset"]
[null,"Asset failures resulting in grass/vegetation fire","Pole and cross arm failure or Pole and cross arm fire",{"$f":"COUNTIF('2. Individual fire start info'!$K$40:$K$251,'1. F-Factor summary'!$J9)","v":9},null,null,null,null,null,{"$f":"B9&\" : \"&C9","v":"Asset failures resulting in grass/vegetation fire : Pole and cross arm failure or Pole and cross arm fire"}]
[null,null,"Oil-filled plant",{"$f":"COUNTIF('2. Individual fire start info'!$K$40:$K$251,'1. F-Factor summary'!$J10)","v":2},null,null,null,null,null,{"$f":"B9&\" : \"&C10","v":"Asset failures resulting in grass/vegetation fire : Oil-filled plant"}]
[null,null,"HV Fuse",{"$f":"COUNTIF('2. Individual fire start info'!$K$40:$K$251,'1. F-Factor summary'!$J11)","v":5},null,null,null,null,null,{"$f":"B9&\" : \"&C11","v":"Asset failures resulting in grass/vegetation fire : HV Fuse"}]
[null,null,"Other Assets",{"$f":"COUNTIF('2. Individual fire start info'!$K$40:$K$251,'1. F-Factor summary'!$J12)","v":36},null,null,null,null,null,{"$f":"B9&\" : \"&C12","v":"Asset failures resulting in grass/vegetation fire : Other Assets"}]
[null,null,"Any fire triggered by any asset failure caused by Lightning",{"$f":"COUNTIF('2. Individual fire start info'!$K$40:$K$251,'1. F-Factor summary'!$J13)","v":9},null,null,null,null,null,{"$f":"B9&\" : \"&C13","v":"Asset failures resulting in grass/vegetation fire : Any fire triggered by any asset failure caused by Lightning"}]
[null,"Grass/vegetation fires from assets (non-asset failures)","Fire starts in grass/vegetation resulting from animal contact with network assets",{"$f":"COUNTIF('2. Individual fire start info'!$K$40:$K$251,'1. F-Factor summary'!$J14)","v":13},null,null,null,null,null,{"$f":"B14&\" : \"&C14","v":"Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from animal contact with network assets"}]
[null,null,"Fire starts in grass/vegetation resulting from trees contacting network assets",{"$f":"COUNTIF('2. Individual fire start info'!$K$40:$K$251,'1. F-Factor summary'!$J15)","v":19},null,null,null,null,null,{"$f":"B14&\" : \"&C15","v":"Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"}]
[null,null,"Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)",{"$f":"COUNTIF('2. Individual fire start info'!$K$40:$K$251,'1. F-Factor summary'!$J16)","v":23},null,null,null,null,null,{"$f":"B14&\" : \"&C16","v":"Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"}]
[null,"Asset failures resulting in asset fire (no grass/vegetation fire)","Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)",{"$f":"COUNTIF('2. Individual fire start info'!$K$40:$K$251,'1. F-Factor summary'!$J17)","v":25},null,null,null,null,null,{"$f":"B17&\" : \"&C17","v":"Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"}]
[null,null,"Oil-filled plant fire",{"$f":"COUNTIF('2. Individual fire start info'!$K$40:$K$251,'1. F-Factor summary'!$J18)","v":0},null,null,null,null,null,{"$f":"B17&\" : \"&C18","v":"Asset failures resulting in asset fire (no grass/vegetation fire) : Oil-filled plant fire"}]
[null,null,"HV Fuse Failure (including ‘hang-ups’ and ‘candling’)",{"$f":"COUNTIF('2. Individual fire start info'!$K$40:$K$251,'1. F-Factor summary'!$J19)","v":13},null,null,null,null,null,{"$f":"B17&\" : \"&C19","v":"Asset failures resulting in asset fire (no grass/vegetation fire) : HV Fuse Failure (including ‘hang-ups’ and ‘candling’)"}]
[null,null,"Other Assets",{"$f":"COUNTIF('2. Individual fire start info'!$K$40:$K$251,'1. F-Factor summary'!$J20)","v":36},null,null,null,null,null,{"$f":"B17&\" : \"&C20","v":"Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"}]
[null,null,"Any fire triggered by any asset failure caused by Lightning",{"$f":"COUNTIF('2. Individual fire start info'!$K$40:$K$251,'1. F-Factor summary'!$J21)","v":2},null,null,null,null,null,{"$f":"B17&\" : \"&C21","v":"Asset failures resulting in asset fire (no grass/vegetation fire) : Any fire triggered by any asset failure caused by Lightning"}]
[null,"Any other Fire Start","Any additional fires, caused by any asset failure, not reported to the ESV and required to be reported by the f-factor Order",{"$f":"COUNTIF('2. Individual fire start info'!$K$40:$K$251,'1. F-Factor summary'!$J22)","v":3},null,null,null,null,null,{"$f":"B22&\" : \"&C22","v":"Any other Fire Start : Any additional fires, caused by any asset failure, not reported to the ESV and required to be reported by the f-factor Order"}]
[null,"Total",null,{"$f":"SUM(D9:D22)","v":195}]
[]
[]
[null,"Table 2: Summary of total fire starts by F factor Order definition"]
[null,"This is a summary of data in worksheet \"2. Fire Start Report\""]
[null,"Kind of Fire Start by definition of fire start under clause 5 of F-factor Order","Total fires by cause",null,null,null,null,null,null,"Overhead conductors"]
[null,"Started in or originated from a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$40:$N$251,'1. F-Factor summary'!$B29)","v":120},null,null,null,null,null,null," - overhead conductor (bare; aluminium core steel reinforced)"]
[null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$40:$N$251,'1. F-Factor summary'!$B30)","v":21},null,null,null,null,null,null," - overhead conductor (bare; all aluminium conductor)"]
[null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$40:$N$251,'1. F-Factor summary'!$B31)","v":19},null,null,null,null,null,null," - overhead conductor (bare; copper)"]
[null,"Started by lightning striking a distribution system or a part of a distribution system ",{"$f":"COUNTIF('2. Individual fire start info'!$N$40:$N$251,'1. F-Factor summary'!$B32)","v":11},null,null,null,null,null,null," - overhead conductor (bare; steel)"]
[null,"Started by any other thing forming part of or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$40:$N$251,'1. F-Factor summary'!$B33)","v":24},null,null,null,null,null,null," - overhead conductor (ABC)"]
[null,"Otherwise started by a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$40:$N$251,'1. F-Factor summary'!$B34)","v":0},null,null,null,null,null,null," - overhead conductor (covered uninsulated)"]
[null,"Total",{"$f":"SUM(C29:C34)","v":195},null,null,null,null,null,null," - overhead conductor (insulated)"]
[null,null,null,null,null,null,null,null,null,"Service lines"]
[null,null,null,null,null,null,null,null,null," - overhead service conductor (residential)"]
[null,null,null,null,null,null,null,null,null," - overhead service conductor (commercial / industrial)"]
[null,null,null,null,null,null,null,null,null," - overhead service conductor (subdivision / construction)"]
[null,null,null,null,null,null,null,null,null," - overhead service conductor (other)"]
[null,null,null,null,null,null,null,null,null," - underground service cable (residential)"]
[null,null,null,null,null,null,null,null,null," - underground service cable (commercial / industrial)"]
[null,null,null,null,null,null,null,null,null," - underground service cable (subdivision / construction)"]
[null,null,null,null,null,null,null,null,null," - underground service cable (other)"]
[null,null,null,null,null,null,null,null,null,"Underground cables"]
[null,null,null,null,null,null,null,null,null," - underground cable"]
[null,null,null,null,null,null,null,null,null," - underground communications cable"]
[null,null,null,null,null,null,null,null,null,"Poles"]
[null,null,null,null,null,null,null,null,null," - pole (concrete)"]
[null,null,null,null,null,null,null,null,null," - pole (steel)"]
[null,null,null,null,null,null,null,null,null," - pole (wood)"]
[null,null,null,null,null,null,null,null,null,"Crossarms"]
[null,null,null,null,null,null,null,null,null," - crossarm (wood)"]
[null,null,null,null,null,null,null,null,null," - crossarm (steel)"]
[null,null,null,null,null,null,null,null,null," - crossarm (other)"]
[null,null,null,null,null,null,null,null,null,"Overhead assets"]
[null,null,null,null,null,null,null,null,null," - capacity balancing units"]
[null,null,null,null,null,null,null,null,null," - connector / termination"]
[null,null,null,null,null,null,null,null,null," - dropper / bridge"]
[null,null,null,null,null,null,null,null,null," - guy wire"]
[null,null,null,null,null,null,null,null,null," - insulator tie wires / connections"]
[null,null,null,null,null,null,null,null,null," - insulators"]
[null,null,null,null,null,null,null,null,null," - tower"]
[null,null,null,null,null,null,null,null,null," - traction lines"]
[null,null,null,null,null,null,null,null,null,"Underground assets"]
[null,null,null,null,null,null,null,null,null," - LV pillar"]
[null,null,null,null,null,null,null,null,null," - services pit"]
[null,null,null,null,null,null,null,null,null,"Transformers"]
[null,null,null,null,null,null,null,null,null," - transformer (pole mounted)"]
[null,null,null,null,null,null,null,null,null," - transformer (kiosk mounted)"]
[null,null,null,null,null,null,null,null,null," - transformer (ground outdoor mounted)"]
[null,null,null,null,null,null,null,null,null," - transformer (indoor chamber mounted)"]
[null,null,null,null,null,null,null,null,null," - transformer (any other type)"]
[null,null,null,null,null,null,null,null,null," - measurement transformer (current transformer)"]
[null,null,null,null,null,null,null,null,null," - measurement transformer (voltage transformer)"]
[null,null,null,null,null,null,null,null,null," - measurement transformer (capacitive voltage transformer)"]
[null,null,null,null,null,null,null,null,null,"Fuses and switchgear"]
[null,null,null,null,null,null,null,null,null," - fuse (boric acid)"]
[null,null,null,null,null,null,null,null,null," - fuse (EDO fuse)"]
[null,null,null,null,null,null,null,null,null," - fuse (Fault Tamer)"]
[null,null,null,null,null,null,null,null,null," - fuse (powder filled)"]
[null,null,null,null,null,null,null,null,null," - fuse (any other type)"]
[null,null,null,null,null,null,null,null,null," - circuit breaker"]
[null,null,null,null,null,null,null,null,null," - switch (disconnector/isolator)"]
[null,null,null,null,null,null,null,null,null," - switch (earth)"]
[null,null,null,null,null,null,null,null,null," - switch (FuseSaver)"]
[null,null,null,null,null,null,null,null,null," - switch (any other type)"]
[null,null,null,null,null,null,null,null,null,"SCADA, network control and protection systems"]
[null,null,null,null,null,null,null,null,null," - audio frequency load controller (AFLC)"]
[null,null,null,null,null,null,null,null,null," - arc suppresion coil"]
[null,null,null,null,null,null,null,null,null," - automatic circuit recloser (ACR)"]
[null,null,null,null,null,null,null,null,null," - communications linear assets"]
[null,null,null,null,null,null,null,null,null," - communications network assets"]
[null,null,null,null,null,null,null,null,null," - communications site infrastructure"]
[null,null,null,null,null,null,null,null,null," - field devices"]
[null,null,null,null,null,null,null,null,null," - local network wiring assets"]
[null,null,null,null,null,null,null,null,null," - master station assets"]
[null,null,null,null,null,null,null,null,null," - neutral earthing resistor"]
[null,null,null,null,null,null,null,null,null," - oil-filled circuit recloser (OCR)"]
[null,null,null,null,null,null,null,null,null," - rapid earth fault current limiter (REFCL)"]
[null,null,null,null,null,null,null,null,null," - surge diverter"]
[null,null,null,null,null,null,null,null,null," - voltage regulator"]
[null,null,null,null,null,null,null,null,null,"Public lighting"]
[null,null,null,null,null,null,null,null,null," - brackets (major road)"]
[null,null,null,null,null,null,null,null,null," - brackets (minor road)"]
[null,null,null,null,null,null,null,null,null," - lamps (major road)"]
[null,null,null,null,null,null,null,null,null," - lamps (minor road)"]
[null,null,null,null,null,null,null,null,null," - luminaries (major road)"]
[null,null,null,null,null,null,null,null,null," - luminaries (minor road)"]
[null,null,null,null,null,null,null,null,null," - poles / columns (major road)"]
[null,null,null,null,null,null,null,null,null," - poles / columns (minor road)"]
[null,null,null,null,null,null,null,null,null,"Other "]
[null,null,null,null,null,null,null,null,null," - connection box"]
[null,null,null,null,null,null,null,null,null," - earth / earthing"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Extra low voltage AC (<50V)"]
[null,null,null,null,null,null,null,null,null,"Low voltage AC (<1kV)"]
[null,null,null,null,null,null,null,null,null,"2.2kV AC"]
[null,null,null,null,null,null,null,null,null,"6.6kV AC"]
[null,null,null,null,null,null,null,null,null,"11kV AC"]
[null,null,null,null,null,null,null,null,null,"12.7kV AC (SWER)"]
[null,null,null,null,null,null,null,null,null,"22kV AC"]
[null,null,null,null,null,null,null,null,null,"33kV AC"]
[null,null,null,null,null,null,null,null,null,"66kV AC"]
[null,null,null,null,null,null,null,null,null,"132kV AC"]
[null,null,null,null,null,null,null,null,null,"220kV AC"]
[null,null,null,null,null,null,null,null,null,"330kV AC"]
[null,null,null,null,null,null,null,null,null,"500kV AC"]
[null,null,null,null,null,null,null,null,null,"Extra low voltage DC (<120V ripple free)"]
[null,null,null,null,null,null,null,null,null,"Low voltage DC (<1.5kV)"]
[null,null,null,null,null,null,null,null,null,"600V DC"]
[null,null,null,null,null,null,null,null,null,"1500V DC"]
[null,null,null,null,null,null,null,null,null,"Earthing cable"]
[]
[]
[null,null,null,null,null,null,null,null,null,"single wire earth return (SWER)"]
[null,null,null,null,null,null,null,null,null,"single phase"]
[null,null,null,null,null,null,null,null,null,"two phase"]
[null,null,null,null,null,null,null,null,null,"three phase"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Negligible: no ground fire"]
[null,null,null,null,null,null,null,null,null,"Localised: less than 10 sq.m"]
[null,null,null,null,null,null,null,null,null,"Small: 10 - 1000 aq.m"]
[null,null,null,null,null,null,null,null,null,"Medium: 1000 sq.m - 10 ha"]
[null,null,null,null,null,null,null,null,null,"Large: more than 10 ha"]

{"sheet":"2. Individual fire start info","index":3,"n_rows":251,"n_cols":24,"rows_kept":251,"cut":false,"hidden":false,"merged":[[23,1,23,20],[19,1,19,20],[26,1,26,20],[21,1,21,23],[29,1,29,22],[37,10,37,13],[25,1,25,20],[37,21,37,23],[35,1,35,4],[37,14,37,19],[37,2,37,9],[30,1,30,20],[28,1,28,23],[31,1,31,20],[3,24,3,26],[4,24,4,26],[5,24,5,26],[7,1,7,23],[27,1,27,20],[11,1,11,2],[13,1,13,11],[22,1,22,23],[24,1,24,23],[14,1,14,22],[15,1,15,20],[16,1,16,20],[17,1,17,20],[20,1,20,20],[9,1,9,23],[18,1,18,20]]}
[null,{"$f":"IF(Cover!C25=\"\",\"[DNSP Name]\", Cover!C25)","v":"Powercor"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!C31=\"\",\"[Year]\",Cover!C31)","v":"2016/17"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"\"Enter into this worksheet fire start data, from any IT system, which have been recorded by \"&IF(Cover!C25=\"\",\"[DNSP Name]\", Cover!C25)&\". Note that fire starts must be in accordance with the definition of a fire start in the Order In Council.\"","v":"Enter into this worksheet fire start data, from any IT system, which have been recorded by Powercor. Note that fire starts must be in accordance with the definition of a fire start in the Order In Council."}]
[]
[null,"\"Fire\" should be interpreted using its common meaning and can be defined as a process in which substances combine chemically with oxygen from the air and typically give out bright light, heat and smoke. A fire should be recorded where there is evidence of smoking, charring, scorching, burning or any other evidence that a fire had occurred.  "]
[]
[null,{"$f":"IF(Cover!C25=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!C25,\" must provide:\"))","v":"Powercor must provide:"}]
[]
[null,"Table 3 - Individual Fire Starts"]
[null,"   (1) Date - dd/mm/yyyy"]
[null,"   (2) Time - if known, the 24-hour time of the fire start hh:mm"]
[null,"   (3) Latitude and longitude of the fire start as decimal coordinates"]
[null,"   (4) Asset number for the asset nearest the fire start"]
[null,{"$f":"\"   (5) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the \"&B1&\" network\"","v":"   (5) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the Powercor network"}]
[null,"   (6) Voltage on the line in which the fire start occurred (note: this may not be the nearest polyphase overhead line)"]
[null,"   (7) Network categorisation - CBD, Urban, Rural Long or Rural Short"]
[null,"   (8) Fire start by category in accordance with ESV quarterly reporting categories"]
[null,"   (9) Asset type of primary asset causing fire in accordance with OSIRIS asset categories"]
[null,"   (10) Where the asset involved in the fire is a transformer or an overhead or underground line, provide the phase of the line or transformer"]
[null,"   (11) Kind of fire start in accordance with categories specified in Clause 5 of the F-factor Order-In-Council"]
[null,"   (12) Rating of High Bushfire Risk Area (HBRA) or Low Bushfire Risk Are (LBRA) as assigned by CFA & MFB under s.80 of the Electricity Safety Act"]
[null,"   (13) Identify the location of the fire start in accordance with the categories specified in Clause 11(b) of the F-factor Order-In-Council"]
[null,"   (14) Has the CFA declared a fire danger period under the Country Fire Authority Act 1958 - Y/N?"]
[null,"   (15) Where a fire danger period has been declared, provide the daily CFA fire danger rating (or leave blank if the area has not yet been declared)"]
[null,{"$f":"\"   (16) \"&IF(Cover!C25=\"\",\"[DNSP Name]\", Cover!C25)&\"'s record number for the incident\"","v":"   (16) Powercor's record number for the incident"}]
[null,"   (17) ESV's OSIRIS reference number for the incident"]
[null,"   (18) Free text description of the fault containing relevant comments from field reports "]
[]
[]
[]
[null,"Table 3: Individual Fire Starts"]
[]
[null,"Number","Fire starts",null,null,null,null,null,null,null,"Fire Type",null,null,null,"Risk Factors",null,null,null,null,null,"IRU \namount"]
[null,null,"Date 1","Time 2","Latitude 3","Longitude 3","ID of \nnearest \nasset 4","ID of nearest \npolyphase \nline 5","Voltage of line in which \nfire start \noccurred 6","Network categorisation 7","Fire start by \nESV category 8","Fire start by\nasset type 9","Phase of \nline or \ntransformer 10","Kind of fire start as per Clause 5\nof F-factor Order-In-Council 11","HBRA or \nLBRA 12","Location \narea 13","Location\nmultiplier","Fire danger period declared? 14","Fire \ndanger \nrating 15","Danger multiplier","Product of multipliers","DNSP record number 16","OSIRIS \n(ESV) reference \nnumber 17","Fault \ndescription 18"]
[null,1,"2016-07-12","13:14:00",-36.308070000000001,145.03192000000001,33088654,"KYM004","66kV AC","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA","LBRA only",{"$f":"IF(P40=\"\",\"\",IF(P40=\"LBRA only\",0.2,IF(P40=\"HBRA only\",1,IF(P40=\"within electric line construction area\",19.8,IF(P40=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"N","No forecast",{"$f":"IF(S40=\"\",\"\",IF(S40=\"No forecast\",0.1,IF(R40=\"N\",0.1,IF(S40=\"Low-moderate\",0.2,IF(S40=\"High\",0.5,IF(S40=\"Very high\",1,IF(S40=\"Severe\",2,IF(S40=\"Extreme\",3.5,5))))))))","v":0.1},{"$f":"IF(OR(Q40=\"\",T40=\"\"),\"\",IF(AND(P40=\"within electric line construction area\",S40=\"No forecast\"),1,Q40*T40))","v":2.0000000000000004E-2},12225,"20160713PWA_02","Customers report a tree over the lines at the above address. Reports of smoke/fire. CFA attended site. A Powercor crew attended and found a tree from outside clearance space had fallen across 66kV/22kV/LV conductors between P309 and 310 SHTS KYM 2 line. No conductors had broken. The 66kV protection operated. The 22kV was still alive when crew arrived. Crew observed possible tracking between 22kV conductors and LV conductors via tree. Operations isolated the 22kV feeder at Kyabram ZSS. Crew cut tree clear of lines. Crew inspected 66kV/22kV/LV conductors for damage. No conductor damage evident. LEI was not called to site and did not attend. No reports of damage from customers on the day. No shocks, injuries or ground fire starts."]
[null,2,"2016-07-13","23:06:00",-37.053410999999997,142.77672999999999,30252068,"STL006","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - fuse (any other type)","single phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"N","No forecast",0.1,2.0000000000000004E-2,12229,"20160715PWA_02","The CFA reported the fuse box smouldering at the above location. When our crew arrived they found that the connections into an LV Service Fuse Base on the meter board had overheated and caused a small fire. The fire was contained to a small area of the meter board (4cm diameter hole). The crew isolated supply and carried out the necessary repairs.  There was no ground fire or reported injuries."]
[null,3,"2016-07-15","20:00:00",-35.978203999999998,145.74101999999999,32182471,"CME014","22kV AC","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : HV Fuse Failure (including ‘hang-ups’ and ‘candling’)"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"N","No forecast",0.1,2.0000000000000004E-2,12236,"20160719PWA_01","Customer reported sparking transformer at the incident location.  On arrival the crew found that a Boric Acid HV fuse had candled, the fuse remained in the carrier intact. Crew pulled the 2 other fuses, which stopped the candling on the red phase. There were no reported injuries, no ground fire, no damage to 3rd party property."]
[null,4,"2016-07-15","19:03:00",-36.587518000000003,142.38893999999999,32090075,"HSM001","12.7kV AC (SWER)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA","HBRA only",1,"N","No forecast",0.1,0.1,12235,"20160718PWA_02","VicFire reported a pole fire at the incident location.  On arrival the crew found that a high voltage wooden SWER s/s pole had burnt through approximately 4m above ground and had fallen to the ground. There was no ground fire. There were no reported injuries."]
[null,5,"2016-07-15","04:39:00",-37.414448,143.12887000000001,30005619,"BAS011","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","two phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"N","No forecast",0.1,0.45999999999999996,12233,"20160715PWA_04","VicFire reported a pole fire at the incident location.  On arrival the crew found that a low voltage junction box mounted on Challicum 1 wooden SWER s/s pole had burnt through and required replacement. There was no ground fire. There were no reported injuries or third party property damage."]
[null,6,"2016-07-22","10:52:00",-38.302446000000003,142.30706000000001,33102370,"KRT013","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : HV Fuse Failure (including ‘hang-ups’ and ‘candling’)"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"N","No forecast",0.1,0.45999999999999996,12283,"20160802PWA_05","A Fault crew attending an outage found that an EDO fuse had operated at the incident location, however the barrel of the EDO fuse stayed in position without dropping down.  The barrel then caught fire.  There was no ground fire.  There were no reported injuries or third party property damages."]
[null,7,"2016-07-24","18:32:00",-37.923163000000002,141.27539999999999,30089503,"PLD003","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"N","No forecast",0.1,0.1,12289," 20160803PWA_02","A  customer reported a small fire at the top of a pole. On arrival the attending crew found that a fire had burnt  and significantly damaged substation pole Dartmoor town 18. There was no evidence of ground fire identifiable.  There were no reported injuries. Crew identified termination/s of insulated HV dropper set (centre phase) was resting on step iron and fire had ignited at this point. Longer HV insulated lead set had been used and extended to reach HV fuse units. Attending crew isolated supply and made temporary repairs. Pole to be replaced  25 July 2016."]
[null,8,"2016-07-25","20:40:00",-34.290818999999999,142.18536,33109198,"RCT023","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Any fire triggered by any asset failure caused by Lightning"," - transformer (pole mounted)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA","LBRA only",0.2,"N","No forecast",0.1,2.0000000000000004E-2,12298,"20160804PWA_01","VicFire Comms reports a transformer on fire at intersection of Avocat Avenue and Moonah St Red Cliffs.  On arrival the crew found Moonah P1A ACR transformer on fire and lid had come off transformer. Isolated ACR and bypassed to restore supply. There was no ground fire. There were no reported injuries or third party property damages."]
[null,9,"2016-08-01","23:15:00",-37.608629000000001,144.59008,33077208,"MLN012","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"N","No forecast",0.1,0.1,12324,"20160818PWA_04","Customer reported fire at substation pole across the road. (Diggers Rest P1 substation is a 63kVA??? transformer on a 12.5m/8kN concrete pole)\nA Powercor crew attended and made the site safe by disconnecting the transformer LVABC FSD isolator and LV leads. LV  Leads were re-dressed and a new transformer LVABC FSD isolator was fitted. There were no reported injuries. There was no ground fire."]
[null,10,"2016-08-08","09:21:00",-38.240499,142.91585000000001,30042402,"TRG004","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"N","No forecast",0.1,2.0000000000000004E-2,12340,"20160822PWA_02","CFA reported pole fire at the incident location. On arrival the crew found that a low voltage connection had overheated and caught fire resulting in damage to the connector. There was no ground fire. There were no reported injuries."]
[null,11,"2016-08-15","10:12:00",-36.365175000000001,145.29991999999999,33088545,"MNA014","22kV AC","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from animal contact with network assets"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA","LBRA only",0.2,"N","No forecast",0.1,2.0000000000000004E-2,12319,"20160815PWA_03","On arrival the fault crew found that a 22kV overhead conductor had broken off at the dead end and the conductor was hanging low about 1.5 meters. \nThe conductor dead end appears to have broken as a result of a flashover involving two black ducks (both deceased) on the substation. The conductor fell and is hanging supported by the “live line clamp and flex” resting in fruit trees and trellis of the fruit trees some of which have been burnt. In addition it appears the galvanized wires supporting the fruit trees were ”ALIVE” at 22kV. The incident has caused damage to a section of polytube irrigation (20 meters) which was running along the ground near the fruit trees. Two areas have been burnt (9m by 1m  & 8m by 1m). Total area burnt about 17 meters square. Also burning evident on some small trees. The crew prepared to isolate the area when the MNA14 22kV feeder circuit breaker tripped. There was no injury as a result of this incident."]
[null,12,"2016-08-19","09:53:00",-34.171382999999999,142.06541000000001,30099608,"MBN021","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in grass/vegetation fire : Other Assets"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"N","No forecast",0.1,2.0000000000000004E-2,12335,"20160819PWA_07","A employee reported a service wire on the ground at the incident location.  On arrival the crew found that a service cable had broken and came to the ground alive resulting in burnt a patch of ground approx. 0.5msq. No protection operated. There were no reported injuries, shocks or third party property damages."]
[null,13,"2016-08-21","18:12:00",-37.958528250000001,144.68636287999999,30110409,"WBE034","22kV AC","Rural Short","Any other Fire Start : Any additional fires, caused by any asset failure, not reported to the ESV and required to be reported by the f-factor Order"," - crossarm (wood)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA","LBRA only",0.2,"N","No forecast",0.1,2.0000000000000004E-2,12372,"20160901PWA_04 ","Customer called the incident in to Powercor. Customer reported a fire on a pole outside his house. He indicated that the fire was extinguished, but sparking was still occurring at the time of his call. There was no ground fire. A Powercor crew attended and discovered that a vehicle had collided into pole LIS 203209 in Diggers Rd. The collision impact had caused an outer phase HV conductor to break free from the HV insulator and fall below the HV crossarm making contact with a wet pole surface. The conductor to pole contact duration was sufficient enough to cause charring/burning of the pole section to require replacing the pole. A damaged vehicle was discovered approx. 100m further along the road, but the driver, or occupants were not present at the scene. There were no reported injuries."]
[null,14,"2016-09-08","06:20:00",-37.967441000000001,144.13079999999999,30068949,"GL015","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : HV Fuse Failure (including ‘hang-ups’ and ‘candling’)"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"N","No forecast",0.1,0.45999999999999996,12406,"20160913PWA_02 ","A customer reported a small flame on the middle of cross arm at the incident location.   On arrival the crew found that an EDO fuse had operated. And they also found evidence of smouldering, however the barrel of the EDO fuse stayed in position without dropping down. No ground fire.  There were no reported injuries. No third party property damage."]
[null,15,"2016-09-09","14:53:00",-38.311548999999999,142.42934,33100239,"KRT031","22kV AC","Urban","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"N","No forecast",0.1,0.45999999999999996,12420,"20160915PWA_01","A reclose occurred on the KRT031 CB at 1441 on 9/9/16. The customer at the incident location called to report they had no supply. On arrival the crew found a blown HV fuse on the substation, with a crow lodged on the Guthrie guard. The customer later reported that at the time of the outage, some of his cows fell down in the dairy, however they recovered quickly. The crew could see no indications of a HVI, they did however find a splash mark on the earth at the base of the concrete substation pole. After removal of the bird, the crew replaced the HV fuse, which resulted in a meter at the dairy catching fire, supply was quickly isolated. Minor damage was caused to the meter board, however the board remained serviceable. An LEI was called, and further tests revealed a burnt off neutral connection in a junction box. No third party damage, no injuries."]
[null,16,"2016-09-10","19:06:00",-36.144179999999999,144.73356999999999,33083600,"ECA012","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"N","No forecast",0.1,0.1,12415,"20160914PWA_02","Vic Fire reported a fire on a pole at the incident location.  On arrival the crew found that a LV FOLCB had failed and caught on fire, no ground fire occurred as a result. There were no reported injuries, no third party damage."]
[null,17,"2016-09-11","01:04:00",-36.441175000000001,145.36259999999999,33096154,"MNA024","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"N","No forecast",0.1,2.0000000000000004E-2,12426,"20160916PWA_01","Vic Fire reported a fire on a pole at the incident location.  On arrival the crew found that a LV FOLCB had failed and caught on fire, no ground fire occurred as a result. There were no reported injuries, no third party damage. Failure of FOLCB coincided with underfloor heating time-switch operation, validated by customer whom I spoke with whilst obtaining photos the following day ( schedule Shepparton visit )."]
[null,18,"2016-09-14","14:20:00",-36.772528399999999,144.43934798000001,33031488,"BET005","12.7kV AC (SWER)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"N","No forecast",0.1,0.45999999999999996,13220,"20170714PWA_03","Crew attending outage found damaged and burnt SWER pole-top. Centre phase burnt off pole-top. Crew repaired and replaced with new 'P' bracket."]
[null,19,"2016-09-23","09:07:00",-38.184604999999998,144.36657,33040421,"GLE012","Low voltage AC (<1kV)","Urban","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"N","No forecast",0.1,2.0000000000000004E-2,12456,"20160927PWA_01","A customer reported a transformer on fire at the incident location. Upon arrival, the Powercor crew found that an overheated FSD ignited and the fire self-extinguished. The crew made the place safe and repairs done. There were no injuries or ground fire."]
[null,20,"2016-10-06","20:05:00",-38.076500000000003,144.36922999999999,30268929,"FNS021","22kV AC","Rural Short","Any other Fire Start : Any additional fires, caused by any asset failure, not reported to the ESV and required to be reported by the f-factor Order"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA","HBRA only",1,"N","No forecast",0.1,0.1,12484,"20161012PWA_05","CFA reported wire crossing roadway on fire. Upon arrival, the Powercor fault crew found a car had hit the pole and left the scene. The centre phase HV conductor tie had broken and the HV was resting on the x-arm. The LV x-arm had burnt through at the neutral pin and broken off. No reported injuries or ground fire."]
[null,21,"2016-10-15","14:29:00",-37.489586000000003,144.56739999999999,30034797,"GSB011","22kV AC","Rural Short","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"N","No forecast",0.1,0.45999999999999996,12493,"20161017PWA_01 ","Customer reported a tree over HV conductors at the incident location. On arrival the crew found that a HV conductor had been brought down by a large tree, resulting in a several small ground fires, 4m square in total. It is suspected that the conductor remained back-fed through transformer HV windings until the feeder protection eventually cleared the fault. Conductors were down over the Gisborne to Bacchus Marsh road also until crews arrived on site and made safe. There were no reported injuries."]
[null,22,"2016-10-15","11:50:00",-37.423369000000001,144.52019999999999,32045417,"WND011","22kV AC","Rural Short","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"N","No forecast",0.1,0.45999999999999996,12494,"20161017PWA_02 ","Customer reported a fire at the incident location. On arrival the crew found that a HV conductor had been brought down by a tree, a ground fire of 1500m square resulted where the HV conductor broke and came to the ground. Protection operated, however a localised backfeed through transformer HV windings meant the downed conductor remained partially energised. There were no reported injuries."]
[null,23,"2016-10-15","11:47:00",-37.507832999999998,144.58004,30034631,"GSB011","22kV AC","Rural Short","Asset failures resulting in grass/vegetation fire : Pole and cross arm failure or Pole and cross arm fire"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"N","No forecast",0.1,0.45999999999999996,12507,"20161021PWA_03 ","Vic Fire reported HV conductors in contact with vegetation at the incident location. On arrival the crew found that a HV t/off cross-arm on Bundaleer P2 broke causing conductor to hang low and make contact with vegetation beneath, the arcing intermittently caused the vegetation to ignite, initial report made reference to flames and sparking. Spur was isolated and repairs carried out. There were no reported injuries, no ground fire & no 3rd party damage."]
[null,24,"2016-10-15","10:09:00",-37.415792000000003,144.58794,32043265,"GSB014","22kV AC","Rural Short","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"N","No forecast",0.1,0.45999999999999996,12530,"20161102PWA_03 ","SCADA alarm indicated supply had been lost beyond “Mt Macedon P130 ACR”. On arrival and subsequent line patrol the crew found that a branch from a cypress tree had fallen over conductors outside #9 Clarke Street, Macedon caused the ACR to trip to L/O, the branch had evidence of arcing and was heavily charred where it was in contact with the 22kV conductors. There were no reported injuries, no ground fire & no 3rd party damage."]
[null,25,"2016-10-15","14:35:00",-34.197735999999999,142.03731999999999,33066831,"MBN014","22kV AC","Rural Short","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from animal contact with network assets"," - crossarm (wood)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA","LBRA only",0.2,"N","No forecast",0.1,2.0000000000000004E-2,12495,"20161017PWA_03","Customer reported a supply interruption and wires hanging low at the incident location. On arrival the crew found that a birds nest containing numerous pieces of wire had shorted out between the concrete pole and an LV isolator, resulting in the wooden LV crossarm burning through and failing. Falling combusting material also started a ground fire of approximately 10m square which self extinguished."]
[null,26,"2016-10-18","20:57:00",-37.633868999999997,143.57362000000001,30000848,"BAS011","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in grass/vegetation fire : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","HBRA","within electric line construction area",19.8,"N","No forecast",0.1,1,12499,"20161019PWA_01","Vic fire reported a pole fire at the incident location.  On arrival the crew found that the connections in a 3 phase fused mains box (FOLCB) had overheated, resulting in the box catching fire. Crew made the site safe and performed repairs. There was a small ground fire. There were no reported injuries."]
[null,27,"2016-10-18","19:22:00",-38.346398000000001,143.78382999999999,32062029,"CLC007","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - underground cable","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"N","No forecast",0.1,2.0000000000000004E-2,12508,"20161021PWA_04","The CFA reported a pole fire at the incident location. On arrival the crew found that a Low Voltage underground cable had faulted and showed signs of burning. Talking to the crew there was no ground fire. No third party damage or injury was reported. The crew suspect moisture ingress as the cause of the cable faulting. The crew made the site safe, replaced the cable and supply was restored."]
[null,28,"2016-10-25","13:48:00",-38.07638,142.87063000000001,32060489,"TRG002","12.7kV AC (SWER)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : HV Fuse Failure (including ‘hang-ups’ and ‘candling’)"," - fuse (any other type)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"N","No forecast",0.1,0.45999999999999996,12522,"20161027PWA_03","A customer reported that she had heard a loud bang and had seen sparks from across the road at the incident location. On arrival the crew found that a large dead pine tree had fallen onto the 12.7kV SWER conductor and eventually caused the conductor to break and fall to the ground. The barrel of the SWER HV fuse on the ISO pole burnt through and part of it fell to the ground. There was no ground fire or injuries."]
[null,29,"2016-10-27","11:35:00",-38.418202999999998,144.17032,30061324,"WPD014","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"N","No forecast",0.1,0.45999999999999996,12537,"20161108PWA_01","The fire brigade reported a pole fire at the incident location. On arrival the crew found that a 3 phase fused mains box controlling two underground services had overheated and caught fire. There was no ground fire or injuries."]
[null,30,"2016-10-30","16:50:00",-36.794114999999998,144.26542000000001,32053336,"BET007","22kV AC","Rural Short","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"N","No forecast",0.1,0.45999999999999996,12528,"20161102PWA_01","VicFire reported a tree over HV conductors ( as conductors smoking ) at the incident location. On arrival the crew found that a HV conductors had been brought down by a large tree from across the road, resulting in a small ground fire, 3m square in total. Cross arm on P15 had broken due to the impact and required replacing. There were no reported injuries or 3rd party damage. Protection operated."]
[null,31,"2016-10-30","13:35:00",-37.717533000000003,144.03339,30010307,"BAS022","12.7kV AC (SWER)","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"N","No forecast",0.1,0.45999999999999996,12527,"20161031PWA_02","A customer reported a tree was on an overhead conductor and a small grass fire has started at the incident location.  On arrival the crew found that a tree had fallen onto the 12.7 KV SWER conductor causing it to break and fall to the ground, resulting in a ground fire. The crew made the site safe and performed repairs. There was a small ground fire approximately 60 Square metres. There were no reported injuries."]
[null,32,"2016-10-31","17:29:00",-36.585008000000002,145.23661000000001,33095223,"MNA034","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"N","No forecast",0.1,2.0000000000000004E-2,12531,"20161102PWA_04","Vic Fire reported a fire on a pole at the incident location.  On arrival the crew found that a LV FOLCB had failed and caught on fire, no ground fire occurred as a result. There were no reported injuries, no third party damage. Failure of FOLCB suspected to be load related, large dairy connected. Supply arrangement on pole appears to have altered since street view photo taken ( FOLCB was previously on support cross-arm )."]
[null,33,"2016-11-02","14:18:00",-36.314933000000003,145.42074,33091042,"SHN011","66kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : Pole and cross arm failure or Pole and cross arm fire"," - insulators","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"N","No forecast",0.1,2.0000000000000004E-2,12533,"20161104PWA_02","A customer called to advise of a grass fire at the above location. A crew attended and found a fire had started at the base of a concrete 66/22kV double CCT P27 SHTS-NKA No1 66kV line. Area burnt was approx. 1m sq. Fire had self-extinguished. No CFA in attendance. No cause for the fire start could be identified but OPS advise there was a 66kV flash over and grass fire at P123 SHT-NKA No2 6kV line at the same time as this reported ground fire start."]
[null,34,"2016-11-06","05:52:00",-37.337245000000003,141.06995000000001,32130701,"HTN004","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,12553,"20161116PWA_03","From 5:52am on Sunday 5 Nov 2016, Powercor started to receive calls from customers in the Dorodong area, reporting dim lights. Crews were dispatched to the area and found a HV fuse had operated on P1 Dorodong line. Crews patrolled the area and later in the morning found a HV conductor on the ground and evidence of a cross arm fire at angle pole P66 Dorodong (LIS 721655). There were no ground fires, injuries or 3rd party property damage reported."]
[null,35,"2016-11-11","23:58:00",-36.865949999999998,143.80421999999999,32032402,"KGT004","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","Low-moderate",0.2,{"$f":"IF(OR(Q74=\"\",T74=\"\"),\"\",IF(AND(P74=\"within electric line construction area\",S74=\"No forecast\"),1,Q74*T74))","v":0.2},12601,"20161130PWA_02","From 1.22am on Friday 11 Nov 2016, Powercor started to receive calls from customers in the Lake Meran area, reporting a pole fire. Crews were dispatched to the area and found a Xarm fire on P130 Boort line (LIS 708869). Crews isolated the line and made safe. There were no ground fires, injuries or 3rd party property damage reported."]
[null,36,"2016-11-12","07:58:00",-35.521346000000001,142.98454000000001,32156207,"CTN003","12.7kV AC (SWER)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Any fire triggered by any asset failure caused by Lightning"," - pole (wood)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,2.2999999999999998,12602,"20161130PWA_03","Powercor started to receive calls from customers in the Sea Lake area, reporting a pole fire. Crews were dispatched to the area and found a lightning strike/pole fire on P32 BOIGBEAT EAST. There were no ground fires, injuries or 3rd party property damage reported."]
[null,37,"2016-11-16","11:00:00",-38.282995,144.31524999999999,33106443,"WPD022","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,12554,"20161116PWA_04","A customer reported loss of power to their residence near the incident location. On arrival the fault crew found that the FMJB mounted on the concrete pole had caught fire and burnt out at the incident location. The fire had self-extinguished. The crew replaced the FMJB. There was no ground fire and no injury as a result of this incident."]
[null,38,"2016-11-18","09:56:00",-34.183816,142.12966,33064891,"MDA033","22kV AC","Urban","Asset failures resulting in grass/vegetation fire : HV Fuse"," - fuse (any other type)","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12567,"20161122PWA_05","A customer reports grass smoking at base of a pole at the incident location. A crew attended and found a bird at the base of SW/P1 MDA Golf S/L and 2 blown HV fuses on the SW pole. One of the fuses had hung up and burnt, dropping debris to the ground starting a grass fire of approx. 1sqm at the base of the pole. CFA did not attend and the fire had self-extinguished before the crew arrived. All 3 HV fuses at P1 where removed and listed for FFU for another crew to replace a fuse unit and 3 fuses the next day. This left 2 substations at the golf club off supply overnight. Next day another crew attended and replaced a fuse unit and all 3 fuses.\n\nNo shocks, injuries or 3rd party property damage."]
[null,39,"2016-11-19","20:43:00",-36.718521000000003,144.2535,30223654,"EHK031","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets","Public lighting","single phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12606,"20161201PWA_03","CFA, reported street light lantern on fire Corner Victoria Street & High Street, Eaglehawk outside 48-48A High Street. When crew arrived onsite the fire had extinguished and CFA no longer present. The 150W HP Sodium lantern had burnt internally and required replacement. There was no ground fire, no reported property damage or reported injuries."]
[null,40,"2016-11-19","19:30:00",-36.536830000000002,145.30506,31035936,"MNA034","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in grass/vegetation fire : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12562,"20161121PWA_06","A customer called to advise that they had lost supply to their pump and a grass fire had started that they attended to extinguish. A crew attended and found a fire had started at the base of a wood pole 11 Elliott Spur at 1375 River Road TOOLAMBA.  Area burnt was approx. 10m X 8m. The cause was a burnt out blue phase connection in customers FOLCB on their underground supply. There were no reported injuries, shocks or third party damage."]
[null,41,"2016-11-19","16:23:00",-36.365513,145.29865000000001,33089756,"MNA014","22kV AC","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from animal contact with network assets"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12561,"20161121PWA_05","A customer called to advise that there was a fuse blow at the neighbours transformer and a grass fire had started that the CFA attended onsite. A crew attended and found a fire had started at the base of a concrete pole 3 Gag Spur at 420 Ardmona Road ARDMONA . A crow was found at the site of ignition.  Area burnt was approx. 15m X 10m. CFA in attendance. There were no reported injuries, shocks or third party damage."]
[null,42,"2016-11-21","18:32:00",-38.262839,144.39713,30063270,"WPD024","22kV AC","Rural Short","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Very High",1,4.5999999999999996,12569,"20161122PWA_02","customer called to report tree branch on line sparking and on fire at the incident location. Powercor crew found multiple small burnt patches on ground, self-extinguished caused by branch falling on line and small pieces falling to the ground alight (largest approx.. 10cm²).  HV may have contacted LV, LEI informed.\n No injury or third party damage."]
[null,43,"2016-11-21","17:30:00",-38.150959999999998,144.36597,32076201,"GCY012","Low voltage AC (<1kV)","Urban","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead service conductor (commercial / industrial)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","Very High",1,0.2,12570,"20161122PWA_03","VicFire called to report sparking wires caused a grass  fire at the incident location.  Powercor crew found a tree branch had fallen on a 2 wire bare service causing it to spark which ignited a small tree near the line. Fire was approx.. 1m x 1.5m. Tree was in front yard of property."]
[null,44,"2016-11-21","16:56:00",-38.132047,144.26651000000001,32084337,"GL012","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : Any fire triggered by any asset failure caused by Lightning"," - switch (disconnector/isolator)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Very High",1,4.5999999999999996,12568,"20161122PWA_01","A Powercor employee called to report a fire start at the base of our pole after noticing CFA activity at the incident location. A reclose was recorded on the feeder prior to this and may have been a lightning strike in the vicinity of the switch pole. Upon inspection the switch was black and the fire (1m x 10m) appears to have originated at or close to the switch earth. A fuse was also down on the substation 1 pole to the east but no other visible damage. No injury or third party damage."]
[null,45,"2016-11-21","16:51:00",-36.573577,143.93729999999999,32033600,"EHK024","22kV AC","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,12571,"20161122PWA_04","CFA reported a broken tree branch has fallen across the HV cables at 222 Bridgewater – Serpentine Road BRIDGEWATER and is burning. When crew arrived on site the 3/2.27 steel cable had burnt through and a small grass fire approximately 12 metres X 10 metres along the road reserve had been contained by the attending CFA.  Isolations were established and repairs made after another crew were called to bring a crossarm and hardware to replace the damaged crossarm at Pole # 1 Morse Spur after shock of the falling cable. There was no injuries or third party property damage."]
[null,46,"2016-11-21","14:30:00",-36.470165999999999,145.62112999999999,30130885,"STN011","12.7kV AC (SWER)","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from animal contact with network assets"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA","HBRA only",1,"Y","Low-moderate",0.2,0.2,12565,"20161123PWA_01","Customers reported loss of supply near the incident location. On arrival the fault crew found that an old disused crane had been left under a SWER line. \nDue to hot weather the line had sagged, a bird (pigeon) perched on top of this crane has caused a flashover between line and the old disused crane.\nThe flashover caused a small fire to be ignited at the base of the crane of approximately 1m by 1m. SWER was measured to be 5.9m above ground, the crane has been moved away from the line. There was no injury as a result of this incident."]
[null,47,"2016-11-24","15:12:00",-38.546567000000003,143.50573,32064661,"CLC006","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA","within electric line construction area",19.8,"Y","Low-moderate",0.2,3.9600000000000004,12610,"20161206PWA_01","An employee doing a line condition audit found a crossarm had caught fire and self-extinguished at the incident location some time previous to the audit. The crossarm was listed as a P1 item and changed later that evening. There was no ground fire. No third party damage or injury was reported."]
[null,48,"2016-11-24","12:00:00",-37.862848999999997,142.56469000000001,30043100,"TRG002","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,12617,"20161208PWA_02","The property owner reported a pole fire at the incident location. A crew attended and found the customers U/G CB and junction box mounted on the pole had overheated and burnt. Supply was isolated and an REC engaged to replace the customers CB. The crew replaced the junction box, damaged wiring and conduit. There was no ground fire start. No CFA attended. No shocks or injuries."]
[null,49,"2016-11-25","10:40:00",-38.255678000000003,143.63156000000001,30050973,"CLC003","22kV AC","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,12583,"20161128PWA_01","The property owner reported a blown fuse and the line on the ground at the incident location. A crew attended and found 1 phase of a Single phase HV line on the ground and 1 HV fuse at the Tee Off blown. A tree branch had fallen across the conductor and broke the conductor approx. 10m from substation P2 Gerrard S/L. The 10m length of conductor hanging from the substation pole remained alive thru back feed from the transformer. The end of the live conductor came into contact with a portion of old wire fencing causing arcing resulting in a grass fire of approx. 1m/sq. The fire had self-extinguished by the time the crew had arrived. No CFA attended. The crew isolated the Gerrard S/L at Tee pole 6 and repaired the 3/12 conductor. \n\nNo shocks, injuries or third party damage."]
[null,50,"2016-11-27","10:02:00",-36.405543000000002,145.31345999999999,33088557,"MNA021","22kV AC","Rural Short","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from animal contact with network assets"," - voltage regulator","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12584,"20161128PWA_02","VicFire reported a transformer “explosion” and ground fire at the incident location. On arrival the crew found that a bird had flashed over between a surge diverter and the HV regulator tank body, the remains of the bird was found on the foundation pad at the base of the regulator, a small ground fire resulted approximately 10M X 4M in area of grass burnt. Some minor damage to one of the HV bushings resulted, the surge diverter will also require replacement. It is unclear if material from the incinerated bird commenced the ground fire or the arc damage ejected material causing the ignition. There were no reported injuries or 3rd party damage. Protection operated ( MNA021 feeder reclosed )."]
[null,51,"2016-11-28","08:10:00",-36.738486999999999,142.20150000000001,33052548,"HSM002","22kV AC","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12585,"20161128PWA_03","Operation received system advise of a lock out of the HSM003 22kV feeder CB at the Horsham ZSS. A customer rang to advise an excavator had struck the overhead line at the above incident location. The attending crew found an excavator had struck the footpath side HV conductor. The excavator struck the O/H conductor while operating near the line. Conductor height was 5.9m over driveway. The line was isolated for repairs. There was a grass fire of approx. 1msq at the base of the excavator. No CFA attended. No shocks, injuries or third party damage.  \n\n\nNote: this is the second time in 3yrs that an excavator from this company has struck this same span of conductor. This has been referred to the connections group to speak to the company about a recoverable works job to removing this span when the company builds their new office complex on the adjoining site."]
[null,52,"2016-11-30","17:40:00",-36.976255999999999,143.89536000000001,33011872,"MRO007","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in grass/vegetation fire : Other Assets"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,12603,"20161201PWA_01","Customer reported a transformer on fire and associated ground fire at the incident location. On arrival the crew found that a LV fused isolator connection was loose and overheated, dropping molten material to the ground, a small ground fire resulted approximately 7M X 16M in area of grass burnt. Customer advised that they couldn’t get through to the CFA & extinguished the fire, they were concerned about their bore pump as it was apparent that they had partial supply. There were no reported injuries or 3rd party damage. White phase 250A HRC fuse operated."]
[null,53,"2016-12-03","09:09:00",-36.329388999999999,145.41570999999999,33096736,"SHTS-NKA2","66kV AC","Unknown","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12612,"20161206PWA_03","SCADA reported protection operations on SHTS-NKA 66KV NO.2 and SHN11 22kV feeders. Crew patrolled between pole 1 and pole 50 of the SHTS-NKA 66KV NO.2 line. On arrival at P22 the crew found that a bird (corella), had flashed over between the centre phase 22kV stand of insulator and the outer phase. (Wø-Bø). The remains of the bird were found at the base of the pole appearing to be the catalyst of the small grass fire which had extinguished itself prior to the crew attending which was approximately 1m X 1m in area of grass burnt. Some minor damage to the stand-off 5 shed centre phase insulator 22kV HV insulator resulted which will require replacement, (top shed cracked in half) due to flashover. FFU has been raised to repair the damaged insulator.\n\nThere were no reported injuries or 3rd party damage."]
[null,54,"2016-12-04","09:33:00",34.298932999999998,142.2209,33064221,"RCTS-MBN","22kV AC","Unknown","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from animal contact with network assets"," - fuse (boric acid)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","Severe",2,0.4,12613,"20161206PWA_04","Vic fire , Bird hit wires and caused small grass fire CFA on site. CFA had left prior to crew arriving. Upon arrival the crew found that a bird had flashed over between a HV dropper and the line side of a BA fuse unit, the remains of the bird was found on the ground at the base of the pole, a small ground fire resulted approximately 4m radius in area of grass burnt. Some minor damage to HV BA fuse unit was evident due to flashover and was changed as a result. The HV dropper was in good condition upon closer inspection using the EPV therefore was left in service.\n\nIt is clear that the incinerated bird commenced the ground fire at the base of the pole.\n\nThere were no reported injuries or 3rd party damage. Protection operated ( N/A )."]
[null,55,"2016-12-05","05:30:00",-37.672583000000003,143.45144999999999,33001737,"BAS021","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,12622,"20161212PWA_02","A person driving past a pole noticed the cross arm was on fire at the address below. On arrival the work crew found a cross arm had burnt off and the conductor was still alive in the air. There was no ground fire. No third party damage or injury was reported."]
[null,56,"2016-12-11","17:10:00","-36.472277,",144.37726000000001,30237533,"EHK024","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : HV Fuse"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,12625,"20161212PWA_05","Vic Fire reported a pole fire at 2024 BENDIGO-TENNYSON ROAD, KAMAROOKA.  On arrival the crew found one of the two BA fuses was candling and had caused a fire underneath the pole. No shock, No injuries, Small ground fire 10m x 100m.  Third party damage to customer canola crop."]
[null,57,"2016-12-12","16:55:00",-35.859203000000001,144.14144999999999,32035769,"CHA006","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : Other Assets"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12627,"20161213PWA_01","Vic Fire reported a pole fire at corner Leitchville-Kerang Rd and Majors Rd.  On arrival the crew found a grass fire and blackened pole.  HV bridge on centre phase had burnt out. ESV Notified. No shock, No injuries, ground fire (approx. 30m x 200m sq.m).  Third party damage to customer fence + hay bale + burnt paddock."]
[null,58,"2016-12-12","15:00:00",-36.797263000000001,144.34299999999999,30041489,"BGO013","22kV AC","Rural Short","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12623,"20161212PWA_03","Vic Fire reported car hit a pole at 767 Strathfieldsaye Rd Strathfieldsaye.  They also reported a damaged cross-arm, wires down on road and footpath, burn marks on houses and a small grass fire.  On arrival the crew found that the HV cross-arm had broken, HV conductors were dislodged and LV conductors were on the ground.  Car had driven off.  A small fire had started on the nature strip that was approx. 2m x 10m. There was a ground fire, no injuries and third-party property damage due to HVI."]
[null,59,"2016-12-12","11:00:00",-37.762805999999998,144.8339,30118234,"SSE012","Low voltage AC (<1kV)","Urban","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12626,"20161212PWA_06","The MFB reported that a truck has hit (side swiped) a pole and started a fire at the incident location. On arrival the fault crew found a truck had collided with pole LIS 21762 adjacent 20 Ayton Road (south side of road) corner Nettlefold Avenue, Sunshine North. The collision resulted in the low voltage wooden cross-arm on this pole breaking in half and the cross-arm and tee-off conductors fell onto the low voltage conductor+X106s below.\n\nContact between the low voltage conductors has caused low voltage bus fuses to operate on the pole three poles north of the incident location (6 Nettlefold Road).  \n\nOperation of the low voltage fuses caused hot debris to fall on the ground near pole LIS 26585 (6 Nettlefold Avenue) resulting in a small grass fire 2*3 meters (6m2).\n\nThe MFB were on site and the grass fire has been extinguished.\n\nThe crew  have replaced the broken low voltage cross-arm and restored the blown low voltage bus fuses.\n\nThere was no injury as a result of this incident."]
[null,60,"2016-12-18","13:30:00",-37.547361000000002,144.23272,32166522,"BMH003","12.7kV AC (SWER)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - earth / earthing","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","Low-moderate",0.2,0.2,12653,"20161223PWA_02","Mick Van Ravenstein, ATL from Ardeer Construction, rang me, as the NAO AH Ardeer, on Monday 19/12/2016 @13:06, to ask if I was aware and had been notified about a pole fire incident the previous day.\n\n\n\nI had discussed with Mick that I had not received any phone call nor an email from dispatch regarding a pole fire. Please note, on Sunday 18/12/2016 many IT systems including OMS were down.\n\n\n\nHe let me know that the crew who attended the pole fire was, Tony Esposito and he had photos and all information regarding the incident.\n\n\n\nI spoke to Tony Esposito on Tuesday 20/12/2016 @ 15:30. Tony advised that the SWER earths at P30E LIS-104332, BLAKEVILLE P30E 25kVA SWER Tx, had been unknowingly damaged at the base of the pole, which had caused a fire at the base of the pole to track upwards along the connection of the earth to the pole.  The fire was contained to the base of the pole only up to where the earths were connected, the ground was dry back from the pole but there was no ground fire, the fire was isolated to the pole only. \n\n\n\nNo protection operated, there were no reported injuries or ground fire start."]
[null,61,"2016-12-20","19:04:00",-37.732649000000002,144.82386,30110872,"SA002","Low voltage AC (<1kV)","Rural Short","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12648,"20161222PWA_01","Mr John Condon phoned in to advise of a wire down and a small grass fire at the incident location.\n\nUpon arrival the crew had found that an unknown truck had come into contact with the CATV at the intersection of Calverton Road/Driscolls Rd (southern side of No. 2 Valewood Drive, Kealba 3021) and flicked the Foxtel into the LV above which caused sparks to fall to the ground.\n\nThe resultant sparks from this caused 2 x minor grass fires and scorch marks on the nature strip approx. 1m x 1m total area, at the intersection of Calverton Road/Driscolls Rd (southern side of No. 2 Valewood Drive, Kealba 3021).\n\nLV Bus Fuses (north circuit) operated at Calverton-Hadley Pole substation.\n\nThe MFB were on site and the grass fire has been extinguished. Police were also on site.\n\nThere was no injury or shocks as a result of this incident."]
[null,62,"2016-12-20","18:43:00",-36.321038000000001,145.11249000000001,32188133,"KYM003","Low voltage AC (<1kV)","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - overhead service conductor (residential)","single phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12646,"20161221PWA_02","Customer reported that they had no supply and that the service cable was on the ground. Neighbour had extinguished a small grass fire. A high load vehicle had made contact with multiphase service mains cable from substation pole direct to house damaging the customers facia board and breaking the service mains cable. Crew attended and the Police were onsite as the service cable was across a main road. Vehicle details unknown by Police in attendance. Small grass fire, Property damage to facia board and customers mains, defect issued and left off supply."]
[null,63,"2016-12-20","14:24:00",-37.867192000000003,143.46184,32008602,"BAS021","12.7kV AC (SWER)","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any other thing forming part of or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,2.2999999999999998,12647,"20161221PWA_03","The CFA reported a machine has struck Power lines at the incident location. On arrival the crew found that a farm sprayer unit had contacted the SWER line when lowering the arms of the sprayer resulting in a strand of the conductor to break and a ground fire to occur. The crew repaired the damaged cable using a splice over the broken strand. There was a ground fire of approximately 100 metres x 50 metres in size. No protection operated. No reported shocks or injuries."]
[null,64,"2016-12-20","06:14:00",-37.753897000000002,144.80484000000001,32167390,"SSE031","22kV AC","Urban","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12650,"20161220PWA_02","Powercor fault crew attending an outage (SSE031 feeder) found a pole-top fire at the incident location. The crew isolated the faulty section and restored the feeder. No evidence of ground fire found. Protection operated as expected. There was suspected HVI however no damage was found. \n\nA person in the street advised our Operator of a fatality inside a house."]
[null,65,"2016-12-20","03:00:00",-36.572930999999997,142.35898,30077099,"HSM001","12.7kV AC (SWER)","Rural Long","Asset failures resulting in grass/vegetation fire : Any fire triggered by any asset failure caused by Lightning"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","HBRA","HBRA only",1,"Y","High",0.5,0.5,12644,"20161221PWA_01","Whilst responding to a fault, a Powercor fault crew reported that lightning had struck a HV SWER line, resulting in a transformer tank rupturing and spraying oil on the ground and on a nearby shed. The lightning strike also damaged the next pole along the line, resulting in a small grassfire of less than 1 square metre in size. There were no injuries, and the protection operated as expected.\n\n\n\nNote: This fault occurred at approx. 3am in the morning, however was not reported to the BH NAO until almost 4pm, the AH NAO was reluctant to take on the job at 4pm, so the job was held over to today, hence the lateness of the report."]
[null,66,"2016-12-22","09:33:00",-38.372993999999998,142.49272999999999,33099041,"WBL002","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets","Public lighting","single phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12655,"20161223PWA_04","VicFire reported a streetlight pole on fire at the incident location. On arrival the crew found that a streetlight lantern mounted on a steel pole and bracket, had caught fire. There was no ground fire, no reported third party damage or any injuries. The light was isolated in the UG pit for later replacement when traffic control is available."]
[null,67,"2016-12-23","21:05:00",-37.744484,144.77803,33071133,"SA004","Low voltage AC (<1kV)","Urban","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets","Other ","three phase","Started in or originated from a distribution system","LBRA","LBRA only",{"$f":"IF(P106=\"\",\"\",IF(P106=\"LBRA only\",0.2,IF(P106=\"HBRA only\",1,IF(P106=\"within electric line construction area\",19.8,IF(P106=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"Y","High",{"$f":"IF(S106=\"\",\"\",IF(S106=\"No forecast\",0.1,IF(R106=\"N\",0.1,IF(S106=\"Low-moderate\",0.2,IF(S106=\"High\",0.5,IF(S106=\"Very high\",1,IF(S106=\"Severe\",2,IF(S106=\"Extreme\",3.5,5))))))))","v":0.5},{"$f":"IF(OR(Q106=\"\",T106=\"\"),\"\",IF(AND(P106=\"within electric line construction area\",S106=\"No forecast\"),1,Q106*T106))","v":0.1},12726,"20170117PWA_05","Mr Charles reported a meter fire at the incident location and base of meter is melted. No sparking or smoking now but loss of supply. On arrival the Powercor crew found melted meter burnt out switch board and meter panel. The fault crew isolated supply, removed the damaged meter panel and issued a defect notice for the customer to engage a REC to undertake the necessary repairs. There was no ground fire. There were no reported injuries or third party property damages."]
[null,68,"2016-12-24","17:26:00",-36.256283000000003,144.72663,31026711,"ECA012","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : Any fire triggered by any asset failure caused by Lightning"," - transformer (pole mounted)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA","HBRA only",1,"Y","High",0.5,0.5,12659,"20161229PWA_02","VicFire reported a pole fire  at the incident location. On arrival the crew found that a transformer has failed rupturing the tank and the ejected oil had ignited, resulting in fire damage to the pole and commencing a ground fire. It is believed that the transformer had suffered damage due to lightning earlier that morning when the spur was affected by an lightning related outage that the crew attended and replaced a section fuse at P1 Quinn spur.\n\n\n\nA ground fire of approximately 50m x 60m resulted, some fencing was slightly burnt as the fire passed through it.\n\n\n\nThere were no reported injuries."]
[null,69,"2016-12-24","15:11:00",-36.666375000000002,143.91492,32039847,"BET001","22kV AC","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,2.2999999999999998,12660,"20161229PWA_03","VicFire reported wire down and ground fire at the incident location. On arrival the crew found that large tree branch had come away from a tree outside the clearance space and fallen onto 1 phase of the 3 phase 22kV line, breaking the conductor and commencing a ground fire. A ground fire of approximately 120Ha resulted, an estimated 300>600M of fencing was burnt to varying degrees and 2 farm sheds also damaged by the fire, at least 12 CFA tankers attended and clean up was still occurring at 8pm as the fire had got into vegetated areas along the river side. There were no reported injuries. Protection operated, 1 fuse at SW/P 10032 operated, and Marong ACR on the BET001 feeder tripped to lockout for the incident."]
[null,70,"2016-12-24","11:59:00",-35.812376,144.21445,32038108,"CHA003","22kV AC","Rural Short","Asset failures resulting in grass/vegetation fire : Any fire triggered by any asset failure caused by Lightning"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA","LBRA only",0.2,"Y","Very High",1,0.2,12658,"20161229PWA_01","Powercor fault crew reported ground fire(s) associated with lightning strike to 22kV overhead conductors at the incident location. On arrival the crew found that lightning had struck overhead conductors between SW/P 46534 & SW/P 10220, both air-break switches flashed over to the switch frame, small ground fires resulted at the base of both these structures, approximately 4M X 4M in area of grass burnt in total.\n\n\n\nThere were no reported injuries or 3rd party damage. Protection operated ( CHA3 & CHA6 feeder CB’s reclosed )."]
[null,71,"2016-12-24","11:59:00",-35.812210999999998,144.21297000000001,30028343,"CHA006","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : Any fire triggered by any asset failure caused by Lightning"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA","LBRA only",0.2,"Y","Very High",1,0.2,12657,"20161229PWA_01","Powercor fault crew reported ground fire(s) associated with lightning strike to 22kV overhead conductors at the incident location. On arrival the crew found that lightning had struck overhead conductors between SW/P 46534 & SW/P 10220, both air-break switches flashed over to the switch frame, small ground fires resulted at the base of both these structures, approximately 4M X 4M in area of grass burnt in total. There were no reported injuries or 3rd party damage. Protection operated ( CHA3 & CHA6 feeder CB’s reclosed )."]
[null,72,"2016-12-25","15:46:00",-38.165894999999999,144.31354999999999,32083825,"WPD013","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in grass/vegetation fire : Other Assets"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Very High",1,0.2,12665,"20161229PWA_08","VicFire advised of a wire down with Arcing and sparking.  Attending crew found service cable had parted in span and supply end had been brushing against cable guard on pole, and had ignited a small ground fire. There was no injuries or third property damage. Fire area 1 sqm. Crew replaced service."]
[null,73,"2016-12-25","12:50:00",-37.59205,143.8656,32010016,"BAS013","22kV AC","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Very High",1,4.5999999999999996,12663,"20161229PWA_06","A Powercor employee reported a pole fire at the incident location.  On arrival the crew found that a three phase 22kV wooden cross arm had previously burnt through at a cross arm strap position and the cross arm was now broken. The pole is located in the road reserve and there was no ground fire. There were no injuries."]
[null,74,"2016-12-28","13:15:00",-37.563884000000002,143.83606,30014532,"BAS014","22kV AC","Urban","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","Very High",1,0.2,12666,"20161229PWA_09","VicFire reported a pole fire at the incident location.  On arrival the crew found that a tree branch had broken in the windy weather conditions and had fallen across high voltage and low voltage conductors which resulted in the branch burning through. There was no ground fire. There were no injuries."]
[null,75,"2016-12-28","08:35:00",-35.166426000000001,141.74145999999999,32139791,"OYN001","22kV AC","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA","HBRA only",1,"Y","Very High",1,1,12661,"20161229PWA_04","VicFire reported wire down and ground fire at the incident location. On arrival the crew found that a tree had fallen over in high winds from outside the clearance space onto 1 phase of the 3 phase 22kV line, breaking the insulator, dislodging the conductor which fell to the ground and commenced a ground fire. A ground fire of approximately 150M x 15M in area, roadside grass burnt. There were no reported injuries or 3rd party damage. Protection operated, Underbool P428 ACR tripped to lockout for the incident."]
[null,76,"2016-12-28","06:42:00",-36.402177000000002,141.64222000000001,32122737,"NHL015","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","Very High",1,1,12664,"20161229PWA_07","VicFire reported a pole fire at the incident location.  On arrival the crew found that a three phase 22kV wooden cross arm had burnt through at the king bolt position and the cross arm with brown fog type insulators was broken in half. The pole is located in a fallow paddock and there was no ground fire. There were no injuries"]
[null,77,"2016-12-29","13:57:00",": -38.334039",144.32451,30292613,"WPD024","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets","Other ","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12704,"20170111PWA_04","customer reported a meter board fire at the incident location. Upon arrival, the Powercor crew found that an overheated meterboard fuse caught fire and melted. \nThere were no injuries or ground fire."]
[null,78,"2016-12-29","13:11:00",-36.514657,145.20384999999999,32191788,"MNA021","22kV AC","Rural Short","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12673,"20161230PWA_05","The customer at the incident location reported that a tree had fallen over the overhead line. It had started a small grass fire which self-extinguished. On arrival the crew found that at the incident location a tree had fallen across the conductors near P1 Dickenson Spur and bought them close to ground. A small ground fire was observed (Less than 1sq metre). No injury and only minor third party damage was reported."]
[null,79,"2016-12-30","17:43:00",38.211056999999997,143.03974400000001,30042574,"CDN006","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in grass/vegetation fire : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,12675,"20170103PWA_01","VicFire reported a junction box on building at dairy on fire at the incident location. On arrival the crew found a customer switchboard had caught fire above the meterboard and a ground fire at the pole servicing the property via an underground cable. The fuse at the pole had overheated and fallen from the box. The pole was located in the road reserve and there were scorch marks on the fence posts but no structural damage. Area of fire approx. 20m x 7m (140m²)."]
[null,80,"2017-01-01","17:00:00",-38.290317999999999,144.30957599999999,33042148,"WPD022","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in grass/vegetation fire : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,12676,"20170103PWA_02","Customer reported all supply fail at the incident location. On arrival the crew found an overheated fuse had melted through the box and fallen to the ground burning a small patch of grass. No injury or third party property damage."]
[null,81,"2017-01-02","07:14:00",-37.539458000000003,143.82660999999999,30014161,"BAN001","22kV AC","Urban","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12677,"20170103PWA_03","A call was received from the CFA that a pole was on fire outside 1253 Howitt Street Wendouree. On arrival the crew found that a Pole Fire had occurred on Lake Nth Howitt Pole 20. Leakage on the HV switch pole had caused damage to the pole where the LV X-arm attaches and burnt through the LV X-arm. The HV switch mounted on the pole was not earthed and it is assumed that leakage current from the HV tracked to the LV neutral conductor and then to earth. The crew isolated supply to the area and the pole and x-arm was replaced. \n\nThe was no ground fire, third party damage or injury. Police and FCA attended the scene."]
[null,82,"2017-01-04","21:46:00",-37.688276999999999,144.43618000000001,33075192,"BMH004","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets","Public lighting","single phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12715,"20170112PWA_06","A passer-by reported that a street light lantern (150W HPS on an outreach bracket) at pole LIS-105857 (12.5m concrete pole) had caught fire resulting in the lantern cover melting and coming down to ground through the tree beneath the pole. The fault crew did not advise of the possible cause of the fire/damage to the lantern. The fault crew isolated supply to the light, and repairs will be undertaken by Powercor’s lighting contractor as a fault follow up. The MFB were in attendance, however they advised that any fire that may have started self-extinguished prior to their arrival on site.  There was no ground fire, injuries or third party damage to report."]
[null,83,"2017-01-05","17:00:00",-36.089916000000002,144.66333,33104974,"ECA010","22kV AC","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : HV Fuse Failure (including ‘hang-ups’ and ‘candling’)"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","Low-moderate",0.2,0.2,12714,"20170112PWA_05","Nearby resident reported that pole sparking and flaming. CFA was leaving as line crew arrived.  Upon arrival crew found that an EDO fuse had candled on sub pole (LIS-924576) P1 DYBALL SPURLINE.  There had been high levels of lightning on Christmas eve. There was no ground fire, injuries or third party property damage"]
[null,84,"2017-01-05","13:19:00",-36.391674999999999,142.39150000000001,32106745,"HSM005","22kV AC","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA","HBRA only",1,"Y","High",0.5,0.5,12685,"20170106PWA_02","Customer reports of “no supply” were received beyond the incident location.  On arrival the crew found that a farmer driving a tractor and towing a grain chaser bin with an auger which was not stowed had contacted an overhead high voltage line. There was a ground fire in private property covering an area of approximately 150 hectares. There is a burn mark on the auger and no other apparent damage to the grain chaser bin. There were no reported injuries."]
[null,85,"2017-01-05","12:02:00",-35.971530000000001,145.62296000000001,33085558,"CME015","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in grass/vegetation fire : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12684,"20170106PWA_01","The CFA reported a pole had caused a grass fire at the incident location. On arrival the crew found that at the incident location a pole box had faulted resulting in approximately 4 acres of grassland being burnt. No injury and or other third party damage was reported. The pole box was replaced and supply returned to normal. The crew were concerned that this fuse assembly had already been replaced at this location and load may have been a factor in it faulting."]
[null,86,"2017-01-07","19:27:00",-37.674726,144.57017999999999,30103772,"MLN014","Low voltage AC (<1kV)","Urban","Asset failures resulting in grass/vegetation fire : Other Assets"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Very High",1,0.2,12688,"20170109PWA_02","Angelique from Vic fire reported sparks fell from a pole at the incident location and started a small fire on nature strip, the fire extinguished by itself and she advised that Vic fire was enroute. Few customers reported no power on their properties. A Powercor crew attended and discovered that at pole LIS 110961 a LV conductor line bridge had burnt at a substation LV bus fuse termination. This caused the sparks and probably hot debris that fell to the ground starting a small ground fire on  a couple of spots on the nature strip (approx.1m square), the fire  extinguished by itself. The crew replaced the LV bridge conductor between the LV bus and the fuse termination. There were no reported injuries or third party damage. LV Bus Fuses operated (COBURNS RD P22 Pole substation)."]
[null,87,"2017-01-07","12:39:00",-38.027079000000001,144.42286999999999,33040304,"FNS012","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in grass/vegetation fire : Other Assets"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Very High",1,0.2,12696,"20170110PWA_01","The customer at the incident location reported that a conductor had faulted and fallen to ground. On arrival the crew found at the incident location, an LV conductor had faulted and showed signs of burning in small patches on the ground. No injury and no third party damage was reported. The Cause appears to be an overheated IPC connector at the ABC t/off"]
[null,88,"2017-01-07","12:32:00",-36.324460999999999,144.97791000000001,33092311,"KYM-ECA1","66kV AC","Unknown","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from animal contact with network assets"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12692,"20170109PWA_06","Control room noted a reclose on KYM-ECA No..1 66kV line. Control Room contacted Chris Tobias on call ZSO to perform patrol of KYM-ECA 1 66kV line. Chris advised that there had been a centre phase to earth flashover the cause of which seemed to be a bird (crow) as there were burnt feathers at the base of the pole.\nCFA had attended. The area affected was approximately 1100m² of burnt grass reserve. There were no reported injuries."]
[null,89,"2017-01-10","18:45:00",-36.755971000000002,144.26065,33021007,"BET002","22kV AC","Rural Short","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - dropper / bridge","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12716,"20170116PWA_01","VICFIRE reported a grassfire at the incident location.  Dispatch contacted NAO at 17:41hrs. Upon arrival the crew noted the CFA leaving the scene after extinguishing a small grass fire which burnt an area of approximately 150m² behind Clark Rubber and Spotlight in Ironbark. The area was both private property and road reserve. Police were also in attendance. Crew noted splash marks across one phase, D and dropper which may have resulted in a phase to earth fault on the line.  FFU has been arranged by crew to replace damaged dropper. A suspected object being thrown over 22kV overhead conductors at the incident location was the cause of the fire. There were no reported injuries or 3rd party damage."]
[null,90,"2017-01-13","14:57:00",-36.311059,143.97399999999999,33017867,"CHA006","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in grass/vegetation fire : Other Assets"," - overhead service conductor (other)","single phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","High",0.5,0.5,12717,"20170116PWA_02","Customer reported cables clashing and a small grass fire started at 6223 Loddon Valley Highway BEARS LAGOON. Crew attended and found small grass fire of approximately 10m X 5m was extinguished. Grey PVC Service cable leads insulation had failed had shorted out causing grass fire.  Crew replaced leads and conducted testing and restored supply. No injuries or property damage reported."]
[null,91,"2017-01-15","10:56:00",-38.263652999999998,143.55610999999999,30054319,"CLC003","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in grass/vegetation fire : Other Assets"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,12722,"20170117PWA_02","A farmer reported that a small grassfire had started on his property. He stated that a nearby pole had been sparking, smoking and glowing orange. The farmer believed this pole was the likely cause of the fire. A crew was dispatched to investigate the incident. The attending crew found evidence of a small grass fire totalling approximately 2m² which had been extinguished by the farmer. An inspection of the transformer pole 3 (LIS-1605) identified a hot connection on a LV isolator. The line worker suggested that this may have caused the sparks and possible hot debris that fell to the ground. The customer’s supply was isolated and the site made safe until appropriate repairs were later completed. There was no third party damage or injuries reported."]
[null,92,"2017-01-15","07:29:00",-37.953527000000001,144.09349,31012957,"GL015","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : Other Assets"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,12721,"20170117PWA_01","System Controller reported that Lethbridge P179 ACR had operated with a nearby grassfire being attended to by CFA shortly after (identified on Vic Emergency website). A crew and operator was dispatched to investigate the cause. Attending crew found steel conductor had broken between P7 (LIS-45724) and P8 (LIS-45726) resulting in a small ground fire. The fire was approximately 10m² on road reserve. There was no third party damage or injuries reported."]
[null,93,"2017-01-16","21:14:00",-38.074241999999998,144.39519000000001,30073835,"FNS032","22kV AC","Rural Short","Asset failures resulting in grass/vegetation fire : Other Assets"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","High",0.5,0.5,12727,"20170118PWA_01","Attending crew found centre phase 19/3.25 AAC HV conductor had hit the ground between P52 (LIS-60484) and P53 (LIS- 44188), conductor had broken off at strain termination fitting. The broken termination was on the load side which meant the conductor on the ground was fed through the windings of the down-stream transformer/s, causing small spot fires/burns to the grass. The CFA and police were onsite. The burns total approximately 30m long and 100mm wide. After a closer look by the crew, it was identified by the crew that the PG clamp had become over heated, causing the conductor to melt and break. The site was made safe and appropriate repairs were made. There was no third party damage or injuries reported."]
[null,94,"2017-01-16","13:22:00",-37.616444999999999,143.83525,30001216,"BAS022","Low voltage AC (<1kV)","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - overhead service conductor (residential)","single phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,2.2999999999999998,12723,"20170117PWA_03","Vic fire reported a grass fire at the base of a pole at the incident location. On arrival the crew found that an unknown vehicle had contacted the LV overhead service, causing it to scrape on a metal saddle and drop debris to the ground, resulting in a small grassfire of approx. 10m x 20m = 200m2 on the road reserve. There was no reported third party damage or any injuries. After restoration the service measured 7.0m above the road."]
[null,95,"2017-01-16","07:48:00",-36.974733999999998,143.95958999999999,33014297,"BETS-MRO","66kV AC","Unknown","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from animal contact with network assets"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Very High",1,4.5999999999999996,12720,"20170116PWA_06","CFA reported a pole fire at the incident location.  Upon arrival the crew found that a bird flashover on 66kV line and fell on to the ground resulting approx. 500 Sqm ground fire.  The protection operated (line auto reclosed). There were no reported injuries or property damage."]
[null,96,"2017-01-19","23:07:00",-38.336399,141.51643000000001,32134228,"PLD006","12.7kV AC (SWER)","Rural Short","Asset failures resulting in grass/vegetation fire : Any fire triggered by any asset failure caused by Lightning"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","HBRA","HBRA only",1,"Y","High",0.5,0.5,12740,"20170123PWA_03","Customers reported a loss of supply and a wire down following a lightning strike at the incident location. A crew attended that night and found the SWER 3/2.75SC had broken and was on the ground between P8 and P10 Logan S/L. The HV fuse at Logan P1 had blown. The line was left off supply until the following morning. In daylight hours the crew found P9 had been struck by lightning. There was also a 2m/sq. patch of grass burnt at the base of P9. A burnt area of approx. 30m in length occurred between P8A and P9 where the SWER conductor had broken and fallen to ground. CFA attended and extinguished the fire. An insulator was replaced at P8 and P9 was replaced. At P10, the pole mounted TX had failed, dropping oil at the base of the pole. There was no run off of oil from site. The TX was replaced. The Environmental group to arrange a contractor to clean up oil spill from site. No shocks, injuries or third party damage. NOTE: Fire start and oil leak reported by crew directly to A/H NAO on 20.01.2017. A/H NAO passed details on to B/H NAO 20.01.2017 after returning to work from being on stand down."]
[null,97,"2017-01-19","22:21:00",-38.251224999999998,144.24817999999999,32079759,"WPD014","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in grass/vegetation fire : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,2.2999999999999998,12741,"20170123PWA_04","A customer reported a grass fire at the base of a pole at the incident location. On arrival the crew found that an LV fuse box overheated, causing it to drop debris to the ground, resulting in a small grassfire of approx. 15m x 3m = 45m2 on the road reserve and part private property. There was no reported third party damage or any injuries."]
[null,98,"2017-01-19","17:34:00","• -36.403547",142.55701999999999,32109005,"HSM005","12.7kV AC (SWER)","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any other thing forming part of or coming into contact with a distribution system","HBRA","HBRA only",1,"Y","High",0.5,0.5,12735,"20170120PWA_01","A customer reported that a farm worker on his property had driven a tipper truck into overhead power lines and bought them down. On arrival the crew found that a tip truck had contacted the SWER conductor near Nullan-Owen Pole 18 and the SWER conductor between Pole 14 and Pole 20 Nullan-Owen Spur had been pulled down. The SWER ACR protecting the line operated for the fault. The truck sustained damage to its tyres as a result of the contact. A ground fire started as a result of the contact. Approx. 5-6 hectares of wheat stubble was burnt. CFA attended and extinguished the fire. There was no other damage, no injury and no shock. The line was isolated and the conductor was repaired."]
[null,99,"2017-01-19","05:34:00",-37.510759999999998,143.94556,30016329,"BAN008","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,{"$f":"IF(OR(Q138=\"\",T138=\"\"),\"\",IF(AND(P138=\"within electric line construction area\",S138=\"No forecast\"),1,Q138*T138))","v":2.2999999999999998},12770,"20170131PWA_03","A customer reported no supply at the incident location. On arrival the crew found that an LV FOLCB overheated and caught fire on the substation pole out front of this address. There was no ground fire, no reported third party damage or any injuries.\n\n\n\nNote: As NAO I was informed of this incident after restoration, hence the lack of some information."]
[null,100,"2017-01-21","02:35:00",-38.372408999999998,141.58595,30240396,"PLD006","22kV AC","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : HV Fuse Failure (including ‘hang-ups’ and ‘candling’)"," - fuse (any other type)","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","Low-moderate",0.2,0.2,12771,"20170131PWA_04","Fire Comms reported a pole fire at the incident location. On arrival the crew found that a HV fuse barrel had failed to operate correctly and had candled. There was no ground fire, no reported third party damage or any injuries."]
[null,101,"2017-01-22","21:25:00",-36.460121999999998,145.40816000000001,32191546,"STN021","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12778,"20170201PWA_07","Customer reported a fire on a pole at the incident location. On arrival the crew found that a LV FSD had failed due to suspected poor connection and caught on fire, molten plastic fell to the ground but no ground fire resulted. \n\n\n\nThere were no reported injuries, no third party damage."]
[null,102,"2017-01-22","01:41:00",-38.398460999999998,143.85293999999999,32065952,"WIN011","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : HV Fuse Failure (including ‘hang-ups’ and ‘candling’)"," - fuse (any other type)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,2.2999999999999998,12776,"20170201PWA_05","Fire Comms reported a pole fire at the incident location. On arrival the crew found that a HV fuse barrel had failed to operate correctly and had candled. There was no ground fire, no reported third party damage or any injuries."]
[null,103,"2017-01-23","20:20:00",-36.747539000000003,144.25629000000001,30019838,"BET001","Low voltage AC (<1kV)","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead service conductor (residential)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","Very High",1,0.2,12755,"20170125PWA_03","Customer reported a tree had brought down an LV service and had commenced a ground fire at the incident location. On arrival the crew found that a LV neutral screened service cable was brought down by a customer tree, resulting in the service breaking and igniting a small ground fire, 0.3m square in total burnt. The service remained alive on the ground until the Powercor fault crew arrived & isolated it. There were no reported injuries, no 3rd party damage, no protection operated. Local SES ( per Craig Guymer, PAL employee ) removed a branch from the same service some 2 weeks earlier, customer was previously advised to cut their tree as it is in poor health."]
[null,104,"2017-01-23","17:50:00",-37.879311000000001,144.67590999999999,33071396,"WBE021","Low voltage AC (<1kV)","Urban","Asset failures resulting in grass/vegetation fire : Other Assets"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12751,"20170124PWA_04","The MFB rang and advised they had extinguished a ground fire under our assets at the above address; also, there did not appear to be anything wrong with our assets.  A neighbour subsequently rang to advise their security camera detected something “dripping” from our assets which caused the fire. On arrival fault crews found a low voltage copper to aluminium dee on the white phase had failed resulting in the ground fire and third party damage to a small bush.   There was no loss of supply.   No protection operated. There was no injury as a result of this incident."]
[null,105,"2017-01-23","15:22:00",-38.147463999999999,144.60444000000001,30065422,"DDL021","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in grass/vegetation fire : Other Assets"," - overhead service conductor (other)","single phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","High",0.5,0.5,12786,"20170127PWA_03","CFA fire investigator requested assistance to determine cause of grass fire. No fault / outage  reports had been received for a small grass fire that had occurred several days previously.  Attending crew lowered service cable to private pole to assist fire investigation. Crew identified overheated connection in customers API box on private pole and remnants of cable tie where CFA had identified the location of grass fire ignition. Crew replaced service, reconnected and restored supply.\nThere was no injuries or third property damage."]
[null,106,"2017-01-23","14:55:00",-37.679969999999997,144.37969000000001,30102859,"BMH003","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : Pole and cross arm failure or Pole and cross arm fire"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","High",0.5,0.5,12795,"20170207PWA_01","Pole Fire - crossarm broken resulting in 40 SQ m ground fire. Details unknown - NAO not notified"]
[null,107,"2017-01-23","13:25:00",-37.653132999999997,144.31496000000001,30116684,"BMH003","12.7kV AC (SWER)","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - pole (wood)","single wire earth return (SWER)","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA","HBRA only",1,"Y","High",0.5,0.5,12754,"20170125PWA_02","CFA reported a pole fire at the above location. A crew attended and found both the HV earths on the wooden SWER S/S pole had been removed. The resulting current leakage cause a pole fire. The embers from the pole fire started a grass fire at the base of the pole. CFA attended and extinguished a fire of approx. 100m x 50m in private paddock and road reserve. After the fire was extinguished, the crew replaced the missing HV earths and restored supply. The crew listed a FFU to have the pole inspected. Police have been notified and a safety link report submitted. \n\nNo shocks, injuries or third party damage."]
[null,108,"2017-01-25","18:44:00",-37.940925,144.09581,30249584,"GL015","22kV AC","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from animal contact with network assets"," - overhead conductor (bare; steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,2.2999999999999998,12783,"20170127PWA_01","Powercor received of a wire down  and possible ground fire.  On arrival the crew found both phases of the HV overhead line  had broken and fallen to ground. A grass fire of some 150 x 300m occurred  on roadside and private farm land. No fencing or other 3rd party property damage was reported damaged. Initially the crews were unsure as to the cause for the broken conductor. After the fire was extinguished, further investigation found evidence of a swan carcass in the area. This was attributed as being the cause of the initial outage and damage to the HV conductors.\n\n\n\nThere was no injuries or other third party property damage reported."]
[null,109,"2017-01-26","17:34:00",-36.755971000000002,144.26065,33021007,"BET002","22kV AC","Rural Short","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from animal contact with network assets"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12785,"20170116PWA_01","CFA reported a grass fire caused by Powercor assets at the incident location. Fault crew had just attended bird flashover @ Wood street when this report was received, after investigation crew found evidence of arcing on a PG clamp at P46 Happy Valley believed to have a high impedance connection which arced when it was subjected to fault current associated with the wood street event, this location being on the same feeder between the terminal station and the fault location.\n\n\n\nIt is believed molten material from the PG fell to the ground igniting an area of grass at the base of the pole, approximately 50M square was burnt.\n\n\n\nThere were no reported injuries, no 3rd party damage, BET002 feeder successfully reclosed."]
[null,110,"2017-01-26","17:16:00",-36.739807999999996,144.26650000000001,30031270,"BET002","22kV AC","Rural Short","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from animal contact with network assets"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12784,"20170127PWA_02","CFA reported a grass fire caused by Powercor assets at the incident location. On arrival the crew found that a bird had  made contact with the surge diverter on HV cable head structure. The bird apparently fell to the ground and ignited a small area of grass at the base of the pole, approximately 1M square was burnt. The resulting fault current appears to have ruptured a connection in Susan street Ironbark leading to a second fire of some 50 sq. metres. There were no reported injuries or 3rd party damage."]
[null,111,"2017-01-26","10:55:00",-34.779772999999999,142.6405,32141451,"WMN013","22kV AC","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","High",0.5,0.5,12787,"20170202PWA_02","Customer reported a low wire at the incident location. On arrival the crew found that a wood cross-arm had burnt through at the insulator pin causing the conductor to come adrift and hang approximately 4.0M above ground at the lowest point.\n\n\n\nThere was no ground fire, no reported injuries, no 3rd party damage, no protection operated."]
[null,112,"2017-01-27","22:39:00",-35.484186000000001,143.66103000000001,31021765,"SHL005","22kV AC","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from animal contact with network assets"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12762,"20170130PWA_02","CFA reported a grass fire caused by Powercor assets at the incident location. On arrival the crew found that a swan had struck HV 3 phase steel conductors between pole 21 & pole 22 of the Tresco spur line, the swan fell to the ground and ignited an area of grass, approximately 50M x 40M was burnt.\n\n\n\nThere were no reported injuries, no 3rd party damage, 1 x 40A fuse operated @ Tresco P2."]
[null,113,"2017-01-27","14:02:00",-36.820366,144.24413000000001,30235097,"BET004","22kV AC","Rural Short","Any other Fire Start : Any additional fires, caused by any asset failure, not reported to the ESV and required to be reported by the f-factor Order"," - pole (wood)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,12765,"20170130PWA_04","A Bobcat operator reported that his machine has hit a pole and smoke coming from the pole at the incident location. Upon arrival, the Powercor crew found that the Bobcat made contact with CHP and the impact cause to damage the steel cable protection, UG cable and fire damage to the pole. The protection operated. There were no injuries or ground fire. The protection operated."]
[null,114,"2017-01-27","06:27:00",-36.507891000000001,145.31061,33095056,"MNA034","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12798,"20170210PWA_01","CFA reported a pole fire at the above location. A crew attended and found a LV U/G pole box had overheated and melted. Crew advise they had found a birds nest in the box. CFA attended. There was no ground fire start. Crew isolated supply and replaced LV U/G pole box. No shocks, injuries, ground fire start or third party damage."]
[null,115,"2017-01-28","14:35:00",-37.67454,143.52520000000001,33005605,"BAS021","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : HV Fuse"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,2.2999999999999998,12767,"20170130PWA_05","VicFire reported a fire at the incident location.  On arrival the crew found that an EDO fuse had operated, however the barrel of the EDO fuse stayed in position without dropping down.  The barrel then caught fire resulting in a ground fire (approx. 50 square metres) on the road reserve an private property. There was also minor damage caused to fencing and a private motor car parked on the property. Tere were no injuries."]
[null,116,"2017-01-29","11:57:00",-38.269089000000001,141.67384000000001,30148494,"PLD001","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : Other Assets"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","Very High",1,1,12763,"20170130PWA_03","At 11:57am the PLD001, TYRENDARRA P493R ACR tripped to lockout, interrupting supply to 521 accounts. Shortly after, Powercor received a call from Vic Fire advising of a fire at the base of a pole in Snapper Point Rd. When LSA crews arrived they found a failed conductor (3/12 steel) at HVCHP P6, Snapper Point Rd and CFA crews in attendance. The fire burnt an area of approx. 100m x 10m along the road reserve and entered into an adjoining Abalone Farm – causing minor damage to a shade cloth structure and possibly perimeter fencing before being extinguished by the CFA. Attending linesman Ben Cumming advised it appeared the conductor had failed due to corrosion. The incident location is within 200m of the coastline. No injuries were reported."]
[null,117,"2017-01-31","13:48:00",-36.333109999999998,141.64399,30077836,"NHL016","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in grass/vegetation fire : Other Assets"," - underground service cable (residential)","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12772,"20170201PWA_02","Vic Fire reported a service down and a ground fire at the incident location. On arrival the crew found that an LV neutral screen service had broken away from the roller at the POA, falling to the ground alive. The sparking service ignited some straw mulch in a garden bed resulting in a ground fire of approx. 10m x 2m = 20m2 on private property. There was no other reported third party damage or any injuries."]
[null,118,"2017-02-03","20:08:00",-37.303924000000002,142.76679999999999,32090686,"ART033","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : Other Assets"," - underground service cable (residential)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,2.2999999999999998,12791,"20170201PWA_02","The CFA reported a pole fire at the incident location. On arrival the crew found that the HV dropper connected to the HV bushing had failed which caused arching at the joint resulting with sparks falling to the ground causing a small ground fire. The crew put parallels in place to isolate the faulty transformer and have marked the transformer to be replaced. There was a ground fire of approximately 15 metres x 5 metres in size. No protection operated. No reported shocks or injuries."]
[null,119,"2017-02-04","11:13:00",-36.532710000000002,144.66537,33079146,"KYM001","12.7kV AC (SWER)","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any other thing forming part of or coming into contact with a distribution system","HBRA","HBRA only",1,"Y","Very High",1,1,12794,"20170206PWA_06","Susan Jordan VIC Fire reported pole down Nhill Road near the corner of McKenzies Road RUNNYMEDE. Crew attended and speaking with attending Police were informed that a local farming contractor was shifting large hay bales and made contact with the HV conductor between pole # 1 Nhill Spur and pole # 2 Nhill Spur causing the cable to fail. As result of the shock load tee off pole # 14 Runnymede Spur failed at ground level [limited life pole]. A stubble fire started and burnt an estimated 10 acres [150m wide by 550-600 metres long]. Tee off pole # 14 Runnymede required replacement and approximately 250 metres of cable replaced from pole # 1 Nhill Spur. Ground fire attended by CFA. No property damage reported no shock or personal injury reported."]
[null,120,"2017-02-05","11:40:00",-37.794519000000001,144.82506000000001,32178417,"SSE014","Low voltage AC (<1kV)","Urban","Asset failures resulting in grass/vegetation fire : Other Assets"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12789,"20170206PWA_01","Ms Jillian Powell reported a service down and a ground fire at the incident location. On arrival the crew found the service cable had broken at he house end roller clamp,  falling to the ground alive. The sparking service ignited some grass area in the garden resulting in a ground fire of approx. 1m x 1m on private property. There was no other reported third party damage or any injuries. Crew replaced service cable."]
[null,121,"2017-02-06","07:14:00",-35.520510999999999,143.00721999999999,32156368,"CTN003","12.7kV AC (SWER)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,12972,"20170405PWA_01","Burnt pole top boigbeat east pole 39 recut poletop and new insulator fitted."]
[null,122,"2017-02-11","10:02:00",-38.532611000000003,142.774687,30136052,"WBL012","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in grass/vegetation fire : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","High",0.5,0.5,12800,"20170213PWA_01","Customer reported small ground fire at the incident location. On arrival the crew found a fuse box had caught fire and melted which started a ground fire burning a small patch of grass in road reserve. Extinguished by customer (volunteer firefighter).  Area of fire approx. 4m². There was no injuries or third party property damage."]
[null,123,"2017-02-16","19:59:00",-37.576047000000003,144.18446,30104525,"BAN011","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : HV Fuse Failure (including ‘hang-ups’ and ‘candling’)"," - fuse (EDO fuse)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,2.2999999999999998,12844,"20170228PWA_01","CFA reported a pole fire at the above address. A crew attended and found that a possum had bridged out between the top of an EDO fuse unit and the steel Xarm on the pole. The resulting current flow caused the pole to burn at the Xarm king bolt. The crew removed the possum and isolated the EDO fuses. The CFA were in attendance and extinguished the pole fire. The pole was replaced and supply restored. There were no shocks, injuries, ground fire start or third party damage."]
[null,124,"2017-02-16","01:47:00",-37.932187999999996,142.4948,30042625,"TRG002","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,2.2999999999999998,12973,"20170405PWA_02","Pole fire reported at Pole 261 Penshurst spur Line. Crossarm burnt through at insulator."]
[null,125,"2017-02-17","15:24:00",37.82732,144.77876000000001,33074084,"LVN024","22kV AC","Urban","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12827,"20170221PWA_01","During feeder patrol following a truck collision reported in incident  12826 a grass fire occurred  at the base of a hv switch at the incident location. The contacts of the switch appear to be welded shut. There were no injuries reported."]
[null,126,"2017-02-17","15:24:00",-37.82732,144.77876000000001,33074084,"LVN024","22kV AC","Urban","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - switch (disconnector/isolator)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12826,"20170221PWA_02","The MFB reported that a truck had hit wires at corner of Australis drive and Robinsons road and started a fire at the incident location. Truck and grass on fire. MFB was on site. On arrival the fault crew found a truck had collided with a 66KV/22KV INT pole LIS 839192 at 354a Robinsons Road (west side of road) near intersection with Australis drive, Derrimut. The wood pole broke nearly at ground level and fell on the ground causing a grass fire approximately 200m x 50m. Crossarm assemblies on both adjacent poles were damaged. The crew said that when they arrive MFB and police were on site. The fire brigade had extinguished the fire and that the truck was being towed away. The crew said that the 66KVO/H line was not in service at that time. Protection operated,  LVN24 22kv feeder CB opened to lockout."]
[null,127,"2017-02-22","13:04:00",-37.848705000000002,141.83669,32127314,"HTN002","12.7kV AC (SWER)","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Severe",2,9.1999999999999993,12832,"20170223PWA_03","VicFire reported a wire down and fire start at the incident location. The Portland Rd P2 SWER ACR tripped to lock out at the same time. A crew attended and found a pine tree adjacent to P16 Portland Rd S/L had fallen and contacted the line. The tie at P16 broke and the conductor came to ground. The conductor did not break. This resulted in a ground fire start of approx. 10m x 150m in the plantation easement. No plantation trees were damaged. The CFA attended and extinguished the fire. The crew replaced the PTA and tie on P16 and retied the conductor at P15 Portland S/L.\n\nThere were no shocks, injuries or third party damage."]
[null,128,"2017-02-27","20:12:00",-37.844918,144.72776999999999,30238362,"LV002","22kV AC","Rural Short","Asset failures resulting in grass/vegetation fire : Other Assets"," - surge diverter","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12893,"20170320PWA_02","Customer reported a loud bang in his street and what looked like a burnt insulator at the base of a pole. Powercor fault crew leader Terry Burton was directed to check the incident as part of a line patrol for a feeder outage on a separate feeder. (LV 003 feeder trip at 20:10hrs on 27.2.17). The Powercor crew attended the site and noted a damaged surge diverter and a small burnt patch on the nature strip beneath a HV cable head outside No 89 Marquands Rd, Truganina. The burnt patch measured approx. 400mm x 400mm. The surge diverter damage is suspected to have occurred as a secondary incident pursuant to reclose events after the original LV 003 feeder trip. The Powercor crew made the site safe by replacing the cable head surge diverter. There were no reported injuries. There were no other reports of ground fire."]
[null,129,"2017-02-28","21:00:00",-35.809147000000003,143.25294,33015899,"CTN003","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","High",0.5,0.5,12894,"20170320PWA_03","VicFire reported a fire on a pole at the incident location. On arrival the crew found that a LV FOLCB had failed due to suspected poor connection and caught on fire, molten plastic fell to the ground but no ground fire resulted. Fire self extinguished prior to CFA arriving. There were no reported injuries, no third party damage, no protection operated."]
[null,130,"2017-02-28","20:34:00",-38.354854000000003,141.61412000000001,32135103,"PLD005","22kV AC","Urban","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - overhead conductor (bare; copper)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","Very High",1,0.2,12848,"20170302PWA_02","A call was made to Powercor advising of a crane making contact with overhead High Voltage wires at the incident location. No contact details were provided. No injuries were reported.\n\n\n\nWhen crews arrived on site they found that an ISO Marshalling timber transporting crane had hit the 3 phase 22kV line between Pole 12 (LIS-997381) and Pole 13 (LIS-905402). The incident caused 2 phases of conductor to break and fall to the ground, and a flashover and small ground fire to occur.\n\n\n\nIt appeared that the crane operator may have driven underneath the line with the boom still in the air. The crew reported that the excavator operator did not appear to be injured or receive any shock, however he appeared to be a bit shaken by the ordeal. He then left the incident site with ISO Marshalling colleagues.\n\n\n\nThe attending crew replaced the 2 spans of the damaged 2 wires (7/.104Cu) with approximately 300m of 7/2.75Cu.\n\n\n\nAs provided by the lineworker (Ben Cumming):\n\n“At approx. 2045 Tuesday 28 February an ISO Marshalling crane operator drove his vehicle into 3 phase 22kv conductors between pole 12 and pole 13 Cliff St spur on PLD005. \n\nThe collision caused a flashover and two of the conductors to break and fall to the ground.  There was no damage to any Powercor assets or to the surrounds of the incident. The conductors were repaired and sagged to a height of 10m at road crossing. (Same height as originally).\n\nThe crane operator was uninjured and the machine did not sustain any damage.”\n\n\n\nI made a follow-up call to the Port of Portland (03 5525 0900) to confirm that the crane operator was OK. During the call, Terry Baily from the Port of Portland advised that they want to have the overhead line relocated to underground, I advised how to get this request moving.\n\n\n\nNo injuries have been reported. Protection systems operated as expected."]
[null,131,"2017-03-02","00:38:00",-38.308850999999997,144.26737,32084185,"WPD014","22kV AC","Rural Short","Asset failures resulting in grass/vegetation fire : HV Fuse"," - fuse (powder filled)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",{"$f":"IF(P170=\"\",\"\",IF(P170=\"LBRA only\",0.2,IF(P170=\"HBRA only\",1,IF(P170=\"within electric line construction area\",19.8,IF(P170=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"Y","Very High",{"$f":"IF(S170=\"\",\"\",IF(S170=\"No forecast\",0.1,IF(R170=\"N\",0.1,IF(S170=\"Low-moderate\",0.2,IF(S170=\"High\",0.5,IF(S170=\"Very high\",1,IF(S170=\"Severe\",2,IF(S170=\"Extreme\",3.5,5))))))))","v":1},{"$f":"IF(OR(Q170=\"\",T170=\"\"),\"\",IF(AND(P170=\"within electric line construction area\",S170=\"No forecast\"),1,Q170*T170))","v":4.5999999999999996},12853,"20170302PWA_06","Mike from CFA reported that a small grassfire had started around the base of a pole. He stated that a fuse had dropped down and started the fire. The CFA were onsite at the time of the report. Mike from CFA reported that a small grassfire had started around the base of a pole. He stated that a fuse had dropped down and started the fire. The CFA were onsite at the time of the report. The attending crew found evidence of a small grass fire around switch pole 3 (LIS-35392) SW21816. \nThe fire, totalling approximately 40m²- 45m², had been extinguished by the CFA. The CFA had left the site when the attending crew arrived. The lineworker (David Pickering) found that 1 of the 3 powder filled fuses was most likely the cause of the fire. He suggested that the fuse had failed to operate correctly and had candled with hot debris falling to the ground. There was minor damage to a private boundary fence (420 Coombes Rd), however the fence appeared to remain intact (secure). Definitive cause is unknown, however with the high humidity (95%) and foggy conditions, the weather could have played a part in the incident. appropriate repairs were completed and the red phase fuse replaced. The site was deemed safe. There were no reported injuries. There were no reported injurie"]
[null,132,"2017-03-03","12:53:00",-37.580055000000002,143.87712999999999,32009382,"BAS013","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in grass/vegetation fire : Other Assets"," - overhead service conductor (other)","single phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12857,"20170306PWA_04","Customer called to advise wire down in driveway at the above location. A crew attended and found a N/S service cable to house had burnt off at roller clamp at house end resulting is the service cable breaking and falling to the ground. An area of approx. 1m/sq. was burnt on the lawn in the front yard. This was extinguished by the property owner. The crew isolated the broken service, replaced it with a new T.S.C and reconnected supply. There were no shocks, injuries or third party damage."]
[null,133,"2017-03-03","08:44:00",-38.214309999999998,141.71377000000001,32135590,"PLD001","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : Pole and cross arm failure or Pole and cross arm fire"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","High",0.5,0.5,12854,"20170303PWA_01","VicFire reported a fire start at the incident location. A crew attended and found a pole fire had occurred at P16 Translator S/L. A fire had starts at the head of the pole, burning thru the pole at the king bolt. The cross arm released from the pole and the conductor came to ground. The conductor did not break. Protection operated. This resulted in a ground fire start of approx. 5m x 5m on private property. There was no third party damage. The CFA attended and extinguished the fire. The crew replaced the pole and supply was restored.  \n\n\n\nThere were no shocks, injuries or third party damage. \n\n\n\nNote: The original Wood HV cross arm, had been replaced in August 2013 with a Steel cross arm as a P2 maintenance item but all original brown insulators and disc where refitted."]
[null,134,"2017-03-04","21:49:00",-36.035127000000003,145.40423999999999,33087082,"NKA006","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : HV Fuse"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12859,"20170307PWA_02","CFA reported grass fire at the above location. A crew attended and the operation of an EDO fuse had caused a  grass fire approx. 200m x 30m in both road reserve and on customer grazing land. Crew isolated supply and  replaced fuse. CFA were in attendance prior to crew arrival and extinguished fire. CFA had to cut customer’s fence to gain access to property. Customer’s fence-line was reported to be concrete posts and therefore no further damage was reported as having been sustained. No shock, no third party damage, no injuries were sustained."]
[null,135,"2017-03-05","10:35:00",-38.256798000000003,142.44117,32198619,"KRT012","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - dropper / bridge","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,12895,"20170320PWA_04","The CFA reported a pole fire at the incident location. On arrival the crew found that the pole had burnt through under the king bolt, attached to the crossarm for the HV fuses. The pole was severely damaged and almost burnt through. This could have caused the pole top to come to ground, if it had burnt through. The pole fire was initially discovered by some horse riders. Fortunately the CFA were in the vicinity undertaking an exercise. No third party damage or injury was reported. The crew made the site safe, and replaced the pole."]
[null,136,"2017-03-06","11:50:00",-36.621414999999999,145.21939,32192135,"MNA034","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in grass/vegetation fire : Other Assets"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12968,"20170323PWA_01","Crew  advised of a small fire  resulting from clashing of Low voltage conductors during works. The white phase overhead conductor burnt through fell to the ground and a fire of less than 1 square metre was initiated.  The crew extinguished the fire. Supply isolated for installation to complete repairs. There was no injuries"]
[null,137,"2017-03-07","21:06:00",-37.452322000000002,142.96902,33048290,"ART033","12.7kV AC (SWER)","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any other thing forming part of or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,2.2999999999999998,12878,"20170308PWA_08","A farmer reported that a B-Double tip truck working on his property had hit the overhead power lines and bought them down. On arrival the crew found that a B-Double tip truck had contacted the SWER conductor between king Pole 35 and King Pole 36 and pulled the SWER conductor low. The SWER ACR protecting the line operated for the fault. The truck sustained damage to its tyres as a result of the contact. A ground fire started as a result of the contact. Approx. 200 (20x10) sq. metres of grass was burnt. There was no other damage, no injury and no shock. The line was isolated and the conductor was repaired."]
[null,138,"2017-03-07","12:48:00",-37.503307999999997,142.81702999999999,30151626,"ART033","12.7kV AC (SWER)","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any other thing forming part of or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,2.2999999999999998,12879,"20170308PWA_07","CFA called to advise of a wire down and a fire start at the above location. On arrival the crew found a farmer had been building a large hay stack under a SWER O/H line. During construction of the stack, the loader contacted the SWER line resulting in the line breaking and falling onto the stack,  starting a fire. Protection operated at P1 Gleeson S/L when a fuse blew. The CFA attended and extinguished the surrounding ground fire. Approx. 1000m/sq. of private grass land was burnt. \n\n\n\nDue to the location of the smouldering stack, the broken SWER line could not be re strung and 1 customer past the location will remain off supply until the CFA can arrange an excavator onsite today to disperse and extinguish the stack. The crew will then be able to re string the SWER conductor and restore supply to the last customer. CFA to notify Powercor when the stack has been extinguished.\n\n\n\nWork cover and ESV have been notified of the incident. \n\nThere were no shocks, injuries or third party damage."]
[null,139,"2017-03-08","13:03:00",-37.657809,143.97219999999999,32002591,"BAS023","22kV AC","Rural Short","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,2.2999999999999998,12880,"20170309PWA_03","CFA called to advise a tree had pulled down a wire and started a grass fire at the above location. On arrival the crew found a tree had contacted 1 phase of a single phase 22kV line and broke the conductor, resulting in the conductor falling to the ground and starting a grass fire on public property. The CFA attended and extinguished the ground fire.  Approx. 500m/sq. of road reserve was burnt. Protection operated at Eureka P97A ACR. The crew removed the tree and repaired the conductor, restoring supply.\n\nThere were no shocks, injuries or third party damage."]
[null,140,"2017-03-08","00:12:00",38.362686199999999,141.61802700000001,32139117,"PLD006","22kV AC","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Very High",1,0.2,12917,"20170321PWA_02","The CFA reported a pole fire at the incident location. On arrival the crew found that the crossarm had caught fire at one of the outside HV insulators. No conductors came to ground hence, no protection activated for this incident. There was no ground fire. No third party damage or injury was reported. The crew made the site safe and replaced the crossarm."]
[null,141,"2017-03-09","22:46:00",-37.870832,144.70094,30111186,"LV004","Low voltage AC (<1kV)","Urban","Asset failures resulting in grass/vegetation fire : Other Assets"," - overhead service conductor (other)","single phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12882,"20170314PWA_02","VicFire phoned in to advise of a wire down at the premises, pole to house and a small grass fire at the incident location. Upon arrival the crew had found that the 2/C Twisted Grey PVC service cable from LV Pole LIS-209218-7728 to POA House No. 6 Sheahan Crescent, Hoppers Crossing 3029, had failed and snapped at the house end which caused the Live LV Service Cable to come to ground in the front yard. The resultant sparks from this caused a minor grass fire in the front yard of  No. 6 Sheahan Crescent, Hoppers Crossing 3029, approx. 5m x 4m total area. The CFA were on site and the grass fire was extinguished. There was no reported injury or shocks as a result of this incident. The LV Service Cable was replaced."]
[null,142,"2017-03-10","18:57:00",-34.613597900000002,142.750336,33064684,"RVL004","22kV AC","Rural Short","Asset failures resulting in grass/vegetation fire : Other Assets"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Very High",1,0.2,12886,"20170314PWA_06","Report from REC that there was a cable down on the road verge and no supply in the area, cable reported to be broken between pole 11 and pole 12. Crew attended and found HV 3/2.75 Steel Cable had failed at cable sleeve with no apparent reason. A burn area on the ground of 3 Metres by 3 Metres was evident, No property damage and No injuries reported."]
[null,143,"2017-03-12","08:10:00",-37.77308,144.82172,30113183,"SSE014","22kV AC","Urban","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12884,"20170314PWA_04","A number of residents/customers in the Sunshine & St Albans Area phoned in to advise that they had no power. Upon arrival the PCA HV Operator, Ashley Magnus, had discovered that a HV X-arm Fire had occurred on HV Strain Pole LIS-25393-7728,  St Albans Rd corner Gilmour Rd. The resultant HV X-arm fire had caused the outer BL side phase conductor and strain/bridging insulator’s to come away from the HV X-arm and fall onto the LV conductor’s below. Protection on 22kV Feeder SSE011 did not operate as it was supposed, this subsequently resulted in the loss of Bus No.1 at SSE Zone Sub, resulting in an outage to approximately 11,000 customers supplied from SSE011, SSE012, SSE013 & SSE014 22kV Feeders. Initial reports from the field crew suggested possible HVI, this was later confirmed by the LEI, Terry Long, who attended. The following damage occurred due to the HVI to a VicTrack Hut at the corner of St Albans Rd Gilmour Rd, (approx. 100m south of LIS-25393). Customer:- BAYSIDE TRAINS COROPORATION, ID 34024473  -  Damaged LV Fused Mains Box, Damaged Customers Unmetered Mains Cable from LV Fused Mains Box to PCA Smart Meter, Damaged PCA Smart Meter. PCA Crew & LEI returned the following day to assist customers REC with repairs. There was no reported ground fire, injury or shocks as a result of this incident."]
[null,144,"2017-03-12","04:37:00",-37.677017200000002,144.432175,31033069,"BMH004","22kV AC","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12921,"20170321PWA_03","CFA called in to advise of a pole on fire cnr Clarinda St & Turner St, Bacchus Marsh, LIS-965846. Upon arrival the crew, had discovered that a HV X-arm had caught fire and burnt through at the HV X-arm Strap. Please Note:- The HV Conductors remained in place and connected to the HV Wood Strain X-arm/HV Insulators. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. The crew made the site safe and replaced the HV X-arm."]
[null,145,"2017-03-14","12:38:00",-38.35248,143.35185200000001,32065090,"CLC006","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,2.2999999999999998,12922,"20170321PWA_04","A customer reported that the pole out front of their house was on fire at the incident location. On arrival the crew found that a fuse box on the substation pole had overheated, resulting in the box catching fire and dropping melted plastic and debris to the ground. The debris landed on short green grass and there was no ground fire, no reported third party damage or any injuries."]
[null,146,"2017-03-14","10:23:00",-36.024185199999998,146.00060999999999,30239162,"CME014","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - switch (disconnector/isolator)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12923,"20170321PWA_05","The Police reported a pole fire at the incident location. On arrival the crew found that a tree had fallen across the line and the blue and white phase conductors had clashed. The clashing caused a flashover at the FSD, this in turn caused a small fire in the area of the FSD. The crew said there was no ground fire. No third party damage or injury was reported."]
[null,147,"2017-03-15","14:08:00",-38.014901000000002,143.25154000000001,32055045,"CDN004","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : Other Assets"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Very High",1,4.5999999999999996,12888,"20170316PWA_02","Vic Fire reported a ground fire at the incident location. On arrival the crew found that a large grassfire of approx. 8ha in size had ignited near Cable Head Pole 210 of the Lismore Line. There was a reclose of the P113 Lismore Line ACR at 2:01pm. Inspections of the CHP at P210 Lismore by the attending crew failed to identify a cause for the grassfire. The area burnt was a mixture of road reserve and private land, with damage caused to fences and approx. 15 hay bales. "]
[null,148,"2017-03-12",null,-37.04954,144.14735400000001,32044587,"CMN004","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : Any fire triggered by any asset failure caused by Lightning"," - overhead conductor (bare; steel)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA","within electric line construction area",19.8,"Y","Very High",1,19.8,12887,"20170315PWA_01","CFA reported cable on the ground grass smouldering corner of Castlemaine - Maldon and Muckleford - Walmer Roads. Crew attended and found HV conductor 3/2.75 Galvanised Steel Conductor had failed believed to be caused by lightning strike. An area of 8 Metres by 2 Metres was burnt on the road verge. HV fuse had operated and suspected back feed was the cause of the small fire. Crew Isolated supply and restored cable. No property damage and No injuries reported"]
[null,149,"2017-03-16","11:01:00",-34.330244,141.73497,32144890,"RCT023","12.7kV AC (SWER)","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - pole (wood)","single wire earth return (SWER)","Started by any other thing forming part of or coming into contact with a distribution system","HBRA","HBRA only",1,"Y","High",0.5,0.5,12889,"20170317PWA_01","Vic Fire reported a tractor hit a pole and caused a ground fire. The crew attended and confirmed that a tractor (Driven by Anthony Rowe) had hit a pole and bought it and the conductors to ground. This caused a ground fire of approximately 5 meters X 40 meters. The site the was made safe. P6 was also considered to be in poor condition following the incident, so both P5 and P6 were changed, before restoring supply."]
[null,150,"2017-03-19","16:26:00",-34.270522999999997,142.17198999999999,32148440,"RCT021","22kV AC","Rural Short","Asset failures resulting in grass/vegetation fire : Other Assets","Other ","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,12925,"20170321PWA_06","Customer reported pole on fire at base of pole. On arrival, crew found 2 separate spot fires (5-10 square meters) at bottom of 2 pole substations within 200m of each other. Customer had extinguished the fire, no CFA attendance. One section fuse operated, there was no evidence of failed assets at either pole. There were no reported injuries, minor property damage."]
[null,151,"2017-03-20","19:11:00",-36.749636000000002,144.32105000000001,31037843,"EHK021","22kV AC","Urban","Asset failures resulting in grass/vegetation fire : Other Assets"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12926,"20170321PWA_01","Vic Fire reported a pole exploded and started ground fire at corner Piper Lane and Piper Rd East Bendigo.  On arrival the crew found one of the HV cable head joint terminations had failed and a fire occurred at the base of the pole approx. 25 sq. meters in area.   The fire had gone through a mesh fence but no property damage evident.  Crew performed switching and logged fault follow up to occur morning of 21/03/2017.  ESV notified.  No shock or injuries. VicFire reported a pole exploded and started ground fire at corner Piper Lane and Piper Rd East Bendigo. \n\nVic Fire reported a pole exploded and started ground fire at corner Piper Lane and Piper Rd East Bendigo.  On arrival the crew found one of the HV cable head joint terminations had failed and a fire occurred at the base of the pole approx. 25 sq. meters in area.   The fire had gone through a mesh fence but no property damage evident.  Crew performed switching and logged fault follow up to occur morning of 21/03/2017.  ESV notified.  No shock or injuries."]
[null,152,"2017-03-21","15:34:00",-35.200409999999998,141.28525999999999,32152227,"OYN001","12.7kV AC (SWER)","Rural Long","Asset failures resulting in grass/vegetation fire : Any fire triggered by any asset failure caused by Lightning"," - pole (wood)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","HBRA","HBRA only",1,"Y","Low-moderate",0.2,0.2,12927,"20170322PWA_13","CFA reported a pole fire at the incident location. Upon arrival, the fault crew found that a HV SWER pole was struck by lightning. This resulted in a  ground fire of some 35 acres in salt bush.  No injuries were reported. There were no reported injuries."]
[null,153,"2017-03-22","00:50:00",-34.785905999999997,142.62693999999999,32139293,"WMN013","22kV AC","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","High",0.5,0.5,12967,"20170403PWA_03","CFA reported pole fire at 3493 Hattah-Robinvale Rd Liparoo.  On arrival, crew found cross-arm had fire on the footpath side of it.  Crew were unsure if the storm activity or asset failure had caused it although they suspected tracking likely to have occurred. Crew advised disc insulator had pulled through and re-drilled 100mm from the affected area.    No injuries, no ground fire, no third party damage."]
[null,154,"2017-03-27","10:48:00",-38.428651000000002,143.57886999999999,33039891,"CLC006","22kV AC","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,12933,"20170328PWA_06","Vic Fire reported a ground fire at the incident location. On arrival the crew found that a grassfire of approx. 1,000m2 in size had ignited beneath the 22kV conductors near Pole 115 of the Gellibrand Line. There was a reclose of the CLC006 feeder CB recorded at approx. 10:42am. Inspections of the HV conductor in the area by the attending crew failed to identify a cause for the grassfire, however it was noted that strong winds were present, and several pieces of bark were scattered on the ground in the area. The area burnt was a mixture of road reserve and private land, with minor damage caused to fences and private trees. The crew were told by the CFA crews onsite that a CFA investigator was to attend the site. There was no other reported third party damage or any injuries."]
[null,155,"2017-03-27","10:43:00",-36.759357999999999,144.26646,32034497,"BET002","22kV AC","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Very High",1,0.2,12971,"20170404PWA_03","Employee report of pole fire. HV xarm burnt off HV insulator sitting on LV crossarm. NO report of ground fire or injuries"]
[null,156,"2017-03-30","18:38:00",-35.597544999999997,143.54223999999999,32155539,"SHL005","12.7kV AC (SWER)","Rural Long","Asset failures resulting in grass/vegetation fire : Pole and cross arm failure or Pole and cross arm fire"," - crossarm (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","High",0.5,0.5,12960,"20170331PWA_01","Customer reported a grass fire caused by Powercor assets ( pole fallen over ) at the incident location. On arrival the crew found that a pole had failed and the SWER conductor made contact with the ground in an adjacent span, a ground fire ignited resulting in approximately 50m x 100m of stubble paddock being burnt. CFA attended & extinguished the fire.\n\n\n\nThere were no reported injuries, no 3rd party damage, BA fuse at “Beauchamp West ISO” operated for the incident."]
[null,157,"2017-03-30","01:00:00",-36.591963999999997,143.92197999999999,30017992,"EHK024","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : Pole and cross arm failure or Pole and cross arm fire"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,2.2999999999999998,12965,"20170403PWA_01","VicFire advised a fire at the above address.  Fire had been extinguished upon crew arrival. Upon arrival noted burning to the pole and 2 small patches of grass at the base of the pole.  .  Pole is limited life.  Follow up has been raised with Bendigo CPL for replacement. There were no injuries, loss or damage to third party property."]
[null,158,"2017-04-02","23:07:00",-37.846004000000001,144.68516,"PA0129419","LV001","22kV AC","Rural Short","Asset failures resulting in grass/vegetation fire : Oil-filled plant"," - transformer (kiosk mounted)","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12969,"20170404PWA_01","Observations from site attendances:\n1) A 315kVA, Etel kiosk in a residential subdivision appears to have sustained a major fault.\n2) A grass fire was initiated in reserve landscaping surrounding the Kiosk location.\n3) The forces of the electrical fault have caused the kiosk to:\na. Disturb the soil adjoining the Kiosk’s concrete plinth.\nb. Rupture and deform the transformer tank, tank lid, welds, tank bracing.\nc. Discharge oil from the transformer tank\nd. Deform and force open the Kiosk roof, doors, steel shell cross members\ne. Snap a HV fuse holder and project Bayonet HV fuses over the road and into residential property\n4) There is indication of discolouration of HV insulation on the inner set, C phase, HV Pin bushing.\n5) Per suggestion by Underground repair personnel attending during daylight hours on 3/4/17, this may be the fourth ETEL Kiosk substation to have faulted in a similar manner in recent times.\n6) There appears to be no indication that customer numbers, and loading type have contributed to a substation overload issue prior to the incident.\nThere were no reported injuries.\nThere was no other reported damage."]
[null,159,"2017-04-03","13:23:00",-37.776795,141.87242000000001,30090621,"HTN002","22kV AC","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,12970,"20170404PWA_02","CFA called to report a tree down, wires sparking and a grass fire start. A crew attended and found that a tree had fallen onto a HV conductor between P130 and P131 Branxholme line resulting is a ground fire start. The tree burnt thru the conductor before the crew could isolate the line and the conductor came to ground. The ACR at Branxholme P30 then tripped to lock out. The attended CFA crews extinguished the ground fire start and once it was confirmed supply was isolated, also extinguished the burning tree. Once the fire was extinguished, the crew repaired the broken conductor and restored supply. The ground fire was approx. 10m x 30M in area on the road reserve. There were no shocks, injuries or 3rd party damage."]
[null,160,"2017-04-03","11:50:00",-37.177385000000001,141.50675000000001,32101722,"CHM011","12.7kV AC (SWER)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : HV Fuse Failure (including ‘hang-ups’ and ‘candling’)"," - dropper / bridge","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","Low-moderate",0.2,0.2,12994,"20170411PWA_01","A customer called to report the top of a pole at their premises was sparking and on fire. A crew attended and found the live line flex had broken off at the top EDO connection at SWER substation pole Thornlea 7, resulting is arcing and the top EDO cap melting/burning. The crew isolated supply and replace the burnt EDO cap and broken flex. CFA did not attended. There was no ground fire start.  \n\n\n\nThere were no shocks, injuries or fire start."]
[null,161,"2017-04-05","01:38:00",-38.181142999999999,144.51353,32076029,"DDL014","66kV AC","Rural Short","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA","HBRA only",1,"Y","High",0.5,0.5,12981,"20170406PWA_03","Customers reported an outage and also a car impacting into a pole at  Corryule Rd Curlewis. Upon arrival the crew found that the car hit the 22/66kV intermediate pole. The driver was taken to hospital with non-life threatening injuries. The broken pole was on the ground and also one end on the roof of car. High voltage injection occurred involving 66Kv, 22kV an aerial earth (connected to LV neutrals remote from site). A number of surge diverters, 22Kv fuses and transformers were damaged  in other parts of the 22kV feeders and a small ground fire of some 10M square occurred during restoration."]
[null,162,"2017-04-08","14:34:00",-37.185371000000004,143.39134000000001,33013577,"MRO008","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : Any fire triggered by any asset failure caused by Lightning"," - guy wire","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,2.2999999999999998,13005,"20170413PWA_03","Customer reported a lightning strike and small grass fire around stay which was extinguished by heavy rain at the incident location. On arrival the crew found no asset or property damage, a ground fire had ignited resulting in approximately 1m x 1m of grass being burnt.\n\n\n\nThere were no reported injuries, no 3rd party damage, no protection operated for the incident."]
[null,163,"2017-04-08","13:40:00",-38.095742000000001,143.68786,32062880,"CLC003","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : HV Fuse Failure (including ‘hang-ups’ and ‘candling’)"," - fuse (any other type)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","High",0.5,{"$f":"IF(OR(Q202=\"\",T202=\"\"),\"\",IF(AND(P202=\"within electric line construction area\",S202=\"No forecast\"),1,Q202*T202))","v":2.2999999999999998},13007,"20170413PWA_04","Customer reported Transformer appears to have flames coming out of top of it. On arrival crew crew found that HV fuse had candled. There was no evidence of ground fire, no reported injuries or third party property damage."]
[null,164,"2017-04-09","22:21:00",-38.402313999999997,144.18583000000001,30065718,"WPD014","22kV AC","Rural Short","Asset failures resulting in grass/vegetation fire : Pole and cross arm failure or Pole and cross arm fire"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,13000,"20170412PWA_05","On Sunday evening, WPD014 tripped at the CB at the WBD Zone Substation. The Powercor control room notified the A/H Operator to investigate the cause. \nThe operator patrolled and conducted some switching to isolated the problem, but could not locate the exact location/cause. A crew was dispatched to investigate early the following morning, a customer reported a leaning pole near the Anglesea River which lead the crew to the incident location. Upon arrival, the crew identified a 21/12 wood pole leaning approx. 45°. This was causing a span of 22kV conductor to be sagging into the Anglesea River. It was identified that the stay rod had rusted through and gave way. The site is now safe and all repairs have been made. A tree top was burnt where the conductor had made contact. There were no reported injuries or third party damage."]
[null,165,"2017-04-09","19:55:00",-35.628131000000003,143.78054,30235186,"KGT004","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : Pole and cross arm failure or Pole and cross arm fire"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","Very High",1,1,13012,"20170418PWA_02","Customer reported wires down and pole fire at the incident location. On arrival the crew found a pole fire had caused a small ground fire resulting in approximately 2m x 3m of grass being burnt.\n\n\n\nThere were no reported injuries, no 3rd party damage, for the incident."]
[null,166,"2017-04-09","07:58:00",-35.110930000000003,141.19869,32149124,"OYN001","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","Very High",1,1,13013,"20170418PWA_03","Crew found the customer outage was the result of a burnt HV strain arm at the incident location. There were no reported injuries, no 3rd party damage or grass fire for the incident."]
[null,167,"2017-04-10","06:45:00",-38.538977000000003,143.97408999999999,30064045,"CLC005","22kV AC","Rural Short","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from trees contacting network assets"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,12997,"20170412PWA_02","The Crew were dispatched to investigate a wires down and possible HVI incident in Grove Rd, Lorne. Attending crew found that a tree had fallen onto a span of 3-7/2.5 AAC HV conductor between Pole 488 (LIS-30400) and Pole 1 (LIS-29595). The HV then hit the ground and left small burn marks on the grass.  The burns total approximately 2m long and 50mm wide. It is suspected that there was also a HVI with the HV making contact with the bare LV. The site was made safe and appropriate repairs were made. The LEI, Allan Garrett, tested all customer connections and confirmed no damage to customer property. Allan advised one customer was unable to be reconnected due to possible faulty CB, and believed this was not related to incident. There was no third party damage or injuries reported."]
[null,168,"2017-04-11","06:24:00",-36.377650000000003,145.42488,33089832,"STN024","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,13021,"20170418PWA_08","Vic Fire reported a Pole Fire at the incident location. On arrival the crew found the FSD unit to be overloaded and burnt out. There were no reported injuries, no 3rd party damage, no ground fire for the incident."]
[null,169,"2017-04-12","22:19:00",-36.333035000000002,145.43177,30305074,"STN024","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : Other Assets"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,13014,"20170418PWA_04","CFA reported a grass fire at the incident location. The crew found a faulty HV bridge caused a small fire 10m x 1m along the drain at the incident location. There were no reported injuries, no 3rd party damage for the incident. "]
[null,170,"2017-04-12","15:35:00",-36.189863000000003,144.74831,32184201,"ECA012","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : Pole and cross arm failure or Pole and cross arm fire"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","Low-moderate",0.2,0.2,13011,"20170418PWA_01","CFA reported wires down and they were controlling a small grass fire at the incident location. The crew found a broken HV termination Xarm which caused a 150m x 100m grass fire in a re-vegetation area at the incident location. There were no reported injuries, no 3rd party damage for the incident."]
[null,171,"2017-04-12","02:24:00",-38.404789000000001,144.19889000000001,33042041,"WPD021","22kV AC","Rural Short","Asset failures resulting in grass/vegetation fire : Oil-filled plant"," - transformer (pole mounted)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,13001,"20170413PWA_01","On Wednesday morning, the crew were conducting some switching for operations. When they closed Switch 20175 (Angsew Spur), the crew noticed an explosion in the distance. They drove to investigate. Upon arrival, the crew found that transformer, Treatment Works 14, had exploded and was on fire. The CFA extinguished the fire. The crew advised that oil had hit the ground and small ground fires had occurred. The property is a Barwon Water treatment plant and a representative was called to attend site at the time of the incident. The Powercor Environmental Group was made aware of the situation. Soil samples were taken and sent off for testing.\nVeolia was arranged to dispose of the contaminated soil. Barwon Water assets remained on supply during the repairs via a generator. Representatives were onsite throughout the day. The site is now safe and all repairs have been made. ESV was notified of the incident. There were no reported injuries or third party damage."]
[null,172,"2017-04-14","12:42:00",-35.224142559999997,143.46718554,30276890,"SHL004","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,13029,"20170420PWA_03","CFA reported that there had been a pole fire at the above-mentioned location. Upon arrival, the crew found that the fuse box had burnt at the 4m mark on the pole. Cause unknown. Crew removed old fuse box and replaced it with a new unit. The site is now safe and all repairs have been made.\nThere were no reported injuries or third party damage."]
[null,173,"2017-04-15","22:40:00",-38.331300919999997,144.32086676,30319569,"WPD032","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,13022,"20170419PWA_01","The CFA reported a pole fire at the incident location. On arrival the crew found that a Low Voltage three phase pole box had faulted and caught fire. \nTalking to the crew there was no ground fire. No third party damage or injury was reported. The crew made the site safe, the pole box was replaced and supply was restored."]
[null,174,"2017-04-18","16:12:00",37.832073309999998,144.79946136000001,31038884,"LVN022","22kV AC","Urban","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,13024,"20170419PWA_03","During Transport an excavator has contacted the HV conductors at 25 Cyanamid st Laverton North. The conductors were slightly damaged and there were flashover marks on the boom. There were burnt HV connections and HV conductors on the ground outside 85 Cherry Lane. At  73 Cherry lane there was evidence of HVI and a ground fire of 3.5 square metres. There were a number of street lights damaged along Cherry Lane. The Protection operated as expected. There were no reported injuries."]
[null,175,"2017-04-18","07:01:00",-37.805844999999998,144.83166,33105773,"SSE033","Low voltage AC (<1kV)","Urban","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,13018,"20170418PWA_06","A customer reported a pole fire at the incident location. Upon arrival, the Powercor crew found that an overheated termination ignited the Krone box on concrete pole. There were no injuries, third party damages or ground fire. The repairs arranged."]
[null,176,"2017-04-19","07:19:00",-38.370666999999997,142.46329,30137969,"WBL006","22kV AC","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","High",0.5,0.1,13033,"20170420PWA_04","VicFire reported a pole smouldering and a wire hanging low. A crew attended and found that a wooden Tee off cross arm on P44 Warrnambool West S/L had burnt thru at the bridging insulator and was hanging from the bridging conductor. The crew isolated the 22kV conductors and replaced Tee off cross arm and all insulators with new units. There was no ground fire start. Local CFA was in attendance. There were no shocks, injuries or 3rd party damage."]
[null,177,"2017-04-20","18:32:00",-35.599643,143.93467999999999,32030269,"KGT003","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","Low-moderate",0.2,0.2,13046,"20170427PWA_03","CFA reported Pole Fire APPROX 600-700 metres SOUTH of intersection of Kerang - Murrabit Road and Guilmartin Road Capels Crossing.   Crew attended and assessed the partially burnt HV intermediate crossarm where the insulator pin had fallen through, crew assessed the integrity of the crossarm and reported as a fault follow-up. No ground fire, no property damage, no reported injuries."]
[null,178,"2017-04-20","18:31:00",-37.689757780000001,144.44213067999999,30115961,"BMH006","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"Y","High",0.5,0.5,13048,"20170427PWA_05","VicFire called in to advise of a wire on fire & brigade en-route. A resident Mrs Kerry Fay also called in to advise of a small box on pole outside property has caught fire, CFA have attended and fire now out, customer has no supply. On arrival the crew had discovered that a Single-Phase FOLCB and approximately 1m of 16mm LV UG Service Cable running down the pole had overheated and burnt out at LV Inter Pole LIS-103032. There was an outage to 3 x LV customers as a result of the Blue-Phase LV Fused Isolator at the Sub Pole Nordic 7 operating. There was no reported ground fire, third party damage, injury or shocks as a result of this incident. The crew made the site safe and replaced the FOLCB and the affected 16mm LV UG Service Cable."]
[null,179,"2017-04-20","17:58:00",-35.913122000000001,143.22664,32024287,"CTN003","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,13042,"20170426PWA_04","CFA reported Pole Fire on the Calder Highway between the towns of Demosa and Nullawil. Crew attended and opened off ACR for isolation and replaced HV intermediate crossarm. No ground fire, no property damage, no reported injuries."]
[null,180,"2017-04-20","13:43:00",-34.199148000000001,142.16515999999999,32150522,"MDA031","22kV AC","Urban","Asset failures resulting in asset fire (no grass/vegetation fire) : Pole and cross arm fire (including ‘smouldering’ or ‘smoke’)"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,13041,"20170426PWA_03","A passer-by informed that a loud bang, sparking and smoking at the incident location. On arrival the crew found that a Pole Fire had occurred on 12 X ETIW-SMATEO 1 (LIS 10044 strain pole). The crew made the place safe and repairs done.  There was no ground fire or injury. CFA attended. Note: At the time of the incident no HVI found. After power restoration, a customer informed some damages to his installation. An inspector attended but no HVI found at the time. He will inspect the customer’s installation again."]
[null,181,"2017-04-21","12:08:00",-36.26249,142.39315999999999,32097104,"HSM005","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in grass/vegetation fire : Other Assets"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,13039,"20170421PWA_03","A customer reported a wire to the house had broken and burn marks on ground where it landed. A crew attended and found a NS service to the premises had burnt off at the roller clamp at the house end and the service had fallen to the ground, resulting is a ground fire start of approx. 100mm/sq.  No CFA attended. The crew replaced the broken service with a new service. There were no shocks, injuries or 3rd party damage."]
[null,182,"2017-04-21","10:16:00","-38.69673949,",143.42459321000001,33039339,"CLC006","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : HV Fuse Failure (including ‘hang-ups’ and ‘candling’)"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"Y","Low-moderate",0.2,0.91999999999999993,13049,"20170427PWA_06","Customer reported a transformer on fire at the incident location.  On arrival the crew found that a HV EDO fuse had operated on a transformer pole, however the barrel of the EDO fuse stayed in position without dropping down.  The barrel then caught fire. There was no injuries, ground fire or third party property damage reported. The fault caused the CLC006 -  Hordern Vale P5 ACR to also trip to Lock Out at 10:16 PM, interrupting supply to 137 accounts. The faulty transformer was disconnected and left off supply overnight. Replacement to be arranged the following day. All other interrupted supply accounts were restored. The previous day the same transformer had been struck by Lighting  - refer OMS 984970. Attending crews feel the incidents are related."]
[null,183,"2017-04-21","08:14:00",-37.668570000000003,144.44512,30112526,"BMH005","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"Y","Low-moderate",0.2,4.0000000000000008E-2,13047,"20170427PWA_04","Vic fire reported a pole fire at the incident location. On arrival the fault crew found that a junction box had overheated and caught fire at the incident location.\nThe crew replaced the burnt out connection box. There was no ground fire and no injury as a result of this incident."]
[null,184,"2017-05-03","07:11:00",-38.254967000000001,143.61215000000001,32061990,"CLC003","22kV AC","Rural Long","Asset failures resulting in grass/vegetation fire : Other Assets"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"N","No forecast",0.1,0.45999999999999996,13068,"20170504PWA_01","REC reports a line had fallen and resulted in a fire start. CFA in attendance. A crew attended and found 1ph on a 3ph HV line had broken and fallen on to a tree below, causing the tree to smoulder. There was no ground fire start. The crew isolated the line and repaired the conductor before supply was restored. There were no shocks, injuries, third party damage or ground fire start. Note: There is a project to re conductor this line this year after 4 breakages of the HV conductors on this line in last 18mths."]
[null,185,"2017-05-07","19:11:00","-37.52496632,",143.74153561,30004238,"BAS011","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : HV Fuse Failure (including ‘hang-ups’ and ‘candling’)"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"N","No forecast",0.1,0.45999999999999996,13084,"20170509PWA_01","VicFire reported a sparking pole top at the incident location.  On arrival the crew found a 22kV candled EDO fuse on the footpath side of the high voltage switch on ARWHITE P1. There was no ground fire. There were no injuries."]
[null,186,"2017-05-07","19:58:00",-36.456727530000002,145.49777997999999,30329181,"STN011","22kV AC","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from animal contact with network assets"," - overhead conductor (bare; steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA","LBRA only",0.2,"N","No forecast",0.1,2.0000000000000004E-2,13137,"20170605PWA_01","Customers advised fuses down and dim lights. On arrival the crew found a bird clashed the conductors, one conductor on ground and second frayed right in middle of bay, grass fire limited to small spots where conductor was laying on ground, made safe, repaired. There were no reported injuries, no property damage for the incident."]
[null,187,"2017-05-10","23:38:00",-34.203372000000002,142.14088000000001,32141697,"MDA033","Low voltage AC (<1kV)","Urban","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - fuse (any other type)","single phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"N","No forecast",0.1,2.0000000000000004E-2,13135,"20170601PWA_06","CFA reported switch board fire, at the incident location. On arrival the crew found meter board had been fire damaged as the result of a fuse base failure, made safe, repaired. There were no reported injuries and no protection operated for the incident."]
[null,188,"2017-05-12","06:47:00",-38.313718999999999,141.52965,32128364,"PLD003","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"N","No forecast",0.1,0.1,13104,"20170515PWA_01","At 06:47hrs today, the customer reports no supply to premises. The smart meter shows a power outage at 01:25hrs this morning. A crew attended and found the fuse box on the substation pole had overheat and started a pole fire. The box, LV leads and LV earth on the pole were damaged. The pole is still serviceable. The crew replaced the damaged items and restored supply. There were no reported shocks, injuries, third party damage or ground fire start."]
[null,189,"2017-05-23","11:58:00",-37.594813000000002,144.46344999999999,32167656,"BMH006","22kV AC","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA","HBRA only",1,"N","No forecast",0.1,0.1,13111,"20170524PWA_01","Emergency Services reported a cable on the ground and sparking at the incident location. Upon arrival, the crew found that a HV conductor down and the live cable caused a small ground fire.  The crew believed a vehicle brought down the cable but no vehicle details or witnesses available. There were no reported injuries."]
[null,190,"2017-06-01","09:00:00",-38.396239899999998,142.69174932999999,32194437,"WBL002","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in grass/vegetation fire : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"N","No forecast",0.1,0.1,13131,"20170601PWA_01 ","CFA reports a transformer fire at the above address. A crew attended and found a fuse box on a service pole had overheated and melted. The resulting falling debris started a grass fire at the base of the pole of approx. 1m/Sq. CFA attended and extinguished fire. The crew replaced the melted fuse box and restores supply. The box feeds a local shire works depot and a church. There were no reported shocks, injuries or third party damage."]
[null,191,"2017-06-02","08:34:00",-38.58460607,143.16674709,33035862,"COB011","Low voltage AC (<1kV)","Rural Long","Asset failures resulting in grass/vegetation fire : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","HBRA","HBRA only",1,"N","No forecast",0.1,{"$f":"IF(OR(Q230=\"\",T230=\"\"),\"\",IF(AND(P230=\"within electric line construction area\",S230=\"No forecast\"),1,Q230*T230))","v":0.1},13136,"20170602PWA_01","Customer reports fire at junction box on pole. A crew attended and found a fuse box on a substation pole had overheated and caught fire. The resulting falling debris started a grass fire at the base of the pole of approx. 5m/Sq. Customer extinguished grass fire. The crew replaced the melted fuse box and restores supply.\nThere were no reported shocks, injuries or third party damage."]
[null,192,"2017-06-04","08:20:00",-37.084360060000002,144.31377232,33026659,"CMN001","22kV AC","Rural Long","Asset failures resulting in asset fire (no grass/vegetation fire) : HV Fuse Failure (including ‘hang-ups’ and ‘candling’)"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"N","No forecast",0.1,0.45999999999999996,13173,"20170621PWA_01","Customer reported all supply fail.  On arrival, crew found evidence of candled fuse.  Crew advised EDO was held up and had appeared to have candled.  Only thing left was the bottom of the unit.  Crew isolated and repaired.  They advised that there was no fire or smouldering on ground (heavy frost).  No injuries, no ground fire, no third party damage."]
[null,193,"2017-06-05","12:03:00",-36.185810019999998,141.79311275000001,32104727,"NHL015","12.7kV AC (SWER)","Rural Long","Grass/vegetation fires from assets (non-asset failures) : Fire starts in grass/vegetation resulting from other causes (vehicle strikes, vandalism etc)"," - pole (wood)","single wire earth return (SWER)","Started by any other thing forming part of or coming into contact with a distribution system","HBRA","HBRA only",1,"N","No forecast",0.1,0.1,13172,"20170606PWA_01","A customer reported no supply at the incident location. On arrival the crew found that a tractor had struck a SWER intermediate pole in a paddock while plowing, knocking the pole over. The SWER conductor contacted the ground resulting in a grassfire of approx. 15m x 20m= 300m2 in a stubble paddock. Protection operated. There was no other reported third party damage or  injuries. Crew attended and replaced pole"]
[null,194,"2017-06-17","17:27:00",-38.428074799999997,144.17338341999999,32079086,"WPD021","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","HBRA","within area delineated on plan LEGL./16-354",4.5999999999999996,"N","No forecast",0.1,0.45999999999999996,13184,"20170627PWA_04 ","CFA reported that a pole mounted fuse box was on fire at the incident location. On arrival the crew found that the fuse box had been on fire and insulation melted away. Melted plastic and debris fell to the ground but did not start a fire due to moisture, no reported third party damage or any injuries."]
[null,195,"2017-06-20","09:02:00",-36.773224509999999,144.24861073,31004007,"BET002","Low voltage AC (<1kV)","Rural Short","Asset failures resulting in asset fire (no grass/vegetation fire) : Other Assets"," - connection box","three phase","Started in or originated from a distribution system","LBRA","LBRA only",0.2,"N","No forecast",0.1,2.0000000000000004E-2,13221,"20170713PWA_06","The CFA reported a pole fire at the incident location. On arrival the crew found that a Low Voltage three phase pole box had faulted and caught fire. Talking to the crew there was no ground fire. No third party damage or injury was reported. The crew made the site safe, the pole box was replaced and supply was restored."]
[null,196,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(P235=\"\",\"\",IF(P235=\"LBRA only\",0.2,IF(P235=\"HBRA only\",1,IF(P235=\"within electric line construction area\",19.8,IF(P235=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":""},null,null,{"$f":"IF(S235=\"\",\"\",IF(S235=\"No forecast\",0.1,IF(R235=\"N\",0.1,IF(S235=\"Low-moderate\",0.2,IF(S235=\"High\",0.5,IF(S235=\"Very high\",1,IF(S235=\"Severe\",2,IF(S235=\"Extreme\",3.5,5))))))))","v":""},""]
[null,197,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,null,"",""]
[null,198,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,null,"",""]
[null,199,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,null,"",""]
[null,200,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,null,"",""]
[null,201,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,null,"",""]
[null,202,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,null,"",""]
[null,203,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,null,"",""]
[null,204,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,null,"",""]
[null,205,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,null,"",""]
[null,206,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,null,"",""]
[null,207,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,null,"",""]
[null,208,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,null,"",""]
[null,209,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,null,"",""]
[null,210,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,null,"",""]
[null,211,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,null,"",""]
[null,212,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,null,"",""]

{"sheet":"3. Systems and Audit","index":4,"n_rows":26,"n_cols":5,"rows_kept":26,"cut":false,"hidden":false,"merged":[[25,1,26,4],[3,5,3,6],[4,5,4,6],[5,5,5,6],[6,1,6,4],[9,1,9,4],[14,1,14,4],[10,1,10,4],[13,1,13,4],[12,1,12,4],[11,1,11,4]]}
[null,{"$f":"IF(Cover!C25=\"\",\"[DNSP Name]\", Cover!C25)","v":"Powercor"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!C31=\"\",\"[Year]\",Cover!C31)","v":"2016/17"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"IF(Cover!C25=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!C25,\" must provide:\"))","v":"Powercor must provide:"}]
[]
[null,"Table 4 - Information or reporting systems"]
[null,"   (1) Name of any IT system used to collect fire start data or fault event data - i.e. SCADA system, or fault reporting system"]
[null,"   (2) Whether the fire recording or fault recording process has been audited or complies with a relevant Australian or industry standard - Yes or No"]
[null,"   (3) List any relevant Australian or industry standards that the fire recording or fault recording process complies with"]
[null,"   (4) Whether the data entered into or removed from the IT system has been audited - Yes or No"]
[]
[]
[null,"Table 4: Information or reporting systems"]
[]
[null,"Information or reporting systems","Name","System Audited","Relevant Standards"]
[null,"System 1","SAP","Yes","None"]
[null,"System 2","Outage Management System (OMS)","Yes","None"]
[null,"System 3 ","SCADA","Yes","None"]
[null,"System 4","etc"]
[null,"System 5","etc"]
[]
[null,"The SGSPAA Internal Audit function undertakes a programme of work in accordance with the SGSPAA Group Internal Audit Plan. This internal audit activity covers elements of the systems and process used for capturing, recording and maintaining fire start data."]