{"text_format":"1","workbook":"xlsx","n_sheets":5,"sheets":["Contents","Cover","1. F-Factor summary","2. Individual fire start info","3. Systems and Audit"],"not_rendered":{"charts":0,"images":2,"macros":1,"external_links":2,"defined_names":97,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Contents","index":0,"n_rows":12,"n_cols":6,"rows_kept":12,"cut":false,"hidden":false,"merged":[[8,2,9,3],[2,1,2,10],[4,1,4,10]]}
[" "]
[]
[null,"Electricity Distribution Network Service Provider\nF-factor Reporting Template"]
[]
[null,"Table of contents"]
[]
[]
[null,null,"Cover sheet",null,null,"2. Fire start report"]
[]
[]
[]
[null,null,"1. F-factor summary",null,null,"3. Systems and Audit"]

{"sheet":"Cover","index":1,"n_rows":49,"n_cols":7,"rows_kept":49,"cut":false,"hidden":false,"merged":[[26,3,26,8],[28,3,28,8],[26,1,26,2],[31,3,31,5],[14,1,14,8],[16,1,16,8],[17,1,17,8],[21,1,21,8],[19,1,19,8],[10,1,11,8],[13,1,13,8],[48,2,48,6],[42,2,42,3],[42,4,42,7],[46,2,46,6],[47,2,47,6],[38,2,38,3],[38,4,38,7],[41,2,41,3],[41,4,41,7],[37,2,37,3],[37,4,37,7],[32,3,32,8],[30,3,30,8],[15,1,15,8]]}
[]
[]
[]
[]
[]
[]
[]
[null,"Distribution Network Service Provider"]
[null,"Fire start report"]
[]
[null,"This template is to be used by a DNSP to provide a fire start report to the AER in accordance with section 5 of the F-factor Order in Council.  "]
[]
[]
[null,"Colour coding of input sheets:"]
[null,"Dark blue = AER headings"]
[null,"Grey = AER instructions"]
[null,"Yellow = Input cells"]
[null,"Light orange = Automatically-generated cells"]
[]
[null,"Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so."]
[null,"The cells and structure of the spreadsheet is locked to prevent inadvertent interference with the automated settings."]
[null,"All dollar amounts are to be unrounded, and in nominal terms."]
[]
[]
[]
[]
[null,"DNSP:",null,"Powercor"]
[]
[null,"DNSP - trading name:",null,"Powercor Australia Ltd"]
[]
[null,"DNSP - Australian business number: ",null,"ACN 064 651 109"]
[]
[null,"Reporting year:",null,"2018/19"]
[]
[]
[]
[]
[null,"Business address","Address",null,"40 Market Street"]
[null,null,"Suburb",null,"Melbourne"]
[null,null,null,"State","Victoria","Postcode",3000]
[]
[null,"Postal address","Address",null,"Locked Bag 14090"]
[null,null,"Suburb",null,"Melbourne"]
[null,null,null,"State","Victoria","Postcode",8001]
[]
[]
[null,"Contact name/s","Rachel Perlaki"]
[null,"Contact phone/s","(03) 9683 4872"]
[null,"Contact email address/s","RPERLAKI@POWERCOR.COM.AU"]

{"sheet":"1. F-Factor summary","index":2,"n_rows":14,"n_cols":15,"rows_kept":14,"cut":false,"hidden":false,"merged":[[12,2,12,3],[13,2,13,3],[6,2,6,3],[7,2,7,3],[8,2,8,3],[9,2,9,3],[10,2,10,3],[5,1,5,2],[3,6,3,8],[4,6,4,8],[5,6,5,8],[11,2,11,3]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"Powercor"},"IRU target:",{"$f":"IF(SUM(K6:O6)=0,\"\",SUM(K6:O6))","v":468},null,null,null,null,null,null,"AusNet Services","CitiPower","Jemena","Powercor","United Energy"]
[null,"F-factor data reporting","IRU amount:",{"$f":"IF(SUM('2. Individual fire start info'!S38:S2000)=0,\"\",SUM('2. Individual fire start info'!S38:S2000))","v":218.31999999999962},null,null,null,null,null,"2016/17",247.7,3.4,9.6999999999999993,468,22.3]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2018/19"},"Revenue adjustment:",{"$f":"IF(OR(D1=\"\",D2=\"\"),\"\",15000*(D1-D2))","v":3745200.0000000056},null,null,null,null,null,"2017/18",247.7,3.4,9.6999999999999993,468,22.3]
[null,null,null,null,null,null,null,null,null,"2018/19",247.7,3.4,9.6999999999999993,468,22.3]
[null,"Table 2: Summary of total fire starts by F factor Order definition",null,null,null,null,null,null,null,"2019/20",221.1,3.4,9.6999999999999993,412.8,22.3]
[null,"This is a summary of data in worksheet \"2. Fire Start Report\"",null,null,null,null,null,null,null,null,{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>K1),\"\",LOOKUP($B3,$J2:$J5,K2:K5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>L1),\"\",LOOKUP($B3,$J2:$J5,L2:L5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>M1),\"\",LOOKUP($B3,$J2:$J5,M2:M5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>N1),\"\",LOOKUP($B3,$J2:$J5,N2:N5))","v":468},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>O1),\"\",LOOKUP($B3,$J2:$J5,O2:O5))","v":""}]
[null,"Kind of Fire Start by definition of fire start under clause 5 of F-factor Order","Total fires by cause"]
[null,"Started in or originated from a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B8)","v":202}]
[null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B9)","v":17}]
[null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B10)","v":27}]
[null,"Started by lightning striking a distribution system or a part of a distribution system ",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B11)","v":15}]
[null,"Started by any other thing forming part of or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B12)","v":13}]
[null,"Otherwise started by a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B13)","v":0}]
[null,"Total",{"$f":"SUM(C8:C13)","v":274}]

{"sheet":"2. Individual fire start info","index":3,"n_rows":317,"n_cols":25,"rows_kept":317,"cut":false,"hidden":false,"merged":[[3,22,3,24],[4,22,4,24],[5,22,5,24],[7,1,7,21],[11,1,11,2],[9,1,9,21],[13,1,13,11],[22,1,22,21],[24,1,24,21],[14,1,14,20],[15,1,15,18],[16,1,16,18],[18,1,18,18],[21,1,21,18],[19,1,19,18],[23,1,23,18],[20,1,20,18],[17,1,17,18],[25,1,25,18],[27,1,27,20],[26,1,26,21],[35,19,35,21],[33,1,33,4],[35,2,35,10],[28,1,28,18],[29,1,29,18],[35,11,35,13],[35,14,35,17]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"Powercor"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2018/19"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"\"Enter into this worksheet fire start data, from any IT system, which have been recorded by \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\". Note that fire starts must be in accordance with the definition of a fire start in the Order In Council.\"","v":"Enter into this worksheet fire start data, from any IT system, which have been recorded by Powercor. Note that fire starts must be in accordance with the definition of a fire start in the Order In Council."}]
[]
[null,"\"Fire\" should be interpreted using its common meaning and can be defined as a process in which substances combine chemically with oxygen from the air and typically give out bright light, heat and smoke. A fire should be recorded where there is evidence of smoking, charring, scorching, burning or any other evidence that a fire had occurred.  "]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"Powercor must provide:"}]
[]
[null,"Table 3 - Individual Fire Starts"]
[null,"   (1) Date - dd/mm/yyyy"]
[null,"   (2) Time - if known, the 24-hour time of the fire start hh:mm"]
[null,"   (3) Latitude and longitude of the fire start as decimal coordinates"]
[null,"   (4) Address of the property on which the incident occurred or closest to the incident"]
[null,"   (5) Asset number for the asset nearest the fire start"]
[null,{"$f":"\"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the \"&B1&\" network\"","v":"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the Powercor network"}]
[null,"   (7) Voltage on the line in which the fire start occurred (note: this may not be the nearest polyphase overhead line)"]
[null,"   (8) Network categorisation - CBD, Urban, Rural Long or Rural Short"]
[null,"   (9) Asset type of primary asset causing fire in accordance with OSIRIS asset categories"]
[null,"   (10) Where the asset involved in the fire is a transformer or an overhead or underground line, provide the phase, or phases, of the line or transformer"]
[null,"   (11) Kind of fire start in accordance with categories specified in Clause 5 of the F-factor Order-In-Council"]
[null,"   (12) Identify the location of the fire start in accordance with the categories specified in Clause 11(b) of the F-factor Order-In-Council"]
[null,"   (13) Provide the BOM fire danger rating applicable at the time of the fire start (data is available on the EM-COP website)"]
[null,{"$f":"\"   (14) \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\"'s record number for the incident\"","v":"   (14) Powercor's record number for the incident"}]
[null,"   (15) ESV's OSIRIS reference number for the incident"]
[null,"   (16) Free text description of the fault containing relevant comments from field reports "]
[]
[]
[]
[null,"Table 2: Individual Fire Starts"]
[]
[null,"Number","Fire starts",null,null,null,null,null,null,null,null,"Fire Type",null,null,"Risk Factors",null,null,null,"IRU \namount","Additional information"]
[null,null,"Date 1","Time 2","Latitude 3","Longitude 3","Address of incident 4","ID of \nnearest \nasset 5","ID of nearest \npolyphase \nline 6","Voltage of line in which \nfire start \noccurred 7","Network categorisation 8","Type of primary asset \ninvolved in fire start 9","Phase(s) of \nline or \ntransformer 10","Kind of fire start as per Clause 5\nof F-factor Order-In-Council 11","Location \narea 12","Location\nmultiplier","Fire \ndanger \nrating 13","Danger multiplier","Product of multipliers","DNSP record number 14","OSIRIS \n(ESV) reference \nnumber 15","Fault \ndescription 16"]
[{"$f":"COUNTA(C38:O38,Q38,T38:V38)","v":17},1,"04/07/2018","03:52","-37.41143132","144.59226608","124 Brougham Road, Mount Macedon 3441",32043129,"GSB014","22kV AC","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O38=\"\",\"\",IF(O38=\"LBRA only\",0.2,IF(O38=\"HBRA only\",1,IF(O38=\"within electric line construction area\",19.8,IF(O38=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"No forecast",{"$f":"IF(Q38=\"\",\"\",IF(Q38=\"No forecast\",0.1,IF(Q38=\"Low-moderate\",0.2,IF(Q38=\"High\",0.5,IF(Q38=\"Very high\",1,IF(Q38=\"Severe\",2,IF(Q38=\"Extreme\",3.5,5)))))))","v":0.1},{"$f":"IF(OR(P38=\"\",R38=\"\"),\"\",IF(AND(O38=\"within electric line construction area\",Q38=\"No forecast\"),1,P38*R38))","v":0.45999999999999996},"INC-0002704","20180705PWA_01","Customer reported wire down and grass fire at incident location and CFA attended to control 10m x 5m grass fire. \nAttending crew found a HV conductor had been brought down by a tree branch starting the fire.\nNo injuries or property damage.",null,null,"Overhead conductors"]
[17,2,"05/07/2018","20:57","-36.25063049","141.50053419","1860 Nhill-Yanac Road, Nhill","32107074","NHL031","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0002707","20180706PWA_01 ","Vic Fire reported a transformer on fire at the incident location.  On arrival the crew found the end of a 22kV strain crossarm had burned off and HV conductors were on the ground.\nThere was no ground fire. no reported injuries or third party property damage.",null,null," - overhead conductor (bare; aluminium core steel reinforced)"]
[17,3,"08/07/2018","21:55","-34.77838000","142.65146000","3794B HATTAH-ROBINVALE ROAD, WEMEN 3549",30099965,"WMN013","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0002718","20180710PWA_01 ","Customer reported a low conductor at the incident location.\nOn arrival the crew found that a wooden intermediate cross-arm failed due to fire damage at a EDO fuse unit mounting position.\nconductor was adrift but remained suspended 4.0M above the ground.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - overhead conductor (bare; all aluminium conductor)"]
[17,4,"09/07/2018","05:52","-35.39086267","142.68413991","Off Patchewollock - Sea Lake rd, Nyarrin","30549570","OYN005","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0004233","20190212PWA_02 ","Following a line outage patrol found a pole fire at the incident location.\nThere was no ground fire, no reported injuries or third party property damage",null,null," - overhead conductor (bare; copper)"]
[17,5,"09/07/2018","08:48","-38.32014399","141.59648569","632 HENTY HIGHWAY, PORTLAND NORTH VIC 3305","33056439","PLD004","Low voltage AC (<1kV)","Rural Short"," - luminaires (major road)","single phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0002711","20180712PWA_03 ","Vic Fire reported a pole fire at the incident location. \nUpon arrival, the Powercor crew found that the street light caught fire at the incident location\nThere was no ground fire, no reported injuries or third party property damage",null,null," - overhead conductor (bare; steel)"]
[17,6,"09/07/2018","03:10","-34.24964943","142.20837013","3296 FOURTEENTH STREET, IRYMPLE VIC 3498","30098208","RCT021","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0002719","20180710PWA_02 ","Customer reported a low conductor and pole fire at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - overhead conductor (ABC)"]
[17,7,"12/07/2018","09:12","-38.25509991","141.62468009","10 SEGTNAN COURT HEATHMERE VIC 3305 (BOLWARRA)","33204908","PLD001","Low voltage AC (<1kV)","Rural Long"," - fuse (any other type)","single phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0004245","20190213PWA_02 ","REC reported meter board fire due to burn fuse.\nThere was no reported injuries",null,null," - overhead conductor (covered uninsulated)"]
[17,8,"12/07/2018","08:52","-37.73599693","141.23970250","185 Uptons Road, Strathdownie ","32134589","HTN002","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0002756","20180718PWA_06 ","Customer reported Pole Fire at Myaring P43, HTN002. \nCrew attended and confirmed incident .\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - overhead conductor (insulated)"]
[17,9,"17/07/2018","10:40","-38.33586304","143.60684439","2 Forest St Colac East","32064073","CLC003","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0002755","20180718PWA_05 ","A Powercor contractor, Electrix, reported a P1 fault that was a pole fire at the incident location. \nUpon arrival, the Powercor crew found that the cross arm had been burnt through some time ago\nThere was no ground fire, no reported injuries or third party property damage.",null,null,"Service lines"]
[17,10,"17/07/2018","12:50","-37.69976944","143.07487645","3399 Woorndoo Streantham Rd Streantham",30356380,"ART033","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0002749","20180718PWA_01 ","A passer-by advised a ground fire at the incident location.\n On arrival the Powercor crew found that a HV conductor lying on the ground.\nThere was a ground fire, no reported injuries.",null,null," - overhead service conductor (residential)"]
[17,11,"20/07/2018","10:13","-36.58119430","145.00326633","115 Moora Rd, Rushworth",30127332,"SHP014","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0002779","20180723PWA_01 ","Crew attended a reported supply outage.\nThey found the HV EDO tube had candled and fallen to the ground.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - overhead service conductor (commercial / industrial)"]
[17,12,"20/07/2018","07:35","-35.25506407","141.58778429","710 Boinka South Rd, Boinka","32140466","OYN001","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0002780","20180723PWA_02","Customer reports outage and pole in paddock on ground. \ncrew attended and found P35 Boinka Sth S/L on ground, burnt off at butt. \nThere was no reports of injuries or third party property damage.",null,null," - overhead service conductor (subdivision / construction)"]
[17,13,"22/07/2018","12:32","-38.18116","144.570648","O/S 14 Buccleugh St, Drysdale","30065961","DDL013","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0002783","20180723PWA_04 ","A customer reported a pole fire at incident location.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - overhead service conductor (other)"]
[17,14,"28/07/2018","13:09","-38.27265139","144.61929393","18 Nelson Rd, Pt Lonsdale 3225","33044427","DDL012","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0002850","20180802PWA_01 ","Customers reported to Powercor \"dim lights and motor driven appliances struggling to work\". \nWhen crews arrived they found a EDO fuse carrier had candled on pole type transformer at the incident location.\nNo evidence of ground fire was found. No injuries or 3rd party property damage was reported.",null,null," - underground service cable (residential)"]
[17,15,"04/08/2018","15:55","-38.37690879","142.46892477","312 Koroit St, Warrnambool","30283657","WBL004","22kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0002967","20180820PWA_02 ","CFA reports a pole fire at the incident location.\nThe crew identified a pole fire had occurred at switch pole 19B\nThe site was safe and no ground fire, injuries or shocks were reported.",null,null," - underground service cable (commercial / industrial)"]
[17,16,"06/08/2018","05:37","-37.86059362","144.80030916","9 & 53 Slough Road  Altona & surrounds ,VIC,3018, ","30141768","AL011","11kV AC","Urban"," - dropper / bridge","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0002871","20180807PWA_01","A customer reported  an explosion from power pole outside 9 Slough rd Altona.\nOn arrival the crew found a possum had bridged across 11kv connections damaging cable termination.\n\nThe fault current caused a HV conductor bridge to burn off  nearby ( LIS 934164 53-65 Slough st)) falling particles ignited a grass fire at the base of the pole. \n\nFault current damage was also sustained to islolators at pole ( Lis 1777) outside 2 Ajax rd altona, hot debris caused minor damage to a number of cars.\n\nThere was no reported injuries.",null,null," - underground service cable (subdivision / construction)"]
[17,17,"10/08/2018","11:11","-34.31611439","142.18631761","147 Jacaranda St, Red cliffs","31019705","RCT023","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,{"$f":"IF(OR(P54=\"\",R54=\"\"),\"\",IF(AND(O54=\"within electric line construction area\",Q54=\"No forecast\"),1,P54*R54))","v":2.0000000000000004E-2},"INC-0002940","20180815PWA_03 ","Customer reported conductor laying on crossarm, at incident location.\nA crew attended and found a previous crossarm fire had occurs at incident location\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - underground service cable (other)"]
[17,18,"15/08/2018","01:53","-37.44235538","144.60507472","212 Baringo Road, New Gisborne, 3438. south off this address in nature strip.",33023842,"GSB012","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0002937","20180815PWA_02 ","A  Tree fell across conductors Between poles 9 and 10 of the water trust  spur line.\nThe conductors contacted the ground causing a 20 square metre grass fire.\nThere were no reported injuries.",null,null,"Underground cables"]
[17,19,"19/08/2018","12:59","-37.57985742","143.92401287","25 Stokes Road, Warrenheip","32002534","BATS-BAS2","66kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0002968","20180820PWA_03","Vic Fire  reported sparking coming from pole, with broken insulator resting on the crossarm at the incident location .\nOn arrival crew found that the centre phase 66kV insulator pin has sheared off at the \"P\" bracket, allowing the insulator with conductor attached to fall.  \nThe conductor fell and lay on the steel crossarm.\nThe hanging insulator brushed the wood pole and burned the pole, requiring it to be replaced.\nThere was no ground fire or any other damage caused by this incident.",null,null," - underground cable"]
[17,20,"24/08/2018","09:23","-34.18934098","142.14990775","168 Thirteenth st, Mildura","32140356","MDA032","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0004255","20190213PWA_05 ","During patrol crew found burnt crossarm\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - underground communications cable"]
[17,21,"01/09/2018","22:55","-36.66834926","144.15614404","394 Vosti Rd Woodvale Vic 3556","33017991","EHK024","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within electric line construction area",19.8,"No forecast",0.1,1,"INC-0003056","20180903PWA_01 ","CFA and landowner reported flames and smoke coming from pole.\nOn arrival, crew found a junction box had melted and a small patch of burnt ground at the base of the pole, approx. 30cm x 30cm.\nThere was no reported injuries or third party property damage.",null,null,"Poles"]
[{"$f":"COUNTA(C59:O59,Q59,T59:V59)","v":17},22,"2019-06-13","07:56:00",-38.461811089999998,142.97626321999999,"127 BROWNS ROAD, TIMBOON VIC 3268",33036205,"TRG003","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O59=\"\",\"\",IF(O59=\"LBRA only\",0.2,IF(O59=\"HBRA only\",1,IF(O59=\"within electric line construction area\",19.8,IF(O59=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"No forecast",0.1,{"$f":"IF(OR(P59=\"\",R59=\"\"),\"\",IF(AND(O59=\"within electric line construction area\",Q59=\"No forecast\"),1,P59*R59))","v":0.45999999999999996},"INC-0007102","20190819PWA_06 ","A customer reported a HV cable on the ground at the incident location. Upon arrival, a crew found that a large tree fell on to HV conductor and the conductor on the ground and a service line. An inspector was called as passible back fed HVI. However no damage or injuries found. ",null,null," - pole (concrete)"]
[17,23,"04/09/2018","14:07","-36.33303483","145.43177304","Corner of Grahamvale & Northey Rd's Grahamvale 3631",30305074,"SHN024","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0003071","20180905PWA_02 ","A pelican struck conductors, breaking conductors and initiating a small grass fire.\nThere was no reported injuries or third party property damage.",null,null," - pole (steel)"]
[17,24,"07/09/2018","23:00","-37.28275197","142.93509007","83 High St Ararat","30339108","ART031","Low voltage AC (<1kV)","Rural Short"," - fuse (any other type)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0003115","20180911PWA_02 ","Report received of fuse on meter panel was smoking and sparking which has since stopped.\nOn arrival crew found meter board fuse had melted and evidence of burning on meter board.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - pole (wood)"]
[17,25,"12/09/2018","10:00","-37.69902","143.558975","49 Linton-Naringhil Road, Linton.3360. ",30009044,"BAS021","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0003148","20180913PWA_02 ","A tree fell down across conductors between Lintonpark P1 & P2. \nThe conductor on the ground has caused grass and dead tree to ignite resulting in a small fire about 3m2 area burnt.\nThere was no injuries reported.",null,null,"Crossarms"]
[17,26,"12/09/2018","05:30",-37.705128649999999,143.98087308999999,"6206 Midland Highway, Clarendon, 3352.",31037826,"BAS022","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0003150","20180913PWA_01 ","A new wooden pole was erected mid-span between Buninyong-P211 and P211A .\nDuring the night strong winds have pushed conductors against this pole (conductors had not yet been tied to insulators  / pole undressed) resulting in pole catching  fire.\nThere was no ground fire and no injuries as a result of this incident.",null,null," - crossarm (wood)"]
[17,27,"14/09/2018","18:17","-37.65620324","144.46394920","100 Oconnell Road, Merrimu, 3340","33072519","BMH006","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0003157","20180918PWA_01 ","A passerby reported pole in front of this premise is on fire.\nUpon arrival the crew had found that the Pole Box/FOLCB opposite, 100 Oconnell Road, Merrimu, had overheated, causing the FOLCB to melt and burn away.\nThe resultant hot melted plastic from the FOLCB above had fallen onto the ground  below causing a small grass fire near the base of the pole approximately 50m² total area.\nThere was no reported injuries or third party property damage.",null,null," - crossarm (steel)"]
[17,28,"16/09/2018","20:13","-38.32622583","144.32369113","45 Fischer Street Torquay","32087132","WPD032","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0003214","20180926PWA_01 ","CFA communications reported a pole fire. Attending crew found that a pole mounted LV fuse box had overheated  \nThere was no ground fire, no reported injuries or third party property damage.",null,null," - crossarm (other)"]
[17,29,"18/09/2018","21:28","-35.18596789","143.26389804","Chinkapook - Nyah W, Nyrraby","32155442","SHL002","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0004266","20190213PWA_06 ","During outage crew located a pole fire at pole 88 Manangatang line\nThere was no ground fire, no reported injuries or third party property damage.",null,null,"Overhead assets"]
[17,30,"18/09/2018","21:39","-35.25154000","143.53665000","335 Tyntynder Central Rd, Tyntynder VIC 3586","32156894","SHL004","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0003177","20180920PWA_03 ","Vic-fire reported pole fire at incident location, upon arrival found that a cross-arm fire had commenced at the HV kingbolt position of an intermediate substation pole.\n The CFA extinguished the fire using an interrupted spray, stopping the fire prior to the cross-arm failing.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - capacity balancing units"]
[17,31,"20/09/2018","19:15","-36.75843542","144.26826556","Corner of Don and Barnard Street BENDIGO (202 Don st )","30026909","BET002","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0003231","20180927PWA_02 ","Emergency services reported a pole fire at incident location.\nOn arrival crew found overheated LV connection had ignited part of the pole top..\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - connector / termination"]
[17,32,"23/09/2018","06:54","-36.78065789","144.56728935","256 KNOWSLEY BARNADOWN ROAD, KNOWSLEY, VIC, 3551","30040888","BGO023","Low voltage AC (<1kV)","Rural Long"," - fuse (any other type)","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0003247","20181002PWA_02 ","Customer reported fire in meter box.\nOn arrival crew found fire out and damage to meter board and fuse unit.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - dropper / bridge"]
[17,33,"24/09/2018","08:37",-37.82253171,144.83444623,"19 Paw Paw Rd  Brooklyn",30117783,"BLT016","22kV AC","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0003241","20181001PWA_02 ","Report from Fire services of pole fire and bin fire.\nThere was also damage to a vehicle parked at the kerb.\nThere was a ground fire (bin) . no reported injuries.",null,null," - guy wire"]
[17,34,"28/09/2018","17:40","-36.92647350","144.68757308","51 Chapmans Lane, Heathcote VIC 3523","33031625","BGO023","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0003284","20181008PWA_02 ","Customer reported supply interruption, upon arrival crew found that a EDO fuse tube had candled and burnt through.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - insulator tie wires / connections"]
[17,35,"03/10/2018","18:21","-35.04164144","143.32383943","3566 Murray Valley Hwy, Piangil VIC 3596",32157328,"SHL002","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0003308","20181012PWA_01 ","A passer-by reported arcing and some intermittent flame from a small branch blown into conductors at incident location.\nOn arrival there was no evidence of ground fire, minor charring found on branch.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - insulators"]
[17,36,"04/10/2018","18:34","-37.68295474","144.58325150","318 HIGH STREET,MELTON,VIC,3337",30102707,"MLN023","Low voltage AC (<1kV)","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0003321","20181015PWA_04 ","Customer, from 298 High street Melton, reported a pole fire at the incident location.  \nOn arrival the crew found that an Low Voltage Insulated Piercing Connectors (IPC) had overheated resulting in burning of the IPC and the LV ABC bridge into the krone box.\nThere was a small fire on the pole but had self-extinguished.\nThere was no reported injuries or third party property damage.",null,null," - tower"]
[17,37,"05/10/2018","10:15","-37.8797646","144.733322","7 Chinook Way Point Cook  3030","34030537","LV010","Low voltage AC (<1kV)","Urban"," - LV pillar","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0003278","20181005PWA_02 ","Lend Lease employee reported a fire at the incident location, Upon arrival the crew found that the LV pillar partially burnt out. \nThe fire was extinguished by the caller. \nThe crew also observed that the pillar had been struck by a third party vehicle but no details are available.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - traction lines"]
[17,38,"06/10/2018","12:00","-38.25295099","142.46596098","1351 WARRNAMBOOL-CARAMUT ROAD WINSLOW 3281",32198425,"KRT012","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,{"$f":"IF(OR(P75=\"\",R75=\"\"),\"\",IF(AND(O75=\"within electric line construction area\",Q75=\"No forecast\"),1,P75*R75))","v":0.91999999999999993},"INC-0003282","20181008PWA_01 ","Powercor received a report that  a wire had been brought down by a truck. The attending crew found that  a tip truck had contacted a  HV line  and had brought down the centre phase conductor.",null,null,"Underground assets"]
[{"$f":"COUNTA(C76:O76,Q76,T76:V76)","v":17},39,"07/10/2018","11:07",-37.943009269999997,144.67395644999999,"400 K ROAD WERRIBEE SOUTH 3030","32171538","WBE034","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O76=\"\",\"\",IF(O76=\"LBRA only\",0.2,IF(O76=\"HBRA only\",1,IF(O76=\"within electric line construction area\",19.8,IF(O76=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"Low-moderate",{"$f":"IF(Q76=\"\",\"\",IF(Q76=\"No forecast\",0.1,IF(Q76=\"Low-moderate\",0.2,IF(Q76=\"High\",0.5,IF(Q76=\"Very high\",1,IF(Q76=\"Severe\",2,IF(Q76=\"Extreme\",3.5,5)))))))","v":0.2},4.0000000000000008E-2,"INC-0004530","20190613PWA_02 ","HV Fuse candled and caught fire. \nFire incident found during outage data review.\nNo ground fire",null,null," - LV pillar"]
[17,40,"08/10/2018","09:43","-37.92709600","144.15650041","482 Maude-She Oak Rd Maude","30070761","GL015","22kV AC","Rural Long"," - pole (concrete)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0003290","20181009PWA_02 ","An excavator hit power pole resulting clashing conductors in side the quarry near the incident location.\nUpon arrival the crew found that the broken conductors had  fallen  to the ground resulting in a small grass fire.\nCFA attended the site.\nThere were no reported injuries or third party property damage.",null,null," - services pit"]
[17,41,"08/10/2018","13:31","-37.76324822","144.62177495"," 231-239 Faulkners rd. Mount Cottrell 3024","32167519","MLN011","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0003298","20181010PWA_01","Customers at incident location reported loss of supply.\nOn arrival a field crew found that a FSD had overheated and melted.\nBurning debris fell to ground and caused a small grass fire which self extinguished.\nThere was no reported injuries or third party property damaged.",null,null,"Transformers"]
[17,42,"09/10/2018","13:52",-36.947633019999998,141.62485376000001,"7332 Nhill-Harrow Rd, Miga Lake VIC 3409","32095476","HSM004","12.7kV AC (SWER)","Rural Long"," - fuse (EDO fuse)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0004531","20190613PWA_03 ","Candled EDO fuse (fire).\nFire incident found during outage data review .\nNo ground fire",null,null," - transformer (pole mounted)"]
[17,43,"09/10/2018","19:39","-35.24701225","143.47134948","171 GOODMAN ROAD, WOORINEN, VIC, 3589","32160058","SHL004","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0003301","20181011PWA_01 ","Vic fire reported a pole fire at incident location.\nThe crossarm broke resulting in a small ground fire.\nThere was no injuries or third party property damage.",null,null," - transformer (kiosk mounted)"]
[17,44,"10/10/2018","14:46","-36.14416189","145.54419106","690 Invergordon Rd Invergordon","30150931","NKA001","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0003329","20181016PWA_02 ","Vic Fire reported a pole fire at the incident location. \nUpon arrival, the crew found that the substation pole ignited and burnt at bridging insulator.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - transformer (ground outdoor mounted)"]
[17,45,"12/10/2018","12:33","-37.24809449","143.96003723","60 Stoney Rises Rd Smeaton VIC 3364.","30000141","BAN009","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0003311","20181012PWA_02 ","An employ of Tuki Trout farm phoned in to report fire on the substation pole which supplies the trout farm. \nCrew attended to find a burnt out low voltage junction box, fire had self extinguished.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - transformer (indoor chamber mounted)"]
[17,46,"22/10/2018","12:32","-37.84869800","144.78090000","60 - Harcourt Road, Altona,  ","30236687","LVN022","22kV AC","Urban"," - overhead conductor (ABC)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0003373","20181023PWA_01 ","A fault on the LVN22 feeder at 12:32 caused a feeder trip. \nA grass fire adjacent to pole LIS 994554 outside 70-72 Harcort Road, Altona  was  ignited when a high voltage ABC overhead cable (Non-metallic screened) faulted, then to fell onto the ground. \n There was no reported injuries or third party property damage.",null,null," - transformer (any other type)"]
[17,47,"22/10/2018","12:32","-37.84461341","144.78841066","Kororoit Creek Rd Altona, Victoria (270 mtrs east of princes freeway)",32173435,"LVN022","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0003374","20181023PWA_02","An ABC conductor faulted and fell to ground outside 60 - Harcort Road, Altona.\nSecondary fault currents caused clashing of conductors adjacent to Kororoit creek rd which ignited two small grass fires on the nature strip.\nThere was no reported injuries or third party property damage.",null,null," - measurement transformer (current transformer)"]
[17,48,"30/10/2018","20:03","-36.28133319","143.35581064","Intersection of Watson Street and Back Street on St Arnaud Road, Charlton","33015547","CTN006","22kV AC","Rural Long"," - crossarm (steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0003430","20181031PWA_03 ","Vic fire reported small grass fire at incident location.\nOn arrival crew found a bird has flashed over on ACR structure and fallen to ground igniting grass.\nthere was no injuries or reported third party property damage",null,null," - measurement transformer (voltage transformer)"]
[17,49,"31/10/2018","16:30","-37.5737648","143.859512","617 Laurie st,  Golden Point (Ballarat)","32006305","BAS023","Low voltage AC (<1kV)","Rural Short"," - underground cable","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0003441","20181102PWA_01 ","Vic Fire reported wires sparking  at the above address, on arrival the crew found a LV paper lead Cable head had failed, \nThere was a small ground fire <1sqm,  no reported injuries, or third party property damage.",null,null," - measurement transformer (capacitive voltage transformer)"]
[17,50,"01/11/2018","15:02","-37.75908209","144.80105961","273-275 Furlong Road, St Albans",30115067,"SU012","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0003442","20181102PWA_02 ","Powercor crews working only about 200m from the incident location heard a loud electrical noise and went to investigate. \nOn arrival the crew found that a truck with a high load had contacted several communications cables in the street, with one cable flicking back over the 22kV HV overhead conductors.\nThis then resulted in a small grassfire of approx. 10m2 on the nature strip.\nThere were no reported injuries.",null,null,"Fuses and switchgear"]
[17,51,"01/11/2018","20:50","-37.49718529","142.84656962","Mortlake Ararat Road, near Malim Road, Rossbridge",33049204,"ART033","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0003453","20181102PWA_04 ","Vic Fire reported a grass fire at the incident location.\nOn arrival the fault crew found that a bird had flashed over a 22kV insulator, attached to a steel crossarm on a concrete pole.",null,null," - fuse (boric acid)"]
[17,52,"01/11/2018","14:20","-37.59870299","143.83131882","144 Grant Street, Sebastopol",33003486,"BAS022","Low voltage AC (<1kV)","Rural Long"," - overhead conductor (ABC)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0003454","20181102PWA_05 ","Following a report a fault crew attended the incident location. \nOn arrival the crew found that Low Voltage flying bridges had failed causing sparks to drop into the grass on the edge of the road, igniting a small grass fire - in to order of 4 square  meters.  \nThere were no injuries or any other damage. The fire had extinguished when the fault crew arrived.",null,null," - fuse (EDO fuse)"]
[17,53,"01/11/2018","17:16","-37.34672745","143.40852017","450 Chute  Waterloo Road, Waterloo",30012734,"BAS011","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0003445","20181102PWA_03 ","Vic Fire reported a wire down and a grass fire at the incident location. \nOn arrival the fault crew found that a cypress tree had fallen over HV conductors, which made contact with a post & wire fence, starting a grass fire - estimated at 4,000 square meters. The fire had been extinguished by the CFA when the fault crew arrived.\nThere were no injuries or any other damage reported.",null,null," - fuse (Fault Tamer)"]
[17,54,"02/11/2018","20:29","-35.93294300","143.92402000","2221 LODDON VALLEY HWY - MACORNA","31005685","KGT003","Earthing cable","Rural Long"," - earth / earthing","single phase","Started in or originated from a distribution system","HBRA only",1,"Severe",2,2,"INC-0003478","20181108PWA_01 ","A customer reported fire at base of pole.\nOn arrival crew found that their was a small fire near the base of a SWER substation.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - fuse (powder filled)"]
[17,55,"06/11/2018","06:39","-34.59853500","142.78926000","32 Smith rd - Robinvale","30095478","RVL001","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0003484","20181109PWA_02 ","Customers reported power failure.\nDuring patrol of line crew found a HV crossarm burnt off at incident location.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - fuse (any other type)"]
[17,56,"06/11/2018","09:48","-37.54321073","143.85207689","3 Wood St, Ballarat","30327257","BAN013","22kV AC","Urban"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0003491","20181109PWA_05 ","Vicfire reported a connection on fire at the incident location.\nOn arrival the crew found that a HV insulated lead had contacted a surge diverter on the transformer, resulting in the lead catching fire.  \nThere was no ground fire,  no reported injuries or third party property damage.",null,null," - circuit breaker"]
[17,57,"06/11/2018","06:48","-37.70086781","144.41674232","89 Kerrs Road Maddingley","32175165","BMH006","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0003488","20181109PWA_04 ","Report received from a passerby of transformer fire on a pole. \nOn arrival the fault crew found the centre 22kV crossarm  had burnt through.\nThere was no ground fire, no reported injuries or third party property damage..",null,null," - switch (disconnector/isolator)"]
[17,58,"09/11/2018","07:50","-37.29107456","144.51763630","22 Clerk Road, Carlsruhe, 3442. ","33108788","WND023","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0003486","20181109PWA_03 ","Vic fire attended this address and extinguished a fire on the pole and on the surrounding grass where burning debris had landed. \nCrew attended to find that the low voltage FOLCB had been burnt out,.\nThere were no reported injuries.",null,null," - switch (earth)"]
[17,59,"09/11/2018","11:00","-38.28784818","144.33872223"," Blackgate Road Mount Duneed 3217 (near Surf Coast Road)","32072179","WPD022","22kV AC","Rural Short"," - pole (wood)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0003495","20181112PWA_01 ","Vic Fire reported wires down causing grass fire.\nOn arrival at incident location crew found a vehicle registration No. YEU 948 had collided with LIS 33540 (Pole 6) knocking it down.\nA small grass fire started,",null,null," - switch (FuseSaver)"]
[17,60,"12/11/2018","14:55","-37.58316774","143.86438452","Elsworth Street W, Golden Point","33002388","BAS013","22kV AC","Rural Short"," - fuse (boric acid)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0003501","20181113PWA_01 ","Powercor received a call from the CFA that a fire had started at the rear of the Soverign Hill complex by a Powercor Pole.\nA crew attended and determined that a bird had flashed over on a Boric Acid fuse unit.\nThe bird fell to the ground starting a small ground fire (10 x 30 mtrs).\nThere was no injuries or third party property damage.",null,null," - switch (any other type)"]
[17,61,"12/11/2018","19:17","-38.20066","144.312775","179-193 COLAC ROAD GROVEDALE 3216",30068071,"WPD012","22kV AC","Urban"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0003503","20181113PWA_02 ","CFA reported wire down and arcing and sparking.\nOn arrival crew found that a HV ampac connection had over heated.\nHot debris fell to ground resulting in a small grassfire (60m2)",null,null,"SCADA, network control and protection systems"]
[17,62,"13/11/2018","08:52","-37.23521021","142.20478758","6502 Heny Highway Glenisla","30553863","HSM002","Earthing cable","Rural Long"," - earth / earthing","single phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0004372","20190220PWA_03 ","Customer reported Power pole smoking heavily at bottom of pole and burnt at top of pole.\nOn arrival crew found SWER earthing was damaged.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - audio frequency load controller (AFLC)"]
[17,63,"13/11/2018","22:58","-35.77806600","143.89248000","427 Old Kerang Rd, Kerang, VIC 3579","30025444","KGT004","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0003537","20181119PWA_03 ","Following on from a feeder operation to lockout a crew found a pole fire had occurred at the incident location.\nThe crossarm had burnt through allowing the conductor to fall to ground.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - arc suppresion coil"]
[17,64,"13/11/2018","21:51","-35.31009800","143.52459000","174 Bish Rd, Murrawee, VIC 3586","32161431","SHL004","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0003535","20181119PWA_01 ","Customer reported a pole fire at the incident location.\nUpon arrival the fault crew found that a 3 phase intermediate substation pole had a pole fire which burnt the intermediate crossarm.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - automatic circuit recloser (ACR)"]
[17,65,"13/11/2018","20:50","-35.01621400","143.31255000","4686 MURRAY VALLEY HIGHWAY, Piangil VIC 3597","32157511","BBD014","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0003536","20181119PWA_02 ","Vicfire report pole fire near the incident location.\nUpon arrival fault crew found a pole fire had occurred, the pole had burnt internally.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - communications linear assets"]
[17,66,"14/11/2018","09:59","-38.25075899","142.91831440","19 CEMETERY ROAD TERANG 3264","32058085","TRG005","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0003610","20181129PWA_02","Vic Fire reported a pole fire at the incident location.\n Upon arrival, the crew found that the LV junction box on the pole caught fire.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - communications network assets"]
[17,67,"16/11/2018","03:19","-37.06664960","143.89371157","3080 Pyrenees Highway Moolort 3465",30023598,"MRO007","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0003525","20181116PWA_01 ","Vic Fire reported grass fire and wire down at incident location.\nCrew found that the centre phase HV copper conductor had broken mid span at sleeve.\nThere was a small grass fire (520 sqm), no reported injuries or third party property damage.",null,null," - communications site infrastructure"]
[17,68,"20/11/2018","15:10","-36.09901948","145.39824563","1750 WALSHS BRIDGE ROAD NUMURKAH 3636.  (Pole northeast of this property.)","33087281","NKA002","22kV AC","Rural Long"," - pole (concrete)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"High",0.5,0.5,"INC-0003549","20181121PWA_01 ","Vicfire reported grass fire under pole at the incident location. Grass fire has been extinguished.\nPowercor fault crew found lightning had struck the overhead 22kV line causing damage to the pole top assets, debris from the strike has fallen onto grass igniting a small fire.\nThere was no reported injuries, no third party property damage.",null,null," - field devices"]
[17,69,"20/11/2018","14:04","-36.19539968","144.91376988","7840 Murray Valley Hwy Koyuga 3622",30125489,"KYM-ECA2","66kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"High",0.5,0.1,"INC-0003550","20181121PWA_02 ","Vic Fire reported a grass fire at the incident location.\nUpon arrival, the fault crew found that the power pole top( LIS 26100) had been struck by lightning. \nThe fallen debris caused small grass fire (10Sqm).\nThere were no reported injuries or third party property damage.",null,null," - local network wiring assets"]
[17,70,"25/11/2018","07:24","-38.29307251","143.16051599","527 Tesbury Road, Tesbury","33036162","CDN002","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,{"$f":"IF(OR(P107=\"\",R107=\"\"),\"\",IF(AND(O107=\"within electric line construction area\",Q107=\"No forecast\"),1,P107*R107))","v":0.91999999999999993},"INC-0003611","20181129PWA_03 ","Report received of pole fire at incident location.\nOn arrival crew found burnt out FSD.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - master station assets"]
[17,71,"26/11/2018","11:48",-36.052731229999999,145.349884,"1421 Boals Rd Numurkah",30347324,"NKA006","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0003590","20181127PWA_01 ","Vic Fire reported a grass fire at incident location.\nOn arrival crew found wind blown fencing material had struck line causing fire.\nThere were no injuries or third party property damage.",null,null," - neutral earthing resistor"]
[17,72,"29/11/2018","04:58","-37.84962044","144.84401913","350 MILLERS ROAD ALTONA NORTH 3025",30116049,"BLTS-AL","66kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0003609","20181129PWA_01 ","Vic Fire reported pole on fire near the intersection of Millers Road and Kororoit Creek Road.\nOn arrival the crew found that a pole fire at the base of the 66kV center phase bridging insulator on pole LIS 5414 had caused it to break of and fall onto the cross-arm causing a 66kV line reclose. \nThere was no ground fire, no reported injuries or third party property damage.",null,null," - oil-filled circuit recloser (OCR)"]
[17,73,"01/12/2018","15:47","-38.33736491","143.35766156","2103 Princes Hwy, SWAN MARSH 3249","30046605","CDN002","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (other)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within electric line construction area",19.8,"Very high",1,19.8,"INC-0003615","20181203PWA_01 ","Vic Fire reported a grass fire at the above incident location.\nWhen crews arrived they found a OH Service wire was in contact (rubbing) with a branch.\nA small grass fire had started on road reserve (4x 55m).\nthere was no injuries or property damage reported.",null,null," - rapid earth fault current limiter (REFCL)"]
[17,74,"02/12/2018","12:38","-35.88844759","144.24956795","660 Kerang-Leitchville Road Leitchville VIC 3567 [300m West of Pipers Road Leitchville]",33021808,"CHA005","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0003648","20181205PWA_01 ","A CFA inspector reported that at an  unknown date it appears a bird flashed over on concrete pole substation at the incident location.\nThe bird fell to ground igniting road side grass.\nThere was no reported injuries or third party property damage.",null,null," - surge diverter"]
[17,75,"05/12/2018","19:16","-36.40046258","144.23008989","9 Hocking Road Dingee","32040819","EHK024","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0003664","20181206PWA_02 ","Vic Fire Reports small grass fire caused by sparks from pole at incident location.\nOn arrival crew found small ground fire caused by a burn out porcelain fuse box.\nThere was no injuries or third party property damage.",null,null," - voltage regulator"]
[17,76,"06/12/2018","16:04","-38.26054680","144.52450366","37 PRESIDENTS AVENUE,OCEAN GROVE,VIC,3226","33042035","DDL011","22kV AC","Rural Short"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0003678","20181210PWA_02 ","VICFIRE reported transformer on fire at this address. Attending crew found that HV insulated leads had overheated.  No ground fire.",null,null,"Public lighting"]
[17,77,"06/12/2018","16:19","-37.92800585","144.64857638","215 Farm Road, Cocoroc, 3030 (Approx. 500m south of Princes Freeway)","30143067","WBE024","22kV AC","Urban"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0003687","20181210PWA_01 ","Grass fire occurred within the Werribee Treatment Plant near HV Gas Switch. The resultant fault-current ruptured a connection on the incoming underground cable interface and a grass fire was ignited.",null,null," - brackets (major road)"]
[17,78,"08/12/2018","20:37",-38.171188039999997,144.32337261999999,"2 HARRISON COURT, HIGHTON ,VIC,3216","30225004","WPD011","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (other)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0004532","20190613PWA_04 ","Pole top fire due to service line failure.\nIncident found during outage data review.\nNo ground fire",null,null," - brackets (minor road)"]
[17,79,"09/12/2018","01:11",-37.721851559999998,144.83436259999999,"20 CHURCH STREET,KEILOR,VIC,3036","31023832","SA002","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (other)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0004534","20190613PWA_05","Tree fire due to tree rubbing on service line. \nIncident found in during outage data review.\n1 sqm ground fire",null,null," - lamps (major road)"]
[17,80,"09/12/2018","15:19",-36.002570900000002,143.54557826999999,"119 SMITHS ROAD BARRAPORT WEST 3537","30554617","CTN001","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0004537","20190613PWA_07 ","Pole fire due to lightning strike.\nFound during outage data review.\nGround fire 300 sqm",null,null," - lamps (minor road)"]
[17,81,"09/12/2018","12:31","-36.47103700","144.99594000","570 JOHNSON ROAD,STANHOPE,VIC,3623","30256538","SHP021","22kV AC","Rural Long"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0003829","20190103PWA_06 ","Customer reported a possible fire on pole at incident location.\nOn arrival the crew found a boric acid fuse had burnt out and failed to operate correctly.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - luminaires (major road)"]
[17,82,"10/12/2018","17:47",-34.24736721,142.19602295000001,"269 BELAR AVENUE IRYMPLE 3498","30099314","RCT021","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0004540","20190613PWA_09 ","Cross arm fire due to leakage current.\nIncident found during outage data review.\nNo ground fire",null,null," - luminaires (minor road)"]
[17,83,"11/12/2018","16:07","-37.12667616","142.99131807","1846 Bulgana Road, Bulgana",32118131,"STL007","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0003736","20181213PWA_02 ","Vic Fire reported a grass fire caused by a fallen SWER conductor at the incident location.\nOn arrival the fault crew found that the pole had previously been struck by lightning, and was split at the top. \nA grass fire - estimated at 60 hectares by CFA personnel present at the incident location - was ignited by the fallen conductor.\nThe fire was extinguished by the CFA.\nThere was no reported injuries",null,null," - poles / columns (major road)"]
[17,84,"11/12/2018","18:30","-37.07236424","143.00152303","668 Joel South Road, Joel South","30086384","STL007","12.7kV AC (SWER)","Rural Long"," - fuse (EDO fuse)","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0003738","20181213PWA_03 ","Vic Fire reported a small grass fire at the incident location.\nOn arrival the fault crew found that an EDO had \"hung Up\" dropping hot material to the ground, igniting a grass fire approx. 6m x 25m in area\nThere were no reported injuries.",null,null," - poles / columns (minor road)"]
[17,85,"13/12/2018","16:45",-38.094058390000001,144.21601870999999,"325 BOOLEY ROAD GHERINGHAP 3331","30323976","GL015","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0004542","20190613PWA_11 ","Candled EDO fuse (fire). \nIncident found during outage data review.\nNo ground fire.",null,null,"Other "]
[17,86,"13/12/2018","08:00","-37.93085458","141.27605283","59 RIVERVIEW TERRACE DARTMOOR 3304.","30089400","PLD003","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0003727","20181213PWA_01 ","Crew attended the incident site and  found that a cross-arm fire had burnt through the cross-arm on the footpath side of the pole. \nThe insulator and end of  the cross-arm with high voltage conductor attached came to rest on the low voltage cross-arm.                            \nPossible high voltage injection to some customers to be confirmed.\nThere were no reported injuries",null,null," - connection box"]
[17,87,"13/12/2018","19:16","-36.62837501","142.631893166327","Gibson Street, Rupanyup","32096251","STL006","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0003743","20181214PWA_01 ","At approx. 19:10hrs on 13/12/18 the Glenorchy ACR P125 tripped to Lockout. \nThe Powercor patrolled the line and found that a X-arm fire had occurred on Gibson Street Pole 2.\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - earth / earthing"]
[17,88,"14/12/2018","15:33",-36.05248924,141.83968969,"DIMBOOLA-RAINBOW ROAD JEPARIT 3423","32120285","NHL016","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0004543","20190531PWA_06 ","Report received of a cross arm fire due to leakage current.\nIncident found during outage data review.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,89,"14/12/2018","23:25",-38.729694909999999,143.37687163999999,"375 Blue Johanna Rd. Johanna","33039953","CLC006","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0004546","20190531PWA_05 ","Report received of a Pole mounted fuse box fire. Incident found during outage data review.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,90,"16/12/2018","08:15",-38.146610369999998,144.35268919999999,"242 LATROBE TERRACE GEELONG WEST 3218","30069174","GCY014","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0004548","20190613PWA_12 ","Cross arm fire due to leakage current.\nIncident found during outage data review.\nNo ground fire.",null,null,"Extra low voltage AC (<50V)"]
[17,91,"16/12/2018","18:25","-37.77405610","144.08363342","454 Morrisons-Elaine Rd, Morrisons 3334","30001236","BAS022","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0003762","20181217PWA_02 ","A report was received from a customer that there was a fuse box fire on the transformer pole at the above location.\nA Powercor crew attended and determined that the LV fuse box on Simpson Spur Pole 4 had caught fire and melted.\nA small section of the pole sustained minor burn damage. \nThere was no ground fire, no reported injuries or third party property damage.",null,null,"Low voltage AC (<1kV)"]
[17,92,"17/12/2018","00:34",-36.07147715,142.34100599999999,"111A QUICKS ROAD BRIM 3391","32090705","HSM003","12.7kV AC (SWER)","Rural Long"," - fuse (EDO fuse)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0004413","20190613PWA_13 ","Candled HV EDO Fuse (Fire)\nFire incident was found during outage data review.\nNo ground fire",null,null,"2.2kV AC"]
[17,93,"17/12/2018","13:40","-36.16661265","144.57102966","355 WILLOW GROVE ROAD KOTTA 3565","33079969","ECA012","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0003764","20181217PWA_04 ","Customer phoned in to report a grass fire has started outside the front of her property, caused by falling debris from the pole.\nOn arrival the crew found that a EDO HV Fuse unit became overheated and dropped hot debris onto the dry grass below igniting a ground fire.\nFire area was around 3 x 150m\nThere was no reported injuries.",null,null,"6.6kV AC"]
[17,94,"19/12/2018","04:02","-38.06323000","144.37690787","43 FAIRBAIRN DRIVE, CORIO VIC 3214","31012734","FNS012","Low voltage AC (<1kV)","Rural Short"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0003803","20181221PWA_02","CFA crew attending a house fire at #33 Fairbairn drive  identified a second fire on a nearby pole.  Attending crew found broken LV isolator. \ndiscussion with CFA fire investigator and review of AMI information confirmed that LV isolator fire was unrelated to house fire. \nHouse fire is being treated as  suspicious and CFA supporting VICPOL forensic investigations",null,null,"11kV AC"]
[17,95,"20/12/2018","14:50","-36.51927340","145.03236589","3587 MCEWEN ROAD WARANGA SHORES 3612","30127581","SHP014","Low voltage AC (<1kV)","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0003804","20181221PWA_01 ","Vic-fire reports conductor down and grass fire at incident location.\nCrew attended to find that a low voltage termination cross-arm had broken \nThere was a small ground fire, no reported injuries",null,null,"12.7kV AC (SWER)"]
[17,96,"21/12/2018","13:50","-36.76664988","144.26630259","54 Thistle St Golden Square Vic 3555","30239616","BET008","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0003852","20190107PWA_02 ","Vicfire reported transformer fire at incident location. \nOn arrival Crew found that the low voltage fuse unit had failed.\nThere was no ground fire, no property damage and no injuries",null,null,"22kV AC"]
[17,97,"24/12/2018","11:23","-38.41933223","144.17008276","22 O’Donohue Road Anglesea 3230","32071083","WPD021","22kV AC","Rural Short"," - dropper / bridge","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0003814","20181224PWA_01 ","Vic Fire reported transformer sparking, starting grass fire near Angahook - Lorne State Park - Fire brigade onsite - REF: 8763 - LIS 29929.\nCrew found a burnt HV dropper/lead had failed which started a small 5m2 grass fire, CFA attended, no property damage, no injuries.",null,null,"33kV AC"]
[17,98,"29/12/2018","09:53","-36.31259900","145.42288000","116 Verney North Road, Congupna VIC 3633","33092637","SHN011","22kV AC","Rural Long"," - transformer (pole mounted)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0003817","20190102PWA_02","Customer reported fire at 116 Verney North road, Congupna.\nUpon arrival the fault crew found that a bird had flashed over substation pole P30 SHTS-NKA #1.\nThe bird fell to ground igniting a grass fire of approximately 10M x 50M in area,\nCFA attended and extinguished the ground fire. \nThere were no reported injuries, minor fence post damage.",null,null,"66kV AC"]
[17,99,"30/12/2018","13:30","-37.70346534","143.64321470","155 GALATEA ROAD NEWTOWN (BALLARAT) 3351","33002011","BAS021","12.7kV AC (SWER)","Rural Long"," - fuse (EDO fuse)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0003941","20190115PWA_03 ","Customer reported following lightning strike pole caught fire.\nThere was no ground fire, no reported injuries or third party property damage",null,null,"132kV AC"]
[17,100,"30/12/2018","23:56","-38.13815079","143.00488833","308 Harrington Road, Glenormiston North 3265","32054677","TRG001","22kV AC","Rural Long"," - dropper / bridge","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0003813","20190102PWA_01","Vicfire reported wires down causing approximately 100m x 100m grass fire, a crew dispatched to investigate.\n\nUpon arrival to the incident location, the lineworker identified evidence of a grassfire and a HV lead had come loose and burnt away from the HV bushing on the pole Tx. Made safe for repairs to be made during daylight hours.",null,null,"220kV AC"]
[17,101,"30/12/2018","21:52","-38.76068445",143.67180304999999,"22 GREAT OCEAN ROAD, APOLLO BAY VIC 3233",32062525,"CLC006","Low voltage AC (<1kV)","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0003816","20190102PWA_03","Vic Fire reports a pole fire at the incident location,  On arrival, the crew finds bare LV conductor has broken off  and is laying on the ground, across the highway. Burns to the grass at the base of the pole were reported.",null,null,"330kV AC"]
[17,102,"30/12/2018","09:30","-36.12766863","142.45822105","Lah East Road Lah","32113994","HSM003","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"High",0.5,{"$f":"IF(OR(P139=\"\",R139=\"\"),\"\",IF(AND(O139=\"within electric line construction area\",Q139=\"No forecast\"),1,P139*R139))","v":0.5},"INC-0003864","20190107PWA_12 ","A customer reported that a pole had been hit by lightning and was on fire.\nOn arrival crew found pole partially destroyed, had been hit by lightning .\nPole had caught fire but fire was extinguished by rain.\nThere was no ground fire, no reported injuries or third party property damage.",null,null,"500kV AC"]
[{"$f":"COUNTA(C140:O140,Q140,T140:V140)","v":17},103,"30/12/2018","09:50",-37.770057919999999,143.68744222999999,"585 Derwent Jacks rd Berringa 3351",30272578,"BAS021","12.7kV AC (SWER)","Rural Long"," - fuse (EDO fuse)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",{"$f":"IF(O140=\"\",\"\",IF(O140=\"LBRA only\",0.2,IF(O140=\"HBRA only\",1,IF(O140=\"within electric line construction area\",19.8,IF(O140=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"Low-moderate",{"$f":"IF(Q140=\"\",\"\",IF(Q140=\"No forecast\",0.1,IF(Q140=\"Low-moderate\",0.2,IF(Q140=\"High\",0.5,IF(Q140=\"Very high\",1,IF(Q140=\"Severe\",2,IF(Q140=\"Extreme\",3.5,5)))))))","v":0.2},0.91999999999999993,"INC-0003865","20190107PWA_13 ","Customer reported following a lightning strike there was a pole fire at the incident location.\nOn arrival crew found EDO fuse hung up and fire extinguished by rain.\nThere was no ground fire, no reported injuries or third party property damage.",null,null,"Extra low voltage DC (<120V ripple free)"]
[17,104,"31/12/2018","12:45",-38.168253290000003,144.71591125,"12 First Ave, St Leonards","32087947","DDL013","Low voltage AC (<1kV)","Rural Short"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0004415","20190613PWA_14 ","Transformer LV isolator burnt off causing small burn marks at base of pole.\nIncident found during outage data review.\nSmall ground fire 0.1 sqm",null,null,"Low voltage DC (<1.5kV)"]
[17,105,"31/12/2018","13:38","-37.29701504","143.49984527","2154 Beaufort – Lexton Road Lexton Vic 3352","30011244","BAN006","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (other)","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0003820","20190102PWA_04 ","Vicfire reported a pole fire caused a grass fire at incident location. \nOn arrival crew found that a  neutral screen service had ruptured at the pole end had started a grass fire.\nThere were no reported injuries",null,null,"600V DC"]
[17,106,"03/01/2019","17:35","-37.12469600","142.84611000","105 MOUNT VIEW ROAD GREAT WESTERN 3374","32116024","ART031","12.7kV AC (SWER)","Rural Short"," - transformer (pole mounted)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0003847","20190104PWA_13 ","Customer reported pole was sparking and this caused a ground fire of approximately 1m² in the vicinity of the base of the pole. \nOn arrival crew found that the transformer had failed.\nThere was no reported injuries or third party property damage",null,null,"1500V DC"]
[17,107,"04/01/2019","21:47","-37.25317800","142.71992000","190 Pollands Rd Moyston 3377",32091855,"ART033","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Severe",2,9.1999999999999993,"INC-0003854","20190107PWA_03 ","Vic Fire reported conductors down and grass fire.\nOn arrival crew found a SWER conductor had fallen to ground starting a small grass fire,\nThere was no reported injuries",null,null,"Earthing cable"]
[17,108,"2019-01-04","22:19:00",-36.454741859999999,145.20332761,"170 GIRGARRE EAST ROAD,TATURA,VIC,3616","33088618","MNA021","22kV AC","Rural Short"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Extreme",3.5,0.70000000000000007,"INC-0004644","20190613PWA_15 ","Customer reports sparking from pole top.\nOn arrival crew found that a boric acid fuse had hung up and was candling.\nThere was no ground fire, no reported injuries or third party property damage.\nEvent found during outage data review."]
[17,109,"06/01/2019","01:33","-37.62341584","143.87891315","1815 Geelong Rd, Ht Helen 3350","33000502","BAS013","22kV AC","Rural Short"," - surge diverter","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0003948","20190116PWA_03","On 6/1/19 at approx. 01:33 hrs a possum caused a flashover on the cable head structure on Buninyong Pole 89 (LIS 342). The possum fell to the ground and caused a small ground fire covering an area of approx. 3 sq metres. The CFA attended and extinguished the fire. There was no third party damage or injury."]
[17,110,"06/01/2019","11:36","-37.50402700","143.93443000","227 Clarkes Rd Glen Park 3352","30015277","BAN008","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0003860","20190107PWA_09 ","Vic Fire reported at pole fire at the incident address.\non arrival crew found that a FOLCB had burnt at the substation pole.\nThere was no ground fire, no injuries or third party property damage.",null,null,"single wire earth return (SWER)"]
[17,111,"07/01/2019","15:22","-37.67291027","141.96157846","368 Partridges Rd Hamilton","32128531","HTN006","12.7kV AC (SWER)","Rural Long"," - transformer (pole mounted)","single wire earth return (SWER)","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0003871","20190108PWA_01 ","A customer reported a bird made contact with line at the incident location causing a small grass fire. \nUpon arrival, crew found that a bird flashover on SWER substation pole resulting in a small fire surrounding the pole base. The grass fire caused a minor damage to the property fence. There was no damage to the pole base.\nThere was no reported injuries.",null,null,"single phase"]
[17,112,"07/01/2019","17:54","-36.69669000","142.22955000","39 Riverside Rd Dooen 3401","32091134","HSM005","22kV AC","Rural Long"," - surge diverter","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0003877","20190108PWA_04 ","A crow caused a flashover at a Lightning Arrestor on a gas switch pole and this resulted in a small grass fire of 5m² at the base of the pole.\nThere was no reported injuries or third party property damage.",null,null,"two phase"]
[17,113,"09/01/2019","20:15","-37.48987400","144.02660000","970 Black Swamp Rd Bullarook 3352","32013164","BAN008","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0003907","20190111PWA_01 ","Powercor received a report from a customer advising while attending to a pump for stock water he found a  nearby wooden pole with evidence of a fire.\nHe believed it had occurred in the last two days, almost burnt through and cross arm barely holding on, wires very low. \nSupply is still on.\nThere was no ground fire, no reported injuries or third party property damage.",null,null,"three phase"]
[17,114,"09/01/2019","12:04","-38.17971213","142.42247515","16 Reeves Rd Woolsthorpe 3279","33101473","KRT012","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0003950","20190116PWA_05 ","A Powercor fault crew reported a candled EDO unit at the incident location. \nThere was no ground fire, no reported injuries or third party property damage."]
[17,115,"11/01/2019","12:31","-36.44396081","145.00903470","cnr of Midland Hwy and Middle Rd  Stanhope","30142962","SHP014","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (other)","single phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0003925","20190114PWA_01 ","Vic fire reported a grass fire at the incident location.\nUpon arrival, Powercor crew found that there was a grass fire that was caused by a fallen service with its junction box across the road.\nThe crew believed the service was pulled down by an unknown high load. \nThere was no reported injuries"]
[17,116,"12/01/2019","11:11","-35.22847500","143.47774000","OUTSIDE TAMERESK 1528 MURRAY VALLEY HIGHWAY - BEVERFORD","32160477","SHL004","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0003938","20190115PWA_02 ","During  a patrol of assets after a feeder operation the remains of a crossarm fire was found at the incident location.\nthere was no ground fire, no reported injuries or third party property damage",null,null,"Negligible: no ground fire"]
[17,117,"14/01/2019","18:45","-34.16516900","142.13744000","38-42 FLORA AVENUA - MILDURA","31034166","MBN023","22kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0003956","20190118PWA_02 ","Report received of pole fire at incident location.\nOn arrival crew found a transformer had failed, causing burning to conduits, leads and pole.\nThere was no ground fire, no reported injuries or third party property damage.",null,null,"Localised: less than 10 sq.m"]
[17,118,"14/01/2019","15:34","-37.70523162",144.60210843999999,"100-128 Ferris Rd, Cobblebank, 3338",34015306,"MLN021","Low voltage AC (<1kV)","Rural Short"," - luminaires (minor road)","single phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0004001","20190124PWA_06 ","Report from Vicfire of street light pole smoking.\nOn arrival crew advised that lantern had failed internally which had caused the lantern to smoke.\nThere was no ground fire, no reported injuries or third party property damage.",null,null,"Small: 10 - 1000 aq.m"]
[17,119,"15/01/2019","21:45","-36.34749700","145.42547000","240 FORD RD - GRAHAMVALE","33096318","SHN024","Low voltage AC (<1kV)","Rural Short"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0003951","20190117PWA_01 ","An IPC  overheated at incident location.\nHot particles caused a small fire at base of pole.\nThere was no reported injuries or third party property damage.",null,null,"Medium: 1000 sq.m - 10 ha"]
[17,120,"16/01/2019","17:55","-38.06223487","142.35840073","\"Kareela\", 292 Kooringal Rd, HAWKESDALE Vic 3287","30347516","KRT013","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0003954","20190118PWA_01 ","Vic Fire reported a grass fire due to a pole fire at the incident location. \nWhen crews arrived they found a small grass fire (10m x 20m) had been started at the base of a pole by a failed LV junction box.\nThere was no reported injuries.",null,null,"Large: more than 10 ha"]
[17,121,"17/01/2019","18:03","-36.35356734","142.35178191","Moloneys Rd, Btn Kranzs rd and Ailsa Wheat Rd, Wallup 3401","30081906","HSM001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Severe",2,2,"INC-0003959","20190118PWA_05 ","Vicfire reported a fire on a pole at the incident location.  On arrival the crew found that a cross arm fire had occurred on a 22kV intermediate pole which caused the cross arm to break and the conductors to fall to the ground, resulting in a ground fire (Approx. 2000 sqm) on the road reserve.  Protection operated. CFA attended. There were no reported shocks or injuries."]
[17,122,"18/01/2019","11:00","-35.88866422","144.09171209","302 BORELLA ROAD MINCHA WEST 3568.","30027998","CHA006","22kV AC","Rural Long"," - transformer (pole mounted)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"Very high",1,1,"INC-0003960","20190118PWA_06 ","Powercor crew were restoring supply when a transformer failed at this address causing a small grass fire. 1m by 3m.      \nTransformer required replacement.\nThere were no injuries due to this incident."]
[17,123,"19/01/2019","15:03","-36.66533642","145.24619535","60 Old Dargalong School Wahring",32192254,"MNA034","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Very high",1,1,"INC-0003964","20190121PWA_01 ","CFA reported tree on conductors and ground fire underneath.\nOn arrival crew identified that a large tree of some 35 metres in height  had fallen breaking conductors and starting a small ground fire.\nThere were no reported injuries.",null,null,"Started in or originated from a distribution system"]
[17,124,"21/01/2019","15:56","-38.31430681","142.42928982","420 CONNS LANE YANGERY 3283","32195757","KRT013","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0003969","20190122PWA_01","Emergency services reported a pole and ground fire . The attending crew found that a pole fire had occurred on pole 1 and a grass fire of some 6 by 20 metres had occurred on the roadside grass. No injuries or direct damage was noted.",null,null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system"]
[17,125,"23/01/2019","09:03",-38.716011510000001,143.72967319,"5750 GREAT OCEAN ROAD,PETTICOAT CREEK,VIC,3233","32062627","CLC001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0004643","20190531PWA_07 ","Report from customer of pole fire .\nPossibly lighning strike but not confirmed.\n22kv crossarm burnt of at one end.\nThere was no ground fire, no reported injuries or third party property damage.",null,null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system"]
[17,126,"24/01/2019","20:24","-37.71292241","144.56356815","4 Hume Avenue, Melton South",30111841,"MLN011","Low voltage AC (<1kV)","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0004008","20190125PWA_02 ","Resident reported that pole outside his house had exploded, showering sparks on to the nature strip below resulting in a small grass fire (approx. 1.5m2 in total).\nUpon arrival the fault crew found that the Aluminium conductor bridging in one of the LV transformer bus isolators at pole LIS-108994 had melted and burnt through.\nThere was no reported injuries or third party injuries.",null,null,"Started by lightning striking a distribution system or a part of a distribution system "]
[17,127,"24/01/2019","18:44",-37.749715190000003,144.76370438999999,"99 Fairfax Circuit, Albanvale",30103829,"SU022","Low voltage AC (<1kV)","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0004005","20190125PWA_01 ","Resident reported they heard a loud bang from the pole and smoke coming from the pole outside their property, and that there was a fire at the bottom of the pole and grass. \nThe residents extinguished the small grass fire (approx 1m2) in the nature stri.\nWhen the fault crew arrived they found that the red phase LV transformer bus fused isolator at pole LIS-014081 had burnt out at the copper to aluminium connector connecting the isolator to the overhead conductor. \nThere were no reported injuries or third party property damage reported.",null,null,"Started by any other thing forming part of or coming into contact with a distribution system"]
[17,128,"25/01/2019","09:57",-36.970396370000003,141.09291590999999,"2067 Wimmera Highway, Apsley VIC, Australia.  On north side of the Highway.",32120393,"CHM011","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started in or originated from a distribution system","HBRA only",1,"Severe",2,2,"INC-0004009","20190125PWA_03 ","A wooden termination cross-arm broke on Aspley P 2 202 the incident location causing conductor clashing and a low conductor across the Wimmera Highway.\nDebris falling to ground is believed to have ignited a grass fire (61,000m2 burnt) which started at this point. This fire was subsequently extinguished by the CFA.\nA large truck passing under the low conductor has snagged the low conductor causing it to break and fall to the ground. \nThere was no reported injuries.",null,null,"Otherwise started by a distribution system"]
[17,129,"25/01/2019","16:33","-37.87057320","144.80555980","32 Kookaburra St, Altona",32167630,"AL006","Low voltage AC (<1kV)","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0004018","20190129PWA_04 ","Report received from Vic fire of wire down, arching and sparking. \nUpon arrival the fault crew found the copper tail on the white phase bus fused LV isolator  had burnt through due to corrosion. Some sparks were splashed on to the dry grass below, with a very small area of grass scorched. \nThere was no reported injuries or third party property damage."]
[17,130,"26/01/2019","02:06","-37.49631611","144.51690070","81 HAIRES ROAD BULLENGAROOK VIC 3437",32043180,"GSB011","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0004013","20190129PWA_01 ","Vic Fire reported trees down over wires and caused grass fire at incident location. \nOn arrival crew found tree through single phase 22kv conductors and small grass fire  between P3 & P4 .\n CFA extinguished 5m x 35m grass fire.\nThere was no reported injuries or third party property damage."]
[17,131,"27/01/2019","09:22","-36.34309749","145.20885497","920 Lilford Road, Gillieston 3616 (near Mulcahy Road)","30127687","SHTS-KYM1","66kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0004017","20190129PWA_03 ","Following a 66kv line trip to lockout a PAL crew found a crossarm fire at the incident location.\nCrew found at SHTS KYM No 1 66kV Line P164, the road side insulator burnt off the x-arm, dropped down and clashed with another phase, small grass fire approximately 300mm x 300mm.\nThere was no reported injuries or third party property damage.",null,null,1]
[17,132,"28/01/2019","16:54","-36.29917134","145.48516005","447 CONGUPNA EAST ROAD CONGUPNA VIC 3633","33090392","SHN024","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0004324","20190218PWA_01 ","Customer reported red glow from top of transformer pole.\nOn arrival crew found EDO fuse hung up and glowing.\nCFA attended site.\nThere was no ground fire, no reported injuries or third party property damage.",null,null,2]
[17,133,"29/01/2019","13:02","-37.86545979","144.82670993","48 David St, Altona.","32164804","AL012","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0004084","20190204PWA_03 ","MFB called to report a pole fire at the incident location. \nOn arrival the crew found that an FOLCB box on the pole had caught fire and was destroyed. \nThere were no reported injuries, ground fire or third party damage.",null,null,3]
[17,134,"30/01/2019","18:57","-34.25145509",142.16201674000001,"36 COORONG AVENUE,IRYMPLE,VIC,3498",30096208,"RCT021","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Severe",2,{"$f":"IF(OR(P171=\"\",R171=\"\"),\"\",IF(AND(O171=\"within electric line construction area\",Q171=\"No forecast\"),1,P171*R171))","v":0.4},"INC-0004057","20190201PWA_01 ","Customers reported wires down at incident location.\nOn arrival crew found a tree stem had  broken and brought down two conductors causing a small ground fire. \nThe stem broke approximately 1.2 m above the ground prior to falling toward overhead conductors.",null,null,4]
[17,135,"30/01/2019","13:28","-36.47180147","145.33402665","308 Pogue Rd Toolamba",33090668,"MNA034","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"Very high",1,0.2,"INC-0004042","20190131PWA_01 ","Vic Fire reported a ground fire at a pole base at the incident location.\nOn arrival, the Powercor crew found a conductor down and small ground fire that was caused by lightning.\nThere were no reported injuries or third party property damage.",null,null,5]
[17,136,"01/02/2019","17:48","-36.39910812","145.41182360","16-18 Poplar Avenue, Shepparton VIC 3630","32192567","STN021","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0004083","20190204PWA_02 ","Emergency services reported a POA fire at IGA in Poplar Avenue, Shepparton. \nUpon arrival crew found that POA did fail due to excessive heat & was likely to have commenced burning as there was evidence of soot on the adjacent veranda façade.\nThe CFA extinguished the POA fire using chemical retardant prior to the fault crews arrival.\nThere was no reported injuries.",null,null,6]
[17,137,"03/02/2019","14:26","-37.82311282","144.80645669","62  Pipe road, Laverton , 3026",33075857,"LVN032","Low voltage AC (<1kV)","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Severe",2,0.4,"INC-0004080","20190204PWA_01 ","Mike from DIAMOND VALLEY PORK PTY LTD reported a truck has clipped the mains wire in street, wire now down on ground across driveway, wire sparking. \nPower to this property is still on.\n On arrival the crew found that a truck had hit an Optus Service Cable, this resulted in the Optus cable detaching from one of the poles and falling down to the ground across the driveway of #62 Pipe road, Laverton. \n\nThe crew advised that most likely the Optus Service Cable flicked up into the LV Bare Mains, causing sparking on the LV conductors as they noticed some splash marks on the red phase & neutral conductors. \nThe sparks and probably hot debris that fell to the ground started a small ground fire on the dry grass,  the fire extinguished by itself.\nThere were no reported injuries or third party property damage.",null,null,7]
[17,138,"03/02/2019","16:42","-36.08560996","144.11462039","Bendigo - Pyramid Rd, Pyramid Hill 3575 - 1.3kM north of Mitiamo - Kerang Rd.",31004471,"CHA006","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0004094","20190205PWA_02 ","Vicfire reported grass fire caused by Network assets at the incident location.\nUpon arrival crew found that the roadside phase conductor broken.\nA ground fire ignited at the incident location.",null,null,8]
[17,139,"03/02/2019","16:30","-36.48952761","144.23022553","Bendigo - Pyramid Rd, Raywood 3570 - 200M Sth of Newton Rd","30151753","EHK024","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0004089","20190205PWA_01 ","Crews were in process of locating a fault on feeder when a ground fire was located at a pole mounted capacitor at the incident location.\nCFA attended and extinguished the fire.\nThere was no reported injuries or third party property damage.",null,null,9]
[17,140,"04/02/2019","16:42","-36.31376800","145.20181000","630 Lancaster - Mooroopna Rd, Gillieston VIC 3616","32191858","KYM003","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (other)","single phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0004106","20190206PWA_01 ","Vicfire reported fire caused by network assets. \nUpon arrival the fault crew found that a truck hit grey twisted service cable crossing the road, the cable broke approximately 30cm from the supply pole end, prior to the LV fuses operating arcing has occurred between active's & neutral conductors & material ejected by the arcing commenced a ground fire emanating at base of pole at the incident location.\nThe CFA attended and extinguished the grass fire.\nThere was no reported injuries.",null,null,10]
[17,141,"05/02/2019","18:14","-36.75141900","144.25610000","1 Jason Street, Long Gully VIC 3550",33012138,"BET001","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0004108","20190206PWA_02 ","Vicfire reported a pole fire at the incident address. \nUpon arrival the Powercor fault crew found that a bird had flashed over on the HV between the centre phase disc string and the fuse unit bracket, damaging the glass disc string which required replacing.\nThe bird fell to ground and ignited 2 small grass fires near the base of the pole.\nThere was no reported injuries or third party property damage.",null,null,{"$f":"Y177+1","v":11}]
[17,142,"05/02/2019","18:11","-36.66016600","143.91507000","236 NEWBRIDGE-BRIDGEWATER ROAD, BRIDGEWATER VIC 3516","32039868","BET001","22kV AC","Rural Long"," - surge diverter","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0004111","20190206PWA_03 ","Customer reported loud explosion and smoke on their substation pole at the incident location. \nUpon arrival Powercor fault crew found that a ABB surge diverter had ruptured ( Polymer type MVK20 ).\nMaterial ejected from the arcing resulted in a very small burnt area at the base of the pole, less than 0.2m square. \nThe customer doused the ground with a pail of water which extinguished the smoldering material.\nThere was no reported injuries or third party property damage",null,null,{"$f":"Y178+1","v":12}]
[17,143,"06/02/2019","01:00","-38.73200779","143.64882454","420 Tuxion Rd, Apollo Bay","32062167","CLC007","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0004115","20190206PWA_04 ","Vic fire reported a pole fire at the incident location.\nOn arrival the crew found that the SWER strain substation pole had burnt off in the area of the transformer, resulting in the top section of the pole including the transformer falling to the ground. \nA small grass fire  resulted and was extinguished by the CFA.\n A small amount of oil was spilt from the transformer, however no oil entered any drains or waterways. There was no other reported third party damage.",null,null,13]
[17,144,"06/02/2019","21:30","-37.08444800","143.94589000","2613 Pyrenees Hwy, Moolort VIC 3465","30017086","MRO007","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0004159","20190208PWA_03 ","Vicfire reported pole fire at the incident location. Upon arrival crew found that a pole fire had occurred on a 66/22/LV pole, Carisbrook 144A.\nPole fire occurred at position #3 crossarm kingbolt, but involved the LV crossarm also at the kingbolt position. All conductors remained aloft.\nNo ground fire, 3rd party damage or injury transpired.",null,null,14]
[17,145,"07/02/2019","13:46",-38.313365699999999,143.32445224,"2317 PRINCES HIGHWAY (near Craigs Lane) STONYFORD VIC 3260",31009370,"CDN002","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within electric line construction area",19.8,"High",0.5,9.9,"INC-0004154","20190208PWA_01 ","Customer reported Transformer on pole has blown, making a \"cooking noise\" before it went off and is now quite dark and damaged at incident location. \nOn arrival crew found one fuse blown and one hung up.\nThere was a small fire at the base of the pole (1 sq metre).\nThe fire was extinguished by the customer\nThere was no reported injuries or third party property damage.",null,null,15]
[17,146,"09/02/2019","15:09","-35.05598228","142.87709548","On Mallee Highway west of the MANANGATANG TOWNSHIP SIGN","32154472","OYN003","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0004196","20190211PWA_03 ","Report received from Vic Fire of wires down and grass fire at incident location.\nOn arrival crew found the end burnt off a crossarm and a small grass fire (20 sq m)\nThere was no reported injuries or third party property damage.",null,null,16]
[17,147,"09/02/2019","23:59","-38.22399239","144.25018507","255 Reservoir Road, Waurn Ponds",33046494,"WPD011","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0004182","20190211PWA_01 ","During a fault patrol a crew found a conductor on the ground at the incident location.\nThere was a small ground fire (30sq m).\nThere was no reported injuries or third party property damage.",null,null,17]
[17,148,"09/02/2019","18:56","-38.08390696","144.42237806","480 A Avalon Road, Avalon","30242888","FNS032","Earthing cable","Rural Short"," - earth / earthing","single phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"Very high",1,1,"INC-0004215","20190212PWA_01 ","CFA reported a pole fire at the above location. \nThe crew attended and noticed the HV earth and the LV cable had been cut off at ground level and above head height on the pole. \nThe cutting of the earth had started the pole fire. The fire was contained to the pole with no ground fire.\n CFA attended.",null,null,18]
[17,149,"10/02/2019","11:17",-38.566235110000001,142.85991494999999,"Lot 67B Old Peterborough Road, Peterborough",30251713,"WBL012","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0004192","20190211PWA_02 ","CFA called regarding a grass fire at the above location involving our assets. \nThe crew attended and found conductor damage due to a bird strike. conductor fell to ground causing a small ground fire.\nThe fire was approximately 50M X 30M.\nThere was no reported injuries.",null,null,19]
[17,150,"14/02/2019","11:06",-36.309847230000003,145.6282832,"30 SUTHERLAND ROAD COSGROVE 363",30129547,"STN024","12.7kV AC (SWER)","Rural Long"," - fuse (boric acid)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0004291","20190214PWA_07 ","A passer-by reported a ground fire at the incident location. \nUpon arrival, the Powercor crew found that the HV fuse hung-up and approx. 2150Ssqm grass had been burnt and extinguished by the CFA.\nThere was no reported injuries.",null,null,20]
[17,151,"14/02/2019","23:37","-38.1491607529005","144.358660253967","126 RYRIE STREET, GEELONG VIC 3220",30266203,"GCY021","Low voltage AC (<1kV)","Urban"," - fuse (any other type)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0004320","20190215PWA_02","REC for Restaurant owner advised that premises had part supply. Attending crew found burnt wooden meter board and fuse carrier."]
[17,152,"15/02/2019","10:30","-37.45033262","144.01599994","151 MYERS ROAD DEAN 3363.  ","32008548","BAN008","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0004319","20190215PWA_01","Property owner advised pole on fire at incident address.\nCrew attended to find pole top and conductors on ground. Pole burnt through at the cross-arm strap bolt.\nNo ground fire and no reported injuries."]
[17,153,"16/02/2019","13:35","-38.02914501","144.41890807","87 Archimedes Ave, Lara.","32085956","FNS022","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0004442","20190226PWA_02 ","Vicfire reported a pole fire at the incident location. \nOn arrival the crew found that a 3 phase Fused mains box had overheated resulting in melted debris falling to the ground. Due to green vegetation and bare earth at the base of the pole, the melted debris did not result in a ground fire. \nThere were no reported injuries or third party damage."]
[17,154,"16/02/2019","00:26",-38.568148280000003,142.85955016,"Paddock off Old Peterborough Rd, 2.5km East of Great Ocean Rd.",30251712,"WBL012","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"High",{"$f":"IF(Q191=\"\",\"\",IF(Q191=\"No forecast\",0.1,IF(Q191=\"Low-moderate\",0.2,IF(Q191=\"High\",0.5,IF(Q191=\"Very high\",1,IF(Q191=\"Severe\",2,IF(Q191=\"Extreme\",3.5,5)))))))","v":0.5},{"$f":"IF(OR(P191=\"\",R191=\"\"),\"\",IF(AND(O191=\"within electric line construction area\",Q191=\"No forecast\"),1,P191*R191))","v":0.5},"INC-0004342","20190219PWA_01 ","A Powercor Fault crew patrolling following an outage, discovered a dead swan in a paddock, beside a downed HV conductor. The conductor falling on the ground resulted in two small grassfires of approx. 600m2 total in size on private property.\n The fire self extinguished, due to dewy conditions. \nThere were no reported injuries or other third party damage."]
[17,155,"17/02/2019","04:06","-37.43206412","143.37846324","11 stuart st Beaufort 3373","33005424","BAS011","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0004449","20190226PWA_05 ","Following report from supply interruption crew found an EDO fuse fuse had candled before falling to the ground.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,156,"22/02/2019","14:20","-38.44761892","143.72564100","390 Dewings Bridge Rd, Gerangamete, Victoria.","33039445","CLC013","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0004405","20190225PWA_01 ","Vic-fire report fire under pole at incident location, caused by HV Fuse unit.\nOn arrival crew found a burnt grass patch which had been caused by a crow which had flashed over on the center phase HV fuse unit. \nThere was no reported injuries."]
[17,157,"23/02/2019","00:26","-38.26978679","144.35033083","750 HORSESHOE BEND ROAD, MOUNT DUNEED VIC 3217","33041574","WPD024","22kV AC","Rural Short"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0004411","20190225PWA_02 ","Vic Fire reported a grass fire start due to an animal fault at the incident location. \nWhen crews arrived they found a possum fault on a HV concrete anchor pole had started a grass fire (50m x 20m) mainly in the road reserve and onto farm land. \nThe fire was extinguished by CFA crews.\nNo injury, or 3rd party property damage other than superficial burning to some farm boundary fence posts and railings."]
[17,158,"25/02/2019","20:41","-37.91173204","141.78380465","94 N Wallacedale Rd, BRANXHOLME 3302 (approx 900m east of Henty Hwy)","31017267","HTN002","22kV AC","Rural Long"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0004434","20190226PWA_01 ","Customer reported a transformer fire and CFA in attendance at incident site. \nWhen crews arrived they found a HV Boric Acid fuse had \"hung up.\nThis resulted in a small grass fire (40m x 2m) along the road reserve that was extinguished by the CFA. \nNo injuries or property damage reported"]
[17,159,"25/02/2019","18:49","-37.67281920","144.58751187","21 Kurunjang Drive, Kurunjang 3337","31025469","MLN012","Low voltage AC (<1kV)","Rural Short"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0004448","20190226PWA_04 ","MFB Comms reported burnt wire, started a grass fire. brigade onsite \nOn arrival the PCA Faults Crew have advised that a burnt out Blue Phase LV Isolator, Cu to Al D-Loop connection has overheated and caused sparks to fall onto the grassed area below.\nThe resultant hot sparks above had fallen onto the ground/grassed nature strip  below causing a small grass fire near the base of the pole (1m x5m).\nThere was no reported injury or shocks as a result of this incident."]
[17,160,"25/02/2019","10:57",-36.273767309999997,144.53875486000001,"21 ALFRED CRESCENT,LOCKINGTON,VIC,3563",33085689,"SHP012","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0004477","20190227PWA_04 ","Vic Fire reported a  pole fire and smoke coming from just above the transformer at the incident location. \nUpon arrival the crew found the centre phase fuse hung up asa result of a  bird flashover. \nThere was no ground fire, no reported injuries or third party property damage."]
[{"$f":"COUNTA(C198:O198,Q198,T198:V198)","v":17},161,"26/02/2019","20:37","-38.41957828","143.83721486","Murroon Rd (250m sth of Barholme Rd), PENNYROYAL 3235","30260049","WIN011","22kV AC","Rural Long"," - dropper / bridge","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0004462","20190227PWA_01 ","CFA reported grass fire at incident location and requested Powercor attendance to check equipment as possible ignition source. \nWhen crews arrived they inspected the Regulator structure at P159 CLC-LRN line and found evidence of a hot spot on the center phase lead to the top of the disconnect switch on the south side of the pole. \nMolten PVC tubing was found on the ground. \nA grass fire of 30m2 had burnt along the road reserve and into private paddock and was extinguished by CFA crews.\n No injuries or property damage reported"]
[{"$f":"COUNTA(C199:O199,Q199,T199:V199)","v":17},162,"27/02/2019","18:51","-37.85926126","144.69908237","42 Evrah Drive, Hoppers Crossing 3029","33072797","LV009","Low voltage AC (<1kV)","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0004496","20190228PWA_03 ","PCA Faults Crew attended a fault call have advised that a burnt out Blue Phase Cu to Al D-Loop connection at incident location has overheated and caused sparks to fall onto the dry grassed area below.\nThis has caused a small grass fire near the base of the pole.\nThere was no reported injury or shocks as a result of this incident."]
[17,163,"27/02/2019","18:13","-34.48499867","142.36342717","Crown land opposite 2768 Kulkyne Way Nangiloc","32149834","RCT013","Low voltage AC (<1kV)","Rural Short"," - overhead conductor (insulated)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0004490","20190228PWA_02 ","CFA called reporting grass fire at incident location. \nOn arrival crew found fire of approx. 1000 m2 and part of the burnt area was under our pole.\nInsulation between D clamp and isolator had melted on LV cables, fallen debris ignited grass below.\nCFA and State Forest Management crews in attendance.\nThere were no injuries or third party property damage."]
[17,164,"28/02/2019","14:41","-35.67693435","143.40267487","4235 Lalbert–Kerang Road, Lalbert 3542",30019603,"SHL001","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"Very high",1,1,"INC-0004557","20190304PWA_02 ","Report of wire has blown into conductors started fire at incident location. \nCrew found that a Willy Willy had blown some old tangled fencing wire onto the SWER overhead conductor.\nThere was a ground fire of approx. 8000 sq m, there was no reported injuries, no asset damage."]
[17,165,"01/03/2019","20:18","-36.48164682",145.2412674,"765 Dhurringile Road Tatura 3616 (corner Toolamba-Rushworth Road)",33097279,"MNA021","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0004560","20190304PWA_03 ","Reports received of small grass fire.\nOn arrival crew found a limb had fallen through conductors between poles 9 & 10  at incident location.\nDisturbance to Conductors caused a small grass fire  between poles 6 & 7.\nThere were no reported injuries or third party property damage."]
[17,166,"01/03/2019","09:25","-37.97242176","144.34854716","1225 BACCHUS MARSH ROAD,ANAKIE,VIC,3213",30228255,"FNS011","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"Very high",1,1,"INC-0004574","20190305PWA_01 ","CIVILEX VICTORIA reports while completing road works, an excavator in travelling mode has  contacted an overhead conductor causing it to break and fall to ground.\nOn arrival crew found Excavator hit line at driveway of 1225 Bacchus Marsh Road Anakie between LIS 986123 and LIS 986124.\nOne conductor has fallen , there are burn marks at 7 individual sites where small fires started mostly spots.\nThe fires were upstream caused by backfeed.\nThere were no reported injuries"]
[17,167,"03/03/2019","02:59","-38.08191472","144.34109062","13 REDFEARN COURT, CORIO VIC 3214","30071844","CRO013","Low voltage AC (<1kV)","Rural Short"," - underground service cable (other)","three phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O204=\"\",\"\",IF(O204=\"LBRA only\",0.2,IF(O204=\"HBRA only\",1,IF(O204=\"within electric line construction area\",19.8,IF(O204=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"Severe",2,0.4,"INC-0004556","20190304PWA_01 ","customer reported no supply and pole on fire.  Attending crew found fused mains box on pole had overheated, burnt service cables and charred pole."]
[17,168,"04/03/2019","11:01","-36.34701865","144.79579479","115 Gibson Road, Nanneella,3561, VIC, Australia.","30121480","KYM001","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0004562","20190304PWA_05 ","Vicfire reported pole fire at incident location.\nOn arrival the crew found that the pole mounted junction box had overheated and melted, \nDebris from this had fallen to ground and started a ground fire approximately 3m by 50m. \n Superficial damage to fencing posts.\nThere was no reported injuries."]
[17,169,"04/03/2019","10:45","-37.04151166","141.28734067","63 POWERS CREEK ROAD EDENHOPE 3318","33053008","CHM011","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0004582","20190305PWA_03 ","A report was received that bird has flashed over the HV EDO unit at the pole at the incident location.\nThe bird fell to ground on fire and ignited a ground fire near the pole 20m by 60m ((1200m2).\nFire extinguished by the CFA.\nThere was no report of injury or third party property damage."]
[17,170,"05/03/2019","07:02","-38.49477428","143.88839212","335 Benwerrin-Mt Sabine Rd Benwerrine","33045906","CLC005","22kV AC","Rural Short"," - surge diverter","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0004594","20190305PWA_05 ","CFA reported a fire at the incident location. \nUpon arrival, the Powercor crew found that a lightning arrestor on  sub pole,  CLC - LRN 217, had been damaged.\nThere was a ground fire, no reported injuries."]
[{"$f":"COUNTA(C208:O208,Q208,T208:V208)","v":17},171,"06/03/2019","00:51","-38.14999813","144.33693454","88 Aphrasia street Newtown","30074160","GL022","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0004617","20190306PWA_05","Emergency services report that cross-arm had burnt and insulator had fallen into conductors below. Attending crew found that a cross arm fire had occurred and high voltage injection damage was apparent"]
[{"$f":"COUNTA(C209:O209,Q209,T209:V209)","v":17},172,"07/03/2019","14:00","-38.25994988","142.92604029","COBDEN-TERANG ROAD TERANG 3264.  200meters south of Bend Road","30043677","TRG003","22kV AC","Rural Long"," - surge diverter","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0004642","20190308PWA_02 ","Report received of a bird flashover at the incident location.\nOn arrival the crew found that a bird had caused a flashover between surge arrestor and its base. The bird fell to ground to ground starting a small grass fire.\nCFA extinquished the fire.\n There was no reported injuries."]
[17,173,"08/03/2019","18:50","-37.72617287","141.98881075","377 Glenelg Hwy, Hamilton, 3300","32139027","HTN006","22kV AC","Rural Long"," - transformer (pole mounted)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0004656","20190312PWA_03 ","CFA reported a transformer had started a grass fire at the incident location. \nOn arrival the crew found an area 20x12m had been burnt. \nWire was found on the transformer possibly from a bird attempting to build a nest. \nThere were no reported injuries."]
[17,174,"09/03/2019","12:50",-37.73633753,144.79749318,"216 BIGGS STREET, ST ALBANS VIC 3021",30232994,"SA009","22kV AC","Urban"," - overhead conductor (ABC)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0004653","20190312PWA_01 ","Calls received from residents to report an outage in the area, with wires down and grass fire in Biggs St, St Albans. \nUpon arrival the fault crew found that a  HV ABC had broken mid span and come to ground on the nature strip below, resulting in a grass fire on the nature strip as well as the grass within the front yard of unit 1 of 216 Biggs St.\nThere was no reported injuries."]
[17,175,"10/03/2019","16:23","-36.72604500","144.50466000","163 MCCORMICKS ROAD, FOSTERVILLE VIC 3551","33019088","EHK031","22kV AC","Rural Short"," - surge diverter","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0004655","20190312PWA_02 ","Fosterville mine reported a grass fire coinciding with a part supply failure.\nUpon arrival the crew found that the transformer mounted porcelain surge diverter had failed & subsequently started a small ground fire of approximately 2M x 1M in size.\nThe mine staff extinguished the fire, no injuries or 3rd party damage reported,"]
[17,176,"10/03/2019","06:42","-36.04282041","141.03192921","TAYLORS ROAD, TELOPEA DOWNS VIC 3420","32121232","NHL031","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0004662","20190312PWA_04 ","Crew reported a fire at the incident location.\nFollowing a patrol the crew found that a pole fire had occurred on a 12.7kV pole, resulting in a ground fire (approx. 50 sqm) on private property. \nThere were no reported injuries."]
[17,177,"15/03/2019","20:18",-38.180856689999999,144.34799932000001,"97 FRANCIS STREET, BELMONT VIC 3216","30268132","GLE012","22kV AC","Urban"," - pole (wood)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0006829","20190528PWA_01 ","Report received of possum flashover which in turn ignited pole top\nThere was no ground fire, no reported injuries or third party property damage."]
[17,178,"16/03/2019","12:35","-37.80992593","142.10834742"," 647 Yatchaw Road, Yatchaw","30092292","HTN003","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0004715","20190318PWA_01 ","Bird flashed over on Yatchaw Rd P27E S/Stn, it came to ground and resulted in a ground fire in the road reserve of approximately 20 M X 100 M."]
[17,179,"16/03/2019","12:27",-36.387897000000002,145.42670000000001,"130-160 Benalla Rd, Shepparton VIC 3630","31033732","STN021","22kV AC","Rural Short"," - dropper / bridge","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0004716","20190702PWA_05 ","Customer from \"good guys warehouse\" reported transformer fire at the incident location. \nUpon arrival crew found that a frond from an adjacent palm tree was making contact with the HV transformer dropper of \"Zurcas 2E\" substation, this caused the frond to burn due to the contact with the HV. \n1 HV fuse operated at Zurcas 2E.\nNo ground fire, injury or 3rd party damage transpired ."]
[17,180,"18/03/2019","03:37","-37.87958395","144.77411021","Corner of Hastie court and May Avenue. Altona Meadows 3028","33076190","LV003","Low voltage AC (<1kV)","Rural Short"," - overhead conductor (ABC)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0004732","20190320PWA_02 ","Vic fire reported a pole fire at the incident location.  \nOn arrival the crew found that a connection on to LV ABC conductors had burnt at the pole . Small pieces of debris had landed on the ground below. \n\nThere were no reported injuries or third party damage."]
[17,181,"19/03/2019","00:00","-36.35209121","144.65627828","310 Diggora Road, Rochester","33081172","SHP012","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0006126","20190322PWA_01 ","A customer reported that when they turned off their irrigation pump on Tuesday (19th March) the power pole started sparking and arcing, made a loud bang, and started a small grassfire. \nThis was not reported to Powercor until Thursday (21st March). \nOn arrival the crew found a porcelain fuse box on the substation pole had overheated and dropped hot debris to the ground resulting in a small grassfire of approx. 10m x 16m= 160m2 in size. \nThere were no reported injuries or third party damage."]
[17,182,"20/03/2019","00:25","-38.15373389","144.36613587","200 Myres Street, Geelong (Cnr block, pole in Swanston Street)","17171688","GCY024","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0004731","20190320PWA_01 ","Following a report of a pole fire on arrival the crew found the top crossarm burnt off on outer phase.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,183,"23/03/2019","07:46","-36.40213700","145.13202000","525 BYRNESIDE-KYABRAM ROAD, MERRIGUM VIC 3618","33094346","SHP014","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"Very high",1,0.2,"INC-0006177","20190327PWA_01 ","A powercor crew responding to an outage identified that High voltage fuses had mal-operated and there had been a small ground fire at the base of the pole."]
[{"$f":"COUNTA(C221:O221,Q221,T221:V221)","v":17},184,"23/03/2019","08:56","-38.34637469","144.29754630"," 33 DUNKEITH AVENUE,JAN JUC,VIC,3228 ","30070945","WPD032","22kV AC","Rural Short"," - fuse (Fault Tamer)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"Very high",1,0.2,"INC-0006214","20190329PWA_02 ","Customers reported intermittent supply. Attending crew found that fault tamer fuse had burnt in half, with the top section of the fuse carrier falling to the ground."]
[{"$f":"COUNTA(C222:O222,Q222,T222:V222)","v":17},185,"23/03/2019","10:17",-36.717221000000002,144.34961000000001,"GOLF COURSE ROAD, WELLSFORD VIC 3551","30026717","EHK022","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0006458","20190416PWA_07 ","Report received of a pole fire at incident location.\nOn arrival crew found a crossarm with the end burnt off .\nThere was no ground fire, no reported injuries or third party property damage."]
[17,186,"24/03/2019","11:44","-38.28259846","144.61484358","135-137 POINT LONSDALE ROAD, POINT LONSDALE VIC 3225","31012844","DDL012","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0006158","20190325PWA_02 ","Passerby reports burnt cross- arm on pole 11924. Attending crew  found end had burnt off from lower HV cross-arm on pole. No HVI identified"]
[17,187,"24/03/2019","11:20","-37.90806370","144.66147987","Burke St. Werribee, along the side of No 31 Wedge St","33071159","WBE024","22kV AC","Urban"," - transformer (pole mounted)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0006170","20190326PWA_02 ","customers reported smoke coming from a power pole (LIS 204796) on the north side of Burke St Werribee \nA Powercor crew attended the site and noted that a 300kVA pole mounted substation (Burke Wedge 22 03 1751)  had faulted"]
[17,188,"24/03/2019","22:27","-38.46571580","144.08123563","3 WERONA ROAD FAIRHAVEN 3231","30060390","WPD014","Low voltage AC (<1kV)","Rural Short"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0006221","20190329PWA_03 ","Customer reported transformer on fire. Attending crew found Fuse switch disconnector had overheated"]
[17,189,"24/03/2019","10:19",-34.311306000000002,142.16585000000001,"CNR BOOBOOK AVE AND WESTCLIFFS AVE - redcliffs","32146224","RCT023","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0006247","20190401PWA_01 ","Report received of a pole fire at the incident location.\nOn arrival crew found that the top of the pole and crossarm had been  burnt.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,190,"24/03/2019","02:48",-34.239603580000001,142.17551528999999,"2172 FIFTEENTH STREET IRYMPLE 3498","31021116","RCT021","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0006823","20190527PWA_02 ","Vic fire reported pole fire at incident location"]
[17,191,"24/03/2019","10:14",-34.972002000000003,143.29392000000001,"5235 MURRAY VALLEY HIGHWAY NATYA 3597","33067603","BBD014","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0006358","20190408PWA_09 ","Customer reported pole fire at incident location.\nOn arrival crew found top of pole had been burnt off at king bolt location\nThere was no ground fire, no reported injuries or third party property damage."]
[17,192,"28/03/2019","20:54",-36.732121679999999,141.18229195000001,"367 Mimimay Frances Road, Minimay",33054660,"HSM004","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0006248","20190329PWA_05 ","A B Double tip truck, while unloading gypsum fertilizer on a farming property, made contact with overhead SWER conductor; bringing the conductor to the ground.  \nThe truck was driving forward with the tipper up, and the driver did not check for clearance from the overhead SWER conductor.\nThe electrical discharge through the truck ignited a grass fire on this property - burning an area approx. 50m x 10m\nThere were no injuries to the truck driver or any other damage caused by this incident."]
[17,193,"29/03/2019","11:34",-35.954959090000003,145.6099619,"6515 Benalla-Tocumwal Road (C371) YARROWEYAH VIC 3644 (Near corner Churchill Road & Lonergan Road)","30326765","CME015","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"Severe",2,0.4,"INC-0006250","20190329PWA_04","Customer reported lightning has struck power pole out the front of property.  Crew found lightning had damaged an EDO fuse unit and started a 100m x 20m grass fire, no reported injuries or property damage."]
[17,194,"29/03/2019","14:17",-37.570535700000001,143.74270387000001,"98 Sago Hill Road Bunkers Hill 3352 (Near Greenhalghs Road)",30282752,"BAS011","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0006253","20190402PWA_01 ","Vicfire reported wire down and a grass fire at the incident location. Crew found a tree had fallen and damaged a bare overhead conductor."]
[17,195,"29/03/2019","18:33",-38.114857440000002,144.35433015000001,"Cnr Mackey St & Princes Hwy, Geelong.",31012241,"GB031","22kV AC","Urban"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0006254","20190402PWA_02 ","Vicfire called to report a pole hit by lightning, conductors down and a grass fire at the incident location. On arrival the crew found that a cross-arm fire had occurred on the 66kV cross arm, causing the 66kV conductors to fall on the 22kV conductors, which subsequently resulted in one phase of the 22kV falling to the ground. The 22kV conductor that fell, landed across the Princes Highway blocking the road, and also fell across the Geelong-Melbourne Railway causing the trains to be stopped. A small ground fire  was ignited at the base of the pole."]
[17,196,"29/03/2019","21:29",-37.856070279999997,144.80800822,"20-24 AJAX ROAD, ALTONA VIC 3018","30108857","AL011","11kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0006256","20190402PWA_03 ","Vic fire reported a pole fire at incident location.\nOn arrival the crew found a crossarm burnt on one end.\nThere was no ground fire, no reported injuries or third party property damage."]
[{"$f":"COUNTA(C234:O234,Q234,T234:V234)","v":17},197,"30/03/2019","18:24",-36.254706429999999,144.99871537000001,"Allot 79A Finlay Rd Tongala","33091308","KYM004","22kV AC","Rural Long"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O234=\"\",\"\",IF(O234=\"LBRA only\",0.2,IF(O234=\"HBRA only\",1,IF(O234=\"within electric line construction area\",19.8,IF(O234=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"High",{"$f":"IF(Q234=\"\",\"\",IF(Q234=\"No forecast\",0.1,IF(Q234=\"Low-moderate\",0.2,IF(Q234=\"High\",0.5,IF(Q234=\"Very high\",1,IF(Q234=\"Severe\",2,IF(Q234=\"Extreme\",3.5,5)))))))","v":0.5},{"$f":"IF(OR(P234=\"\",R234=\"\"),\"\",IF(AND(O234=\"within electric line construction area\",Q234=\"No forecast\"),1,P234*R234))","v":0.1},"INC-0006258","20190402PWA_05 ","A PAL crew returning from another fault found CFA in attendance at a small grass fire at the incident location.\nOn arrival crew found a HV isolator appears to have flashed.\nThere were no reported injuries or third party property damage."]
[{"$f":"COUNTA(C235:O235,Q235,T235:V235)","v":17},198,"31/03/2019","13:36",-35.312609469999998,141.30166733999999,"174 GUNAMALARY ROAD, COWANGIE VIC 3506","32151897","OYN001","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",{"$f":"IF(O235=\"\",\"\",IF(O235=\"LBRA only\",0.2,IF(O235=\"HBRA only\",1,IF(O235=\"within electric line construction area\",19.8,IF(O235=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":1},"Low-moderate",{"$f":"IF(Q235=\"\",\"\",IF(Q235=\"No forecast\",0.1,IF(Q235=\"Low-moderate\",0.2,IF(Q235=\"High\",0.5,IF(Q235=\"Very high\",1,IF(Q235=\"Severe\",2,IF(Q235=\"Extreme\",3.5,5)))))))","v":0.2},{"$f":"IF(OR(P235=\"\",R235=\"\"),\"\",IF(AND(O235=\"within electric line construction area\",Q235=\"No forecast\"),1,P235*R235))","v":0.2},"INC-0006259","20190402PWA_06 ","CFA reported pole fire on Gunamalary Rd.  \nOn arrival crew found that a HV cross arm had burnt through at the kingbolt.   \nThe centre phase insulator was on the ground.  \nA Ground fire had occurred, there were no reported injuries or third party damage."]
[17,199,"31/03/2019","08:15",-35.070230940000002,143.33542317000001,"28 HANKINSON LANE PIANGIL 3597","32162865","SHL002","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0006825","20190527PWA_03 ","Report of pole fire at incident location"]
[17,200,"31/03/2019","15:06",-34.718537210000001,143.14957636,"TOWER 13 MURRAY VALLEY HIGHWAY BOUNDARY BEND VIC 3599","32143607","BBD021","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0006826","20190527PWA_04 ","Pole fire found at incident location"]
[{"$f":"COUNTA(C238:O238,Q238,T238:V238)","v":17},201,"31/03/2019","11:39",-35.139825760000001,142.02493741999999,"21 Glen St Walpeup","30097832","OYN001","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",{"$f":"IF(O238=\"\",\"\",IF(O238=\"LBRA only\",0.2,IF(O238=\"HBRA only\",1,IF(O238=\"within electric line construction area\",19.8,IF(O238=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":1},"Low-moderate",{"$f":"IF(Q238=\"\",\"\",IF(Q238=\"No forecast\",0.1,IF(Q238=\"Low-moderate\",0.2,IF(Q238=\"High\",0.5,IF(Q238=\"Very high\",1,IF(Q238=\"Severe\",2,IF(Q238=\"Extreme\",3.5,5)))))))","v":0.2},{"$f":"IF(OR(P238=\"\",R238=\"\"),\"\",IF(AND(O238=\"within electric line construction area\",Q238=\"No forecast\"),1,P238*R238))","v":0.2},"INC-0006355","20190408PWA_08 ","Reports of pole fire, crew arrived and CFA and police in attendance. \n HV cross-arm had burnt out and HV conductors were on LV cross arm.  \nCrew checked and HV conductors have not made contact with LV conductors and no reports of HV injection.  \n No ground fire.  No injuries.  No third party damage."]
[{"$f":"COUNTA(C239:O239,Q239,T239:V239)","v":17},202,"03/04/2019","13:10",-35.254719809999997,141.10778443000001,"MALLEE HIGHWAY CARINA 3512","32153602","OYN001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",{"$f":"IF(O239=\"\",\"\",IF(O239=\"LBRA only\",0.2,IF(O239=\"HBRA only\",1,IF(O239=\"within electric line construction area\",19.8,IF(O239=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":1},"High",{"$f":"IF(Q239=\"\",\"\",IF(Q239=\"No forecast\",0.1,IF(Q239=\"Low-moderate\",0.2,IF(Q239=\"High\",0.5,IF(Q239=\"Very high\",1,IF(Q239=\"Severe\",2,IF(Q239=\"Extreme\",3.5,5)))))))","v":0.5},{"$f":"IF(OR(P239=\"\",R239=\"\"),\"\",IF(AND(O239=\"within electric line construction area\",Q239=\"No forecast\"),1,P239*R239))","v":0.5},"INC-0007291","20190701PWA_04 ","Following report from customer a pole fire was found at the incident location.\nOn arrival crew found end burnt of crossarm and conductor hanging low across paddock.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,203,"05/04/2019","19:39",-35.28677347,141.08105599999999,"1047 NGALLO ROAD,CARINA,VIC,3512 ","31021367","OYN001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0006349","20190408PWA_06 ","Customer reported wire down in the paddock, wire is only 8 foot off the ground at 1047 Ngallo Road, wire is resting on top of a poly tank and goes over the gateway. \nCrew found Carina P26 Burnt and broken cross arm\nThere was no ground fire, no property damage and no injuries."]
[17,204,"05/04/2019","14:15",-38.28763344,141.51731326999999,"359 Foleys Rd, Gorae West.","32128662","PLD003","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Very high",1,1,"INC-0006346","20190408PWA_03 ","Vicfire advised of grass fire caused by a large plantation gum tree falling across conductors.\nOn arrival crew found that  a large gum tree had fallen across SWER  conductors causing a grass fire\nThere was no reported injuries"]
[17,205,"07/04/2019","12:27",-35.923847420000001,144.20650606999999,"Peaces Road corner Mansfield Bridge Road Leitchville","31038390","CHA005","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0006344","20190408PWA_02 ","Report of pole fire and ground fire at incident location. \nCrew found a pole fire had started a 1 acre grass fire, no property damage, no injuries."]
[17,206,"08/04/2019","14:22",-37.391335179999999,144.05750535000001,"475 Telegraph Road Mount Prospect 3364",31001430,"BAN008","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0006365","20190409PWA_02 ","Vicfire reported lines down, grass fire caused by lines down, wires sparking at incident location. \nCrew found a broken xarm and a broken conductor \nThere was a  ground fire of 2 x 30m2,, no injuries, no property damage."]
[17,207,"08/04/2019","20:35",-38.161552909999997,144.34445746,"406 Pakington St, NEWTOWN  (sth of Rutland St)",32087669,"GL022","22kV AC","Urban"," - pole (wood)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0006367","20190409PWA_04 ","Powercor received a report from Vic FIre of an explosion and pole on fire in Pakington St.\nWhen crews arrived they found a possum had shorted across the HV switch. \nThis resulted in some grass igniting on the pole which had  grown up the pole along the earth cable and behind the possum guard approx. 1.5m above ground level.\nThis was also the location of the end of the HV switch handle and it appears that an arc had occurred been the switch handle and possum guard. \nThere was no ground fire, no reported injuries or third party property damage."]
[17,208,"09/04/2019","03:02",-35.768347040000002,142.05417539999999,"22 Byrne Street,, Yapeet","32123038","NHL015","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0006364","20190409PWA_01 ","Powercor received a report from the CFA of a Pole Fire at 222 Byrne Street Yapeet.\nA Powercor crew attended at determined that a Pole Fire had occurred on Jeparit Pole 627. \nThe X-arm had burnt through at the X-arm strap bolt and one of the HV conductor had come to rest on a LV conductor on the x-arm below. \nThere was no ground fire or reported injuries."]
[17,209,"09/04/2019","01:13",-36.602713100000003,143.94291132999999,"27 Main Street Bridgewater","30028650","BET001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0006366","20190409PWA_03 ","Vic Fire reported pole on fire, sparks everywhere.\nCrew found pole fire/burnt HV strain xarm, no ground fire, no property damage, no injuri"]
[17,210,"09/04/2019","15:04",-35.158927830000003,141.0412547,"246 Simon Road Panitya Vic 3512 (near Mickan Road)","32146042","OYN001","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0006370","20190410PWA_01","Customer advised fuse down on pole located on Panitya North Rd. \nCrew found SWER pole had burnt down 2m from top,\nThere was a small stubble fire , no reported injuries."]
[17,211,"11/04/2019","18:14",-34.205485609999997,142.14820460000001,"359 San Mateo Avenue Mildura","33063508","MDA034","22kV AC","Urban"," - crossarm (steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0006431","20190412PWA_03 ","A Sparking Transformer was  reported by customers.\nSparks reaching ground and started a grass fire.\nThree magpies flashed over at the top of the substation pole.\nCFA Attended small scorched area where magpies fell. \nThere was no reported injuries or third party property damage."]
[17,212,"11/04/2019","07:50",-36.499779009999997,142.56803244,"548 MINYIP-COROMBY ROAD, MINYIP VIC 3392","32112021","STL006","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0006395","20190411PWA_03 ","CFA Brigade reported as per police, pole fire, Cnr Robbins Rd & Coromby-Minyip Rd Minyip, top of pole on fire, Brigade enroute. \nDue to a pole fire the crew found live SWER conductor hanging approximately 3.6m above road and railway line\nThere was a small  ground fire: 50m x 30m = 1,500m2, no property damage, no injuries."]
[17,213,"15/04/2019","15:59",-36.375208280000003,145.39916251,"outside 29 Welsford Street Shepparton","30259528","SHN023","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0006638","20190506PWA_03 ","Powercor crew responding to a fault found a LV Fused Gang Operated Fused dis-connector switch [FSD] had burnt out"]
[17,214,"15/04/2019","11:40",-37.555160999999998,143.89729500000001,"32 Water St, Brown Hill",30283126,"BAN015","Low voltage AC (<1kV)","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0006444","20190416PWA_01 ","A crew investigating an outage found that an unknown vehicle had contacted a communications cable above Water St, \nThe force of the impact caused the communications cable to contact the overhead LV conductors. \nThis resulted in hot debris falling to the ground, starting a small grass fire.\nThere was no reported injuries or third party property damage."]
[17,215,"16/04/2019","09:32",-38.14558581,143.62966903,"1992 Colac Ballarat Road, Beeac",30052273,"CLC003","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very high",1,4.5999999999999996,"INC-0006478","20190418PWA_02","A customer called concerned about a tree branch that had fallen onto the High Voltage conductors and started a fire.   On arrival the crew found that a tree branch had fallen and contacted the HV conductors and then onto the ground.\nThis caused a ground fire of approx.  750m2. \nThe  CFA did not notify Powercor of the fire at the time of their attendance. \nThere were no reported injuries."]
[17,216,"21/04/2019","05:34",-38.600395259999999,143.00119311,"2520 Cobden-Port Campbell Rd, Port Campbell 3269","32056227","TRG003","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0006649","20190507PWA_02 ","CFA reported pole fire at incident location. On arrival crew found bird nest material in FOLCB had caught fire and melted the box and conductor insulation. Melted plastic fell to the ground but did not start a fire."]
[17,217,"21/04/2019","18:31",-36.466873999999997,145.27778000000001,"690 Craven Rd, Tatura VIC 3616","30133198","MNA034","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0006650","20190507PWA_03 ","Vic Fire report a pole fire at the incident location. Upon arrival the fault crew found that a 3 phase intermediate pole had ignited."]
[17,218,"21/04/2019","12:39",-35.23250324,141.02080387999999,"OUYEN HIGHWAY CARINA VIC 3512","31021260","OYN001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0007294","20190701PWA_05 ","Customer reported low conductors and pole fire.\nOn arrival crew found crossarm burnt in half.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,219,"23/04/2019","14:37",-34.167831,142.06578999999999,"149 Commercial Street, Merbein VIC 3505","32151664","MBN031","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0006652","20190507PWA_05 ","Vic Fire reported a pole fire at the incident location. Upon arrival crew found that an intermediate crossarm had burnt through at the kingbolt, dropping down onto the LV cross arm below"]
[17,220,"23/04/2019","15:34",-34.235810399999998,142.17134647,"2135 Fifteenth St Irymple","30099579","MDA023","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0006653","20190507PWA_06 ","A pole fire reported at the incident location. The attending crew found the HV strain cross-arm had burnt"]
[17,221,"23/04/2019","14:29",-34.251006689999997,142.08305820999999,"3420 Deakin Av Mildura","30098768","MBN032","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,"INC-0006654","20190507PWA_07 ","Vic Fire reported a pole fire at the incident location, attending crew found HV cross-ram had burnt"]
[17,222,"23/04/2019","12:13",-34.231915639999997,142.18482255999999,"685 Irymple Av Irymple",30558650,"RCT011","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0006648","20190507PWA_01 ","Vic Fire reported  a pole fire at the incident location. Upon arrival, the crew found that the pole top burnt through and fell onto LV"]
[17,223,"23/04/2019","12:08",-34.192691920000001,142.14982307,"16 Princess St Mildura",32149824,"MDA033","22kV AC","Urban"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0006525","20190424PWA_01 ","A pole fire reported at the incident location. \nUpon arrival, that the crew found HV cross arm burnt through. \nThere were no injuries or ground fire. HVI damage was reported."]
[17,224,"23/04/2019","14:28",-34.211273869999999,142.18061207,"396-402 SANDILONG AVENUE IRYMPLE 3498","30100024","MDA024","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0006526","20190424PWA_02 ","pole fire reported at the incident location. Upon arrival, that the crew found HV cross arm bunt through. \nThere were no injuries or ground fire.\n HVI reported."]
[17,225,"23/04/2019","22:40",-34.241747699999998,142.10347791000001,"3219 SAN MATEO AVENUE MILDURA 3500","32146495","MBN032","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0006527","20190424PWA_03 ","A pole fire reported at the incident location.\nHVI was found . \nThere were no injuries or ground fire."]
[17,226,"23/04/2019","11:39",-34.427404209999999,142.34923624000001," BLAKE ROAD, IRAAK VIC 3494","30098951","RCT014","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0007296","20190701PWA_06 ","Customer reports pole fire at incident location.\nOn arrival crew found termination crossarm burnt\nThere was no ground fire, no reported injuries or third party property damage."]
[17,227,"24/04/2019","16:45",-34.271586999999997,142.16202000000001,"264 Coorong Ave, Irymple VIC 3498","32148573","RCT021","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0006661","20190508PWA_01 ","Customer reported wire down at the incident location. Upon arrival crew found that a Tee Off cross-arm burnt off at eye bolt  position. Supply remained on as the conductor remained aloft suspended by the bridging cable."]
[17,228,"24/04/2019","13:58",-34.463976000000002,142.34136000000001,"73 Sculthorpe Road, Nangiloc VIC 3494","32144798","RCT013","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0006655","20190507PWA_08 ","Customer reported broken cross arm at incident location. Upon arrival crew found that a intermediate cross arm burnt through at the kingbolt, the cross arm straps kept the conductors aloft."]
[17,229,"26/04/2019","09:02",-37.059413390000003,144.20858989999999,"29 RICHARDS ROAD, CASTLEMAINE VIC 3450",32045602,"BETS-CMN","66kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0006663","20190508PWA_02 ","Vic Fire reported a pole fire at the incident location. Upon arrival, the fault crew found 66kV cross arm ignited."]
[17,230,"26/04/2019","10:18",-38.066986759999999,144.35896914,"214 Baccush Marsh Service Rd Corio","32073948","FNS011","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0006664","20190508PWA_03 ","Vic Fire reported a pole fire at the service road of this  incident location. The attended crew made the site safe and repairs arranged"]
[17,231,"26/04/2019","15:58",-36.257429999999999,145.35095999999999,"CNR MEDLAND RD AND ALDINGA DVE - BUNBARTHA ",33097110,"SHN011","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0006551","20190429PWA_03 ","Customer advised that tree fell across bare overhead mains and reported smoking from wire/tree. \nAttending crew found A tree had fallen directly across all three phases and  tree had caught fire.  There were small fires where the conductors had been brought to ground."]
[17,232,"26/04/2019","13:37",-36.267460450000002,144.2320776,"BENDIGO-PYRAMID ROAD, MITIAMO VIC 3573","31005276","CHA006","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0006548","20190429PWA_01 ","Vic Fire reported a pole fire at the incident location. A fault crew found that the cross arm burnt through and fallen debris caused a ground fire approx. 7*100 Sqm area."]
[17,233,"26/04/2019","00:45",-38.385917990000003,142.49158757000001,"74 Barkly st Warrnambool, vic 3280","30544142","WBL008","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0007299","20190701PWA_08 ","Call from customer reporting pole fire outside 74 barkly st.\nNo ground fire, no injuries or third party property damage."]
[17,234,"26/04/2019","16:18",-34.225834980000002,142.09343801,"3171 ONTARIO AVENUE MILDURA 3500","30099184","MBN032","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0007314","20190702PWA_04","Report received of a pole fire at incident location.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,235,"01/05/2019","06:01",-34.447651,142.33548999999999,"2351 KULKYNE WAY, IRAAK VIC 3494","30096877","RCT013","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0006913","20190514PWA_03 ","Vic fire reported a pole fire. The attending crew found that a cross arm had burnt at the king bolt position."]
[17,236,"01/05/2019","04:30",-35.241042,143.47192999999999,"Cnr ray and heslop rd (outsie 68 heslop rd - beverford).","32161041","SHL004","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0006914","20190603PWA_02 ","Customer reported a pole fire at the incident location.\nOn arrival crew reported end burnt of wooden crossarm.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,237,"01/05/2019","05:47",-35.724978950000001,142.36156836000001,"39 TOOLE STREET, HOPETOUN VIC 3396","32098179","HSM003","Low voltage AC (<1kV)","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0006665","20190508PWA_04 ","Vic Fire reported a pole fire at the incident location.\nOn arrival the fault crew found that an LV crossarm had burned through on a HV / LV 2 way tee off pole.\nThe Powercor pole was also burned at the kingbolt location."]
[17,238,"01/05/2019","06:17",-35.328660999999997,143.5566,"9 KING STREET, SWAN HILL VIC 3585","32161090","SHL004","22kV AC","Rural Short"," - overhead conductor (insulated)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"INC-0006610","20190503PWA_01 ","Powercor received an alarm indicating that a high voltage automatic circuit recloser had opened.  The attending crew found that a pole top fire had occurred which destroyed the top of a pole and dislodged overhead conductors. The crew indicated that the fire may have ignited in the vicinity of the low voltage cross-arm supporting isolators and an LV underground cable.\nNo ground fire."]
[17,239,"01/05/2019","09:10",-36.140604250000003,144.75984527,"121 OGILVIE AVENUE ECHUCA 3564",30121458,"ECA001","22kV AC","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0006572","20190501PWA_05 ","Emergency services report pole fire O/S 121 OGILVIE AVENUE  ECHUCA\nPowercor crew attended site to find the lowest high voltage cross-arm had burnt thru on the king bolt, conductors  fell onto low voltage circuit below"]
[17,240,"01/05/2019","10:55",-37.92856227,141.84698223999999,"597 WALLACEDALE-BYADUK ROAD WALLACEDALE 3303",30087598,"HTN002","12.7kV AC (SWER)","Rural Long"," - earth / earthing","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0006574","20190501PWA_06 ","customer reports earth is burning where it meets the pole.\nCrew attended site to find SWER earth getting very hot near base of pole. Appears to have ignited a small grass fire about 0.5m2."]
[17,241,"01/05/2019","12:30",-36.254652669999999,145.0319083,"617 MCEWEN ROAD WYUNA 3620 southwest of property.",31027332,"KYM004","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0006593","20190502PWA_01 ","Customer reported loud bang and power went out.\nCrew attended site to find broken HV cross-arm on Harris P5, with a flash over and pole fire on Tongala East -P79"]
[17,242,"01/05/2019","06:54",-35.920251489999998,144.21877384000001,"130 PEACES ROAD LEITCHVILLE VIC 3567","32033752","CHA005","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0007209","20190627PWA_03","Report of pole fire at incident location.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,243,"02/05/2019","00:07",-34.302370000000003,142.14238,"436 myall street,cardross,vic,3496",30095563,"MDA023","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0006915","20190603PWA_03 ","Vic fire reported a pole fire at the incident location.\nOn arrival the crew found that a pole fire had occurred resulting in the pole being burnt between the HV and LV crossarms.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,244,"02/05/2019","06:29",-34.284649000000002,141.66121000000001," HARDS LANE - WERRIMULL VIC 3496",30283808,"MBN031","12.7kV AC (SWER)","Rural Short"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0006688","20190510PWA_07 ","Vicfire reported a pole fire in Hards lane, the attending crew found the top of the pole had burnt and signs of burning on the ground."]
[17,245,"07/05/2019","18:46",-35.337333579999999,141.10803634000001,"901 CARINA SOUTH ROAD, CARINA VIC 3512","32154757","OYN001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,"INC-0006683","20190510PWA_05 ","Customer reported pole fire in paddock.  On arrival crew found pole was burning on the inside and on the tee-off cross arm"]
[17,246,"13/05/2019","08:40",-38.170631829999998,144.34231327000001,"BELMONT PRIMARY SCHOOL, 51 MT PLEASANT ROAD, BELMONT VIC 3216","31010963","GCY023","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0006707","20190514PWA_06 ","Belmont Primary School advises top of pole is on fire, pole is located directly at front of the school and at school crossing.\n\nPowercor crew arrived to find a fuse switch disconnect (FSD) device had overheated and caught fire. The Fire brigade had extinguished the fire prior to the crew attending."]
[17,247,"13/05/2019","12:31",-35.500825570000003,142.71706671000001,"MYALL ROAD LASCELLES 3487","32159145","OYN005","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0006706","20190514PWA_05 ","Customer reported pole in paddock has burnt to the ground in past 24 hours, not currently on fire, paddock is on Mitchell road between where it meets Myall School Bus Road and Sea Lake-Lascelles Road. Crew found SWER pole had been burnt due to pole fire, minor ground fire damage around where pole was."]
[17,248,"18/05/2019","17:30",-35.819994610000002,144.19384941000001,"119 COHUNA-MCMILLANS ROAD, COHUNA VIC 3568",33019552,"CHA006","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0006771","20190521PWA_01","Emergency services reported wire down and ground fire at the incident location. Upon arrival fault crew found that road side 22kV conductor failed approximately 20M from pole 41 Greens Rd.\nThe downed conductor caused localised burning of grass in the immediate vicinity of where it came to rest, approximately 2.0M in burnt area comprised of small patches."]
[17,249,"19/05/2019","18:17",-36.276383000000003,145.41128,"185 Zeerust Rd, Zeerust VIC 3634","33093329","SHN011","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0006950","20190605PWA_05 ","CFA reported transformer fire at the incident location.\nUpon arrival crew found that a LV fuse box had melted and candled due to excessive hea.\nNo ground fire resulted or any other 3 party damage."]
[17,250,"21/05/2019","19:01",-37.35205689,144.14229535000001,"5 Macadam St, Daylesford","31001630","BAN011","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0006885","20190531PWA_02 ","CFA reported reported a fire on a pole at the incident location. \nOn arrival, the crew found that a connection in a pole mounted LV fuse box had overheated, causing the box to melt and catch fire. \nThere was no ground fire. There were no reported injuries or third party property damages."]
[17,251,"27/05/2019","21:52",-37.708629100000003,144.78811103999999,"1A BOBBORA COURT TAYLORS LAKES 3038","17978879","SA003","Low voltage AC (<1kV)","Urban"," - transformer (kiosk mounted)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0006832","20190528PWA_04 ","Customers and Fire Brigade reported BOBBORA-ADMIRALS 300kVA Kiosk on fire. \nLV switchboard end of the kiosk was burnt out internally.\nFire brigade extinguished the fire.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,252,"27/05/2019","22:57",-38.386474499999998,142.49282263000001,"58 BARKLY STREET  WARRNAMBOOL 3280 ","32194380","WBL008","22kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"INC-0006830","20190528PWA_02 ","CFA Comms reported pole fire. Attending crew found pole top had burnt  above HV strain cross arm and would require replacement in daylight. no customers impacted"]
[17,253,"27/05/2019","21:49",-37.355689529999999,144.72182372,"278 KNOX ROAD ROMSEY 3434","31006494","WND012","22kV AC","Rural Long"," - transformer (pole mounted)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0007230","20190628PWA_01 ","Transformer failed and caught fire\nCFA attended\nThere was no ground fire, no reported injuries or third party property damage."]
[17,254,"29/05/2019","09:00",-38.488415549999999,142.70108074000001,"784 CHILDERS COVE ROAD THE COVE 3268","33105330","WBL012","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0006890","20190531PWA_03 ","Vic Fire reports a pole fire at 784 Childers Cove Rd The Cove.\nCrew attended to find that EDO fuse on 22kV substation  had mal-operated."]
[17,255,"30/05/2019","03:34",-38.124687139999999,144.66448456000001,"122 SIMSON STREET,PORTARLINGTON,VIC,3223","32070815","DDL013","Low voltage AC (<1kV)","Rural Short"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0006992","20190606PWA_08 ","Vicfire reported a pole fire. \nAttending crew found that a LV switch disconnector had failed\nThere was no ground fire , no reported injuries or third party property damage."]
[17,256,"31/05/2019","08:49",-36.322570290000002,145.16390383000001,"Ground water Pump site, Davies Rd, Lancaster","30222670","KYM003","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,"INC-0006997","20190606PWA_10 ","Following a report of the HV fuse down at the incident location, crews attended and found that lightning had struck the HV OH conductors mid-span.\nInsulation  was burnt from a section of  LV transformer leads adjacent to the FOLCB . \nA birds nest inside the FOLCB was scorched - refer image\nThere was no ground fire, no reported injuries."]
[17,257,"31/05/2019","06:53",-36.415106000000002,141.66019392000001,"Winiam Rd, near the corner of D Manns Rd, Nhill 3418","32122897","NHL015","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0007009","20190607PWA_01 ","Vic fire reported a pole fire at the incident location. \nOn arrival the crew found  minor burning of the wooden pole top. \nThe conductor stayed in position until crews arrived to perform repairs.\nThere were no reported injuries, and no ground fire."]
[17,258,"03/06/2019","18:41",-37.840012530000003,144.84393506999999,"22 Cooper Avenue, Altona North","32164659","AL002","Low voltage AC (<1kV)","Urban"," - transformer (pole mounted)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0007019","20190607PWA_04 ","MFB reported a transformer was on fire. \nUpon arrival the fault crew found a melted red phase LV bushing a 300kVA pole sub.\n The fire self extinguished according to the MFB. \nThe fire was contained to the area immediately surrounding the LV bushing and transformer tank on the pole itself. \nThere was no ground fire to report. No reports of shock, injury or third party damage."]
[17,259,"04/06/2019","11:20",-37.826967019999998,144.77130450999999,"255 Dohertys Rd Laverton North",30114188,"LVN021","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0007021","20190607PWA_05 ","Vic Fire reported a transformer on fire at the incident location. \nUpon arrival a Powercor crew found that a service termination box on a Pole Substation  had melted. \nThere was no ground fire, no reported injuries or third party property damage."]
[17,260,"05/06/2019","04:50",-36.660983280000004,142.1168232,"Bedderson rd Vectis,","32090809","HSM006","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0006967","20190606PWA_01 ","Customer reported loss of supply and wire down near their place, on arrival the work crew found a pole fire had occurred resulting in the top of the pole burning off and the conductors fell to the ground. \nThere was a small ground fire 1m sq. There was no reported injuries."]
[17,261,"06/06/2019","10:32",-38.411079479999998,144.18485462999999,"14 Minifie Avenue, Anglesea","33043992","WPD021","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0007029","20190607PWA_07 ","Emergency Services reported a pole fire and a grass fire at the incident location.\nOn arrival the crew found that a 3 phase FOLCB had overheated and dropped hot debris to the ground, resulting in a small ground fire of less than 1 metre square at the base of the pole. There were no reported injuries."]
[17,262,"08/06/2019","19:15",-38.271031970000003,144.51923423,"45 Osborne Street, Ocean Grove","30233688","DDL023","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (other)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0007044","20190611PWA_01 ","Crew were dispatched to incident following reports transformer and pole were on fire. The fire brigade were also enroute.\nUpon arrival, the crew identified a 2 wire neutral screened service to 45 Osborne St had burnt at the pole junction box. \nThe wire fell to the ground causing 1m2 of grass to burn.\nThere was no reported injuries."]
[17,263,"08/06/2019","17:43",-37.72065757,144.83827822999999,"662 OLD CALDER HIGHWAY,KEILOR,VIC,3036","33073634 ","SA002","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0007073","20190612PWA_02 ","MFB and a customer reported conductors and a transformer on fire. \nPole located outside a row of townhouses near intersection of Flora street and Calder Highway.\nThey advised it was a small fire and still currently on supply. CFA have been called.\nOn arrival the Powercor crew found that the connections in a krone box had overheated and the box melted. The small fire  extinguished by itself. \nThere was no ground fire, no reported injuries or third party property damage."]
[17,264,"16/06/2019","00:24",-35.295854089999999,143.45396876000001,"25 Woorinen-Goschen Road Woorinen South, Victoria","30259059","SHL004","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0007112","20190617PWA_01 ","VIC Fire reported pole fire, possible junction box, brigade en route.\nCrew found remains of a burnt fuse box.\nThere was no ground fire, no pole fire just light black stain from smoke and spatter.\nThere was no reported injuries or third party property damage."]
[17,265,"18/06/2019","08:44",-37.768209040000002,144.43989307000001,"3573 Geelong - Bacchus Marsh Rd, Parwan Vic","32163946","BMH006","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,"INC-0007183","20190624PWA_04 ","An employee reported a fire on a pole at the incident location.  \nOn arrival the crew found that a cross arm fire had occurred on a 22kV pole which burnt the cross arm only.  \nThere was no ground fire.  There were no reported injuries or third party property damages."]
[{"$f":"COUNTA(C303:O303,Q303,T303:V303)","v":17},266,"22/06/2019","17:03",-38.073948549999997,144.30901408,"110 Evans Rd, Lovely Banks 3213","31011781","CRO022","Low voltage AC (<1kV)","Urban"," - overhead service conductor (other)","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O303=\"\",\"\",IF(O303=\"LBRA only\",0.2,IF(O303=\"HBRA only\",1,IF(O303=\"within electric line construction area\",19.8,IF(O303=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"No forecast",{"$f":"IF(Q303=\"\",\"\",IF(Q303=\"No forecast\",0.1,IF(Q303=\"Low-moderate\",0.2,IF(Q303=\"High\",0.5,IF(Q303=\"Very high\",1,IF(Q303=\"Severe\",2,IF(Q303=\"Extreme\",3.5,5)))))))","v":0.1},{"$f":"IF(OR(P303=\"\",R303=\"\"),\"\",IF(AND(O303=\"within electric line construction area\",Q303=\"No forecast\"),1,P303*R303))","v":0.45999999999999996},"INC-0007177","20190624PWA_01 ","Vicfire & customer reported a pole fire at the incident location. \nWhen crews arrived they found a FOLCB located on the pole had caught on fire. \nMolten plastic and hot debris had dropped into the cable guard below resulting in a secondary fire start to the enclosed customer conduit and cable. \nNo ground fire start found or injuries reported."]
[17,267,"26/06/2019","05:36",-37.911929999999998,144.667303,"28 Nangiloc Crescent, Werribee 3030","60071893","WBE024","Low voltage AC (<1kV)","Urban"," - LV pillar","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,"INC-0007204","20190627PWA_02 ","Vic Fire reported pillar on fire,\nOn arrival crew found LV pillar had been on fire which was extinguished by CFA.\nNo reported injuries or third party property damage."]
[17,268,"29/06/2019","00:16",-37.666418,143.67389,"180 Browns Rd Scarsdale 3351","30005437","BAS021","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0007322","20190703PWA_01 ","VicFire reported a pole fire. \nOn arrival the fault crew found a melted FOLCB at incident location.\nThere was no ground fire, no reported injuries or third party property damage."]
[17,269,"2018-11-26","12:55:00",-37.740935370000003,144.70103882000001,"699 NEALE ROAD, DEANSIDE VIC 3336",31023328,"MLN021","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (other)","single phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0003718","20181212PWA_02 ","A customer reported a cable pulled out from the pole and also the meter board at the incident location. \nThe attended crew found that the service had been vandalised and cut off from both pole end and the meter board.\nThere also appears to be potential sign of fire at the pole end adjacent to FOLCB.\nThere was no injuries reported."]
[17,270,"2019-06-07","15:49:00",-38.214202669999999,143.54534960999999,"115 WARRION HILL ROAD WARRION VIC 3249",30054866,"CLC003","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,"INC-0007481","20190717PWA_03 ","Hung up fuse reported by customer"]
[17,271,"2019-04-25","12:56:00",-35.121338000000002,142.01991000000001,"139 LOWAN TANK ROAD - WALPEUP, VIC, 3507",32147524,"OYN001","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0006550","20190429PWA_02 ","Cross arm fire due to leakage current."]
[17,272,"2019-01-28","13:29:00",-36.679495129999999,142.30322362999999,"37 Field Days Road, Longerenong",33047656,"HSM003","Low voltage AC (<1kV)","Rural Long"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,"INC-0004015","20190129PWA_02","Vic Fire reported a grass fire at the incident location.  \nOn arrival the fault crew found that a crossarm on a private pole had broken allowing the open wire low voltage / service conductors to clash, dropping hot material to the ground, igniting a grass fire approx. 15 hectares in area. Failure on private line caused secondary failure at LV isols on our system and this secondary failure caused grass fire."]
[17,273,"2019-02-01","08:53:00",-36.050452999999997,143.170863,"308 Denneys Rd, Wycheproof VIC 3527",32027183,"CTN001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,"INC-0007642","20190730PWA_05","Report received of HV crossarm burnt off. There was no ground fire."]
[17,274,"2019-04-01","09:50:00",-35.026648999999999,142.74641399999999,"Mallee HWY, Manangatang 3546",30099720,"OYN003","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,"INC-0007643","20190730PWA_06","Report from customer of burn crossarm and conductors hanging low."]
[{"$f":"COUNTA(C312:O312,Q312,T312:V312)","v":0},275,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(O312=\"\",\"\",IF(O312=\"LBRA only\",0.2,IF(O312=\"HBRA only\",1,IF(O312=\"within electric line construction area\",19.8,IF(O312=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":""},null,"",{"$f":"IF(OR(P312=\"\",R312=\"\"),\"\",IF(AND(O312=\"within electric line construction area\",Q312=\"No forecast\"),1,P312*R312))","v":""}]
[0,276,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,277,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,278,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,279,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,280,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]

{"sheet":"3. Systems and Audit","index":4,"n_rows":29,"n_cols":5,"rows_kept":29,"cut":false,"hidden":false,"merged":[[28,1,29,4],[3,5,3,6],[4,5,4,6],[5,5,5,6],[6,1,6,4],[9,1,9,4],[14,1,14,4],[10,1,10,4],[13,1,13,4],[12,1,12,4],[11,1,11,4]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"Powercor"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2018/19"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"Powercor must provide:"}]
[]
[null,"Table 4 - Information or reporting systems"]
[null,"   (1) Name of any IT system used to collect fire start data or fault event data - i.e. SCADA system, or fault reporting system"]
[null,"   (2) Whether the fire recording or fault recording process has been audited or complies with a relevant Australian or industry standard - Yes or No"]
[null,"   (3) List any relevant Australian or industry standards that the fire recording or fault recording process complies with"]
[null,"   (4) Whether the data entered into or removed from the IT system has been audited - Yes or No"]
[]
[]
[null,"Table 4: Information or reporting systems"]
[]
[null,"Information or reporting systems","Name","System Audited","Relevant Standards"]
[null,"System 1","Network Incidents Database","Yes","None applicable"]
[null,"System 2","Outage Management System (OMS)","Yes","None applicable"]
[null,"System 3 ","Smallworld GIS (Graphical Information System)","Yes","None applicable"]
[null,"System 4"]
[null,"System 5"]
[null,"System 6"]
[null,"System 7"]
[null,"System 8"]
[]
[null,"The SGSPAA Internal Audit function undertakes a programme of work in accordance with the SGSPAA Group Internal Audit Plan. This internal audit activity covers elements of the systems and process used for capturing, recording and maintaining fire start data."]