{"text_format":"1","workbook":"xlsx","n_sheets":5,"sheets":["Contents","Cover","1. F-Factor summary","2. Individual fire start info","3. Systems and Audit"],"not_rendered":{"charts":0,"images":2,"macros":1,"external_links":2,"defined_names":97,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Contents","index":0,"n_rows":12,"n_cols":6,"rows_kept":12,"cut":false,"hidden":false,"merged":[[8,2,9,3],[2,1,2,10],[4,1,4,10]]}
[" "]
[]
[null,"Electricity Distribution Network Service Provider\nF-factor Reporting Template"]
[]
[null,"Table of contents"]
[]
[]
[null,null,"Cover sheet",null,null,"2. Fire start report"]
[]
[]
[]
[null,null,"1. F-factor summary",null,null,"3. Systems and Audit"]

{"sheet":"Cover","index":1,"n_rows":49,"n_cols":7,"rows_kept":49,"cut":false,"hidden":false,"merged":[[10,1,11,8],[13,1,13,8],[48,2,48,6],[42,2,42,3],[42,4,42,7],[46,2,46,6],[47,2,47,6],[38,2,38,3],[38,4,38,7],[41,2,41,3],[41,4,41,7],[37,2,37,3],[37,4,37,7],[32,3,32,8],[30,3,30,8],[15,1,15,8],[26,3,26,8],[28,3,28,8],[26,1,26,2],[31,3,31,5],[14,1,14,8],[16,1,16,8],[17,1,17,8],[21,1,21,8],[19,1,19,8]]}
[]
[]
[]
[]
[]
[]
[]
[null,"Distribution Network Service Provider"]
[null,"Fire start report"]
[]
[null,"This template is to be used by a DNSP to provide a fire start report to the AER in accordance with section 5 of the F-factor Order in Council.  "]
[]
[]
[null,"Colour coding of input sheets:"]
[null,"Dark blue = AER headings"]
[null,"Grey = AER instructions"]
[null,"Yellow = Input cells"]
[null,"Light orange = Automatically-generated cells"]
[]
[null,"Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so."]
[null,"The cells and structure of the spreadsheet is locked to prevent inadvertent interference with the automated settings."]
[null,"All dollar amounts are to be unrounded, and in nominal terms."]
[]
[]
[]
[]
[null,"DNSP:",null,"Powercor"]
[]
[null,"DNSP - trading name:",null,"Powercor Australia Ltd"]
[]
[null,"DNSP - Australian business number: ",null,"ACN 064 651 109"]
[]
[null,"Reporting year:",null,"2017/18"]
[]
[]
[]
[]
[null,"Business address","Address",null,"40 Market Street"]
[null,null,"Suburb",null,"Melbourne"]
[null,null,null,"State","Victoria","Postcode",3000]
[]
[null,"Postal address","Address",null,"Locked Bag 14090"]
[null,null,"Suburb",null,"Melbourne"]
[null,null,null,"State","Victoria","Postcode",8001]
[]
[]
[null,"Contact name/s","Rachel Perlaki"]
[null,"Contact phone/s","(03) 9683 4872"]
[null,"Contact email address/s","RPERLAKI@POWERCOR.COM.AU"]

{"sheet":"1. F-Factor summary","index":2,"n_rows":14,"n_cols":15,"rows_kept":14,"cut":false,"hidden":false,"merged":[[5,1,5,2],[3,6,3,8],[4,6,4,8],[5,6,5,8],[11,2,11,3],[12,2,12,3],[13,2,13,3],[6,2,6,3],[7,2,7,3],[8,2,8,3],[9,2,9,3],[10,2,10,3]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"Powercor"},"IRU target:",{"$f":"IF(SUM(K6:O6)=0,\"\",SUM(K6:O6))","v":468},null,null,null,null,null,null,"AusNet Services","CitiPower","Jemena","Powercor","United Energy"]
[null,"F-factor data reporting","IRU amount:",{"$f":"IF(SUM('2. Individual fire start info'!S38:S2000)=0,\"\",SUM('2. Individual fire start info'!S38:S2000))","v":401.65999999999985},null,null,null,null,null,"2016/17",247.7,3.4,9.6999999999999993,468,22.3]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2017/18"},"Revenue adjustment:",{"$f":"IF(OR(D1=\"\",D2=\"\"),\"\",15000*(D1-D2))","v":995100.00000000221},null,null,null,null,null,"2017/18",247.7,3.4,9.6999999999999993,468,22.3]
[null,null,null,null,null,null,null,null,null,"2018/19",247.7,3.4,9.6999999999999993,468,22.3]
[null,"Table 2: Summary of total fire starts by F factor Order definition",null,null,null,null,null,null,null,"2019/20",221.1,3.4,9.6999999999999993,412.8,22.3]
[null,"This is a summary of data in worksheet \"2. Fire Start Report\"",null,null,null,null,null,null,null,null,{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>K1),\"\",LOOKUP($B3,$J2:$J5,K2:K5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>L1),\"\",LOOKUP($B3,$J2:$J5,L2:L5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>M1),\"\",LOOKUP($B3,$J2:$J5,M2:M5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>N1),\"\",LOOKUP($B3,$J2:$J5,N2:N5))","v":468},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>O1),\"\",LOOKUP($B3,$J2:$J5,O2:O5))","v":""}]
[null,"Kind of Fire Start by definition of fire start under clause 5 of F-factor Order","Total fires by cause"]
[null,"Started in or originated from a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B8)","v":188}]
[null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B9)","v":38}]
[null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B10)","v":30}]
[null,"Started by lightning striking a distribution system or a part of a distribution system ",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B11)","v":7}]
[null,"Started by any other thing forming part of or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B12)","v":13}]
[null,"Otherwise started by a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$2000,'1. F-Factor summary'!$B13)","v":0}]
[null,"Total",{"$f":"SUM(C8:C13)","v":276}]

{"sheet":"2. Individual fire start info","index":3,"n_rows":317,"n_cols":25,"rows_kept":317,"cut":false,"hidden":false,"merged":[[25,1,25,18],[27,1,27,20],[26,1,26,21],[35,19,35,21],[33,1,33,4],[35,2,35,10],[28,1,28,18],[29,1,29,18],[35,11,35,13],[35,14,35,17],[13,1,13,11],[22,1,22,21],[24,1,24,21],[14,1,14,20],[15,1,15,18],[16,1,16,18],[18,1,18,18],[21,1,21,18],[19,1,19,18],[23,1,23,18],[20,1,20,18],[17,1,17,18],[3,22,3,24],[4,22,4,24],[5,22,5,24],[7,1,7,21],[11,1,11,2],[9,1,9,21]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"Powercor"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2017/18"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"\"Enter into this worksheet fire start data, from any IT system, which have been recorded by \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\". Note that fire starts must be in accordance with the definition of a fire start in the Order In Council.\"","v":"Enter into this worksheet fire start data, from any IT system, which have been recorded by Powercor. Note that fire starts must be in accordance with the definition of a fire start in the Order In Council."}]
[]
[null,"\"Fire\" should be interpreted using its common meaning and can be defined as a process in which substances combine chemically with oxygen from the air and typically give out bright light, heat and smoke. A fire should be recorded where there is evidence of smoking, charring, scorching, burning or any other evidence that a fire had occurred.  "]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"Powercor must provide:"}]
[]
[null,"Table 3 - Individual Fire Starts"]
[null,"   (1) Date - dd/mm/yyyy"]
[null,"   (2) Time - if known, the 24-hour time of the fire start hh:mm"]
[null,"   (3) Latitude and longitude of the fire start as decimal coordinates"]
[null,"   (4) Address of the property on which the incident occurred or closest to the incident"]
[null,"   (5) Asset number for the asset nearest the fire start"]
[null,{"$f":"\"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the \"&B1&\" network\"","v":"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the Powercor network"}]
[null,"   (7) Voltage on the line in which the fire start occurred (note: this may not be the nearest polyphase overhead line)"]
[null,"   (8) Network categorisation - CBD, Urban, Rural Long or Rural Short"]
[null,"   (9) Asset type of primary asset causing fire in accordance with OSIRIS asset categories"]
[null,"   (10) Where the asset involved in the fire is a transformer or an overhead or underground line, provide the phase, or phases, of the line or transformer"]
[null,"   (11) Kind of fire start in accordance with categories specified in Clause 5 of the F-factor Order-In-Council"]
[null,"   (12) Identify the location of the fire start in accordance with the categories specified in Clause 11(b) of the F-factor Order-In-Council"]
[null,"   (13) Provide the BOM fire danger rating applicable at the time of the fire start (data is available on the EM-COP website)"]
[null,{"$f":"\"   (14) \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\"'s record number for the incident\"","v":"   (14) Powercor's record number for the incident"}]
[null,"   (15) ESV's OSIRIS reference number for the incident"]
[null,"   (16) Free text description of the fault containing relevant comments from field reports "]
[]
[]
[]
[null,"Table 2: Individual Fire Starts"]
[]
[null,"Number","Fire starts",null,null,null,null,null,null,null,null,"Fire Type",null,null,"Risk Factors",null,null,null,"IRU \namount","Additional information"]
[null,null,"Date 1","Time 2","Latitude 3","Longitude 3","Address of incident 4","ID of \nnearest \nasset 5","ID of nearest \npolyphase \nline 6","Voltage of line in which \nfire start \noccurred 7","Network categorisation 8","Type of primary asset \ninvolved in fire start 9","Phase(s) of \nline or \ntransformer 10","Kind of fire start as per Clause 5\nof F-factor Order-In-Council 11","Location \narea 12","Location\nmultiplier","Fire \ndanger \nrating 13","Danger multiplier","Product of multipliers","DNSP record number 14","OSIRIS \n(ESV) reference \nnumber 15","Fault \ndescription 16"]
[{"$f":"COUNTA(C38:O38,Q38,T38:V38)","v":17},1,"2017-07-01","06:17:00","-37.98302685","144.50026095","720 Old Melbourne Rd., Little River.","30059970","FNS022","Low voltage AC (<1kV)","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",{"$f":"IF(O38=\"\",\"\",IF(O38=\"LBRA only\",0.2,IF(O38=\"HBRA only\",1,IF(O38=\"within electric line construction area\",19.8,IF(O38=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":1},"No forecast",{"$f":"IF(Q38=\"\",\"\",IF(Q38=\"No forecast\",0.1,IF(Q38=\"Low-moderate\",0.2,IF(Q38=\"High\",0.5,IF(Q38=\"Very high\",1,IF(Q38=\"Severe\",2,IF(Q38=\"Extreme\",3.5,5)))))))","v":0.1},{"$f":"IF(OR(P38=\"\",R38=\"\"),\"\",IF(AND(O38=\"within electric line construction area\",Q38=\"No forecast\"),1,P38*R38))","v":0.1},13270,"20170731PWA_05","At 6:17am, a fault was reported as All Supply Fail at the incident location. The crew attended and found that a LV Crossarm and fuse box had caught fire overnight. Debris fell to the ground but did not start a fire. The crew made repairs as required and the site was made safe. There were no reported shocks, injuries or ground fire.",null,null,"Overhead conductors"]
[17,2,"2017-07-05","12:04:00","-36.68321263","144.92031643","431 Andersons Rd., Goobarup.","33102775","SHP021","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"No forecast",0.1,0.1,13205,"20170706PWA_02","A customer reports a tree had been cut and it had fallen onto the power lines and started a fire at the above address. A crew attended and found the land owner had been pushing trees over with a bull dozer when one of the trees had contacted an SWER O/H HV conductor, breaking the conductor, causing it to fall to the ground. The contacting tree branch started to burn but there was no ground fire start. The customer extinguished the fire. Protection operated. Colbinabbin P244A ACR went to lock out. The crew repaired the broken conductor and restored supply. Final conductor height btn P12 and P12E Karagounis S/L is 8.3m mid span. There were no reported shocks, injuries or 3rd party damage.",null,null," - overhead conductor (bare; aluminium core steel reinforced)"]
[17,3,"2017-07-09","18:40:00","-36.87484888","143.87416363","3842 Bendigo Maryborough Rd., Eddington.",32029298,"MRO007","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,13207,"20170711PWA_01","VicFire reported that a conductor was down at the incident location,  A customer also reported flickering lights and partial supply for a period of approximately 15 minutes.  On arrival the crew found that a conductor of a single phase spur line had failed approximately 10m from T/off pole 213 Tarnagulla, the conductor remained back-fed via the HV winding of the load side transformer for a period prior to Tarnagulla ACR tripping to lockout on SEF. A fuse on Tarnagulla P211 operated but hung up. Approximately 12 small patches of burnt crop were observed by the crew, caused by the downed HV conductor remaining in an energised state until the ACR operated.There were no reported injuries or 3rd party damage. \tNAO requested crew to send section of failed conductor to asset investigations team.",null,null," - overhead conductor (bare; all aluminium conductor)"]
[17,4,"2017-07-14","09:29:00","-37.86957256","144.72514986","1 Industrial Ave, Hoppers Crossing.","30115749","LV005","22kV AC","Urban"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,13267,"20170731PWA_02","A customer informed a broken insulator on the ground and the wire resting on cross arm at the incident location. On arrival the Powercor crew found that a Pole Fire had occurred on INDUSTRIAL DUNLOP P02E (LIS 204466 intermediate pole). The crew made the place safe and repairs arranged.  There was no ground fire, third party damage, injury, outage or HVI found.",null,null," - overhead conductor (bare; copper)"]
[17,5,"2017-07-25","11:49:00","-34.35970805","141.97983566","Cnr of Meridian Rd and Millewa Rd., Merrinee.","32141660","RCT023","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"No forecast",0.1,0.1,13254,"20170726PWA_02","Emergency Services reported a grass fire at the incident location. Upon arrival, the Powercor crew found that a bird flashover and small grass fire (150 sq mts). No obvious damage on network assets found. Crew made the place safe.\r\nAppears a bird flashed over from live line flex to steel crossarm. A FFU raised to complete repairs including earthing. There was a ground fire (150 sq mts) no injuries.",null,null," - overhead conductor (bare; steel)"]
[17,6,"2017-07-30","21:56:00","-37.60142707","143.84094246","235 Albert St., Sebastopol.","34000831","BAS034","Low voltage AC (<1kV)","Urban"," - lamps (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,13266,"20170731PWA_01","A report was received from Vic Fire that a street light was on fire outside of 235 Albert Street Sebastopol. On arrival the crew found that one of the light heads on the pole in the median strip at the above location had caught fire and self-extinguished. The crew isolated supply to the pole and the light will be replaced at a later date. There was no injury, shock, ground fire or third party damage.",null,null," - overhead conductor (ABC)"]
[17,7,"2017-08-03","17:50:00","-36.74891577","144.28504632","79 Lucan St., Bendigo.","30027839","EHK033","Low voltage AC (<1kV)","Urban"," - fuse (any other type)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,13327,"20170818PWA_01","Vicfire called reporting pole fire. Upon arrival crew were advised that the CFA had already departed. No sparking was evident from the FSD at pole LUCAN 73 (LIS-424910). The FSD is a normally open point between bare LV and LV ABC. The cause of the sparking is believed to have been incited by wet weather. Crew advised that the LV fuse back at the substation had blown therefore there was no more evident sparking. Crew advised only slight burning, (hardly visible) of the cross-arm under which sat the fuse box. The crew replaced the partially melted fuse box and restored supply. There was no other damage to assets or private property.",null,null," - overhead conductor (covered uninsulated)"]
[17,8,"2017-08-03","18:51:00","-37.88807590","144.61829758","4 Valley Mews, Wyndham Vale.","30320417","WBE023","Low voltage AC (<1kV)","Rural Short"," - fuse (any other type)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,13322,"20170817PWA_01","Powercor was contacted by several customers indicating no supply. On arrival, the crew found that the LV fuse board of the Kiosk substation ‘VALLEY-GREENS’ had  caught fire due to an overheating fault.\r The fire was contained inside the kiosk substation and extinguished by itself. The LV board was deemed not serviceable and the 3 x LV cables attached to the LV board and connections were damaged. The crew made the place safe and at the time of my call the crew was in the process to repair the LV cables. Repair works still to be completed. There were no reported injuries, third party damage or ground fire.",null,null," - overhead conductor (insulated)"]
[17,9,"2017-08-15","18:24:00","-36.71372268","142.19901795","2 Bradbury lane, Horsham.","30260985","HSM010","Low voltage AC (<1kV)","Urban"," - fuse (any other type)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,13344,"20170828PWA_01","Vic Fire reported an overhead service cable on fire at the incident location.  On arrival the crew found that the LV Fused Mains Box connected to the overhead service had been on fire  The LV Fused mains box had melted, and parts had fallen to the ground.\r\nThere was no ground fire or any other damage caused by this incident.",null,null,"Service lines"]
[17,10,"2017-08-20","07:36:00","-38.38342379","142.16867619","2976 Princes Highway, Port Fairy.","30135294","KRT013","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,13360,"20170908PWA_03","The CFA reported a pole fire at the incident location. On arrival the crew found that the pole had burnt and the CFA had extinguished it. Talking to the crew there was no ground fire. No third party damage or injury was reported. The crew made the site safe, conducted repairs and supply was restored.",null,null," - overhead service conductor (residential)"]
[17,11,"2017-09-10","21:06:00","-38.11347315","144.65764493","2 The Esplanade, Portarlington.","32070587","DDL021","Low voltage AC (<1kV)","Rural Short"," - fuse (any other type)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,13375,"20170926PWA_06","CFA reported a pole fire at the incident location. On arrival the crew found that fuse box, LV droppers and conduit had melted due to an overheated connection. The CFA told the crew they had extinguished a fire prior to their arrival and only melted plastic on the ground.\r\nNo ground fire, no injuries, no third party damage.",null,null," - overhead service conductor (commercial / industrial)"]
[17,12,"2017-09-11","16:19:00","-37.97095435","141.73206568","Henty Highway, Condah.",33058882,"HYT011","22kV AC","Rural Short"," - pole (concrete)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"No forecast",0.1,0.1,13362,"20170912PWA_03","Vicfire reported a two vehicle collision brought down power lines and started a grass fire at the incident location. On arrival the crew found that a truck had veered off the road to miss another vehicle hitting the pole and the HV conductors had started multiple small fires (approx. 5m2 in total).\r\nHamilton Police were also in attendance and reported no injuries.",null,null," - overhead service conductor (subdivision / construction)"]
[17,13,"2017-09-17","08:57:00","-38.25233286,","142.41669021","420 Thwaites Rd., Winslow.","32195765","KRT012","Low voltage AC (<1kV)","Rural Long"," - fuse (any other type)","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,13374,"20170926PWA_05","The CFA reported a fire in the meter board at their dairy at the incident location. On arrival the Electrical Inspector found that a Low Voltage fuse/s has failed and caused the meter panel including the meter to catch fire. The LV fuses are a Powercor asset. Talking to the Electrical Inspector there was no ground fire. No third party damage and no injury was reported. The crew made the site safe, the meter panel and associated equipment was replaced and supply was restored.",null,null," - overhead service conductor (other)"]
[17,14,"2017-09-18","18:57:00","-34.18144579","142.05563670","128 Fifth St., Merbein.","32142995","MBN014","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,13372,"20170926PWA_03","CFA Comms reported pole fire at 128 Fifth St Merbein.  On arrival crew found HV cross arm that had caught fire but had extinguished.  Crew inspected arm which had charring on it and raised fault follow up to repair.  No injuries, no ground fire, no third party damage.",null,null," - underground service cable (residential)"]
[17,15,"2017-09-18","19:44:00","-34.12829024","142.00884079","791 Wentworth Rd., Yelta.","32150293","MBN013","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,13371,"20170926PWA_02","CFA Comms reported wires sparking at 791 Wentworth Rd Yelta.  On arrival crew found HV intermediate cross arm that had caught fire but has since extinguished.  Insulator had snapped as a result of the fire and conductor was on the cross-arm.  Crew isolated and repaired on site.  No injuries, no ground fire, no third party damage.",null,null," - underground service cable (commercial / industrial)"]
[17,16,"2017-09-25","04:41:00","-38.27937004","142.20564062","Spencer rd (Cnr of old spencer rd), Tarrone.","30144811","KRT013","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,13373,"20170926PWA_04","Person driving past reported a pole fire. On arrival the crew found that the High Voltage cross arm on pole 1 had burnt. The crew isolated supply and installed a new cross-arm on a raiser bracket. \rThere was no reported ground fire, injury or shocks.",null,null," - underground service cable (subdivision / construction)"]
[17,17,"2017-09-28","16:16:00","-36.30583987"," 141.06623411","692 Dinyarrak, Lillmur.",33047492,"NHL031","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"No forecast",0.1,{"$f":"IF(OR(P54=\"\",R54=\"\"),\"\",IF(AND(O54=\"within electric line construction area\",Q54=\"No forecast\"),1,P54*R54))","v":0.1},13395,"20171002PWA_01","CFA reported a wire down and a fire start at the above location. A crew attended and found a tree had fallen across 1 phase of a single phase HV line, breaking 2 Cross arms and starting a ground fire but no conductor on ground. CFA attended and extinguished fire. One blown 16K HV fuse at P443 Kaniva S/L. Crew replaced broken blown fuse and HV Xarms at P25 and P26 Dinyarrak S/L. Fire started at tree that had fallen onto line. Fire area approx. 50m x 25m. Grass fire in paddock. No third party damage.\r\nThere were no reported shocks, injuries or 3rd party damage.",null,null," - underground service cable (other)"]
[17,18,"2017-10-04","11:29:00","-36.34760627","145.44063807","335 Ford Rd., Grahamvale.","33096629","SHN024","Low voltage AC (<1kV)","Rural Short"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,13398,"20171005PWA_01","A customer reported a fire on the pole at the incident location. On arrival the crew found that a neutral connection in a crossarm mounted junction box had overheated. Hot debris fell to the ground causing a grassfire of approx. 1m x 2m= 2m2 on the roadside. The crew also stated that the customer had to replace a damaged power circuit breaker on their switchboard. The initial report stated that the customer had sustained damage to some equipment, however this could not be verified. There were no injuries reported.",null,null,"Underground cables"]
[17,19,"2017-10-07","14:38:00","-35.50218803","143.67216428","21 cornish Avenue, Tresco.",30247555,"KGT004","22kV AC","Rural Long"," - underground cable","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,13412,"20171009PWA_03","Powercor received report of a fire. Fire was out on when crew attended onsite.  Cause  to be confirmed, however it is  suspected that the fire started at the HV Underground Cable Head Pole and was possibly a bird flashover (KGT004).",null,null," - underground cable"]
[17,20,"2017-10-07","21:51:00","-38.388109","142.565220","10440 Princes Hwy, Allandford.","31030223","WBL002","22kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,13410,"20171009PWA_01","Powercor received a call from VicFire reporting “sparking wires”  at Warrnambool.\r When crews arrived on site they found CFA crews in attendance and they had extinguished a number of spot fires, approx. 5m x 80m along the Princes Hwy, approx. 1.2km east of Staffords Rd. The cause of the fires appeared to be a broken 22kV conductor.",null,null," - underground communications cable"]
[17,21,"2017-10-08","11:49:00","-38.04708347","144.14165308","BANNOCKBURN-SHELFORD Rd., Bannockburn.","30231988","GL012","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,13411,"20171009PWA_02","On Sun 8 Oct 2017 at 11:49am, Powercor received a call from VicFire reporting a wire down at LIS989876 with a small grass fire when crews arrived at the incident site, they found a broken tree branch across the 22kV HV overhead conductors. A small ground fire (2m x 2m) near the base of the pole had been extinguished by the CFA. The tree was part of the Bannockburn Recreation Reserve. No conductors fell to ground. No other third party property damage was reported. No injuries were reported.",null,null,"Poles"]
[17,22,"2017-10-09","12:56:00","-36.35844026","142.99145627","27-29 Corack Rd., Donald.","32019143","CTN006","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,13415,"20171011PWA_02","Numerous customers reported no supply . Crew attended to find end of HV cross-arm  had burnt off  and HV insulator was resting on LV cross-arm.\r\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - pole (concrete)"]
[17,23,"2017-10-11","20:25:00","-38.11989462","144.32707340","18 Heather St., Hamlyn Heights.","30074807","GL013","Low voltage AC (<1kV)","Urban"," - fuse (any other type)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,13463,"20171103PWA_03","A customer reported pole fire outside the above address. Crew Located Burnt out FSD. Report from customers that had been on fire and now out there was no ground fire, no injuries or third party property damage.\r\nRecord located during OMS month end search.",null,null," - pole (steel)"]
[17,24,"2017-10-11","15:57:00","-34.21014657","142.19179688","473-481 Karadoc Ave, Nichols Point.","30095498","RCT011","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,13461,"20171103PWA_01","Pole fire on \"Pole 8\". HV Xarm Replaced. No report of ground fire.\r\nRecord found during OMS data check at month end.",null,null," - pole (wood)"]
[17,25,"2017-10-11","18:41:00","-37.58894686"," 143.96398948","2805 Old Melbourne Rd., Dunnstown.","33006274","BAS023","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,13462,"20171103PWA_02","Customer rang to advise of intermittent supply and sparks/fire coming from pole out front of property. Crew attended and found the foot path side EDO fuse had blown but the tube had hung up. This cause the tube to arc and burn internally. The crew also found the copper flex between the EDO unit and the O/H mains had frayed and stranded. The crew isolated the transformer, repairing the flex and replacing the burnt EDO tube. The crew then restored supply. There was not ground fire start. There were no reported shocks, injuries, or 3rd party damage.\rNote: Incident was not reported to the A/H NAO. It was picked up the next day by the asset investigation group.",null,null,"Crossarms"]
[17,26,"2017-10-12","07:09:00","-35.24898179","143.47224915","Athorn Rd., Woorinen.","31022238","SHL004","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,13464,"20171103PWA_04","Passing truck driver advised crossarm rotten, has broken and wires hanging low with insulator off  beam, not within reachable height but a breeze could cause wires to make contact with pole.  In Athorn Rd between Ridge  Rd and Goodman Rd.  Area also known as Woorinen North or Beverford.\r\nOn arrival crew found crossarm burnt off at end.",null,null," - crossarm (wood)"]
[17,27,"2017-10-13","09:40:00","-35.05216529","142.50476315","Lot 1 Daley Rd., Ouyen.","32153108","OYN003","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,13458,"20171030PWA_02","A customer reported a pole down at the incident location. On arrival the crew found that a pole fire the pole appears to have burnt from the base upward and was laying on the ground.\r\nThe crew also reported there was no ground fire. Third party damage in the form of a dead sheep was found by the crew. No injury was reported.",null,null," - crossarm (steel)"]
[17,28,"2017-10-14","01:52:00","-37.96336084","144.50522521","7 Harold court, Little River.","33040949","FNS022","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,13456,"20171030PWA_01","Vicfire reported a fire at this address. On arrival the crew found that a fused Overhead line connector box had failed.\r\nThe falling ash and debris fell to ground without causing a ground fire. There was no reported injuries or third party property damage.",null,null," - crossarm (other)"]
[17,29,"2017-10-18","13:20:00","-38.0187035","144.391754","39 Kees Rd., Lara.","30071450","FNS012","22kV AC","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,13425,"20171019PWA_01","Local resident reported that a tree branch has fallen  across the high voltage overhead line one phase has broken and  a small ground fire  at the incident location.\r\nOn arrival the fault crew found that a branch from a large tree towering over the line had broken off, falling onto the high voltage overhead breaking the outer phase conductor which then fell onto the low voltage circuit below.\r\nThere was no injury as result of this incident. High voltage injection suspected but no damage found (over 100 customers checked). Crew carried out repairs to conductors.",null,null,"Overhead assets"]
[17,30,"2017-10-25","03:51:00","-34.29972053"," 142.18533345","15 Avocat Avenue N, Red Cliffs.","32141274","RCT023","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13465,"20171108PWA_01 ","Pole fire found on Avocat Sewerage 6. Conductors down in tree, tree on fire. HV And LV crossarms replaced.\r\nThere was no ground fire, no reported injuries or third party property damage.",null,null," - capacity balancing units"]
[17,31,"2017-10-29","15:48:00","-37.52578822",143.86604303999999,"2 Easey St., Invermay Park.",33005393,"BAN007","22kV AC","Rural Short"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,13460,"20171031PWA_01","A customer rang to advise a pole was arcing and sparking resulting in a ground fire start at the incident location. A crew attended and found that at P8 Swinglers S/L, the roadside boric acid HV fuse had hung up and burnt, dropping debris on the ground resulting in a ground fire of approx. 1m/sq on road reserve.  A CFA crew attended and extinguished the fire. The crew replaced the failed HV fuse and restored supply. There were no reported shocks or injuries.Note: The original fuse operation is related to a previous 48hr report on the 29/10/2017 at 15:48hrs when a tree contact the HV conductors at 12 Taylor Rd., Invermay.",null,null," - connector / termination"]
[17,32,"2017-11-02","13:59:00","-38.22273909","141.75523419","1514 Clay Rd., Tyrendarra.","30091494","PLD001","12.7kV AC (SWER)","Rural Long"," - fuse (boric acid)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,13539,"20171220PWA_01 ","A Fault crew attending following an outage found that an Boric Acid fuse had operated at the incident location, however the barrel of the Boric Acid fuse stayed in position without dropping down.  \r\nThe barrel then caught fire. There was no ground fire.  There were no reported injuries or third party property damages.",null,null," - dropper / bridge"]
[17,33,"2017-11-09","19:43:00","-36.37549983","145.43190412","109 Doyles Rd., Grahamvale.",33092008,"STN024","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13477,"20171110PWA_03","Crew attended to find small ground fire had been extinguished by Vic Fire on road verge. \r\nEvidence of a dead crow at the base of the pole. Feeder CB STN024 operated just prior to report from Vic Fire.\r\nThere were no injuries or third party property damage.",null,null," - guy wire"]
[17,34,"2017-11-11","10:36:00","-38.11631","144.328949","134 Vines Rd., Hamlyn Heights.","32080104","GL013","Low voltage AC (<1kV)","Urban","Service lines","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13479," 20171113PWA_03","Vicfire reported a fire at the incident location. On arrival the crew found that a neutral screen service cable had failed at the house end roller termination, resulting in blackening of the POA area and the live service cable falling to the ground. The service cable falling to the ground in turn resulted in a grassfire of approx. 1m x 2m= 2m2 in a garden bed in the front yard of the house. There were no injuries or other damage reported.",null,null," - insulator tie wires / connections"]
[17,35,"2017-11-11","10:53:00","-37.75861529","142.11218310","541 W Schultz Rd., Hamilton.","33058168","NRB-HTN","66kV AC","Unknown"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,13480,"20171113PWA_04","A Powercor crew were patrolling following a 66kV fault, and reported a fire at the incident location. On arrival the crew found that an Ibis had caused a flashover on a 66kV pole and fallen to the ground starting a grassfire of approx.  200m2 of mostly road reserve, with a small area of private land burnt and minor fence damage. \r\nThe crew extinguished the fire, the CFA did not attend. There were no injuries or other damage reported.",null,null," - insulators"]
[17,36,"2017-11-12","06:45:00","-37.8768234","142.29509","59 Watton St., Penhurst.","32127148","HTN003","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13488,"20171117PWA_05","A Powercor fault crew were patrolling following a feeder outage and found a crossarm burnt off at the strap bolt at the incident location. There was no ground fire and no reported third party damage or any injuries.",null,null," - tower"]
[17,37,"2017-11-12","11:59:00","-37.0883636","143.797623","437 Landrigan Rd., Carisbrook.","33011414","MRO007","Low voltage AC (<1kV)","Rural Long"," - connector / termination","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,13478,"20171113PWA_02","Crew attended to find a connection between bare LV Mains and Service Connection Junction Box had Burnt off on the red phase.\r\nA small ground fire on the road verge area resulted.\rThis fire was  extinguished by Vic Fire .\rOn arrival crew carried out repairs. There was no property damage, No injuries or reported shocks.",null,null," - traction lines"]
[17,38,"2017-11-14","05:11:00","-35.05154696","143.31663428","70 MURRAY STREET, PIANGIL.","30147267","SHL002","Low voltage AC (<1kV)","Rural Long"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,{"$f":"IF(OR(P75=\"\",R75=\"\"),\"\",IF(AND(O75=\"within electric line construction area\",Q75=\"No forecast\"),1,P75*R75))","v":0.4},13651,"20180123PWA_07","Crew attended to find Junction Box had burnt out between Gang Operated LV Switch and customer Underground Mains.\nNo Ground Fire , No property damage, No injuries, No reported shocks.",null,null,"Underground assets"]
[{"$f":"COUNTA(C76:O76,Q76,T76:V76)","v":17},39,"2017-11-16","14:36:00","-37.3616676","144.550919","1808 Mt Macedon Rd., Woodend.","31006854","WND012","22kV AC","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O76=\"\",\"\",IF(O76=\"LBRA only\",0.2,IF(O76=\"HBRA only\",1,IF(O76=\"within electric line construction area\",19.8,IF(O76=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"Low-moderate",{"$f":"IF(Q76=\"\",\"\",IF(Q76=\"No forecast\",0.1,IF(Q76=\"Low-moderate\",0.2,IF(Q76=\"High\",0.5,IF(Q76=\"Very high\",1,IF(Q76=\"Severe\",2,IF(Q76=\"Extreme\",3.5,5)))))))","v":0.2},0.91999999999999993,13485,"20171117PWA_02","Emergency Services informed a pole fire at the incident location. On arrival the crew found that a HV conductor sitting on the cross arm and the arm smoking (one stage the arm and pole slightly burnt through). The protection operated. This was due to a damage/crack on top part of insulator that came off with conductor and rested on the arm. The crew made the place safe and repairs done.  There was no ground fire, third party damage or injury.",null,null," - LV pillar"]
[17,40,"2017-11-17","10:17:00","-38.1196556","144.349167","41- 47 Roseneath St., North Geelong.","32081845","GB031","22kV AC","Urban"," - overhead conductor (bare; copper)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13486,"20171117PWA_03","A contractor reported that a scissor lift has inadvertently contacted overhead lines at the incident location. On arrival the fault crew found that a contractor was repairing the scissor lift which was located under the high voltage overhead line, not being fully aware of the high voltage line above. \r\nThe contractor raised the lift which contacted the live overhead line. This caused arcing between line and scissor lift, the overhead power line broke falling onto the ground starting a small fire at the incident location.\r\nMFB crews arrived on site and a small fire was extinguished. (1m by 0.5m). The operator of the lift appeared to be uninjured, he was advised to seek medical attention.",null,null," - services pit"]
[17,41,"2017-11-18","11:36:00","-36.0738831","145.417465","128 Allens Rd., Numurkah.","32185391","SHTS-NKA2","66kV AC","Unknown"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13495,"20171121PWA_02","Vicfire advised of a x-arm fire AT P375 ON SHTS-NKA No.2 line. Upon arrival crew found that the 66kV x-arm had burnt off and the 66kV conductor had landed on the subsidiary 22kV line breaking a 22kV insulator.\r\nThe structure was a 66kV/22kV INTER. Maree in operations organised the 66kV switching for repairs to be made. All repairs to 66kV and 22kV apparatus were made by 17:30\r\nCausal effects lending to the incident were a dirty 66kV insulator and misting rain at the time of the fault causing the 66kV to track over the x-arm strap onto the arm thereby creating an arm fire.\r\nA ground fire ensued in road reserve covering an area of approximately 70m x 5m, there was no reported damage to private property.",null,null,"Transformers"]
[17,42,"2017-11-22","08:04:00","-35.00414586","143.04091930","578 Walters Rd., Manangatang.","30350763","BBD014","12.7kV AC (SWER)","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","single wire earth return (SWER)","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,13506,"20171127PWA_01","Customer reports a fire start after harvester contact SWER O/H conductor on property. Customer states on the 22nd Nov he was operating a harvester in the paddock when a ground fire start occurred, burning approx. 20 acres of stubble paddock. CFA attended and extinguished fire. Smart meter data shows a momentary outage for a SWER ACR reclose at the time of this event. \r\nThe next day ( 23rd Nov ) the customer notices a burn make on the harvesters GPS aerial. The fire started when the harvester drove under the SWER overhead conductor. A crew attended and measured to SWER O/H at 5.8m ( Policy states the minimum clearance height for transvers able land is 5.6M ). The crew fitted a raiser bracket to P102 and re tensioned the SWER conductor at P103 to achieve a mid span ground clearance of 7.1m. No damage to the 3/2.75SC. There were no reported shocks or injuries. Note: The span btn P102 and P103 was listed as low conductor in March 2016 at 5.5m. P103 was replaced in April 2016 to achieve a clearance of 5.8m. Customer harvester clearance is 6.0m to top of aerial.",null,null," - transformer (pole mounted)"]
[17,43,"2017-11-22","14:41:00","-38.16677763","144.37001824","186 Fyans St., South Geelong.","32069759","GLE033","22kV AC","Urban"," - switch (disconnector/isolator)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13504,"20171123PWA_01","A bird flashover occurred at pole adjacent to 170 fryans st ( Lis 17498). Due to fault current there was a flashover  at an isolator pole( Lis 17264) which caused a ground fire  due to fallen debris.\r\nThere were no reported injuries or third party property damage.",null,null," - transformer (kiosk mounted)"]
[17,44,"2017-11-22","14:17:00","-35.955452","145.567657","381 Churchill Rd., Yarroweyah.","32185760","CME015","22kV AC","Rural Short"," - switch (disconnector/isolator)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13505,"20171123PWA_02","VicFire reported a fire at the incident location. On arrival the crew found that a bird had caused a flashover on open point switch pole, causing the bird to fall to the ground resulting in a ground fire on road reserve. \r\nThere were no reported injuries.",null,null," - transformer (ground outdoor mounted)"]
[17,45,"2017-11-25","19:11:00","-37.84726520","144.67978120","1 Verona avenue, Tarneit.","35264672","LV001","22kV AC","Rural Short"," - transformer (kiosk mounted)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,13507,"20171127PWA_02","Customer reported car hit pole at the incident location. On arrival the crew found serious multiple vehicle accident and one of the vehicle had hit the Sayers – Verona 315kVA Kiosk substation causing major damage to the substation starting fire and oil leak as a result of the vehicle impact.\r\nNo oil loss into any nearby drains. Ground fire at the base of the kiosk (small area), possible third party property damage to the fence adjacent to the substation due to fire and smoke. The occupants of the vehicle were taken to hospital prior to the fault crew arriving at the scene.",null,null," - transformer (indoor chamber mounted)"]
[17,46,"2017-11-26","16:30:00","-35.85244828","142.29081810","1175 Rosebery-Rainbow Rd., Beulah.",32109148,"HSM003","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,13508,"20171127PWA_03","A Powercor LSA crew attended a reported fire at the incident location. On arrival the crew found that a cactus bush centre runner had caused a HV conductor to break and fall to the ground starting a grassfire of approx 100 acres of private grass land. The CFA extinguished the fire, There were no reported injuries or other damage.",null,null," - transformer (any other type)"]
[17,47,"2017-11-26","02:22:00","-35.9405327","145.66951","146 (150) Pullar Rd., Cobram.",33083463,"CME021","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (residential)","two phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13516,"20171201PWA_01","Vic Fire rang to advise of wire down and small grass fire at the incident location. On arrival the crew found a tree limb had damaged service wire resulting in a grass fire of approx. 2m X 10m  \r\nA Vic Fire crew attended and extinguished the fire. There were no reported shocks or injuries.",null,null," - measurement transformer (current transformer)"]
[17,48,"2017-11-28","02:51:00","-38.07099243","144.22791481","1366 Midland Hwy (Cnr Bakers Bridge rd), Gheringhap.","30266389","GL015","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,13511,"20171129PWA_01","At 2:51am, emergency services reported conductor down across the road at the incident location. Attending crew found the red phase of steel conductor had broken between P71 (LIS-59813) and P1 (LIS-747554) resulting in a small ground fire/burns to the ground. The fire was approximately 3m long (100mm wide).\r\nThe crew indicated the cause was a failed/deteriorated splice and conductor. The crew made the site safe and handed over to the daytime faults crew, who later replaced the damaged span. There was no third party damage or injuries reported.",null,null," - measurement transformer (voltage transformer)"]
[17,49,"2017-11-28","15:45:00","-36.02009792","145.3861068465576","1335 Boothroyds Rd., Numurkah (Katunga).","32186418","NKA006","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (residential)","two phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,13517,"20171204PWA_01","Vic Fire rang to advise of a  grass fire at the incident location. On arrival the crew found a tree had fallen onto service line straining connections in fuse box, this in turn caused arcing  resulting in a grass fire of approx. 0.5HA. \r\nA Vic Fire crew attended and extinguished the fire. There were no reported shocks or injuries.",null,null," - measurement transformer (capacitive voltage transformer)"]
[17,50,"2017-11-29","13:57:00","-38.30334862","142.99422427","380 Erreys Rd., Cobrico.",30305107,"TRG003","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,13514,"20171130PWA_02","Crew patrolling line in response to a feeder outage found vegetation had contacted the line resulting in some singing of the vegetation.",null,null,"Fuses and switchgear"]
[17,51,"2017-11-29","20:05:00","-37.737793","144.807373","83 Millewa ave, St Albans.","31024776","SA005","Low voltage AC (<1kV)","Urban"," - fuse (any other type)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13515,"20171130PWA_03","Vic Fire rang to advise fuse has blown and caused grass fire at the incident location. On arrival the crew found at the cnr of Biggs St and Millawa Ave, St Albans on LIS 8958 red phase LV fused isolator had failed dropping debris on the ground resulting in a grass fire of approx. 2m X 10m on road reserve.  A  Fire crew attended and extinguished the fire.",null,null," - fuse (boric acid)"]
[17,52,"2017-11-29","08:49:00","-37.76129189","144.24884438","400 Brisbane ranges Rd., Mt Wallace.","31025054","BMH003","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,13592,"20180117PWA_03","Emergency Services informed a fallen transformer on fire. On arrival the crew found that a Pole Fire had occurred at the incident location. The top part of this swer pole burnt through and fell on to ground. On arrival crew isolated supply and carried out repairs. There was no ground fire ,no injuries or third party property damage.",null,null," - fuse (EDO fuse)"]
[17,53,"2017-11-29","21:06:00","-37.29687997","144.87627342","715 Kilmore Lancefield Rd., Forbes.","33024727","WND013","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within electric line construction area",19.8,"High",0.5,9.9,13519,"20171204PWA_03","Customer advised of loud bang, no supply and small grass fire at the incident location. On arrival the crew found at an EDO fuse had operated resulting in a grass fire of approx. 300mm x 300mm but\r\nThere were no reported shocks or injuries. There are no photos available. The crew replaced EDO fuse.",null,null," - fuse (Fault Tamer)"]
[17,54,"2017-12-04","19:42:00","-36.23895521","145.46512067","410 Victoria Rd., Tallygaroopna.","33090222","SHN011","22kV AC","Rural Long"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13524,"20171205PWA_02","Following the recent storm events and a reclose on the SHTS-NKA No 1 line, a crew was asked to patrol 20 poles either side of the distance to fault that was recorded in the fault log. \r\nAt P 109 SHTS-NKA No 2 line the crew found that a bird had flashed over an insulator, it had come to ground and started a ground fire of approximately 40 m X 6 m. On arrival crew assessed damage and arranged repairs.\nNo third party damage or injury was reported.",null,null," - fuse (powder filled)"]
[17,55,"2017-12-08","10:45:00","-36.01261938","144.55497197","174 Fulham Rd., Torrumbarry.","33017122","CHA005","22kV AC","Rural Long"," - connector / termination","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,13538,"20171219PWA_03","The CFA reported a grass fire at the incident location. On arrival the crew found that a “T” Clamp had faulted at the incident location. The ground fire was approximately 100m X 250m. Damage was reported to the grassland only, no injury was reported. The crew made the site safe, and repaired the connection.",null,null," - fuse (any other type)"]
[17,56,"2017-12-10","10:45:00","-34.307208886941396","142.1562754404755","75 Nealie St., Cardross.","33062189","RCT023","Low voltage AC (<1kV)","Rural Long"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,13525,"20171212PWA_01","Customer reported a “pole fire” and grass fire caused by Powercor assets  at the incident location. \r\nOn arrival the crew found that a FOLCB on a concrete pole had failed and ignited, the molten material falling to the ground  and igniting a small area of grass at the base of the pole approximately 3m x 1m in size. \r\nCFA attended & extinguished the fire. There were no reported injuries, no 3rd party damage.",null,null," - circuit breaker"]
[17,57,"2017-12-12","20:24:00","-36.24029417","142.39752350","23 Rainbow Rd., Warracknabeal.","33050983","HSM003","Low voltage AC (<1kV)","Rural Long"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,13526,"20171214PWA_01","CFA reported sparking on a pole at the incident location. On arrival the crew found that a connection had overheated on a LV isolator causing hot debris to fall to the ground resulting in a ground fire (Approx. 30m x 40m) on private property. \r\nOn arrival crew isolated supply and carried out repairs. There were no reported injuries or third party property damages.",null,null," - switch (disconnector/isolator)"]
[17,58,"2017-12-13","13:15:00","-36.27289156","143.35832119","3 Jenkins St., Charlton.","30021640","CTN005","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,13528,"20171214PWA_04","The customer reported a wire down that had started a small fire at the incident location. On arrival the crew found that an LV neutral screened service cable had faulted. It caused a ground fire of approximately 2m X 2m. No damage or injury was reported. The crew made the site safe, and replaced the service.",null,null," - switch (earth)"]
[17,59,"2017-12-13","13:24:00","-38.39973047","143.88586762","36 Deans Marsh – Lorne Rd., Deans Marsh.","33039995","WIN011","22kV AC","Rural Long"," - overhead conductor (insulated)","single phase","Started in or originated from a distribution system","within electric line construction area",19.8,"High",0.5,9.9,13529,"20171215PWA_01","Customer reported a grass fire near one of our poles. On arrival the crew found that the Insulated cable connected to the fuse unit had faulted.  A fire of approximately 300 mm diameter was subsequently found at the base of the pole.",null,null," - switch (FuseSaver)"]
[17,60,"2017-12-13","10:22:00","\t-36.21554046","145.46509981","Edwards Rd., (Cnr of McKenzie Rd), Tallygaroopna.","33090074","SHTS-NKA1","66kV AC","Unknown"," - overhead conductor (bare; steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Very High",1,0.2,13527,"20171214PWA_02","The CFA reported a grass fire at the incident location. On arrival the crew found that a hawk had flashed over on our HV assets, coming to ground and causing a ground fire. The ground fire was approximately 120m X 10m. Damage was reported to the grassland and fence line, no injury was reported. The crew found no damage to our assets.",null,null," - switch (any other type)"]
[17,61,"2017-12-14","17:38:00","-36.54479311","144.93193440","GEODETIC ROAD N, CARAG CARAG.","30255374","SHP021","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,13530,"20171215PWA_06","Crew attended to find small ground fire had been extinguished by local farmer on road verge area burnt 150 metres by 6 metres. Starling birds had caused a flashover on the concrete pole steel crossarm ACR structure, starting a small grass fire. No property damage, No injuries, No reported shocks.\r\nOn arrival crew confirmed site safe - no damage to assets.",null,null,"SCADA, network control and protection systems"]
[17,62,"2017-12-15","18:00:00","-37.58958757","143.75741380","4 Kingston Court, Smythes Creek.","32007168","BAS021","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,13537,"20171218PWA_05","Vic Fire reported a fire at the incident location. On arrival the crew found that an EDO fuse had operated. The barrel of the EDO fuse stayed in position without dropping down. \r\nThe barrel then caught fire resulting in a ground fire (approx. 50 square metres) on the road reserve and private property. There were no reported injuries .",null,null," - audio frequency load controller (AFLC)"]
[17,63,"2017-12-19","12:31:00","-36.45755071","145.32567859","800 Toolamba Rd., Toolamba.",32189917,"MNA034","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,13540,"20171220PWA_03","The CFA reported a grass fire at the incident location. On arrival the crew found that a HV Splice had faulted at Tee Pole 118  and the conductor had come to ground between Tee pole 118 and pole 1 causing a ground fire. \r\nOn further inspection it was found that a bird had flashed over at pole 1 Waugh spur. Damage was reported to grassland only, no injury was reported.",null,null," - arc suppresion coil"]
[17,64,"2017-12-20","10:35:00","-36.12938359","144.55265119","1578 Mount Terrick Rd., Rosylnmead.","32181340","ECA012","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (residential)","two phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,13543,"20171221PWA_03","The CFA reported a grass fire at the incident location. On arrival the crew found that a tree had come over causing an LV service to come to ground and short out on a steel fence poSt., which in turn caused a ground fire of approximately 10m X 10m at the incident location. \r\nDamage was reported to the grassland only, no injury was reported.",null,null," - automatic circuit recloser (ACR)"]
[17,65,"2017-12-20","16:36:00","-35.51158350","143.88425762","691 Murrabit West Rd., Murrabait.",33022802,"KGT003","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Very High",1,1,13544,"20171222PWA_01","Crew attended to find pole had been extinguished by CFA in paddock. Crew found tree across SWER between pole # 1 and pole # 2 Murrabit West Spur.  \r\nNo property damage, No injuries, No reported shocks.",null,null," - communications linear assets"]
[17,66,"2017-12-20","17:50:00","-36.99440384","144.38380602","585 Jennings Rd., Sutton Grange.",33029021,"CMN003","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,13545,"20171222PWA_02","Crew attended to find cable down between pole # 9 and pole # 10 Sutton Grange East Spur where an epicormics attached limb had dislodged and was blown across the HV Conductors .\r\nEstimated 50 acres of property burnt. \rNo injurie, no reported shocks.",null,null," - communications network assets"]
[17,67,"2017-12-21","19:10:00","-38.33854702","143.82442224","4100 Ripple Vale Cape Otway Rd., Birregurra.","32062882","WIN011","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started in or originated from a distribution system","within electric line construction area",19.8,"Low-moderate",0.2,3.9600000000000004,13546,"20171222PWA_03","Customer reported a whirly wind had blown straw onto power lines at the incident location. On arrival the crew found that the straw had caused a flash over which in turn started a ground fire at the base of Ingleby P12 (LIS-7534) (approx. 16m2 in total).\r\nThe fire self-extinguished due to the moist ground. A successful reclose occurred on the upstream ACR (@1703hrs). No injuries, no third party damage reported.",null,null," - communications site infrastructure"]
[17,68,"2017-12-22","16:12:00","-36.73828668","144.15520","1229 Calder Highway, Marong.","30147098","BET001","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within electric line construction area",19.8,"High",0.5,9.9,13550,"20180102PWA_02","VicFire Reported a grass fire near the intersection of allies st Marong. Attending crew found branch had contacted HV and high voltage fuses had operated.",null,null," - field devices"]
[17,69,"2017-12-26","21:14:00","-37.037680","143.47849","340 Avoca- Bealiba Rd., Rathscar.","30020147","MRO008","Low voltage AC (<1kV)","Rural Long"," - fuse (any other type)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,13551,"20180102PWA_03","VicFire Reported grass fire around the base of wood pole. The attending powercor crew found that a low voltage fuse box  had malfunctioned.",null,null," - local network wiring assets"]
[17,70,"2017-12-26","13:36:00","-34.190067","142.09628","85 Gibbs St., Mildura.",33064015,"MBN012","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Very High",1,{"$f":"IF(OR(P107=\"\",R107=\"\"),\"\",IF(AND(O107=\"within electric line construction area\",Q107=\"No forecast\"),1,P107*R107))","v":0.2},13552,"20180102PWA_04","Powercor crew were patrolling line after reclose and found small fire in the vicinity of the line.",null,null," - master station assets"]
[17,71,"2017-12-26","14:43:00","-35.969852","145.63590","146 Healy Rd., Cobram.","33087379","CME015","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,13553,"20180102PWA_05","Vicfire reported grassfire started by an EDO fuse falling to the ground at the intersection of Healy Rd and Cobram South Rd. \r\nAttending crew identified fault tamer fuse had mal-operated.",null,null," - neutral earthing resistor"]
[17,72,"2017-12-26","14:06:00","-36.280125","145.42837","35 Zeerust Rd., Congupna.","33093453","SHN011","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,13555,"20180102PWA_06","Powercor crew locating fault found that a tree had fallen, bringing down conductor and resulting in a small grass fire",null,null," - oil-filled circuit recloser (OCR)"]
[17,73,"2017-12-29","23:02:00","-34.6173058","142.7695","282 Crete Rd., Robinvale.","33061544","RVL001","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (residential)","two phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,13558,"20180102PWA_08","Vic Fire reported grass fire and powerline down at intersection of Robinvale-Sea Lake Road and Crete Road Robinvale.  Attending crew found service line to unoccupied house was on the ground and a small grass fire had occurred.",null,null," - rapid earth fault current limiter (REFCL)"]
[17,74,"2017-12-30","14:35:00","-37.01383","143.11824","105 Rifle Butts Rd., Landsborough.","33050264","STL007","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,13560,"20180102PWA_09","Customer called to advise of a fire start at the above address. A crew attended and found a HV fuse tube malfunctioned, dropping hot material onto the ground, starting a ground fire of approx. 20m x 10m in area on private property. Customer extinguished fire.",null,null," - surge diverter"]
[17,75,"2018-01-03","11:35:00","-36.4698470","145.08976181","623 Harston Rd., Harston.",30126897,"SHP014","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,13563,"20180103PWA_03","Emergency Services reported a grass fire that occurred two days ago at the incident location and possible cause was tree branches touching the power line. Upon arrival, the Powercor crew found that tree branches contacting the power line when there is a wind.",null,null," - voltage regulator"]
[17,76,"2018-01-04","10:53:00","-38.4383163","143.7394","170 Dewings Bridge Rd., Gerangamete.","32065469","CLC007","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,13597,"20180105PWA_01","VicFire report a grass fire start at the above location.  A crew attended and found a bird had  caused a flash - over igniting approximately 30m/sq of grass burnt in a private paddock. No injuries or damage to Powercor assets.",null,null,"Public lighting"]
[17,77,"2018-01-06","14:55:00","-38.17365197","142.96592474","38 Wallaces Rd., Glenormiston South.",30049396,"TRG001","22kV AC","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Extreme",3.5,16.099999999999998,13564,"20180108PWA_01","Powercor protection equipment reclosed on a rural feeder, 3 minutes later the CFA control centre received a call  advising of a grass fire start at the Wallace lane, Glenormiston south. Powercor assistance was offered but not initially required. Vicpol and CFA fire investigators to conduct investigation. A fire of some 31 Ha ensued. A crew was despatched following morning to confirm isolations and determine probable cause. The crew advises “Customer has lost about 50 acres caused by fire. Lost a old house, hay shed full of hay, silage, fence posts, hay stacked in paddock and one cow. At Wallace rd pole 1 SW 10819 we found a crow skeleton about 1.4m from the pole in the direction of the wind. Farmer across the rd heard a bang and looked towards switch pole and sore fire at bottom of pole just inside paddock which fits where bird skeleton is. Looked over SW pole and it all looks ok but it does have and old gac switch on it”. Supply to shed/s restored to provide water for livestock.\r There were no reported shocks or injuries.\r The fire was rapidly brought under control by 5 aircraft  and 23 ground based units\r. Note image of crow taken by crew does not appear fresh, further discussion with fire investigators in progress to confirm cause.",null,null," - brackets (major road)"]
[17,78,"2018-01-06","15:53:00","-36.73858512","144.15765856","1181 Calder HWY, Marong.","30147096","BET006","22kV AC","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within electric line construction area",19.8,"Severe",2,39.6,13572,"20180110PWA_01","During high winds tree branch's  were blown onto HV conductors starting a small grass fire at the incident location.\r\nThere were no reported shocks or injuries. The crew removed branches, replaced fuses and restored supply.",null,null," - brackets (minor road)"]
[17,79,"2018-01-06","19:26:00","-36.33843117","144.67353591","358 Restdown Rd., Rochester.",32184954,"SHP012","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Severe",2,0.4,13574,"20180110PWA_02","CFA reported  a small grass fire at the incident location. On arrival the crew found at mid span from LIS 17037 trees making contact to HV resulting in a grass fire of approx. 100m x 100m, with damage to fencing & machinery. There were no reported shocks or injuries. The crew made safe/trimmed trees and restored supply.",null,null," - lamps (major road)"]
[17,80,"2018-01-06","14:40:00","-38.46602585","144.08126531","1 Werona Rd., Fairhaven.","33041158","WPD014","Low voltage AC (<1kV)","Rural Short"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Extreme",3.5,0.70000000000000007,13565,"20180108PWA_02","Vicfire reported a small grass fire at Fairhaven. On arrival the Powercor crew found the fire had been extinguished by local residents. An area of grass some 5 by 5 metres at the base of the substation pole was burnt. A ruptured  copper to aluminium tee clamp connection was subsequently found and repaired. \r\n\rThere were no reported shocks or injuries.",null,null," - lamps (minor road)"]
[17,81,"2018-01-06","19:45:00","-37.79910726","144.80462730","129A The Avenue, Sunshine West.","Pa0119174","SU035","Low voltage AC (<1kV)","Urban"," - transformer (kiosk mounted)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Extreme",3.5,0.70000000000000007,13581,"20180111PWA_05","Customer reported a transformer fire at the incident location. On arrival the crew found that a kiosk substation had caught fire, resulting in a fire behind the closed doors of the kiosk substation.\r\nProtection operated. There were no reported injuries, no shocks, no ground fire, no HVI. The fence adjacent to the kiosk damaged due to the fire. Supply isolated. Repairs/replacement organised.",null,null," - luminaires (major road)"]
[17,82,"2018-01-07","03:01:00","-36.05109767","145.20580210","1 Kostadt St., Nathalia.","33079710","NKA002","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,13575,"20180110PWA_03","An EDO Candled and burnt in Half at the incident location. On arrival crew carried out repairs and restored supply. There was no ground fire, no reported injuries or third party property damage. ",null,null," - luminaires (minor road)"]
[17,83,"2018-01-08","19:49:00","-35.76325969","143.93149776","Loddon Valley Hwy corner of Murray Valley Hwy, Kerang.","32029791","KGT003","22kV AC","Rural Long"," - pole (wood)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"Very High",1,1,13579,"20180111PWA_03","Vic Fire reported pole fire at the incident location. On arrival the crew found a pole had been struck by lightning causing the transformer to fail and ignited a small grass fire. 10m x 10m.  \r\nThere were no reported shocks or injuries.",null,null," - poles / columns (major road)"]
[17,84,"2018-01-08","22:40:00","-34.88611870","143.12723987","Bolton - Kooloonong Rd., Bolton.","32149634","BBD014","12.7kV AC (SWER)","Rural Short"," - pole (wood)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"Very High",1,1,13576,"20180110PWA_04","Customer reported outage. Crew attended and found SWER pole had been struck by lightning and had burnt through at the base, falling to ground. There was a resulting ground fire start around the base of the pole of approx. 6mx6m.\r\nThere were no reported shocks or injuries. Fire extinguished by crew. Pole replaced supply restored.",null,null," - poles / columns (minor road)"]
[17,85,"2018-01-09","19:56:00","36.15737795","143.27268392","2112 CHARLTON-THALIA Rd., TEDDYWADDY WEST.","32029041","CTN003","22kV AC","Rural Long"," - pole (wood)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very High",1,4.5999999999999996,13578,"20180111PWA_02","Vic Fire reported grass fire at the incident location but fire start was not initially thought to be connected to Powercor assets . On arrival the crew found damaged pole at 2112 Charlton-Thalia Rd Teddywaddy WeSt., LIS 602961, and another damaged pole at LIS 602320, Calder Highway Glenloth. The following day it was identified ( CFA investigation) that the fire start was related to Goanna at LIS 602961, starting a grass fire of approx. 100HA, damaging shedding & fencing and destroying an unoccupied dwelling.  The crew made safe, replacing both poles. There were no reported shocks or injuries.",null,null,"Other "]
[17,86,"2018-01-10","21:50:00","38.56623511","142.85991495","Great Ocean Rd., Peterborough.","30251713","WBL012","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,13577,"20180111PWA_01","Customer called to report no supply,  On arrival the Powercor crew found one strand of the steel conductor had unravelled and a fire of approximately 1 acre had occurred.\r\nOn further inspection, the deteriorated carcass of a pelican was found near the conductor damage indicating that this may have previously initiated the conductor damage.\nFire had been extinguished by CFA. There were no reported shocks or injuries. On arrival crew isolated supply and carried out repairs.",null,null," - connection box"]
[17,87,"2018-01-10","11:37:00","-36.89827234","144.21426693","88 BICKFORDS Rd.,, RAVENSWOOD.","30333711","CMN003","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,13582,"20180112PWA_01","A contractor reported a crane had struck and pulled down wires at the above location. A crew attended and found a Franna crane had struck and broken one 22kV conductor and brought two others to the ground. This resulted in clashing conductors and a ground fire start btn P240 and P241A Harcourt S/L. CFA attended and extinguished fire of approx. 4 Acres in area. Damage was sustained to a number of trees and fences on private property. The site is a temporary works yard for C.P.B contractors who are constructing a new roundabout for VicRoads. The company who owns and operates the crane is Big Hill Cranes. The site supervisor for C.P.B advises the crane had just completed loading an item onto a semi with the help of a spotter. The crane operator then backed up to collect another load while the spotter was securing the load to the truck. The crane was still raised and back into the HV conductors. The crane operator lowered the boom and left the crane before the crew arrived. The ACR at Harcourt P82 reclosed and all three HV fuses at Harcourt P231 operated. Two fuses operated correctly but the third unit hung up. \r\nPole 240, 241 and 241A all sustained damage. Crew made repairs and restored supply. Final conductor heights after repairs are 7.8m\r\n\r\nThere were no reported shocks or injuries.",null,null," - earth / earthing"]
[17,88,"2018-01-11","01:09:00","-38.40279186","144.19091662","16 Wray St., Anglesea.","30073092","WPD021","Low voltage AC (<1kV)","Rural Short"," - fuse (any other type)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very High",1,0.2,13583,"20180112PWA_02","Vic Fire reported a transformer on fire at the incident location. Upon arrival, the Powercor crew found that an UG service fuse box on a pole caught fire and melted debris fell on to ground causing a small ground fire. \r\nThere were no injuries. CFA attended. On arrival crew isolated supply and carried out repairs."]
[17,89,"2018-01-11","16:39:00","-37.6819954","144.575531","24 Vista Drive, Melton.","32178447","MLN022","Low voltage AC (<1kV)","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Very High",1,0.2,13584,"20180112PWA_03","Report received from residents that a tent/gazebo had blown onto the wires outside their property, causing sparks. Upon arrival the fault crew found that a lightweight portable gazebo had in fact been swept up by the wind and blown into the open wire LV conductors. \r\nThis caused the sparking and shorting between circuits which was reported by the residents, and eventually led to the red phase and neutral conductor to break mid span and come to ground, causing a small grass fire of (3m2) in the nature strip in front of 24 Vista Drive. \r\nThe MFB were also in attendance and the small grass fire was extinguished. There was no reported third party property damage. No shock or injuries to report. On arrival crew isolated supply and carried out repairs."]
[17,90,"2018-01-12","21:54:00","-36.34311262","145.19951820","1020 Lilford Rd., Gillieston.","30128571","SHTS-KYM1","66kV AC","Unknown"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,13587,"20180115PWA_03","Vic Fire reported a pole fire  at the incident location. On arrival the crew found that a wood cross-arm had burnt through at the insulator pin causing the conductor to come adrift and rest on the cross arm.\r\nCFA extinguished the cross-arm fire, a controlled interruption on SHTS-KYM #1 was required. There was no ground fire, no reported injuries, no 3rd party damage, no protection operated. Note: incident location was advised as P171 by crew, upon investigation it was found that the pole fire location was in fact P172.",null,null,"Extra low voltage AC (<50V)"]
[17,91,"2018-01-12","12:56:00","-37.27639404","142.93347477","47 McNeill St., Ararat.","32109235","ART031","22kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,13585,"20180115PWA_01","Customer advised loud bang at the incident location. On arrival the crew found, that HV conductor fell on to LV due to damaged cross arm.  \r\nThere was suspected HVI damage to around 10 houses. There was no ground fire or injuries reported.",null,null,"Low voltage AC (<1kV)"]
[17,92,"2018-01-13","17:40:00","-35.383422731135546","142.18751449465572","54 Federation St., PATCHEWOLLOCK.","32151382","OYN005","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very High",1,1,13586,"20180115PWA_02","Customers reported all supply fail and hearing nearby fire sirens at incident location. On arrival the crew found that a HV strain cross-arm had burnt through on P124 Patchewollock line on the footpath side causing HV conductor to fall onto the LV circuit below.\r\nCFA in attendance, to extinguish the cross-arm fire, but also the air conditioning unit in the adjacent Town Hall building which the embers from the burning cross-arm are believed to have entered, CFA have had to remove the evaporative unit to douse the roof cavity to extinguish the fire in the roof of the structure\r\nLEI ( BE Garraway ) advised damage due to HVI relatively minor with only 1 fridge found damaged @ #44 Federation St., the rest of the damage ( other than the town hall ) was loss of freezer stock at the general store and pub due to the lengthy outage duration.\r\nThere were no reported injuries, go ground fire.\r\nProtection operated, Patchewollock P1A ACR tripped to lockout ( DMS case F-10974-B ), also LV HRC fuses at S/Stn “Yenolum Main 123” operated.\r\n\r\nDamage\r\n•\t1x Westinghouse fridge at #44 Federation Street ( Melting ice / thawing food inside unit, confirming it was in operation prior to incident )\r\n•\tFreezer stock losses at General Store \r\n•\tFreezer stock losses at Pub\r\n•\tEvaporative cooler / roof damage, carpet damage and possible other water damage at Town hall",null,null,"2.2kV AC"]
[17,93,"2018-01-14","22:26:00","-37.11373917","144.05772420","16 Campbell St., Newstead.","30031722","CMN002","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,13590,"20180116PWA_02","CFA reported a grass fire caused by Powercor assets at the incident location. On arrival the crew found that a possum had flashed over on a HV circuit which transitions from vertical to horizontal construction, causing the possum to fall to the ground and ignite a small grass fire, approximately 20M x 40M square was burnt.\r\nCFA extinguished the fire and reported the freshly deceased possum in the fire area. There were no reported injuries, no 3rd party damage, CMN002 feeder successfully reclosed. On arrival crew inspected assets  no repairs required. Design check being initiated.",null,null,"6.6kV AC"]
[17,94,"2018-01-15","11:41:00","-37.73423204","142.018555","40 Dickens St., Hamiton.","30089969","HTN004","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13591,"20180116PWA_03","A customer advised a loud bang and power outage at the incident location. On arrival the crew found that a HV cross arm caught fire and a part of arm fell on to ground. The fallen debris from the ignited arm caused very minor grass fire at the pole base. There was no injuries or third party property damage\r\nOn arrival crew carried out repairs.",null,null,"11kV AC"]
[17,95,"2018-01-15","11:03:00","-35.06809733","143.33548174","4077 Murray Valley Highway, Piangil.","30100069","SHL002","22kV AC","Rural Long"," - capacity balancing units","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"High",0.5,0.1,13589,"20180116PWA_01","Emergency Services reported a pole fire at the incident location. Upon arrival, the Powercor crew found 100*20 Sqm grass fire. There was a report of capacitor unit and transformer sparking at the incident location. The protection operated. CFA attended. There were no injuries.\r\nThe crew was not able to find the direct cause of this grass fire. An investigation of the plant and equipment is underway.",null,null,"12.7kV AC (SWER)"]
[17,96,"2018-01-15","16:52:00","-36.29780290","145.22308033","1580 Tatura -  Undera Rd., Undera.","33096503","KYM003","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,13594,"20180117PWA_02","FA reported a grass fire caused by tree over powerlines at the incident location. On arrival the crew found that tree branch approximately 15M in length from outside the clearance space had failed and fallen over one phase of a 3 phase spur line.\r\nThe conductor struck the fence igniting  2 ground fires 300 metres apart  (140x 10 & 70 x 10 mtrs) . The conductor remained suspended in free air still alive. There were no reported injuries. On arrival crew isolated supply and carried out repairs.",null,null,"22kV AC"]
[17,97,"2018-01-16","21:26:00","-37.55561594","143.97299788","57 Bungaree - Wallace Rd., Bungaree.","32000693","BAN011","22kV AC","Rural Long"," - connector / termination","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,13596,"20180118PWA_01","VicFire reported a fire start in proximity of a Powercor asset at the incident location. A crew attended but were unable to identify possible cause of fire start.\r\nCFA attended and extinguished ground fire of approx. 20m x 10m in area.  A crew attended the following day and identified an overheated connection. \r\nThere were no reported shocks, injuries or third party property damages. The crew replaced the overheated connection.",null,null,"33kV AC"]
[17,98,"2018-01-17","09:38:00","-37.84671700357965","144.72452705886076","8 Toritta Way, Truganina.","30239859","LV002","Low voltage AC (<1kV)","Rural Short"," - LV pillar","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,13595,"20180117PWA_04","A customer advised a pillar box has been hit by a car at the incident location. The customer also reported the box on fire, which was extinguished by persons unknown.\r\nUpon arrival, the Powercor crew found that the UG pillar had been run over by a vehicle causing a small fire. There were no injuries or third party property damage. On arrival crew isolated supply and carried out repairs.",null,null,"66kV AC"]
[17,99,"2018-01-18","00:54:00","38.75095014","143.66329754","1/29 Murray St., Apollo Bay.","30052457","CLC007","Low voltage AC (<1kV)","Rural Long"," - fuse (any other type)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,13864,"20180309PWA_01","Crew reported FSD burnt out and had caught fire. Customers underground service burnt off.\r\nThere was no ground fire, no reported injuries.",null,null,"132kV AC"]
[17,100,"2018-01-18","14:18:00","-38.19268140","144.61133747","561 Anderson Rd., Drysdale.","32083675","DDL012","22kV AC","Rural Short"," - fuse (powder filled)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very High",1,1,13602,"20180119PWA_01","A passer-by reported something dropped from pole and started a grass fire at the incident location. Upon arrival, the Powercor crew found that a grass fire (approx. 3 acres area) in the vicinity of the pole.\r\nThere were no injuries. The grass fire on a private property and it caused minor fire damage to fence.  No other damage identified by the crew.",null,null,"220kV AC"]
[17,101,"2018-01-18","23:47:00","-38.02332106","144.36538033","10 Fairway Drive, Lara.","33044395","FNS011","22kV AC","Rural Short"," - fuse (powder filled)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very High",1,1,13609,"20180122PWA_03","At approximately 11:30pm on 18/01/18, the CFA reported a pole had caused grass fire at the incident location. A crew was dispatched to investigate the incident. The attending crew found evidence of a small grass fire around substation pole 2 Fairway Drive (LIS-59510). The roadside LA on the pole was broken in half but remained attached to the pole. It was unknown what had caused this to occur. The roadside HV powder filled fuse had operated and fallen to the ground.\r The fire, totalling approximately 3m x 5m had been extinguished by the CFA and nearby resident. There was minor burns to a private fence post (10 Fairway Drive, Lara), however the fence appeared to remain intact (secure). Definitive cause of the fire is unknown, however it seems that fallen debris from either the blown powder filled fuse or the broken lightning arrestor may have been the ignition.\r\n \r\nAppropriate isolations were made and the site was made safe, the fault was handed to the day time crew for final repairs. 1 customer was left off supply for the remainder of the night.",null,null,"330kV AC"]
[17,102,"2018-01-19","10:51:00","-36.35049097","141.63397215","Corner  of Western Hwy and Irwins Rd., Nhill.","30077028","NHL016","22kV AC","Rural Long"," - surge diverter","three phase","Started in or originated from a distribution system","HBRA only",1,"Severe",2,{"$f":"IF(OR(P139=\"\",R139=\"\"),\"\",IF(AND(O139=\"within electric line construction area\",Q139=\"No forecast\"),1,P139*R139))","v":2},13608,"20180122PWA_02","CFA reported a ground fire start near a Powercor pole at the incident location. CFA attended and extinguished fire. A crew attended and found an area of approx. 1acre burnt around the base of the pole. \r\nProtection operated. There were no reported shocks or injuries.",null,null,"500kV AC"]
[{"$f":"COUNTA(C140:O140,Q140,T140:V140)","v":17},103,"2018-01-19","20:04:00","-36.77244762","144.49577389","120 Sugarloaf Rd., Axedale.","30266277","BET005","22kV AC","Rural Long"," - underground cable","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O140=\"\",\"\",IF(O140=\"LBRA only\",0.2,IF(O140=\"HBRA only\",1,IF(O140=\"within electric line construction area\",19.8,IF(O140=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"Very High",{"$f":"IF(Q140=\"\",\"\",IF(Q140=\"No forecast\",0.1,IF(Q140=\"Low-moderate\",0.2,IF(Q140=\"High\",0.5,IF(Q140=\"Very high\",1,IF(Q140=\"Severe\",2,IF(Q140=\"Extreme\",3.5,5)))))))","v":1},4.5999999999999996,13612,"20180122PWA_06","Numerous Customers called reporting supply issues of partial supply. Powercor Employee Mark Kita also part of the local community and affected by the supply issues went for a quick patrol along the HV line and came across the HV Underground cable on a concrete pole burning at pole 5 Cochrane South Spur 120 Sugarloaf Road AXEDALE. Mark quick thinking doused the grass fire at the bottom of the pole. HV underground failed above the steel covers and cable head connections to overhead line. Crew attended and made isolations of the affected spur line and HV underground to restore supply to majority of customers. Small grass fire at base of the pole. No property damage, shock reports or injuries reported.",null,null,"Extra low voltage DC (<120V ripple free)"]
[17,104,"2018-01-19","18:49:00","-34.31273065","142.18653210","107 Jacaranda St., Red Cliffs.","32140300","RCT023","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (residential)","two phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,13611,"20180122PWA_05","Customer reported wire down at premise starting a small grass fire. Crew attended and found Black XLPE  service mains cable had failed at the Point of Attachment and had fallen onto concrete footpath and scorched ground.\r\n There were no reported shocks or injuries or damages. On arrival crew isolated supply and carried out repairs.",null,null,"Low voltage DC (<1.5kV)"]
[17,105,"2018-01-19","10:51:00","-36.31066129","145.36914379","McCrakens Rd., Shepparton.","33094747","SHN021","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"Very High",1,1,13607,"20180122PWA_01","A customer reported a burnt area of ground around a pole at the incident location. The customer requested a crew attended to inspect the substation pole. \r\nA crew attended and found an area approx. 25m x 25m burnt around the base of P70 Boulevard S/L. A dead magpie was found at the base of the pole.\r\nCrew suspect the bird had flashed over and fallen to the ground causing the fire start.\rThis fire had occurred sometime previous to today.\r\nNo damage to pole or third party assets. There were no reported shocks or injuries.",null,null,"600V DC"]
[17,106,"2018-01-19","10:51:00","-37.68551904","143.36498260","Cnr Montgomery and Anderson St., Skipton..","33106473","BAS021","Low voltage AC (<1kV)","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Severe",2,0.4,13753,"20180208PWA_05","A customer reported that a truck has struck a wire and the wire was on the ground and started a ground fire at the incident location.  On arrival the crew found that a truck had contacted the LV mains conductors crossing Glenelg Hwy and causing a conductor to break and fall to the ground. There was a resulting ground fire start of approx. 1m/sq on road reserve. CFA attended. Following repairs, the final height was measured at 7.2m above the point of contact. There were no reported injuries or third party property damages.",null,null,"1500V DC"]
[17,107,"2018-01-20","12:12:00","-37.98418959","143.34377289","Corner of Four tree rd & Gnarpurt Rd., Lismore.","30042226","CDN004","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,13865,"20180309PWA_02","CFA reported a pole fire at the incident location. On arrival crew found HV crossarm burnt off. There was no ground fire, no reported injuries or third party property damage. On arrival crew isolated supply and carried out repairs.",null,null,"Earthing cable"]
[17,108,"2018-01-20","17:43:00","-35.92517450","145.49447536","Mywee Rd., Strathmerton.",30124251,"NKA003","22kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Very High",1,0.2,13610,"20180122PWA_04","Customer Chris Scott at 50 Mywee Road Strathmerton call that trees were in contact with HV and had started a grass fire in Roadside Vegetation Plantation. Approximately  110 metres by 22 metres and another small 10 metres by 10 metres grass fire in road verge and into customers property.  \r\nProperty damage was some fencing and irrigation pipes. \rThere were no reported injuriesCrew attended no operations on the network no loss of supply. Reported to Vegetation Manager who arranged for the trees in all three spans to be cut."]
[17,109,"2018-01-20","17:10:00","-36.75451451","144.30396449","2 Harpin Place, East Bendigo.","33032935","BGO022","Low voltage AC (<1kV)","Urban"," - fuse (any other type)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very High",1,0.2,13614,"20180123PWA_02","Numerous customers called reporting no supply. Crew attended to LV Fused Disconnecting Box on Substation Pole # 6 Lloyd Solomon in Lloyd Street Bendigo East. \r\nLV Fuse had overheated and melted the box and fell to the ground resulting is causing a small grass fire at base of the pole. No property damage, shock reports or injuries reported."]
[17,110,"2018-01-21","15:44:00","-37.58091435","143.84150245","901 Skipton St., Redan.","30012689","BAS034","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13613,"20180123PWA_01","A Powercor crew attended a report of an All Supply Failure at the above location. On arrival the crew found that the white phase LV Isolator on the North Circuit of “Skipton-Cooke” substation had failed and molten metal had fallen to the group starting a small fire (4 x 2 metres) which self-extinguished. \r\nThere was no injury, shock or third party damage. On arrival the crew replaced the damaged isolator and restored supply.",null,null,"single wire earth return (SWER)"]
[17,111,"2018-01-22","02:34:00","-35.33931368","143.56095417","123  CURLEWIS STREET, SWAN HILL.","32158229","SHL008","22kV AC","Urban"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very High",1,0.2,13656,"20180125PWA_02","VicFire reported a pole fire at the incident location. On arrival, crew found that a candled fuse hanging up on SW#34828.\r\nThere were no injuries and ground fire.",null,null,"single phase"]
[17,112,"2018-01-23","14:06:00","-38.15320270","143.10695933","599 DARLINGTON-CAMPERDOWN Rd., BOOKAAR.","33037204","CDN006","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,13655,"20180125PWA_01","The CFA reported a fire at the incident location. On arrival the crew found that a bird had caused a flashover on a 22kV pole and fallen to the ground starting a grassfire of approx. 2 Hectares of mostly road reserve, with some private land burnt and fence damage. There were no injuries or other damage reported. The protection operated.",null,null,"two phase"]
[17,113,"2018-01-25","11:23:00","-36.44109882","143.96782735","1789 BRIDGEWATER-SERPENTINE Rd., SERPENTINE.","30027013","EHK024","Low voltage AC (<1kV)","Rural Long"," - overhead conductor (bare; copper)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","within electric line construction area",19.8,"High",0.5,9.9,13684,"20180129PWA_02","CFA reports a car has hit a pole resulting in a grass fire at the incident location. Police also in attendance. A crew attended and found a high load had contacted and broken a low voltage conductor across a road, resulting in the conductor falling to the ground, starting a grass fire of 600sq/m on the road reserve, The high load vehicle did not stop. The crew isolated the LV supply and repaired the conductor. The 3 remaining LV conductor not broken in the incident measured a height of 5.6m at centre of road  . There were no reported shocks or injuries. Note: Police advise witnesses saw a truck with a grain auger contact and break the conductor. Contact Serpentine Police on 5437 8318 for further detail.",null,null,"three phase"]
[17,114,"2018-01-28","14:24:00","-38.60302069","143.01630735","129 Currells Rd., Port Campbell.",30045051,"TRG003","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very High",1,4.5999999999999996,13678,"20180129PWA_01","The CFA reported a grass fire which had possibly started due to trees being too close to powerlines. A crew was dispatched to investigate. The crew attended and confirmed a fire had occurred due to trees within close range to the road side conductor (2-3/2.75 ST/GZ) HV line between P4 (LIS-400219) and P5 (LIS-400220). The grass fire of approximately 10m x 60m in the road reserve had been extinguished prior to their arrival and the crew could make necessary repairs. The crew cut some branches back and made as safe as possible. They advised there were more trees in the same span which they could not reach which required trimming as soon as possible. The NAO reported this to the Vegetation Manager and Dispatch, a job was created for the trimming to take place later that night. The Escalation Manager was updated of the situation.\r\n\r\nThe crew advised there was a small amount of damage to a customer’s fence.\r\n\r\nNo protection operated. There were no reported shocks or injuries."]
[17,115,"2018-01-28","14:26:00","-38.23871363","143.14135479","4 Shaw St., Camperdown.","32059660","CDN003","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Very High",1,0.2,13698,"20180129PWA_04","The CFA reported a grass fire which had possibly started due to powerlines. A crew was dispatched to investigate. The crew attended and confirmed a 5m x 7m ground fire had occurred outside 3 Shaw St around the base of LV pole (LIS-422531). It was identified that the neutral screen service to # 4 Shaw St had failed, leaving the customer with no power. There was a loose neutral connection on (LIS-422531) which may have contributed to the fault. There were no obvious signs of how the fire started, however the crew suggested that fault current in the failed service at the loose connection may have caused a spark to fall to the ground, igniting the fire. The neutral screen service cable and connection was sent to Warrnambool depot, to be forwarded to the failed asset team in Ballarat.\r\n\r\nNo protection operated. There were no reported shocks or injuries. No further damage identified."]
[17,116,"2018-01-28","19:45:00","-38.2684021","144.521988","73-75 Dare St., Ocean Grove.","32071761","DDL023","Low voltage AC (<1kV)","Rural Short"," - fuse (any other type)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very High",1,0.2,13710,"20180130PWA_01","The CFA reported a ground fire had occurred at the incident location. A crew was dispatched to investigate. The crew attended and found an FSD had burnt out and fallen to the ground. This had caused scattered burns to the ground totalling approximately 1m x 1m. The CFA had left site before the crew arrived.\r\nThe FSD was a substation bus fuse for “Presidents Terrace P61” S/S pole. The crew made appropriate repairs and the site safe.\r There were no reported shocks or injuries. No further damage identified.",null,null,"Negligible: no ground fire"]
[17,117,"2018-01-28","19:45:00","-38.20741342","144.30270706","23-29 Ghazeepoore Rd., Waurn Ponds.","32084727","WPD031","Low voltage AC (<1kV)","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very High",1,0.2,13725,"20180131PWA_01","The CFA reported a ground fire had occurred at the incident location. The report from the CFA was that the fire had started from a blown fuse. A crew was dispatched to investigate. The crew attended and found evidence of a ground fire totalling approximately 1m x 3m. They advised the cause was likely falling debris from an overheated LV copper-aluminium clamp. The CFA was not onsite when the crew arrived. The crew performed appropriate repairs and made the site safe. There were no reported shocks or injuries. No further damage identified.",null,null,"Localised: less than 10 sq.m"]
[17,118,"2018-01-29","21:27:00","-38.04156823","142.81945467","412 MORTLAKE-ARARAT Rd., MORTLAKE.","32061375","TRG002","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,13873,"20180315PWA_01","Report from Vic Fire of pole fire at incident location. On arrival crew found crossarm burnt off.\r\nThere was no ground fire , no reported injuries and no third party property damage.",null,null,"Small: 10 - 1000 aq.m"]
[17,119,"2018-01-29","15:30:00","-36.29199490","145.39933881","385 SHEPPARTON-ZEERUST Rd., ZEERUST.","33093573","SHN011","22kV AC","Rural Long"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Very High",1,0.2,13724,"20180130PWA_08","Vic Fire reported grass fire at base of pole # 84.  On arrival the crew found evidence of a flashover on a 22kV insulator that has had damage to one of the sheds on the insulator which will need to be replaced.  Crew found a “raven or crow” at base of pole that was burnt along with approx. 100m x 5m of burnt grass in road reserve.  Crew arrange a fault follow up to repair insulator.  Also a small amount of damage was noticed on the fence adjacent to the road reserve.   ESV notified.  No shock or injuries.",null,null,"Medium: 1000 sq.m - 10 ha"]
[17,120,"2018-01-29","19:45:00","-37.6757431","144.544","94 Westlake Drive, Melton West.","34031832","MLN022","Low voltage AC (<1kV)","Rural Short"," - LV pillar","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very High",1,0.2,13726,"20180131PWA_02","Customer  reported a fire incident at an LV pillar in front of No. 94 Westlake Drive Melton 3337.\r\nThe fire brigade was called and attended to the fire.\rThere were no reported injurieThere was no ground fire.",null,null,"Large: more than 10 ha"]
[17,121,"2018-01-30","05:27:00","-36.22941927","140.99669386","SERVICETON NORTH-TELOPEA DOWNS Rd., SERVICETON.","32120511","NHL031","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very High",1,1,13785,"20180207PWA_01","A crew attended an outage at the incident location.  On arrival the crew found that a pole fire had occurred on a 22kV pole which burnt the top of the pole.  Protection operated.  There was no ground fire.  There were no reported injuries or third party property damages. \r\nThere was No ground fire start, no reported injuries or third party property damage."]
[17,122,"2018-02-03","12:01:00","-36.12977543","145.04245073","116 Hutchins Lane, Kotupna.","32193175","KYM004","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,13784,"20180206PWA_01","Vicfire reported grassfire started by a HV wire falling to the within private property, fire brigade were onsite as well as police. Upon arrival crew found that the fire had been extinguished and that the CFA were still onsite. Linesmen confirmed that the fire was indeed started by a HV wire falling to the ground (the wire was broken by a falling tree branch). Only one wire of the single phase line was broken. The fire was approximately 3-4acres in area (fire burnt in private property).   The fire burnt between LOWBAR P3 (LIS-17394) (Northern pole) and LOWBAR P4 (LIS-17395) (Southern pole).  Repair works consisted of approx. 250m of 3/12 steel being replaced as the steel that had lay on the ground in the fire had the galvanisation burnt off it. A couple of HV arms initially appeared to be twisted due to the force of the branch falling on the wire however these pulled back into placed once the new conductor was sleeved in. Restoration time was about 13:30 with only one customer on LOBAR S/L remaining off for slightly longer than the other customers. There was no  private property damage sustained , no injuries, no reported shocks. Isolation was made at WYUNA P6 ACR."]
[17,123,"2018-02-06","15:53:00","-37.72638","142.0239","93 Park St., Hamilton.","30094546","HTN004","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Very High",1,0.2,13788,"20180207PWA_04","Vicfire reported a wire down and sparking at the incident location. On arrival the crew found that a neutral screen service had failed near the POA and fallen to the ground starting a grassfire of approx. 2 square metres of the customer’s front lawn. There were no injuries or other damage reported.\r\nOn arrival crew isolated supply and carried out repairs.",null,null,"Started in or originated from a distribution system"]
[17,124,"2018-02-07","22:38:00","-36.20614661","144.61686941","72 Bamawm Rd., Bamawm Extension.","33084014","ECA012","22kV AC","Rural Long"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Very High",1,0.2,13789,"20180209PWA_01","Emergency services reported grass fire possibly started by Powercor assets, requested Powercor attend. Upon arrival crew found that there had been a flashover on the t-off arm on P153 BAMAWM RD LIS-28004. Crew recovered remains of bird from the arm. \r\nThe bird had flashed across the 5 shed bridging insulator on the t-off arm. No damage to private assets or Powercor assets was sustained.",null,null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system"]
[17,125,"2018-02-08","16:20:00","-37.73943820","144.82224900","2 Biggs St., St Albans.","32175211","SA005","Low voltage AC (<1kV)","Urban"," - fuse (any other type)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,13791,"20180212PWA_01","VicFire reported a Fire outside 2 Biggs St., St Albans. Upon arrival the crew had found that the POA/FOLCB at incident location, had failed and caused the POA/FOLCB to melt and burn away, approximately 6-7 inches of the customers mains had also been damaged and burnt as a result of this incident.\r\nThe resultant hot melted plastic from the POA/FOLCB above had fallen onto the grassed front yard/lawn below causing a very-minor grass fire within the front yard of  approximately 0.5m² total area.\r The MFB attended site and the grass fire was extinguished.\r There was no reported injury or shocks as a result of this incident.",null,null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system"]
[17,126,"2018-02-09","18:58:00","-36.37988138","145.41534968","34 - 36 Byass St., Shepparton.","33093066","STN013","22kV AC","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very High",1,0.2,13793,"20180212PWA_02","CFA reported pole fire at corner of Bypass St and Lockwood Road. (SPC) Upon arrival crew found that the fire had been extinguished. The small fire approx. 3m² was in nature strip around the base of LIS-2698 HV SW# 21825 conc pole. Crew found that there had been evidence of a flashover between the LA on the HV cable head and the HV screen  on the centre phase.",null,null,"Started by lightning striking a distribution system or a part of a distribution system "]
[17,127,"2018-02-11","23:48:00","-38.47640461","143.75054598","1724  BIRREGURRA-FORREST Rd., BARWON DOWNS.","33039489","CLC007","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,13798,"20180214PWA_02","Powercor received a call from VicFire reporting a grass fire caused by a pole fire at 1724 Forrest Rd., Barwon Downs. When crews arrived at the incident site, they found a deceased possum on the ground at the base of the pole., located on the road reserve. \r\nA small ground fire (35m x 15m) near the base of the pole had been extinguished by the CFA. No conductors fell to ground. No electrical asset damage was found.  No other third party property damage was reported. No injuries were reported.",null,null,"Started by any other thing forming part of or coming into contact with a distribution system"]
[17,128,"2018-02-13","17:43:00","-37.75753376","144.83555748","96 Munro Avenue, Sunshine North.","30245830","SSE012","22kV AC","Urban"," - overhead conductor (ABC)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,13802,"20180215PWA_01","Upon arrival the crew had found that the 185mm 3/C HVABC at HV Pole LIS-727309 had failed, resulting in a flashover, the resultant sparks from the failed HVABC have fallen onto the nature strip grassed area below causing a grass fire of approximately 6m x 2m.\nThe crew has advised that upon arrival the grass-fire had self-extinguished. There was no reported HVI, injury or shocks as a result of this incident.",null,null,"Otherwise started by a distribution system"]
[17,129,"2018-02-13","20:43:00","-36.85650627","144.19975889","74 BELVOIR PARK Rd., RAVENSWOOD.","32014982","BET004","22kV AC","Rural Short"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,13801,"20180214PWA_05","A customer reported sparking at top of pole behind their house. Upon arrival @21:30:00 crew found that a BA fuse had candled on the T/Pole at the incident location.\r\nThere was no ground fire, no injuries or third party property damage. "]
[17,130,"2018-02-15","13:05:00","-35.95156457","145.68240072","3186  MURRAY VALLEY HIGHWAY, COBRAM.","30143478","CME021","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,13811,"20180216PWA_03","CFA reported a grass fire at the incident location. On arrival the crew found that a branch had blown onto the HV fuses at P1 Wyatt Spur in high winds, it subsequently came to ground and caused a ground fire at the incident location. \r\nThe ground fire was approximately 20m X 40m. Damage was reported to the grassland only, no injury was reported. The crew made the site safe, and inspected the HV fuses for damage."]
[17,131,"2018-02-15","13:15:00","-38.23218392","141.44966090","1901 PORTLAND-NELSON Rd., GORAE WEST.","32129434","PLD003","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,13810,"20180216PWA_02","The CFA reported a grass fire at the incident location. On arrival the crew found that a crossarm had caught fire which also resulted in a ground fire at the incident location. The ground fire was spread across approximately 1.5 acres. \r\nDamage was reported to the grassland only, no injury was reported. The crew made the site safe, and replaced the crossarm.",null,null,1]
[17,132,"2018-02-16","14:01:00","-37.68935646","144.60304998","66 HIGH STREET, MELTON.","30112318","MLN021","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13948,"20180409PWA_01","During feeder patrol crew located pole fire outside 66 High St. Melton. A HV termination crossarm had broken as a result of a pole fire.\r\nThere was no ground fire, no reporteed injuries or third party property damage.",null,null,2]
[17,133,"2018-02-16","03:40:00","-37.6301765","144.067947","847 yendon - egerton Rd., Millbrook.","32007089","BAN011","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,13817,"20180219PWA_01","A call was received from the customer at 847 Yendon-Egerton Rd., Millbrook that an explosion had occurred on the pole out the front of the above property. On arrival the crew found that a X-arm Fire had occurred on Millbrook Pole 82. The X-arm had burnt through where the EDO fuse unit mounts to the X-arm. Protection operated as expected",null,null,3]
[17,134,"2018-02-17","17:22:00","-35.863382","145.58724","TORGANNAH Rd., KOONOOMOO.","32181198","NKA005","Low voltage AC (<1kV)","Rural Short"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,{"$f":"IF(OR(P171=\"\",R171=\"\"),\"\",IF(AND(O171=\"within electric line construction area\",Q171=\"No forecast\"),1,P171*R171))","v":0.5},13819,"20180220PWA_02","CFA reported a grass fire near Powercor assets at the incident location. On arrival the crew found that a LV isolator overheated, dropping burning materials to the ground and igniting a grass fire around the base of the substation pole, approximately 10 metres square was burnt.",null,null,4]
[17,135,"2018-02-18","05:47:00","-36.70819163","144.24277605","132 Sailors Gully Rd., Sailors Gully rd.","30030467","EHK024","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,13833,"20180223PWA_08","Vic Fire reported a pole fire at the incident location. On arrival the crew found that a wood cross-arm had burnt through at the insulator pin causing the conductor to come adrift and hang by the bridge. There was no sign of the HV conductor making contact with the LV circuit below.\r\nCFA extinguished the cross-arm fire, a controlled interruption was required. \rThere was no ground fire, no reported injuries, no 3rd party damage, no protection operatedNote: the initial report from the CFA suggested that nearby vegetation was ignited, there was no evidence on site to support this statement.",null,null,5]
[17,136,"2018-02-18","19:17:00","-34.18444722","142.19304039","15 Benetook Ave, Mildura.","30099309","MDA024","22kV AC","Urban"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Very High",1,0.2,13820,"20180220PWA_03","Customer reported dim lights and a load bang at the incident location. On arrival the crew found that tree branch from a nearby tree (outside clearance space ) was blown onto single phase transformer, landing between the HV bushings and surge diverters. The branch began to burn due to electrical tracking, dropping burning material to the ground, a grass fire approximately 3m square resulted at the base of the pole.",null,null,6]
[17,137,"2018-02-18","11:47:00","-35.81807415","142.13220835","570 Whites Rd., Rainbow.","320898781","NHL015","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any other thing forming part of or coming into contact with a distribution system","HBRA only",1,"Very High",1,1,13818,"20180220PWA_01","Vic Fire reported that a tractor towing a grain auger had contacted the SWER line as 570 Whites Rd., Rainbow. On arrival the crew found that farmer towing a grain auger had contacted the SWER line between Poles 32 and 33 Nandemarriman Spur line. The contact resulted in a fire that burnt approx. 0.1 hectares of stubble paddock and also destroyed the tractor. Minor damage was sustained to the conductor. At the point of contact the conductor height was measured at 7.4 metres.  The crew isolated supply and carried out repairs. The driver of the tractor reported receiving a minor shock when he jumped off the tractor. The crew advised him to seek a medical assessment. The driver Patrick White attended the local hospital later in the day for checks.",null,null,7]
[17,138,"2018-02-19","07:09:00","-36.74803508","144.28811743","125 BRIDGE STREET, BENDIGO.","30025745","EHK033","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very High",1,0.2,13847,"20180227PWA_02","A passer-by reported a pole fire at the incident location. On arrival the Powercor fault crew found that the HV cross am and pole top slightly burnt through.\r\nThere was no ground fire, no reported injuries or third party property damage. \rOn arrival crew isolated supply and carried out repairs.",null,null,8]
[17,139,"2018-02-19","14:44:00","-36.27880941","144.77413771","ECHUCA-NANNEELLA Rd., NANNEELLA.","30122451","KYM001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very High",1,0.2,13822,"20180221PWA_01","Customer reported a low conductor at the incident location. On arrival the crew found that a wood cross-arm had burnt through at the kingbolt through to the insulator pin on one side causing the conductor to come adrift and hang approximately 5.0m above the ground, the other phase was still attached to the pole via the cross-arm strap.\r\r\nThere was no ground fire, no reported injuries, no 3rd party damage, no protection operated. Note: The cross-arm fire was believed to have occurred on the night of the 18th of February, not discovered till the following day by the customer making the report. The crew were questioned about the conductor height and advised it was still 5.0m above the ground, not within reach as the reporter indicated.",null,null,9]
[17,140,"2018-02-19","06:59:00","-36.74813724","144.26915259","32 BANNERMAN STREET, BENDIGO.","32040059","BET002","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very High",1,0.2,13834,"20180223PWA_09","Vic Fire reported a pole fire at the incident location. On arrival the Powercor fault crew found that a HV cross am and pole top had slightly burnt through. There were no injuries, HVI or ground fire.",null,null,10]
[17,141,"2018-02-20","23:48:00","-37.65400531","142.30651809","45 Cavendish Rd., Dunkeld.","33058547","HTN005","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very High",1,4.5999999999999996,13823,"20180221PWA_02","The CFA reported a grass fire at the incident location. On arrival the crew found that a grass fire (10x10m) had been extinguished by the CFA. Fire started at the base of the pole, flash marks observed on the LV buckram strap.\r\nNo damage, no injuries were reported. The crew made the site safe, and inspected all connections on the pole. Earth fault targets were present on the upstream auto sectionaliser but did not cause any prot to operate.",null,null,{"$f":"Y177+1","v":11}]
[17,142,"2018-02-21","19:57:00","-35.88529941","144.23161251","90 HORFIELD SCHOOL Rd., HORFIELD.","33022765","CHA005","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Very High",1,0.2,13824,"20180223PWA_01","CFA reported a grass fire caused by Powercor assets at the incident location. On arrival the crew found that a bird had flashed over on the bypass switch on load side of an ACR pole, causing the bird to fall to the ground and ignite a small area of grass commencing at the base of the pole and running along a roadside drain, approximately 10m x 60m square was burnt.\r\nCFA attended and extinguished the fire. There were no reported injuries, no 3rd party damage, Hawken P1 ACR successfully reclosed.",null,null,{"$f":"Y178+1","v":12}]
[17,143,"2018-02-22","22:03:00","-36.61544152","142.42896795","1976 WIMMERA HIGHWAY, MURTOA.","30085231","HSM001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,13829,"20180223PWA_06","VicFire reported a pole fire at the incident location. On arrival the crew found that the wooden crossarm and pole top assembly required replacement due to fire damage. There was no ground fire, no reported injuries or third party property damage.",null,null,13]
[17,144,"2018-02-22","21:47:00","-36.76572166","141.10013723","7894 NATIMUK-FRANCES Rd., NEUARPURR.","32091284","HSM004","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,13828,"20180223PWA_05","VicFire reported a pole fire at the incident location. On arrival the crew found that the wooden pole and crossarm required replacement due to pole top fire damage. There was no ground fire, no injuries or third party  party property damage.",null,null,14]
[17,145,"2018-02-22","09:56:00","-37.59714186","143.76861697","679 GLENELG HIGHWAY,  SMYTHES CREEK.","33000200","BAS021","22kV AC","Rural Long"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,13827,"20180223PWA_04","A number of customers reported voltage issues beyond P1 Bells Rd., Smythes Creek. On arrival the crew found a HV boric acid fuse had hung up and burnt through. This caused a ground fire in two spots of approximately 1m square and 2m square. Damage was reported to the grassland only, no injury was reported. The crew made the site safe, and the HV fuse was replaced.",null,null,15]
[17,146,"2018-02-23","09:39:00","-36.41122171","142.48413189","790 KEWELL EAST Rd., KEWELL.","30226897","HSM005","12.7kV AC (SWER)","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Severe",2,2,13835,"20180223PWA_10","Customers called to advise of an outage and a pole fire that had occurred at the above location. A crew attended and found there had been a pole fire at P34A Kellalac east S/L. Protection operated. CFA did not attend. Customer extinguished fire. Ground fire start of approx.2sq/m on private property.\r\nThere were no reported shocks or injuries.",null,null,16]
[17,147,"2018-02-23","04:35:00","-37.74349719","142.02819907","1237 French St., Hamilton.","32126397","HTN005","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,13878,"20180315PWA_06","Emergency services reported a pole on fire. On arrival the attending  crew found the wooden HV cross-arm on pole 47  had ignited at the king bolt  and burnt the pole top and cross-arm. There was no ground fire. There were no reported shocks or injuries.",null,null,17]
[17,148,"2018-02-25","14:23:00","-37.39842951","143.94647264","135 KINGSTON Rd., KINGSTON.","32001388","BAN009","Low voltage AC (<1kV)","Rural Long"," - overhead conductor (bare; copper)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,13846,"20180227PWA_01","Customer reported a small ground fire at the incident location. On arrival the crew found that an elm tree branch had come down in windy conditions and contacted a 3 phase open wire low voltage line. \r\nThere was a small ground fire of approximately 3m².\r There were no injuries.",null,null,18]
[17,149,"2018-02-26","18:50:00","-37.74718873","144.57146880","1243-1257 EXFORD Rd., EXFORD.","30142925","MLN011","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,13915,"20180327PWA_05","Report received from a motorist driving along Exford Rd towards Eynesbury of a line that had come down; not disconnected but hanging low in the paddock. Upon arrival the fault crew found that at LIS-936380 the outer section of the 3-phase HV wood crossarm had burnt through.\r\nThe outer phase HV conductor falling to within 1.5m-2.0m of the ground. Supply remained alive and no protection operated as a result of the incident, and apart from the burnt crossarm, there was no further damage sustained to the pole or the HV conductor. There was no asset fire/ground fire, shock or third party damage to report.",null,null,19]
[17,150,"2018-02-28","18:39:00","-37.88152012","142.97343112","1316 DARLINGTON-NERRIN Rd., DUNDONNELL.","30047629","CDN006","22kV AC","Rural Long"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very High",1,4.5999999999999996,13854,"20180301PWA_03","Customer reported information about a potential cause of an outage and that “a transformer had arced out caused a fire but has now been put out”.\r On arrival the attending crew found a HV fuse had mal-operated . Parts of the fuse barrel had fallen to the ground  and there was a  fire of some 150m x 6m on the road reserve.\r\nThere were no reported shocks or injuries. Crew advised that they also suspect there was an internal fault in the transformer.",null,null,20]
[17,151,"2018-02-28","14:41:00","-38.50696204","142.93408879","BOUNDARY Rd., TIMBOON WEST.","30255711","TRG005","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very High",1,4.5999999999999996,13852,"20180301PWA_01","Emergency services reported power lines down and had possibly caused a fire. On arrival the attending crew found a tree had broken brought down 3 HV conductors  between poles 35 and 36 of the Peterborough line. There was a  fire of some 200 by 20 m on private property.\r\nCrew advise large gum tree broke approximately 1 metre above the ground during high winds. Unclear if tree is on private property or unused road reserve. There were no reported shocks or injuries."]
[17,152,"2018-02-28","15:29:00","-36.76123879","144.28797682","MUNDY STREET, BENDIGO.","33017852","BGOEHK","66kV AC","Unknown"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Very High",1,0.2,13856,"20180302PWA_01","66Kv Feeder CB for BGO EHK 66Kv Feeder dropped off BGO Zone Substation 22KV feeders. Line patrol found tree in contact with 66Kv at Pole # 22 LIS # 413178 in gusty wind in VLine Reserve near the corner of Mundy and McLaren Streets BENDIGO. Ground fire 15 Metres X 8 Metres. No shocks, No third party damage."]
[17,153,"2018-02-28","13:30:00","-38.09026","144.264481","35 CULLINAN Rd., BATESFORD.","33043550","GL015","Low voltage AC (<1kV)","Rural Long"," - fuse (any other type)","single phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very High",1,4.5999999999999996,13964,"20180411PWA_03","A customer reported that their lights are flickering and a smell is coming from the supply box at the incident location. On arrival the fault crew found that a loose connection had caused heating of the fuse connection resulting in charring of the meter panel. On arrival crew isolated supply and replaced meter board.\nThere was no ground fire and no injury as a result of this incident."]
[17,154,"2018-03-01","13:58:00","-38.16516189","144.41690544","2415 PORTARLINGTON Rd., BELLARINE.","30076493","GLE031","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",{"$f":"IF(Q191=\"\",\"\",IF(Q191=\"No forecast\",0.1,IF(Q191=\"Low-moderate\",0.2,IF(Q191=\"High\",0.5,IF(Q191=\"Very high\",1,IF(Q191=\"Severe\",2,IF(Q191=\"Extreme\",3.5,5)))))))","v":0.2},{"$f":"IF(OR(P191=\"\",R191=\"\"),\"\",IF(AND(O191=\"within electric line construction area\",Q191=\"No forecast\"),1,P191*R191))","v":4.0000000000000008E-2},13921,"20180328PWA_03","A passer-by reported an insulator hanging down. On arrival the crew found that a HV crossarm had burnt through and the insulator had let go from the crossarm. There was no ground fire, no third party damage or injury was reported."]
[17,155,"2018-03-01","06:11:00","-37.86679552","144.82511519","36 ROMAWI STREET, ALTONA.","30107670","AL012","11kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13918,"20180328PWA_01","Vic Fire reported a pole fire at the incident location. On arrival the crew found that a pole and HV crossarm had caught fire. There was no ground fire, no reported injuries or third party property damage."]
[17,156,"2018-03-01","08:33:00","-37.72607636","144.81573257","12 TARELLA DRIVE, KEILOR DOWNS.","30111815","SA006","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13920,"20180328PWA_02","Customer reported an insulator hanging down. On arrival the crew found that a HV crossarm had burnt through and the insulator had let go from the crossarm. There was no ground fire, no third party damage or injury was reported."]
[17,157,"2018-03-01","07:10:00","-37.88609438","144.77766417","46 EDWARDS DRIVE, ALTONA MEADOWS.","30116799","LVN022","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13917,"20180327PWA_07","A customer reported that there is a pole on fire  at the incident location. On arrival the fault crew found that the roadside fog insulator and end of the wooden cross-arm had burnt through causing the cross-arms to fail at the incident location. \r\nThere was no ground fire and no injury as a result of this incident."]
[17,158,"2018-03-01","07:10:00","-37.88348963","144.77883397","16  EDWARDS DRIVE, ALTONA MEADOWS.","30116842","LVN022","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13916,"20180327PWA_06","A customer reported that there is a pole on fire  at the incident location. On arrival the fault crew found that the roadside fog insulator and end of the wooden cross-arm had burnt through causing the cross-arms to fail at the incident location. There was no ground fire and no injury as a result of this incident."]
[17,159,"2018-03-02","14:20:00","-37.68319177","144.48853779","735 BACCHUS MARSH Rd.,, MERRIMU.","30116368","BMH006","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,13857,"20180305PWA_01","Employee reports a broken HV Xarm at P84 Melton line. Xarm burnt though at king bolt and hanging from pole by bridges. \r\nOn arrival crew isolated supply and carried out repairs. \rNo ground fire sta There were no reported shocks or injuries."]
[17,160,"2018-03-02","23:45:00","-35.98026038","142.91278334","13  MORRISON STREET, BIRCHIP.","32018655","CTN001","Low voltage AC (<1kV)","Rural Long"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,13859,"20180305PWA_02","CFA advised pole fire outside 13 Morrison St – Birchip.\r Upon arrival crew found that an LV bushing cover had melted and had fallen to the ground at incident location.\r\nThe melted bushing had caused a 1m² grassfire at the base of the pole.\r There was no shock, no injury, no damage to private property.\r On arrival crew isolated supply and carried out repairs."]
[{"$f":"COUNTA(C198:O198,Q198,T198:V198)","v":17},161,"2018-03-02","07:06:00","-37.94144240","144.70887774","749 Duncans Rd., Werribee South.",30112650,"WBE034","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,14051,"20180514PWA_01","Reported pole fire at incident location. There was no ground fire, no reported injuries or third party property damage."]
[{"$f":"COUNTA(C199:O199,Q199,T199:V199)","v":17},162,"2018-03-02","09:10:00","-35.08197575","142.17059948","GALAH NORTH Rd., OUYEN.","32145208","OYN001","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,14052,"20180514PWA_02","Pole fire reported at incident location. There was no ground fire, no reported injuries or third party property damage."]
[17,163,"2018-03-03","14:03:00","-37.42247150","142.85688994","7507 MORTLAKE-ARARAT Rd., MAROONA.","33054332","ART033","22kV AC","Rural Long"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very High",1,4.5999999999999996,13861,"20180306PWA_01","Emergency Services reported a grass and scrub fire at the incident location. On arrival the attending crew found a HV Flex on the white phase had failed causing it to flash over on the blue phase. \r\nThe result has caused two grass fires, one 20 mtrs x 75 mtrs and the second 5 mtrs x 5 mtrs both in the road reserve and customers property which had been extinguished by the CFA prior to Powercor attendance . \r\nThere were no reported shocks or injuries. \rThe crews replaced the Blue and White phase Flex’s and inspected the Red phase which was in good order."]
[17,164,"2018-03-04","09:36:00","-37.86985413","144.78563043","44 TALBOT STREET, ALTONA MEADOWS.","32177509","LVN022","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13862,"20180306PWA_02","Report was received of a HV conductor down at pole LIS 213813 Cnr of Talbot st and Alma Ave. Possible HVI, LEI required. On arrival the crew found, that a  HV conductor fell on to LV due to a burnt off HV crossarm cross arm. \r\nThis resulted in  the outer phase HV conductor falling on top of the LV conductors. There was no ground fire, no third party damage or injuries reported. The LEI, Damian Harris, tested all customer connections and confirmed no HVI and no damage to customer property.\r\nThe site was made safe and appropriate repairs were made."]
[17,165,"2018-03-08","14:55:00","-36.49884418","144.93079068","980 TWO TREE Rd., CARAG CARAG.","30255469","SHP021","22kV AC","Rural Long"," - fuse (boric acid)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"High",0.5,0.5,13866,"20180309PWA_03","Vic Fire reported grass fire and fuses down near intersection of Two Trees Rd and Geodetic Rd Carag Carag. On arrival the crew found evidence of a flashover on the Boric Acid fuse unit. Flash over marks on fuse unit bracket.  \r\nAn Area of approx. 80m x 20m of burnt grass in road reserve.  Also a small amount of damage was noticed on the fence adjacent to the road reserve. There was no reported injuries."]
[17,166,"2018-03-09","20:34:00","-36.72566313","144.25826013","369 EAGLEHAWK Rd., CALIFORNIA GULLY.","30026311","EHK031","22kV AC","Rural Short"," - overhead conductor (bare; copper)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,13871,"20180314PWA_01","Customer reported powerline down at 69 Victoria St Eaglehawk.  When crew arrived they reported that they suspected a bat had flown into HV conductors causing a phase to phase fault.  They were unsure if a HVI had occurred as HV conductors had dropped into LV conductors.  LEI Bill Rounds attended site and confirmed that no HVI had occurred at this site.  Report room advised that a subsequential fault had also occurred that was likely due to fault current.  Crew attended secondary site and found that centre phase HV conductor had come down and a ground fire had been extinguished at base of the pole.  Crew advised that the fault appeared to be due to a bad connection at the connection between the bridge and conductor on the centre phase.  Crew replaced connection.   Area of fire was approx. 12m x 6m.  The following day, a customer reported that they still had no power and had heard a loud bang coming from her meter box shortly after noticing a fire outside her window (at base of pole).  LEI Bill Rounds attended and confirmed that either a LVI or HVI had occurred but was unsure which.  Bill also confirmed that property damage had occurred to at least an oven and some medical charging equipment.  ESV notified of ground fire with unknown cause, property damage with unknown cause, media and community interest.  Local paper had reported an outage at a cycling event which may have been related.  Could not confirm but also advised ESV that there was interest from the community about this outage also.  Later found that cycling event outage was unrelated to this incident.  No shock or injuries."]
[17,167,"2018-03-10","02:37:00","-36.35641819","145.46192390","105 Lemnos North Rd., Lemnos.","33096892","SHN024","22kV AC","Rural Short"," - insulators","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",{"$f":"IF(O204=\"\",\"\",IF(O204=\"LBRA only\",0.2,IF(O204=\"HBRA only\",1,IF(O204=\"within electric line construction area\",19.8,IF(O204=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"Low-moderate",0.2,4.0000000000000008E-2,13867,"20180313PWA_01","Vic Fire reported grass fire at 105 Lemnos North Rd Lemnos.  On arrival the crew found evidence of a flashover from a bat on a HV 5 shed insulator.  Crew raised fault follow up to replace insulator.  Area of approx. 15m x 30m of burnt grass in the road reserve.  Also a steel fence adjacent to the road reserve was blackened. ESV notified.  No shock or injuries."]
[17,168,"2018-03-11","01:44:00","-37.56578712","143.87324182","146 EUREKA STREET, BALLARAT EAST.","30262779","BAN015","Low voltage AC (<1kV)","Rural Short"," - luminaires (minor road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,13874,"20180315PWA_02","VicFire reported a pole fire at the incident location. On arrival the crew found that the wiring in the 80w Mercury Vapour Street Light attached to this pole had shorted and had melted / burned the wiring in the Street Light. There was no ground fire. There were no injuries."]
[17,169,"2018-03-11","12:25:00","-37.80089808","143.11048440","380 PEMBERTONS Rd., VITE VITE.","32061488","CDN006","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,13882,"20180316PWA_04","A customer reported an insulator on a cross arm had broken causing conductor to hang very low. The attending crew found evidence of a HV crossarm fire. The live HV conductor was hanging at a waste height. There was no evidence of ground fire. There were no reported shocks or injuries."]
[17,170,"2018-03-11","18:15:00","-38.36423959","141.62532641","823 MADEIRA PACKET Rd., PORTLAND.","32135488","PLD006","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,13922,"20180328PWA_04","An employee reported a pole fire had occurred at the incident location. The attending crew found that Pole 13 (LIS-905457) had caught fire at the HV tee off insulator position. There were no reported shocks or injuries. No evidence of ground fire."]
[{"$f":"COUNTA(C208:O208,Q208,T208:V208)","v":17},171,"2018-03-11","07:16:00","-38.16526772","144.36704636","161 FYANS STREET, SOUTH GEELONG.","35407507","GLE033","Low voltage AC (<1kV)","Urban"," - luminaires (minor road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,14053,"20180514PWA_03","Report from customer of Public Lantern on fire at incident location. There was no ground fire, no reported injuries and no third party property damage."]
[{"$f":"COUNTA(C209:O209,Q209,T209:V209)","v":17},172,"2018-03-13","06:40:00","-37.74803359","144.66738939","171 TROUPS ROAD S, TRUGANINA.","30108240","MLN021","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,13875,"20180315PWA_03","CFA reported a pole fire at the incident location. On arrival the Powercor fault crew found that a HV cross arm had slightly burnt through. There was no ground fire, no reported injuries or third party property damage."]
[17,173,"2018-03-15","09:45:00","-37.37356087","143.74882403","970 Coghills Creek Rd., Coghills Creek.","30006858","BAN006","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,13879,"20180316PWA_01","An employee reported a burnt cross arm on a pole at the incident location.  On arrival the crew found that a cross arm fire had occurred on a 22kV pole which burnt the cross arm only.  Protection operated.  There was no ground fire.  There were no reported injuries or third party property damages.\r"]
[17,174,"2018-03-15","15:12:00","-38.33059551","141.58720305","Corner of Henty Hwy & Wilson Rd., Portland.","32134173","PLD002","22kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,13880,"20180316PWA_02","Vicfire reported a pole on fire at the incident location. On arrival the crew found that a 22kV angle pole was on fire just below the steel cross arm. The crew attempted to isolate supply, however the pole burnt off before the isolation was completed, resulting in the crossarm and conductors falling to the ground causing a small grass fire on the road reserve of around 20m2 in size. There were no injuries, and no other damage reported."]
[17,175,"2018-03-15","17:32:00","-38.0953636","144.339249","18 MALINDA CRESCENT, BELL PARK.","34013007","CRO022","Low voltage AC (<1kV)","Urban"," - LV pillar","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13881,"20180316PWA_03","A customer reported that the pillar outside his property had caught on fire at the incident location. On arrival the crew found that a 415V LV UG pillar had been damaged by an unknown vehicle at some time in the past. \r\nThe Customer reported that he tried to straighten the Pillar by pushing on the lid, at which time the cables inside the pillar began arcing, resulting in a small grass fire of less than 0.5m2 around the base of the pillar. \r\nThe Customer did not receive a shock, and was not injured. There were no injuries, and no other damage reported."]
[17,176,"2018-03-16","07:39:00","-37.40481807","143.89216661","Lot 1 10 BROOMFIELD Rd., CRESWICK.","30013362","BAN009","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,14054,"20180514PWA_05","Report of a pole fire at the incident location. There was no ground fire, no reported injuries or third party property damage."]
[17,177,"2018-03-17","00:00:00","-38.44804243","143.14160083","880 TIMBOON-COLAC Rd., SIMPSON.","30044211","COB011","12.7kV AC (SWER)","Rural Long"," - overhead conductor (bare; steel)","single wire earth return (SWER)","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Severe",2,2,13901,"20180322PWA_06","Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was in the Simpson (Timboon Colac road) area. \rA farmer reported the pole was severely damaged.\r\nThe attending crew replaced a pole and subsequently identified a large tree had contacted  with the 22kV line between poles 2 and 3 of the SMIT spur. There was a ground fire of some 400 by 500 m that was extinguished by the CFA.\r\nIt is unconfirmed that the CFA found the conductor suspended approximately 1.8 m above the road and cut the tree allowing the conductor to clear the road. The conductor was sitting on but not attached to the damaged pole.\r\nThis fire has not (yet) been given a specific name. This fire does not appear in EMCOP, there is another fire nearby that this one may have been confused with. Preliminary information only. Site made safe. Pole replaced."]
[17,178,"2018-03-17","15:04:00","-38.37398596","142.49128527","85 Jamieson St., Warrnambool.","30137710","WBL008","22kV AC","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,13896,"20180322PWA_02","It could not be determined who reported this incident. On arrival the crew found that a 22kV HV Isolator top connection had failed, causing hot debris to fall to the ground, resulting in a grass fire of approx. 8m x 8m = 64m2. \r\nThere were no injuries, and no other damage reported. "]
[17,179,"2018-03-17","21:59:00","-38.54708305","143.09185584","100 BOOROOK Rd., COORIEMUNGLE.","30149644","COB011","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Severe",2,2,13889,"20180320PWA_03","A customer reported a Cyprus tree fell on to powerlines at the incident location. Upon arrival, the Powercor crew found a large tree fell on to the HV line, conductors had been damaged and approx. 2sqm grass burnt.\r\nThere were no injuries."]
[17,180,"2018-03-17","21:40:00","-38.29901377","142.43315220","MAILORS FLAT-KOROIT Rd., MAILORS FLAT.","31017376","KRT-PLD2","66kV AC","Unknown"," - pole (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Severe",2,9.1999999999999993,13895,"20180322PWA_01","On arrival the crew found that a pole fire had occurred on a 22kV & 66kV pole. The pole fire resulted in a grass fire of approx. 5m x 100m = 500m2 of mostly road reserve. \r\nThere was minor damage to fences and a small area of private property burnt. There were no injuries, and no other damage reported."]
[17,181,"2018-03-17","20:49:00","-38.21841956863587","142.77409740747066","OCCUPATION LANE, THE SISTERS.","32055108","TRG002","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Severe",2,9.1999999999999993,13891,"20180321PWA_04","Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was  in the Garvoc area. The attending crew found evidence of broken pole. The site was left undisturbed and referred  to Victoria Police prior to any restoration works.\r\nFire damage and response activities undertaken as part of response to 4 fires in the area. Address approximate."]
[17,182,"2018-03-17","21:00:00","-38.23100986","142.95088219","20 SPRING DAM Rd., TERANG.","32055460","TRG001","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Severe",2,9.1999999999999993,13899,"20180322PWA_03","Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was  in the Terang (Spring Dam road) area. An off duty Powercor worker was part of the CFA crew attending. He  subsequently reported that there was a large gum tree in contact with the 22kV line  between poles 2 and 3 of the spring dam spur.\r\nThere was a ground fire of some 300m x 500 m that was extinguished by the CFA prior to them mobilising to the nearby Terang fire. This fire has not (yet) been given a specific name. Fire damage and response activities undertaken as part of response to other fires in the area and may have initially been considered as advance spotting of another fire"]
[17,183,"2018-03-17","00:00:00","-38.38667874","142.84634113","2450 COBDEN-WARRNAMBOOL Rd., LAANG.","32056486","TRG005","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Severe",2,9.1999999999999993,13902,"20180322PWA_07","Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was in the Laang Area (Warrnambool – Cobden Road)  area. \rThe information from fire investigators is that this fire originated where a large tree may have contacted a high voltage line.\r It is to be confirmed that a Powercor crew attended removed the tree and undertook repairs.  Powercor crew attended removed the tree and undertook repairs."]
[{"$f":"COUNTA(C221:O221,Q221,T221:V221)","v":17},184,"2018-03-17","20:45:00","-38.23740028046317","142.92894065774158","Oppossite 6695 Princess Hwy, Terang.",32194776,"TRG004","22kV AC","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Severe",2,9.1999999999999993,13892,"20180321PWA_03","Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was  in the Terang area. The attending crew found evidence of conductor clashing under strong winds the site was left undisturbed and referred  to Victoria Police prior to any restoration works.\r\nFire damage and response activities undertaken as part of response to 4 fires in the area."]
[{"$f":"COUNTA(C222:O222,Q222,T222:V222)","v":17},185,"2018-03-17","00:00:00","-38.232913498476854","143.0798449841309","CROSS FOREST Rd., NAROGHID.",33037538,"CDN006","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Severe",2,9.1999999999999993,13893,"20180321PWA_01","Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires  was  in the Gnotuk area. Preliminary investigations by the Arson squad have identified that this fire originated near the intersection of Cross Forrest road and Saddlers roads in Gnotuk ( Naroghid)\r\nThe police information attributes this fire to a tree  branch that had contacted power lines. Exact point of origin to be clarified. At this time this has not been verified by Powercor personnel."]
[17,186,"2018-03-17","10:46:00","-38.51103073","143.55287019","90 Fry's Rd., Gellibrand.","33039091","CLC006","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within electric line construction area",19.8,"Severe",2,39.6,13883,"20180319PWA_01","Customer reported power lines down and had caused a fire. On arrival the crew found a tree had fallen and brought down a HV conductor between BLANC pole 5 and 6. There was a ground fire (30x10m) in the road reserve.\r\nCrew advised a large tree had fallen in high winds bring 1 conductor to ground and starting a fire. There were no reported shocks or injuries."]
[17,187,"2018-03-17","20:45:00","-37.87584266","142.15078728","BANEMORE 992 TWOMEYS BRIDGE Rd.,, YATCHAW.","33058409","HTN003","22kV AC","Rural Long"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Severe",2,9.1999999999999993,13890,"20180321PWA_02","Customer reported wires down had started a fire in paddock at the incident location. On arrival the crew found that a tree (Blue gum) had fallen on the line and brought down a HV conductor between ELLBURGER P1 & P2.\r\nThe fire was at the northern edge of a large bushfire. Victoria police requested to attend. Crew attended. Tree cleared and line restored after site observed by Victoria Police as part of investigation into cluster of fires."]
[17,188,"2018-03-17","23:28:00","-38.07172725","142.43978262","1209 HARRIS Rd., MINJAH.","33102095","KRT012","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Severe",2,9.1999999999999993,14016,"20180423PWA_03","Emergency services reported that there was a number of fires in the south west of Victoria. One of these fires was in the Minjah Hawkesdale area. The attending crew found damaged conductor near the intersection of Harris Road.\nFire damage and response activities were undertaken as part of response to a number of fires in the area."]
[17,189,"2018-03-18","11:55:00","-37.83138202","144.85071803","348 BLACKSHAWS Rd., ALTONA NORTH.","30117064","BLTS-SCI","22kV AC","Unknown"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,13924,"20180329PWA_01","Powercor/Citipower Controller, Tony Speechley, @ 11:55 & 11:56 on 18/03/2018, emailed the NAO AH Ardeer to advise of a Pole Fire on the BLTS-SCI 66kV Pole 34 LIS-5873, Blackshaws Rd corner Mahon Ave, Altona North. NAO spoke to the field crew and PCA Operator, and they advised that the pole fire appeared to have started at the 22kV X-arm King-Bolt and 22kV Centre-Phase Insulator and tracked upwards and downwards along the pole. The MFB attended site and extinguished the fire. The pole was inspected on the day 18/03/2018 for damage and field crews undertook repairs to the damaged pole the very next day -  19/03/2018 @ approx. 17:00.\rThere was no reported HVI, injury, shocks or ground fire as a result of this incident."]
[17,190,"2018-03-18","00:25:00","-38.39037496","142.64088338","4350 COBDEN-WARRNAMBOOL, ALLANSFORD.","30134052","WBL002","22kV AC","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Severe",2,2,13900,"20180323PWA_02","Multiple customers called to report no supply in the area. On arrival the crew found that a large tree branch had contacted the HV conductors at the incident location. The subsequent clashing of the 22kV conductors resulted in a grass fire of approx. 4000m2 of road reserve and private property. There was damage to fences pasture and a tree plantation. \r\nThere were no injuries."]
[17,191,"2018-03-18","10:05:00","-38.19120171","144.47356768","2-4 CHRISTIES Rd., LEOPOLD.","31012208","DDL014","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,14055,"20180515PWA_01","Customer reported pole fire at incident location. There was no ground fire, no reported injuries or third party property damage."]
[17,192,"2018-03-18","15:06:00","-37.83707143","144.80016870","PRINCES FREEWAY, LAVERTON NORTH.","31024388","ATS-TYA","66kV AC","Unknown"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,13884,"20180319PWA_02","A Powercor Line Worker advised of a grass fire in the road reserve of the Princes Freeway, Laverton North near the base of DBL CCT 66kV Pole 108. The pole appears to have burnt through and snapped at this point, just below the bottom 66kV x-arm. \rThe resultant sparks from this have fallen to the ground below and caused a grass fire of approximately 8m x 5m near the base of Pole 108 LIS-3172. There was no reported HVI, injury or shocks as a result of this incident."]
[17,193,"2018-03-18","02:53:00","-37.06899506","144.21684417","2A Greenhill Avenue, Castlemaine.","32049313","CMN003","Low voltage AC (<1kV)","Rural Long"," - overhead conductor (bare; copper)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Very High",1,0.2,13905,"20180326PWA_01","Report of damaged powerline and grass fire, at the incident location. On arrival the crew found at Greenhill Ave, Castlemaine, between LIS 508022 & LIS 508023 trees making contact with LV, causing conductors to clash with a broken conductor making contact with the ground, causing a small 20m x 1.5m grass fire\r\nThere were no reported shocks or injuries."]
[17,194,"2018-03-18","11:37:00","-36.36537307","141.15880213","WESTERN HIGHWAY, LILLIMUR.","32122137","NHL031","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very High",1,1,13886,"20180319PWA_04","An customer reported a low conductor at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole which burnt the cross arm only. \r\nNo protection operated. There was no ground fire. There were no reported injuries or third party property damages."]
[17,195,"2018-03-18","07:51:00","-37.52062781","142.04037186","10024 NATIMUK-HAMILTON Rd., CAVENDISH.","32125402","HTN004","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Severe",2,9.1999999999999993,13944,"20180405PWA_03","Vicfire reported a pole fire at the incident location. On arrival the crew found that a Strain cross-arm had burnt off at one end, allowing the conductor and insulators to fall onto a service cable below. \r\nThere was no ground fire, and further tests showed that there was no apparent HVI. There was no reported third party damage or any injuries."]
[17,196,"2018-03-18","11:36:00","-37.82846633","144.78915811","105-121 DOHERTYS Rd., LAVERTON NORTH.",32176040,"LVN032","22kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,13887,"20180320PWA_01","Powercor/Citipower Controller reported there is a fire burning at the top of the pole Pole 95 LIS-30506 (BLTS-SCI & BLTS-LVN DBL CCT 66kV) & (LVN032 22KV feeder).\r\nThere was no reported HVI, injury, shocks or ground fire as a result of this incident. Upon isolation crew carried out repairs and made site safe."]
[{"$f":"COUNTA(C234:O234,Q234,T234:V234)","v":17},197,"2018-03-19","15:55:00","-37.00015299","141.80886013","Digger Jims Rd., Toolondo.","30082900","HOTS-CHM","66kV AC","Unknown"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",{"$f":"IF(O234=\"\",\"\",IF(O234=\"LBRA only\",0.2,IF(O234=\"HBRA only\",1,IF(O234=\"within electric line construction area\",19.8,IF(O234=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":1},"High",{"$f":"IF(Q234=\"\",\"\",IF(Q234=\"No forecast\",0.1,IF(Q234=\"Low-moderate\",0.2,IF(Q234=\"High\",0.5,IF(Q234=\"Very high\",1,IF(Q234=\"Severe\",2,IF(Q234=\"Extreme\",3.5,5)))))))","v":0.5},{"$f":"IF(OR(P234=\"\",R234=\"\"),\"\",IF(AND(O234=\"within electric line construction area\",Q234=\"No forecast\"),1,P234*R234))","v":0.5},13897,"20180322PWA_04","Customers reported a supply outage in the Charam area and there was a loss of supply to the Charam Zone Substation at 15:51 hours on 19/03/18. There was also a subsequent report of a ground fire at the incident location. \rOn arrival the crew found that a pole fire on a wooden 66 kV pole had resulted in the pole top structure including a steel x arm falling to the ground. \r\nThere was a ground fire of approximately 150m². \rThere were no injuries."]
[{"$f":"COUNTA(C235:O235,Q235,T235:V235)","v":17},198,"2018-03-19","23:19:00","-36.33683382","141.70002591","7165  WESTERN HIGHWAY, NHILL.","32112322","NHL015","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",{"$f":"IF(O235=\"\",\"\",IF(O235=\"LBRA only\",0.2,IF(O235=\"HBRA only\",1,IF(O235=\"within electric line construction area\",19.8,IF(O235=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":1},"High",{"$f":"IF(Q235=\"\",\"\",IF(Q235=\"No forecast\",0.1,IF(Q235=\"Low-moderate\",0.2,IF(Q235=\"High\",0.5,IF(Q235=\"Very high\",1,IF(Q235=\"Severe\",2,IF(Q235=\"Extreme\",3.5,5)))))))","v":0.5},{"$f":"IF(OR(P235=\"\",R235=\"\"),\"\",IF(AND(O235=\"within electric line construction area\",Q235=\"No forecast\"),1,P235*R235))","v":0.5},13898,"20180322PWA_05","VicFire reported a pole fire at the incident location. On arrival the crew found that a wooden crossarm required replacement due to the pole fire. There was a small ground fire in private property of approximately 10x3m in the vicinity of the base of the pole. There were no injuries."]
[17,199,"2018-03-19","00:25:00","-37.52740733","144.47687362","1328  BACCHUS MARSH Rd., BULLENGAROOK.","33075101","BMH006","22kV AC","Rural Long"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very High",1,1,13907,"20180326PWA_02","A PCA fault crew attended a fault at the incident location. On arrival they noticed a grass fire had started (10 x 5 mtrs). They found a burnt EDO fuse tube in the burnt area. There were no reported injuries, there was minor damage to the customers fence and service pit."]
[17,200,"2018-03-20","03:20:00","-36.41235122","143.61264590","21 TANTALLA STREET, WEDDERBURN.","30018807","CTN002","22kV AC","Rural Long"," - overhead conductor (bare; copper)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,13908,"20180326PWA_03","Customers reported damaged powerline and sparking, at the incident location. On arrival the crew found at 21 Tantalla Street Wedderburn, between LIS 852793 & LIS 610343 a tree had made contact with HV, broken conductors making contact with the ground, causing a small 1m x 1m grass fire.\r\nThere were no reported shocks or injuries."]
[{"$f":"COUNTA(C238:O238,Q238,T238:V238)","v":17},201,"2018-03-20","00:38:00","-37.16632311","142.86737484","GARDEN GULLY VINEYARD, 1477 WESTERN HIGHWAY, GREAT WESTERN.",31014142,"ART-STL","66kV AC","Unknown"," - pole (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",{"$f":"IF(O238=\"\",\"\",IF(O238=\"LBRA only\",0.2,IF(O238=\"HBRA only\",1,IF(O238=\"within electric line construction area\",19.8,IF(O238=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":4.5999999999999996},"High",{"$f":"IF(Q238=\"\",\"\",IF(Q238=\"No forecast\",0.1,IF(Q238=\"Low-moderate\",0.2,IF(Q238=\"High\",0.5,IF(Q238=\"Very high\",1,IF(Q238=\"Severe\",2,IF(Q238=\"Extreme\",3.5,5)))))))","v":0.5},{"$f":"IF(OR(P238=\"\",R238=\"\"),\"\",IF(AND(O238=\"within electric line construction area\",Q238=\"No forecast\"),1,P238*R238))","v":2.2999999999999998},13904,"20180323PWA_06","VicFire reported a pole fire at the incident location. On arrival the crew found that a wooden 66/22 kV pole was slightly damaged between the steel crossarms on the centre and bottom circuits. There was no ground fire. There were no injuries."]
[{"$f":"COUNTA(C239:O239,Q239,T239:V239)","v":17},202,"2018-03-21","20:51:00","-36.20442159","144.94812329","171 HENDERSON Rd., TONGALA.","33107920","KYM006","22kV AC","Rural Short"," - overhead conductor (bare; copper)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",{"$f":"IF(O239=\"\",\"\",IF(O239=\"LBRA only\",0.2,IF(O239=\"HBRA only\",1,IF(O239=\"within electric line construction area\",19.8,IF(O239=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"High",{"$f":"IF(Q239=\"\",\"\",IF(Q239=\"No forecast\",0.1,IF(Q239=\"Low-moderate\",0.2,IF(Q239=\"High\",0.5,IF(Q239=\"Very high\",1,IF(Q239=\"Severe\",2,IF(Q239=\"Extreme\",3.5,5)))))))","v":0.5},{"$f":"IF(OR(P239=\"\",R239=\"\"),\"\",IF(AND(O239=\"within electric line construction area\",Q239=\"No forecast\"),1,P239*R239))","v":0.1},13909,"20180326PWA_04","Report of grass fire at incident location. On arrival the crew found at 171 Henderson Road Tongala, LIS 953084, two dead birds were found at base of pole and a 10m x 10m burnt area of grass. There was no reported shocks, injuries or property damage."]
[17,203,"2018-03-24","11:42:00","-36.05379999","143.10217699","BIRCHIP-WYCHEPROOF Rd., NARRAPORT.","30023395","CTN001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very High",1,4.5999999999999996,13925,"20180329PWA_02","SCADA alarm advised that Birchip P29 ACR had tripped to lockout, shortly after customer reported a conductor down at the incident location. On arrival the crew found that a wooden angle-strain cross-arm had burnt through at the roadside disc / bridging insulator, causing the conductor to fall to ground.\r\nThere was no ground fire, no reported injuries, no 3rd party damage, protection operated."]
[17,204,"2018-03-24","14:19:00","-36.30104308","144.47983647","1845 PRAIRIE-ROCHESTER Rd., LOCKINGTON.","30122637","SHP012","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13912,"20180327PWA_02","Vicfire reported a pole fire at the incident location. On arrival the crew found that a single phase intermediate pole had caught on fire about 1.5M below the cross-arm, the embers which fell commenced a ground fire of approximately 6M x 40M in area, grass on the road side burnt, minor damage to a nearby fence occurred.\r\nCFA in attendance to extinguish ground fire & pole fire. There was no reported injuries."]
[17,205,"2018-03-24","10:21:00","-37.80459845","144.76370731","161 AUSTRALIS DRIVE, DERRIMUT.","30266247","TNA024","Low voltage AC (<1kV)","Urban"," - services pit","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,14002,"20180418PWA_06","“P & N ENGINEERING PTY LTD, phoned in on 24/03/2018 @ 10:21 to advise Rain went into pit and caught on fire. It is still on fire. No supply. Cust haven’t called 000 but adv to. Currently raining.”\r On arrival @ 11:41 on 24/03/2018 the PCA ATL advised that the LV Service Pit in the road reserve between No. 161 & 163 Australis Drive, Derrimut, 3030 was smoking and there was flames coming out of the pit.  Eric advised that he then proceeded to Australis-Westpark 750kVA Kiosk s/stn and isolated the LV Street circuit supplying this pit. Eric advised that he has organised civils and the UG field crew Cameron McCallum Serle to attend site for repairs. On arrival @ 13:46 on 24/03/2018 the UG field crew Cameron McCallum Serle has advised that, what appears to be a fault in the pit, has caused the whole pit to melt, including 1-2m of 4/C 35mm LV Service Cable, 4 x LV Pit Connectors and approx. 150-300mm of consumers lv mains to 161 and 163 Australis Drive, Derrimut, 3030. There was no reported ground fire, injury or shocks as a result of this incident. The crew made the site safe and replaced the LV Service Pit, installed a new LV SJ and ran a new section of 35mm² 4/c lv service cable into the new pit.\r A defect notice was issued to No. 161 & 163 Australis Drive, Derrimut, 3030."]
[17,206,"2018-03-24","13:45:00","-38.16460561","144.40924902","8 WATTLEPARK AVENUE, MOOLAP.","31011967","GLE031","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,13928,"20180329PWA_05","A customer reported  to Powercor a pole fire at the incident location. On arrival the crew found that a wooden pole with HV wood cross arm had sustained significant damage due to a pole fire. The top of the pole structure had collapsed onto itself resulting in the HV assets resting in close proximity to the LV conductors. Initially is was suspected that a HVI may of also occurred however no evidence of a HVI has been found. There was no ground fire, no reported injuries, no 3rd party damage, protection operated as expected."]
[17,207,"2018-03-24","10:12:00","-38.20277449","144.33786652","24 PIONEER Rd., GROVEDALE.","32084603","WPD012","22kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,13927,"20180329PWA_04","Vic Fire report to Powercor advising of a pole smoking at the incident location. On arrival the crew found that a wooden pole with HV steel cross arms appeared to be burning internally, at approx. ¾ distance up the pole. \rThe pole was still intact and supply remained on with no wires falling to ground. A controlled interruption was undertaken in the area to allow fire brigade crews safe access to extinguish the fire. The pole was found to be extensively damaged and  required replacement. There was no ground fire, no reported injuries, no 3rd party damage."]
[17,208,"2018-03-24","21:53:00","-36.24667864","142.51649380","3117 BORUNG HIGHWAY, WARRACKNABEAL.","32111009","HSM003","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,14056,"20180515PWA_03","Customer reported a pole fire at incident location. There was no ground fire, no reported injuries or third party property damage."]
[17,209,"2018-03-24","16:54:00","-35.26263951","143.50244132","94 MCKENZIE Rd., TYNTYNDER SOUTH VIC.","32155814","SHL004","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very High",1,0.2,13926,"20180329PWA_03","Customer reported a pole had exploded and it was smoking / smouldering at the incident location. On arrival the crew found that a wooden termination cross-arm had burnt through at the disc insulator string, causing the conductor to fall to ground.\r\nThere was no ground fire, no reported injuries, no 3rd party damage, protection operated."]
[17,210,"2018-03-25","22:42:00","-36.38403348","143.29302865","1422 CHARLTON-ST ARNAUD Rd., YEUNGROON.","32027217","CTN006","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very High",1,4.5999999999999996,13931,"20180329PWA_08","Vicfire reported a pole fire at the incident location. On arrival the crew found that a wooden support ( for ISO single phase side HV fuse units ) cross-arm was fire damaged but supply remained on.\r\nThere was no ground fire, no reported injuries, no 3rd party damage."]
[17,211,"2018-03-25","23:45:00","-35.15574032","141.19054870","1198 MURRAYVILLE NORTH Rd., MURRAYVILLE.","32147691","OYN001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very High",1,1,13936,"20180403PWA_04","Following customer calls, a patrol found pole fire at incident location. There was no ground fire or third party property damage."]
[17,212,"2018-03-25","22:03:00","-35.33030418","141.24865349","759 GUNAMALARY Rd., MURRAYVILLE.","32153230","OYN001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very High",1,1,13940,"20180403PWA_09","Following customer calls, a patrol found pole fire at incident location (Gunmalary 15 ). There was no ground fire or third party property damage."]
[17,213,"2018-03-25","23:37:00","-35.50430711","142.84043490","19  HANNON STREET, SEA LAKE.","32157793","OYN005","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very High",1,1,13930,"20180329PWA_07","Vicfire reported a pole fire at the incident location. On arrival the crew found that a wooden angle-strain cross-arm failed due to fire damage but conductors remained suspended by cross-arm braces.\r\nThere was no ground fire, no reported injuries, no 3rd party damage."]
[17,214,"2018-03-26","15:59:00","-37.96333751","144.69539813","535 OCONNORS Rd., WERRIBEE SOUTH.","30110190","WBE034","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,13941,"20180403PWA_10","Report of a pole fire at the incident location. On arrival the field crew has advised that there was a burnt out HV Inter X-arm. There was no reported Ground fire, HVI, injury, shock or third party damage as a result of this incident."]
[17,215,"2018-03-26","09:20:00","-36.18476792","142.39861534","772 HENTY HIGHWAY, WARRACKNABEAL.","32107264","HSM003","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,13929,"20180329PWA_06","A passer-by reported a pole fire at the incident location. On arrival the Powercor fault crew found that a HV cross arm burnt through. The crew made the place safe and the repairs have been completed. \r\nThere were no injuries, HVI or ground fire"]
[17,216,"2018-03-26","06:52:00","-36.11297130","141.52061257","831  YANAC-NETHERBY Rd., YANAC.","32113215","NHL031","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,13914,"20180327PWA_04","Customers reported a power outage and dim lights at the incident location. On arrival the Powercor fault crew found that the HV cross arm and pole top burnt through. \r\nProtection operated. There was no ground fire, no injuries or third party property damage."]
[17,217,"2018-03-26","00:57:00","-35.16033494","141.42572258","867 SUNSET Rd., COWANGIE.",32145257,"OYN001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,13937,"20180403PWA_05","Following customer calls, a patrol found pole fire at incident location. There was no ground fire or third party property damage."]
[17,218,"2018-03-26","00:57:00","-35.15189015","141.41934155","867 SUNSET Rd., COWANGIE.",32145306,"OYN001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,13938,"20180403PWA_06","Following customer calls, a patrol found pole fire at incident location. There was no ground fire or third party property damage."]
[17,219,"2018-03-26","00:57:00","-35.14955231","141.42001506","867 SUNSET Rd., COWANGIE.","32145320","OYN001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,13939,"20180403PWA_08","Following customer calls, a patrol found pole fire at incident location (Tyalla P43). There was no ground fire or third party property damage."]
[17,220,"2018-03-26","04:08:00","-35.24020757","141.04125053","7332 MALLEE HIGHWAY, PANITYA.","32153749","OYN001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,13935,"20180403PWA_03","Following customer calls, a patrol found pole fire at Murrayville 988. There was no ground fire or third party property damage."]
[17,221,"2018-03-26","09:59:00","-35.28645765","141.14337444","431 NGALLO Rd., MURRAYVILLE.","32153983","OYN001","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,14058,"20180515PWA_05","Customer reported a pole fire at the incident location. There was no ground fire, no reported injuries or third party property damage."]
[17,222,"2018-03-26","16:00:00","-35.39013900","142.66317821","4723 PATCHEWOLLOCK-SEA LAKE Rd., NYARRIN.","32158659","OYN005","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,14059,"20180515PWA_06","Customer reported pole fire at incident location. There was no ground fire, no reported injuries or third party property damage."]
[17,223,"2018-03-26","03:21:00","-35.69224368","142.58103786","1463 HOPETOUN-SEA LAKE Rd., HOPETOUN.","32159080","OYN005","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,14057,"20180515PWA_04","Customer reported pole fire at incident location. There was no ground fire, no reported injuries  or third party property damage."]
[17,224,"2018-03-26","17:50:00","-35.39065932","142.69452810","4780 PATCHEWOLLOCK-SEA LAKE Rd., NYARRIN.","33069395","OYN005","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,14060,"20180515PWA_07","Customer reported pole fire at incident location. There was no ground fire, no reported injuries or third party property damage."]
[17,225,"2018-03-30","11:33:00","-38.31537603","142.40539477","931 TOWER HILL Rd., ILLOWA.","32195786","KRT013","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,13947,"20180406PWA_02","Vicfire reported a pole smoking at the incident location. On arrival the crew found the pole had burnt around the bolts of an LA bracket. There were no reported injuries, ground fire or third party damage."]
[17,226,"2018-03-31","22:53:00","-37.27168363","142.92032719","13 Golf Links Rd., Ararat.","30081982","ART034","Low voltage AC (<1kV)","Rural Short"," - fuse (any other type)","single phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,14026,"20180501PWA_01","Vic Fire reported a pole fire at the incident location.  On arrival the crew found that the 3 phase LV Fused Junction Box had melted and dropped from its mounting position, and wiring in the Underground Service Pit at the base of this pole were running hot. There was no pole fire, no ground fire or any other damage caused by this incident. The cause of the melted Junction Box appears to be the high electrical loading in the domestic installation connected via this U/G Service Pit. Investigations by the fault crew revealed illegal wiring at the meter box; with wiring connected to bypass the meters. Police on site found a hydroponics set up inside the installation, and later TV reports showed vision of Police removing in the order of 200 leafy green plants from this property. Police advised the fault crew not to restore supply to this installation. The fault crew cut the U/G service tails to isolate the installation at the Service Pit."]
[17,227,"2018-04-04","17:44:00","-37.82717473","144.86712449","48  NEW STREET, SOUTH KINGSVILLE.","33072189","BLT022","22kV AC","Urban"," - overhead conductor (bare; copper)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,13942,"20180405PWA_01","Jemena Dispatch advised, MFB had reported that balloons went through powerlines near LIS 28296 and the sub on the pole blown at the incident location.\r\nOn arrival the crew found HV has tracked through insulator and fuse unit through to conductive pole and LV earth which is now also damaged. \r\nThe crew suspects possible HVI. The fallen debris caused very minor grass fire (2m x 1m) at the pole base."]
[17,228,"2018-04-07","23:43:00","-38.33537530737897","143.05592306613153","16 L GRAYLANDS Rd., COBDEN.","30149427","COB012","22kV AC","Urban"," - connector / termination","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"Low-moderate",0.2,0.2,13951,"20180409PWA_05","Vicfire reported “grass fire, powerline and pole sparking may be the possible cause.” \rOn arrival the crew found a grass fire near the base of the cable head pole which burnt an area of around 20m by 3 m. The crew identified some evidence of flashover on the cable terminations but were unable determine a cause.\r There were no reported injuries."]
[17,229,"2018-04-08","09:55:00","-36.43975730","145.22597169","91 Hogan St., Tatura.","30140525","MNA021","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very High",1,0.2,14119,"20180529PWA_02","CFA called to advise that sparks were coming from the pole. Upon arrival crew found that an EDO fuse had candled on (LIS-931068), supply had not been interrupted however.  EDO fuse was changed like for like and supply was restored after a brief interruption to change the fuse.\r\nThere were no emergency services onsite, no police. There was no shock, no injury, no damage to private property or any additional damage to PCA property recorded."]
[17,230,"2018-04-08","16:55:00","-37.79165936","144.77877617","61 CASTRO WAY, DERRIMUT.",30244805,"SU013","22kV AC","Urban"," - switch (disconnector/isolator)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Very High",1,0.2,13957,"20180410PWA_02","A flashover occured due to bird contact at HV SW# 23203 (HV isolators at pole LIS-726276), sparking a small grass fire (5m x 2m) in the nature strip below outside 61 Castro Way. ESV was notified of the small grass fire per the details within this report. \rNo shock, third party damage or injuries to report."]
[17,231,"2018-04-08","14:21:00","-38.38767019965601","143.0697075238037","645 COBDEN-PORT CAMPBELL Rd., GLENFYNE.","33036052","COB011","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Very High",1,1,13952,"20180409PWA_04","Emergency services reported a tree pulled wires down, started grass fire in Cobden-port Campbell Rd., Cobden. On arrival the crew found a large gum tree had fallen bringing down conductors on the opposite side of the road. There was a grass fire initiated  which then burnt an area of around 300m by 5 m, largely along road reserve. \r\nSome farm fencing was damaged. There were no reported injuries."]
[17,232,"2018-04-08","16:55:00",-37.791642400000001,144.78401184000001,"159 Studley Court, Derrimut","PA0128151","SU013","22kV AC","Urban"," - transformer (kiosk mounted)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,14266,"20180723PWA_05","Fire at kiosk substation due to bird induced fault at HV SW# 23203 (HV isolators at pole LIS-726276) (refer incident #13957). Secondary faults occurred and caused fire. Kiosk substation ignited during re-energisation. "]
[17,233,"2018-04-12","20:28:00","-37.18007555","144.36180059","1243 CALDER HIGHWAY, DRUMMOND NORTH.","30033573","CMN001","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very High",1,4.5999999999999996,13989,"20180416PWA_08","CFA reported a grass fire caused by Powercor assets at the incident location. On arrival the crew found that a possum had flashed over on a single phase substation structure, the exact location of the flashover has not been confirmed, causing the possum to fall to the ground and ignite a small grass fire, approximately 10M x 20M square was burnt.\r\nCFA extinguished the fire, and doused the pole also at its base. There were no reported injuries, no 3rd party damage."]
[17,234,"2018-04-12","09:02:00","-36.33131433","145.68670595","55 DOOKIE STREET, DOOKIE.","33090594","STN024","Low voltage AC (<1kV)","Rural Long"," - overhead service conductor (residential)","two phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,13977,"20180412PWA_07","A customer, Suzanne Hall advised a wire had come down and resulted in fire on the nature strip. On arrival the crew found that a catenary and service cable had faulted and come to ground. This caused a ground fire of approximately 10m X 5m. \r\nThere was no injury or third party damage reported."]
[17,235,"2018-04-14","16:40:00","-37.02795026","143.87086764","636 BARINGHUP Rd., CARISBROOK.","30017729","MRO007","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,13985,"20180416PWA_03","Vicfire reported a low conductor and pole fire at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage at the kingbolt, resulting in the conductors being suspended approximately 2m above the ground.\r\nThere was no ground fire, no reported injuries, no 3rd party damage,"]
[17,236,"2018-04-14","16:40:00","-34.64633733","142.85342769","585B TOL TOL Rd., TOL TOL.","30097375","RVL008","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very High",1,1,13990,"20180417PWA_01","Customer reported a low conductor and pole fire at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage at the cross-arm strap, conductor remained suspended above the ground.\r\nThere was no ground fire, no reported injuries, no 3rd party damage."]
[17,237,"2018-04-14","15:30:00","-35.33952971","143.55095721","132 STRADBROKE AVENUE,, SWAN HILL.","30101023","SHL008","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very High",1,0.2,13988,"20180416PWA_07","SCADA alarm for SHL008 feeder lockout initiated a fault crew investigating the outage cause, discovering a pole fire at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage at a cross-arm strap resulting in the conductor falling onto the LV circuit below, contacting the red phase.\r\nThere was no ground fire, no reported injuries, no 3rd party damage, no evidence of HV injection was found by LEI."]
[17,238,"2018-04-14","21:56:00","-35.22062577","143.44629765","1764 MURRAY VALLEY HIGHWAY, BEVERFORD.","30546795","SHL004","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very High",1,1,14061,"20180517PWA_01","Pole fire reported at incident location. There was no ground fire, no reported injuries and no third party property damage."]
[17,239,"2018-04-14","15:36:00","-36.50447960","142.92369183","863 WELLS Rd., AVON PLAINS.","32021671","CTN006","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very High",1,4.5999999999999996,13983,"20180416PWA_01","SCADA alarm from Swanwater ACR initiated fault crew response who discovered a pole fire at the incident location. On arrival the crew found that a three phase intermediate pole had burnt off at the pole top. The embers which fell commenced a ground fire of approximately 6m x 5m in area, grass on the road side burnt, fire self extinguished.\r\nThere was no reported injuries, no 3rd party property damage."]
[17,240,"2018-04-14","23:59:00","-35.57988087","143.93105296","KERANG-MURRABIT Rd., CAPELS CROSSING.","32030396","KGT003","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"Very High",1,1,13991,"20180417PWA_02","Customer reported a low conductor at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage at a grey fog pin insulator, conductor was adrift but remained suspended above the ground.\r\nThere was no ground fire, no reported injuries, no 3rd party damage, no protection operated."]
[17,241,"2018-04-14","14:00:00","-36.65676301","144.52131288","1541 AXEDALE-GOORNONG Rd., BARNADOWN.","32038909","EHK023","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very High",1,4.5999999999999996,14014,"20180423PWA_01","A nearby customer reported a fire on a pole at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole which burnt the cross arm only. Protection operated. There was no ground fire.  There were no reported injuries or third party property damages."]
[17,242,"2018-04-14","16:40:00","-34.62251284","142.78660588","54B  DAMASCUS Rd., ROBINVALE.","32141555","RVL001","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very High",1,0.2,13984,"20180416PWA_02","Vicfire reported a low conductor and pole fire at the incident location. On arrival the crew found that a wooden intermediate cross-arm failed due to fire damage at the kingbolt, conductors remained suspended above the ground.\r\nThere was no ground fire, no reported injuries, no 3rd party damage."]
[17,243,"2018-04-14","19:31:00","-34.17578555","142.03143223","444 COWANNA AVENUE, MERBEIN.","32145013","MBN031","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very High",1,0.2,13986,"20180416PWA_05","Customer called reporting a pole fire at the incident location. On arrival the crew found that a wooden termination cross-arm failed due to fire damage at the bridging insulator / disc string hardware mounting points, the overhead conductor remained suspended held up by the bridge.\r\nThere was no ground fire, no reported injuries, no 3rd party damage"]
[17,244,"2018-04-14","16:40:00","-34.18980573","141.62194082","3584 OLD MAIL Rd., CULLULLERAINE.","32147375","MBN031","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Very High",1,4.5999999999999996,13987,"20180416PWA_06","SCADA alarm for Lake Cullulleraine P264 ACR lockout initiated a fault crew investigating the outage cause, subsequently a customer with specific location details called reporting a pole fire at the incident location. \r\nOn arrival the crew found that a wooden termination cross-arm failed due to fire damage at a EDO fuse unit mounting location, resulting in the conductor falling onto the ground below.\r\nThere was no ground fire, no reported injuries, no 3rd party damage."]
[17,245,"2018-04-16","08:34:00","-36.31446196","141.11655896","BRIMBLE Rd., LILLIMUR.","32094204","NHL031","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,14008,"20180419PWA_02","Following a line outage, a crew reported a fire on a pole at the incident location. On arrival the crew found that a pole fire had occurred on a 12.7kV pole which burnt the pole top only.  \r\nProtection operated.  There was no ground fire.  There were no reported injuries or third party property damages."]
[17,246,"2018-04-18","08:13:00","-36.03307494","142.03668265","5125 DIMBOOLA-RAINBOW Rd., RAINBOW.","32121639","NHL015","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,14007,"20180419PWA_01","Following a feeder outage, a crew reported a fire on a pole at the incident location. On arrival the crew found that a cross arm fire had occurred on a 22kV pole which burnt the cross arm only. \r\nProtection operated. There was no ground fire.  There were no reported injuries or third party property damages."]
[17,247,"2018-04-19","14:23:00","-36.34749784","145.41737168","145 FORD Rd., GRAHAMVALE.","33088530","SHTS-STN","66kV AC","Unknown"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,14013,"20180420PWA_01","Customer rang to advise he heard a loud bang and reports ground fire at the incident location. There was a reclose of the SHTS-STN 66kV line at that time. A crew attended and found a 3mx3m grass fire had start at the base of S/S P13 Ford Tie S/L, Fire had self-extinguished when crew arrived. \r\nCrew advise a pair of birds had flashed over on the 66kV pole SHTS-STN P9 on the cnr of Verney Rd and Ford Rd., resulting in a HVI into a street lighting CCT that was fed from the Ford Rd P13 S/S. This flash over caused damage to a  66kV insulator on P9, 9 damaged street lights and a melted fuse box on P13, that started the ground fire.\nAn LEI attended. No damage to customer installation identified. The crew replaced the fuse box and left the street lighting CCT off supply awaiting repairs. Damaged 66kV insulator listed for replacement.\r\nThere were no reported shocks or injuries."]
[17,248,"2018-04-21","16:43:00","-37.58447995","143.84104908","29 Albert St.,  Sebastopol.","30013047","BAS034","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,14033,"20180503PWA_03","A broken HV Xarm was reported . A crew attended and found a HV conductor with attached insulator and portion of burnt wooden Xarm was hanging above the LV conductor on pole."]
[17,249,"2018-04-22","21:41:00","-36.63783629","144.52476218","AXEDALE-GOORNONG Rd., GOORNONG.","33021748","EHK023","22kV AC","Rural Long"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,14017,"20180426PWA_01","Vic Fire reported wires down and grass fire at incident location. On arrival at LIS 425449, Axedale-Goornong Road Barnadown, crew found a HV conductor had failed, starting a 120m² grass fire, where a 3m section of 6/1/093 conductor had been spliced into the 3/4/093 line during previous works, crew made safe returning the line to service with temporary repairs with final repairs completed the next day. There was no reported shocks, injuries or property damage.\r"]
[17,250,"2018-04-23","13:28:00","-34.66520474","142.71060840","156 HOCKING Rd., HAPPY VALLEY.","32147929","WMN014","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very High",1,0.2,14062,"20180517PWA_02","Report of pole fire at incident location.\r\nThere was no ground fire, no reported injuries and no third part property damage."]
[17,251,"2018-04-24","15:39:00","-38.27637767","144.24278498","1360 BLACKGATE Rd., FRESHWATER CREEK.","30067860","WPD014","22kV AC","Rural Short"," - transformer (pole mounted)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","within area delineated on plan LEGL./16-354",4.5999999999999996,"High",0.5,2.2999999999999998,14022,"20180427PWA_02","A customer called regarding a supply interruption. The crew attended and found failed transformers in the area. Harrison F’Water Ck transformer had been hit by lightning and this resulted in a ground fire. \r\nThe fire was approximately 1 X 2 meters. No injury or third party damage had occurred."]
[17,252,"2018-04-25","07:42:00","-36.19499213","144.91210740","7840 MURRAY VALLEY HIGHWAY, KOYUGA.",30125482,"ECA005","22kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,14018,"20180426PWA_02","Police reported wires sparking and explosion at incident location. On arrival the crew found Magpies had caused a HV fault, starting a 15m x 60m grass fire.\r\nThere was no reported shocks, injuries or property damage."]
[17,253,"2018-04-28","23:51:00","-38.44991933","144.097913","96 Bambra Rd., AIREYS INLET.","33045917","WPD014","Low voltage AC (<1kV)","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"Low-moderate",0.2,0.91999999999999993,14032,"20180503PWA_02","CFA reported a pole fire at  Bambra Rd., Aireys Inlet. A crew was dispatched to investigate. Upon arrival, the crew found evidence of a LV crossarm fire and a burnt LV service fuse mount. The crew made safe and made necessary repairs. There was evidence of a small ground fire at the base of pole."]
[17,254,"2018-05-01","04:16:00","-36.34748529","145.59662461","205 COSGROVE-LEMNOS Rd., COSGROVE.","30132664","STN024","22kV AC","Rural Long"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,14079,"20180522PWA_06","Following a supply interruption there was a report of fallen conductors and a small ground fire at incident location.There was a ground fire, no reported injuries or third party property damage."]
[17,255,"2018-05-02","03:30:00","-37.8214951","144.7868","144 Fitzgerald Rd., Laverton North.","30112356","LVN034","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,14031,"20180503PWA_01","Truck contacted pole and ground fire some  distance away was attributed to fault current damage. A ground fire was reported at the address in this reportand crews found a HV cable termination requires repair. A  separate report of a truck contacting  a pole, twisting cross-arm and dislodging conductor was also received . This pole is on the same feeder and downstream of the ground fire location by some 2.1 Km."]
[17,256,"2018-05-03","23:24:00","-36.35414593","145.40550622","19-23 HAWKINS STREET, SHEPPARTON.","32189058","SHN012","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,14080,"20180522PWA_07","Vicfire reported pole fire on Hawkins Street, near Allen Street, Shepparton. Crew attended and found HV Intermediate crossarm had burnt the end of and was laying on LV crossarm of the substation.\r\nThere was no ground fire, no injuries or third party property damage."]
[17,257,"2018-05-04","10:08:00","-35.93991673","143.85841370","2126 LODDON RIVER Rd., APPIN SOUTH.","32037296","KGT004","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,14037,"20180508PWA_01","All supply failure reported, crew attended at incident location. They walked an inaccessible area and found SWER Intermediate Pole 6 Appin South had burnt off. An area of 100m Square was reported as burnt. There was no reported shocks, no injuries reported. No CFA in attendance."]
[17,258,"2018-05-04","08:32:00","-36.47317657","145.32737911","350 POGUE Rd., TOOLAMBA.","32188653","MNA034","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,14038,"20180509PWA_01","A Powercor fault crew attending a feeder outage on MNA034 found that a pole top burnt through at Pogue P3E. There were shocks, no injuries or ground fire start."]
[17,259,"2018-05-05","17:45:00","-37.56352500","144.56352500","107 LA COTE Rd., GREENDALE.","30112192","BMH003","Low voltage AC (<1kV)","Rural Long"," - fuse (any other type)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,14133,"20180601PWA_01","Customer called in to advise transformer is on fire and the fire brigade has been called and are on the way. On arrival the crew has advised that a Three-Phase FOLCB had overheated and burnt out on LV Service Pole. \r\nAs a result of this, the burnt out FOLCB has fallen onto the ground below. There was no reported ground fire, third party damage, injury or shocks as a result of this incident."]
[17,260,"2018-05-06","17:50:00","-37.59818410","143.69400501","205 HADDON SCHOOL Rd., HADDON.","32013728","BAS011","Low voltage AC (<1kV)","Rural Long"," - fuse (any other type)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,14036,"20180507PWA_01","A report was received from a customer of sparks coming from our pole at the above location. On arrival the crew found that the 100A FOLCB had overheated and caught fire. \r\nMolten plastic and metal had dropped to the ground and caused a small grass fire which burnt an area 5 x 1 metres. The CFA were onsite and had extinguished the fire.\r\nThere was no injury, shock or third party damage."]
[17,261,"2018-05-09","23:51:00","-37.70509973","144.55265570","2 MAPLEWOOD CLOSE, BROOKFIELD.","31024012","MLN013","Low voltage AC (<1kV)","Rural Short"," - fuse (any other type)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,14081,"20180522PWA_08","Customer called in to advise. Pole is on fire directly outside. Weather is raining customer is calling the Fire Brigade. On arrival the crew has advised that an FSD/Krone box has overheated and burnt out on transformer pole.\r\nThe resultant heat has also caused the insulation to melt off the LV UG Street cct mains cable. There was no reported ground fire, third party damage, injury or shocks as a result of this incident"]
[17,262,"2018-05-10","02:45:00","-34.36673871","141.91747028","MILLEWA Rd., MERRINEE.","32140161","RCT023","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,14048,"20180510PWA_06","Following on from a line patrol the crew found pole fire.  There was no ground fire, no reported injuries or third party property damage. On arrival crew isolated supply and carried out repairs."]
[17,263,"2018-05-11","12:47:00","-38.24997380","142.69077540","89 STUARTS Rd., FRAMLINGHAM.","30047279","TRG004","Low voltage AC (<1kV)","Rural Short"," - fuse (any other type)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,14084,"20180522PWA_11","Customer reported a fire on a pole at the incident location. On arrival, the crew found that a pole mounted LV fuse box had overheated, causing the box to melt and catch fire. There was no ground fire. There were no reported injuries or third party property damages."]
[17,264,"2018-05-17","19:05:00","-37.24817646","144.76204451","21 WOODVALE CRESCENT, LANCEFIELD.","33030123","WND013","Low voltage AC (<1kV)","Rural Long"," - fuse (any other type)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,14064,"20180518PWA_01","Customer advised there appears to be a pole fire at incident location. On arrival the crew has advised that an FSD/Krone box has overheated and burnt out. There was no ground fire, no reported injuries and no third party property damage."]
[17,265,"2018-05-18","08:13:00","-35.83217292","144.24728117","6134 MURRAY VALLEY HIGHWAY, COHUNA.","32033895","CHA003","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,14065,"20180518PWA_02","Vicfire reports pole fire at the incident location. A crew attended and found a pole top fire had occurred, damaging top of pole and Xarm. CFA attended. There were shocks, no injuries or ground fire start."]
[{"$f":"COUNTA(C303:O303,Q303,T303:V303)","v":17},266,"2018-05-20","14:26:00","-38.64077912","143.13356916","2310 PRINCETOWN Rd., PRINCETOWN.","33037378","COB011","Low voltage AC (<1kV)","Rural Long"," - fuse (any other type)","three phase","Started in or originated from a distribution system","HBRA only",{"$f":"IF(O303=\"\",\"\",IF(O303=\"LBRA only\",0.2,IF(O303=\"HBRA only\",1,IF(O303=\"within electric line construction area\",19.8,IF(O303=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":1},"No forecast",{"$f":"IF(Q303=\"\",\"\",IF(Q303=\"No forecast\",0.1,IF(Q303=\"Low-moderate\",0.2,IF(Q303=\"High\",0.5,IF(Q303=\"Very high\",1,IF(Q303=\"Severe\",2,IF(Q303=\"Extreme\",3.5,5)))))))","v":0.1},{"$f":"IF(OR(P303=\"\",R303=\"\"),\"\",IF(AND(O303=\"within electric line construction area\",Q303=\"No forecast\"),1,P303*R303))","v":0.1},14134,"20180601PWA_02","A customer reported pole on fire in the middle below transformer. On arrival the crew found a fuse box had been on fire and extinguished from the rain. No ground fire, injuries, 3rd party property damage was reported. On arrival crew isolated supply and carried out repairs."]
[17,267,"2018-05-23","23:45:00","-36.41048686","145.24951414","6065 MIDLAND HIGHWAY, TATURA.","30138758","SHTS-SHP","Low voltage AC (<1kV)","Unknown"," - fuse (any other type)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,14114,"20180528PWA_03","CFA reported transformer explosion and grass fire at incident location. On arrival  crew found a FOLCB had failed. \rThere was a 15x10 metre grass fir There was no reported injuries or third party property damage."]
[17,268,"2018-05-29","20:52:00","-37.10183762","144.20551485","3 ELEANOR DRIVE, CAMPBELLS CREEK.","30255740","CMN001","22kV AC","Rural Long"," - overhead conductor (insulated)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,14203,"20180705PWA_02","Customer reported transformer was on fire but still sparking and another neighbour had heard a loud bang. Crew attended and found that two of the HV insulated leads between HV fuse and HV bushings on transformer had crossed over on two of the phases and melted. There were no injuries, no ground fire, no third party property damage."]
[17,269,"2018-05-29","13:56:00","-35.06657612","142.03510836","WAKEFIELD Rd., WALPEUP.","32147316","OYN001","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"No forecast",0.1,0.1,14130,"20180531PWA_05","A Powercor fault crew attending a feeder fault found that a burnt pole.  Crew believed the pole was hit by lightning. The pole fell on to ground and burnt through. There was no injuries or third party property damage. On arrival crew arranged for isolation and pole was replaced."]
[17,270,"2018-05-29","13:56:00","-35.06356516","142.03450703","WAKEFIELD Rd., WALPEUP.","32147329","OYN001","12.7kV AC (SWER)","Rural Long"," - pole (wood)","single wire earth return (SWER)","Started by lightning striking a distribution system or a part of a distribution system ","HBRA only",1,"No forecast",0.1,0.1,14131,"20180531PWA_06","A Powercor fault crew attending a feeder fault found that a burnt pole. Crew believed the pole was hit by lightning. The pole fell on to ground and burnt through. There was no injuries or third party property damage. On arrival crew arranged for isolation and pole was replaced."]
[17,271,"2018-05-29","15:17:00","-35.48458078","142.84699668","CALDER HIGHWAY, SEA LAKE.","32160325","OYN005","22kV AC","Rural Long"," - crossarm (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,14132,"20180531PWA_07","A Powercor fault crew attending an outage found a partially burnt pole top. There was no ground fire, no injuries or third party property damage. On arrival crew isolated supply and carried out repairs."]
[17,272,"2018-06-07","04:00:00","-37.83921635","144.74575281","231 LEAKES Rd., TRUGANINA.","30233147","ATS-WBE","66kV AC","Unknown"," - insulators","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,14143,"20180612PWA_02","Multiple members of the public reported outages, flickering/low volts and hearing explosions.\n\n22kV feeder CB tripped disconnecting 7630 customers.\n\nWhile patrolling the feeder, Powercor electrical operator Joel Guy observed a 66KV clamp top insulator detached, and suspended below its pole top structure.\nThe polymeric, 66kV insulator had broken/sheared clear of its insulator stud mount on the pole’s centre phase, steel, P bracket\n\nThe 37/3.75 AAC, centre phase, 66KV conductor had displaced to the roadside and came to rest on the 66kV steel crossarm.\nThe centre phase has discharged through the cross arm, crossarm braces, into the 22kV arm and down through its braces, and into a 22kV cable head termination beneath.\nThe discharge caused the pole to catch alight and the 22kV cable head termination to sustain some damage.\n\nThe 66kV and 22kV was confirmed as de-energised and the Fire Brigade were instructed to hose the pole down.\n\nThe fault appears to have originated at pole LIS 990959 ATS-WBE P67 \nPowercor crews attended and made the site safe.\nPowercor crews were dispatched to other sites along LV003 were other explosions were reported – as secondary faults to LIS 990959\n\nThe repair activity was transferred to a Lendlease day crew to replace the damaged assets.\n\nAt LIS 990959 ATS-WBE P67 the three polymeric 66kV insulators were replaced with porcelain units, as well as three 22kV surge diverters and connections on the cable head.\n\nThere were no shocks, reported injuries or ground fire."]
[17,273,"2018-06-08","06:20:00","-35.50062546","142.84950254","121 HORACE STREET, SEA LAKE.","31022293","OYN005","22kV AC","Rural Long"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,14142,"20180612PWA_01","Vicfire reported a low conductor and pole fire at the incident location. On arrival the crew found that a wooden intermediate pole failed due to fire damage at the LV kingbolt position, resulting in the pole top assembly being suspended above the LV circuit below. There was no ground fire, no reported injuries, no 3rd party damage"]
[17,274,"2018-06-20","16:44:00","-37.69639282","144.56605598","64 Coburns Rd., Brookfield.","30103173","MLN013","22kV AC","Rural Short"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,14196,"20180704PWA_01","Burnt crossarm found replaced under EAP."]
[17,275,"2017-11-28","18:26:00",-34.298995342277102,142.22092785650801,"166 Pumps Road, Red Cliffs",33064221,"RCTS-MBN","66kV AC","Unknown"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by lightning striking a distribution system or a part of a distribution system ","LBRA only",0.2,"High",0.5,0.1,13518,"20171204PWA_02","Report of lightning strike at the incident location. On arrival the crew found there had been  a lighting strike to centre phase of RCTS-MBN 66/22KV had caused a small 300mm x 300mm grass fire around the earth stake of the customer installation. \nThere were no reported shocks or injuries. LEI inspected installation and found no damage had been caused."]
[17,276,"2018-06-09","19:03:00",-38.294072530000001,143.22067909,"540 Purrumbete Estate, Koallah.",32059366,"CDN002","Low voltage AC (<1kV)","Rural Long"," - fuse (any other type)","three phase","Started in or originated from a distribution system","within area delineated on plan LEGL./16-354",4.5999999999999996,"No forecast",0.1,0.45999999999999996,14144,"20180612PWA_04","Vicfire reported a transformer fire at the incident location. On arrival the crew found that a 480V LV fuse box had burnt out at one end. There was no ground fire. There was no reported third party damage or any injuries."]
[0,277,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,278,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,279,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]
[0,280,null,null,null,null,null,null,null,null,null,null,null,null,null,"",null,"",""]

{"sheet":"3. Systems and Audit","index":4,"n_rows":29,"n_cols":5,"rows_kept":29,"cut":false,"hidden":false,"merged":[[28,1,29,4],[3,5,3,6],[4,5,4,6],[5,5,5,6],[6,1,6,4],[9,1,9,4],[14,1,14,4],[10,1,10,4],[13,1,13,4],[12,1,12,4],[11,1,11,4]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"Powercor"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2017/18"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"Powercor must provide:"}]
[]
[null,"Table 4 - Information or reporting systems"]
[null,"   (1) Name of any IT system used to collect fire start data or fault event data - i.e. SCADA system, or fault reporting system"]
[null,"   (2) Whether the fire recording or fault recording process has been audited or complies with a relevant Australian or industry standard - Yes or No"]
[null,"   (3) List any relevant Australian or industry standards that the fire recording or fault recording process complies with"]
[null,"   (4) Whether the data entered into or removed from the IT system has been audited - Yes or No"]
[]
[]
[null,"Table 4: Information or reporting systems"]
[]
[null,"Information or reporting systems","Name","System Audited","Relevant Standards"]
[null,"System 1","Network Incidents Database","Yes","None aplicable"]
[null,"System 2","Outage Management System (OMS)","Yes","None aplicable"]
[null,"System 3 ","Smallworld GIS (Graphical Information System)","Yes","None aplicable"]
[null,"System 4"]
[null,"System 5"]
[null,"System 6"]
[null,"System 7"]
[null,"System 8"]
[]
[null,"The SGSPAA Internal Audit function undertakes a programme of work in accordance with the SGSPAA Group Internal Audit Plan. This internal audit activity covers elements of the systems and process used for capturing, recording and maintaining fire start data."]