## Assumptions
Risk Monetisation Model - FOLCB Replacements - ELCA
#VALUE!
Disproportionate Factors
Probablity Tree (ELCA)
| Category | Factor | Reference
| Catastrophic Bushfire | 6 | Industry workshop facilitated by AMCL & presented to ESV |  | FOLCB fire start (likelihood)
| Major Bushfire | 3 | Industry workshop facilitated by AMCL & presented to ESV |  | 0.01641%
| Moderate fire | 1 | Industry workshop facilitated by AMCL & presented to ESV
| Minor fire | 1 | Industry workshop facilitated by AMCL & presented to ESV
|  |  |  | Fire start on Non-TFB Day |  | Fire start on TFB Day
Consequence Costs
| Category | $m 2021 | Reference | 96.44% |  | 3.562%
| Catastrophic Bushfire | 378.4582 | DEDJTR Regulatory Impact Statement 2015
| F-Factor Penalty per site per fire start (ELCA) | 0.57038 | Powercor estimate
|  |  |  | Fire start leads to "Catastrophic Bushfire" |  | Fire start leads to "Major Fire" | Fire start leads to "Moderate Fire" | Fire start leads to "Minor Fire"
Units
| Category | Qty | Reference | 5% |  | * not modelled | * not modelled | * not modelled
| FOLCB units - total | 103585 | Asset data
| Total FOLCBs in ELCA | 1989 | PAL estimate
| No of FOLCBs units replaced pa in ELCA | 397.8 | Proactive replacements
| Risk reduction when FOLCB has been proactively replaced | 86% | Cause mitigation analysis
| Unit Rate | 1247.7745 | FOLCB unit rate $2021
| Asset life (years) | 51 | Selection of regulatory life or economic life in years
Probabilities
| Category | Metric | Reference
| No. Fires per year due to FOLCBs p.a | 17 | PAL: FOLCB fire starts data
| Annual Fire Start rate per FOLCB | 0.01641% | See calculation
| Fire start on Non-TFB Day | 96.44% | See calculation
| Fire start on day of Severe and above fire danger | 3.562% | PAL records (past 20 years TFB Days record. Avg.13 TFBDs pa)
| Unsupressed Fire Start causes a Catastrophic Fire | 5% | DEDJTR Regulatory Impact Statement 2015
| Risk reduction when a FOLCB has been replaced | 86% | Cause mitigation analysis
End of Sheet

## Capex Costs
Risk Monetisation Model - FOLCB Replacements - ELCA
#VALUE!
Project Capex
Cost $2021
| Option | Description | FY20/21 | FY21/22 | FY22/23 | FY23/24 | FY24/25 | FY25/26 | FY26/27 | FY27/28 | FY28/29 | FY29/30 | FY30/31
| 1 | FOLCB replacement program | Cost $2021 FY21/22: 496364.693; Cost $2021 FY22/23: 496364.693; Cost $2021 FY23/24: 496364.693; Cost $2021 FY24/25: 496364.693; Cost $2021 FY25/26: 496364.693
2
3
4
5
6
7
8
9
10

## Inflation
Risk Monetisation Model - FOLCB Replacements - ELCA
#VALUE!
Inflation index
|  | Financial Year | FY09/10 | FY10/11 | FY11/12 | FY12/13 | FY13/14 | FY14/15 | FY15/16 | FY16/17 | FY17/18 | FY18/19 | FY19/20 | FY20/21 | FY21/22
|  | Conversion Factor to 2021 | 1.2517 | 1.2398 | 1.211 | 1.1698 | 1.1468 | 1.1226 | 1.0973 | 1.0809 | 1.07 | 1.0497 | 1.0389 | 1.0202 | 1

## Scenario Manager
Risk Monetisation Model - FOLCB Replacements - ELCA
#VALUE!
| Sensitivity Movements | [5 empty] | Forecast Start
| Element | Lower 2 | Lower | Central | Upper |  | 21
| PoF | -75% | -45% | 0% | 15%
| CoF | -75% | -45% | 0% | 15%
| Capex & opex | -15% | -15% | 0% | 15%
| Demand | -1.188% | -1.188% | 0% | 1.312%
| VCR | -15% | -15% | 0% | 15%
| Discount rate | 2.079% | 2.391% | 2.75% | 3.163%
| Environmental costs | -15% | -15% | 100% | 15%
Sensitivity Levels by Scenario
| Scenario | PoF | CoF | Capex | Demand | VCR | Opex | Environment | Discount rate | Notes
| Base case - Do Nothing | Central | Central | Central | Central | Central | Central | Central | Central | Do nothing flat risk cost
| A - Preferred Option | Central | Central | Central | Central | Central | Central | Central | Central | Reducing risk cost as units are replaced
| B - Sensitivity 1 | Upper | Upper | Central | Central | Central | Central | Central | Central | Upper sensitivity
| C - Sensitivity 2 | Lower | Central | Central | Central | Central | Central | Central | Central | PoF lower. CoF central
| D - Sensitivity 3 | Central | Lower | Central | Central | Central | Central | Central | Central | PoF central. CoF lower
| E - Sensitivity 4 | Lower | Lower | Central | Central | Central | Central | Central | Central | PoF lower. CoF lower
| F - Sensitivity 5 | Lower 2 | Lower 2 | Central | Central | Central | Central | Central | Central | PoF lower 2. CoF lower 2
Sensitivity Results by Scenario
| Scenario | PoF | CoF | Capex | Opex | Demand | VCR | Environment | Discount rate
| Base case - Do Nothing | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 2.75%
| A - Preferred Option | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 2.75%
| B - Sensitivity 1 | 15% | 15% | 0% | 0% | 0% | 0% | 100% | 2.75%
| C - Sensitivity 2 | -45% | 0% | 0% | 0% | 0% | 0% | 100% | 2.75%
| D - Sensitivity 3 | 0% | -45% | 0% | 0% | 0% | 0% | 100% | 2.75%
| E - Sensitivity 4 | -45% | -45% | 0% | 0% | 0% | 0% | 100% | 2.75%
| F - Sensitivity 5 | -75% | -75% | 0% | 0% | 0% | 0% | 100% | 2.75%
End of Sheet

## Base Case
Risk Monetisation Model - FOLCB Replacements - ELCA
#VALUE!
Total Consequence Calculation
[11 empty] | $m 2021 |  |  |  |  | $m 2021
| Failure Mode | Risk | Description | [7 empty] | Network Performance | Tangible community cost | OPEX | CAPEX | Environment | Concequence cost | DF | Total concequence cost
| 1 | Catastrophic Busfire | [13 empty] | 0 |  | 2271.3198
|  |  | Catastrophic bushfire | [8 empty] | 378.4582 |  |  |  | 378.4582 | 6
0
|  |  | F-Factor | [10 empty] | 0.57038 |  | 0.57038 | 1
0
0
0
0
| 2 | Major Fire | [13 empty] | 0 |  | 0
0
0
0
0
0
0
| 3 | Moderate Fire | [13 empty] | 0 |  | 0
0
0
| 4 | Minor Fire | [13 empty] | 0 |  | 0
0
0
| 5 | [14 empty] | 0 |  | 0
0
| Total annual risk cost | [14 empty] | 379.0286 |  | 2271.3198
Annual Probabilty of Failure per Scenario
Probability of failure x no. Units
| Base Year | 21
Probability of Failure
| Failure Mode | Risk |  | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
| 1 | FOLCBs Fire start in ELCAs on Severe Fire Danger days |  | 0.05813% | 0.05813% | 0.05813% | 0.05813% | 0.05813% | 0.05813% | 0.05813% | 0.05813% | 0.05813% | 0.05813% | 0.05813%
2
3
4
5
Annual Risk Cost per Scenario
Consequence Cost per Scenario x Probability of Failure
Annual Risk Cost ($m)
| Failure Mode | Risk |  | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total
| 1 | Catastrophic Busfire |  | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 14.5237
| 2 | Major Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | Moderate Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | Minor Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total |  |  | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 14.5237
End of Sheet

## Scenario A
Risk Monetisation Model - FOLCB Replacements - ELCA
#VALUE!
Total Consequence Calculation
[11 empty] | $m 2021 |  |  |  |  | $m 2021
| Failure Mode | Risk | Description | [7 empty] | Network Performance | Tangible community cost | OPEX | CAPEX | Environment | Concequence cost | DF | Total Cosequence
| 1 | Catastrophic Fire starting in ELCA | [13 empty] | 0 |  | 2271.3198
|  |  | Catastrophic bushfire | [8 empty] | 378.4582 |  |  |  | 378.4582 | 6
0
|  |  | F-Factor | [10 empty] | 0.57038 |  | 0.57038 | 1
0
0
0
0
| 2 | Major Fire | [13 empty] | 0 |  | 0
0
0
0
0
0
0
| 3 | Moderate Fire | [13 empty] | 0 |  | 0
0
0
| 4 | Minor Fire | [13 empty] | 0 |  | 0
0
0
| 5 | [14 empty] | 0 |  | 0
0
| Total annual risk cost | [14 empty] | 379.0286 |  | 2271.3198
Annual reduction in number of FOLCB units
| BAU Replacements (cumulative) |  |  | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
| Amount |  |  |  | 0% | 397.8 | 795.6 | 1193.4 | 1591.2 | 1989 | 1989 | 1989 | 1989 | 1989
Annual Probabilty of Failure per Scenario
| Base Year | 21
Probability of Failure
| Failure Mode | Risk |  | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
| 1 | FOLCBs Fire start in ELCAs on Severe Fire Danger days |  | 0.05813% | 0.05813% | 0.04813% | 0.03813% | 0.02814% | 0.01814% | 0.008138% | 0.008138% | 0.008138% | 0.008138% | 0.008138%
2
3
4
5
Annual Risk Cost per Scenario
Consequence Cost per Scenario x Probability of Failure
Annual Risk Cost ($m)
| Failure Mode | Risk |  | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total
| 1 | Catastrophic Busfire |  | 1.3203 | 1.3203 | 1.0932 | 0.86614 | 0.63904 | 0.41195 | 0.18485 | 0.18485 | 0.18485 | 0.18485 | 0.18485 | 6.5753
| 2 | Major Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | Moderate Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | Minor Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total |  |  | 1.3203 | 1.3203 | 1.0932 | 0.86614 | 0.63904 | 0.41195 | 0.18485 | 0.18485 | 0.18485 | 0.18485 | 0.18485 | 6.5753
End of Sheet

## Scenario B
Risk Monetisation Model - FOLCB Replacements - ELCA
#VALUE!
Total Consequence Calculation
[11 empty] | $m 2021 |  |  |  |  | $m 2021
| Failure Mode | Risk | Description | [7 empty] | Network Performance | Tangible community cost | OPEX | CAPEX | Environment | Concequence cost | DF | Total Cosequence
| 1 | Catastrophic Busfire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 2271.3198
|  |  | Catastrophic bushfire | [7 empty] | 0 | 378.4582 | 0 | 0 | 0 | 378.4582 | 6
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | F-Factor | [7 empty] | 0 | 0 | 0 | 0.57038 | 0 | 0.57038 | 1
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2 | Major Fire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3 | Moderate Fire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4 | Minor Fire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total annual risk cost | [14 empty] | 379.0286 |  | 2271.3198
Annual Probabilty of Failure per Scenario
| Base Year | 21
Probability of Failure
| Failure Mode | Risk |  | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
| 1 | FOLCBs Fire start in ELCAs on Severe Fire Danger days |  | 0.06685% | 0.06685% | 0.05535% | 0.04385% | 0.03236% | 0.02086% | 0.009359% | 0.009359% | 0.009359% | 0.009359% | 0.009359%
| 2 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
| 3 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
| 4 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
| 5 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
Annual Risk Cost per Scenario
Consequence Cost per Scenario x Probability of Failure
Annual Risk Cost ($m 2021)
| Failure Mode | Risk |  | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total
| 1 | Catastrophic Busfire |  | 1.5184 | 1.5184 | 1.2572 | 0.99606 | 0.7349 | 0.47374 | 0.21257 | 0.21257 | 0.21257 | 0.21257 | 0.21257 | 7.5616
| 2 | Major Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | Moderate Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | Minor Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total |  |  | 1.5184 | 1.5184 | 1.2572 | 0.99606 | 0.7349 | 0.47374 | 0.21257 | 0.21257 | 0.21257 | 0.21257 | 0.21257 | 7.5616
End of Sheet

## Scenario C
Risk Monetisation Model - FOLCB Replacements - ELCA |  |  |  | Menu
#VALUE!
Total Consequence Calculation
[11 empty] | $m 2021 |  |  |  |  | $m 2021
| Failure Mode | Risk | Description | [7 empty] | Network Performance | Tangible community cost | OPEX | CAPEX | Environment | Concequence cost | DF | Total Cosequence
| 1 | Catastrophic Busfire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 2271.3198
|  |  | Catastrophic bushfire | [7 empty] | 0 | 378.4582 | 0 | 0 | 0 | 378.4582 | 6
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | F-Factor | [7 empty] | 0 | 0 | 0 | 0.57038 | 0 | 0.57038 | 1
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2 | Major Fire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3 | Moderate Fire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4 | Minor Fire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total annual risk cost | [14 empty] | 379.0286 |  | 2271.3198
Annual Probabilty of Failure per Scenario
| Base Year | 21
Probability of Failure
| Failure Mode | Risk |  | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
| 1 | FOLCBs Fire start in ELCAs on Severe Fire Danger days |  | 0.03197% | 0.03197% | 0.02647% | 0.02097% | 0.01547% | 0.009975% | 0.004476% | 0.004476% | 0.004476% | 0.004476% | 0.004476%
| 2 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
| 3 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
| 4 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
| 5 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
Annual Risk Cost per Scenario
Consequence Cost per Scenario x Probability of Failure
Annual Risk Cost ($m)
| Failure Mode | Risk |  | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total
| 1 | Catastrophic Busfire |  | 0.72619 | 0.72619 | 0.60128 | 0.47638 | 0.35147 | 0.22657 | 0.10167 | 0.10167 | 0.10167 | 0.10167 | 0.10167 | 3.6164
| 2 | Major Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | Moderate Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | Minor Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total |  |  | 0.72619 | 0.72619 | 0.60128 | 0.47638 | 0.35147 | 0.22657 | 0.10167 | 0.10167 | 0.10167 | 0.10167 | 0.10167 | 3.6164
End of Sheet

## Scenario D
Risk Monetisation Model - FOLCB Replacements - ELCA |  |  |  | Menu
#VALUE!
Total Consequence Calculation
[11 empty] | $m 2021 |  |  |  |  | $m 2021
| Failure Mode | Risk | Description | [7 empty] | Network Performance | Tangible community cost | OPEX | CAPEX | Environment | Concequence cost | DF | Total Cosequence
| 1 | Catastrophic Busfire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 2271.3198
|  |  | Catastrophic bushfire | [7 empty] | 0 | 378.4582 | 0 | 0 | 0 | 378.4582 | 6
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | F-Factor | [7 empty] | 0 | 0 | 0 | 0.57038 | 0 | 0.57038 | 1
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2 | Major Fire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3 | Moderate Fire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4 | Minor Fire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total annual risk cost | [14 empty] | 379.0286 |  | 2271.3198
Annual Probabilty of Failure per Scenario
| Base Year | 21
Probability of Failure
| Failure Mode | Risk |  | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
| 1 | FOLCBs Fire start in ELCAs on Severe Fire Danger days |  | 0.05813% | 0.05813% | 0.04813% | 0.03813% | 0.02814% | 0.01814% | 0.008138% | 0.008138% | 0.008138% | 0.008138% | 0.008138%
| 2 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
| 3 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
| 4 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
| 5 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
Annual Risk Cost per Scenario
Consequence Cost per Scenario x Probability of Failure
Annual Risk Cost ($m)
| Failure Mode | Risk |  | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total
| 1 | Catastrophic Busfire |  | 1.3203 | 1.3203 | 1.0932 | 0.86614 | 0.63904 | 0.41195 | 0.18485 | 0.18485 | 0.18485 | 0.18485 | 0.18485 | 6.5753
| 2 | Major Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | Moderate Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | Minor Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total |  |  | 1.3203 | 1.3203 | 1.0932 | 0.86614 | 0.63904 | 0.41195 | 0.18485 | 0.18485 | 0.18485 | 0.18485 | 0.18485 | 6.5753
End of Sheet

## Scenario E
Risk Monetisation Model - FOLCB Replacements - ELCA |  |  |  | Menu
#VALUE!
Total Consequence Calculation
[11 empty] | $m 2021 |  |  |  |  | $m 2021
| Failure Mode | Risk | Description | [7 empty] | Network Performance | Tangible community cost | OPEX | CAPEX | Environment | Concequence cost | DF | Total Cosequence
| 1 | Catastrophic Busfire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 2271.3198
|  |  | Catastrophic bushfire | [7 empty] | 0 | 378.4582 | 0 | 0 | 0 | 378.4582 | 6
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | F-Factor | [7 empty] | 0 | 0 | 0 | 0.57038 | 0 | 0.57038 | 1
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2 | Major Fire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3 | Moderate Fire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4 | Minor Fire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total annual risk cost | [14 empty] | 379.0286 |  | 2271.3198
Annual Probabilty of Failure per Scenario
| Base Year | 21
Probability of Failure
| Failure Mode | Risk |  | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
| 1 | FOLCBs Fire start in ELCAs on Severe Fire Danger days |  | 0.03197% | 0.03197% | 0.02647% | 0.02097% | 0.01547% | 0.009975% | 0.004476% | 0.004476% | 0.004476% | 0.004476% | 0.004476%
| 2 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
| 3 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
| 4 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
| 5 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
Annual Risk Cost per Scenario
Consequence Cost per Scenario x Probability of Failure
Annual Risk Cost ($m)
| Failure Mode | Risk |  | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total
| 1 | Catastrophic Busfire |  | 0.72619 | 0.72619 | 0.60128 | 0.47638 | 0.35147 | 0.22657 | 0.10167 | 0.10167 | 0.10167 | 0.10167 | 0.10167 | 3.6164
| 2 | Major Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | Moderate Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | Minor Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total |  |  | 0.72619 | 0.72619 | 0.60128 | 0.47638 | 0.35147 | 0.22657 | 0.10167 | 0.10167 | 0.10167 | 0.10167 | 0.10167 | 3.6164
End of Sheet

## Scenario F
Risk Monetisation Model - FOLCB Replacements - ELCA |  |  |  | Menu
#VALUE!
Total Consequence Calculation
[11 empty] | $m 2021 |  |  |  |  | $m 2021
| Failure Mode | Risk | Description | [7 empty] | Network Performance | Tangible community cost | OPEX | CAPEX | Environment | Concequence cost | DF | Total Cosequence
| 1 | Catastrophic Busfire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 2271.3198
|  |  | Catastrophic bushfire | [7 empty] | 0 | 378.4582 | 0 | 0 | 0 | 378.4582 | 6
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | F-Factor | [7 empty] | 0 | 0 | 0 | 0.57038 | 0 | 0.57038 | 1
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 2 | Major Fire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 3 | Moderate Fire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 4 | Minor Fire | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
| Total annual risk cost | [14 empty] | 379.0286 |  | 2271.3198
Annual Probabilty of Failure per Scenario
| Base Year | 21
Probability of Failure
| Failure Mode | Risk |  | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
| 1 | FOLCBs Fire start in ELCAs on Severe Fire Danger days |  | 0.01453% | 0.01453% | 0.01203% | 0.009533% | 0.007034% | 0.004534% | 0.002035% | 0.002035% | 0.002035% | 0.002035% | 0.002035%
| 2 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
| 3 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
| 4 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
| 5 | 0 | bar: Probability of Failure 21 to Probability of Failure 31
Annual Risk Cost per Scenario
Consequence Cost per Scenario x Probability of Failure
Annual Risk Cost ($m)
| Failure Mode | Risk |  | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total
| 1 | Catastrophic Busfire |  | 0.33008 | 0.33008 | 0.27331 | 0.21654 | 0.15976 | 0.10299 | 0.046212 | 0.046212 | 0.046212 | 0.046212 | 0.046212 | 1.6438
| 2 | Major Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | Moderate Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4 | Minor Fire |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total |  |  | 0.33008 | 0.33008 | 0.27331 | 0.21654 | 0.15976 | 0.10299 | 0.046212 | 0.046212 | 0.046212 | 0.046212 | 0.046212 | 1.6438
End of Sheet

## Annualised Cost
Risk Monetisation Model - FOLCB Replacements - ELCA | [5 empty] | Menu
#VALUE!
Opex Cost per Scenario ($2021)
| Scenario | Description | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
| Base | FOLCB replacement program | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| A | x 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| B | x 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| C | x 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| D | x 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| E | x 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| F | x 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capex Cost per Scenario ($2021)
| Scenario | Description | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
| Base | FOLCB replacement program
| A | x 1 | 0 | 496364.693 | 496364.693 | 496364.693 | 496364.693 | 496364.693 | 0 | 0 | 0 | 0 | 0
| B | x 1 | 0 | 496364.693 | 496364.693 | 496364.693 | 496364.693 | 496364.693 | 0 | 0 | 0 | 0 | 0
| C | x 1 | 0 | 496364.693 | 496364.693 | 496364.693 | 496364.693 | 496364.693 | 0 | 0 | 0 | 0 | 0
| D | x 1 | 0 | 496364.693 | 496364.693 | 496364.693 | 496364.693 | 496364.693 | 0 | 0 | 0 | 0 | 0
| E | x 1 | 0 | 496364.693 | 496364.693 | 496364.693 | 496364.693 | 496364.693 | 0 | 0 | 0 | 0 | 0
| F | x 1 | 0 | 496364.693 | 496364.693 | 496364.693 | 496364.693 | 496364.693 | 0 | 0 | 0 | 0 | 0
| Real wacc, reverse counter |  | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
| Base |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| A |  | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
| B |  | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
| C |  | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
| D |  | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
| E |  | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
| F |  | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
| Real wacc, reverse index | Discount rate | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
| Base | 2.75% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| A | 2.75% | 0 | 1.1146 | 1.0848 | 1.0558 | 1.0275 | 1 | 0 | 0 | 0 | 0 | 0
| B | 2.75% | 0 | 1.1146 | 1.0848 | 1.0558 | 1.0275 | 1 | 0 | 0 | 0 | 0 | 0
| C | 2.75% | 0 | 1.1146 | 1.0848 | 1.0558 | 1.0275 | 1 | 0 | 0 | 0 | 0 | 0
| D | 2.75% | 0 | 1.1146 | 1.0848 | 1.0558 | 1.0275 | 1 | 0 | 0 | 0 | 0 | 0
| E | 2.75% | 0 | 1.1146 | 1.0848 | 1.0558 | 1.0275 | 1 | 0 | 0 | 0 | 0 | 0
| F | 2.75% | 0 | 1.1146 | 1.0848 | 1.0558 | 1.0275 | 1 | 0 | 0 | 0 | 0 | 0
| Annualised cost | $2021
| Base | 0
| A | 96232.5111
| B | 96232.5111
| C | 96232.5111
| D | 96232.5111
| E | 96232.5111
| F | 96232.5111
End of Sheet

## Summary
Risk Monetisation Model - FOLCB Replacements - ELCA
#VALUE!
Annual Risk Cost per Scenario
|  | $m | [11 empty] | Sensitivities
| Annual Risk Cost | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Pof | Capex | Demand | VCR | Opex | Environment | Notes
| Base case | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 | 1.3203 |  | Central | Central | Central | Central | Central | Central | Do nothing flat risk cost
| Scenario A | 1.3203 | 1.3203 | 1.0932 | 0.86614 | 0.63904 | 0.41195 | 0.18485 | 0.18485 | 0.18485 | 0.18485 | 0.18485 |  | Central | Central | Central | Central | Central | Central | Reducing risk cost as units are replaced
| Scenario B | 1.5184 | 1.5184 | 1.2572 | 0.99606 | 0.7349 | 0.47374 | 0.21257 | 0.21257 | 0.21257 | 0.21257 | 0.21257 |  | Upper | Central | Central | Central | Central | Central | Upper sensitivity
| Scenario C | 0.72619 | 0.72619 | 0.60128 | 0.47638 | 0.35147 | 0.22657 | 0.10167 | 0.10167 | 0.10167 | 0.10167 | 0.10167 |  | Lower | Central | Central | Central | Central | Central | PoF lower. CoF central
| Scenario D | 1.3203 | 1.3203 | 1.0932 | 0.86614 | 0.63904 | 0.41195 | 0.18485 | 0.18485 | 0.18485 | 0.18485 | 0.18485 |  | Central | Central | Central | Central | Central | Central | PoF central. CoF lower
| Scenario E | 0.72619 | 0.72619 | 0.60128 | 0.47638 | 0.35147 | 0.22657 | 0.10167 | 0.10167 | 0.10167 | 0.10167 | 0.10167 |  | Lower | Central | Central | Central | Central | Central | PoF lower. CoF lower
| Scenario F | 0.33008 | 0.33008 | 0.27331 | 0.21654 | 0.15976 | 0.10299 | 0.046212 | 0.046212 | 0.046212 | 0.046212 | 0.046212 |  | Lower 2 | Central | Central | Central | Central | Central | PoF lower 2. CoF lower 2
Project Cost per Scenario
$m
| Annualised Project cost | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Capex | Opex | Discount rate
| Base case | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Central | Central | Central
| Scenario A | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 |  | Central | Central | Central
| Scenario B | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 |  | Central | Central | Central
| Scenario C | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 |  | Central | Central | Central
| Scenario D | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 |  | Central | Central | Central
| Scenario E | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 |  | Central | Central | Central
| Scenario F | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 | 0.096233 |  | Central | Central | Central
Reduction in risk per Scenario
$m
| Reduction in risk | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
| Base case | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Scenario A | 0 | 0 | 0.2271 | 0.4542 | 0.6813 | 0.90839 | 1.1355 | 1.1355 | 1.1355 | 1.1355 | 1.1355
| Scenario B | 0 | 0 | 0.26116 | 0.52233 | 0.78349 | 1.0447 | 1.3058 | 1.3058 | 1.3058 | 1.3058 | 1.3058
| Scenario C | 0 | 0 | 0.1249 | 0.24981 | 0.37471 | 0.49962 | 0.62452 | 0.62452 | 0.62452 | 0.62452 | 0.62452
| Scenario D | 0 | 0 | 0.2271 | 0.4542 | 0.6813 | 0.90839 | 1.1355 | 1.1355 | 1.1355 | 1.1355 | 1.1355
| Scenario E | 0 | 0 | 0.1249 | 0.24981 | 0.37471 | 0.49962 | 0.62452 | 0.62452 | 0.62452 | 0.62452 | 0.62452
| Scenario F | 0 | 0 | 0.056775 | 0.11355 | 0.17032 | 0.2271 | 0.28387 | 0.28387 | 0.28387 | 0.28387 | 0.28387
Total risk vs annualised cost | [12 empty] | Reduction in risk vs annualised cost
End of Sheet