## Definitions
Option 1 - Introduction of Digital Network
This adds the Digital Network infrastructure to the baseline option including foundation, comms, Integration, Security and Application Platforms.
It does not include any additional devices but relies on the existing AMI devices that provide current and voltage measurement.
It will provide benefits in LV Asset Failure Prediction, LV Phase Identification, LV Mapping, DSS Asset Monitoring and Electricity Theft Detection, Accurate & Dynamic Cost Reflective Pricing, EV Charging Optimisation and Customer Level Monitoring and Optimisation
Option 2 - Increased coverage of AMI and other network devices
The foundation for Digital Network is implemented in Option 1. This option increases the current coverage of network devices to improve efficiency, accuracy, effectiveness and coverage of the Digital Network as well as adding additional functionalities.
Devices include contestable metering sites and CT measuring devices and communications at critical/high risk distribution transformers.

## Summary
| 20 Year Summary NPV |  | 20 Year Opex Summary NPV |  | 5 Year Cost Summary (FY2021-2025) - NPV
Summary Benefits (M$AUD) | Option 1 | Option 2 | Option 1 | Option 2 |  | Option 1 | Option 2
Benefit Category 1 - Reduction of non-technical losses | 3.6057 | 9.4845
Benefit Category 2 - Cost Reflective Pricing | 10.6235 | 14.3418
Benefit Category 3 - Electric Vehicle (EV) Charging Optimisation | 46.0618 | 79.8404
Benefit Category 4 - Customer Load Monitoring and Optimisation | 79.1232 | 81.5465
Total benefits | 139.4143 | 185.2132
Summary Costs ($MAUD)
Capex for IT Systems | 20.0883 | 20.0883 |  |  |  | 19.8177 | 19.8177
Opex for IT Systems |  |  | 15.4729 | 15.4729 |  | 2.824 | 2.824
Replacement Capex for IT Systems | 15.1771 | 15.1771
Capex for Network Devices |  | 8.6789 |  |  |  |  | 7.3003
Opex for Network Devices |  |  |  | 10.768 |  |  | 1.271
Benefit Category 2 - Program Costs (opex) |  |  | 7.4187 | 9.5825 |  | 1.4807 | 1.8578
Benefit Category 3 - Program Costs (opex) |  |  | 9.7769 | 18.4118 |  | 0.49084 | 1.6498
Benefit Category 4 - Program Costs (opex) |  |  | 12.4365 | 16.3606 |  | 0.82342 | 2.1339
Total costs | 35.2654 | 43.9443 | 45.1051 | 70.5957 | Total Opex | 5.619 | 9.7365
[5 empty] | Total Capex | 19.8177 | 27.118
Total CAPEX NPV | 35.2654 | 43.9443 |  |  |  | 25.4366 | 36.8545
Total OPEX NPV |  |  | 45.1051 | 70.5957
| Excluding Opex |  | Including Opex
Net Benefit (NPV) - $MAUD | 104.1489 | 141.2688 | 59.0438 | 70.6732
NPV - C/B Ratio | 3.9533 | 4.2147 | 1.7346 | 1.617
C/B Ratio |  |  | 1.8826 | 1.8693
IRR | 28.73% | 30.64% | 18.77% | 19.76%

## Benefit Input Pars
|  | Option 1 | Option 2
List of Input Parameters | NPV | 59.0438 | 70.6732 | $Million
All years in this model represent financial years
Key Parameters | Central |  | Notes
Real Discount Rate | 2.75% | Percent | Provided by regulation in Options Analysis - Digital Network v2.0
Project Assessment Period | 20 | Years
Electricity Distributed in VPN | 16637 | GWh | AER State of the Energy Market - 2018
Peak Network Demand | 3573 | MW | Based on data supplied by VPN (Network Device Rollout - Business CaseV017(Powercor)
Total Number of VPN Residential Customers | 1177500 | Customers | Mark Pilkington e-mail 6th June
Million | 1000000 | Number | Definition of million included to avoid mistakes in calculations
Augmentation Capex 21-25 - CitiPower | 747.1183 | $/kVA | CitiPower Augmentation for 2021-2025
Augmentation Capex 21-25- Powercor | 666.9933 | $/kVA | Powercor Augmentation for 2021-2025
Augmentation Capex 21-25 - VPN | 694.7353 | $/kVA | VPN Combined number, based on size
Augmentation Capex 21-25 - United Energy | 517.6825 | $/kVA | UE Augmentation for 2021-2025
Parameters for Option 2 | Option 2
Start Rollout Option 2 Devices | 2022 | Year
Number of years Rollout Option 2 Devices | 5 | Year
Unmetered Service (UMS) Rollout - Excluding all public & watchman lights | 10% | Percent
1 Phase Customers Rollout | 10% | Percent
3 Phase Customers Rollout | 50% | Percent
LVCT Customer Rollout | 30% | Percent
HV Customer Rollout | 100% | Percent
LV Tx-S/S Rollout >300 kVA with 2 or more contestable customers | 24.48% | Percent
Benefit Specific Inputs
Benefit Category 1 - Reduction in Non Technical Losses
Value per KWh saved | 0.2 | $/KWh | Appendix B UE Network Device Rollout Paper - average electricity price was 0.28 c/KWh and this uses as conservative 0.2c/kWh after discounts are applied. Services charges are excluded
Percentage of Energy Theft in Victoria that could be reduced with full metering and network devices at Substations | 0.03% | Percent | Appendix B UE Network Device Rollout Paper 0 .03% could be saved with Option 3 (metering on everything). This may be total theft
Percentage theft reduction with Digital Network Option 1 | 25% | Percent | Smaller that Option 2 - Assume to stil have some benefit so included at 50% of the value for option 2
Year when Theft Detection is available in Option 1 | 2 | Year
Percentage Theft Reduction with Digital Network Option 2 | 50% | Percent | Set to align with the value of saving in UE Network Device Rollout Paper
Year when Option 2 Theft Detection Available | 3 | Year
Averge demand per NC-UMS category: "Other" | 1200 | kWh/a | Mark Pilkington email 28/6/2019
Demand growth of UMS "Other" per annum | 2.5% | Percent | Likely to see significant growth as includes NBN sites and exchanges.
Percentage of electricity of UMS customer that is under recorded | 10% | Percent
Percentage unrecorded UMS reduction with Digital Network Option 2 | 50% | Percent
Year when Option 2 UMS under recording Available | 2 | Year
Benefit Category 2 - Cost Reflective Pricing
Year when Digital Network and 'Summer Saver' type program is available for VPN with Option 1 | 3 | Year | Digital Network System reflecting what is done in UE with saving of around $8m per year
VPN cost reflective pricing program, total rolling savings to augmentation | 12 | MAUD | Based on UE being around $12m. Assume the equivalent saved each year so treated as one permanent deferment. Did not increase this number as VPN does not spend as much on DSS (ref: comments from UE on model)
Years to reach savings | 1 | Year | Time between start of program and savings materialise
Increased value with additional meter deployment - program extension in Option 2 | 35% | Percent | Estimate
Number of periods to spread augmentation benefits | 3 | Years
Benefit Category 3 - Electric Vehicle (EV) Charging Optimisation
Residential Charging Infrastructure
Average increase in residential peak for customers with EV | 0.69 | kW | Average over 20 years, based on mixture of different charging patterns (convernient, night-time charging, daytime charging), VIC EV growth as per AEMO ISP 2019 and adjusted to relative size of VPN in VIC. This value is not used a time-series is included in the model.
Percentage of EVs charging through Digital Network Control on TOU tariffs | 30% | Percent | Estimate
EV AEMO 2019 Scenario - Number of EVs | 1 | C=1, F=2, S=3 | Central, Fast Change or Slow Change as per AEMO EV forecast ISP2019
Year when Option 1 Digital Network Charging for Residential EVs available | 2 | Year
Year when Option 2 Digital Network Charging for Public Charging Infrastructure available | 2 | Year
Year when Option 2 Digital Network Charging for Commercial Infrastructure available | 3 | Year
Number of commercial charging poles as percentage of EV | 20% | Percent | Estimate number of commercial charging poles assumed 20% of all EV
Percentage of Commercial Charging infrastructure charging through Digital Network Control | 20% | Percent | Conservative number, these are likely commercial buildings
Number of public charging poles as % of EV | 20% | Percent | Number of public charging poles assumed only 20% of all EV
Percentage of Public charging Infrastructure Charging at Peak with Digital Networks | 90% | Percent | Large share of public charging controlled by DNSP assumed
Benefit Category 4 - Customer Load Monitoring and Optimisation
Annual Number of Customers per year that have load control devices fitted each year | 2500 | Cust Numbers | Jacobs estimate
Growth of fitting load control devices | 10% |  | Based on input from VPN
Average kVA saved per customer | 1 | kVA | Aligns with air conditioner customers from Perth Solar City and from the US report suggested 0.8-1.5kW.
Year when Option 1 Customer Load Monitoring and Optimisation Available | 2 | Year | Estimate - start early as high benefit
Initial number of solar customers that are export constrained where VPN use Digital Network to control charging | 2500 | Cust Numbers | Initial assumption, conservative number
Increase in number of solar customers that are export constrained where VPN use Digital Network to control charging | 1000 | Cust Numbers | Conservative - Less than 0.1% of customers per annum
Average annual kWh of Solar PV utilised for charging hot water storage (as opposed to not being utilised/tripped/curtailed) | 1215 | kWh | Assume at least 10 kWh per day for a hot water storage system (around 3650 kWh per year, this could be higher as typical usage is around 5,000 per annum) - Still needs grid charging - assumed 1/3rd can be charged with solar PV
Avoided wholesale cost of KWh | 11 | c/kwh | Approx wholesale price calculations from Jacobs based on AER, State of the Energy Market Report
Year when hot water storage and solar PV load control program begins | 2 | Year | Estimate - start early as high benefit
Average kVA saved per large customer | 5 | kVA | Average estimate of large customer demand impact - conservative, could be much higher
Large customers included in program - extended coverage in Option 2 | 25% | Percent | Estimate

## Platform Cost Inputs
General Assumptions on IT Costs
| Replacement Costs % of original Cost | 50%
| Replacement asset life | 7
VPN IT Platform Cost for Option 1 and 2
| VPN Initiative ID | Initiative Group | Initiative Name | Duration (months) | Capex start year | Implementation Years | Operational Year | Capex | Base Annual Opex
| UD01-VPN | Real-Time Unified Data Space | Real-Time Data Platform | 18 | 2021 | 1.5 | 2022.5 | 2112063 | 200000
| UD03-VPN |  | IoT Platform for Network Sensors | 54 | 2021 | 4.5 | 2025.5 | 5079840 | 124000
| UD04-VPN |  | IoT Platform Extension for Customer Sensors | 12 | 2022 | 1 | 2023 | 1191840 | 166000
| GA01-VPN | Real-Time Grid Analytics | Real-Time Grid Analytics Platform | 12 | 2021 | 1 | 2022 | 2069720 | 200000
| GA02-VPN |  | Real-Time LV Power Flow Analysis | 12 | 2022 | 1 | 2023 | 1081860 | 50000
| GA03-VPN |  | LV Model Extension | 18 | 2021 | 1.5 | 2022.5 | 3167424 | 0
| MC02-VPN | Real-Time Monitoring & Control | Real-Time Grid Monitoring and Control | 12 | 2022 | 1 | 2023 | 2169700 | 210000
| MC03-VPN |  | LV Management Capability | 12 | 2023 | 1 | 2024 | 965880 | 74000
| MC05-VPN |  | Dynamic Forecasting Capability | 12 | 2023 | 1 | 2024 | 1070262 | 0
| MC06-VPN |  | DER - Monitoring Capability | 12 | 2023 | 1 | 2024 | 1059864 | 74000
| NA01-VPN | Network Flexibility and Automation | DER - Dispatching Automation | 12 | 2025 | 1 | 2026 | 1069860 | 74000
| Total | [6 empty] | 21038313 | 1172000

## Time Series Data Inputs
Financial Year |  |  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Project Year |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
EV Take Up Numbers
Residential Evs for VPN | Number |  | 1399.4645 | 2334.9631 | 4347.7388 | 8093.7158 | 13823.7941 | 22252.8398 | 34039.5648 | 49601.3393 | 69486.5591 | 93990.7287 | 122406.9471 | 155204.3577 | 192985.5187 | 236286.4799 | 285335.0427 | 357933.9567 | 426947.7883 | 492259.0527 | 554242.9049 | 612822.4821
Commercial Charging Infrastructure (guess) | Number | 20% | 279.8929 | 466.9926 | 869.5478 | 1618.7432 | 2764.7588 | 4450.568 | 6807.913 | 9920.2679 | 13897.3118 | 18798.1457 | 24481.3894 | 31040.8715 | 38597.1037 | 47257.296 | 57067.0085 | 71586.7913 | 85389.5577 | 98451.8105 | 110848.581 | 122564.4964
Public Charging Infrasturcture | Number | 20% | 279.8929 | 466.9926 | 869.5478 | 1618.7432 | 2764.7588 | 4450.568 | 6807.913 | 9920.2679 | 13897.3118 | 18798.1457 | 24481.3894 | 31040.8715 | 38597.1037 | 47257.296 | 57067.0085 | 71586.7913 | 85389.5577 | 98451.8105 | 110848.581 | 122564.4964
|  |  |  | 124.4% | 132.8% | 135.9% | 134.8% | 140.6% | 148.1% | 148.3% | 147.6% | 146.9% | 143.6% | 141.5% | 141.5% | 141.9% | 141.8% | 134.7% | 124.6% | 118.8% | 115.1% | 112.6%
Residential EV Vic (AEMO ISP 2019) | Number - Central |  | 3514 | 5863 | 10917 | 20323 | 34711 | 55876 | 85472 | 124547 | 174478 | 236007 | 307359 | 389712 | 484579 | 593306 | 716465 | 898758 | 1072049 | 1236043 | 1391682 | 1538773
Residential EV Vic (AEMO ISP 2019) | Number - Fast Change |  | 8616 | 16101 | 28308 | 46614 | 75054 | 115251 | 167618 | 232667 | 310181 | 398451 | 495898 | 603394 | 721652 | 850467 | 994907 | 1140858 | 1295254 | 1448523 | 1596956 | 1747921
Residential EV Vic (AEMO ISP 2019) | Number - Slow Change |  | 2598 | 3231 | 4291 | 5831 | 7858 | 11045 | 16362 | 24264 | 35825 | 52639 | 75581 | 106914 | 151261 | 214588 | 304343 | 410091 | 510914 | 607108 | 698887 | 786711
Share for VPN (based on customer numbers) | % | 39.83% | 1399.4645 | 2334.9631 | 4347.7388 | 8093.7158 | 13823.7941 | 22252.8398 | 34039.5648 | 49601.3393 | 69486.5591 | 93990.7287 | 122406.9471 | 155204.3577 | 192985.5187 | 236286.4799 | 285335.0427 | 357933.9567 | 426947.7883 | 492259.0527 | 554242.9049 | 612822.4821
Share fo UE | % | 23.32% | 819.5269 | 1367.3552 | 2546.0373 | 4739.6827 | 8095.2185 | 13031.2704 | 19933.5805 | 29046.5608 | 40691.3522 | 55041.0021 | 71681.5491 | 90887.7237 | 113012.3841 | 138369.4415 | 167092.2962 | 209606.2445 | 250020.7673 | 288267.0655 | 324564.83 | 358869.05
|  |  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
EV max added demand (kW) per vehicle - charging pattern | kW - Neutral |  | 0.94732 | 0.9056 | 0.87431 | 0.8326 | 0.79088 | 0.75959 | 0.73873 | 0.70745 | 0.68659 | 0.6553 | 0.64487 | 0.63444 | 0.61359 | 0.60316 | 0.59273 | 0.5823 | 0.56144 | 0.55101 | 0.54058 | 0.53015
EV max added demand (kW) per vehicle - charging pattern | kW - Fast |  | 0.8812 | 0.8302 | 0.7792 | 0.7282 | 0.6772 | 0.6432 | 0.6092 | 0.57521 | 0.54121 | 0.50721 | 0.49021 | 0.47321 | 0.45621 | 0.43921 | 0.42221 | 0.41507 | 0.42033 | 0.42558 | 0.43084 | 0.43448
EV max added demand (kW) per vehicle - charging pattern | kW - Slow |  | 1.1532 | 1.1475 | 1.1419 | 1.1362 | 1.1305 | 1.1267 | 1.123 | 1.1192 | 1.1154 | 1.1116 | 1.1097 | 1.1079 | 1.106 | 1.1041 | 1.1022 | 1.1003 | 1.0984 | 1.0965 | 1.0946 | 1.0946
EV max added demand (kW) per vehicle - charging pattern | kW - Scenario |  | 0.94732 | 0.9056 | 0.87431 | 0.8326 | 0.79088 | 0.75959 | 0.73873 | 0.70745 | 0.68659 | 0.6553 | 0.64487 | 0.63444 | 0.61359 | 0.60316 | 0.59273 | 0.5823 | 0.56144 | 0.55101 | 0.54058 | 0.53015
Residential Charging |  |  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
kVa demand increase savings - Benefit Category 3 | kVa - cumulative |  | 0 | 634.3625 | 1140.3844 | 2021.6384 | 3279.8868 | 5070.9256 | 7543.8562 | 10527.0931 | 14312.6049 | 18477.6763 | 23681.0545 | 29540.5048 | 35523.9069 | 42755.2774 | 50737.7213 | 62527.241 | 71911.6144 | 81371.9686 | 89884.0194 | 97466.7738
kVa demand increase savings - Benefit Category 3 | kVa - par annum |  | 0 | 634.3625 | 506.022 | 881.254 | 1258.2484 | 1791.0388 | 2472.9306 | 2983.2369 | 3785.5118 | 4165.0714 | 5203.3782 | 5859.4503 | 5983.4021 | 7231.3704 | 7982.4439 | 11789.5198 | 9384.3734 | 9460.3541 | 8512.0508 | 7582.7544
Public Charging
kVa demand increase savings - Benefit Category 3 | kVa - cumulative |  | 0 | 380.6175 | 684.2307 | 1212.983 | 1967.9321 | 3042.5554 | 4526.3137 | 6316.2559 | 8587.5629 | 11086.6058 | 14208.6327 | 17724.3029 | 21314.3442 | 25653.1664 | 30442.6328 | 37516.3446 | 43146.9687 | 48823.1811 | 53930.4116 | 58480.0643
kVa demand increase savings - Benefit Category 3 | kVa - par annum |  | 0 | 380.6175 | 303.6132 | 528.7524 | 754.9491 | 1074.6233 | 1483.7584 | 1789.9421 | 2271.3071 | 2499.0428 | 3122.0269 | 3515.6702 | 3590.0413 | 4338.8223 | 4789.4664 | 7073.7119 | 5630.624 | 5676.2125 | 5107.2305 | 4549.6526
Commercial Charging
kVa demand increase savings - Benefit Category 3 | kVa - cumulative |  | 0 | 0 | 152.0513 | 269.5518 | 437.3182 | 676.1234 | 1005.8475 | 1403.6124 | 1908.3473 | 2463.6902 | 3157.4739 | 3938.734 | 4736.5209 | 5700.7036 | 6765.0295 | 8336.9655 | 9588.2153 | 10849.5958 | 11984.5359 | 12995.5698
kVa demand increase savings - Benefit Category 3 | kVa - par annum |  | 0 | 0 | 152.0513 | 117.5005 | 167.7665 | 238.8052 | 329.7241 | 397.7649 | 504.7349 | 555.3429 | 693.7838 | 781.26 | 797.787 | 964.1827 | 1064.3259 | 1571.936 | 1251.2498 | 1261.3806 | 1134.9401 | 1011.0339
Commercial Load Control (Benefit Category 4)
kVa demand increase savings - Benefit Category 4 | MVA - cumulative |  | 0 | 2.5 | 5.25 | 8.275 | 11.6025 | 15.2628 | 19.289 | 23.7179 | 28.5897 | 33.9487 | 39.8436 | 46.3279 | 53.4607 | 61.3068 | 69.9375 | 79.4312 | 89.8743 | 101.3618 | 113.9979 | 127.8977
kVa demand increase savings - Benefit Category 4 | MVA - par annum (incremental) |  | 0 | 2.5 | 2.75 | 3.025 | 3.3275 | 3.6603 | 4.0263 | 4.4289 | 4.8718 | 5.359 | 5.8949 | 6.4844 | 7.1328 | 7.8461 | 8.6307 | 9.4937 | 10.4431 | 11.4874 | 12.6362 | 13.8998
Commercial Load Control (Benefit Category 4)
kVa demand increase savings - Benefit Category 4 | MVA - cumulative |  | 0 | 3.8133 | 7.8766 | 12.2149 | 16.8557 | 21.8292 | 25.8555 | 30.2844 | 35.1562 | 40.5152 | 46.4101 | 52.8944 | 60.0272 | 67.8733 | 76.504 | 85.9977 | 96.4408 | 107.9283 | 120.5644 | 134.4642
kVa demand increase savings - Benefit Category 4 | MVA - par annum (incremental) |  | 0 | 3.8133 | 4.0633 | 4.3383 | 4.6408 | 4.9735 | 4.0263 | 4.4289 | 4.8718 | 5.359 | 5.8949 | 6.4844 | 7.1328 | 7.8461 | 8.6307 | 9.4937 | 10.4431 | 11.4874 | 12.6362 | 13.8998

## Device Cost Input
Financial Year
Network Device Roll-out costs - Option 2 |  |  |  | Start date: | 2022 | Years RO: | 5
CitiPower/ Powercor - VPN | Rollout % | Total # | Rollout # | Hardware $ | Installation $ | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Unmetered Supply (UMS) - New # | 10% | 5780 | 578 |  |  | 0 | 115.6 | 115.6 | 115.6 | 115.6 | 115.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unmetered Supply (UMS) - New $ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unmetered Supply (UMS) - Retrofit # | 10% | 8097 | 809.7 |  |  | 0 | 161.94 | 161.94 | 161.94 | 161.94 | 161.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unmetered Supply (UMS) - Retrofit $ |  |  |  | 200 | 206 | 0 | 0.065748 | 0.065748 | 0.065748 | 0.065748 | 0.065748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 Phase Customers # | 10% | 1034 | 103.4 |  |  | 0 | 20.68 | 20.68 | 20.68 | 20.68 | 20.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 Phase Customers $ |  |  |  | 192 | 128 | 0 | 0.0066176 | 0.0066176 | 0.0066176 | 0.0066176 | 0.0066176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 Phase Customers # | 50% | 4056 | 2028 |  |  | 0 | 405.6 | 405.6 | 405.6 | 405.6 | 405.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 Phase Customers $ |  |  |  | 365.7 | 200 | 0 | 0.22945 | 0.22945 | 0.22945 | 0.22945 | 0.22945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LVCT Customers # | 30% | 9466 | 2839.8 |  |  | 0 | 567.96 | 567.96 | 567.96 | 567.96 | 567.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LVCT Customers $ |  |  |  | 668.5857 | 300 | 0 | 0.55012 | 0.55012 | 0.55012 | 0.55012 | 0.55012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HV Customers # | 100% | 282 | 282 |  |  | 0 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HV Customers $ |  |  |  | 700 | 600 | 0 | 0.07332 | 0.07332 | 0.07332 | 0.07332 | 0.07332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LV Tx - S/S >300 kVA (with 2 or more contestable customers) $ | 24.48% | 8682 | 2125 |  |  | 0 | 425 | 425 | 425 | 425 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LV Tx - S/S >300 kVA (with 2 or more contestable customers) # |  |  |  | 879.9857 | 1430.64 | 0 | 0.98202 | 0.98202 | 0.98202 | 0.98202 | 0.98202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total $ for additional device rollouts | [5 empty] | 0 | 1.9073 | 1.9073 | 1.9073 | 1.9073 | 1.9073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Additional customers that could be equipped with load control |  | Applicable for |  | 25% |  | 0 | 262.66 | 262.66 | 262.66 | 262.66 | 262.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted increase of devices |  | 37397 |  | 6640.9 | 17.76% | 0 | 1328.18 | 1328.18 | 1328.18 | 1328.18 | 1328.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other | 0 |  |  | 100% | 17.76% | 0 | 1753.18 | 1753.18 | 1753.18 | 1753.18 | 1753.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Roll-out % of all devices |  | 0% | 20% | 40% | 60% | 80% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Meter operational cost
Annual Devices Opex for UMS | 73 | pa
Annual Devices Opex for 3 Phase DC | 91 | pa
Annual Devices Opex for other devices | 113 | pa
Program Costs for benefit categories 2, 3 and 4
Cost per FTE - General | 125000
FTEs for Benefit Category 2 | 2
FTEs for Benefit Category 3 - EV Control | 2
Additional Cost per customer for Benefit Category 3- EV control | 10
FTEs for Benefit Category 4 - AC Control | 2
Additional Cost per customer for Benefit Category 4- AC control | 10
FTSe for Benefit Category 4 - Hot Water load Control with Solar | 1
Additional Cost per customer for Benefit Category 4- Hot Water load control | 10
Recurring program costs (legal, marketing) for all Benefit Categories | 300000 | based on costs for Energy Partners project. (email Aaron Obrien 25/06/2019), including some costs for customer service

## Benefit Calcs
Benefit Calculations
Financial Year
Standing Data |  |  | Assumed discount rate |  | 2.75%
Financial Year |  |  |  |  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Project Year |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Discount Rate (Mid Year Discount) |  |  |  |  | 0.98653 | 0.96012 | 0.93443 | 0.90942 | 0.88508 | 0.86139 | 0.83834 | 0.8159 | 0.79406 | 0.77281 | 0.75213 | 0.732 | 0.71241 | 0.69334 | 0.67478 | 0.65672 | 0.63915 | 0.62204 | 0.60539 | 0.58919
Benefits for Option 1 - Introduction of Digital Network (and Baseline for relevant Initiatives)
$MAUD
Benefit Category 1 - Reduction in Non Technical Losses
Electricity theft in VPN that could be avoided with Full metering and Digital Network | GWh |  |  |  | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911
Value of Electricity Theft that could be avoided with Full metering and Digital Network | $MAUD |  |  |  | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822
Value of theft reduction | $MAUD | NPV | 3.6057 | 4.7415 | 0 | 0.24955 | 0.24955 | 0.24955 | 0.24955 | 0.24955 | 0.24955 | 0.24955 | 0.24955 | 0.24955 | 0.24955 | 0.24955 | 0.24955 | 0.24955 | 0.24955 | 0.24955 | 0.24955 | 0.24955 | 0.24955 | 0.24955
Benefit Category 2 - Cost Reflective Pricing
Annual Total Deferred Savings from Summer Saver Program | $MAUD |  |  |  | 0 | 0 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Avoided augmentation expenditure | $MAUD | NPV | 10.6235 | 12 | 0 | 0 | 0 | 4 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefit Category 3 - Electric Vehicle (EV) Charging Optimisation
Number of customers with controlled EV incremental | # |  |  |  | 0 | 700.4889 | 578.7657 | 1058.4414 | 1590.9482 | 2357.8949 | 3347.5246 | 4216.9062 | 5513.5076 | 6355.9631 | 8068.8507 | 9235.579 | 9751.5454 | 11989.2222 | 13467.3233 | 20246.5488 | 16714.8415 | 17169.1003 | 15746.1041 | 14302.9738
Cumulative Number of Customers | # |  |  |  | 0 | 700.4889 | 1279.2546 | 2337.696 | 3928.6443 | 6286.5392 | 9634.0638 | 13850.9699 | 19364.4776 | 25720.4407 | 33789.2914 | 43024.8704 | 52776.4157 | 64765.6379 | 78232.9612 | 98479.51 | 115194.3515 | 132363.4518 | 148109.5559 | 162412.5297
Peak Demand Charging capacity required for Evs BAU | KVA |  |  |  | 1325.735 | 2114.5416 | 3801.2814 | 6738.7947 | 10932.9562 | 16903.0854 | 25146.1873 | 35090.3103 | 47708.6829 | 61592.2542 | 78936.8483 | 98468.3493 | 118413.0231 | 142517.5912 | 169125.7376 | 208424.1368 | 239705.3814 | 271239.8953 | 299613.3979 | 324889.2459
Peak Demand Charging capacity required for Evs Option 1 Digital Network | KVA |  |  |  | 1325.735 | 1480.1791 | 2660.897 | 4717.1563 | 7653.0693 | 11832.1598 | 17602.3311 | 24563.2172 | 33396.078 | 43114.578 | 55255.7938 | 68927.8445 | 82889.1162 | 99762.3138 | 118388.0164 | 145896.8958 | 167793.767 | 189867.9267 | 209729.3785 | 227422.4722
Annual decrease in MD through EV control - kVA Residential | kVA |  |  |  | 0 | 634.3625 | 506.022 | 881.254 | 1258.2484 | 1791.0388 | 2472.9306 | 2983.2369 | 3785.5118 | 4165.0714 | 5203.3782 | 5859.4503 | 5983.4021 | 7231.3704 | 7982.4439 | 11789.5198 | 9384.3734 | 9460.3541 | 8512.0508 | 7582.7544
$/MVA calculations residential - total reduced augmentation capex | $MAUD | NPV | 46.0618 | 66.9213 | 0 | 0 | 0 | 0.61224 | 0.87415 | 1.2443 | 1.718 | 2.0726 | 2.6299 | 2.8936 | 3.615 | 4.0708 | 4.1569 | 5.0239 | 5.5457 | 8.1906 | 6.5197 | 6.5724 | 5.9136 | 5.268
Commercial & Public charging will require option 2
Benefit Category 4 - Customer Load Monitoring and Optimisation
Number of Customers with load control added | Cust Numbers |  |  |  | 0 | 2500 | 2750 | 3025 | 3327.5 | 3660.25 | 4026.275 | 4428.9025 | 4871.7928 | 5358.972 | 5894.8692 | 6484.3562 | 7132.7918 | 7846.0709 | 8630.678 | 9493.7458 | 10443.1204 | 11487.4325 | 12636.1757 | 13899.7933
Cumulative Number of Customers at start of year | Cust Numbers |  |  |  | 0 | 2500 | 5250 | 8275 | 11602.5 | 15262.75 | 19289.025 | 23717.9275 | 28589.7203 | 33948.6923 | 39843.5615 | 46327.9177 | 53460.7094 | 61306.7804 | 69937.4584 | 79431.2042 | 89874.3247 | 101361.7571 | 113997.9328 | 127897.7261
MVA Saved | MVA |  |  |  | 0 | 2.5 | 5.25 | 8.275 | 11.6025 | 15.2628 | 19.289 | 23.7179 | 28.5897 | 33.9487 | 39.8436 | 46.3279 | 53.4607 | 61.3068 | 69.9375 | 79.4312 | 89.8743 | 101.3618 | 113.9979 | 127.8977
MVA Incremental Reduction | MVA |  |  |  | 0 | 2.5 | 2.75 | 3.025 | 3.3275 | 3.6603 | 4.0263 | 4.4289 | 4.8718 | 5.359 | 5.8949 | 6.4844 | 7.1328 | 7.8461 | 8.6307 | 9.4937 | 10.4431 | 11.4874 | 12.6362 | 13.8998
Value of MVA Reduction for Distribution Network | $MAUD | NPV | 59.2386 | 85.2077 | 0 | 0 | 0 | 2.1016 | 2.3117 | 2.5429 | 2.7972 | 3.0769 | 3.3846 | 3.7231 | 4.0954 | 4.5049 | 4.9554 | 5.4509 | 5.996 | 6.5956 | 7.2552 | 7.9807 | 8.7788 | 9.6567
Additional Number of Solar and Hot Water Customers that are export Constrained | Cust Numbers |  |  |  | 0 | 2500 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
Cumulative Number at Start of the Year | Cust Numbers |  |  |  | 0 | 2500 | 3500 | 4500 | 5500 | 6500 | 7500 | 8500 | 9500 | 10500 | 11500 | 12500 | 13500 | 14500 | 15500 | 16500 | 17500 | 18500 | 19500 | 20500
kWh Supplied by otherwise constrained power | kWh |  |  |  | 0 | 3037500 | 4252500 | 5467500 | 6682500 | 7897500 | 9112500 | 10327500 | 11542500 | 12757500 | 13972500 | 15187500 | 16402500 | 17617500 | 18832500 | 20047500 | 21262500 | 22477500 | 23692500 | 24907500
Value of KWh | $MAUD | NPV | 19.8847 | 28.4006 | 0 | 0 | 0 | 0.60142 | 0.73508 | 0.86872 | 1.0024 | 1.136 | 1.2697 | 1.4033 | 1.537 | 1.6706 | 1.8043 | 1.9379 | 2.0716 | 2.2052 | 2.3389 | 2.4725 | 2.6062 | 2.7398
Total benefits for Option 1 |  | NPV | 139.4143 | 197.2712 | 0 | 0.24955 | 0.24955 | 7.5648 | 8.1705 | 8.9055 | 5.7672 | 6.5351 | 7.5338 | 8.2696 | 9.4969 | 10.4959 | 11.1661 | 12.6623 | 13.8629 | 17.241 | 16.3633 | 17.2752 | 17.5481 | 17.9141
Net benefit - time series Option 1 |  |  |  |  | -6.7182 | -7.3825 | -5.3513 | 4.1358 | 4.1149 | 6.278 | 3.0559 | 0.36825 | 0.94618 | 3.1084 | 5.7341 | 6.3132 | 7.6217 | 8.9096 | 6.52 | 9.2839 | 9.6782 | 11.8416 | 11.5679 | 12.459
Breakeven Option 1 |  |  |  |  | -6.7182 | -14.1008 | -19.4521 | -15.3163 | -11.2013 | -4.9233 | -1.8674 | -1.4992 | -0.55299 | 2.5555 | 8.2896 | 14.6028 | 22.2245 | 31.1341 | 37.6541 | 46.938 | 56.6162 | 68.4577 | 80.0257 | 92.4846
Breakeven Option 1 - no Opex |  |  |  |  | -6.7182 | -13.8008 | -17.7761 | -11.3401 | -4.8039 | 4.1016 | 9.8687 | 13.0447 | 16.9124 | 23.0695 | 32.002 | 41.6807 | 52.8468 | 65.5091 | 76.0129 | 89.5878 | 103.8387 | 120.5495 | 137.2805 | 155.1946
Net benefit - time series Option 1, no opex |  |  |  |  | -6.7182 | -7.0825 | -3.9753 | 6.4359 | 6.5362 | 8.9055 | 5.7672 | 3.1759 | 3.8677 | 6.1571 | 8.9324 | 9.6787 | 11.1661 | 12.6623 | 10.5037 | 13.575 | 14.2509 | 16.7108 | 16.731 | 17.9141
Total Demand Deferred/reduced - Benefit Category 3 and 4 | MVA |  |  |  | 0 | 3.1344 | 3.256 | 3.9063 | 4.5857 | 5.4513 | 6.4992 | 7.4121 | 8.6573 | 9.524 | 11.0982 | 12.3438 | 13.1162 | 15.0774 | 16.6131 | 21.2833 | 19.8275 | 20.9478 | 21.1482 | 21.4825
Benefits for Option 2 - Increased Coverage of AMI Devices
$MAUD
Benefit Category 1 - Reduction in Non Technical Losses
Electricity theft in VPN that could be avoided with Full metering and Digital Network | GWh |  |  |  | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911 | 4.9911
Value of Electricity Theft that could be avoided with Full metering and Digital Network | $MAUD |  |  |  | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822
Value of theft reduction | $MAUD | NPV | 6.697 | 8.9341 | 0 | 0.24955 | 0.34938 | 0.39929 | 0.4492 | 0.49911 | 0.49911 | 0.49911 | 0.49911 | 0.49911 | 0.49911 | 0.49911 | 0.49911 | 0.49911 | 0.49911 | 0.49911 | 0.49911 | 0.49911 | 0.49911 | 0.49911
Unmetered supply rolled-out |  |  |  |  | 0% | 20% | 40% | 60% | 80% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Underecording per UMS in VPN per annum | kWh |  |  |  | 0 | 63.0375 | 64.6134 | 66.2288 | 67.8845 | 69.5816 | 71.3211 | 73.1042 | 74.9318 | 76.8051 | 78.7252 | 80.6933 | 82.7107 | 84.7784 | 86.8979 | 89.0703 | 91.2971 | 93.5795 | 95.919 | 98.317
Value of Under recording UMS | $MAUD | NPV | 2.7875 | 3.8307 | 0 | 0.034991 | 0.071731 | 0.11029 | 0.15073 | 0.19312 | 0.19794 | 0.20289 | 0.20797 | 0.21316 | 0.21849 | 0.22396 | 0.22956 | 0.23529 | 0.24118 | 0.24721 | 0.25339 | 0.25972 | 0.26621 | 0.27287
Benefit Category 2 - Cost Reflective Pricing
Annual Total Deferred Savings from Summer Saver Program | $MAUD |  |  |  | 0 | 0 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2
Avoided augmentation expenditure | $MAUD | NPV | 14.3418 | 16.2 | 0 | 0 | 0 | 5.4 | 5.4 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefit Category 3 - Electric Vehicle (EV) Charging Optimisation
Number of customers with controlled EV (incremental) | # |  |  |  | 0 | 1120.7823 | 1099.9347 | 1834.6318 | 2757.6436 | 4087.0178 | 5802.376 | 7309.304 | 9556.7466 | 11017.0027 | 13986.0079 | 16008.337 | 16902.6786 | 20781.3184 | 23343.3603 | 35094.0179 | 28972.392 | 29759.7739 | 27293.2471 | 24791.8213
Number of customers with controlled EV (cumulative) | # |  |  |  | 0 | 1120.7823 | 2220.717 | 4055.3487 | 6812.9923 | 10900.0102 | 16702.3862 | 24011.6902 | 33568.4367 | 44585.4394 | 58571.4473 | 74579.7843 | 91482.4629 | 112263.7813 | 135607.1416 | 170701.1595 | 199673.5515 | 229433.3254 | 256726.5725 | 281518.3938
Increased Peak Demand on LV Network with EV - Residential | KVA |  |  |  | 1325.735 | 2114.5416 | 3801.2814 | 6738.7947 | 10932.9562 | 16903.0854 | 25146.1873 | 35090.3103 | 47708.6829 | 61592.2542 | 78936.8483 | 98468.3493 | 118413.0231 | 142517.5912 | 169125.7376 | 208424.1368 | 239705.3814 | 271239.8953 | 299613.3979 | 324889.2459
Peak Demand Charging capacity required for Residential Evs Option 1 Digital Network | KVA |  |  |  | 1325.735 | 1480.1791 | 2660.897 | 4717.1563 | 7653.0693 | 11832.1598 | 17602.3311 | 24563.2172 | 33396.078 | 43114.578 | 55255.7938 | 68927.8445 | 82889.1162 | 99762.3138 | 118388.0164 | 145896.8958 | 167793.767 | 189867.9267 | 209729.3785 | 227422.4722
Incremental capacity | KVA |  |  |  | 0 | 634.3625 | 1140.3844 | 2021.6384 | 3279.8868 | 5070.9256 | 7543.8562 | 10527.0931 | 14312.6049 | 18477.6763 | 23681.0545 | 29540.5048 | 35523.9069 | 42755.2774 | 50737.7213 | 62527.241 | 71911.6144 | 81371.9686 | 89884.0194 | 97466.7738
Annual decrease in MD through EV control - kVA Residential | kVA |  |  |  | 0 | 634.3625 | 506.022 | 881.254 | 1258.2484 | 1791.0388 | 2472.9306 | 2983.2369 | 3785.5118 | 4165.0714 | 5203.3782 | 5859.4503 | 5983.4021 | 7231.3704 | 7982.4439 | 11789.5198 | 9384.3734 | 9460.3541 | 8512.0508 | 7582.7544
$/MVA calculations residential - total reduced augmentation capex | $MAUD | NPV | 46.0618 | 66.9213 | 0 | 0 | 0 | 0.61224 | 0.87415 | 1.2443 | 1.718 | 2.0726 | 2.6299 | 2.8936 | 3.615 | 4.0708 | 4.1569 | 5.0239 | 5.5457 | 8.1906 | 6.5197 | 6.5724 | 5.9136 | 5.268
Increased Peak Demand on LV Network with EV - Public Infrastructure | KVA |  |  |  | 265.147 | 422.9083 | 760.2563 | 1347.7589 | 2186.5912 | 3380.6171 | 5029.2375 | 7018.0621 | 9541.7366 | 12318.4508 | 15787.3697 | 19693.6699 | 23682.6046 | 28503.5182 | 33825.1475 | 41684.8274 | 47941.0763 | 54247.9791 | 59922.6796 | 64977.8492
Peak Demand Charging capacity required for Public Infrastructure with Option 2 Digital Network | KVA |  |  |  | 265.147 | 42.2908 | 76.0256 | 134.7759 | 218.6591 | 338.0617 | 502.9237 | 701.8062 | 954.1737 | 1231.8451 | 1578.737 | 1969.367 | 2368.2605 | 2850.3518 | 3382.5148 | 4168.4827 | 4794.1076 | 5424.7979 | 5992.268 | 6497.7849
Incremental capacity | KVA |  |  |  | 0 | 380.6175 | 684.2307 | 1212.983 | 1967.9321 | 3042.5554 | 4526.3137 | 6316.2559 | 8587.5629 | 11086.6058 | 14208.6327 | 17724.3029 | 21314.3442 | 25653.1664 | 30442.6328 | 37516.3446 | 43146.9687 | 48823.1811 | 53930.4116 | 58480.0643
Saving in Peak Demand Capacity from Digital Network Initiatives for Public Infrastructure | kVA |  |  |  | 0 | 380.6175 | 303.6132 | 528.7524 | 754.9491 | 1074.6233 | 1483.7584 | 1789.9421 | 2271.3071 | 2499.0428 | 3122.0269 | 3515.6702 | 3590.0413 | 4338.8223 | 4789.4664 | 7073.7119 | 5630.624 | 5676.2125 | 5107.2305 | 4549.6526
Value of Capacity Savings from Digital Network for Public Infrastructure | $MAUD | NPV | 27.6371 | 40.1528 | 0 | 0 | 0 | 0.36734 | 0.52449 | 0.74658 | 1.0308 | 1.2435 | 1.578 | 1.7362 | 2.169 | 2.4425 | 2.4941 | 3.0143 | 3.3274 | 4.9144 | 3.9118 | 3.9435 | 3.5482 | 3.1608
Peak Demand Charging Capacity required for Commercial EV sites | KVA |  |  |  | 265.147 | 422.9083 | 760.2563 | 1347.7589 | 2186.5912 | 3380.6171 | 5029.2375 | 7018.0621 | 9541.7366 | 12318.4508 | 15787.3697 | 19693.6699 | 23682.6046 | 28503.5182 | 33825.1475 | 41684.8274 | 47941.0763 | 54247.9791 | 59922.6796 | 64977.8492
Peak Demand Charging capacity require for Commercial Sites with Option 2 Digital Network | KVA |  |  |  | 265.147 | 422.9083 | 608.205 | 1078.2072 | 1749.273 | 2704.4937 | 4023.39 | 5614.4497 | 7633.3893 | 9854.7607 | 12629.8957 | 15754.9359 | 18946.0837 | 22802.8146 | 27060.118 | 33347.8619 | 38352.861 | 43398.3832 | 47938.1437 | 51982.2794
Alternative 1 | KVA |  |  |  | 0 | 0 | 152.0513 | 269.5518 | 437.3182 | 676.1234 | 1005.8475 | 1403.6124 | 1908.3473 | 2463.6902 | 3157.4739 | 3938.734 | 4736.5209 | 5700.7036 | 6765.0295 | 8336.9655 | 9588.2153 | 10849.5958 | 11984.5359 | 12995.5698
Alternative 1 | $MAUD | NPV | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Alternative 2 | kVA |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Alternative 2 | $MAUD | NPV | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Peak Demand Charging Capacity required for Commercial EV sites | kVA |  |  |  | 0 | 0 | 152.0513 | 117.5005 | 167.7665 | 238.8052 | 329.7241 | 397.7649 | 504.7349 | 555.3429 | 693.7838 | 781.26 | 797.787 | 964.1827 | 1064.3259 | 1571.936 | 1251.2498 | 1261.3806 | 1134.9401 | 1011.0339
Peak Demand Charging capacity savings for Commercial Sites with Option 2 Digital Network | $MAUD | NPV | 6.1416 | 8.9228 | 0 | 0 | 0 | 0.081632 | 0.11655 | 0.16591 | 0.22907 | 0.27634 | 0.35066 | 0.38582 | 0.482 | 0.54277 | 0.55425 | 0.66985 | 0.73942 | 1.0921 | 0.86929 | 0.87633 | 0.78848 | 0.7024
Benefit Category 4 - Customer Load Monitoring and Optimisation
Number of Customers with load control added | Cust Numbers |  |  |  | 0 | 2500 | 2750 | 3025 | 3327.5 | 3660.25 | 4026.275 | 4428.9025 | 4871.7928 | 5358.972 | 5894.8692 | 6484.3562 | 7132.7918 | 7846.0709 | 8630.678 | 9493.7458 | 10443.1204 | 11487.4325 | 12636.1757 | 13899.7933
Cumulative Number of Customers at start of year | Cust Numbers |  |  |  | 0 | 2500 | 5250 | 8275 | 11602.5 | 15262.75 | 19289.025 | 23717.9275 | 28589.7203 | 33948.6923 | 39843.5615 | 46327.9177 | 53460.7094 | 61306.7804 | 69937.4584 | 79431.2042 | 89874.3247 | 101361.7571 | 113997.9328 | 127897.7261
Number of additional Customers with load control added - Option 2 | Cust Numbers |  |  |  | 0 | 262.66 | 262.66 | 262.66 | 262.66 | 262.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative Number of additional Customers with load control added - Option 2 | Cust Numbers |  |  |  | 0 | 262.66 | 525.32 | 787.98 | 1050.64 | 1313.3 | 1313.3 | 1313.3 | 1313.3 | 1313.3 | 1313.3 | 1313.3 | 1313.3 | 1313.3 | 1313.3 | 1313.3 | 1313.3 | 1313.3 | 1313.3 | 1313.3
MVA Saved | MVA |  |  |  | 0 | 3.8133 | 7.8766 | 12.2149 | 16.8557 | 21.8292 | 25.8555 | 30.2844 | 35.1562 | 40.5152 | 46.4101 | 52.8944 | 60.0272 | 67.8733 | 76.504 | 85.9977 | 96.4408 | 107.9283 | 120.5644 | 134.4642
MVA Incremental Reduction | MVA |  |  |  | 0 | 3.8133 | 4.0633 | 4.3383 | 4.6408 | 4.9735 | 4.0263 | 4.4289 | 4.8718 | 5.359 | 5.8949 | 6.4844 | 7.1328 | 7.8461 | 8.6307 | 9.4937 | 10.4431 | 11.4874 | 12.6362 | 13.8998
Value of MVA Reduction for Distribution Network | $MAUD | NPV | 61.6618 | 87.9449 | 0 | 0 | 0 | 3.014 | 3.2241 | 3.4553 | 2.7972 | 3.0769 | 3.3846 | 3.7231 | 4.0954 | 4.5049 | 4.9554 | 5.4509 | 5.996 | 6.5956 | 7.2552 | 7.9807 | 8.7788 | 9.6567
Additional Number of Solar and Hot Water Customers that are export Constrained | Cust Numbers |  |  |  | 0 | 2500 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
Cumulative Number at Start of the Year | Cust Numbers |  |  |  | 0 | 2500 | 3500 | 4500 | 5500 | 6500 | 7500 | 8500 | 9500 | 10500 | 11500 | 12500 | 13500 | 14500 | 15500 | 16500 | 17500 | 18500 | 19500 | 20500
kWh Supplied by otherwise constrained power | kWh |  |  |  | 0 | 3037500 | 4252500 | 5467500 | 6682500 | 7897500 | 9112500 | 10327500 | 11542500 | 12757500 | 13972500 | 15187500 | 16402500 | 17617500 | 18832500 | 20047500 | 21262500 | 22477500 | 23692500 | 24907500
Value of KWh | $MAUD | NPV | 19.8847 | 28.4006 | 0 | 0 | 0 | 0.60142 | 0.73508 | 0.86872 | 1.0024 | 1.136 | 1.2697 | 1.4033 | 1.537 | 1.6706 | 1.8043 | 1.9379 | 2.0716 | 2.2052 | 2.3389 | 2.4725 | 2.6062 | 2.7398
Total Benefits for Option 2 |  | NPV | 185.2132 | 261.3073 | 0 | 0.28455 | 0.42111 | 10.5862 | 11.4743 | 12.573 | 7.4745 | 8.5074 | 9.9199 | 10.8543 | 12.6159 | 13.9546 | 14.6936 | 16.8313 | 18.4204 | 23.7442 | 21.6473 | 22.6043 | 22.4006 | 22.2997
Net Benefits for Option 2 |  |  |  |  | -6.7182 | -9.3436 | -6.9639 | 4.5704 | 4.64 | 6.9693 | 3.5809 | 1.1273 | 2.0786 | 4.3928 | 7.4936 | 8.3447 | 9.6505 | 11.4919 | 9.3922 | 13.9532 | 13.0057 | 15.0882 | 14.2225 | 14.5418
Cumulative Net Benefits for Option 2 |  |  |  |  | -6.7182 | -16.0618 | -23.0257 | -18.4553 | -13.8154 | -6.8461 | -3.2652 | -2.1379 | -0.059312 | 4.3335 | 11.8271 | 20.1718 | 29.8223 | 41.3142 | 50.7064 | 64.6595 | 77.6652 | 92.7535 | 106.976 | 121.5178
Cumulative Net Benefits for Option 2 - no Opex |  |  |  |  | -6.7182 | -15.673 | -21.3841 | -13.834 | -5.9012 | 4.7645 | 12.2391 | 17.3874 | 23.6412 | 32.3831 | 44.4345 | 57.572 | 72.2656 | 89.0969 | 104.1582 | 124.2364 | 143.7713 | 165.8112 | 187.3946 | 209.6943
Net benefit - time series Option 2, no opex |  |  |  |  | -6.7182 | -8.9548 | -5.711 | 7.5501 | 7.9328 | 10.6658 | 7.4745 | 5.1483 | 6.2539 | 8.7418 | 12.0515 | 13.1375 | 14.6936 | 16.8313 | 15.0613 | 20.0782 | 19.5349 | 22.0399 | 21.5834 | 22.2997
Total Demand Deferred/reduced - Benefit Category 3 and 4 | MVA |  |  |  | 0 | 4.8283 | 5.025 | 5.8658 | 6.8218 | 8.078 | 8.3127 | 9.5998 | 11.4333 | 12.5784 | 14.9141 | 16.6407 | 17.504 | 20.3804 | 22.4669 | 29.9289 | 26.7094 | 27.8854 | 27.3904 | 27.0432

## Cost Calcs
Cost Calculations
Standing Data
Financial Year |  |  |  | Financial Year | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Project Year |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Discount Rate (Mid Year Discount) |  |  |  |  | 0.98653 | 0.96012 | 0.93443 | 0.90942 | 0.88508 | 0.86139 | 0.83834 | 0.8159 | 0.79406 | 0.77281 | 0.75213 | 0.732 | 0.71241 | 0.69334 | 0.67478 | 0.65672 | 0.63915 | 0.62204 | 0.60539 | 0.58919
Costs for Option 1 - Introduction of Digital Network
Capex |  |  | NPV $MAUD | $MAUD
Real-Time Data Platform | $MAUD | NPV | 2.065 | 2.1121 | 1.408 | 0.70402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iot Platform for Network Sensors | $MAUD | NPV | 4.7785 | 5.0798 | 1.1289 | 1.1289 | 1.1289 | 1.1289 | 0.56443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IoT Platform Extension for Network Sensors | $MAUD | NPV | 1.1443 | 1.1918 | 0 | 1.1918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Real Time Grid Analytics Platform | $MAUD | NPV | 2.0418 | 2.0697 | 2.0697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Real Time LV Power Flow Analysis | $MAUD | NPV | 1.0387 | 1.0819 | 0 | 1.0819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LV Model Extension | $MAUD | NPV | 3.0969 | 3.1674 | 2.1116 | 1.0558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Real Time Grid Monitoring and Control | $MAUD | NPV | 2.0832 | 2.1697 | 0 | 2.1697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LV Management Capability | $MAUD | NPV | 0.90254 | 0.96588 | 0 | 0 | 0.96588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dynamic Forecasting Capacity | $MAUD | NPV | 1.0001 | 1.0703 | 0 | 0 | 1.0703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DER - Monitoring Capability | $MAUD | NPV | 0.99037 | 1.0599 | 0 | 0 | 1.0599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DER- Dispatching Automation | $MAUD | NPV | 0.94691 | 1.0699 | 0 | 0 | 0 | 0 | 1.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal - Capex | $MAUD | NPV | 20.0883 | 21.0383 | 6.7182 | 7.3321 | 4.2249 | 1.1289 | 1.6343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex
Real-Time Data Platform | $MAUD | NPV | 2.7937 | 3.7 | 0 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Iot Platform for Network Sensors | $MAUD | NPV | 1.3891 | 1.922 | 0 | 0 | 0 | 0 | 0.062 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124
IoT Platform Extension for Network Sensors | $MAUD | NPV | 2.2391 | 2.988 | 0 | 0 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166
Real Time Grid Analytics Platform | $MAUD | NPV | 2.8897 | 3.8 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Real Time LV Power Flow Analysis | $MAUD | NPV | 0.67443 | 0.9 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
LV Model Extension | $MAUD | NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Real Time Grid Monitoring and Control | $MAUD | NPV | 2.8326 | 3.78 | 0 | 0 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21
LV Management Capability | $MAUD | NPV | 0.92901 | 1.258 | 0 | 0 | 0 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074
Dynamic Forecasting Capacity | $MAUD | NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DER - Monitoring Capability | $MAUD | NPV | 0.92901 | 1.258 | 0 | 0 | 0 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074
DER- Dispatching Automation | $MAUD | NPV | 0.79621 | 1.11 | 0 | 0 | 0 | 0 | 0 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074
Subtotal - Opex | $MAUD | NPV | 15.4729 | 20.716 | 0 | 0.3 | 0.826 | 0.974 | 1.036 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172
Refresh Capex
Iot Platform for Network Sensors | $MAUD | NPV | 1.5602 | 2.1121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70402 | 0.35201 | 0 | 0 | 0 | 0 | 0 | 0.70402 | 0.35201 | 0 | 0 | 0 | 0
Real Time LV Power Flow Analysis | $MAUD | NPV | 3.6102 | 5.0798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56443 | 0.56443 | 0.56443 | 0.56443 | 0.28221 | 0 | 0 | 0.56443 | 0.56443 | 0.56443 | 0.56443 | 0.28221 | 0
Real Time Grid Monitoring and Control | $MAUD | NPV | 0.86455 | 1.1918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59592 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59592 | 0 | 0 | 0 | 0
LV Management Capability | $MAUD | NPV | 1.5426 | 2.0697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0349 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0349 | 0 | 0 | 0 | 0 | 0
Dynamic Forecasting Capacity | $MAUD | NPV | 0.78477 | 1.0819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54093 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54093 | 0 | 0 | 0 | 0
DER - Monitoring Capability | $MAUD | NPV | 2.3397 | 3.1674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0558 | 0.5279 | 0 | 0 | 0 | 0 | 0 | 1.0558 | 0.5279 | 0 | 0 | 0 | 0
Real Time Data Platform | $MAUD | NPV | 1.5739 | 2.1697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0849 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0849 | 0 | 0 | 0 | 0
IOT Platform Extension Customer Sensors | $MAUD | NPV | 0.68189 | 0.96588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48294 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48294 | 0 | 0 | 0
Real Time Grid Analytics Platform | $MAUD | NPV | 0.75558 | 1.0703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53513 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53513 | 0 | 0 | 0
LV Model Extension | $MAUD | NPV | 0.74824 | 1.0599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52993 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52993 | 0 | 0 | 0
DER Dispatching Automation | $MAUD | NPV | 0.71541 | 1.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53493 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53493 | 0
Subtotal - Repex | $MAUD | NPV | 15.1771 | 21.0383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3591 | 3.666 | 2.1124 | 0.56443 | 0.81714 | 0 | 0 | 3.3591 | 3.666 | 2.1124 | 0.56443 | 0.81714 | 0
Program Cost - Opex
Benefit Category 2 - All Opex | $MAUD | NPV | 7.4187 | 9.9 | 0 | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
Benefit Category 3 - Standard Program Costs for Customer Load control | $MAUD | NPV | 3.1385 | 4.25 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Benefit Category 3 - Incremental Costs with increased customer load control | $MAUD | NPV | 6.6384 | 10.1027 | 0 | 0 | 0 | 0.023377 | 0.039286 | 0.062865 | 0.096341 | 0.13851 | 0.19364 | 0.2572 | 0.33789 | 0.43025 | 0.52776 | 0.64766 | 0.78233 | 0.9848 | 1.1519 | 1.3236 | 1.4811 | 1.6241
Benefit Category 4 - Standard Program Costs for Customer Load control | $MAUD | NPV | 3.1385 | 4.25 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Benefit Category 4 - Incremental Costs with increased customer load control | $MAUD | NPV | 6.2409 | 9.2412 | 0 | 0 | 0 | 0.08275 | 0.11603 | 0.15263 | 0.19289 | 0.23718 | 0.2859 | 0.33949 | 0.39844 | 0.46328 | 0.53461 | 0.61307 | 0.69937 | 0.79431 | 0.89874 | 1.0136 | 1.14 | 1.279
Benefit Category 4 - Standard Program Costs for Solar to Hot Water Control | $MAUD | NPV | 1.5693 | 2.125 | 0 | 0 | 0 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125
Benefit Category 4 - Incremental Costs with Solar to Hot Water Control | $MAUD | NPV | 1.4878 | 2.125 | 0 | 0 | 0 | 0.045 | 0.055 | 0.065 | 0.075 | 0.085 | 0.095 | 0.105 | 0.115 | 0.125 | 0.135 | 0.145 | 0.155 | 0.165 | 0.175 | 0.185 | 0.195 | 0.205
Subtotal - Program Opex | $MAUD | NPV | 29.6322 | 41.994 | 0 | 0 | 0.55 | 1.3261 | 1.3853 | 1.4555 | 1.5392 | 1.6357 | 1.7495 | 1.8767 | 2.0263 | 2.1935 | 2.3724 | 2.5807 | 2.8117 | 3.1191 | 3.4007 | 3.6973 | 3.9911 | 4.2831
Total cost Option 1 |  | NPV | 80.3705 | 104.7866 | 6.7182 | 7.6321 | 5.6009 | 3.429 | 4.0556 | 2.6275 | 2.7112 | 6.1668 | 6.5876 | 5.1611 | 3.7628 | 4.1827 | 3.5444 | 3.7527 | 7.3428 | 7.9571 | 6.6851 | 5.4337 | 5.9802 | 5.4551
[5 empty] | -6.7182 | -7.6321 | -5.6009 | -3.429 | -4.0556 | -2.6275 | -2.7112 | -6.1668 | -6.5876 | -5.1611 | -3.7628 | -4.1827 | -3.5444 | -3.7527 | -7.3428 | -7.9571 | -6.6851 | -5.4337 | -5.9802 | -5.4551
[5 empty] | -6.7182 | -7.3321 | -4.2249 | -1.1289 | -1.6343 | 0 | 0 | -3.3591 | -3.666 | -2.1124 | -0.56443 | -0.81714 | 0 | 0 | -3.3591 | -3.666 | -2.1124 | -0.56443 | -0.81714 | 0
Costs for Option 2 - Increased Coverage of FlexiGrid
Capex |  |  |  | $MAUD
Real-Time Data Platform | $MAUD | NPV | 2.065 | 2.1121 | 1.408 | 0.70402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Iot Platform for Network Sensors | $MAUD | NPV | 4.7785 | 5.0798 | 1.1289 | 1.1289 | 1.1289 | 1.1289 | 0.56443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IoT Platform Extension for Network Sensors | $MAUD | NPV | 1.1443 | 1.1918 | 0 | 1.1918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Real Time Grid Analytics Platform | $MAUD | NPV | 2.0418 | 2.0697 | 2.0697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Real Time LV Power Flow Analysis | $MAUD | NPV | 1.0387 | 1.0819 | 0 | 1.0819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LV Model Extension | $MAUD | NPV | 3.0969 | 3.1674 | 2.1116 | 1.0558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Real Time Grid Monitoring and Control | $MAUD | NPV | 2.0832 | 2.1697 | 0 | 2.1697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LV Management Capability | $MAUD | NPV | 0.90254 | 0.96588 | 0 | 0 | 0.96588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dynamic Forecasting Capacity | $MAUD | NPV | 1.0001 | 1.0703 | 0 | 0 | 1.0703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DER - Monitoring Capability | $MAUD | NPV | 0.99037 | 1.0599 | 0 | 0 | 1.0599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DER- Dispatching Automation | $MAUD | NPV | 0.94691 | 1.0699 | 0 | 0 | 0 | 0 | 1.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal - Capex | $MAUD | NPV | 20.0883 | 21.0383 | 6.7182 | 7.3321 | 4.2249 | 1.1289 | 1.6343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex
Real-Time Data Platform | $MAUD | NPV | 2.7937 | 3.7 | 0 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Iot Platform for Network Sensors | $MAUD | NPV | 1.3891 | 1.922 | 0 | 0 | 0 | 0 | 0.062 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124
IoT Platform Extension for Network Sensors | $MAUD | NPV | 2.2391 | 2.988 | 0 | 0 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166 | 0.166
Real Time Grid Analytics Platform | $MAUD | NPV | 2.8897 | 3.8 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Real Time LV Power Flow Analysis | $MAUD | NPV | 0.67443 | 0.9 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
LV Model Extension | $MAUD | NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Real Time Grid Monitoring and Control | $MAUD | NPV | 2.8326 | 3.78 | 0 | 0 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21
LV Management Capability | $MAUD | NPV | 0.92901 | 1.258 | 0 | 0 | 0 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074
Dynamic Forecasting Capacity | $MAUD | NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DER - Monitoring Capability | $MAUD | NPV | 0.92901 | 1.258 | 0 | 0 | 0 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074
DER- Dispatching Automation | $MAUD | NPV | 0.79621 | 1.11 | 0 | 0 | 0 | 0 | 0 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074 | 0.074
Subtotal - Opex | $MAUD | NPV | 15.4729 | 20.716 | 0 | 0.3 | 0.826 | 0.974 | 1.036 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172 | 1.172
Refresh Capex
Real-Time Data Platform | $MAUD | NPV | 1.5602 | 2.1121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70402 | 0.35201 | 0 | 0 | 0 | 0 | 0 | 0.70402 | 0.35201 | 0 | 0 | 0 | 0
Iot Platform for Network Sensors | $MAUD | NPV | 3.6102 | 5.0798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56443 | 0.56443 | 0.56443 | 0.56443 | 0.28221 | 0 | 0 | 0.56443 | 0.56443 | 0.56443 | 0.56443 | 0.28221 | 0
IoT Platform Extension for Network Sensors | $MAUD | NPV | 0.86455 | 1.1918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59592 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59592 | 0 | 0 | 0 | 0
Real Time Grid Analytics Platform | $MAUD | NPV | 1.5426 | 2.0697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0349 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0349 | 0 | 0 | 0 | 0 | 0
Real Time LV Power Flow Analysis | $MAUD | NPV | 0.78477 | 1.0819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54093 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54093 | 0 | 0 | 0 | 0
LV Model Extension | $MAUD | NPV | 2.3397 | 3.1674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0558 | 0.5279 | 0 | 0 | 0 | 0 | 0 | 1.0558 | 0.5279 | 0 | 0 | 0 | 0
Real Time Grid Monitoring and Control | $MAUD | NPV | 1.5739 | 2.1697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0849 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0849 | 0 | 0 | 0 | 0
LV Management Capability | $MAUD | NPV | 0.68189 | 0.96588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48294 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48294 | 0 | 0 | 0
Dynamic Forecasting Capacity | $MAUD | NPV | 0.75558 | 1.0703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53513 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53513 | 0 | 0 | 0
DER - Monitoring Capability | $MAUD | NPV | 0.74824 | 1.0599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52993 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52993 | 0 | 0 | 0
DER- Dispatching Automation | $MAUD | NPV | 0.71541 | 1.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53493 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53493 | 0
Subtotal - Repex | $MAUD | NPV | 15.1771 | 21.0383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3591 | 3.666 | 2.1124 | 0.56443 | 0.81714 | 0 | 0 | 3.3591 | 3.666 | 2.1124 | 0.56443 | 0.81714 | 0
Device Costs
Capex - Network Devices at Contestable Meter Sites
Number of UMS Retrofits |  |  |  |  | 0 | 277.54 | 277.54 | 277.54 | 277.54 | 277.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost of UMS Retrofits | $MAUD | NPV | 0.29918 | 0.32874 | 0 | 0.065748 | 0.065748 | 0.065748 | 0.065748 | 0.065748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative Number of UMS Retrofit (need this for Metering Reading Opex and Replacements) |  |  |  |  | 0 | 277.54 | 555.08 | 832.62 | 1110.16 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7
Number of HV Customers |  |  |  |  | 0 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost of HV Customers | $MAUD | NPV | 0.33364 | 0.3666 | 0 | 0.07332 | 0.07332 | 0.07332 | 0.07332 | 0.07332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative Number of HV Customers |  |  |  |  | 0 | 56.4 | 112.8 | 169.2 | 225.6 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282
Number of LVCT Customers |  |  |  |  | 0 | 567.96 | 567.96 | 567.96 | 567.96 | 567.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost of LVCT Customers | $MAUD | NPV | 2.5033 | 2.7506 | 0 | 0.55012 | 0.55012 | 0.55012 | 0.55012 | 0.55012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative Number of LVCT Customers |  |  |  |  | 0 | 567.96 | 1135.92 | 1703.88 | 2271.84 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8
Number of 1 Phase DC Customers |  |  |  |  | 0 | 20.68 | 20.68 | 20.68 | 20.68 | 20.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost of 1 Phase DC Customers | $MAUD | NPV | 0.030113 | 0.033088 | 0 | 0.0066176 | 0.0066176 | 0.0066176 | 0.0066176 | 0.0066176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative Number of 1 Phase DC Customers |  |  |  |  | 0 | 20.68 | 41.36 | 62.04 | 82.72 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4
Number of 3 Phase DC Customers |  |  |  |  | 0 | 405.6 | 405.6 | 405.6 | 405.6 | 405.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost of 3 Phase DC Customers | $MAUD | NPV | 1.0441 | 1.1472 | 0 | 0.22945 | 0.22945 | 0.22945 | 0.22945 | 0.22945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative Number of 3 Phase DC Customers |  |  |  |  | 0 | 405.6 | 811.2 | 1216.8 | 1622.4 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028
Subtotal - Network Device Capex | $MAUD | NPV | 4.2103 | 4.6263 | 0 | 0.92525 | 0.92525 | 0.92525 | 0.92525 | 0.92525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capex - Network Device Installations at Non-ZSS Distribution Transformer Sites +IT cost
Number of Non-ZSS Distribution Transformers (>300 kVA) |  |  |  |  | 0 | 425 | 425 | 425 | 425 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost of >300 kVA Network Devices | $MAUD | NPV | 4.4686 | 4.9101 | 0 | 0.98202 | 0.98202 | 0.98202 | 0.98202 | 0.98202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative number of network devices on > 300 kVA Network Devices |  |  |  |  | 0 | 425 | 850 | 1275 | 1700 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125
Network Device IT Cost | $MAUD | NPV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal - Network Device Capex | $MAUD | NPV | 4.4686 | 4.9101 | 0 | 0.98202 | 0.98202 | 0.98202 | 0.98202 | 0.98202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex for Reading Devices
Average Number of UMS Retrofit Devices read |  |  |  |  | 0 | 138.77 | 416.31 | 693.85 | 971.39 | 1248.93 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7 | 1387.7
Cost of reading UMS Retrofit Devices | $MAUD | NPV | 1.2282 | 1.6715 | 0 | 0.01013 | 0.030391 | 0.050651 | 0.070911 | 0.091172 | 0.1013 | 0.1013 | 0.1013 | 0.1013 | 0.1013 | 0.1013 | 0.1013 | 0.1013 | 0.1013 | 0.1013 | 0.1013 | 0.1013 | 0.1013 | 0.1013
Average Number of HV Customers |  |  |  |  | 0 | 28.2 | 84.6 | 141 | 197.4 | 253.8 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282 | 282
Cost of Reading HV Meters | $MAUD | NPV | 0.38635 | 0.52579 | 0 | 0.0031866 | 0.0095598 | 0.015933 | 0.022306 | 0.028679 | 0.031866 | 0.031866 | 0.031866 | 0.031866 | 0.031866 | 0.031866 | 0.031866 | 0.031866 | 0.031866 | 0.031866 | 0.031866 | 0.031866 | 0.031866 | 0.031866
Average Number of LVCT Customers |  |  |  |  | 0 | 283.98 | 851.94 | 1419.9 | 1987.86 | 2555.82 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8 | 2839.8
Cost of Reading LVCT Customers | $MAUD | NPV | 3.8906 | 5.2948 | 0 | 0.03209 | 0.096269 | 0.16045 | 0.22463 | 0.28881 | 0.3209 | 0.3209 | 0.3209 | 0.3209 | 0.3209 | 0.3209 | 0.3209 | 0.3209 | 0.3209 | 0.3209 | 0.3209 | 0.3209 | 0.3209 | 0.3209
Average Number of 1 Phase DC Customers |  |  |  |  | 0 | 10.34 | 31.02 | 51.7 | 72.38 | 93.06 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4
Cost of reading 1 Phase DC Customers | $MAUD | NPV | 0.11408 | 0.15526 | 0 | 0.00094094 | 0.0028228 | 0.0047047 | 0.0065866 | 0.0084685 | 0.0094094 | 0.0094094 | 0.0094094 | 0.0094094 | 0.0094094 | 0.0094094 | 0.0094094 | 0.0094094 | 0.0094094 | 0.0094094 | 0.0094094 | 0.0094094 | 0.0094094 | 0.0094094
Average Number of 3 Phase DC Customers |  |  |  |  | 0 | 202.8 | 608.4 | 1014 | 1419.6 | 1825.2 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028
Cost of reading 3 Phase DC Customers | $MAUD | NPV | 2.2375 | 3.045 | 0 | 0.018455 | 0.055364 | 0.092274 | 0.12918 | 0.16609 | 0.18455 | 0.18455 | 0.18455 | 0.18455 | 0.18455 | 0.18455 | 0.18455 | 0.18455 | 0.18455 | 0.18455 | 0.18455 | 0.18455 | 0.18455 | 0.18455
Average Number of Non-ZSS Distribution Transformers (> 300kVA) |  |  |  |  | 0 | 212.5 | 637.5 | 1062.5 | 1487.5 | 1912.5 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125 | 2125
Cost of reading devices for >300 kVA Transformers | $MAUD | NPV | 2.9113 | 3.9621 | 0 | 0.024013 | 0.072038 | 0.12006 | 0.16809 | 0.21611 | 0.24013 | 0.24013 | 0.24013 | 0.24013 | 0.24013 | 0.24013 | 0.24013 | 0.24013 | 0.24013 | 0.24013 | 0.24013 | 0.24013 | 0.24013 | 0.24013
Subtotal - Network Device Reading (Opex) | $MAUD | NPV | 10.768 | 14.6544 | 0 | 0.088815 | 0.26644 | 0.44407 | 0.6217 | 0.79933 | 0.88815 | 0.88815 | 0.88815 | 0.88815 | 0.88815 | 0.88815 | 0.88815 | 0.88815 | 0.88815 | 0.88815 | 0.88815 | 0.88815 | 0.88815 | 0.88815
Program Cost
Benefit Category 2 - Standard Program Cost | $MAUD | NPV | 7.4187 | 9.9 | 0 | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
Benefit Category 2 - Program cost for expansion | $MAUD | NPV | 2.1638 | 2.8875 | 0 | 0 | 0.16042 | 0.16042 | 0.16042 | 0.16042 | 0.16042 | 0.16042 | 0.16042 | 0.16042 | 0.16042 | 0.16042 | 0.16042 | 0.16042 | 0.16042 | 0.16042 | 0.16042 | 0.16042 | 0.16042 | 0.16042
Benefit Category 3 - Standard Program Costs for Customer Load control | $MAUD | NPV | 6.9048 | 9.35 | 0 | 0 | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
Benefit Category 3 - Incremental Costs with increased customer load control | $MAUD | NPV | 11.507 | 17.5119 | 0 | 0 | 0 | 0.040553 | 0.06813 | 0.109 | 0.16702 | 0.24012 | 0.33568 | 0.44585 | 0.58571 | 0.7458 | 0.91482 | 1.1226 | 1.3561 | 1.707 | 1.9967 | 2.2943 | 2.5673 | 2.8152
Benefit Category 4 - Standard Program Costs for Customer Load control | $MAUD | NPV | 6.9048 | 9.35 | 0 | 0 | 0 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
Benefit Category 4 - Incremental Costs with increased customer load control | $MAUD | NPV | 6.3987 | 9.4566 | 0 | 0 | 0 | 0.09063 | 0.12653 | 0.16576 | 0.20602 | 0.25031 | 0.29903 | 0.35262 | 0.41157 | 0.47641 | 0.54774 | 0.6262 | 0.71251 | 0.80745 | 0.91188 | 1.0268 | 1.1531 | 1.2921
Benefit Category 4 - Standard Program Costs for Solar to Hot Water Control | $MAUD | NPV | 1.5693 | 2.125 | 0 | 0 | 0 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125
Benefit Category 4 - Incremental Costs with Solar to Hot Water Control | $MAUD | NPV | 1.4878 | 2.125 | 0 | 0 | 0 | 0.045 | 0.055 | 0.065 | 0.075 | 0.085 | 0.095 | 0.105 | 0.115 | 0.125 | 0.135 | 0.145 | 0.155 | 0.165 | 0.175 | 0.185 | 0.195 | 0.205
Subtotal - Program Opex | $MAUD | NPV | 44.3548 | 62.7061 | 0 | 0 | 0.16042 | 1.5616 | 1.6351 | 1.7252 | 1.8335 | 1.9608 | 2.1151 | 2.2889 | 2.4977 | 2.7326 | 2.983 | 3.2793 | 3.609 | 4.0649 | 4.469 | 4.8915 | 5.3008 | 5.6977
Total cost Option 2 |  | NPV | 107.1213 | 139.7895 | 6.7182 | 9.6282 | 7.385 | 6.0158 | 6.8343 | 5.6038 | 3.8936 | 7.3801 | 7.8413 | 6.4615 | 5.1223 | 5.6099 | 5.0431 | 5.3394 | 9.0283 | 9.7911 | 8.6416 | 7.5161 | 8.1781 | 7.7579
[5 empty] | -6.7182 | -9.6282 | -7.385 | -6.0158 | -6.8343 | -5.6038 | -3.8936 | -7.3801 | -7.8413 | -6.4615 | -5.1223 | -5.6099 | -5.0431 | -5.3394 | -9.0283 | -9.7911 | -8.6416 | -7.5161 | -8.1781 | -7.7579
[5 empty] | -6.7182 | -9.2393 | -6.1321 | -3.0361 | -3.5416 | -1.9073 | 0 | -3.3591 | -3.666 | -2.1124 | -0.56443 | -0.81714 | 0 | 0 | -3.3591 | -3.666 | -2.1124 | -0.56443 | -0.81714 | 0

## Retailer Controlled Load (hidden)
Retailer Tariffs - 16th May 2019
| Controlled load | FiT | Difference
1 | 9.91 | 13.5 | -3.59 c/kWh
2 | 9.91 | 9.9 | -0.01 c/kWh
3 | 12.5 | 11.3 | +1.20 c/kWh
4 | 11.47 | 9.9 | +1.57 c/kWh
5 | 10.9 | 9.9 | +1.00 c/kWh
6 | 16.08 | 12 | +4.08 c/kWh
7 | 18.6 | 9.9 | +8.70 c/kWh
8 | 14.5 | 11.3 | +3.20 c/kWh
9 | 19 | 11.3 | +7.70 c/kWh
10 | 12.99 | 9.9 | +3.09 c/kWh
Average | 13.586 | 10.89