## Inputs
Powercor - Inglewood Regulator Replacement Risk Monetisation Model
Inputs | [8 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
General inputs, timing and costs
General inputs
|  | Company |  | Powercor
|  | Title |  | Inglewood Regulator Replacement Risk Monetisation Model
|  | Model start & timeline |  | 2019
|  | Real WACC |  | 2.75%
|  | Asset Life (years) |  | 50
Inflation
|  | Year | [6 empty] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
|  |  | Nominal escalation index to June $2021 | [5 empty] | 125.4% | 122% | 117.9% | 115.6% | 113.1% | 110.6% | 108.9% | 107.8% | 105.8% | 103.6% | 102% | 100%
Capex
|  | Replacement capex regulator, real $2019 |  | 1219000 |  |  |  |  | 0 | 0 | 0 | 0 | 200000 | 1019000 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Capex ($2021) | 1263186.0531 |  |  |  |  | 0 | 0 | 0 | 0 | 207249.5575 | 1055936.4956 | 0 | 0 | 0 | 0 | 0 | 0
Opex
|  |  |  | Pre-replacement | Post-replacement
|  | Annual opex, real $2019 |  | 7100 | 1500
|  |  | Opex ($2021) | 7357.3593 | 1554.3717
Scenario manager
Sensitivity bounds
|  | Bound |  | Lower | Central | Upper
|  |  | PoF | -10% | 0% | 10%
|  |  | Capex | -10% | 0% | 10%
|  |  | Opex | -10% | 0% | 10%
|  |  | Demand | -5% | 0% | 5%
|  |  | VCR | -10% | 0% | 10%
|  |  | Environment | -10% | 0% | 10%
Scenario selection
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | Central | Central | Central | Central | Central | 2010: Central
|  |  | A | Lower | Upper | Upper | Lower | Lower | 2010: Lower
|  |  | B | Lower | Lower | Lower | Lower | Lower | 2010: Lower
|  |  | C | Upper | Upper | Upper | Upper | Upper | 2010: Upper
|  |  | D | Upper | Lower | Lower | Upper | Upper | 2010: Upper
Scenario output
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | 100% | 100% | 100% | 100% | 100% | 2010: 100%
|  |  | A | 90% | 110% | 110% | 95% | 90% | 2010: 90%
|  |  | B | 90% | 90% | 90% | 95% | 90% | 2010: 90%
|  |  | C | 110% | 110% | 110% | 105% | 110% | 2010: 110%
|  |  | D | 110% | 90% | 90% | 105% | 110% | 2010: 110%
Network assumptions
Probability of failure (PoF)
|  | Failure mode |  | Failure code
|  |  | Significant | 1 |  |  |  |  | 17.17% | 18.2% | 19.3% | 20.46% | 21.7% | 23.02% | 24.43% | 25.92% | 27.51% | 29.21% | 31.01% | 32.93%
|  |  | Major | 2 |  |  |  |  | 0.09233% | 0.09786% | 0.1037% | 0.11% | 0.1167% | 0.1238% | 0.1313% | 0.1394% | 0.1479% | 0.157% | 0.1667% | 0.177%
|  |  | Catastrophic | 3 |  |  |  |  | 0.09233% | 0.09786% | 0.1037% | 0.11% | 0.1167% | 0.1238% | 0.1313% | 0.1394% | 0.1479% | 0.157% | 0.1667% | 0.177%
Value of customer reliability (VCR)
|  | Sector |  | MWh | $/MWh ($2018) | Load Duration | Duration Weighted $/MWh ($2021)
|  |  | Residential | 36986.691 | 26450 | 20% | 3291.9308
|  |  | Agricultural | 3269.234 | 50930 | 15% | 420.2043
|  |  | Commercial | 20457.538 | 47770 | 40% | 6576.8531
|  |  | Industrial | 2156.745 | 47070 | 80% | 1366.4147
|  |  | Total | 62870.208 | 35367.6998 | 31.15% | 11655.4029
Asset information
|  | Assets at risk |  | 1
|  | N-rating, MVA |  | 20
|  |  | N-1 Rating before transfers, MVA | 20
|  |  | N-2 Rating before transfers, MVA | 0
|  |  | N-3 Rating before transfers, MVA | 0
|  |  | N-4 Rating before transfers, MVA | 0
|  |  | Transfer capacity, MVA | 0
Environmental assumptions
Environmental consequence
|  | Settings |  | Real $2019 | Real $2021
|  |  | Value Consequence Loss Oil / litre | 100 | 103.6248
|  |  | Value Consequence Loss SF6/Kg | 598 | 619.6762
|  |  | Value Consequence Fire | 10000 | 10362.4779
|  |  | Value Consequence Waste / tonne | 1000 | 1036.2478
|  |  | Value Consequence Disturbance | 400 | 414.4991
|  |  | Value Fire brigade attendance | 50000 | 51812.3894
|  | Failure Mode |  | Significant | Major | Catastrophic
|  |  | Average Consequence Loss Oil | 500 | 4050 | 4050
|  |  | Average Consequences Loss SF6 kgs | 0 | 0 | 0
|  |  | Average Consequence Fire | 0.05 | 2.5 | 5
|  |  | Average Consequence Waste | 10 | 405 | 405
|  |  | Average Consequence Disturbance | 2 | 3 | 5
|  |  | Average Cost of Fault (Air Insulated) | 11709.6 | 446830.046 | 473565.2389
|  |  | Average Cost of Fault (SF6 Insulated) | 11709.6 | 446830.046 | 473565.2389
|  |  | Average Cost of Fault (Oil Insulated) | 63521.9894 | 866510.4 | 893245.5929
Generation assumptions
Generation requirements
Generator detail
|  |  | Generator capacity, MVA | 1
|  |  | Generators per site | 4
|  |  | Step-up transformer capacity | 5
|  |  | Number of transformers required per site | 1
|  |  | Generator sites connected per day | 3
|  |  | Fuel usage / MWh in Litres | 270
|  |  | Days in week | 7
|  |  | Setup, persons required | 5
|  |  | Setup, hours employed per day | 16
|  |  | Hours per day | 24
|  | Generator detail by failure mode |  | Significant | Major | Coincidental | Catastrophic
|  |  | Switching time only (hours required) | 2 | 2 | 0 | 0
|  |  | Number of weeks generation required | 1.1905 | 6 | 6 | 12
|  |  | Max demand load net of transfers, MVA | 0 | 0 | 17.0121 | 17.0121
|  |  | Number of generators | 0 | 0 | 18 | 18
|  |  | Generator sites | 0 | 0 | 5 | 5
|  |  | Number of days to connect all generators | 0 | 0 | 2 | 2
|  | Generation costs |  | Real $2019 | Real $2021
|  |  | Generator hire per week | 7000 | 7253.7345
|  |  | Fuel cost $ per litre including delivery | 1.5 | 1.5544
|  |  | Fitter cost (blended 24hr rate) $ per hr | 150 | 155.4372
|  |  | Traffic management and security per site | 10000 | 10362.4779
|  |  | Transformer hire per week | 7000 | 7253.7345
|  |  | Earthing and bunding per site | 2000 | 2072.4956
|  |  | Temporary fencing per site per week | 3000 | 3108.7434
|  |  | Miscellaneous material per site | 2000 | 2072.4956
|  |  | Install and remove step down transformers per site | 2500 | 2590.6195
|  |  | Council permits per site | 4000 | 4144.9912
|  |  | Crane hire to install / remove generators per site | 2500 | 2590.6195
|  |  | Cable hire per site | 3000 | 3108.7434
|  | Generation costs by failure mode |  | Significant | Major | Coincidental | Catastrophic
|  |  | Generator hire | 0 | 0 | 826925.7345 | 1588567.8584
|  |  | Fuel cost | 0 | 0 | 2242135.5086 | 4484271.0173
|  |  | Fitter cost | 0 | 0 | 845578.1947 | 1628981.5221
|  |  | Traffic management cost | 0 | 0 | 2176120.354 | 4352240.708
|  |  | Transformer hire | 0 | 0 | 229701.5929 | 441268.8496
|  |  | Earthing and bunding | 0 | 0 | 10362.4779 | 10362.4779
|  |  | Temporary fencing | 0 | 0 | 93262.3009 | 186524.6018
|  |  | Miscellaneous materials | 0 | 0 | 10362.4779 | 10362.4779
|  |  | Installation & removal of step-down transformers | 0 | 0 | 12953.0973 | 12953.0973
|  |  | Council permits | 0 | 0 | 20724.9558 | 20724.9558
|  |  | Crane hire | 0 | 0 | 12953.0973 | 12953.0973
|  |  | Cable hire | 0 | 0 | 15543.7168 | 15543.7168
|  |  | Total | 0 | 0 | 6496623.5086 | 12764754.3801
Safety assumptions
Safety consequence
|  | Value of consquence |  | Base Value ($2018) | Disproportion Factor | Reference Value ($2021)
|  |  | Minor | 127274.0425 | 1 | 134627.6539
|  |  | Serious | 672376.8885 | 2 | 1422450.662
|  |  | Fataility | 4500000 | 3 | 14280000
|  | Probability of event, by failure mode |  | Significant | Major | Catastrophic
|  |  | Minor | 1.172% | 4.103% | 4.103%
|  |  | Serious | 0.2345% | 0.8206% | 0.8206%
|  |  | Fataility | 0.02345% | 0.08206% | 0.08206%
|  |  | Value of event | 8261.6388 | 28915.7357 | 28915.7357
|  |  | Weighted likelyhood of consequence | 0.05217% | 0.1826% | 0.1826%
Base Case PoE, Load and VCR assumptions
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA | 10% |  |  |  |  | 21.22 | 20.936 | 19.435 | 18.848 | 18.418 | 18.415 | 18.161 | 18.161 | 18.161 | 18.161 | 18.161 | 18.161
|  |  | 50% PoE forecast, MVA | 50% |  |  |  |  | 18.504 | 17.745 | 16.897 | 16.469 | 16.083 | 15.936 | 15.507 | 15.507 | 15.507 | 15.507 | 15.507 | 15.507
|  |  | Selected | 70% |  |  |  |  | 19.3188 | 18.7023 | 17.6584 | 17.1827 | 16.7835 | 16.6797 | 16.3032 | 16.3032 | 16.3032 | 16.3032 | 16.3032 | 16.3032
Load at risk
Selected profile, MVA
|  |  | N | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 | [5 empty] | 19.3188 | 18.7023 | 17.6584 | 17.1827 | 16.7835 | 16.6797 | 16.3032 | 16.3032 | 16.3032 | 16.3032 | 16.3032 | 16.3032
|  |  | N-3 | [5 empty] | 19.3188 | 18.7023 | 17.6584 | 17.1827 | 16.7835 | 16.6797 | 16.3032 | 16.3032 | 16.3032 | 16.3032 | 16.3032 | 16.3032
|  |  | N-4 | [5 empty] | 19.3188 | 18.7023 | 17.6584 | 17.1827 | 16.7835 | 16.6797 | 16.3032 | 16.3032 | 16.3032 | 16.3032 | 16.3032 | 16.3032
End

## Base Case
Powercor - Inglewood Regulator Replacement Risk Monetisation Model
Base Case | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario Base case: Consequence calculation
Consequence calculation
|  | Scenario |  |  | Base case
|  |  | PoF |  | 100%
|  |  | Capex |  | 100%
|  |  | Opex |  | 100%
|  |  | Demand |  | 100%
|  |  | VCR |  | 100%
|  |  | Environment |  | 100%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 13510103.7979 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 12764754.3801 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 1263186.0531 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 893245.5929 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 450336.7933 | 0 | 0 | 0 | 0 | 96% | 432323.3215 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 100% | 28915.7357 | 28915.7357
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 1263186.0531 | 0 | 100% | 1263186.0531 | 1263186.0531
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 866510.4 | 100% | 866510.4 | 866510.4
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 13510103.7979 | 0 | 6496623.5086 | 0 | 0 | 4% | 800269.0923 | 259864.9403
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 450336.7933 | 0 | 0 | 0 | 0 | 96% | 432323.3215 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 7357.3593 | 0 | 100% | 7357.3593 | 7357.3593
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 63521.9894 | 100% | 63521.9894 | 63521.9894
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 13510103.7979 | 0 | 1289012.6009 | 0 | 0 | 4% | 591964.656 | 51560.504
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 13960440.5912 | 8261.6388 | 1340824.9903 | 7357.3593 | 63521.9894 | 7.511% | 1155241.3543 | 182513.8809
[5 empty] | 2 | Major |  | 13960440.5912 | 28915.7357 | 6548435.898 | 1263186.0531 | 866510.4 | 15.19% | 3443016.9919 | 2470289.5185
[5 empty] | 3 | Catastrophic |  | 13510103.7979 | 28915.7357 | 12816566.7695 | 1263186.0531 | 893245.5929 | 0% | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 4598258.3462; 2026: 2652803.3993
Scenario Base case: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 20
|  |  | N-1 Rating before transfers, MVA |  |  | 20
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 21.22 | 20.936 | 19.435 | 18.848 | 18.418 | 18.415 | 18.161 | 18.161 | 18.161 | 18.161 | 18.161 | 18.161
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 18.504 | 17.745 | 16.897 | 16.469 | 16.083 | 15.936 | 15.507 | 15.507 | 15.507 | 15.507 | 15.507 | 15.507
|  |  | Selected |  |  | 70% |  | 19.3188 | 18.7023 | 17.6584 | 17.1827 | 16.7835 | 16.6797 | 16.3032 | 16.3032 | 16.3032 | 16.3032 | 16.3032 | 16.3032
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 19.3188 | 18.7023 | 17.6584 | 17.1827 | 16.7835 | 16.6797 | 16.3032 | 16.3032 | 16.3032 | 16.3032 | 16.3032 | 16.3032
|  |  | N-3 |  |  |  |  | 19.3188 | 18.7023 | 17.6584 | 17.1827 | 16.7835 | 16.6797 | 16.3032 | 16.3032 | 16.3032 | 16.3032 | 16.3032 | 16.3032
|  |  | N-4 |  |  |  |  | 19.3188 | 18.7023 | 17.6584 | 17.1827 | 16.7835 | 16.6797 | 16.3032 | 16.3032 | 16.3032 | 16.3032 | 16.3032 | 16.3032
VCR at risk
Average load at risk (pu)
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Adjustment |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Adjustment |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Adjustment |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 450336.7933 | 435965.6815 | 411631.5315 | 400542.5812 | 391236.9076 | 388817.2459 | 380040.7276 | 380040.7276 | 380040.7276 | 380040.7276 | 380040.7276 | 380040.7276
|  |  | N-1 |  |  | Major |  | 450336.7933 | 435965.6815 | 411631.5315 | 400542.5812 | 391236.9076 | 388817.2459 | 380040.7276 | 380040.7276 | 380040.7276 | 380040.7276 | 380040.7276 | 380040.7276
|  |  | N-2 |  |  | Catastrophic |  | 13510103.7979 | 13078970.4464 | 12348945.9441 | 12016277.4359 | 11737107.2267 | 11664517.3778 | 11401221.8273 | 11401221.8273 | 11401221.8273 | 11401221.8273 | 11401221.8273 | 11401221.8273
|  |  | N-3 |  |  | Catastrophic |  | 13510103.7979 | 13078970.4464 | 12348945.9441 | 12016277.4359 | 11737107.2267 | 11664517.3778 | 11401221.8273 | 11401221.8273 | 11401221.8273 | 11401221.8273 | 11401221.8273 | 11401221.8273
|  |  | N-4 |  |  | Catastrophic |  | 13510103.7979 | 13078970.4464 | 12348945.9441 | 12016277.4359 | 11737107.2267 | 11664517.3778 | 11401221.8273 | 11401221.8273 | 11401221.8273 | 11401221.8273 | 11401221.8273 | 11401221.8273
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 17.17% | 18.2% | 19.3% | 20.46% | 21.7% | 23.02% | 24.43% | 25.92% | 27.51% | 29.21% | 31.01% | 32.93%
|  |  | Major |  |  |  |  | 0.09233% | 0.09786% | 0.1037% | 0.11% | 0.1167% | 0.1238% | 0.1313% | 0.1394% | 0.1479% | 0.157% | 0.1667% | 0.177%
|  |  | Catastrophic |  |  |  |  | 0.09233% | 0.09786% | 0.1037% | 0.11% | 0.1167% | 0.1238% | 0.1313% | 0.1394% | 0.1479% | 0.157% | 0.1667% | 0.177%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 74245.369 | 76182.0684 | 76255.62 | 78680.4586 | 81508.5498 | 85929.4911 | 89114.1155 | 94569.3711 | 100377.6415 | 106562.4308 | 113148.8361 | 120142.3336
|  |  | Network Performance |  |  | Major |  | 399.1687 | 409.581 | 409.9765 | 423.0132 | 438.218 | 461.9865 | 479.1081 | 508.4375 | 539.6647 | 572.9163 | 608.3271 | 645.9265
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 92806.7113 | 95227.5854 | 95319.525 | 98350.5732 | 101885.6873 | 107411.8639 | 111392.6444 | 118211.7139 | 125472.0518 | 133203.0385 | 141436.0452 | 150177.917
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 498.9608 | 511.9763 | 512.4706 | 528.7665 | 547.7725 | 577.4831 | 598.8852 | 635.5468 | 674.5809 | 716.1454 | 760.4088 | 807.4082
|  |  | Other significant risks |  |  | Significant |  | 31344.1578 | 33221.9502 | 35219.8813 | 37345.8937 | 39608.4653 | 42016.6465 | 44580.0988 | 47309.1371 | 50214.774 | 53308.7678 | 56603.6735 | 60102.2304
|  |  | Other major risks |  |  | Major |  | 2280.8442 | 2417.4869 | 2562.8719 | 2717.5771 | 2882.2193 | 3057.4573 | 3243.994 | 3442.58 | 3654.0167 | 3879.1597 | 4118.9226 | 4373.5047
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 7357.3593 | 7357.3593 | 7357.3593 | 7357.3593 | 7357.3593 | 7357.3593 | 7357.3593 | 7357.3593 | 7357.3593 | 7357.3593 | 7357.3593 | 7357.3593
|  |  | Subtotal |  |  |  |  | 208932.571 | 215328.0075 | 217637.7046 | 225403.6416 | 234228.2716 | 246812.2877 | 256766.2054 | 272034.1458 | 288290.0889 | 305599.8178 | 324033.5725 | 343606.6798
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 207249.5575 | 1055936.4956 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 47000.6825
|  |  | Post-replacement opex |  |  | 1554.3717
|  |  | Total annuity |  |  | 48555.0542
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 208932.571 | 215328.0075 | 217637.7046 | 225403.6416 | 234228.2716 | 246812.2877 | 256766.2054 | 272034.1458 | 288290.0889 | 305599.8178 | 324033.5725 | 343606.6798
|  |  | Annualised cost |  |  |  |  | 48555.0542 | 48555.0542 | 48555.0542 | 48555.0542 | 48555.0542 | 48555.0542 | 48555.0542 | 48555.0542 | 48555.0542 | 48555.0542 | 48555.0542 | 48555.0542
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario A
Powercor - Inglewood Regulator Replacement Risk Monetisation Model
Scenario A | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario A: Consequence calculation
Consequence calculation
|  | Scenario |  |  | A
|  |  | PoF |  | 90%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 11551138.7472 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 14041229.8181 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 1389504.6584 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 803921.0336 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 385037.9582 | 0 | 0 | 0 | 0 | 96% | 369636.4399 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 100% | 28915.7357 | 28915.7357
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 1389504.6584 | 0 | 100% | 1389504.6584 | 1389504.6584
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 779859.36 | 100% | 779859.36 | 779859.36
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 11551138.7472 | 0 | 7146285.8595 | 0 | 0 | 4% | 747896.9843 | 285851.4344
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 385037.9582 | 0 | 0 | 0 | 0 | 96% | 369636.4399 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 8093.0952 | 0 | 100% | 8093.0952 | 8093.0952
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 57169.7904 | 100% | 57169.7904 | 57169.7904
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 11551138.7472 | 0 | 1417913.861 | 0 | 0 | 4% | 518762.1043 | 56716.5544
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 11936176.7054 | 8261.6388 | 1474907.4893 | 8093.0952 | 57169.7904 | 7.556% | 1018916.697 | 187234.7072
[5 empty] | 2 | Major |  | 11936176.7054 | 28915.7357 | 7203279.4878 | 1389504.6584 | 779859.36 | 15.81% | 3372806.8066 | 2541124.8168
[5 empty] | 3 | Catastrophic |  | 11551138.7472 | 28915.7357 | 14098223.4464 | 1389504.6584 | 803921.0336 | 0% | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 4391723.5035; 2026: 2728359.5239
Scenario A: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 20
|  |  | N-1 Rating before transfers, MVA |  |  | 20
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 20.159 | 19.8892 | 18.4632 | 17.9056 | 17.4971 | 17.4942 | 17.253 | 17.253 | 17.253 | 17.253 | 17.253 | 17.253
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 17.5788 | 16.8577 | 16.0521 | 15.6456 | 15.2788 | 15.1392 | 14.7316 | 14.7316 | 14.7316 | 14.7316 | 14.7316 | 14.7316
|  |  | Selected |  |  | 70% |  | 18.3529 | 17.7672 | 16.7755 | 16.3236 | 15.9443 | 15.8457 | 15.488 | 15.488 | 15.488 | 15.488 | 15.488 | 15.488
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 18.3529 | 17.7672 | 16.7755 | 16.3236 | 15.9443 | 15.8457 | 15.488 | 15.488 | 15.488 | 15.488 | 15.488 | 15.488
|  |  | N-3 |  |  |  |  | 18.3529 | 17.7672 | 16.7755 | 16.3236 | 15.9443 | 15.8457 | 15.488 | 15.488 | 15.488 | 15.488 | 15.488 | 15.488
|  |  | N-4 |  |  |  |  | 18.3529 | 17.7672 | 16.7755 | 16.3236 | 15.9443 | 15.8457 | 15.488 | 15.488 | 15.488 | 15.488 | 15.488 | 15.488
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 385037.9582 | 372750.6577 | 351944.9594 | 342463.9069 | 334507.556 | 332438.7453 | 324934.8221 | 324934.8221 | 324934.8221 | 324934.8221 | 324934.8221 | 324934.8221
|  |  | N-1 |  |  | Major |  | 385037.9582 | 372750.6577 | 351944.9594 | 342463.9069 | 334507.556 | 332438.7453 | 324934.8221 | 324934.8221 | 324934.8221 | 324934.8221 | 324934.8221 | 324934.8221
|  |  | N-2 |  |  | Catastrophic |  | 11551138.7472 | 11182519.7316 | 10558348.7822 | 10273917.2077 | 10035226.6789 | 9973162.358 | 9748044.6624 | 9748044.6624 | 9748044.6624 | 9748044.6624 | 9748044.6624 | 9748044.6624
|  |  | N-3 |  |  | Catastrophic |  | 11551138.7472 | 11182519.7316 | 10558348.7822 | 10273917.2077 | 10035226.6789 | 9973162.358 | 9748044.6624 | 9748044.6624 | 9748044.6624 | 9748044.6624 | 9748044.6624 | 9748044.6624
|  |  | N-4 |  |  | Catastrophic |  | 11551138.7472 | 11182519.7316 | 10558348.7822 | 10273917.2077 | 10035226.6789 | 9973162.358 | 9748044.6624 | 9748044.6624 | 9748044.6624 | 9748044.6624 | 9748044.6624 | 9748044.6624
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 15.46% | 16.38% | 17.37% | 18.42% | 19.53% | 20.72% | 21.98% | 23.33% | 24.76% | 26.29% | 27.91% | 29.64%
|  |  | Major |  |  |  |  | 0.0831% | 0.08808% | 0.09337% | 0.09901% | 0.105% | 0.1114% | 0.1182% | 0.1254% | 0.1331% | 0.1413% | 0.1501% | 0.1593%
|  |  | Catastrophic |  |  |  |  | 0.0831% | 0.08808% | 0.09337% | 0.09901% | 0.105% | 0.1114% | 0.1182% | 0.1254% | 0.1331% | 0.1413% | 0.1501% | 0.1593%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 57131.8114 | 58622.1016 | 58678.6996 | 60544.6129 | 62720.8291 | 66122.7434 | 68573.3119 | 72771.1311 | 77240.5951 | 81999.7905 | 87068.0294 | 92449.5257
|  |  | Network Performance |  |  | Major |  | 307.1603 | 315.1726 | 315.4769 | 325.5087 | 337.2088 | 355.4986 | 368.6737 | 391.2426 | 415.272 | 440.8591 | 468.1077 | 497.0405
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 71414.7643 | 73277.627 | 73348.3745 | 75680.7661 | 78401.0364 | 82653.4293 | 85716.6399 | 90963.9139 | 96550.7439 | 102499.7381 | 108835.0367 | 115561.9072
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 383.9503 | 393.9657 | 394.3461 | 406.8858 | 421.5109 | 444.3733 | 460.8421 | 489.0533 | 519.09 | 551.0739 | 585.1346 | 621.3006
|  |  | Other significant risks |  |  | Significant |  | 28939.4032 | 30673.1295 | 32517.7774 | 34480.68 | 36569.6649 | 38793.0881 | 41159.8698 | 43679.5336 | 46362.2472 | 49218.8668 | 52260.984 | 55491.1282
|  |  | Other major risks |  |  | Major |  | 2111.6224 | 2238.1273 | 2372.7258 | 2515.953 | 2668.38 | 2830.6166 | 3003.3136 | 3187.166 | 3382.9157 | 3591.3548 | 3813.329 | 4049.0231
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 8093.0952 | 8093.0952 | 8093.0952 | 8093.0952 | 8093.0952 | 8093.0952 | 8093.0952 | 8093.0952 | 8093.0952 | 8093.0952 | 8093.0952 | 8093.0952
|  |  | Subtotal |  |  |  |  | 168381.8073 | 173613.219 | 175720.4956 | 182047.5017 | 189211.7254 | 199292.8445 | 207375.7463 | 219575.1358 | 232563.9591 | 246394.7783 | 261123.7167 | 276763.0204
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 227974.5133 | 1161530.1451 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 51700.7508
|  |  | Post-replacement opex |  |  | 1709.8088
|  |  | Total annuity |  |  | 53410.5597
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 168381.8073 | 173613.219 | 175720.4956 | 182047.5017 | 189211.7254 | 199292.8445 | 207375.7463 | 219575.1358 | 232563.9591 | 246394.7783 | 261123.7167 | 276763.0204
|  |  | Annualised cost |  |  |  |  | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario B
Powercor - Inglewood Regulator Replacement Risk Monetisation Model
Scenario B | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario B: Consequence calculation
Consequence calculation
|  | Scenario |  |  | B
|  |  | PoF |  | 90%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 11551138.7472 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 11488278.9421 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 1136867.4478 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 803921.0336 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 385037.9582 | 0 | 0 | 0 | 0 | 96% | 369636.4399 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 100% | 28915.7357 | 28915.7357
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 1136867.4478 | 0 | 100% | 1136867.4478 | 1136867.4478
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 779859.36 | 100% | 779859.36 | 779859.36
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 11551138.7472 | 0 | 5846961.1578 | 0 | 0 | 4% | 695923.9962 | 233878.4463
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 385037.9582 | 0 | 0 | 0 | 0 | 96% | 369636.4399 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 6621.6234 | 0 | 100% | 6621.6234 | 6621.6234
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 57169.7904 | 100% | 57169.7904 | 57169.7904
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 11551138.7472 | 0 | 1160111.3408 | 0 | 0 | 4% | 508450.0035 | 46404.4536
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 11936176.7054 | 8261.6388 | 1206742.4913 | 6621.6234 | 57169.7904 | 7.543% | 996770.6464 | 165088.6566
[5 empty] | 2 | Major |  | 11936176.7054 | 28915.7357 | 5893592.3082 | 1136867.4478 | 779859.36 | 15.46% | 3057834.13 | 2226152.1402
[5 empty] | 3 | Catastrophic |  | 11551138.7472 | 28915.7357 | 11534910.0925 | 1136867.4478 | 803921.0336 | 0% | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 4054604.7764; 2026: 2391240.7968
Scenario B: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 20
|  |  | N-1 Rating before transfers, MVA |  |  | 20
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 20.159 | 19.8892 | 18.4632 | 17.9056 | 17.4971 | 17.4942 | 17.253 | 17.253 | 17.253 | 17.253 | 17.253 | 17.253
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 17.5788 | 16.8577 | 16.0521 | 15.6456 | 15.2788 | 15.1392 | 14.7316 | 14.7316 | 14.7316 | 14.7316 | 14.7316 | 14.7316
|  |  | Selected |  |  | 70% |  | 18.3529 | 17.7672 | 16.7755 | 16.3236 | 15.9443 | 15.8457 | 15.488 | 15.488 | 15.488 | 15.488 | 15.488 | 15.488
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 18.3529 | 17.7672 | 16.7755 | 16.3236 | 15.9443 | 15.8457 | 15.488 | 15.488 | 15.488 | 15.488 | 15.488 | 15.488
|  |  | N-3 |  |  |  |  | 18.3529 | 17.7672 | 16.7755 | 16.3236 | 15.9443 | 15.8457 | 15.488 | 15.488 | 15.488 | 15.488 | 15.488 | 15.488
|  |  | N-4 |  |  |  |  | 18.3529 | 17.7672 | 16.7755 | 16.3236 | 15.9443 | 15.8457 | 15.488 | 15.488 | 15.488 | 15.488 | 15.488 | 15.488
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 385037.9582 | 372750.6577 | 351944.9594 | 342463.9069 | 334507.556 | 332438.7453 | 324934.8221 | 324934.8221 | 324934.8221 | 324934.8221 | 324934.8221 | 324934.8221
|  |  | N-1 |  |  | Major |  | 385037.9582 | 372750.6577 | 351944.9594 | 342463.9069 | 334507.556 | 332438.7453 | 324934.8221 | 324934.8221 | 324934.8221 | 324934.8221 | 324934.8221 | 324934.8221
|  |  | N-2 |  |  | Catastrophic |  | 11551138.7472 | 11182519.7316 | 10558348.7822 | 10273917.2077 | 10035226.6789 | 9973162.358 | 9748044.6624 | 9748044.6624 | 9748044.6624 | 9748044.6624 | 9748044.6624 | 9748044.6624
|  |  | N-3 |  |  | Catastrophic |  | 11551138.7472 | 11182519.7316 | 10558348.7822 | 10273917.2077 | 10035226.6789 | 9973162.358 | 9748044.6624 | 9748044.6624 | 9748044.6624 | 9748044.6624 | 9748044.6624 | 9748044.6624
|  |  | N-4 |  |  | Catastrophic |  | 11551138.7472 | 11182519.7316 | 10558348.7822 | 10273917.2077 | 10035226.6789 | 9973162.358 | 9748044.6624 | 9748044.6624 | 9748044.6624 | 9748044.6624 | 9748044.6624 | 9748044.6624
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 15.46% | 16.38% | 17.37% | 18.42% | 19.53% | 20.72% | 21.98% | 23.33% | 24.76% | 26.29% | 27.91% | 29.64%
|  |  | Major |  |  |  |  | 0.0831% | 0.08808% | 0.09337% | 0.09901% | 0.105% | 0.1114% | 0.1182% | 0.1254% | 0.1331% | 0.1413% | 0.1501% | 0.1593%
|  |  | Catastrophic |  |  |  |  | 0.0831% | 0.08808% | 0.09337% | 0.09901% | 0.105% | 0.1114% | 0.1182% | 0.1254% | 0.1331% | 0.1413% | 0.1501% | 0.1593%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 57131.8114 | 58622.1016 | 58678.6996 | 60544.6129 | 62720.8291 | 66122.7434 | 68573.3119 | 72771.1311 | 77240.5951 | 81999.7905 | 87068.0294 | 92449.5257
|  |  | Network Performance |  |  | Major |  | 307.1603 | 315.1726 | 315.4769 | 325.5087 | 337.2088 | 355.4986 | 368.6737 | 391.2426 | 415.272 | 440.8591 | 468.1077 | 497.0405
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 71414.7643 | 73277.627 | 73348.3745 | 75680.7661 | 78401.0364 | 82653.4293 | 85716.6399 | 90963.9139 | 96550.7439 | 102499.7381 | 108835.0367 | 115561.9072
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 383.9503 | 393.9657 | 394.3461 | 406.8858 | 421.5109 | 444.3733 | 460.8421 | 489.0533 | 519.09 | 551.0739 | 585.1346 | 621.3006
|  |  | Other significant risks |  |  | Significant |  | 25516.4615 | 27045.1233 | 28671.587 | 30402.3182 | 32244.2188 | 34204.6562 | 36291.4959 | 38513.1348 | 40878.5381 | 43397.2778 | 46079.5745 | 48927.6585
|  |  | Other major risks |  |  | Major |  | 1849.8866 | 1960.7112 | 2078.6262 | 2204.1004 | 2337.634 | 2479.7614 | 2631.0526 | 2792.1165 | 2963.603 | 3146.206 | 3340.6665 | 3547.1463
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 6621.6234 | 6621.6234 | 6621.6234 | 6621.6234 | 6621.6234 | 6621.6234 | 6621.6234 | 6621.6234 | 6621.6234 | 6621.6234 | 6621.6234 | 6621.6234
|  |  | Subtotal |  |  |  |  | 163225.6579 | 168236.3248 | 170108.7336 | 176185.8154 | 183084.0614 | 192882.0856 | 200663.6396 | 212542.2156 | 225189.4654 | 238656.5687 | 252998.1728 | 268226.2021
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 186524.6018 | 950342.846 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 42300.6143
|  |  | Post-replacement opex |  |  | 1398.9345
|  |  | Total annuity |  |  | 43699.5488
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 163225.6579 | 168236.3248 | 170108.7336 | 176185.8154 | 183084.0614 | 192882.0856 | 200663.6396 | 212542.2156 | 225189.4654 | 238656.5687 | 252998.1728 | 268226.2021
|  |  | Annualised cost |  |  |  |  | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario C
Powercor - Inglewood Regulator Replacement Risk Monetisation Model
Scenario C | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario C: Consequence calculation
Consequence calculation
|  | Scenario |  |  | C
|  |  | PoF |  | 110%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 15604169.8866 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 14041229.8181 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 1389504.6584 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 982570.1522 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 520138.9962 | 0 | 0 | 0 | 0 | 96% | 499333.4364 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 100% | 28915.7357 | 28915.7357
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 1389504.6584 | 0 | 100% | 1389504.6584 | 1389504.6584
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 953161.44 | 100% | 953161.44 | 953161.44
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 15604169.8866 | 0 | 7146285.8595 | 0 | 0 | 4% | 910018.2298 | 285851.4344
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 520138.9962 | 0 | 0 | 0 | 0 | 96% | 499333.4364 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 8093.0952 | 0 | 100% | 8093.0952 | 8093.0952
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 69874.1883 | 100% | 69874.1883 | 69874.1883
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 15604169.8866 | 0 | 1417913.861 | 0 | 0 | 4% | 680883.3499 | 56716.5544
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 16124308.8828 | 8261.6388 | 1474907.4893 | 8093.0952 | 69874.1883 | 7.483% | 1323439.3369 | 199939.1051
[5 empty] | 2 | Major |  | 16124308.8828 | 28915.7357 | 7203279.4878 | 1389504.6584 | 953161.44 | 14.93% | 3837927.1286 | 2714426.8968
[5 empty] | 3 | Catastrophic |  | 15604169.8866 | 28915.7357 | 14098223.4464 | 1389504.6584 | 982570.1522 | 0% | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 5161366.4655; 2026: 2914366.0018
Scenario C: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 20
|  |  | N-1 Rating before transfers, MVA |  |  | 20
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 22.281 | 21.9828 | 20.4067 | 19.7904 | 19.3389 | 19.3358 | 19.0691 | 19.0691 | 19.0691 | 19.0691 | 19.0691 | 19.0691
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 19.4292 | 18.6323 | 17.7418 | 17.2925 | 16.8871 | 16.7328 | 16.2824 | 16.2824 | 16.2824 | 16.2824 | 16.2824 | 16.2824
|  |  | Selected |  |  | 70% |  | 20.2847 | 19.6374 | 18.5413 | 18.0418 | 17.6227 | 17.5137 | 17.1184 | 17.1184 | 17.1184 | 17.1184 | 17.1184 | 17.1184
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0.28474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0.28474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 20.2847 | 19.6374 | 18.5413 | 18.0418 | 17.6227 | 17.5137 | 17.1184 | 17.1184 | 17.1184 | 17.1184 | 17.1184 | 17.1184
|  |  | N-3 |  |  |  |  | 20.2847 | 19.6374 | 18.5413 | 18.0418 | 17.6227 | 17.5137 | 17.1184 | 17.1184 | 17.1184 | 17.1184 | 17.1184 | 17.1184
|  |  | N-4 |  |  |  |  | 20.2847 | 19.6374 | 18.5413 | 18.0418 | 17.6227 | 17.5137 | 17.1184 | 17.1184 | 17.1184 | 17.1184 | 17.1184 | 17.1184
VCR at risk
Average load at risk (pu)
|  |  |  | Unserved energy day 1 |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Unserved energy day 1 |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 7301.2707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 520138.9962 | 503540.3622 | 475434.4188 | 462626.6813 | 451878.6282 | 449083.919 | 438947.0404 | 438947.0404 | 438947.0404 | 438947.0404 | 438947.0404 | 438947.0404
|  |  | N-1 |  |  | Major |  | 520138.9962 | 503540.3622 | 475434.4188 | 462626.6813 | 451878.6282 | 449083.919 | 438947.0404 | 438947.0404 | 438947.0404 | 438947.0404 | 438947.0404 | 438947.0404
|  |  | N-2 |  |  | Catastrophic |  | 15604169.8866 | 15106210.8656 | 14263032.5654 | 13878800.4384 | 13556358.8469 | 13472517.5713 | 13168411.2106 | 13168411.2106 | 13168411.2106 | 13168411.2106 | 13168411.2106 | 13168411.2106
|  |  | N-3 |  |  | Catastrophic |  | 15604169.8866 | 15106210.8656 | 14263032.5654 | 13878800.4384 | 13556358.8469 | 13472517.5713 | 13168411.2106 | 13168411.2106 | 13168411.2106 | 13168411.2106 | 13168411.2106 | 13168411.2106
|  |  | N-4 |  |  | Catastrophic |  | 15604169.8866 | 15106210.8656 | 14263032.5654 | 13878800.4384 | 13556358.8469 | 13472517.5713 | 13168411.2106 | 13168411.2106 | 13168411.2106 | 13168411.2106 | 13168411.2106 | 13168411.2106
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 18.89% | 20.02% | 21.23% | 22.51% | 23.87% | 25.32% | 26.87% | 28.51% | 30.26% | 32.13% | 34.11% | 36.22%
|  |  | Major |  |  |  |  | 0.1016% | 0.1076% | 0.1141% | 0.121% | 0.1283% | 0.1361% | 0.1445% | 0.1533% | 0.1627% | 0.1727% | 0.1834% | 0.1947%
|  |  | Catastrophic |  |  |  |  | 0.1016% | 0.1076% | 0.1141% | 0.121% | 0.1283% | 0.1361% | 0.1445% | 0.1533% | 0.1627% | 0.1727% | 0.1834% | 0.1947%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 94328.7413 | 96789.3179 | 96882.7653 | 99963.5226 | 103556.6126 | 109173.4185 | 113219.4838 | 120150.386 | 127529.7935 | 135387.5684 | 143755.5963 | 152640.8349
|  |  | Network Performance |  |  | Major |  | 507.1438 | 520.3727 | 520.8751 | 537.4383 | 556.756 | 586.9539 | 608.7069 | 645.9698 | 685.6441 | 727.8902 | 772.8795 | 820.6496
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 117910.9266 | 120986.6473 | 121103.4566 | 124954.4033 | 129445.7657 | 136466.7731 | 141524.3547 | 150187.9825 | 159412.2418 | 169234.4604 | 179694.4954 | 190801.0436
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 633.9297 | 650.4658 | 651.0939 | 671.7979 | 695.945 | 733.6923 | 760.8836 | 807.4623 | 857.0551 | 909.8627 | 966.0994 | 1025.8121
|  |  | Other significant risks |  |  | Significant |  | 37770.3609 | 40033.1397 | 42440.6882 | 45002.5773 | 47729.023 | 50630.9313 | 53719.9446 | 57008.4924 | 60509.8452 | 64238.172 | 68208.6017 | 72424.4354
|  |  | Other major risks |  |  | Major |  | 2756.8847 | 2922.0464 | 3097.7751 | 3284.7691 | 3483.7743 | 3695.5866 | 3921.0558 | 4161.0891 | 4416.6553 | 4688.7884 | 4978.5928 | 5286.3094
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 8093.0952 | 8093.0952 | 8093.0952 | 8093.0952 | 8093.0952 | 8093.0952 | 8093.0952 | 8093.0952 | 8093.0952 | 8093.0952 | 8093.0952 | 8093.0952
|  |  | Subtotal |  |  |  |  | 262001.0823 | 269995.085 | 272789.7493 | 282507.6036 | 293560.9718 | 309380.4508 | 321847.5246 | 341054.4774 | 361504.3301 | 383279.8373 | 406469.3603 | 431092.1803
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 227974.5133 | 1161530.1451 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 51700.7508
|  |  | Post-replacement opex |  |  | 1709.8088
|  |  | Total annuity |  |  | 53410.5597
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 262001.0823 | 269995.085 | 272789.7493 | 282507.6036 | 293560.9718 | 309380.4508 | 321847.5246 | 341054.4774 | 361504.3301 | 383279.8373 | 406469.3603 | 431092.1803
|  |  | Annualised cost |  |  |  |  | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario D
Powercor - Inglewood Regulator Replacement Risk Monetisation Model
Scenario D | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario D: Consequence calculation
Consequence calculation
|  | Scenario |  |  | D
|  |  | PoF |  | 110%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 15604169.8866 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 11488278.9421 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 1136867.4478 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 982570.1522 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 520138.9962 | 0 | 0 | 0 | 0 | 96% | 499333.4364 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 100% | 28915.7357 | 28915.7357
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 1136867.4478 | 0 | 100% | 1136867.4478 | 1136867.4478
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 953161.44 | 100% | 953161.44 | 953161.44
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 15604169.8866 | 0 | 5846961.1578 | 0 | 0 | 4% | 858045.2418 | 233878.4463
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 520138.9962 | 0 | 0 | 0 | 0 | 96% | 499333.4364 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 6621.6234 | 0 | 100% | 6621.6234 | 6621.6234
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 69874.1883 | 100% | 69874.1883 | 69874.1883
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 15604169.8866 | 0 | 1160111.3408 | 0 | 0 | 4% | 670571.2491 | 46404.4536
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 16124308.8828 | 8261.6388 | 1206742.4913 | 6621.6234 | 69874.1883 | 7.472% | 1301293.2863 | 177793.0545
[5 empty] | 2 | Major |  | 16124308.8828 | 28915.7357 | 5893592.3082 | 1136867.4478 | 953161.44 | 14.6% | 3522954.452 | 2399454.2202
[5 empty] | 3 | Catastrophic |  | 15604169.8866 | 28915.7357 | 11534910.0925 | 1136867.4478 | 982570.1522 | 0% | 0 | 0
[5 empty] | Subtotal |  |  | 2025: 4824247.7384; 2026: 2577247.2747
Scenario D: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 1
|  | N-rating, MVA |  |  |  | 20
|  |  | N-1 Rating before transfers, MVA |  |  | 20
|  |  | N-2 Rating before transfers, MVA |  |  | 0
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 22.281 | 21.9828 | 20.4067 | 19.7904 | 19.3389 | 19.3358 | 19.0691 | 19.0691 | 19.0691 | 19.0691 | 19.0691 | 19.0691
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 19.4292 | 18.6323 | 17.7418 | 17.2925 | 16.8871 | 16.7328 | 16.2824 | 16.2824 | 16.2824 | 16.2824 | 16.2824 | 16.2824
|  |  | Selected |  |  | 70% |  | 20.2847 | 19.6374 | 18.5413 | 18.0418 | 17.6227 | 17.5137 | 17.1184 | 17.1184 | 17.1184 | 17.1184 | 17.1184 | 17.1184
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0.28474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0.28474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 20.2847 | 19.6374 | 18.5413 | 18.0418 | 17.6227 | 17.5137 | 17.1184 | 17.1184 | 17.1184 | 17.1184 | 17.1184 | 17.1184
|  |  | N-3 |  |  |  |  | 20.2847 | 19.6374 | 18.5413 | 18.0418 | 17.6227 | 17.5137 | 17.1184 | 17.1184 | 17.1184 | 17.1184 | 17.1184 | 17.1184
|  |  | N-4 |  |  |  |  | 20.2847 | 19.6374 | 18.5413 | 18.0418 | 17.6227 | 17.5137 | 17.1184 | 17.1184 | 17.1184 | 17.1184 | 17.1184 | 17.1184
VCR at risk
Average load at risk (pu)
|  |  |  | Unserved energy day 1 |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Unserved energy day 1 |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) |  |  |  | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 7301.2707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 520138.9962 | 503540.3622 | 475434.4188 | 462626.6813 | 451878.6282 | 449083.919 | 438947.0404 | 438947.0404 | 438947.0404 | 438947.0404 | 438947.0404 | 438947.0404
|  |  | N-1 |  |  | Major |  | 520138.9962 | 503540.3622 | 475434.4188 | 462626.6813 | 451878.6282 | 449083.919 | 438947.0404 | 438947.0404 | 438947.0404 | 438947.0404 | 438947.0404 | 438947.0404
|  |  | N-2 |  |  | Catastrophic |  | 15604169.8866 | 15106210.8656 | 14263032.5654 | 13878800.4384 | 13556358.8469 | 13472517.5713 | 13168411.2106 | 13168411.2106 | 13168411.2106 | 13168411.2106 | 13168411.2106 | 13168411.2106
|  |  | N-3 |  |  | Catastrophic |  | 15604169.8866 | 15106210.8656 | 14263032.5654 | 13878800.4384 | 13556358.8469 | 13472517.5713 | 13168411.2106 | 13168411.2106 | 13168411.2106 | 13168411.2106 | 13168411.2106 | 13168411.2106
|  |  | N-4 |  |  | Catastrophic |  | 15604169.8866 | 15106210.8656 | 14263032.5654 | 13878800.4384 | 13556358.8469 | 13472517.5713 | 13168411.2106 | 13168411.2106 | 13168411.2106 | 13168411.2106 | 13168411.2106 | 13168411.2106
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 18.89% | 20.02% | 21.23% | 22.51% | 23.87% | 25.32% | 26.87% | 28.51% | 30.26% | 32.13% | 34.11% | 36.22%
|  |  | Major |  |  |  |  | 0.1016% | 0.1076% | 0.1141% | 0.121% | 0.1283% | 0.1361% | 0.1445% | 0.1533% | 0.1627% | 0.1727% | 0.1834% | 0.1947%
|  |  | Catastrophic |  |  |  |  | 0.1016% | 0.1076% | 0.1141% | 0.121% | 0.1283% | 0.1361% | 0.1445% | 0.1533% | 0.1627% | 0.1727% | 0.1834% | 0.1947%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 94328.7413 | 96789.3179 | 96882.7653 | 99963.5226 | 103556.6126 | 109173.4185 | 113219.4838 | 120150.386 | 127529.7935 | 135387.5684 | 143755.5963 | 152640.8349
|  |  | Network Performance |  |  | Major |  | 507.1438 | 520.3727 | 520.8751 | 537.4383 | 556.756 | 586.9539 | 608.7069 | 645.9698 | 685.6441 | 727.8902 | 772.8795 | 820.6496
|  |  | Network Performance |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 117910.9266 | 120986.6473 | 121103.4566 | 124954.4033 | 129445.7657 | 136466.7731 | 141524.3547 | 150187.9825 | 159412.2418 | 169234.4604 | 179694.4954 | 190801.0436
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 633.9297 | 650.4658 | 651.0939 | 671.7979 | 695.945 | 733.6923 | 760.8836 | 807.4623 | 857.0551 | 909.8627 | 966.0994 | 1025.8121
|  |  | Other significant risks |  |  | Significant |  | 33586.7655 | 35598.9099 | 37739.7888 | 40017.9128 | 42442.3666 | 45022.848 | 47769.7099 | 50694.005 | 53807.5341 | 57122.8965 | 60653.5456 | 64402.4169
|  |  | Other major risks |  |  | Major |  | 2436.9853 | 2582.9823 | 2738.32 | 2903.6159 | 3079.5292 | 3266.7635 | 3466.0701 | 3678.2508 | 3904.1619 | 4144.7177 | 4400.8942 | 4672.9044
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annual opex, pre-replacement |  |  |  |  | 6621.6234 | 6621.6234 | 6621.6234 | 6621.6234 | 6621.6234 | 6621.6234 | 6621.6234 | 6621.6234 | 6621.6234 | 6621.6234 | 6621.6234 | 6621.6234
|  |  | Subtotal |  |  |  |  | 256026.1157 | 263750.3193 | 266257.9229 | 275670.3141 | 286398.5984 | 301872.0726 | 313970.8323 | 332785.6798 | 352818.0538 | 374149.0192 | 396865.1338 | 420985.2849
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 0 | 186524.6018 | 950342.846 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 0% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 42300.6143
|  |  | Post-replacement opex |  |  | 1398.9345
|  |  | Total annuity |  |  | 43699.5488
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 256026.1157 | 263750.3193 | 266257.9229 | 275670.3141 | 286398.5984 | 301872.0726 | 313970.8323 | 332785.6798 | 352818.0538 | 374149.0192 | 396865.1338 | 420985.2849
|  |  | Annualised cost |  |  |  |  | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Summary
Powercor - Inglewood Regulator Replacement Risk Monetisation Model
Summary |  |  |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Risk cost vs annualised cost
Risks vs benefits
|  | Year |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost | Scenario Base case | 208932.571 | 215328.0075 | 217637.7046 | 225403.6416 | 234228.2716 | 246812.2877 | 256766.2054 | 272034.1458 | 288290.0889 | 305599.8178 | 324033.5725 | 343606.6798
|  |  | Annualised cost | Scenario Base case | 48555.0542 | 48555.0542 | 48555.0542 | 48555.0542 | 48555.0542 | 48555.0542 | 48555.0542 | 48555.0542 | 48555.0542 | 48555.0542 | 48555.0542 | 48555.0542
|  |  | Risk cost | Scenario A | 168381.8073 | 173613.219 | 175720.4956 | 182047.5017 | 189211.7254 | 199292.8445 | 207375.7463 | 219575.1358 | 232563.9591 | 246394.7783 | 261123.7167 | 276763.0204
|  |  | Annualised cost | Scenario A | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597
|  |  | Risk cost | Scenario B | 163225.6579 | 168236.3248 | 170108.7336 | 176185.8154 | 183084.0614 | 192882.0856 | 200663.6396 | 212542.2156 | 225189.4654 | 238656.5687 | 252998.1728 | 268226.2021
|  |  | Annualised cost | Scenario B | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488
|  |  | Risk cost | Scenario C | 262001.0823 | 269995.085 | 272789.7493 | 282507.6036 | 293560.9718 | 309380.4508 | 321847.5246 | 341054.4774 | 361504.3301 | 383279.8373 | 406469.3603 | 431092.1803
|  |  | Annualised cost | Scenario C | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597 | 53410.5597
|  |  | Risk cost | Scenario D | 256026.1157 | 263750.3193 | 266257.9229 | 275670.3141 | 286398.5984 | 301872.0726 | 313970.8323 | 332785.6798 | 352818.0538 | 374149.0192 | 396865.1338 | 420985.2849
|  |  | Annualised cost | Scenario D | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488 | 43699.5488
Charts
End