## Output tables
Output tables
| $m | July 2018 to October 2019 | Modelled annual impact
|  | 8 REFCL ZSs | 22 REFCL ZS
| Value of unserved energy | 3.1284 | 20.6638
| Option | Description | Value of unserved energy, $m
| 0 | Do nothing - do not replace traditional ACRs with smart ACRs | 94.7207
| 1 | Mitigate reliability impacts - replace traditional ACRs with smart ACRs on REFCL network | 50.4304
| Zone substation | No. of events, July 2018 to October 2019 | Additional unserved energy, mwh | Value of additional unserved energy, $m
| CLC | 8 | 15.4193 | 0.689
| GSB | 7 | 14.9395 | 0.66756
| WIN | 2 | 2.4746 | 0.11058
| EHK | 4 | 16.1708 | 0.72258
| MRO | 3 | 5.3751 | 0.24018
| CMN | 2 | 8.4158 | 0.37605
| CDN | 4 | 2.9842 | 0.13334
| WND | 8 | 4.2316 | 0.18909
| Total | 38 | 70.011 | 3.1284
| Tranche | Additional CMOS with REFCL and traditional protection | Additional unserved energy with REFCL | Value of additional unserved energy with REFCL | Value of additional unserved energy with REFCL and smart ACRS | Value of energy saved by installing smart ACRs
|  | minutes p.a. | mwh p.a. | $m p.a. | $m p.a. | $m p.a.
| Tranche 1 ZSS (excl. CLC) | 6931889.067 | 152.978 | 6.8357 | 3.9992 | 2.8364
| Tranche 2 ZSS (incl. CLC) | 9663185.4343 | 213.254 | 9.529 | 4.3797 | 5.1493
| Tranche 3 ZSS | 4359623.8105 | 96.211 | 4.2991 | 2.8452 | 1.4539
| Total | 20954698.3118 | 462.443 | 20.6638 | 11.2242 | 9.4396
|  | Value of energy saved, $m | Value of energy saved, $m
|  | 2021-2026 | 2026-2031
| Tranche 1 | 14.1822 | 14.1822
| Tranche 2 | 25.7464 | 25.7464
| Tranche 3 | 4.3616 | 7.2694
| Total | 44.2903 | 47.1981
| $m | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2021-2026
| Value of saved energy | 7.9857 | 7.9857 | 9.4396 | 9.4396 | 9.4396 | 44.2903
End

## 2021-2026 Unserved Energy
Key assumptions
Key inputs
| Network Energy MWh | 9415128.2345
| 2018 Average Cust Numbers | 811694
| Value of customer reliability (June $2021/MWh) | 44683.9425
Scenarios: Customer minutes off supply (CMOS)
|  | Base Case |  |  |  |  | Current Operational REFCL Practices |  |  |  |  | Operational Practices With Smart ACR's
|  | 5 Year Average Base Performance Pre REFCL 11/12' to 15/16' |  |  |  |  | T1 Performance Less CLC ZSS - With Current REFCL Protection 11/12' to 15/16' |  |  |  |  | T1 Performance - Less CLC - With REFCL & Smart ACR's 11/12' to 15/16'
| Outage Level | Urban | Rural Short | Rural Long | Total |  | Urban | Rural Short | Rural Long | Total |  | Urban | Rural Short | Rural Long | Total
| 22KV Dist Sub Outage | 68814.4 | 241269.8 | 484006.2 | 794090.4 |  | 55120.3344 | 193257.1098 | 387688.9662 | 636066.4104 |  | 55120.3344 | 193257.1098 | 387688.9662 | 636066.4104
| HV 22kv ACR Outage | 0 | 528337 | 4075888 | 4604225 |  | 0 | 344343.6397 | 2656460.004 | 3000803.6437 |  | 0 | 915248.7518 | 5908572.3183 | 6823821.0701
| HV 22KV CB Outage | 193029.6 | 1021329.6 | 5374548 | 6588907.2 |  | 170101.906 | 2068306.6677 | 14568093.0511 | 16806501.6248 |  | 152756.0852 | 1342242.1112 | 8612119.7303 | 10107117.9267
| HV 22KV Line Outage | 25408.8 | 551531.2 | 2827325.8 | 3404265.8 |  | 14032.0098 | 304583.1052 | 1561390.673 | 1880005.788 |  | 14032.0098 | 304583.1052 | 1561390.673 | 1880005.788
| Subtotal | 287252.8 | 2342467.6 | 12761768 | 15391488.4 |  | 239254.2502 | 2910490.5224 | 19173632.6944 | 22323377.467 |  | 221908.4294 | 2755331.078 | 16469771.6878 | 19447011.1953
|  | 5 Year Average Base Performance Pre REFCL 14/15' to 18/19' |  |  |  |  | T2 Performance + CLC ZSS - With Current REFCL Protection 14/15' to 18/19' |  |  |  |  | T2 Performance + CLC ZSS - With REFCL & Smart ACR's 14/15' to 18/19'
| Outage Level | Urban | Rural Short | Rural Long | Total |  | Urban | Rural Short | Rural Long | Total |  | Urban | Rural Short | Rural Long | Total
| 22KV Dist Sub Outage | 335473.8 | 452416.2 | 728322 | 1516212 |  | 268714.5138 | 362385.3762 | 583385.922 | 1214485.812 |  | 268714.5138 | 362385.3762 | 583385.922 | 1214485.812
| HV 22kv ACR Outage | 110652 | 1118584.6 | 7734594.2 | 8963830.8 |  | 72117.441 | 729037.5131 | 5041021.7699 | 5842176.7239 |  | 318738.6186 | 1711650.165 | 9012456.65 | 11042845.4336
| HV 22KV CB Outage | 1534726 | 2778215.8 | 5194006.6 | 9506948.4 |  | 1585236.1938 | 4430228.9071 | 18691613.5601 | 24707078.6609 |  | 1322113.3239 | 3074393.4487 | 9888139.2313 | 14284646.0039
| HV 22KV Line Outage | 288672 | 579578.8 | 3852161.4 | 4720412.2 |  | 159419.112 | 320072.3923 | 2127356.1331 | 2606847.6374 |  | 159419.112 | 320072.3923 | 2127356.1331 | 2606847.6374
| Subtotal | 2269523.8 | 4928795.4 | 17509084.2 | 24707403.4 |  | 2085487.2606 | 5841724.1886 | 26443377.3851 | 34370588.8343 |  | 2068985.5683 | 5468501.3822 | 21611337.9364 | 29148824.8869
|  | 5 Year Average Base Performance Pre REFCL 14/15' to 18/19' |  |  |  |  | T3 Performance - With Current REFCL Protection 14/15' to 18/19' |  |  |  |  | T3 Performance - With REFCL & Smart ACR's 14/15' to 18/19'
| Outage Level | Urban | Rural Short | Rural Long | Total |  | Urban | Rural Short | Rural Long | Total |  | Urban | Rural Short | Rural Long | Total
| 22KV Dist Sub Outage | 435705.2 | 589821 | 525151.8 | 1550678 |  | 348999.8652 | 472446.621 | 420646.5918 | 1242093.078 |  | 348999.8652 | 472446.621 | 420646.5918 | 1242093.078
| HV 22kv ACR Outage | 585214.8 | 1151570.2 | 2799098.8 | 4535883.8 |  | 381413.7459 | 750535.8779 | 1824312.6429 | 2956262.2666 |  | 877478.949 | 2032673.8552 | 3503269.4075 | 6413422.2117
| HV 22KV CB Outage | 1462551.2 | 1900736.8 | 599494.2 | 3962782.2 |  | 1779718.5532 | 5030124.0219 | 4863451.6511 | 11673294.2263 |  | 1366468.1489 | 3048956.7354 | 2326352.2305 | 6741777.1148
| HV 22KV Line Outage | 325239.8 | 1698617.2 | 1242880.6 | 3266737.6 |  | 179613.6795 | 938061.3487 | 686380.8113 | 1804055.8396 |  | 179613.6795 | 938061.3487 | 686380.8113 | 1804055.8396
| Subtotal | 2808711 | 5340745.2 | 5166625.4 | 13316081.6 |  | 2689745.8438 | 7191167.8695 | 7794791.6972 | 17675705.4105 |  | 2772560.6427 | 6492138.5603 | 6936649.0411 | 16201348.2441
Energy not supplied
| Scenario | Unplanned CMOS Base Case | Base Case Unplanned Lost MWhs | Unplanned CMOS Current Operational REFCL Practices | Current Ops Practices Unplanned Lost MWhs | Unplanned CMOS Operational Practices With Smart ACRs | Smart ACRs Unplanned Lost MWhs
| Tranche 1 (Less CLC) | 15391488.4 | 339.672 | 22323377.467 | 492.65 | 19447011.1953 | 429.172
| Tranche 2 + CLC | 24707403.4 | 545.263 | 34370588.8343 | 758.517 | 29148824.8869 | 643.279
| Tranche 3 | 13316081.6 | 293.87 | 17675705.4105 | 390.081 | 16201348.2441 | 357.544
Value of energy saved
| VCR $ | REFCLs | Smart ACRs | Value of energy saved | Residual
| Tranche 1 | 6835660.1513 | 3999212.8512 | 2836447.3002 | 3999212.8512
| Tranche 2 | 9529029.4677 | 4379741.3052 | 5149288.1625 | 4379741.3052
| Tranche 3 | 4299086.7891 | 2845205.3529 | 1453881.4362 | 2845205.3529
| VCR $m | REFCLs | Smart ACRs | Value of energy saved | Residual
| Tranche 1 | 6.8357 | 3.9992 | 2.8364 | 3.9992
| Tranche 2 | 9.529 | 4.3797 | 5.1493 | 4.3797
| Tranche 3 | 4.2991 | 2.8452 | 1.4539 | 2.8452
| Total | 20.6638 | 11.2242 | 9.4396 | 11.2242
| VCR Comparison | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | Total
| REFCL | 16.3647 | 16.3647 | 20.6638 | 20.6638 | 20.6638 | 94.7207
| Smart ACR | 8.379 | 8.379 | 11.2242 | 11.2242 | 11.2242 | 50.4304
| Value of energy saved | 7.9857 | 7.9857 | 9.4396 | 9.4396 | 9.4396 | 44.2903
Other Reliability Data
[6 empty] | Current REFCL Outages |  |  | Outages Without REFCL
| Order | Feeder | Zone Substation | Order Start Date |  | Custs Affected Sustained | Unplanned Lost MWh's |  | New Cust Affected Sustained | New CMOS | Unplanned Lost MWh's | Variance | Comments
| F-12998-b | GSB014 | GSB | 2018-07-04 03:49 |  | 2019 | 2.4551 |  | 679 | 56120 | 1.2385 | 1.2166
| F-13195-b | GSB014 | GSB | 2018-07-23 03:44 |  | 2024 | 9.2937 |  | 679 | 211914 | 4.6767 | 4.617
| F-14011-b | CDN006 | CDN | 2018-10-18 20:04 |  | 988 | 1.5487 |  | 554 | 59025 | 1.3026 | 0.24609
| F-172-c | WND022 | WND | 2018-11-02 15:32 |  | 3317 | 3.8768 |  | 2236 | 177627 | 3.92 | 0
| F-126-d | CMN001 | CMN | 2018-12-02 00:22 |  | 4695 | 8.0014 |  | 996 | 115373 | 2.5461 | 5.4553
| F-14633-b | CMN003 | CMN | 2018-12-09 12:39 |  | 2935 | 7.4201 |  | 1176 | 202080 | 4.4597 | 2.9605
| F-14643-b | MRO005 | MRO | 2018-12-09 14:08 |  | 2065 | 4.1121 |  | 345 | 46696 | 1.0305 | 3.0816
| F-15274-b | CDN001 | CDN | 2019-01-24 17:01 |  | 1764 | 2.3872 |  | 0 | 0 | 0 | 2.3872 | Only a momentary outage with traditional protection
| F-15323-b | GSB011 | GSB | 2019-01-26 02:04 |  | 2376 | 2.626 |  | 264 | 19832 | 0.43767 | 2.1884
| F-15431-b | WND022 | WND | 2019-01-30 16:08 |  | 3352 | 6.1964 |  | 2236 | 280944 | 6.2001 | 0
| F-15434-b | WND024 | WND | 2019-01-30 16:18 |  | 2474 | 3.0823 |  | 525 | 44458 | 0.98113 | 2.1012
| F-15438-b | EHK024 | EHK | 2019-01-30 16:24 |  | 2147 | 6.9926 |  | 249 | 55121 | 1.2165 | 5.7761
| 1224779-1 | WND013 | WND | 2019-01-31 11:26 |  | 2694 | 0.59453 |  | 880 | 13200 | 0.29131 | 0.30323
| 1224779-1 | WND022 | WND | 2019-01-31 11:26 |  | 1971 | 0.43498 |  | 0 | 0 | 0 | 0.43498
| F-15530-b | EHK024 | EHK | 2019-02-03 08:09 |  | 1589 | 4.0988 |  | 249 | 43656 | 0.96344 | 3.1354
| F-15533-b | EHK024 | EHK | 2019-02-03 08:09 |  | 2145 | 11.632 |  | 692 | 255061 | 5.6289 | 6.0031
| F-15935-b | WND024 | WND | 2019-02-09 19:13 |  | 2475 | 1.7983 |  | 456 | 22519 | 0.49697 | 1.3013
| F-16051-b | MRO005 | MRO | 2019-02-18 20:03 |  | 2069 | 2.5853 |  | 345 | 29301 | 0.64664 | 1.9387
| F-16076-b | CLC006 | CLC | 2019-02-21 02:11 |  | 2728 | 0.12041 |  | 1 | 2 | 4.4138e-05 | 0.12036 | REFCL Testing
| F-16077-b | CLC002 | CLC | 2019-02-21 02:31 |  | 2942 | 2.3707 |  | 1 | 37 | 0.00081655 | 2.3699 | REFCL Testing
| F-16145-b | WIN011 | WIN | 2019-02-27 06:15 |  | 2139 | 3.4716 |  | 1215 | 134033 | 2.9579 | 0.51367
| F-16170-b | WND022 | WND | 2019-03-01 12:40 |  | 3177 | 1.1772 |  | 2236 | 56315 | 1.2428 | 0
| F-16237-b | CLC014 | CLC | 2019-03-05 04:24 |  | 2206 | 2.8719 |  | 1 | 59 | 0.0013021 | 2.8706 | REFCL Testing
| F-16295-b | CLC006 | CLC | 2019-03-07 12:25 |  | 2725 | 1.0549 |  | 1 | 18 | 0.00039724 | 1.0545 | REFCL Testing
| F-16479-b | WND013 | WND | 2019-03-24 09:06 |  | 2694 | 0.17836 |  | 880 | 3960 | 0.087392 | 0.090968
| F-16530-b | MRO005 | MRO | 2019-03-25 14:49 |  | 2073 | 0.43862 |  | 345 | 3795 | 0.083751 | 0.35487
| F-16625-b | CDN003 | CDN | 2019-03-31 11:14 |  | 1688 | 0.074504 |  | 2 | 4 | 8.8275e-05 | 0.074416
| F-16727-b | EHK024 | EHK | 2019-04-09 01:44 |  | 2148 | 2.4082 |  | 685 | 52200 | 1.152 | 1.2562
| F-16938-b | CDN006 | CDN | 2019-05-01 22:11 |  | 966 | 1.9779 |  | 554 | 77098 | 1.7015 | 0.27641
| F-17437-b | GSB013 | GSB | 2019-06-09 21:55 |  | 2448 | 1.1345 |  | 0 | 0 | 0 | 1.1345 | Only a momentary outage with traditional protection
| F-17590-b | GSB014 | GSB | 2019-06-29 13:16 |  | 2035 | 4.7558 |  | 679 | 71904 | 1.5868 | 3.169
| F-17624-b | CLC013 | CLC | 2019-06-29 22:31 |  | 2968 | 2.5722 |  | 1117 | 67020 | 1.4791 | 1.0931
| F-18363-b | WIN011 | WIN | 2019-07-10 18:02 |  | 2165 | 3.0778 |  | 536 | 50608 | 1.1169 | 1.961
| F-17706-b | GSB014 | GSB | 2019-07-12 00:30 |  | 2035 | 2.2465 |  | 679 | 50948 | 1.1244 | 1.1221
| F-17777-b | GSB014 | GSB | 2019-07-14 15:45 |  | 2036 | 2.9853 |  | 679 | 67670 | 1.4934 | 1.4919
| F-18135-b | CLC006 | CLC | 2019-08-13 05:50 |  | 2725 | 6.3984 |  | 1790 | 190451 | 4.203 | 2.1954
| F-17813-b | CLC014 | CLC | 2019-09-07 00:31 |  | 2206 | 4.0065 |  | 398 | 858 | 0.018935 | 3.9875
| F-18457-b | CLC006 | CLC | 2019-09-17 08:35 |  | 2748 | 2.1771 |  | 378 | 20355 | 0.44921 | 1.7279
| Subtotal |  |  |  |  | 89951 | 124.6348 |  | 24738 | 2480262 | 54.7364 | 70.011
End

## T1 Base
Global Inputs
E/L or SEF Faults Eliminated
|  | 22KV Dist Sub Outage | 18% | [%]
|  | HV 22kv ACR Outage | 20% | [%]
|  | HV 22KV CB Outage | 30% | [%]
|  | HV 22KV Line Outage | 30% | [%]
E/L or SEF Faults Escalated
|  | 22KV Dist Sub Outage | 2% | [%]
|  | HV 22kv ACR Outage | 15% | [%]
|  | HV 22KV CB Outage | 0% | [%]
|  | HV 22KV Line Outage | 15% | [%]
|  | No. of Years | 5 | [Yrs]
|  | % REFCL Availability | 99.5% | [%]
|  | Network Energy MWh | 9415128.2345 | [#]
|  | Average Customer Numbers | 811694 | [Customers - Matches Energy Supplied]
|  | From | 2011/2012 | [#]
|  | To | 2015/2016 | [#]
Number of Orders
[5 empty] | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  | [#] | 62 | 660 | 2016
|  | HV 22kv ACR Outage |  | [#] |  | 25 | 150
|  | HV 22KV CB Outage |  | [#] | 16 | 38 | 108
|  | HV 22KV Line Outage |  | [#] | 11 | 224 | 1035
CMOS - Customer Minutes off Supply
[5 empty] | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  | [Mins] | 344072 | 1206349 | 2420031
|  | HV 22kv ACR Outage |  | [Mins] |  | 2641685 | 20379440
|  | HV 22KV CB Outage |  | [Mins] | 965148 | 5106648 | 26872740
|  | HV 22KV Line Outage |  | [Mins] | 127044 | 2757656 | 14136629
Calculations
Annual Average Performance Before 2011/2012 - 2015/2016
|  | Number of order |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 12.4 | 132 | 403.2 | 547.6
|  | HV 22kv ACR Outage |  |  | 0 | 5 | 30 | 35
|  | HV 22KV CB Outage |  |  | 3.2 | 7.6 | 21.6 | 32.4
|  | HV 22KV Line Outage |  |  | 2.2 | 44.8 | 207 | 254
|  | CMOS |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 68814.4 | 241269.8 | 484006.2 | 794090.4
|  | HV 22kv ACR Outage |  |  | 0 | 528337 | 4075888 | 4604225
|  | HV 22KV CB Outage |  |  | 193029.6 | 1021329.6 | 5374548 | 6588907.2
|  | HV 22KV Line Outage |  |  | 25408.8 | 551531.2 | 2827325.8 | 3404265.8
|  | Average Cust Effected Per Event |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 5549.5484 | 1827.8015 | 1200.4122
|  | HV 22kv ACR Outage |  |  | 0 | 105667.4 | 135862.9333
|  | HV 22KV CB Outage |  |  | 60321.75 | 134385.4737 | 248821.6667
|  | HV 22KV Line Outage |  |  | 11549.4545 | 12310.9643 | 13658.5787
|  | Energy not supplied |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 1.519 | 5.325 | 10.681 | 17.525
|  | HV 22kv ACR Outage |  |  | 0 | 11.66 | 89.95 | 101.61
|  | HV 22KV CB Outage |  |  | 4.26 | 22.54 | 118.61 | 145.409
|  | HV 22KV Line Outage |  |  | 0.561 | 12.172 | 62.396 | 75.128
|  | Subtotal |  |  | 6.34 | 51.697 | 281.637 | 339.672
Annual Average Performance After
|  | No Events With REFCL Not In Service |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 0.062 | 0.66 | 2.016
|  | HV 22kv ACR Outage |  |  | 0 | 0.025 | 0.15
|  | HV 22KV CB Outage |  |  | 0.016 | 0.038 | 0.108
|  | HV 22KV Line Outage |  |  | 0.011 | 0.224 | 1.035
|  | # Faults Still Occurring With REFCL In Service |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 9.8704 | 105.072 | 320.9472
|  | HV 22kv ACR Outage |  |  | 0 | 3.2337 | 19.4025
|  | HV 22KV CB Outage |  |  | 2.2288 | 5.2934 | 15.0444
|  | HV 22KV Line Outage |  |  | 1.2039 | 24.5168 | 113.2807
|  | # E/L or SEF Faults Eliminated |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 2.2208 | 23.6412 | 72.2131
|  | HV 22kv ACR Outage |  |  | 0 | 0.995 | 5.97
|  | HV 22KV CB Outage |  |  | 0.9552 | 2.2686 | 6.4476
|  | HV 22KV Line Outage |  |  | 0.6567 | 13.3728 | 61.7895
|  | E/L or SEF Faults Escalated - CB Trip |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 0.24676 | 2.6268 | 8.0237
|  | HV 22kv ACR Outage |  |  | 0 | 0.74625 | 4.4775
|  | HV 22KV CB Outage |  |  | 0 | 0 | 0
|  | HV 22KV Line Outage |  |  | 0.32835 | 6.6864 | 30.8947
|  | Total # Events Occurring |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 9.9324 | 105.732 | 322.9632 | 438.6276
|  | HV 22kv ACR Outage |  |  | 0 | 3.2587 | 19.5525 | 22.8112
|  | HV 22KV CB Outage |  |  | 2.8199 | 15.3909 | 58.5483 | 76.7591
|  | HV 22KV Line Outage |  |  | 1.2149 | 24.7408 | 114.3157 | 140.2715
|  | CMOS |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 55120.3344 | 193257.1098 | 387688.9662 | 636066.4104
|  | HV 22kv ACR Outage |  |  | 0 | 344343.6397 | 2656460.004 | 3000803.6437
|  | HV 22KV CB Outage |  |  | 170101.906 | 2068306.6677 | 14568093.0511 | 16806501.6248
|  | HV 22KV Line Outage |  |  | 14032.0098 | 304583.1052 | 1561390.673 | 1880005.788
|  | Energy not supplied |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 1.216 | 4.265 | 8.556 | 14.037
|  | HV 22kv ACR Outage |  |  | 0 | 7.599 | 58.625 | 66.224
|  | HV 22KV CB Outage |  |  | 3.754 | 45.645 | 321.5 | 370.899
|  | HV 22KV Line Outage |  |  | 0.31 | 6.722 | 34.458 | 41.489
|  | Subtotal |  |  | 5.28 | 64.231 | 423.139 | 492.649
End

## T2 Base
Global Inputs
E/L or SEF Faults Eliminated
|  | 22KV Dist Sub Outage | 18% | [%]
|  | HV 22kv ACR Outage | 20% | [%]
|  | HV 22KV CB Outage | 30% | [%]
|  | HV 22KV Line Outage | 30% | [%]
E/L or SEF Faults Escalated
|  | 22KV Dist Sub Outage | 2% | [%]
|  | HV 22kv ACR Outage | 15% | [%]
|  | HV 22KV CB Outage | 0% | [%]
|  | HV 22KV Line Outage | 15% | [%]
|  | No. of Years | 5 | [Yrs]
|  | % REFCL Availability | 99.5% | [%]
|  | Network Energy MWh | 9415128.2345 | [#]
|  | Average Customer Numbers | 811694 | [Customers - Matches Energy Supplied]
|  | From | 2014/2015 | [#]
|  | To | 2018/2019 | [#]
Number of Orders
[5 empty] | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  | [#] | 357 | 840 | 3108
|  | HV 22kv ACR Outage |  | [#] | 3 | 35 | 340
|  | HV 22KV CB Outage |  | [#] | 39 | 63 | 103
|  | HV 22KV Line Outage |  | [#] | 36 | 230 | 1245
CMOS - Customer Minutes off Supply
[5 empty] | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  | [Mins] | 1677369 | 2262081 | 3641610
|  | HV 22kv ACR Outage |  | [Mins] | 553260 | 5592923 | 38672971
|  | HV 22KV CB Outage |  | [Mins] | 7673630 | 13891079 | 25970033
|  | HV 22KV Line Outage |  | [Mins] | 1443360 | 2897894 | 19260807
Calculations
Annual Average Performance Before 2014/2015 - 2018/2019
|  | Number of order |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 71.4 | 168 | 621.6 | 861
|  | HV 22kv ACR Outage |  |  | 0.6 | 7 | 68 | 75.6
|  | HV 22KV CB Outage |  |  | 7.8 | 12.6 | 20.6 | 41
|  | HV 22KV Line Outage |  |  | 7.2 | 46 | 249 | 302.2
|  | CMOS |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 335473.8 | 452416.2 | 728322 | 1516212
|  | HV 22kv ACR Outage |  |  | 110652 | 1118584.6 | 7734594.2 | 8963830.8
|  | HV 22KV CB Outage |  |  | 1534726 | 2778215.8 | 5194006.6 | 9506948.4
|  | HV 22KV Line Outage |  |  | 288672 | 579578.8 | 3852161.4 | 4720412.2
|  | Average Cust Effected Per Event |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 4698.5126 | 2692.9536 | 1171.6892
|  | HV 22kv ACR Outage |  |  | 184420 | 159797.8 | 113744.0324
|  | HV 22KV CB Outage |  |  | 196759.7436 | 220493.3175 | 252136.2427
|  | HV 22KV Line Outage |  |  | 40093.3333 | 12599.5391 | 15470.5277
|  | Energy not supplied |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 7.404 | 9.984 | 16.073 | 33.461
|  | HV 22kv ACR Outage |  |  | 2.442 | 24.686 | 170.693 | 197.821
|  | HV 22KV CB Outage |  |  | 33.87 | 61.312 | 114.625 | 209.807
|  | HV 22KV Line Outage |  |  | 6.371 | 12.791 | 85.013 | 104.174
|  | Subtotal |  |  | 50.087 | 108.773 | 386.404 | 545.263
Annual Average Performance After
|  | No Events With REFCL Not In Service |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 0.357 | 0.84 | 3.108
|  | HV 22kv ACR Outage |  |  | 0.003 | 0.035 | 0.34
|  | HV 22KV CB Outage |  |  | 0.039 | 0.063 | 0.103
|  | HV 22KV Line Outage |  |  | 0.036 | 0.23 | 1.245
|  | # Faults Still Occurring With REFCL In Service |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 56.8344 | 133.728 | 494.7936
|  | HV 22kv ACR Outage |  |  | 0.38805 | 4.5273 | 43.979
|  | HV 22KV CB Outage |  |  | 5.4327 | 8.7759 | 14.3479
|  | HV 22KV Line Outage |  |  | 3.9402 | 25.1735 | 136.2652
|  | # E/L or SEF Faults Eliminated |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 12.7877 | 30.0888 | 111.3286
|  | HV 22kv ACR Outage |  |  | 0.1194 | 1.393 | 13.532
|  | HV 22KV CB Outage |  |  | 2.3283 | 3.7611 | 6.1491
|  | HV 22KV Line Outage |  |  | 2.1492 | 13.731 | 74.3265
|  | E/L or SEF Faults Escalated - CB Trip |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 1.4209 | 3.3432 | 12.3698
|  | HV 22kv ACR Outage |  |  | 0.08955 | 1.0447 | 10.149
|  | HV 22KV CB Outage |  |  | 0 | 0 | 0
|  | HV 22KV Line Outage |  |  | 1.0746 | 6.8655 | 37.1632
|  | Total # Events Occurring |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 57.1914 | 134.568 | 497.9016 | 689.661
|  | HV 22kv ACR Outage |  |  | 0.39105 | 4.5623 | 44.319 | 49.2723
|  | HV 22KV CB Outage |  |  | 8.0567 | 20.0923 | 74.133 | 102.282
|  | HV 22KV Line Outage |  |  | 3.9762 | 25.4035 | 137.5102 | 166.8899
|  | CMOS |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 268714.5138 | 362385.3762 | 583385.922 | 1214485.812
|  | HV 22kv ACR Outage |  |  | 72117.441 | 729037.5131 | 5041021.7699 | 5842176.7239
|  | HV 22KV CB Outage |  |  | 1585236.1938 | 4430228.9071 | 18691613.5601 | 24707078.6609
|  | HV 22KV Line Outage |  |  | 159419.112 | 320072.3923 | 2127356.1331 | 2606847.6374
|  | Energy not supplied |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 5.93 | 7.997 | 12.875 | 26.802
|  | HV 22kv ACR Outage |  |  | 1.592 | 16.089 | 111.249 | 128.93
|  | HV 22KV CB Outage |  |  | 34.984 | 97.77 | 412.501 | 545.255
|  | HV 22KV Line Outage |  |  | 3.518 | 7.064 | 46.948 | 57.53
|  | Subtotal |  |  | 46.024 | 128.92 | 583.573 | 758.517
End

## T3 Base
Global Inputs
E/L or SEF Faults Eliminated
|  | 22KV Dist Sub Outage | 18% | [%]
|  | HV 22kv ACR Outage | 20% | [%]
|  | HV 22KV CB Outage | 30% | [%]
|  | HV 22KV Line Outage | 30% | [%]
E/L or SEF Faults Escalated
|  | 22KV Dist Sub Outage | 2% | [%]
|  | HV 22kv ACR Outage | 15% | [%]
|  | HV 22KV CB Outage | 0% | [%]
|  | HV 22KV Line Outage | 15% | [%]
|  | No. of Years | 5 | [Yrs]
|  | % REFCL Availability | 99.5% | [%]
|  | Network Energy MWh | 9415128.2345 | [#]
|  | Average Customer Numbers | 811694 | [Customers - Matches Energy Supplied]
|  | From | 2015/2016 | [#]
|  | To | 2018/2019 | [#]
Number of Orders
[5 empty] | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  | [#] | 440 | 1196 | 1521
|  | HV 22kv ACR Outage |  | [#] | 13 | 44 | 127
|  | HV 22KV CB Outage |  | [#] | 39 | 47 | 18
|  | HV 22KV Line Outage |  | [#] | 63 | 409 | 564
CMOS - Customer Minutes off Supply
[5 empty] | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  | [Mins] | 2178526 | 2949105 | 2625759
|  | HV 22kv ACR Outage |  | [Mins] | 2926074 | 5757851 | 13995494
|  | HV 22KV CB Outage |  | [Mins] | 7312756 | 9503684 | 2997471
|  | HV 22KV Line Outage |  | [Mins] | 1626199 | 8493086 | 6214403
Calculations
Annual Average Performance Before 2015/2016 - 2018/2019
|  | Number of order |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 88 | 239.2 | 304.2 | 631.4
|  | HV 22kv ACR Outage |  |  | 2.6 | 8.8 | 25.4 | 36.8
|  | HV 22KV CB Outage |  |  | 7.8 | 9.4 | 3.6 | 20.8
|  | HV 22KV Line Outage |  |  | 12.6 | 81.8 | 112.8 | 207.2
|  | CMOS |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 435705.2 | 589821 | 525151.8 | 1550678
|  | HV 22kv ACR Outage |  |  | 585214.8 | 1151570.2 | 2799098.8 | 4535883.8
|  | HV 22KV CB Outage |  |  | 1462551.2 | 1900736.8 | 599494.2 | 3962782.2
|  | HV 22KV Line Outage |  |  | 325239.8 | 1698617.2 | 1242880.6 | 3266737.6
|  | Average Cust Effected Per Event |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 4951.1955 | 2465.8069 | 1726.3373
|  | HV 22kv ACR Outage |  |  | 225082.6154 | 130860.25 | 110200.7402
|  | HV 22KV CB Outage |  |  | 187506.5641 | 202206.0426 | 166526.1667
|  | HV 22KV Line Outage |  |  | 25812.6825 | 20765.4914 | 11018.445
|  | Energy not supplied |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 9.615 | 13.017 | 11.589 | 34.222
|  | HV 22kv ACR Outage |  |  | 12.915 | 25.414 | 61.773 | 100.101
|  | HV 22KV CB Outage |  |  | 32.277 | 41.947 | 13.23 | 87.454
|  | HV 22KV Line Outage |  |  | 7.178 | 37.486 | 27.429 | 72.093
|  | Subtotal |  |  | 61.985 | 117.864 | 114.021 | 293.87
Annual Average Performance After
|  | No Events With REFCL Not In Service |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 0.44 | 1.196 | 1.521
|  | HV 22kv ACR Outage |  |  | 0.013 | 0.044 | 0.127
|  | HV 22KV CB Outage |  |  | 0.039 | 0.047 | 0.018
|  | HV 22KV Line Outage |  |  | 0.063 | 0.409 | 0.564
|  | # Faults Still Occurring With REFCL In Service |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 70.048 | 190.4032 | 242.1432
|  | HV 22kv ACR Outage |  |  | 1.6816 | 5.6914 | 16.4275
|  | HV 22KV CB Outage |  |  | 5.4327 | 6.5471 | 2.5074
|  | HV 22KV Line Outage |  |  | 6.8953 | 44.765 | 61.7298
|  | # E/L or SEF Faults Eliminated |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 15.7608 | 42.8407 | 54.4822
|  | HV 22kv ACR Outage |  |  | 0.5174 | 1.7512 | 5.0546
|  | HV 22KV CB Outage |  |  | 2.3283 | 2.8059 | 1.0746
|  | HV 22KV Line Outage |  |  | 3.7611 | 24.4173 | 33.6708
|  | E/L or SEF Faults Escalated - CB Trip |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 1.7512 | 4.7601 | 6.0536
|  | HV 22kv ACR Outage |  |  | 0.38805 | 1.3134 | 3.7909
|  | HV 22KV CB Outage |  |  | 0 | 0 | 0
|  | HV 22KV Line Outage |  |  | 1.8805 | 12.2086 | 16.8354
|  | Total # Events Occurring |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 70.488 | 191.5992 | 243.6642 | 505.7514
|  | HV 22kv ACR Outage |  |  | 1.6946 | 5.7354 | 16.5544 | 23.9844
|  | HV 22KV CB Outage |  |  | 9.4915 | 24.8762 | 29.2053 | 63.5731
|  | HV 22KV Line Outage |  |  | 6.9583 | 45.174 | 62.2938 | 114.4262
|  | CMOS |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 348999.8652 | 472446.621 | 420646.5918 | 1242093.078
|  | HV 22kv ACR Outage |  |  | 381413.7459 | 750535.8779 | 1824312.6429 | 2956262.2666
|  | HV 22KV CB Outage |  |  | 1779718.5532 | 5030124.0219 | 4863451.6511 | 11673294.2263
|  | HV 22KV Line Outage |  |  | 179613.6795 | 938061.3487 | 686380.8113 | 1804055.8396
|  | Energy not supplied |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 7.702 | 10.426 | 9.283 | 27.411
|  | HV 22kv ACR Outage |  |  | 8.417 | 16.563 | 40.26 | 65.241
|  | HV 22KV CB Outage |  |  | 39.276 | 111.009 | 107.33 | 257.615
|  | HV 22KV Line Outage |  |  | 3.964 | 20.702 | 15.148 | 39.813
|  | Subtotal |  |  | 59.359 | 158.7 | 172.021 | 390.08
End

## T1 Smart ACRs
Global Inputs
E/L or SEF Faults Eliminated
|  | 22KV Dist Sub Outage | 18% | [%]
|  | HV 22kv ACR Outage | 20% | [%]
|  | HV 22KV CB Outage | 30% | [%]
|  | HV 22KV Line Outage | 30% | [%]
E/L or SEF Faults Escalated
|  | 22KV Dist Sub Outage | 2% | [%]
|  | HV 22kv ACR Outage | 0% | [%]
|  | HV 22KV CB Outage | 0% | [%]
|  | HV 22KV Line Outage | 15% | [%]
|  | Trips by SMART ACRs | 50% | [%]
|  | No. of Years | 5 | [Yrs]
|  | % REFCL Availability | 99.5% | [%]
|  | Network Energy MWh | 9415128.2345 | [#]
|  | Average Customer Numbers | 811694 | [Customers - Matches Energy Supplied]
|  | From | 2011/2012 | [#]
|  | To | 2015/2016 | [#]
Number of Orders
[5 empty] | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  | [#] | 62 | 660 | 2016
|  | HV 22kv ACR Outage |  | [#] | 0 | 25 | 150
|  | HV 22KV CB Outage |  | [#] | 16 | 38 | 108
|  | HV 22KV Line Outage |  | [#] | 11 | 224 | 1035
CMOS - Customer Minutes off Supply
[5 empty] | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  | [Mins] | 344072 | 1206349 | 2420031
|  | HV 22kv ACR Outage |  | [Mins] | 0 | 2641685 | 20379440
|  | HV 22KV CB Outage |  | [Mins] | 965148 | 5106648 | 26872740
|  | HV 22KV Line Outage |  | [Mins] | 127044 | 2757656 | 14136629
Calculations
Annual Average Performance Before 2011/2012 - 2015/2016
|  | Number of order |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 12.4 | 132 | 403.2 | 547.6
|  | HV 22kv ACR Outage |  |  | 0 | 5 | 30 | 35
|  | HV 22KV CB Outage |  |  | 3.2 | 7.6 | 21.6 | 32.4
|  | HV 22KV Line Outage |  |  | 2.2 | 44.8 | 207 | 254
|  | CMOS |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 68814.4 | 241269.8 | 484006.2 | 794090.4
|  | HV 22kv ACR Outage |  |  | 0 | 528337 | 4075888 | 4604225
|  | HV 22KV CB Outage |  |  | 193029.6 | 1021329.6 | 5374548 | 6588907.2
|  | HV 22KV Line Outage |  |  | 25408.8 | 551531.2 | 2827325.8 | 3404265.8
|  | Average Cust Effected Per Event |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 5549.5484 | 1827.8015 | 1200.4122
|  | HV 22kv ACR Outage |  |  | 0 | 105667.4 | 135862.9333
|  | HV 22KV CB Outage |  |  | 60321.75 | 134385.4737 | 248821.6667
|  | HV 22KV Line Outage |  |  | 11549.4545 | 12310.9643 | 13658.5787
|  | Energy not supplied |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 1.519 | 5.325 | 10.681 | 17.525
|  | HV 22kv ACR Outage |  |  | 0 | 11.66 | 89.95 | 101.61
|  | HV 22KV CB Outage |  |  | 4.26 | 22.54 | 118.61 | 145.409
|  | HV 22KV Line Outage |  |  | 0.561 | 12.172 | 62.396 | 75.128
|  | Subtotal |  |  | 6.34 | 51.697 | 281.637 | 339.672
Annual Average Performance After
|  | No Events With REFCL Not In Service |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 0.062 | 0.66 | 2.016
|  | HV 22kv ACR Outage |  |  | 0 | 0.025 | 0.15
|  | HV 22KV CB Outage |  |  | 0.016 | 0.038 | 0.108
|  | HV 22KV Line Outage |  |  | 0.011 | 0.224 | 1.035
|  | # Faults Still Occurring With REFCL In Service |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 9.8704 | 105.072 | 320.9472
|  | HV 22kv ACR Outage |  |  | 0 | 3.98 | 23.88
|  | HV 22KV CB Outage |  |  | 2.2288 | 5.2934 | 15.0444
|  | HV 22KV Line Outage |  |  | 1.2039 | 24.5168 | 113.2807
|  | # E/L or SEF Faults Eliminated |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 2.2208 | 23.6412 | 72.2131
|  | HV 22kv ACR Outage |  |  | 0 | 0.995 | 5.97
|  | HV 22KV CB Outage |  |  | 0.9552 | 2.2686 | 6.4476
|  | HV 22KV Line Outage |  |  | 0.6567 | 13.3728 | 61.7895
|  | E/L or SEF Faults Escalated - CB Trip |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 0.24676 | 2.6268 | 8.0237
|  | HV 22kv ACR Outage |  |  | 0 | 0 | 0
|  | HV 22KV CB Outage |  |  | 0 | 0 | 0
|  | HV 22KV Line Outage |  |  | 0.32835 | 6.6864 | 30.8947
|  | Total # Events Occurring |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 9.9324 | 105.732 | 322.9632 | 438.6276
|  | HV 22kv ACR Outage |  |  | 0.28756 | 8.6616 | 43.4892 | 52.4384
|  | HV 22KV CB Outage |  |  | 2.5324 | 9.988 | 34.6116 | 47.132
|  | HV 22KV Line Outage |  |  | 1.2149 | 24.7408 | 114.3157 | 140.2715
|  | CMOS |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 55120.3344 | 193257.1098 | 387688.9662 | 636066.4104
|  | HV 22kv ACR Outage |  |  | 0 | 915248.7518 | 5908572.3183 | 6823821.0701
|  | HV 22KV CB Outage |  |  | 152756.0852 | 1342242.1112 | 8612119.7303 | 10107117.9267
|  | HV 22KV Line Outage |  |  | 14032.0098 | 304583.1052 | 1561390.673 | 1880005.788
|  | Energy not supplied |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 1.216 | 4.265 | 8.556 | 14.037
|  | HV 22kv ACR Outage |  |  | 0 | 20.198 | 130.395 | 150.593
|  | HV 22KV CB Outage |  |  | 3.371 | 29.622 | 190.059 | 223.052
|  | HV 22KV Line Outage |  |  | 0.31 | 6.722 | 34.458 | 41.489
|  | Subtotal |  |  | 4.897 | 60.807 | 363.468 | 429.171
End

## T2 Smart ACRs
Global Inputs
E/L or SEF Faults Eliminated
|  | 22KV Dist Sub Outage | 18% | [%]
|  | HV 22kv ACR Outage | 20% | [%]
|  | HV 22KV CB Outage | 30% | [%]
|  | HV 22KV Line Outage | 30% | [%]
E/L or SEF Faults Escalated
|  | 22KV Dist Sub Outage | 2% | [%]
|  | HV 22kv ACR Outage | 0% | [%]
|  | HV 22KV CB Outage | 0% | [%]
|  | HV 22KV Line Outage | 15% | [%]
|  | Trips by SMART ACRs | 50% | [%]
|  | No. of Years | 5 | [Yrs]
|  | % REFCL Availability | 99.5% | [%]
|  | Network Energy MWh | 9415128.2345 | [#]
|  | Average Customer Numbers | 811694 | [Customers - Matches Energy Supplied]
|  | From | 2011/2012 | [#]
|  | To | 2015/2016 | [#]
Number of Orders
[5 empty] | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  | [#] | 357 | 840 | 3108
|  | HV 22kv ACR Outage |  | [#] | 3 | 35 | 340
|  | HV 22KV CB Outage |  | [#] | 39 | 63 | 103
|  | HV 22KV Line Outage |  | [#] | 36 | 230 | 1245
CMOS - Customer Minutes off Supply
[5 empty] | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  | [Mins] | 1677369 | 2262081 | 3641610
|  | HV 22kv ACR Outage |  | [Mins] | 553260 | 5592923 | 38672971
|  | HV 22KV CB Outage |  | [Mins] | 7673630 | 13891079 | 25970033
|  | HV 22KV Line Outage |  | [Mins] | 1443360 | 2897894 | 19260807
Calculations
Annual Average Performance Before 2011/2012 - 2015/2016
|  | Number of order |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 71.4 | 168 | 621.6 | 861
|  | HV 22kv ACR Outage |  |  | 0.6 | 7 | 68 | 75.6
|  | HV 22KV CB Outage |  |  | 7.8 | 12.6 | 20.6 | 41
|  | HV 22KV Line Outage |  |  | 7.2 | 46 | 249 | 302.2
|  | CMOS |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 335473.8 | 452416.2 | 728322 | 1516212
|  | HV 22kv ACR Outage |  |  | 110652 | 1118584.6 | 7734594.2 | 8963830.8
|  | HV 22KV CB Outage |  |  | 1534726 | 2778215.8 | 5194006.6 | 9506948.4
|  | HV 22KV Line Outage |  |  | 288672 | 579578.8 | 3852161.4 | 4720412.2
|  | Average Cust Effected Per Event |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 4698.5126 | 2692.9536 | 1171.6892
|  | HV 22kv ACR Outage |  |  | 184420 | 159797.8 | 113744.0324
|  | HV 22KV CB Outage |  |  | 196759.7436 | 220493.3175 | 252136.2427
|  | HV 22KV Line Outage |  |  | 40093.3333 | 12599.5391 | 15470.5277
|  | Energy not supplied |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 7.404 | 9.984 | 16.073 | 33.461
|  | HV 22kv ACR Outage |  |  | 2.442 | 24.686 | 170.693 | 197.821
|  | HV 22KV CB Outage |  |  | 33.87 | 61.312 | 114.625 | 209.807
|  | HV 22KV Line Outage |  |  | 6.371 | 12.791 | 85.013 | 104.174
|  | Subtotal |  |  | 50.087 | 108.773 | 386.404 | 545.263
Annual Average Performance After
|  | No Events With REFCL Not In Service |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 0.357 | 0.84 | 3.108
|  | HV 22kv ACR Outage |  |  | 0.003 | 0.035 | 0.34
|  | HV 22KV CB Outage |  |  | 0.039 | 0.063 | 0.103
|  | HV 22KV Line Outage |  |  | 0.036 | 0.23 | 1.245
|  | # Faults Still Occurring With REFCL In Service |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 56.8344 | 133.728 | 494.7936
|  | HV 22kv ACR Outage |  |  | 0.4776 | 5.572 | 54.128
|  | HV 22KV CB Outage |  |  | 5.4327 | 8.7759 | 14.3479
|  | HV 22KV Line Outage |  |  | 3.9402 | 25.1735 | 136.2652
|  | # E/L or SEF Faults Eliminated |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 12.7877 | 30.0888 | 111.3286
|  | HV 22kv ACR Outage |  |  | 0.1194 | 1.393 | 13.532
|  | HV 22KV CB Outage |  |  | 2.3283 | 3.7611 | 6.1491
|  | HV 22KV Line Outage |  |  | 2.1492 | 13.731 | 74.3265
|  | E/L or SEF Faults Escalated - CB Trip |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 1.4209 | 3.3432 | 12.3698
|  | HV 22kv ACR Outage |  |  | 0 | 0 | 0
|  | HV 22KV CB Outage |  |  | 0 | 0 | 0
|  | HV 22KV Line Outage |  |  | 1.0746 | 6.8655 | 37.1632
|  | Total # Events Occurring |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 57.1914 | 134.568 | 497.9016 | 689.661
|  | HV 22kv ACR Outage |  |  | 1.7283 | 10.7113 | 79.2345 | 91.6742
|  | HV 22KV CB Outage |  |  | 6.7194 | 13.9432 | 39.2174 | 59.8801
|  | HV 22KV Line Outage |  |  | 3.9762 | 25.4035 | 137.5102 | 166.8899
|  | CMOS |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 268714.5138 | 362385.3762 | 583385.922 | 1214485.812
|  | HV 22kv ACR Outage |  |  | 318738.6186 | 1711650.165 | 9012456.65 | 11042845.4336
|  | HV 22KV CB Outage |  |  | 1322113.3239 | 3074393.4487 | 9888139.2313 | 14284646.0039
|  | HV 22KV Line Outage |  |  | 159419.112 | 320072.3923 | 2127356.1331 | 2606847.6374
|  | Energy not supplied |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 5.93 | 7.997 | 12.875 | 26.802
|  | HV 22kv ACR Outage |  |  | 7.034 | 37.774 | 198.894 | 243.702
|  | HV 22KV CB Outage |  |  | 29.177 | 67.848 | 218.219 | 315.245
|  | HV 22KV Line Outage |  |  | 3.518 | 7.064 | 46.948 | 57.53
|  | Subtotal |  |  | 45.659 | 120.683 | 476.936 | 643.279
End

## T3 Smart ACRs
Global Inputs
E/L or SEF Faults Eliminated
|  | 22KV Dist Sub Outage | 18% | [%]
|  | HV 22kv ACR Outage | 20% | [%]
|  | HV 22KV CB Outage | 30% | [%]
|  | HV 22KV Line Outage | 30% | [%]
E/L or SEF Faults Escalated
|  | 22KV Dist Sub Outage | 2% | [%]
|  | HV 22kv ACR Outage | 0% | [%]
|  | HV 22KV CB Outage | 0% | [%]
|  | HV 22KV Line Outage | 15% | [%]
|  | Trips by SMART ACRs | 50% | [%]
|  | No. of Years | 5 | [Yrs]
|  | % REFCL Availability | 99.5% | [%]
|  | Network Energy MWh | 9415128.2345 | [#]
|  | Average Customer Numbers | 811694 | [Customers - Matches Energy Supplied]
|  | From | 2011/2012 | [#]
|  | To | 2015/2016 | [#]
Number of Orders
[5 empty] | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  | [#] | 440 | 1196 | 1521
|  | HV 22kv ACR Outage |  | [#] | 13 | 44 | 127
|  | HV 22KV CB Outage |  | [#] | 39 | 47 | 18
|  | HV 22KV Line Outage |  | [#] | 63 | 409 | 564
CMOS - Customer Minutes off Supply
[5 empty] | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  | [Mins] | 2178526 | 2949105 | 2625759
|  | HV 22kv ACR Outage |  | [Mins] | 2926074 | 5757851 | 13995494
|  | HV 22KV CB Outage |  | [Mins] | 7312756 | 9503684 | 2997471
|  | HV 22KV Line Outage |  | [Mins] | 1626199 | 8493086 | 6214403
Calculations
Annual Average Performance Before 2011/2012 - 2015/2016
|  | Number of order |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 88 | 239.2 | 304.2 | 631.4
|  | HV 22kv ACR Outage |  |  | 2.6 | 8.8 | 25.4 | 36.8
|  | HV 22KV CB Outage |  |  | 7.8 | 9.4 | 3.6 | 20.8
|  | HV 22KV Line Outage |  |  | 12.6 | 81.8 | 112.8 | 207.2
|  | CMOS |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 435705.2 | 589821 | 525151.8 | 1550678
|  | HV 22kv ACR Outage |  |  | 585214.8 | 1151570.2 | 2799098.8 | 4535883.8
|  | HV 22KV CB Outage |  |  | 1462551.2 | 1900736.8 | 599494.2 | 3962782.2
|  | HV 22KV Line Outage |  |  | 325239.8 | 1698617.2 | 1242880.6 | 3266737.6
|  | Average Cust Effected Per Event |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 4951.1955 | 2465.8069 | 1726.3373
|  | HV 22kv ACR Outage |  |  | 225082.6154 | 130860.25 | 110200.7402
|  | HV 22KV CB Outage |  |  | 187506.5641 | 202206.0426 | 166526.1667
|  | HV 22KV Line Outage |  |  | 25812.6825 | 20765.4914 | 11018.445
|  | Energy not supplied |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 9.615 | 13.017 | 11.589 | 34.222
|  | HV 22kv ACR Outage |  |  | 12.915 | 25.414 | 61.773 | 100.101
|  | HV 22KV CB Outage |  |  | 32.277 | 41.947 | 13.23 | 87.454
|  | HV 22KV Line Outage |  |  | 7.178 | 37.486 | 27.429 | 72.093
|  | Subtotal |  |  | 61.985 | 117.864 | 114.021 | 293.87
Annual Average Performance After
|  | No Events With REFCL Not In Service |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 0.44 | 1.196 | 1.521
|  | HV 22kv ACR Outage |  |  | 0.013 | 0.044 | 0.127
|  | HV 22KV CB Outage |  |  | 0.039 | 0.047 | 0.018
|  | HV 22KV Line Outage |  |  | 0.063 | 0.409 | 0.564
|  | # Faults Still Occurring With REFCL In Service |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 70.048 | 190.4032 | 242.1432
|  | HV 22kv ACR Outage |  |  | 2.0696 | 7.0048 | 20.2184
|  | HV 22KV CB Outage |  |  | 5.4327 | 6.5471 | 2.5074
|  | HV 22KV Line Outage |  |  | 6.8953 | 44.765 | 61.7298
|  | # E/L or SEF Faults Eliminated |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 15.7608 | 42.8407 | 54.4822
|  | HV 22kv ACR Outage |  |  | 0.5174 | 1.7512 | 5.0546
|  | HV 22KV CB Outage |  |  | 2.3283 | 2.8059 | 1.0746
|  | HV 22KV Line Outage |  |  | 3.7611 | 24.4173 | 33.6708
|  | E/L or SEF Faults Escalated - CB Trip |  |  | Urban | Rural Short | Rural Long
|  | 22KV Dist Sub Outage |  |  | 1.7512 | 4.7601 | 6.0536
|  | HV 22kv ACR Outage |  |  | 0 | 0 | 0
|  | HV 22KV CB Outage |  |  | 0 | 0 | 0
|  | HV 22KV Line Outage |  |  | 1.8805 | 12.2086 | 16.8354
|  | Total # Events Occurring |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 70.488 | 191.5992 | 243.6642 | 505.7514
|  | HV 22kv ACR Outage |  |  | 3.8985 | 15.5332 | 31.7899 | 51.2215
|  | HV 22KV CB Outage |  |  | 7.2876 | 15.0785 | 13.9699 | 36.3359
|  | HV 22KV Line Outage |  |  | 6.9583 | 45.174 | 62.2938 | 114.4262
|  | CMOS |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 348999.8652 | 472446.621 | 420646.5918 | 1242093.078
|  | HV 22kv ACR Outage |  |  | 877478.949 | 2032673.8552 | 3503269.4075 | 6413422.2117
|  | HV 22KV CB Outage |  |  | 1366468.1489 | 3048956.7354 | 2326352.2305 | 6741777.1148
|  | HV 22KV Line Outage |  |  | 179613.6795 | 938061.3487 | 686380.8113 | 1804055.8396
|  | Energy not supplied |  |  | Urban | Rural Short | Rural Long | Total
|  | 22KV Dist Sub Outage |  |  | 7.702 | 10.426 | 9.283 | 27.411
|  | HV 22kv ACR Outage |  |  | 19.365 | 44.859 | 77.313 | 141.536
|  | HV 22KV CB Outage |  |  | 30.156 | 67.287 | 51.34 | 148.783
|  | HV 22KV Line Outage |  |  | 3.964 | 20.702 | 15.148 | 39.813
|  | Subtotal |  |  | 61.187 | 143.274 | 153.084 | 357.543
End