## Inputs
Powercor - Robinvale Transformer No.2 Replacement Risk Monetisation Model
Inputs | [8 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
General inputs, timing and costs
General inputs
|  | Company |  | Powercor
|  | Title |  | Robinvale Transformer No.2 Replacement Risk Monetisation Model
|  | Model start & timeline |  | 2019 | FY19/20
|  | Real WACC |  | 2.75%
|  | Asset Life (years) |  | 50
Inflation
|  | Year | [6 empty] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
|  |  | Nominal escalation index to June $2021 | [5 empty] | 125.4% | 122% | 117.9% | 115.6% | 113.1% | 110.6% | 108.9% | 107.8% | 105.8% | 103.6% | 102% | 100%
Capex
|  | Replacement capex regulator, real $2019 |  | 3748000 |  |  |  |  | 0 | 0 | 0 | 50000 | 750000 | 2948000 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Capex ($2021) | 3883856.708 |  |  |  |  | 0 | 0 | 0 | 51812.3894 | 777185.8407 | 3054858.4779 | 0 | 0 | 0 | 0 | 0 | 0
Opex
|  |  |  | Pre-replacement | Post-replacement
|  | Annual opex, real $2019 |  | 32300 | 14400
|  |  | Opex ($2021) | 33470.8035 | 14921.9681
Scenario manager
Sensitivity bounds
|  | Bound |  | Lower | Central | Upper
|  |  | PoF | -10% | 0% | 10%
|  |  | Capex | -10% | 0% | 10%
|  |  | Opex | -10% | 0% | 10%
|  |  | Demand | -5% | 0% | 5%
|  |  | VCR | -10% | 0% | 10%
|  |  | Environment | -10% | 0% | 10%
Scenario selection
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | Central | Central | Central | Central | Central | 2010: Central
|  |  | A | Lower | Upper | Upper | Lower | Lower | 2010: Lower
|  |  | B | Lower | Lower | Lower | Lower | Lower | 2010: Lower
|  |  | C | Upper | Upper | Upper | Upper | Upper | 2010: Upper
|  |  | D | Upper | Lower | Lower | Upper | Upper | 2010: Upper
Scenario output
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | 100% | 100% | 100% | 100% | 100% | 2010: 100%
|  |  | A | 90% | 110% | 110% | 95% | 90% | 2010: 90%
|  |  | B | 90% | 90% | 90% | 95% | 90% | 2010: 90%
|  |  | C | 110% | 110% | 110% | 105% | 110% | 2010: 110%
|  |  | D | 110% | 90% | 90% | 105% | 110% | 2010: 110%
Network assumptions
Probability of failure (PoF)
|  | Failure mode |  | Failure code
|  |  | Significant | 1 |  |  |  |  | 11.92% | 12.67% | 13.46% | 14.31% | 15.22% | 16.19% | 17.22% | 18.33% | 19.51% | 20.77% | 22.12% | 23.56%
|  |  | Major | 2 |  |  |  |  | 0.0641% | 0.0681% | 0.07238% | 0.07694% | 0.08182% | 0.08703% | 0.09259% | 0.09853% | 0.1049% | 0.1117% | 0.1189% | 0.1266%
|  |  | Catastrophic | 3 |  |  |  |  | 0.0641% | 0.0681% | 0.07238% | 0.07694% | 0.08182% | 0.08703% | 0.09259% | 0.09853% | 0.1049% | 0.1117% | 0.1189% | 0.1266%
Value of customer reliability (VCR)
|  | Sector |  | MWh | $/MWh ($2018) | Load Duration | Duration Weighted $/MWh ($2021)
|  |  | Residential | 35144 | 26450 | 20% | 2886.146
|  |  | Agricultural | 7084 | 50930 | 15% | 840.1463
|  |  | Commercial | 18747 | 47770 | 40% | 5561.071
|  |  | Industrial | 7162 | 47070 | 80% | 4186.778
|  |  | Total | 68137 | 37028.4346 | 34.4% | 13474.1413
Asset information
|  | Assets at risk |  | 3
|  | N-rating, MVA |  | 31.5
|  |  | N-1 Rating before transfers, MVA | 20.4
|  |  | N-2 Rating before transfers, MVA | 10.6
|  |  | N-3 Rating before transfers, MVA | 0
|  |  | N-4 Rating before transfers, MVA | 0
|  |  | Transfer capacity, MVA | 0
Environmental assumptions
Environmental consequence
|  | Settings |  | Real $2019 | Real $2021
|  |  | Value Consequence Loss Oil / litre | 100 | 103.6248
|  |  | Value Consequence Loss SF6/Kg | 598 | 619.6762
|  |  | Value Consequence Fire | 10000 | 10362.4779
|  |  | Value Consequence Waste / tonne | 1000 | 1036.2478
|  |  | Value Consequence Disturbance | 400 | 414.4991
|  |  | Value Fire brigade attendance | 50000 | 51812.3894
|  | Failure Mode |  | Significant | Major | Catastrophic
|  |  | Average Consequence Loss Oil | 500 | 4050 | 12150
|  |  | Average Consequences Loss SF6 kgs | 0 | 0 | 0
|  |  | Average Consequence Fire | 0.05 | 2.5 | 5
|  |  | Average Consequence Waste | 10 | 405 | 1215
|  |  | Average Consequence Disturbance | 2 | 3 | 5
|  |  | Average Cost of Fault (Air Insulated) | 11709.6 | 446830.046 | 1312925.9469
|  |  | Average Cost of Fault (SF6 Insulated) | 11709.6 | 446830.046 | 1312925.9469
|  |  | Average Cost of Fault (Oil Insulated) | 63521.9894 | 866510.4 | 2571967.0088
Generation assumptions
Generation requirements
Generator detail
|  |  | Generator capacity, MVA | 1
|  |  | Generators per site | 4
|  |  | Step-up transformer capacity | 5
|  |  | Number of transformers required per site | 1
|  |  | Generator sites connected per day | 3
|  |  | Fuel usage / MWh in Litres | 270
|  |  | Days in week | 7
|  |  | Setup, persons required | 5
|  |  | Setup, hours employed per day | 16
|  |  | Hours per day | 24
|  | Generator detail by failure mode |  | Significant | Major | Coincidental | Catastrophic
|  |  | Switching time only (hours required) | 0 | 0 | 0 | 0
|  |  | Number of weeks generation required | 1.1905 | 6 | 6 | 12
|  |  | Max demand load net of transfers, MVA | 2.0505 | 2.0505 | 11.8505 | 22.4505
|  |  | Number of generators | 3 | 3 | 12 | 23
|  |  | Generator sites | 1 | 1 | 3 | 6
|  |  | Number of days to connect all generators | 1 | 1 | 1 | 2
|  | Generation costs |  | Real $2019 | Real $2021
|  |  | Generator hire per week | 7000 | 7253.7345
|  |  | Fuel cost $ per litre including delivery | 1.5 | 1.5544
|  |  | Fitter cost (blended 24hr rate) $ per hr | 150 | 155.4372
|  |  | Traffic management and security per site | 10000 | 10362.4779
|  |  | Transformer hire per week | 7000 | 7253.7345
|  |  | Earthing and bunding per site | 2000 | 2072.4956
|  |  | Temporary fencing per site per week | 3000 | 3108.7434
|  |  | Miscellaneous material per site | 2000 | 2072.4956
|  |  | Install and remove step down transformers per site | 2500 | 2590.6195
|  |  | Council permits per site | 4000 | 4144.9912
|  |  | Crane hire to install / remove generators per site | 2500 | 2590.6195
|  |  | Cable hire per site | 3000 | 3108.7434
|  | Generation costs by failure mode |  | Significant | Major | Coincidental | Catastrophic
|  |  | Generator hire | 44185.6057 | 134194.0885 | 536776.354 | 2029836.708
|  |  | Fuel cost | 59207.6672 | 298406.6425 | 1724593.9049 | 6534409.2344
|  |  | Fitter cost | 43522.4071 | 169115.6389 | 507346.9168 | 1954777.8265
|  |  | Traffic management cost | 86353.9823 | 435224.0708 | 1305672.2124 | 5222688.8496
|  |  | Transformer hire | 14728.5352 | 44731.3628 | 134194.0885 | 529522.6195
|  |  | Earthing and bunding | 2072.4956 | 2072.4956 | 6217.4867 | 12434.9735
|  |  | Temporary fencing | 3700.885 | 18652.4602 | 55957.3805 | 223829.5221
|  |  | Miscellaneous materials | 2072.4956 | 2072.4956 | 6217.4867 | 12434.9735
|  |  | Installation & removal of step-down transformers | 2590.6195 | 2590.6195 | 7771.8584 | 15543.7168
|  |  | Council permits | 4144.9912 | 4144.9912 | 12434.9735 | 24869.9469
|  |  | Crane hire | 2590.6195 | 2590.6195 | 7771.8584 | 15543.7168
|  |  | Cable hire | 3108.7434 | 3108.7434 | 9326.2301 | 18652.4602
|  |  | Total | 268279.047 | 1116904.2283 | 4314280.7509 | 16594544.5476
Safety assumptions
Safety consequence
|  | Value of consquence |  | Base Value ($2018) | Disproportion Factor | Reference Value ($2021)
|  |  | Minor | 127274.0425 | 1 | 134627.6539
|  |  | Serious | 672376.8885 | 2 | 1422450.662
|  |  | Fataility | 4500000 | 3 | 14280000
|  | Probability of event, by failure mode |  | Significant | Major | Catastrophic
|  |  | Minor | 1.172% | 4.103% | 4.103%
|  |  | Serious | 0.2345% | 0.8206% | 0.8206%
|  |  | Fataility | 0.02345% | 0.08206% | 0.08206%
|  |  | Value of event | 8261.6388 | 28915.7357 | 28915.7357
|  |  | Weighted likelyhood of consequence | 0.05217% | 0.1826% | 0.1826%
Base Case PoE, Load and VCR assumptions
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA | 10% |  |  |  |  | 23.804 | 23.657 | 23.997 | 23.973 | 23.928 | 24.87 | 25.027 | 25.027 | 25.027 | 25.027 | 25.027 | 25.027
|  |  | 50% PoE forecast, MVA | 50% |  |  |  |  | 21.078 | 20.643 | 21.055 | 21.239 | 21.515 | 21.6 | 21.928 | 21.928 | 21.928 | 21.928 | 21.928 | 21.928
|  |  | Weighting to 50% PoE | 70% |  |  |  |  | 21.8958 | 21.5472 | 21.9376 | 22.0592 | 22.2389 | 22.581 | 22.8577 | 22.8577 | 22.8577 | 22.8577 | 22.8577 | 22.8577
Load at risk
Selected profile, MVA
|  |  | N | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | [5 empty] | 1.4958 | 1.1472 | 1.5376 | 1.6592 | 1.8389 | 2.181 | 2.4577 | 2.4577 | 2.4577 | 2.4577 | 2.4577 | 2.4577
|  |  | N-2 | [5 empty] | 11.2958 | 10.9472 | 11.3376 | 11.4592 | 11.6389 | 11.981 | 12.2577 | 12.2577 | 12.2577 | 12.2577 | 12.2577 | 12.2577
|  |  | N-3 | [5 empty] | 21.8958 | 21.5472 | 21.9376 | 22.0592 | 22.2389 | 22.581 | 22.8577 | 22.8577 | 22.8577 | 22.8577 | 22.8577 | 22.8577
|  |  | N-4 | [5 empty] | 21.8958 | 21.5472 | 21.9376 | 22.0592 | 22.2389 | 22.581 | 22.8577 | 22.8577 | 22.8577 | 22.8577 | 22.8577 | 22.8577
End

## Base Case
Powercor - Robinvale Transformer No.2 Replacement Risk Monetisation Model
Base Case | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario Base case: Consequence calculation
Consequence calculation
|  | Scenario |  |  | Base case
|  |  | PoF |  | 100%
|  |  | Capex |  | 100%
|  |  | Opex |  | 100%
|  |  | Demand |  | 100%
|  |  | VCR |  | 100%
|  |  | Environment |  | 100%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 17701626.1925 | 0 | 0 | 0 | 0 | 20% | 3540325.2385 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 16594544.5476 | 0 | 0 | 20% | 3318908.9095 | 3318908.9095
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 11651570.1239 | 0 | 20% | 2330314.0248 | 2330314.0248
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2571967.0088 | 20% | 514393.4018 | 514393.4018
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 20% | 10362.4779 | 10362.4779
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 967421.7871 | 0 | 0 | 0 | 0 | 76% | 735240.5582 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 1116904.2283 | 0 | 0 | 80% | 893523.3827 | 893523.3827
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3883856.708 | 0 | 80% | 3107085.3664 | 3107085.3664
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 866510.4 | 80% | 693208.32 | 693208.32
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 80% | 41449.9115 | 41449.9115
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 7305657.8575 | 0 | 4314280.7509 | 0 | 0 | 4% | 464797.5443 | 172571.23
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 967421.7871 | 0 | 0 | 0 | 0 | 96% | 928724.9157 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 268279.047 | 0 | 0 | 100% | 268279.047 | 268279.047
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 33470.8035 | 0 | 100% | 33470.8035 | 33470.8035
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 63521.9894 | 100% | 63521.9894 | 63521.9894
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 7305657.8575 | 0 | 1124287.1325 | 0 | 0 | 4% | 337197.7996 | 44971.4853
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 8273079.6446 | 8261.6388 | 1444378.5688 | 33470.8035 | 63521.9894 | 17.22% | 1691268.5833 | 470317.3533
[5 empty] | 2 | Major |  | 8273079.6446 | 28915.7357 | 5482997.3686 | 3883856.708 | 866510.4 | 32.15% | 5958437.6716 | 4930970.7991
[5 empty] | 3 | Catastrophic |  | 17701626.1925 | 28915.7357 | 16646356.937 | 11651570.1239 | 2571967.0088 | 20% | 9720087.1996 | 6179761.9611
[5 empty] | Subtotal |  |  | 2025: 17369793.4545; 2026: 11581050.1135
Scenario Base case: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 31.5
|  |  | N-1 Rating before transfers, MVA |  |  | 20.4
|  |  | N-2 Rating before transfers, MVA |  |  | 10.6
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 23.804 | 23.657 | 23.997 | 23.973 | 23.928 | 24.87 | 25.027 | 25.027 | 25.027 | 25.027 | 25.027 | 25.027
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 21.078 | 20.643 | 21.055 | 21.239 | 21.515 | 21.6 | 21.928 | 21.928 | 21.928 | 21.928 | 21.928 | 21.928
|  |  | Weighting to 50% PoE |  |  | 70% |  | 21.8958 | 21.5472 | 21.9376 | 22.0592 | 22.2389 | 22.581 | 22.8577 | 22.8577 | 22.8577 | 22.8577 | 22.8577 | 22.8577
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 1.4958 | 1.1472 | 1.5376 | 1.6592 | 1.8389 | 2.181 | 2.4577 | 2.4577 | 2.4577 | 2.4577 | 2.4577 | 2.4577
|  |  | N-2 |  |  |  |  | 11.2958 | 10.9472 | 11.3376 | 11.4592 | 11.6389 | 11.981 | 12.2577 | 12.2577 | 12.2577 | 12.2577 | 12.2577 | 12.2577
|  |  | N-3 |  |  |  |  | 21.8958 | 21.5472 | 21.9376 | 22.0592 | 22.2389 | 22.581 | 22.8577 | 22.8577 | 22.8577 | 22.8577 | 22.8577 | 22.8577
|  |  | N-4 |  |  |  |  | 21.8958 | 21.5472 | 21.9376 | 22.0592 | 22.2389 | 22.581 | 22.8577 | 22.8577 | 22.8577 | 22.8577 | 22.8577 | 22.8577
VCR at risk
Average load at risk (pu)
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Adjustment |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Adjustment |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 967421.7871 | 741961.6755 | 994456.3043 | 1073102.1722 | 1189324.7255 | 1410580.905 | 1589539.0602 | 1589539.0602 | 1589539.0602 | 1589539.0602 | 1589539.0602 | 1589539.0602
|  |  | N-1 |  |  | Major |  | 967421.7871 | 741961.6755 | 994456.3043 | 1073102.1722 | 1189324.7255 | 1410580.905 | 1589539.0602 | 1589539.0602 | 1589539.0602 | 1589539.0602 | 1589539.0602 | 1589539.0602
|  |  | N-2 |  |  | Catastrophic |  | 7305657.8575 | 7080197.7459 | 7332692.3746 | 7411338.2426 | 7527560.7958 | 7748816.9754 | 9909718.9132 | 9909718.9132 | 9909718.9132 | 9909718.9132 | 9909718.9132 | 9909718.9132
|  |  | N-3 |  |  | Catastrophic |  | 17701626.1925 | 17419801.053 | 17735419.3389 | 17833726.6739 | 17979004.8654 | 18255575.0899 | 18479272.7838 | 18479272.7838 | 18479272.7838 | 18479272.7838 | 18479272.7838 | 18479272.7838
|  |  | N-4 |  |  | Catastrophic |  | 17701626.1925 | 17419801.053 | 17735419.3389 | 17833726.6739 | 17979004.8654 | 18255575.0899 | 18479272.7838 | 18479272.7838 | 18479272.7838 | 18479272.7838 | 18479272.7838 | 18479272.7838
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 11.92% | 12.67% | 13.46% | 14.31% | 15.22% | 16.19% | 17.22% | 18.33% | 19.51% | 20.77% | 22.12% | 23.56%
|  |  | Major |  |  |  |  | 0.0641% | 0.0681% | 0.07238% | 0.07694% | 0.08182% | 0.08703% | 0.09259% | 0.09853% | 0.1049% | 0.1117% | 0.1189% | 0.1266%
|  |  | Catastrophic |  |  |  |  | 0.0641% | 0.0681% | 0.07238% | 0.07694% | 0.08182% | 0.08703% | 0.09259% | 0.09853% | 0.1049% | 0.1117% | 0.1189% | 0.1266%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 110725.6064 | 90226.2878 | 128522.7528 | 147434.3302 | 173755.6974 | 219196.1009 | 262793.5976 | 279662.0166 | 297686.8187 | 316949.9203 | 337539.1579 | 359465.8835
|  |  | Network Performance |  |  | Major |  | 471.2783 | 384.0277 | 547.0278 | 627.5207 | 739.5516 | 932.9583 | 1118.5211 | 1190.3177 | 1267.0362 | 1349.0252 | 1436.6586 | 1529.9847
|  |  | Network Performance |  |  | Catastrophic |  | 2269.2962 | 2372.688 | 2567.3294 | 2744.3877 | 2942.0502 | 3177.4312 | 3421.9548 | 3641.6062 | 3876.3153 | 4127.1489 | 4395.2507 | 4680.7686
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 34840.1721 | 35874.4921 | 39486.3088 | 42427.0601 | 45822.8014 | 50171.7195 | 68264.3046 | 72646.1118 | 77328.3057 | 82332.1652 | 87680.507 | 93376.28
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 187.3128 | 192.8736 | 212.292 | 228.1025 | 246.3591 | 269.7404 | 367.0124 | 390.5705 | 415.7436 | 442.646 | 471.4006 | 502.023
|  |  | Other significant risks |  |  | Significant |  | 56072.7652 | 59576.0062 | 63316.0895 | 67309.6477 | 71574.5088 | 76129.7834 | 80995.9579 | 86194.9954 | 91750.4432 | 97687.5489 | 104033.3847 | 110791.4494
|  |  | Other major risks |  |  | Major |  | 3160.6795 | 3358.1483 | 3568.9673 | 3794.074 | 4034.4734 | 4291.2427 | 4565.5366 | 4858.5932 | 5171.7396 | 5506.3992 | 5864.0979 | 6245.0329
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 3961.1362 | 4208.6149 | 4472.8248 | 4754.9408 | 5056.2225 | 5378.0198 | 5721.7799 | 6089.0543 | 6481.5066 | 6900.9203 | 7349.2078 | 7826.6163
|  |  | Annual opex, pre-replacement |  |  |  |  | 33470.8035 | 33470.8035 | 33470.8035 | 33470.8035 | 33470.8035 | 33470.8035 | 33470.8035 | 33470.8035 | 33470.8035 | 33470.8035 | 33470.8035 | 33470.8035
|  |  | Subtotal |  |  |  |  | 245159.0501 | 229663.9421 | 276164.396 | 302790.8672 | 337642.4679 | 393017.7997 | 460719.4684 | 488144.0692 | 517448.7125 | 548766.5777 | 582240.4688 | 617888.842
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 51812.3894 | 777185.8407 | 3054858.4779 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 144760.291
|  |  | Post-replacement opex |  |  | 14921.9681
|  |  | Total annuity |  |  | 159682.2592
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 245159.0501 | 229663.9421 | 276164.396 | 302790.8672 | 337642.4679 | 393017.7997 | 460719.4684 | 488144.0692 | 517448.7125 | 548766.5777 | 582240.4688 | 617888.842
|  |  | Annualised cost |  |  |  |  | 159682.2592 | 159682.2592 | 159682.2592 | 159682.2592 | 159682.2592 | 159682.2592 | 159682.2592 | 159682.2592 | 159682.2592 | 159682.2592 | 159682.2592 | 159682.2592
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario A
Powercor - Robinvale Transformer No.2 Replacement Risk Monetisation Model
Scenario A | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario A: Consequence calculation
Consequence calculation
|  | Scenario |  |  | A
|  |  | PoF |  | 90%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 15134890.3946 | 0 | 0 | 0 | 0 | 20% | 3026978.0789 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 18253999.0024 | 0 | 0 | 20% | 3650799.8005 | 3650799.8005
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 12816727.1363 | 0 | 20% | 2563345.4273 | 2563345.4273
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2314770.308 | 20% | 462954.0616 | 462954.0616
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 20% | 11398.7257 | 11398.7257
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 233421.0655 | 0 | 0 | 0 | 0 | 76% | 177400.0098 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 1228594.6512 | 0 | 0 | 80% | 982875.7209 | 982875.7209
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 4272242.3788 | 0 | 80% | 3417793.903 | 3417793.903
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 779859.36 | 80% | 623887.488 | 623887.488
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 80% | 45594.9027 | 45594.9027
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 5937833.5288 | 0 | 4745708.826 | 0 | 0 | 4% | 427341.6942 | 189828.353
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 233421.0655 | 0 | 0 | 0 | 0 | 96% | 224084.2229 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 295106.9517 | 0 | 0 | 100% | 295106.9517 | 295106.9517
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 36817.8839 | 0 | 100% | 36817.8839 | 36817.8839
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 57169.7904 | 100% | 57169.7904 | 57169.7904
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 5937833.5288 | 0 | 1236715.8457 | 0 | 0 | 4% | 286981.975 | 49468.6338
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 6171254.5943 | 8261.6388 | 1588816.4257 | 36817.8839 | 57169.7904 | 12.28% | 965416.091 | 503818.5269
[5 empty] | 2 | Major |  | 6171254.5943 | 28915.7357 | 6031297.1055 | 4272242.3788 | 779859.36 | 32.97% | 5698026.3071 | 5283112.9562
[5 empty] | 3 | Catastrophic |  | 15134890.3946 | 28915.7357 | 18310992.6307 | 12816727.1363 | 2314770.308 | 20% | 9721259.241 | 6694281.1621
[5 empty] | Subtotal |  |  | 2025: 16384701.6391; 2026: 12481212.6452
Scenario A: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 31.5
|  |  | N-1 Rating before transfers, MVA |  |  | 20.4
|  |  | N-2 Rating before transfers, MVA |  |  | 10.6
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 22.6138 | 22.4741 | 22.7971 | 22.7743 | 22.7316 | 23.6265 | 23.7756 | 23.7756 | 23.7756 | 23.7756 | 23.7756 | 23.7756
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 20.0241 | 19.6108 | 20.0023 | 20.1771 | 20.4393 | 20.52 | 20.8316 | 20.8316 | 20.8316 | 20.8316 | 20.8316 | 20.8316
|  |  | Weighting to 50% PoE |  |  | 70% |  | 20.801 | 20.4698 | 20.8407 | 20.9562 | 21.127 | 21.452 | 21.7148 | 21.7148 | 21.7148 | 21.7148 | 21.7148 | 21.7148
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0.40101 | 0.06984 | 0.44072 | 0.55624 | 0.72696 | 1.052 | 1.3148 | 1.3148 | 1.3148 | 1.3148 | 1.3148 | 1.3148
|  |  | N-2 |  |  |  |  | 10.201 | 9.8698 | 10.2407 | 10.3562 | 10.527 | 10.852 | 11.1148 | 11.1148 | 11.1148 | 11.1148 | 11.1148 | 11.1148
|  |  | N-3 |  |  |  |  | 20.801 | 20.4698 | 20.8407 | 20.9562 | 21.127 | 21.452 | 21.7148 | 21.7148 | 21.7148 | 21.7148 | 21.7148 | 21.7148
|  |  | N-4 |  |  |  |  | 20.801 | 20.4698 | 20.8407 | 20.9562 | 21.127 | 21.452 | 21.7148 | 21.7148 | 21.7148 | 21.7148 | 21.7148 | 21.7148
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 1 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 233421.0655 | 40652.67 | 256535.5776 | 323777.7948 | 423148.0778 | 612322.1113 | 765331.334 | 765331.334 | 765331.334 | 765331.334 | 765331.334 | 765331.334
|  |  | N-1 |  |  | Major |  | 233421.0655 | 40652.67 | 256535.5776 | 323777.7948 | 423148.0778 | 612322.1113 | 765331.334 | 765331.334 | 765331.334 | 765331.334 | 765331.334 | 765331.334
|  |  | N-2 |  |  | Catastrophic |  | 5937833.5288 | 5745065.1334 | 5960948.041 | 6028190.2581 | 6127560.5411 | 6316734.5746 | 6469743.7973 | 6469743.7973 | 6469743.7973 | 6469743.7973 | 6469743.7973 | 6469743.7973
|  |  | N-3 |  |  | Catastrophic |  | 15134890.3946 | 14893929.9003 | 15163783.5348 | 15247836.3062 | 15372049.16 | 15608516.7019 | 15799778.2302 | 15799778.2302 | 15799778.2302 | 15799778.2302 | 15799778.2302 | 15799778.2302
|  |  | N-4 |  |  | Catastrophic |  | 15134890.3946 | 14893929.9003 | 15163783.5348 | 15247836.3062 | 15372049.16 | 15608516.7019 | 15799778.2302 | 15799778.2302 | 15799778.2302 | 15799778.2302 | 15799778.2302 | 15799778.2302
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 10.73% | 11.4% | 12.12% | 12.88% | 13.7% | 14.57% | 15.5% | 16.49% | 17.56% | 18.69% | 19.91% | 21.2%
|  |  | Major |  |  |  |  | 0.05769% | 0.06129% | 0.06514% | 0.06925% | 0.07364% | 0.07832% | 0.08333% | 0.08868% | 0.09439% | 0.1005% | 0.107% | 0.114%
|  |  | Catastrophic |  |  |  |  | 0.05769% | 0.06129% | 0.06514% | 0.06925% | 0.07364% | 0.07832% | 0.08333% | 0.08868% | 0.09439% | 0.1005% | 0.107% | 0.114%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 24044.4452 | 4449.213 | 29839.0112 | 40035.6715 | 55638.2534 | 85636.1779 | 113876.8852 | 121186.5116 | 128997.2359 | 137344.555 | 146266.5312 | 155768.0839
|  |  | Network Performance |  |  | Major |  | 102.3397 | 18.9371 | 127.003 | 170.4027 | 236.8116 | 364.4909 | 484.691 | 515.8028 | 549.0474 | 584.5758 | 622.5502 | 662.9914
|  |  | Network Performance |  |  | Catastrophic |  | 1746.2234 | 1825.7834 | 1975.56 | 2111.8064 | 2263.9076 | 2445.0333 | 2633.1942 | 2802.2159 | 2982.8246 | 3175.8411 | 3382.1454 | 3601.8514
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 25485.402 | 26198.5853 | 28889.5594 | 31058.163 | 33570.4749 | 36809.3985 | 40110.8557 | 42685.5254 | 45436.6968 | 48376.873 | 51519.4608 | 54866.1927
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 137.0183 | 140.8526 | 155.3202 | 166.9794 | 180.4864 | 197.9 | 215.6498 | 229.4921 | 244.2833 | 260.0907 | 276.9863 | 294.9795
|  |  | Other significant risks |  |  | Significant |  | 54060.1957 | 57437.698 | 61043.5418 | 64893.7628 | 69005.5491 | 73397.3253 | 78088.8426 | 83101.2757 | 88457.3268 | 94181.3373 | 100299.4077 | 106814.9113
|  |  | Other major risks |  |  | Major |  | 3047.7577 | 3238.1715 | 3441.4585 | 3658.5229 | 3890.3335 | 4137.9292 | 4402.4234 | 4685.0099 | 4986.9685 | 5309.6717 | 5654.5909 | 6021.9161
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 3861.8418 | 4103.117 | 4360.7039 | 4635.7481 | 4929.4775 | 5243.2082 | 5578.3513 | 5936.4192 | 6319.0338 | 6727.934 | 7164.9842 | 7630.4255
|  |  | Annual opex, pre-replacement |  |  |  |  | 36817.8839 | 36817.8839 | 36817.8839 | 36817.8839 | 36817.8839 | 36817.8839 | 36817.8839 | 36817.8839 | 36817.8839 | 36817.8839 | 36817.8839 | 36817.8839
|  |  | Subtotal |  |  |  |  | 149303.1077 | 134230.2418 | 166650.0418 | 183548.9407 | 206533.1779 | 245049.3472 | 282208.777 | 297960.1365 | 314791.301 | 332778.7625 | 352004.5407 | 372479.2357
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 56993.6283 | 854904.4248 | 3360344.3257 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 159236.3201
|  |  | Post-replacement opex |  |  | 16414.165
|  |  | Total annuity |  |  | 175650.4851
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 149303.1077 | 134230.2418 | 166650.0418 | 183548.9407 | 206533.1779 | 245049.3472 | 282208.777 | 297960.1365 | 314791.301 | 332778.7625 | 352004.5407 | 372479.2357
|  |  | Annualised cost |  |  |  |  | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario B
Powercor - Robinvale Transformer No.2 Replacement Risk Monetisation Model
Scenario B | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario B: Consequence calculation
Consequence calculation
|  | Scenario |  |  | B
|  |  | PoF |  | 90%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 15134890.3946 | 0 | 0 | 0 | 0 | 20% | 3026978.0789 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 14935090.0929 | 0 | 0 | 20% | 2987018.0186 | 2987018.0186
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 10486413.1115 | 0 | 20% | 2097282.6223 | 2097282.6223
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2314770.308 | 20% | 462954.0616 | 462954.0616
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 20% | 9326.2301 | 9326.2301
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 233421.0655 | 0 | 0 | 0 | 0 | 76% | 177400.0098 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 1005213.8055 | 0 | 0 | 80% | 804171.0444 | 804171.0444
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3495471.0372 | 0 | 80% | 2796376.8297 | 2796376.8297
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 779859.36 | 80% | 623887.488 | 623887.488
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 80% | 37304.9204 | 37304.9204
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 5937833.5288 | 0 | 3882852.6758 | 0 | 0 | 4% | 392827.4482 | 155314.107
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 233421.0655 | 0 | 0 | 0 | 0 | 96% | 224084.2229 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 241451.1423 | 0 | 0 | 100% | 241451.1423 | 241451.1423
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 30123.7232 | 0 | 100% | 30123.7232 | 30123.7232
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 57169.7904 | 100% | 57169.7904 | 57169.7904
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 5937833.5288 | 0 | 1011858.4192 | 0 | 0 | 4% | 277987.6779 | 40474.3368
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 6171254.5943 | 8261.6388 | 1299940.712 | 30123.7232 | 57169.7904 | 11.71% | 885709.3459 | 424111.7819
[5 empty] | 2 | Major |  | 6171254.5943 | 28915.7357 | 4934697.6317 | 3495471.0372 | 779859.36 | 31.51% | 4855100.329 | 4440186.9781
[5 empty] | 3 | Catastrophic |  | 15134890.3946 | 28915.7357 | 14981721.2433 | 10486413.1115 | 2314770.308 | 20% | 8589342.1586 | 5562364.0797
[5 empty] | Subtotal |  |  | 2025: 14330151.8335; 2026: 10426662.8396
Scenario B: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 31.5
|  |  | N-1 Rating before transfers, MVA |  |  | 20.4
|  |  | N-2 Rating before transfers, MVA |  |  | 10.6
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 22.6138 | 22.4741 | 22.7971 | 22.7743 | 22.7316 | 23.6265 | 23.7756 | 23.7756 | 23.7756 | 23.7756 | 23.7756 | 23.7756
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 20.0241 | 19.6108 | 20.0023 | 20.1771 | 20.4393 | 20.52 | 20.8316 | 20.8316 | 20.8316 | 20.8316 | 20.8316 | 20.8316
|  |  | Weighting to 50% PoE |  |  | 70% |  | 20.801 | 20.4698 | 20.8407 | 20.9562 | 21.127 | 21.452 | 21.7148 | 21.7148 | 21.7148 | 21.7148 | 21.7148 | 21.7148
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0.40101 | 0.06984 | 0.44072 | 0.55624 | 0.72696 | 1.052 | 1.3148 | 1.3148 | 1.3148 | 1.3148 | 1.3148 | 1.3148
|  |  | N-2 |  |  |  |  | 10.201 | 9.8698 | 10.2407 | 10.3562 | 10.527 | 10.852 | 11.1148 | 11.1148 | 11.1148 | 11.1148 | 11.1148 | 11.1148
|  |  | N-3 |  |  |  |  | 20.801 | 20.4698 | 20.8407 | 20.9562 | 21.127 | 21.452 | 21.7148 | 21.7148 | 21.7148 | 21.7148 | 21.7148 | 21.7148
|  |  | N-4 |  |  |  |  | 20.801 | 20.4698 | 20.8407 | 20.9562 | 21.127 | 21.452 | 21.7148 | 21.7148 | 21.7148 | 21.7148 | 21.7148 | 21.7148
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 1 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 233421.0655 | 40652.67 | 256535.5776 | 323777.7948 | 423148.0778 | 612322.1113 | 765331.334 | 765331.334 | 765331.334 | 765331.334 | 765331.334 | 765331.334
|  |  | N-1 |  |  | Major |  | 233421.0655 | 40652.67 | 256535.5776 | 323777.7948 | 423148.0778 | 612322.1113 | 765331.334 | 765331.334 | 765331.334 | 765331.334 | 765331.334 | 765331.334
|  |  | N-2 |  |  | Catastrophic |  | 5937833.5288 | 5745065.1334 | 5960948.041 | 6028190.2581 | 6127560.5411 | 6316734.5746 | 6469743.7973 | 6469743.7973 | 6469743.7973 | 6469743.7973 | 6469743.7973 | 6469743.7973
|  |  | N-3 |  |  | Catastrophic |  | 15134890.3946 | 14893929.9003 | 15163783.5348 | 15247836.3062 | 15372049.16 | 15608516.7019 | 15799778.2302 | 15799778.2302 | 15799778.2302 | 15799778.2302 | 15799778.2302 | 15799778.2302
|  |  | N-4 |  |  | Catastrophic |  | 15134890.3946 | 14893929.9003 | 15163783.5348 | 15247836.3062 | 15372049.16 | 15608516.7019 | 15799778.2302 | 15799778.2302 | 15799778.2302 | 15799778.2302 | 15799778.2302 | 15799778.2302
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 10.73% | 11.4% | 12.12% | 12.88% | 13.7% | 14.57% | 15.5% | 16.49% | 17.56% | 18.69% | 19.91% | 21.2%
|  |  | Major |  |  |  |  | 0.05769% | 0.06129% | 0.06514% | 0.06925% | 0.07364% | 0.07832% | 0.08333% | 0.08868% | 0.09439% | 0.1005% | 0.107% | 0.114%
|  |  | Catastrophic |  |  |  |  | 0.05769% | 0.06129% | 0.06514% | 0.06925% | 0.07364% | 0.07832% | 0.08333% | 0.08868% | 0.09439% | 0.1005% | 0.107% | 0.114%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 24044.4452 | 4449.213 | 29839.0112 | 40035.6715 | 55638.2534 | 85636.1779 | 113876.8852 | 121186.5116 | 128997.2359 | 137344.555 | 146266.5312 | 155768.0839
|  |  | Network Performance |  |  | Major |  | 102.3397 | 18.9371 | 127.003 | 170.4027 | 236.8116 | 364.4909 | 484.691 | 515.8028 | 549.0474 | 584.5758 | 622.5502 | 662.9914
|  |  | Network Performance |  |  | Catastrophic |  | 1746.2234 | 1825.7834 | 1975.56 | 2111.8064 | 2263.9076 | 2445.0333 | 2633.1942 | 2802.2159 | 2982.8246 | 3175.8411 | 3382.1454 | 3601.8514
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 25485.402 | 26198.5853 | 28889.5594 | 31058.163 | 33570.4749 | 36809.3985 | 40110.8557 | 42685.5254 | 45436.6968 | 48376.873 | 51519.4608 | 54866.1927
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 137.0183 | 140.8526 | 155.3202 | 166.9794 | 180.4864 | 197.9 | 215.6498 | 229.4921 | 244.2833 | 260.0907 | 276.9863 | 294.9795
|  |  | Other significant risks |  |  | Significant |  | 45507.588 | 48350.7516 | 51386.1319 | 54627.2277 | 58088.5078 | 61785.4818 | 65734.7764 | 69954.2161 | 74462.9117 | 79281.3536 | 84431.513 | 89916.2296
|  |  | Other major risks |  |  | Major |  | 2561.4849 | 2721.518 | 2892.3704 | 3074.8019 | 3269.6269 | 3477.7184 | 3700.0123 | 3937.5118 | 4191.2927 | 4462.5083 | 4752.3952 | 5061.1134
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 3208.8539 | 3409.3325 | 3623.3648 | 3851.9025 | 4095.9661 | 4356.649 | 4635.1236 | 4932.6469 | 5250.5663 | 5590.3267 | 5953.4773 | 6340.2184
|  |  | Annual opex, pre-replacement |  |  |  |  | 30123.7232 | 30123.7232 | 30123.7232 | 30123.7232 | 30123.7232 | 30123.7232 | 30123.7232 | 30123.7232 | 30123.7232 | 30123.7232 | 30123.7232 | 30123.7232
|  |  | Subtotal |  |  |  |  | 132917.0786 | 117238.6967 | 149012.044 | 165220.6783 | 187467.7577 | 225196.573 | 261514.9114 | 276367.6458 | 292238.5818 | 309199.8473 | 327328.7827 | 346635.3835
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 46631.1504 | 699467.2566 | 2749372.6301 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 130284.2619
|  |  | Post-replacement opex |  |  | 13429.7713
|  |  | Total annuity |  |  | 143714.0332
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 132917.0786 | 117238.6967 | 149012.044 | 165220.6783 | 187467.7577 | 225196.573 | 261514.9114 | 276367.6458 | 292238.5818 | 309199.8473 | 327328.7827 | 346635.3835
|  |  | Annualised cost |  |  |  |  | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332
|  |  | Feasible ? |  |  |  |  | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario C
Powercor - Robinvale Transformer No.2 Replacement Risk Monetisation Model
Scenario C | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario C: Consequence calculation
Consequence calculation
|  | Scenario |  |  | C
|  |  | PoF |  | 110%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 20445378.2524 | 0 | 0 | 0 | 0 | 20% | 4089075.6505 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 18253999.0024 | 0 | 0 | 20% | 3650799.8005 | 3650799.8005
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 12816727.1363 | 0 | 20% | 2563345.4273 | 2563345.4273
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2829163.7097 | 20% | 565832.7419 | 565832.7419
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 20% | 11398.7257 | 11398.7257
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1843035.5183 | 0 | 0 | 0 | 0 | 76% | 1400706.9939 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 1228594.6512 | 0 | 0 | 80% | 982875.7209 | 982875.7209
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 4272242.3788 | 0 | 80% | 3417793.903 | 3417793.903
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 953161.44 | 80% | 762529.152 | 762529.152
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 80% | 45594.9027 | 45594.9027
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 11018868.9947 | 0 | 4745708.826 | 0 | 0 | 4% | 630583.1128 | 189828.353
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 1843035.5183 | 0 | 0 | 0 | 0 | 96% | 1769314.0976 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 295106.9517 | 0 | 0 | 100% | 295106.9517 | 295106.9517
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 36817.8839 | 0 | 100% | 36817.8839 | 36817.8839
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 69874.1883 | 100% | 69874.1883 | 69874.1883
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 11018868.9947 | 0 | 1236715.8457 | 0 | 0 | 4% | 490223.3936 | 49468.6338
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 12861904.513 | 8261.6388 | 1588816.4257 | 36817.8839 | 69874.1883 | 18.72% | 2726591.7822 | 516522.9248
[5 empty] | 2 | Major |  | 12861904.513 | 28915.7357 | 6031297.1055 | 4272242.3788 | 953161.44 | 30.08% | 7263216.3739 | 5421754.6202
[5 empty] | 3 | Catastrophic |  | 20445378.2524 | 28915.7357 | 18310992.6307 | 12816727.1363 | 2829163.7097 | 20% | 10886235.493 | 6797159.8425
[5 empty] | Subtotal |  |  | 2025: 20876043.649; 2026: 12735437.3875
Scenario C: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 31.5
|  |  | N-1 Rating before transfers, MVA |  |  | 20.4
|  |  | N-2 Rating before transfers, MVA |  |  | 10.6
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 24.9942 | 24.8399 | 25.1969 | 25.1716 | 25.1244 | 26.1135 | 26.2784 | 26.2784 | 26.2784 | 26.2784 | 26.2784 | 26.2784
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 22.1319 | 21.6752 | 22.1077 | 22.301 | 22.5907 | 22.68 | 23.0244 | 23.0244 | 23.0244 | 23.0244 | 23.0244 | 23.0244
|  |  | Weighting to 50% PoE |  |  | 70% |  | 22.9906 | 22.6246 | 23.0345 | 23.1622 | 23.3508 | 23.71 | 24.0006 | 24.0006 | 24.0006 | 24.0006 | 24.0006 | 24.0006
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 2.5906 | 2.2246 | 2.6345 | 2.7622 | 2.9508 | 3.3101 | 3.6006 | 3.6006 | 3.6006 | 3.6006 | 3.6006 | 3.6006
|  |  | N-2 |  |  |  |  | 12.3906 | 12.0246 | 12.4345 | 12.5622 | 12.7508 | 13.11 | 13.4006 | 13.4006 | 13.4006 | 13.4006 | 13.4006 | 13.4006
|  |  | N-3 |  |  |  |  | 22.9906 | 22.6246 | 23.0345 | 23.1622 | 23.3508 | 23.71 | 24.0006 | 24.0006 | 24.0006 | 24.0006 | 24.0006 | 24.0006
|  |  | N-4 |  |  |  |  | 22.9906 | 22.6246 | 23.0345 | 23.1622 | 23.3508 | 23.71 | 24.0006 | 24.0006 | 24.0006 | 24.0006 | 24.0006 | 24.0006
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | N-3 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | N-4 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | 3 | 3
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 1843035.5183 | 1582629.0894 | 1874260.3856 | 1965096.3631 | 2099333.4121 | 2354884.2995 | 2561580.9687 | 2561580.9687 | 2561580.9687 | 2561580.9687 | 2561580.9687 | 2561580.9687
|  |  | N-1 |  |  | Major |  | 1843035.5183 | 1582629.0894 | 1874260.3856 | 1965096.3631 | 2099333.4121 | 2354884.2995 | 2561580.9687 | 2561580.9687 | 2561580.9687 | 2561580.9687 | 2561580.9687 | 2561580.9687
|  |  | N-2 |  |  | Catastrophic |  | 11018868.9947 | 10693360.9585 | 11057900.0787 | 11171445.0506 | 11339241.3619 | 11658679.9711 | 11917050.8076 | 11917050.8076 | 11917050.8076 | 11917050.8076 | 11917050.8076 | 11917050.8076
|  |  | N-3 |  |  | Catastrophic |  | 20445378.2524 | 20119870.2162 | 20484409.3364 | 20597954.3083 | 20765750.6196 | 21085189.2288 | 25612272.0784 | 25612272.0784 | 25612272.0784 | 25612272.0784 | 25612272.0784 | 25612272.0784
|  |  | N-4 |  |  | Catastrophic |  | 20445378.2524 | 20119870.2162 | 20484409.3364 | 20597954.3083 | 20765750.6196 | 21085189.2288 | 25612272.0784 | 25612272.0784 | 25612272.0784 | 25612272.0784 | 25612272.0784 | 25612272.0784
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 13.11% | 13.93% | 14.81% | 15.74% | 16.74% | 17.81% | 18.94% | 20.16% | 21.46% | 22.85% | 24.33% | 25.91%
|  |  | Major |  |  |  |  | 0.07051% | 0.07491% | 0.07962% | 0.08464% | 0.09% | 0.09573% | 0.1018% | 0.1084% | 0.1154% | 0.1228% | 0.1308% | 0.1393%
|  |  | Catastrophic |  |  |  |  | 0.07051% | 0.07491% | 0.07962% | 0.08464% | 0.09% | 0.09573% | 0.1018% | 0.1084% | 0.1154% | 0.1228% | 0.1308% | 0.1393%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 232037.7222 | 211701.2611 | 266450.7366 | 296984.7055 | 337374.8536 | 402528.9156 | 465848.122 | 495750.3776 | 527702.5267 | 561849.7807 | 598347.8452 | 637216.8436
|  |  | Network Performance |  |  | Major |  | 987.6158 | 901.0582 | 1134.0869 | 1264.0478 | 1435.9593 | 1713.2727 | 1982.7765 | 2110.0487 | 2246.0457 | 2391.3857 | 2546.7314 | 2712.1685
|  |  | Network Performance |  |  | Catastrophic |  | 2883.1408 | 3014.5 | 3261.792 | 3486.7446 | 3737.8747 | 4036.9264 | 5217.1123 | 5551.9928 | 5909.8303 | 6292.2512 | 6700.9992 | 7136.2998
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 57803.0383 | 59600.1409 | 65501.0736 | 70347.4475 | 75928.3652 | 83035.8525 | 90301.26 | 96097.5941 | 102291.2851 | 108910.4812 | 115985.3647 | 123519.8365
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 310.769 | 320.4309 | 352.1563 | 378.2121 | 408.217 | 446.4293 | 485.4906 | 516.6537 | 549.9531 | 585.5402 | 623.5772 | 664.0851
|  |  | Other significant risks |  |  | Significant |  | 67739.6982 | 71971.8506 | 76490.1245 | 81314.6132 | 86466.8544 | 91969.9346 | 97848.603 | 104129.3924 | 110840.7496 | 118013.1754 | 125679.3749 | 133843.5748
|  |  | Other major risks |  |  | Major |  | 3822.7911 | 4061.6265 | 4316.6087 | 4588.8717 | 4879.6309 | 5190.1892 | 5521.9433 | 5876.3905 | 6255.1361 | 6659.9015 | 7092.5323 | 7553.2671
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 4792.567 | 5091.9908 | 5411.6575 | 5752.9889 | 6117.5087 | 6506.8503 | 6922.7646 | 7367.1289 | 7841.9558 | 8349.4032 | 8891.7849 | 9469.4001
|  |  | Annual opex, pre-replacement |  |  |  |  | 36817.8839 | 36817.8839 | 36817.8839 | 36817.8839 | 36817.8839 | 36817.8839 | 36817.8839 | 36817.8839 | 36817.8839 | 36817.8839 | 36817.8839 | 36817.8839
|  |  | Subtotal |  |  |  |  | 407195.2262 | 393480.7429 | 459736.12 | 500935.5153 | 553167.1477 | 632246.2545 | 710945.9563 | 754217.4626 | 800455.3664 | 849869.8031 | 902686.0938 | 958933.3593
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 56993.6283 | 854904.4248 | 3360344.3257 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 159236.3201
|  |  | Post-replacement opex |  |  | 16414.165
|  |  | Total annuity |  |  | 175650.4851
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 407195.2262 | 393480.7429 | 459736.12 | 500935.5153 | 553167.1477 | 632246.2545 | 710945.9563 | 754217.4626 | 800455.3664 | 849869.8031 | 902686.0938 | 958933.3593
|  |  | Annualised cost |  |  |  |  | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario D
Powercor - Robinvale Transformer No.2 Replacement Risk Monetisation Model
Scenario D | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario D: Consequence calculation
Consequence calculation
|  | Scenario |  |  | D
|  |  | PoF |  | 110%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 20445378.2524 | 0 | 0 | 0 | 0 | 20% | 4089075.6505 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 14935090.0929 | 0 | 0 | 20% | 2987018.0186 | 2987018.0186
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 10486413.1115 | 0 | 20% | 2097282.6223 | 2097282.6223
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2829163.7097 | 20% | 565832.7419 | 565832.7419
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 20% | 9326.2301 | 9326.2301
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 1843035.5183 | 0 | 0 | 0 | 0 | 76% | 1400706.9939 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 1005213.8055 | 0 | 0 | 80% | 804171.0444 | 804171.0444
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3495471.0372 | 0 | 80% | 2796376.8297 | 2796376.8297
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 953161.44 | 80% | 762529.152 | 762529.152
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 80% | 37304.9204 | 37304.9204
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 11018868.9947 | 0 | 3882852.6758 | 0 | 0 | 4% | 596068.8668 | 155314.107
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 1843035.5183 | 0 | 0 | 0 | 0 | 96% | 1769314.0976 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 241451.1423 | 0 | 0 | 100% | 241451.1423 | 241451.1423
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 30123.7232 | 0 | 100% | 30123.7232 | 30123.7232
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 69874.1883 | 100% | 69874.1883 | 69874.1883
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 11018868.9947 | 0 | 1011858.4192 | 0 | 0 | 4% | 481229.0966 | 40474.3368
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 12861904.513 | 8261.6388 | 1299940.712 | 30123.7232 | 69874.1883 | 18.55% | 2646885.0371 | 436816.1798
[5 empty] | 2 | Major |  | 12861904.513 | 28915.7357 | 4934697.6317 | 3495471.0372 | 953161.44 | 28.82% | 6420290.3958 | 4578828.6421
[5 empty] | 3 | Catastrophic |  | 20445378.2524 | 28915.7357 | 14981721.2433 | 10486413.1115 | 2829163.7097 | 20% | 9754318.4105 | 5665242.76
[5 empty] | Subtotal |  |  | 2025: 18821493.8434; 2026: 10680887.5819
Scenario D: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 31.5
|  |  | N-1 Rating before transfers, MVA |  |  | 20.4
|  |  | N-2 Rating before transfers, MVA |  |  | 10.6
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 0
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 24.9942 | 24.8399 | 25.1969 | 25.1716 | 25.1244 | 26.1135 | 26.2784 | 26.2784 | 26.2784 | 26.2784 | 26.2784 | 26.2784
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 22.1319 | 21.6752 | 22.1077 | 22.301 | 22.5907 | 22.68 | 23.0244 | 23.0244 | 23.0244 | 23.0244 | 23.0244 | 23.0244
|  |  | Weighting to 50% PoE |  |  | 70% |  | 22.9906 | 22.6246 | 23.0345 | 23.1622 | 23.3508 | 23.71 | 24.0006 | 24.0006 | 24.0006 | 24.0006 | 24.0006 | 24.0006
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 2.5906 | 2.2246 | 2.6345 | 2.7622 | 2.9508 | 3.3101 | 3.6006 | 3.6006 | 3.6006 | 3.6006 | 3.6006 | 3.6006
|  |  | N-2 |  |  |  |  | 12.3906 | 12.0246 | 12.4345 | 12.5622 | 12.7508 | 13.11 | 13.4006 | 13.4006 | 13.4006 | 13.4006 | 13.4006 | 13.4006
|  |  | N-3 |  |  |  |  | 22.9906 | 22.6246 | 23.0345 | 23.1622 | 23.3508 | 23.71 | 24.0006 | 24.0006 | 24.0006 | 24.0006 | 24.0006 | 24.0006
|  |  | N-4 |  |  |  |  | 22.9906 | 22.6246 | 23.0345 | 23.1622 | 23.3508 | 23.71 | 24.0006 | 24.0006 | 24.0006 | 24.0006 | 24.0006 | 24.0006
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | N-3 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | N-4 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | 3 | 3
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 1843035.5183 | 1582629.0894 | 1874260.3856 | 1965096.3631 | 2099333.4121 | 2354884.2995 | 2561580.9687 | 2561580.9687 | 2561580.9687 | 2561580.9687 | 2561580.9687 | 2561580.9687
|  |  | N-1 |  |  | Major |  | 1843035.5183 | 1582629.0894 | 1874260.3856 | 1965096.3631 | 2099333.4121 | 2354884.2995 | 2561580.9687 | 2561580.9687 | 2561580.9687 | 2561580.9687 | 2561580.9687 | 2561580.9687
|  |  | N-2 |  |  | Catastrophic |  | 11018868.9947 | 10693360.9585 | 11057900.0787 | 11171445.0506 | 11339241.3619 | 11658679.9711 | 11917050.8076 | 11917050.8076 | 11917050.8076 | 11917050.8076 | 11917050.8076 | 11917050.8076
|  |  | N-3 |  |  | Catastrophic |  | 20445378.2524 | 20119870.2162 | 20484409.3364 | 20597954.3083 | 20765750.6196 | 21085189.2288 | 25612272.0784 | 25612272.0784 | 25612272.0784 | 25612272.0784 | 25612272.0784 | 25612272.0784
|  |  | N-4 |  |  | Catastrophic |  | 20445378.2524 | 20119870.2162 | 20484409.3364 | 20597954.3083 | 20765750.6196 | 21085189.2288 | 25612272.0784 | 25612272.0784 | 25612272.0784 | 25612272.0784 | 25612272.0784 | 25612272.0784
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 13.11% | 13.93% | 14.81% | 15.74% | 16.74% | 17.81% | 18.94% | 20.16% | 21.46% | 22.85% | 24.33% | 25.91%
|  |  | Major |  |  |  |  | 0.07051% | 0.07491% | 0.07962% | 0.08464% | 0.09% | 0.09573% | 0.1018% | 0.1084% | 0.1154% | 0.1228% | 0.1308% | 0.1393%
|  |  | Catastrophic |  |  |  |  | 0.07051% | 0.07491% | 0.07962% | 0.08464% | 0.09% | 0.09573% | 0.1018% | 0.1084% | 0.1154% | 0.1228% | 0.1308% | 0.1393%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 232037.7222 | 211701.2611 | 266450.7366 | 296984.7055 | 337374.8536 | 402528.9156 | 465848.122 | 495750.3776 | 527702.5267 | 561849.7807 | 598347.8452 | 637216.8436
|  |  | Network Performance |  |  | Major |  | 987.6158 | 901.0582 | 1134.0869 | 1264.0478 | 1435.9593 | 1713.2727 | 1982.7765 | 2110.0487 | 2246.0457 | 2391.3857 | 2546.7314 | 2712.1685
|  |  | Network Performance |  |  | Catastrophic |  | 2883.1408 | 3014.5 | 3261.792 | 3486.7446 | 3737.8747 | 4036.9264 | 5217.1123 | 5551.9928 | 5909.8303 | 6292.2512 | 6700.9992 | 7136.2998
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 57803.0383 | 59600.1409 | 65501.0736 | 70347.4475 | 75928.3652 | 83035.8525 | 90301.26 | 96097.5941 | 102291.2851 | 108910.4812 | 115985.3647 | 123519.8365
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 310.769 | 320.4309 | 352.1563 | 378.2121 | 408.217 | 446.4293 | 485.4906 | 516.6537 | 549.9531 | 585.5402 | 623.5772 | 664.0851
|  |  | Other significant risks |  |  | Significant |  | 57286.5109 | 60865.5828 | 64686.6235 | 68766.6259 | 73123.8038 | 77777.6814 | 82749.1887 | 88060.764 | 93736.4645 | 99802.0842 | 106285.2814 | 113189.6305
|  |  | Other major risks |  |  | Major |  | 3228.4577 | 3430.1611 | 3645.5009 | 3875.4349 | 4120.9895 | 4383.2649 | 4663.4409 | 4962.7818 | 5282.6435 | 5624.4795 | 5989.8488 | 6378.9526
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 3994.4707 | 4244.032 | 4510.4653 | 4794.9555 | 5098.7725 | 5423.2779 | 5769.9308 | 6140.2961 | 6536.051 | 6958.9942 | 7411.0542 | 7892.4803
|  |  | Annual opex, pre-replacement |  |  |  |  | 30123.7232 | 30123.7232 | 30123.7232 | 30123.7232 | 30123.7232 | 30123.7232 | 30123.7232 | 30123.7232 | 30123.7232 | 30123.7232 | 30123.7232 | 30123.7232
|  |  | Subtotal |  |  |  |  | 388655.4485 | 374200.8902 | 439666.1583 | 480021.897 | 531352.5589 | 609469.3439 | 687141.0451 | 729314.232 | 774378.5231 | 822538.7202 | 874014.4254 | 928834.0201
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 0 | 0 | 46631.1504 | 699467.2566 | 2749372.6301 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 0% | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 130284.2619
|  |  | Post-replacement opex |  |  | 13429.7713
|  |  | Total annuity |  |  | 143714.0332
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 388655.4485 | 374200.8902 | 439666.1583 | 480021.897 | 531352.5589 | 609469.3439 | 687141.0451 | 729314.232 | 774378.5231 | 822538.7202 | 874014.4254 | 928834.0201
|  |  | Annualised cost |  |  |  |  | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Summary
Powercor - Robinvale Transformer No.2 Replacement Risk Monetisation Model
Summary |  |  |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Risk cost vs annualised cost
Risks vs benefits
|  | Year |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost | Scenario Base case | 245159.0501 | 229663.9421 | 276164.396 | 302790.8672 | 337642.4679 | 393017.7997 | 460719.4684 | 488144.0692 | 517448.7125 | 548766.5777 | 582240.4688 | 617888.842
|  |  | Annualised cost | Scenario Base case | 159682.2592 | 159682.2592 | 159682.2592 | 159682.2592 | 159682.2592 | 159682.2592 | 159682.2592 | 159682.2592 | 159682.2592 | 159682.2592 | 159682.2592 | 159682.2592
|  |  | Risk cost | Scenario A | 149303.1077 | 134230.2418 | 166650.0418 | 183548.9407 | 206533.1779 | 245049.3472 | 282208.777 | 297960.1365 | 314791.301 | 332778.7625 | 352004.5407 | 372479.2357
|  |  | Annualised cost | Scenario A | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851
|  |  | Risk cost | Scenario B | 132917.0786 | 117238.6967 | 149012.044 | 165220.6783 | 187467.7577 | 225196.573 | 261514.9114 | 276367.6458 | 292238.5818 | 309199.8473 | 327328.7827 | 346635.3835
|  |  | Annualised cost | Scenario B | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332
|  |  | Risk cost | Scenario C | 407195.2262 | 393480.7429 | 459736.12 | 500935.5153 | 553167.1477 | 632246.2545 | 710945.9563 | 754217.4626 | 800455.3664 | 849869.8031 | 902686.0938 | 958933.3593
|  |  | Annualised cost | Scenario C | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851 | 175650.4851
|  |  | Risk cost | Scenario D | 388655.4485 | 374200.8902 | 439666.1583 | 480021.897 | 531352.5589 | 609469.3439 | 687141.0451 | 729314.232 | 774378.5231 | 822538.7202 | 874014.4254 | 928834.0201
|  |  | Annualised cost | Scenario D | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332 | 143714.0332
Charts
End