## Inputs
Powercor - Warrnambool Transformer Replacement Risk Monetisation Model
Inputs | [8 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
General inputs, timing and costs
General inputs
|  | Company |  | Powercor
|  | Title |  | Warrnambool Transformer Replacement Risk Monetisation Model
|  | Model start & timeline |  | 2019 | FY19/20
|  | Real WACC |  | 2.75%
|  | Asset Life (years) |  | 50
Inflation
|  | Year | [6 empty] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021
|  |  | Nominal escalation index to June $2021 | [5 empty] | 125.4% | 122% | 117.9% | 115.6% | 113.1% | 110.6% | 108.9% | 107.8% | 105.8% | 103.6% | 102% | 100%
Capex
|  | Replacement capex regulator, real $2019 |  | 3748000 |  |  |  |  | 0 | 50000 | 750000 | 2948000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Capex ($2021) | 3883856.708 |  |  |  |  | 0 | 51812.3894 | 777185.8407 | 3054858.4779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex
|  |  |  | Pre-replacement | Post-replacement
|  | Annual opex, real $2019 |  | 16200 | 4100
|  |  | Opex ($2021) | 16787.2142 | 4248.6159
Scenario manager
Sensitivity bounds
|  | Bound |  | Lower | Central | Upper
|  |  | PoF | -10% | 0% | 10%
|  |  | Capex | -10% | 0% | 10%
|  |  | Opex | -10% | 0% | 10%
|  |  | Demand | -5% | 0% | 5%
|  |  | VCR | -10% | 0% | 10%
|  |  | Environment | -10% | 0% | 10%
Scenario selection
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | Central | Central | Central | Central | Central | 2010: Central
|  |  | A | Lower | Upper | Upper | Lower | Lower | 2010: Lower
|  |  | B | Lower | Lower | Lower | Lower | Lower | 2010: Lower
|  |  | C | Upper | Upper | Upper | Upper | Upper | 2010: Upper
|  |  | D | Upper | Lower | Lower | Upper | Upper | 2010: Upper
Scenario output
|  | Element |  | PoF | Capex | Opex | Demand | VCR | 2010: Environment
|  |  | Base case | 100% | 100% | 100% | 100% | 100% | 2010: 100%
|  |  | A | 90% | 110% | 110% | 95% | 90% | 2010: 90%
|  |  | B | 90% | 90% | 90% | 95% | 90% | 2010: 90%
|  |  | C | 110% | 110% | 110% | 105% | 110% | 2010: 110%
|  |  | D | 110% | 90% | 90% | 105% | 110% | 2010: 110%
Network assumptions
Probability of failure (PoF)
|  | Failure mode |  | Failure code
|  |  | Significant | 1 |  |  |  |  | 38.16% | 41.11% | 44.3% | 47.74% | 51.47% | 55.49% | 59.85% | 64.56% | 69.65% | 75.16% | 81.12% | 87.55%
|  |  | Major | 2 |  |  |  |  | 0.2052% | 0.221% | 0.2382% | 0.2567% | 0.2767% | 0.2983% | 0.3218% | 0.3471% | 0.3745% | 0.4041% | 0.4361% | 0.4707%
|  |  | Catastrophic | 3 |  |  |  |  | 0.2052% | 0.221% | 0.2382% | 0.2567% | 0.2767% | 0.2983% | 0.3218% | 0.3471% | 0.3745% | 0.4041% | 0.4361% | 0.4707%
Value of customer reliability (VCR)
|  | Sector |  | MWh | $/MWh ($2018) | Load Duration | Duration Weighted $/MWh ($2021)
|  |  | Residential | 58186 | 26450 | 20% | 1404.9718
|  |  | Agricultural | 15590 | 50930 | 15% | 543.6313
|  |  | Commercial | 145450 | 47770 | 40% | 12685.9324
|  |  | Industrial | 12514 | 47070 | 80% | 2150.9176
|  |  | Total | 231740 | 42591.6928 | 37.26% | 16785.4532
Asset information
|  | Assets at risk |  | 3
|  | N-rating, MVA |  | 98.9
|  |  | N-1 Rating before transfers, MVA | 59
|  |  | N-2 Rating before transfers, MVA | 19.05
|  |  | N-3 Rating before transfers, MVA | 0
|  |  | N-4 Rating before transfers, MVA | 0
|  |  | Transfer capacity, MVA | 12.3
Environmental assumptions
Environmental consequence
|  | Settings |  | Real $2019 | Real $2021
|  |  | Value Consequence Loss Oil / litre | 100 | 103.6248
|  |  | Value Consequence Loss SF6/Kg | 598 | 619.6762
|  |  | Value Consequence Fire | 10000 | 10362.4779
|  |  | Value Consequence Waste / tonne | 1000 | 1036.2478
|  |  | Value Consequence Disturbance | 400 | 414.4991
|  |  | Value Fire brigade attendance | 50000 | 51812.3894
|  | Failure Mode |  | Significant | Major | Catastrophic
|  |  | Average Consequence Loss Oil | 500 | 4050 | 12150
|  |  | Average Consequences Loss SF6 kgs | 0 | 0 | 0
|  |  | Average Consequence Fire | 0.05 | 2.5 | 5
|  |  | Average Consequence Waste | 10 | 405 | 1215
|  |  | Average Consequence Disturbance | 2 | 3 | 5
|  |  | Average Cost of Fault (Air Insulated) | 11709.6 | 446830.046 | 1312925.9469
|  |  | Average Cost of Fault (SF6 Insulated) | 11709.6 | 446830.046 | 1312925.9469
|  |  | Average Cost of Fault (Oil Insulated) | 63521.9894 | 866510.4 | 2571967.0088
Generation assumptions
Generation requirements
Generator detail
|  |  | Generator capacity, MVA | 1
|  |  | Generators per site | 4
|  |  | Step-up transformer capacity | 5
|  |  | Number of transformers required per site | 1
|  |  | Generator sites connected per day | 3
|  |  | Fuel usage / MWh in Litres | 270
|  |  | Days in week | 7
|  |  | Setup, persons required | 5
|  |  | Setup, hours employed per day | 16
|  |  | Hours per day | 24
|  | Generator detail by failure mode |  | Significant | Major | Coincidental | Catastrophic
|  |  | Switching time only (hours required) | 0 | 0 | 0 | 0
|  |  | Number of weeks generation required | 1.1905 | 6 | 6 | 12
|  |  | Max demand load net of transfers, MVA | 0 | 0 | 21.3552 | 40.4052
|  |  | Number of generators | 0 | 0 | 22 | 41
|  |  | Generator sites | 0 | 0 | 6 | 11
|  |  | Number of days to connect all generators | 0 | 0 | 2 | 4
|  | Generation costs |  | Real $2019 | Real $2021
|  |  | Generator hire per week | 7000 | 7253.7345
|  |  | Fuel cost $ per litre including delivery | 1.5 | 1.5544
|  |  | Fitter cost (blended 24hr rate) $ per hr | 150 | 155.4372
|  |  | Traffic management and security per site | 10000 | 10362.4779
|  |  | Transformer hire per week | 7000 | 7253.7345
|  |  | Earthing and bunding per site | 2000 | 2072.4956
|  |  | Temporary fencing per site per week | 3000 | 3108.7434
|  |  | Miscellaneous material per site | 2000 | 2072.4956
|  |  | Install and remove step down transformers per site | 2500 | 2590.6195
|  |  | Council permits per site | 4000 | 4144.9912
|  |  | Crane hire to install / remove generators per site | 2500 | 2590.6195
|  |  | Cable hire per site | 3000 | 3108.7434
|  | Generation costs by failure mode |  | Significant | Major | Coincidental | Catastrophic
|  |  | Generator hire | 0 | 0 | 1010687.0088 | 3667971.7522
|  |  | Fuel cost | 0 | 0 | 3365858.609 | 12736784.5163
|  |  | Fitter cost | 0 | 0 | 1014693.8336 | 3583759.3487
|  |  | Traffic management cost | 0 | 0 | 2611344.4248 | 9574929.5575
|  |  | Transformer hire | 0 | 0 | 275641.9115 | 984089.9823
|  |  | Earthing and bunding | 0 | 0 | 12434.9735 | 22797.4513
|  |  | Temporary fencing | 0 | 0 | 111914.7611 | 410354.1239
|  |  | Miscellaneous materials | 0 | 0 | 12434.9735 | 22797.4513
|  |  | Installation & removal of step-down transformers | 0 | 0 | 15543.7168 | 28496.8142
|  |  | Council permits | 0 | 0 | 24869.9469 | 45594.9027
|  |  | Crane hire | 0 | 0 | 15543.7168 | 28496.8142
|  |  | Cable hire | 0 | 0 | 18652.4602 | 34196.177
|  |  | Total | 0 | 0 | 8489620.3364 | 31140268.8915
Safety assumptions
Safety consequence
|  | Value of consquence |  | Base Value ($2018) | Disproportion Factor | Reference Value ($2021)
|  |  | Minor | 127274.0425 | 1 | 134627.6539
|  |  | Serious | 672376.8885 | 2 | 1422450.662
|  |  | Fataility | 4500000 | 3 | 14280000
|  | Probability of event, by failure mode |  | Significant | Major | Catastrophic
|  |  | Minor | 1.172% | 4.103% | 4.103%
|  |  | Serious | 0.2345% | 0.8206% | 0.8206%
|  |  | Fataility | 0.02345% | 0.08206% | 0.08206%
|  |  | Value of event | 8261.6388 | 28915.7357 | 28915.7357
|  |  | Weighted likelyhood of consequence | 0.05217% | 0.1826% | 0.1826%
Base Case PoE, Load and VCR assumptions
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA | 10% |  |  |  |  | 49.722 | 50.829 | 52.928 | 54.759 | 57.465 | 58.552 | 60.924 | 60.924 | 60.924 | 60.924 | 60.924 | 60.924
|  |  | 50% PoE forecast, MVA | 50% |  |  |  |  | 44.816 | 45.594 | 46.667 | 48.885 | 49.566 | 50.767 | 53.599 | 53.599 | 53.599 | 53.599 | 53.599 | 53.599
|  |  | Weighting to 50% PoE | 70% |  |  |  |  | 46.2878 | 47.1645 | 48.5453 | 50.6472 | 51.9357 | 53.1025 | 55.7965 | 55.7965 | 55.7965 | 55.7965 | 55.7965 | 55.7965
Load at risk
Selected profile, MVA
|  |  | N | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 | [5 empty] | 14.9378 | 15.8145 | 17.1953 | 19.2972 | 20.5857 | 21.7525 | 24.4465 | 24.4465 | 24.4465 | 24.4465 | 24.4465 | 24.4465
|  |  | N-3 | [5 empty] | 33.9878 | 34.8645 | 36.2453 | 38.3472 | 39.6357 | 40.8025 | 43.4965 | 43.4965 | 43.4965 | 43.4965 | 43.4965 | 43.4965
|  |  | N-4 | [5 empty] | 33.9878 | 34.8645 | 36.2453 | 38.3472 | 39.6357 | 40.8025 | 43.4965 | 43.4965 | 43.4965 | 43.4965 | 43.4965 | 43.4965
End

## Base Case
Powercor - Warrnambool Transformer Replacement Risk Monetisation Model
Base Case | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario Base case: Consequence calculation
Consequence calculation
|  | Scenario |  |  | Base case
|  |  | PoF |  | 100%
|  |  | Capex |  | 100%
|  |  | Opex |  | 100%
|  |  | Demand |  | 100%
|  |  | VCR |  | 100%
|  |  | Environment |  | 100%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 41076045.0856 | 0 | 0 | 0 | 0 | 20% | 8215209.0171 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 31140268.8915 | 0 | 0 | 20% | 6228053.7783 | 6228053.7783
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 11651570.1239 | 0 | 20% | 2330314.0248 | 2330314.0248
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2571967.0088 | 20% | 514393.4018 | 514393.4018
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 20% | 10362.4779 | 10362.4779
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3883856.708 | 0 | 80% | 3107085.3664 | 3107085.3664
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 866510.4 | 80% | 693208.32 | 693208.32
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 80% | 41449.9115 | 41449.9115
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 15044264.5665 | 0 | 8489620.3364 | 0 | 0 | 4% | 941355.3961 | 339584.8135
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 16787.2142 | 0 | 100% | 16787.2142 | 16787.2142
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 63521.9894 | 100% | 63521.9894 | 63521.9894
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 51812.3894 | 0 | 0 | 100% | 51812.3894 | 51812.3894
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 15044264.5665 | 0 | 1684448.4794 | 0 | 0 | 4% | 669148.5218 | 67377.9392
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 15044264.5665 | 8261.6388 | 1736260.8688 | 16787.2142 | 63521.9894 | 4.799% | 809531.7535 | 207761.1709
[5 empty] | 2 | Major |  | 15044264.5665 | 28915.7357 | 8541432.7258 | 3883856.708 | 866510.4 | 16.94% | 4806231.5825 | 4204460.9999
[5 empty] | 3 | Catastrophic |  | 41076045.0856 | 28915.7357 | 31192081.2809 | 11651570.1239 | 2571967.0088 | 20% | 17304115.847 | 9088906.8299
[5 empty] | Subtotal |  |  | 2025: 22919879.183; 2026: 13501129.0006
Scenario Base case: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 98.9
|  |  | N-1 Rating before transfers, MVA |  |  | 59
|  |  | N-2 Rating before transfers, MVA |  |  | 19.05
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 12.3
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 49.722 | 50.829 | 52.928 | 54.759 | 57.465 | 58.552 | 60.924 | 60.924 | 60.924 | 60.924 | 60.924 | 60.924
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 44.816 | 45.594 | 46.667 | 48.885 | 49.566 | 50.767 | 53.599 | 53.599 | 53.599 | 53.599 | 53.599 | 53.599
|  |  | Weighting to 50% PoE |  |  | 70% |  | 46.2878 | 47.1645 | 48.5453 | 50.6472 | 51.9357 | 53.1025 | 55.7965 | 55.7965 | 55.7965 | 55.7965 | 55.7965 | 55.7965
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 14.9378 | 15.8145 | 17.1953 | 19.2972 | 20.5857 | 21.7525 | 24.4465 | 24.4465 | 24.4465 | 24.4465 | 24.4465 | 24.4465
|  |  | N-3 |  |  |  |  | 33.9878 | 34.8645 | 36.2453 | 38.3472 | 39.6357 | 40.8025 | 43.4965 | 43.4965 | 43.4965 | 43.4965 | 43.4965 | 43.4965
|  |  | N-4 |  |  |  |  | 33.9878 | 34.8645 | 36.2453 | 38.3472 | 39.6357 | 40.8025 | 43.4965 | 43.4965 | 43.4965 | 43.4965 | 43.4965 | 43.4965
VCR at risk
Average load at risk (pu)
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Days to connect generators, plus 1 day lead time | bar: 2019 to 2030
|  |  |  | Adjustment |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Adjustment |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Adjustment |  |  |  | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Days to connect generators, plus 1 day lead time |  |  |  | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Adjustment |  |  |  | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 15044264.5665 | 15927212.9756 | 17317854.2021 | 19434734.8467 | 20732418.2334 | 21907534.2408 | 29544881.8748 | 29544881.8748 | 29544881.8748 | 29544881.8748 | 29544881.8748 | 29544881.8748
|  |  | N-3 |  |  | Catastrophic |  | 41076045.0856 | 42135583.1765 | 51105078.0897 | 54068710.9921 | 55885467.7335 | 57530630.1439 | 61329111.0607 | 61329111.0607 | 61329111.0607 | 61329111.0607 | 61329111.0607 | 61329111.0607
|  |  | N-4 |  |  | Catastrophic |  | 41076045.0856 | 42135583.1765 | 51105078.0897 | 54068710.9921 | 55885467.7335 | 57530630.1439 | 61329111.0607 | 61329111.0607 | 61329111.0607 | 61329111.0607 | 61329111.0607 | 61329111.0607
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 38.16% | 41.11% | 44.3% | 47.74% | 51.47% | 55.49% | 59.85% | 64.56% | 69.65% | 75.16% | 81.12% | 87.55%
|  |  | Major |  |  |  |  | 0.2052% | 0.221% | 0.2382% | 0.2567% | 0.2767% | 0.2983% | 0.3218% | 0.3471% | 0.3745% | 0.4041% | 0.4361% | 0.4707%
|  |  | Catastrophic |  |  |  |  | 0.2052% | 0.221% | 0.2382% | 0.2567% | 0.2767% | 0.2983% | 0.3218% | 0.3471% | 0.3745% | 0.4041% | 0.4361% | 0.4707%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 16856.4559 | 18626.8499 | 24342.8329 | 27756.8852 | 30927.1164 | 34328.1907 | 39465.9386 | 42571.264 | 45930.1896 | 49563.8507 | 53495.1662 | 57738.3065
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 229663.2719 | 261922.6967 | 306862.6847 | 371147.2726 | 426808.8731 | 486282.0311 | 707263.0404 | 762913.1018 | 823107.8936 | 888226.1771 | 958678.6789 | 1034719.3464
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 1234.7488 | 1408.1865 | 1649.7994 | 1995.4154 | 2294.6714 | 2614.4195 | 3802.4895 | 4101.6833 | 4425.3113 | 4775.4096 | 5154.1864 | 5563.0072
|  |  | Other significant risks |  |  | Significant |  | 79291.1978 | 85415.7068 | 92035.2919 | 99190.9493 | 106927.1204 | 115291.9848 | 124337.777 | 134121.1313 | 144703.4553 | 156151.3356 | 168536.9785 | 181905.0283
|  |  | Other major risks |  |  | Major |  | 8626.9639 | 9293.3167 | 10013.5344 | 10792.0773 | 11633.7807 | 12543.8865 | 13528.078 | 14592.517 | 15743.8847 | 16989.4259 | 18336.9966 | 19791.4541
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 18649.1611 | 20089.6357 | 21646.5514 | 23329.5504 | 25149.0853 | 27116.4879 | 29244.0435 | 31545.0726 | 34034.018 | 36726.5409 | 39639.624 | 42783.7677
|  |  | Annual opex, pre-replacement |  |  |  |  | 16787.2142 | 16787.2142 | 16787.2142 | 16787.2142 | 16787.2142 | 16787.2142 | 16787.2142 | 16787.2142 | 16787.2142 | 16787.2142 | 16787.2142 | 16787.2142
|  |  | Subtotal |  |  |  |  | 371109.0134 | 413543.6065 | 473337.9089 | 550999.3644 | 620527.8613 | 694964.2146 | 934428.5812 | 1006631.9842 | 1084731.9667 | 1169219.9539 | 1260628.8447 | 1359288.1244
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 51812.3894 | 777185.8407 | 3054858.4779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 144760.291
|  |  | Post-replacement opex |  |  | 4248.6159
|  |  | Total annuity |  |  | 149008.907
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 371109.0134 | 413543.6065 | 473337.9089 | 550999.3644 | 620527.8613 | 694964.2146 | 934428.5812 | 1006631.9842 | 1084731.9667 | 1169219.9539 | 1260628.8447 | 1359288.1244
|  |  | Annualised cost |  |  |  |  | 149008.907 | 149008.907 | 149008.907 | 149008.907 | 149008.907 | 149008.907 | 149008.907 | 149008.907 | 149008.907 | 149008.907 | 149008.907 | 149008.907
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario A
Powercor - Warrnambool Transformer Replacement Risk Monetisation Model
Scenario A | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario A: Consequence calculation
Consequence calculation
|  | Scenario |  |  | A
|  |  | PoF |  | 90%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 34451084.6674 | 0 | 0 | 0 | 0 | 20% | 6890216.9335 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 34254295.7807 | 0 | 0 | 20% | 6850859.1561 | 6850859.1561
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 12816727.1363 | 0 | 20% | 2563345.4273 | 2563345.4273
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2314770.308 | 20% | 462954.0616 | 462954.0616
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 20% | 11398.7257 | 11398.7257
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 4272242.3788 | 0 | 80% | 3417793.903 | 3417793.903
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 779859.36 | 80% | 623887.488 | 623887.488
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 80% | 45594.9027 | 45594.9027
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 11442041.5184 | 0 | 9338582.37 | 0 | 0 | 4% | 831224.9555 | 373543.2948
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 18465.9356 | 0 | 100% | 18465.9356 | 18465.9356
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 57169.7904 | 100% | 57169.7904 | 57169.7904
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 11442041.5184 | 0 | 1852893.3274 | 0 | 0 | 4% | 531797.3938 | 74115.7331
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 11442041.5184 | 8261.6388 | 1909886.9557 | 18465.9356 | 57169.7904 | 5.007% | 672688.3869 | 215006.7262
[5 empty] | 2 | Major |  | 11442041.5184 | 28915.7357 | 9395575.9983 | 4272242.3788 | 779859.36 | 19.07% | 4941633.8377 | 4483952.177
[5 empty] | 3 | Catastrophic |  | 34451084.6674 | 28915.7357 | 34311289.409 | 12816727.1363 | 2314770.308 | 20% | 16784557.4512 | 9894340.5178
[5 empty] | Subtotal |  |  | 2025: 22398879.6759; 2026: 14593299.421
Scenario A: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 98.9
|  |  | N-1 Rating before transfers, MVA |  |  | 59
|  |  | N-2 Rating before transfers, MVA |  |  | 19.05
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 12.3
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 47.2359 | 48.2875 | 50.2816 | 52.021 | 54.5917 | 55.6244 | 57.8778 | 57.8778 | 57.8778 | 57.8778 | 57.8778 | 57.8778
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 42.5752 | 43.3143 | 44.3336 | 46.4407 | 47.0877 | 48.2287 | 50.919 | 50.919 | 50.919 | 50.919 | 50.919 | 50.919
|  |  | Weighting to 50% PoE |  |  | 70% |  | 43.9734 | 44.8063 | 46.118 | 48.1148 | 49.3389 | 50.4474 | 53.0067 | 53.0067 | 53.0067 | 53.0067 | 53.0067 | 53.0067
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 12.6234 | 13.4563 | 14.768 | 16.7648 | 17.9889 | 19.0974 | 21.6567 | 21.6567 | 21.6567 | 21.6567 | 21.6567 | 21.6567
|  |  | N-3 |  |  |  |  | 31.6734 | 32.5063 | 33.818 | 35.8148 | 37.0389 | 38.1474 | 40.7067 | 40.7067 | 40.7067 | 40.7067 | 40.7067 | 40.7067
|  |  | N-4 |  |  |  |  | 31.6734 | 32.5063 | 33.818 | 35.8148 | 37.0389 | 38.1474 | 40.7067 | 40.7067 | 40.7067 | 40.7067 | 40.7067 | 40.7067
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 11442041.5184 | 12196962.4082 | 13385960.6569 | 15195893.608 | 16305412.9036 | 17310137.09 | 19629923.6499 | 19629923.6499 | 19629923.6499 | 19629923.6499 | 19629923.6499 | 19629923.6499
|  |  | N-3 |  |  | Catastrophic |  | 34451084.6674 | 35356989.7351 | 36783787.6335 | 38955707.1748 | 47001652.0512 | 48408265.9121 | 51655967.096 | 51655967.096 | 51655967.096 | 51655967.096 | 51655967.096 | 51655967.096
|  |  | N-4 |  |  | Catastrophic |  | 34451084.6674 | 35356989.7351 | 36783787.6335 | 38955707.1748 | 47001652.0512 | 48408265.9121 | 51655967.096 | 51655967.096 | 51655967.096 | 51655967.096 | 51655967.096 | 51655967.096
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 34.35% | 37% | 39.87% | 42.97% | 46.32% | 49.94% | 53.86% | 58.1% | 62.68% | 67.64% | 73.01% | 78.8%
|  |  | Major |  |  |  |  | 0.1847% | 0.1989% | 0.2143% | 0.231% | 0.249% | 0.2685% | 0.2896% | 0.3124% | 0.337% | 0.3637% | 0.3925% | 0.4237%
|  |  | Catastrophic |  |  |  |  | 0.1847% | 0.1989% | 0.2143% | 0.231% | 0.249% | 0.2685% | 0.2896% | 0.3124% | 0.337% | 0.3637% | 0.3925% | 0.4237%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 12723.9823 | 14067.2174 | 15769.0677 | 17998.583 | 23409.7174 | 25996.4363 | 29917.0503 | 32271.0341 | 34817.2587 | 37571.7459 | 40551.8692 | 43768.3705
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 157205.0939 | 180520.9211 | 213472.5584 | 261177.889 | 302104.9135 | 345810.1527 | 422921.5601 | 456198.5864 | 492193.2218 | 531131.9538 | 573260.3845 | 618730.3666
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 845.1887 | 970.5426 | 1147.7019 | 1404.1822 | 1624.22 | 1859.1944 | 2273.7718 | 2452.6806 | 2646.2001 | 2855.5481 | 3082.0451 | 3326.5073
|  |  | Other significant risks |  |  | Significant |  | 73850.7908 | 79555.0789 | 85720.4744 | 92385.1606 | 99590.5298 | 107381.4558 | 115806.5891 | 124918.6781 | 134774.9171 | 145437.3239 | 156973.1507 | 169423.9785
|  |  | Other major risks |  |  | Major |  | 8280.3965 | 8919.9802 | 9611.2649 | 10358.5317 | 11166.4217 | 12039.9662 | 12984.6202 | 14006.298 | 15111.4123 | 16306.9168 | 17600.3521 | 18996.3804
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 18271.6182 | 19682.9311 | 21208.3278 | 22857.2554 | 24639.9547 | 26567.5282 | 28652.0125 | 30906.4584 | 33345.0164 | 35983.0305 | 38837.1397 | 41917.6317
|  |  | Annual opex, pre-replacement |  |  |  |  | 18465.9356 | 18465.9356 | 18465.9356 | 18465.9356 | 18465.9356 | 18465.9356 | 18465.9356 | 18465.9356 | 18465.9356 | 18465.9356 | 18465.9356 | 18465.9356
|  |  | Subtotal |  |  |  |  | 289643.0058 | 322182.6068 | 365395.3307 | 424647.5375 | 481001.6926 | 538120.6691 | 631021.5397 | 679219.6711 | 731353.9619 | 787752.4547 | 848770.8769 | 914629.1706
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 56993.6283 | 854904.4248 | 3360344.3257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 159236.3201
|  |  | Post-replacement opex |  |  | 4673.4775
|  |  | Total annuity |  |  | 163909.7976
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 289643.0058 | 322182.6068 | 365395.3307 | 424647.5375 | 481001.6926 | 538120.6691 | 631021.5397 | 679219.6711 | 731353.9619 | 787752.4547 | 848770.8769 | 914629.1706
|  |  | Annualised cost |  |  |  |  | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario B
Powercor - Warrnambool Transformer Replacement Risk Monetisation Model
Scenario B | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario B: Consequence calculation
Consequence calculation
|  | Scenario |  |  | B
|  |  | PoF |  | 90%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 95%
|  |  | VCR |  | 90%
|  |  | Environment |  | 90%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 34451084.6674 | 0 | 0 | 0 | 0 | 20% | 6890216.9335 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 28026242.0024 | 0 | 0 | 20% | 5605248.4005 | 5605248.4005
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 10486413.1115 | 0 | 20% | 2097282.6223 | 2097282.6223
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2314770.308 | 20% | 462954.0616 | 462954.0616
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 20% | 9326.2301 | 9326.2301
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3495471.0372 | 0 | 80% | 2796376.8297 | 2796376.8297
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 779859.36 | 80% | 623887.488 | 623887.488
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 80% | 37304.9204 | 37304.9204
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 11442041.5184 | 0 | 7640658.3028 | 0 | 0 | 4% | 763307.9928 | 305626.3321
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 15108.4927 | 0 | 100% | 15108.4927 | 15108.4927
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 57169.7904 | 100% | 57169.7904 | 57169.7904
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 11442041.5184 | 0 | 1516003.6315 | 0 | 0 | 4% | 518321.806 | 60640.1453
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 11442041.5184 | 8261.6388 | 1562634.7819 | 15108.4927 | 57169.7904 | 4.933% | 645492.8784 | 187811.2176
[5 empty] | 2 | Major |  | 11442041.5184 | 28915.7357 | 7687289.4532 | 3495471.0372 | 779859.36 | 18.11% | 4244009.8195 | 3786328.1587
[5 empty] | 3 | Catastrophic |  | 34451084.6674 | 28915.7357 | 28072873.1528 | 10486413.1115 | 2314770.308 | 20% | 15070811.3951 | 8180594.4616
[5 empty] | Subtotal |  |  | 2025: 19960314.0929; 2026: 12154733.838
Scenario B: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 98.9
|  |  | N-1 Rating before transfers, MVA |  |  | 59
|  |  | N-2 Rating before transfers, MVA |  |  | 19.05
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 12.3
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 47.2359 | 48.2875 | 50.2816 | 52.021 | 54.5917 | 55.6244 | 57.8778 | 57.8778 | 57.8778 | 57.8778 | 57.8778 | 57.8778
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 42.5752 | 43.3143 | 44.3336 | 46.4407 | 47.0877 | 48.2287 | 50.919 | 50.919 | 50.919 | 50.919 | 50.919 | 50.919
|  |  | Weighting to 50% PoE |  |  | 70% |  | 43.9734 | 44.8063 | 46.118 | 48.1148 | 49.3389 | 50.4474 | 53.0067 | 53.0067 | 53.0067 | 53.0067 | 53.0067 | 53.0067
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 12.6234 | 13.4563 | 14.768 | 16.7648 | 17.9889 | 19.0974 | 21.6567 | 21.6567 | 21.6567 | 21.6567 | 21.6567 | 21.6567
|  |  | N-3 |  |  |  |  | 31.6734 | 32.5063 | 33.818 | 35.8148 | 37.0389 | 38.1474 | 40.7067 | 40.7067 | 40.7067 | 40.7067 | 40.7067 | 40.7067
|  |  | N-4 |  |  |  |  | 31.6734 | 32.5063 | 33.818 | 35.8148 | 37.0389 | 38.1474 | 40.7067 | 40.7067 | 40.7067 | 40.7067 | 40.7067 | 40.7067
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Unserved energy day 1 |  |  |  | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1 | 1 | 1 | 1 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 11442041.5184 | 12196962.4082 | 13385960.6569 | 15195893.608 | 16305412.9036 | 17310137.09 | 19629923.6499 | 19629923.6499 | 19629923.6499 | 19629923.6499 | 19629923.6499 | 19629923.6499
|  |  | N-3 |  |  | Catastrophic |  | 34451084.6674 | 35356989.7351 | 36783787.6335 | 38955707.1748 | 47001652.0512 | 48408265.9121 | 51655967.096 | 51655967.096 | 51655967.096 | 51655967.096 | 51655967.096 | 51655967.096
|  |  | N-4 |  |  | Catastrophic |  | 34451084.6674 | 35356989.7351 | 36783787.6335 | 38955707.1748 | 47001652.0512 | 48408265.9121 | 51655967.096 | 51655967.096 | 51655967.096 | 51655967.096 | 51655967.096 | 51655967.096
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 34.35% | 37% | 39.87% | 42.97% | 46.32% | 49.94% | 53.86% | 58.1% | 62.68% | 67.64% | 73.01% | 78.8%
|  |  | Major |  |  |  |  | 0.1847% | 0.1989% | 0.2143% | 0.231% | 0.249% | 0.2685% | 0.2896% | 0.3124% | 0.337% | 0.3637% | 0.3925% | 0.4237%
|  |  | Catastrophic |  |  |  |  | 0.1847% | 0.1989% | 0.2143% | 0.231% | 0.249% | 0.2685% | 0.2896% | 0.3124% | 0.337% | 0.3637% | 0.3925% | 0.4237%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 12723.9823 | 14067.2174 | 15769.0677 | 17998.583 | 23409.7174 | 25996.4363 | 29917.0503 | 32271.0341 | 34817.2587 | 37571.7459 | 40551.8692 | 43768.3705
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 157205.0939 | 180520.9211 | 213472.5584 | 261177.889 | 302104.9135 | 345810.1527 | 422921.5601 | 456198.5864 | 492193.2218 | 531131.9538 | 573260.3845 | 618730.3666
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 845.1887 | 970.5426 | 1147.7019 | 1404.1822 | 1624.22 | 1859.1944 | 2273.7718 | 2452.6806 | 2646.2001 | 2855.5481 | 3082.0451 | 3326.5073
|  |  | Other significant risks |  |  | Significant |  | 64509.642 | 69492.4131 | 74877.9676 | 80699.6591 | 86993.6444 | 93799.1212 | 101158.5865 | 109118.1167 | 117727.6717 | 127041.4251 | 137118.1223 | 147994.085
|  |  | Other major risks |  |  | Major |  | 6992.1126 | 7532.1883 | 8115.9213 | 8746.9265 | 9429.1231 | 10166.7594 | 10964.4419 | 11827.1646 | 12760.3426 | 13769.8477 | 14862.0472 | 16040.878
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 15106.8885 | 16273.7554 | 17534.9463 | 18898.2718 | 20372.1993 | 21965.908 | 23689.3499 | 25553.3153 | 27569.5036 | 29750.6013 | 32110.3655 | 34657.3019
|  |  | Annual opex, pre-replacement |  |  |  |  | 15108.4927 | 15108.4927 | 15108.4927 | 15108.4927 | 15108.4927 | 15108.4927 | 15108.4927 | 15108.4927 | 15108.4927 | 15108.4927 | 15108.4927 | 15108.4927
|  |  | Subtotal |  |  |  |  | 272491.4006 | 303965.5306 | 346026.6559 | 404034.0044 | 459042.3103 | 514706.0648 | 606033.2533 | 652529.3903 | 702822.6913 | 757229.6147 | 816093.3265 | 879626.002
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 46631.1504 | 699467.2566 | 2749372.6301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 130284.2619
|  |  | Post-replacement opex |  |  | 3823.7543
|  |  | Total annuity |  |  | 134108.0163
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 272491.4006 | 303965.5306 | 346026.6559 | 404034.0044 | 459042.3103 | 514706.0648 | 606033.2533 | 652529.3903 | 702822.6913 | 757229.6147 | 816093.3265 | 879626.002
|  |  | Annualised cost |  |  |  |  | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario C
Powercor - Warrnambool Transformer Replacement Risk Monetisation Model
Scenario C | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario C: Consequence calculation
Consequence calculation
|  | Scenario |  |  | C
|  |  | PoF |  | 110%
|  |  | Capex |  | 110%
|  |  | Opex |  | 110%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 56303820.9163 | 0 | 0 | 0 | 0 | 20% | 11260764.1833 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 34254295.7807 | 0 | 0 | 20% | 6850859.1561 | 6850859.1561
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 12816727.1363 | 0 | 20% | 2563345.4273 | 2563345.4273
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2829163.7097 | 20% | 565832.7419 | 565832.7419
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 20% | 11398.7257 | 11398.7257
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 4272242.3788 | 0 | 80% | 3417793.903 | 3417793.903
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 953161.44 | 80% | 762529.152 | 762529.152
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 80% | 45594.9027 | 45594.9027
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 19112664.6349 | 0 | 9338582.37 | 0 | 0 | 4% | 1138049.8802 | 373543.2948
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 18465.9356 | 0 | 100% | 18465.9356 | 18465.9356
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 69874.1883 | 100% | 69874.1883 | 69874.1883
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 56993.6283 | 0 | 0 | 100% | 56993.6283 | 56993.6283
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 19112664.6349 | 0 | 1852893.3274 | 0 | 0 | 4% | 838622.3185 | 74115.7331
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 19112664.6349 | 8261.6388 | 1909886.9557 | 18465.9356 | 69874.1883 | 4.698% | 992217.7095 | 227711.1241
[5 empty] | 2 | Major |  | 19112664.6349 | 28915.7357 | 9395575.9983 | 4272242.3788 | 953161.44 | 15.96% | 5387100.4264 | 4622593.841
[5 empty] | 3 | Catastrophic |  | 56303820.9163 | 28915.7357 | 34311289.409 | 12816727.1363 | 2829163.7097 | 20% | 21257983.3814 | 9997219.1981
[5 empty] | Subtotal |  |  | 2025: 27637301.5172; 2026: 14847524.1632
Scenario C: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 98.9
|  |  | N-1 Rating before transfers, MVA |  |  | 59
|  |  | N-2 Rating before transfers, MVA |  |  | 19.05
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 12.3
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 52.2081 | 53.3705 | 55.5744 | 57.497 | 60.3383 | 61.4796 | 63.9702 | 63.9702 | 63.9702 | 63.9702 | 63.9702 | 63.9702
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 47.0568 | 47.8737 | 49.0004 | 51.3293 | 52.0443 | 53.3054 | 56.279 | 56.279 | 56.279 | 56.279 | 56.279 | 56.279
|  |  | Weighting to 50% PoE |  |  | 70% |  | 48.6022 | 49.5227 | 50.9726 | 53.1796 | 54.5325 | 55.7576 | 58.5863 | 58.5863 | 58.5863 | 58.5863 | 58.5863 | 58.5863
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 17.2522 | 18.1727 | 19.6226 | 21.8296 | 23.1825 | 24.4076 | 27.2363 | 27.2363 | 27.2363 | 27.2363 | 27.2363 | 27.2363
|  |  | N-3 |  |  |  |  | 36.3022 | 37.2227 | 38.6726 | 40.8796 | 42.2325 | 43.4576 | 46.2863 | 46.2863 | 46.2863 | 46.2863 | 46.2863 | 46.2863
|  |  | N-4 |  |  |  |  | 36.3022 | 37.2227 | 38.6726 | 40.8796 | 42.2325 | 43.4576 | 46.2863 | 46.2863 | 46.2863 | 46.2863 | 46.2863 | 46.2863
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 19112664.6349 | 20132470.0474 | 21738660.664 | 24183657.8085 | 25682482.1201 | 32447689.3305 | 36208185.4381 | 36208185.4381 | 36208185.4381 | 36208185.4381 | 36208185.4381 | 36208185.4381
|  |  | N-3 |  |  | Catastrophic |  | 56303820.9163 | 57731548.4938 | 59980215.357 | 63403211.3593 | 65501565.3956 | 67401727.9797 | 71788973.4386 | 71788973.4386 | 71788973.4386 | 71788973.4386 | 71788973.4386 | 71788973.4386
|  |  | N-4 |  |  | Catastrophic |  | 56303820.9163 | 57731548.4938 | 59980215.357 | 63403211.3593 | 65501565.3956 | 67401727.9797 | 71788973.4386 | 71788973.4386 | 71788973.4386 | 71788973.4386 | 71788973.4386 | 71788973.4386
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 41.98% | 45.22% | 48.73% | 52.52% | 56.61% | 61.04% | 65.83% | 71.01% | 76.61% | 82.67% | 89.23% | 96.31%
|  |  | Major |  |  |  |  | 0.2257% | 0.2431% | 0.262% | 0.2823% | 0.3044% | 0.3282% | 0.3539% | 0.3818% | 0.4119% | 0.4445% | 0.4797% | 0.5178%
|  |  | Catastrophic |  |  |  |  | 0.2257% | 0.2431% | 0.262% | 0.2823% | 0.3044% | 0.3282% | 0.3539% | 0.3818% | 0.4119% | 0.4445% | 0.4797% | 0.5178%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 25416.0584 | 28073.483 | 31427.3504 | 35803.7614 | 39873.55 | 44240.0388 | 50816.669 | 54815.1117 | 59140.0922 | 63818.8242 | 68880.8185 | 74344.3211
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 320947.879 | 364185.871 | 423716.5913 | 508021.7754 | 581584.9479 | 792266.3002 | 953450.5019 | 1028471.4996 | 1109619.1791 | 1197404.1424 | 1292380.084 | 1394889.3464
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 1725.5262 | 1957.9886 | 2278.0462 | 2731.2999 | 3126.8008 | 4259.4962 | 5126.078 | 5529.4167 | 5965.6945 | 6437.6567 | 6948.28 | 7499.4051
|  |  | Other significant risks |  |  | Significant |  | 95595.517 | 102979.3834 | 110960.1263 | 119587.1717 | 128914.0995 | 138998.9962 | 149904.8371 | 161699.9018 | 174458.2251 | 188260.0853 | 203192.5365 | 219309.4028
|  |  | Other major risks |  |  | Major |  | 10433.4051 | 11239.2888 | 12110.3163 | 13051.882 | 14069.8337 | 15170.511 | 16360.787 | 17648.114 | 19040.5722 | 20546.9231 | 22176.6681 | 23935.6815
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 22564.1797 | 24307.0531 | 26190.8121 | 28227.1231 | 30428.633 | 32809.0524 | 35383.2458 | 38167.33 | 41178.7797 | 44436.544 | 47961.1706 | 51765.3644
|  |  | Annual opex, pre-replacement |  |  |  |  | 18465.9356 | 18465.9356 | 18465.9356 | 18465.9356 | 18465.9356 | 18465.9356 | 18465.9356 | 18465.9356 | 18465.9356 | 18465.9356 | 18465.9356 | 18465.9356
|  |  | Subtotal |  |  |  |  | 495148.5011 | 551209.0034 | 625149.1782 | 725888.9491 | 816463.8004 | 1046210.3303 | 1229508.0544 | 1324797.3095 | 1427868.4783 | 1539370.1113 | 1660005.4934 | 1790209.4569
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 56993.6283 | 854904.4248 | 3360344.3257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 159236.3201
|  |  | Post-replacement opex |  |  | 4673.4775
|  |  | Total annuity |  |  | 163909.7976
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 495148.5011 | 551209.0034 | 625149.1782 | 725888.9491 | 816463.8004 | 1046210.3303 | 1229508.0544 | 1324797.3095 | 1427868.4783 | 1539370.1113 | 1660005.4934 | 1790209.4569
|  |  | Annualised cost |  |  |  |  | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Scenario D
Powercor - Warrnambool Transformer Replacement Risk Monetisation Model
Scenario D | [7 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Scenario D: Consequence calculation
Consequence calculation
|  | Scenario |  |  | D
|  |  | PoF |  | 110%
|  |  | Capex |  | 90%
|  |  | Opex |  | 90%
|  |  | Demand |  | 105%
|  |  | VCR |  | 110%
|  |  | Environment |  | 110%
[5 empty] | Failure Mode | Risk | Description | Network Performance | Safety | OPEX | CAPEX | Environment | Likelihood of consequence | Consequence incl. network performance | Consequence ex. network performance
[5 empty] | 3 | Catastrophic | Unserved energy | 56303820.9163 | 0 | 0 | 0 | 0 | 20% | 11260764.1833 | 0
[5 empty] | 3 | Catastrophic | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 20% | 5783.1471 | 5783.1471
[5 empty] | 3 | Catastrophic | Temporary generators and associated costs | 0 | 0 | 28026242.0024 | 0 | 0 | 20% | 5605248.4005 | 5605248.4005
[5 empty] | 3 | Catastrophic | Cost of replacement assets | 0 | 0 | 0 | 10486413.1115 | 0 | 20% | 2097282.6223 | 2097282.6223
[5 empty] | 3 | Catastrophic | Environmental consequence | 0 | 0 | 0 | 0 | 2829163.7097 | 20% | 565832.7419 | 565832.7419
[5 empty] | 3 | Catastrophic | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 20% | 9326.2301 | 9326.2301
[5 empty] | 3 | Catastrophic | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 20% | 0 | 0
[5 empty] | 3 | Catastrophic | Coincident outage risk | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 3 | Catastrophic | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | Unserved energy | 0 | 0 | 0 | 0 | 0 | 76% | 0 | 0
[5 empty] | 2 | Major | Safety consequence | 0 | 28915.7357 | 0 | 0 | 0 | 80% | 23132.5885 | 23132.5885
[5 empty] | 2 | Major | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Cost of replacement assets | 0 | 0 | 0 | 3495471.0372 | 0 | 80% | 2796376.8297 | 2796376.8297
[5 empty] | 2 | Major | Environmental consequence | 0 | 0 | 0 | 0 | 953161.44 | 80% | 762529.152 | 762529.152
[5 empty] | 2 | Major | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 80% | 37304.9204 | 37304.9204
[5 empty] | 2 | Major | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 80% | 0 | 0
[5 empty] | 2 | Major | Coincident outage risk | 19112664.6349 | 0 | 7640658.3028 | 0 | 0 | 4% | 1070132.9175 | 305626.3321
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 2 | Major | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | Unserved energy | 0 | 0 | 0 | 0 | 0 | 96% | 0 | 0
[5 empty] | 1 | Significant | Safety consequence | 0 | 8261.6388 | 0 | 0 | 0 | 100% | 8261.6388 | 8261.6388
[5 empty] | 1 | Significant | Temporary generators and associated costs | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Cost of replacement assets | 0 | 0 | 0 | 15108.4927 | 0 | 100% | 15108.4927 | 15108.4927
[5 empty] | 1 | Significant | Environmental consequence | 0 | 0 | 0 | 0 | 69874.1883 | 100% | 69874.1883 | 69874.1883
[5 empty] | 1 | Significant | Fire brigade attendance | 0 | 0 | 46631.1504 | 0 | 0 | 100% | 46631.1504 | 46631.1504
[5 empty] | 1 | Significant | Disruption to adjacent residential and commercial customers | 0 | 0 | 0 | 0 | 0 | 100% | 0 | 0
[5 empty] | 1 | Significant | Coincident outage risk | 19112664.6349 | 0 | 1516003.6315 | 0 | 0 | 4% | 825146.7307 | 60640.1453
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant | [Spare] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0
[5 empty] | 1 | Significant |  | 19112664.6349 | 8261.6388 | 1562634.7819 | 15108.4927 | 69874.1883 | 4.647% | 965022.2009 | 200515.6155
[5 empty] | 2 | Major |  | 19112664.6349 | 28915.7357 | 7687289.4532 | 3495471.0372 | 953161.44 | 14.99% | 4689476.4081 | 3924969.8227
[5 empty] | 3 | Catastrophic |  | 56303820.9163 | 28915.7357 | 28072873.1528 | 10486413.1115 | 2829163.7097 | 20% | 19544237.3252 | 8283473.1419
[5 empty] | Subtotal |  |  | 2025: 25198735.9342; 2026: 12408958.5802
Scenario D: PoE, Load and VCR assumptions
Asset information
|  | Assets at risk |  |  |  | 3
|  | N-rating, MVA |  |  |  | 98.9
|  |  | N-1 Rating before transfers, MVA |  |  | 59
|  |  | N-2 Rating before transfers, MVA |  |  | 19.05
|  |  | N-3 Rating before transfers, MVA |  |  | 0
|  |  | N-4 Rating before transfers, MVA |  |  | 0
|  |  | Transfer capacity, MVA |  |  | 12.3
Probability of exceedance (PoE) forecast, Mega Volt Ampere (MVA)
PoE forecast
|  |  | 10% PoE forecast, MVA |  |  | 10% |  | 52.2081 | 53.3705 | 55.5744 | 57.497 | 60.3383 | 61.4796 | 63.9702 | 63.9702 | 63.9702 | 63.9702 | 63.9702 | 63.9702
|  |  | 50% PoE forecast, MVA |  |  | 50% |  | 47.0568 | 47.8737 | 49.0004 | 51.3293 | 52.0443 | 53.3054 | 56.279 | 56.279 | 56.279 | 56.279 | 56.279 | 56.279
|  |  | Weighting to 50% PoE |  |  | 70% |  | 48.6022 | 49.5227 | 50.9726 | 53.1796 | 54.5325 | 55.7576 | 58.5863 | 58.5863 | 58.5863 | 58.5863 | 58.5863 | 58.5863
Load at risk
Selected profile, MVA
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  |  |  | 17.2522 | 18.1727 | 19.6226 | 21.8296 | 23.1825 | 24.4076 | 27.2363 | 27.2363 | 27.2363 | 27.2363 | 27.2363 | 27.2363
|  |  | N-3 |  |  |  |  | 36.3022 | 37.2227 | 38.6726 | 40.8796 | 42.2325 | 43.4576 | 46.2863 | 46.2863 | 46.2863 | 46.2863 | 46.2863 | 46.2863
|  |  | N-4 |  |  |  |  | 36.3022 | 37.2227 | 38.6726 | 40.8796 | 42.2325 | 43.4576 | 46.2863 | 46.2863 | 46.2863 | 46.2863 | 46.2863 | 46.2863
VCR at risk
Average load at risk (pu)
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N | Average load at risk (pu) | bar: 2019 to 2030
Unserved energy day 1 | bar: 2019 to 2030
|  |  |  | Unserved energy day 2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 | Average load at risk (pu) | bar: 2019 to 2030
|  |  |  | Unserved energy day 1 |  |  |  | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Unserved energy day 2 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | N-2 | Average load at risk (pu) |  |  |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-3 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Unserved energy day 1 |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | Unserved energy day 2 |  |  |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  |  | N-4 | Average load at risk (pu) |  |  |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Selected profile, VCR at risk
|  |  | N |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-1 |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N-2 |  |  | Catastrophic |  | 19112664.6349 | 20132470.0474 | 21738660.664 | 24183657.8085 | 25682482.1201 | 32447689.3305 | 36208185.4381 | 36208185.4381 | 36208185.4381 | 36208185.4381 | 36208185.4381 | 36208185.4381
|  |  | N-3 |  |  | Catastrophic |  | 56303820.9163 | 57731548.4938 | 59980215.357 | 63403211.3593 | 65501565.3956 | 67401727.9797 | 71788973.4386 | 71788973.4386 | 71788973.4386 | 71788973.4386 | 71788973.4386 | 71788973.4386
|  |  | N-4 |  |  | Catastrophic |  | 56303820.9163 | 57731548.4938 | 59980215.357 | 63403211.3593 | 65501565.3956 | 67401727.9797 | 71788973.4386 | 71788973.4386 | 71788973.4386 | 71788973.4386 | 71788973.4386 | 71788973.4386
Risk cost calculation
Risk table forecast
Failure mode
|  |  | Significant |  |  |  |  | 41.98% | 45.22% | 48.73% | 52.52% | 56.61% | 61.04% | 65.83% | 71.01% | 76.61% | 82.67% | 89.23% | 96.31%
|  |  | Major |  |  |  |  | 0.2257% | 0.2431% | 0.262% | 0.2823% | 0.3044% | 0.3282% | 0.3539% | 0.3818% | 0.4119% | 0.4445% | 0.4797% | 0.5178%
|  |  | Catastrophic |  |  |  |  | 0.2257% | 0.2431% | 0.262% | 0.2823% | 0.3044% | 0.3282% | 0.3539% | 0.3818% | 0.4119% | 0.4445% | 0.4797% | 0.5178%
Risk costs
|  |  | Network Performance |  |  | Significant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Major |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Network Performance |  |  | Catastrophic |  | 25416.0584 | 28073.483 | 31427.3504 | 35803.7614 | 39873.55 | 44240.0388 | 50816.669 | 54815.1117 | 59140.0922 | 63818.8242 | 68880.8185 | 74344.3211
|  |  | Network Performance - Coincidental outage |  |  | Significant |  | 320947.879 | 364185.871 | 423716.5913 | 508021.7754 | 581584.9479 | 792266.3002 | 953450.5019 | 1028471.4996 | 1109619.1791 | 1197404.1424 | 1292380.084 | 1394889.3464
|  |  | Network Performance - Coincidental outage |  |  | Major |  | 1725.5262 | 1957.9886 | 2278.0462 | 2731.2999 | 3126.8008 | 4259.4962 | 5126.078 | 5529.4167 | 5965.6945 | 6437.6567 | 6948.28 | 7499.4051
|  |  | Other significant risks |  |  | Significant |  | 84178.5574 | 90680.5696 | 97708.1735 | 105304.892 | 113517.9062 | 122398.365 | 132001.7228 | 142388.1046 | 153622.703 | 165776.209 | 178925.2795 | 193117.3107
|  |  | Other major risks |  |  | Major |  | 8858.8359 | 9543.0987 | 10282.6741 | 11082.1424 | 11946.4687 | 12881.036 | 13891.6802 | 14984.7288 | 16167.0425 | 17446.0608 | 18829.851 | 20323.4008
|  |  | Other catastrophic risls |  |  | Catastrophic |  | 18696.1767 | 20140.2828 | 21701.1235 | 23388.3655 | 25212.4875 | 27184.85 | 29317.7693 | 31624.5994 | 34119.8196 | 36819.1305 | 39739.5577 | 42891.6279
|  |  | Annual opex, pre-replacement |  |  |  |  | 15108.4927 | 15108.4927 | 15108.4927 | 15108.4927 | 15108.4927 | 15108.4927 | 15108.4927 | 15108.4927 | 15108.4927 | 15108.4927 | 15108.4927 | 15108.4927
|  |  | Subtotal |  |  |  |  | 474931.5264 | 529689.7865 | 602222.4518 | 701440.7293 | 790370.6537 | 1018338.579 | 1199712.914 | 1292921.9536 | 1393743.0237 | 1502810.5164 | 1620812.3635 | 1748173.9047
Annualised cost
Annualised cost calculation
PMT calculation
|  |  | Capex ($2021) |  |  |  |  | 0 | 46631.1504 | 699467.2566 | 2749372.6301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse counter |  |  |  |  | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Real WACC, reverse discount factor index |  |  |  |  | 0% | 105.6% | 102.8% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Annualised capex |  |  | 130284.2619
|  |  | Post-replacement opex |  |  | 3823.7543
|  |  | Total annuity |  |  | 134108.0163
Risk cost vs annualised cost
Risks vs benefits
|  | Year | [5 empty] | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost |  |  |  |  | 474931.5264 | 529689.7865 | 602222.4518 | 701440.7293 | 790370.6537 | 1018338.579 | 1199712.914 | 1292921.9536 | 1393743.0237 | 1502810.5164 | 1620812.3635 | 1748173.9047
|  |  | Annualised cost |  |  |  |  | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163
|  |  | Feasible ? |  |  |  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
End

## Summary
Powercor - Warrnambool Transformer Replacement Risk Monetisation Model
Summary |  |  |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Risk cost vs annualised cost
Risks vs benefits
|  | Year |  |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
|  |  | Risk cost | Scenario Base case | 371109.0134 | 413543.6065 | 473337.9089 | 550999.3644 | 620527.8613 | 694964.2146 | 934428.5812 | 1006631.9842 | 1084731.9667 | 1169219.9539 | 1260628.8447 | 1359288.1244
|  |  | Annualised cost | Scenario Base case | 149008.907 | 149008.907 | 149008.907 | 149008.907 | 149008.907 | 149008.907 | 149008.907 | 149008.907 | 149008.907 | 149008.907 | 149008.907 | 149008.907
|  |  | Risk cost | Scenario A | 289643.0058 | 322182.6068 | 365395.3307 | 424647.5375 | 481001.6926 | 538120.6691 | 631021.5397 | 679219.6711 | 731353.9619 | 787752.4547 | 848770.8769 | 914629.1706
|  |  | Annualised cost | Scenario A | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976
|  |  | Risk cost | Scenario B | 272491.4006 | 303965.5306 | 346026.6559 | 404034.0044 | 459042.3103 | 514706.0648 | 606033.2533 | 652529.3903 | 702822.6913 | 757229.6147 | 816093.3265 | 879626.002
|  |  | Annualised cost | Scenario B | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163
|  |  | Risk cost | Scenario C | 495148.5011 | 551209.0034 | 625149.1782 | 725888.9491 | 816463.8004 | 1046210.3303 | 1229508.0544 | 1324797.3095 | 1427868.4783 | 1539370.1113 | 1660005.4934 | 1790209.4569
|  |  | Annualised cost | Scenario C | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976 | 163909.7976
|  |  | Risk cost | Scenario D | 474931.5264 | 529689.7865 | 602222.4518 | 701440.7293 | 790370.6537 | 1018338.579 | 1199712.914 | 1292921.9536 | 1393743.0237 | 1502810.5164 | 1620812.3635 | 1748173.9047
|  |  | Annualised cost | Scenario D | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163 | 134108.0163
Charts
End