## Summary
Radio network replacement - Cost models
Options summary
Description | NPV
Option 1 - Do nothing | -34424067.4228
Option 2 - Replace radio components to operate at new frequency | -7319153.1327 | Recommended option
Option 3 - Move to Another Technology | -46459220.5156
Option 4 - Use cellular communications where possible | -8235636.1957

## Option 1
Option 1 - Do nothing
Expenditure / benefits profile
Year
|  | 2021/2022 | 2022/2023 | 2023/2024 | 2024/2025 | 2025/2026 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031 | 2031/2032 | 2032 / 2033 | 2033 / 2034 | 2034/2035 | 2036/2037 | 2037/2038 | 2038/2039 | 2039/2040 | 2040/2041
Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits | Reliability | 0 | 0 | 1721493.756 | 1721493.756 | 2869156.26 | 2869156.26 | 2869156.26 | 2869156.26 | 2869156.26 | 2869156.26 | 2869156.26 | 2869156.26 | 2869156.26 | 2869156.26 | 2869156.26 | 2869156.26 | 2869156.26 | 2869156.26 | 2869156.26
Inputs
WACC | 2.75%
Affect of spectum allocation on reliability |  | 0% | 0% | 60% | 60% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Capital costs
No capital outlay with this options
Benefits
Reliability costs
Value of unserved energy | -2869156.26
Totals
Impact | Cost | Benefit
Reliability | 0 | -34424067.4228
Capital replacement | 0 | 0
Net benefits |  | -34424067.4228

## Option 2
Option 2 - Replace radio components to operate at new frequency
Expenditure / benefits profile
Year
|  | 2021/2022 | 2022/2023 | 2023/2024 | 2024/2025 | 2025/2026 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031 | 2031/2032 | 2032 / 2033 | 2033 / 2034 | 2034/2035 | 2036/2037 | 2037/2038 | 2038/2039 | 2039/2040 | 2040/2041
Costs |  | 1000000 | 1184119.3333 | 1184119.3333 | 2334475 | 2334475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total |  | 1000000 | 1184119.3333 | 1184119.3333 | 2334475 | 2334475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inputs
WACC | 2.75%
Capital costs
Unit quantities
Item | Number
800 MHz P2P links | 10
800 MHz P2MP & P2P links | 30
Links needing to be "split" due to reduced propagation (800MHz) | 6
1.5GHz P2P links | 23
Links needing to be "split" due to reduced propagation (1.5GHz) | 10
Total affected sites | 63
Unit costs for replacement
Item | Cost per link | Total
Replace 800 MHz P2P with 8GHz | 96710 | 967100
Replace 800 MHz P2MP & P2P with 8GHz | 31145.5556 | 934366.6667
Cost to adding new links (800MHz to 8GHz) | 244462 | 1466772
Rework 1.5GHz P2P Links | 96710 | 2224330
Cost to add new links (1.5GHz to 8GHz) | 244462 | 2444620
Total unit cost |  | 8037188.6667
Total 800MHz to 8GHz costs | 3368238.6667
Total 1.5GHz to 8GHz costs | 4668950
Total program costs | 8037188.6667
Benefits
This option maintains current reliability level
Totals
Expenditure forecast | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | Total
Capital expenditure | 1000000 | 1184119.3333 | 1184119.3333 | 2334475 | 2334475 | 8037188.6667
Impact | Cost | Benefit
Reliability | 0 | 0
Capital replacement | 7319153.1327 | 0
Net benefits |  | -7319153.1327

## Option 3
Option 3 - Move to Another Technology
Expenditure / benefits profile
Year
|  | 2021/2022 | 2022/2023 | 2023/2024 | 2024/2025 | 2025/2026 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031 | 2031/2032 | 2032 / 2033 | 2033 / 2034 | 2034/2035 | 2036/2037 | 2037/2038 | 2038/2039 | 2039/2040 | 2040/2041
Total costs |  | 0 | 0 | 2323352.9334 | 2323352.9334 | 3872254.889 | 3872254.889 | 3872254.889 | 3872254.889 | 3872254.889 | 3872254.889 | 3872254.889 | 3872254.889 | 3872254.889 | 3872254.889 | 3872254.889 | 3872254.889 | 3872254.889 | 3872254.889 | 3872254.889
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Benefits |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Total |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inputs
WACC | 2.75%
Spend profile (according to spectrum changes) |  | 0% | 0% | 60% | 60% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Capital costs
Unit quantities
Item | Number
Total distance covered by radio network | 2581.5033
Unit costs
Item | Cost
Optical fibre leasing (per km per year) | 1500
Construction costs | 20000
Item | Quantity | Unit cost | Total cost
Optical fibre leasing (per km per year) | 2581.5033 | 1500 | 3872254.889
Construction costs | 2581.5033 | 20000 | 51630065.1866
Benefits
This option maintains current reliability level
Total
Item | Cost | Benefit
Operational costs | 46459220.5156 | 0
Reliability impact (10 years) | 0 | 0
Total |  | -46459220.5156

## Option 4
Option 4 - Use cellular communications where possible
Expenditure / benefits profile
Year
|  | 2021/2022 | 2022/2023 | 2023/2024 | 2024/2025 | 2025/2026 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031 | 2031/2032 | 2032 / 2033 | 2033 / 2034 | 2034/2035 | 2036/2037 | 2037/2038 | 2038/2039 | 2039/2040 | 2040/2041
Total costs |  | 1000000 | 742114.0889 | 742114.0889 | 2334475 | 2334475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total benefits | Reliability | 0 | 0 | 136937.0033 | 136937.0033 | 136937.0033 | 136937.0033 | 136937.0033 | 136937.0033 | 136937.0033 | 136937.0033 | 136937.0033 | 136937.0033 | 136937.0033 | 136937.0033 | 136937.0033 | 136937.0033 | 136937.0033 | 136937.0033 | 136937.0033
Inputs
WACC | 2.75%
Affect of spectum allocation on reliability |  | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Capital costs
Links to be replaced by cellular communications
Item | QTY |  | Reference only - Radio replacement cost for sites
800MHz point to point links | 5 |  | 483550
800MHz multipoint links | 16 |  | 498328.8889
Cost to install 3G communications into a substation
Item | Cost
Materials | 1970.4
Field labour (including antenna installation, installation of modem, travel time) | 2464
SCADA specialist time for configuration and test. | 226
Total | 4660.4
Total site installation costs
Item | QTY
Number of sites | 21
Total cost | 97868.4
Radio replacement costs to meet compliance
Item | Cost
Total 800MHz to 8GHz costs | 2386359.7778
Total 1.5GHz to 8GHz costs | 4668950
Total | 7055309.7778
Benefits
Reliability impact
Item | Cost
Number of zone substations | 21
Reliability impact of no communications to zone subs per annum (from option 1) | -2869156.26
Average reliability impact per zone sub (based on the 20 zone subs) | -130416.1936
Communications reliability | 95%
Resulting average reliability reduction per zone sub per annum | -6520.8097
Total Reliability costs
Value of unserved energy | -136937.0033
Total
Item | Cost | Benefit
Capital costs | 6493033.7848 | 0
Reliability impact (10 years) | 0 | -1742602.411
Total |  | -8235636.1957