## Information
Calibration Quantities - Switchgear
Purpose
Adjust RIN reported switchgear replacement volumes, so that the quantities are suitable for use in prediction of future replacement need.
Context
"Reporting 1 - Diffs - RIN" - lists projects that made up RIN replacement data, and modifications to the RIN data to adjust the basis on which data is determined.
"Reporting 2 - Diffs - Equipment" - lists projects that had replacement volumes in the RIN data, however, some equipment quantities are not reflective of future capex replacement need, and these quantities are excluded.
"Reporting 3 - Difference - CBCT" - Where a CB and CTs were replaced with a deadtank CB, this would only have been reported as a CB replacement in the RIN data (CT quantities were not recorded). Those CTs still required replacement, and should be included in future replacement need quantities.
"Reporting 4 - Project Diffs" - some projects replaced switchgear where condition was not a driver. This sheet removes those quantities not replaced due to condition driver.
"Reporting 5 - Totals" - totals all the changes above, starting with the reported RIN data, and finishing (cells K135 - K138) with average replacement quantities appropriate for use in the calibration (2010) repex model.

## Reporting 1 - Diffs - RIN
Adjustments to RIN Data - Data Source of Replacement Volume
Project | Project Name | Year | Voltage | CB | IsolES | VT | CT | Description
CP.00836 | Cairns 132kV Substation Rebuild | 2011 | 132 |  | -6 | 14 | 1 | Procurement vs Equipment Records.
CP.00881 | Ingham/Yabulu Sth 275/132kV Line Replacement | 2012 | 132 | 2 | 6 |  | 6 | Procurement vs Equipment Records.
CP.01018 | Swanbank A 110kV Substation Rebuild | 2011 | 132 |  |  | 3 |  | Procurement vs Equipment Records.
CP.01019 | Moranbah Secondary Systems Replacement | 2014 | 132 |  |  | 1 |  | Procurement vs Equipment Records.
CP.01177 | Belmont 110kV Substation Replacement | 2012 | 132 | -3 | -64 | -40 | -4 | Procurement vs Equipment Records. Split up of RIN data into additional voltage level (11kV).
CP.01177 | Belmont 110kV Substation Replacement | 2012 | 11 |  | 2 |  |  | Split up of RIN data into additional voltage level.
CP.01292 | Broadsound Secondary Systems Replacement | 2013 | 275 |  |  | -4 |  | Procurement vs Equipment Records.
CP.01401 | Woolooga transformer replacement | 2013 | 132 | 1 |  |  |  | Procurement vs Equipment Records.
CP.01401 | Woolooga transformer replacement | 2013 | 275 | 1 | 4 | 1 | 3 | Procurement vs Equipment Records.
CP.01548 | Kareeya Substation Redevelopment | 2013 | 132 |  |  |  | -12 | Split up of RIN data into additional voltage level.
CP.01548 | Kareeya Substation Redevelopment | 2013 | 11 |  |  |  | 12 | Split up of RIN data into additional voltage level.
CP.01658 | Richlands Primary & Secondary Plant Replacement | 2014 | 132 |  | -3 |  | -3 | Procurement vs Equipment Records. Split up of RIN data into additional voltage level.
CP.01658 | Richlands Primary & Secondary Plant Replacement | 2014 | 66 |  | 3 |  |  | Split up of RIN data into additional voltage level.
CP.01780 | Gladstone Switchyard Rebuild | 2013 | 132 |  |  |  | 3 | Procurement vs Equipment Records.
CP.01780 | Gladstone Switchyard Rebuild | 2014 | 132 | 2 | 13 | 4 | 6 | Procurement vs Equipment Records.
CP.01780 | Gladstone Switchyard Rebuild | 2014 | 275 |  |  |  | 1 | Procurement vs Equipment Records.
CP.02058 | Replacement of 66kV Equipment at Tarong | 2013 | 66 | -1 |  |  |  | Procurement vs Equipment Records.
CP.02059 | Woree and Chalumbin Single Pole Auto Reclose | 2013 | 275 |  |  |  | -3 | Procurement vs Equipment Records.
CP.01163 | Swanbank B 275 kV Substation Rebuild | 2015 | 275 |  | 1 | 1 | 3 | 275 kV equipment required for project execution (temporary stage), not included in RIN data.

## Reporting 2 - Diffs - Equipment
Adjustment to RIN Data - Equipment Type Exclusions
Project | Project Name | Year | Voltage | CB | IsolES | VT | CT | Description
CP.00836 | Cairns 132kV Substation Rebuild | 2011 | 132 |  |  |  | -2 | Exclude cap bank balance CTs
CP.01177 | Belmont 110kV Substation Replacement | 2012 | 132 |  |  |  | -2 | Exclude cap bank balance CTs
CP.01292 | Broadsound Secondary Systems Replacement | 2013 | 275 |  |  | -12 |  | 12 VTs are site infrastructure assets

## Reporting 3 - Difference - CBCT
Adjustment to RIN Data - Deadtank CB / CT Adjustment
| Project | Project Name | Voltage | Year | DeadTank CBs Replaced | CTs Replaced
| CP.00881 | Ingham/Yabulu Sth 275/132kV Line Replacement | 132 | 2012 | 4 | 12
| CP.01018 | Swanbank A 110kV Substation Rebuild | 132 | 2011 | 11 | 33
| CP.01019 | Moranbah Secondary Systems Replacement | 132 | 2014 | 8 | 24
| CP.01401 | Woolooga transformer replacement | 132 | 2013 | 3 | 9
| CP.01658 | Richlands Primary & Secondary Plant Replacement | 132 | 2014 | 9 | 27
| CP.01732 | Runcorn 110kV Substation Replacement | 132 | 2013 | 5 | 15
| CP.02058 | Replacement of 66kV Equipment at Tarong | 66 | 2013 | 9 | 27
| CP.02059 | Woree and Chalumbin Single Pole Auto Reclose | 275 | 2013 | 2 | 6
| CP.02207 | Loganlea 110kV substation rebuild | 132 | 2014 | 7 | 21
| CP.01127 | Loganlea 110kV Secondary Systems Replacement | 132 | 2015 | 1 | 3
| CP.02039 | Collinsville 132 kV Substation Replacement | 132 | 2015 | 10 | 30

## Reporting 4 - Project Diffs
Adjustment - Projects With Drivers Not Completely Asset Condition
| Project | Project Name | Voltage | Year | Project Driver | CB | IsolES | VT | CT
| CP.00881 | Ingham/Yabulu Sth 275/132kV Line Replacement | 132 | 2012 | Lines condition, switchgear was incidental. | -4 | -14 | -13 | -18
| CP.01166 | Palmwoods Secondary Systems Replacement | 132 | 2011 | Secondary Systems Replacement. | 0 | 0 | -12 | 0
| CP.01292 | Broadsound Secondary Systems Replacement | 275 | 2013 | Secondary Systems Replacement. | 0 | 0 | -4 | 0
| CP.01397 | Nebo 275/132kV No. 1 Transformer Replacement | 132 | 2014 | Condition of Transformer. Switchgear incidental. | -1 | -2 | -4 | 0
| CP.01397 | Nebo 275/132kV No. 1 Transformer Replacement | 275 | 2014 | Condition of Transformer. Switchgear incidental. | -1 | -2 | 0 | 0
| CP.01401 | Woolooga transformer replacement | 132 | 2013 | Condition of Transformer. Switchgear incidental. | -4 | -5 | -1 | -9
| CP.01401 | Woolooga transformer replacement | 275 | 2013 | Condition of Transformer. Switchgear incidental. | -1 | -7 | -1 | -3
| CP.02058 | Replacement of 66kV Equipment at Tarong | 66 | 2013 | CBs replaced due to condition. Other equipment replaced due to fault level. | 0 | -31 | 0 | -27
| CP.02059 | Woree and Chalumbin Single Pole Auto Reclose | 275 | 2013 | System Functionality. | -2 | -6 | 0 | -12
| CP.02207 | Loganlea 110kV substation rebuild | 132 | 2014 | Fault Level / Condition. | -7 | -20 | -15 | -21

## Reporting 5 - Totals
Calculate Replacement Quantities
| Year |  | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | Total | Average |  | Summation of type for 5 years
| Financial Year |  | 2011 | 2012 | 2013 | 2014 | 2015 |  | Per Year
Reported RIN Quantities
| Equipment | Voltage (kV)
| CB | 66 | 0 | 0 | 10 | 0 | 0 | 10 | 2 |  | CB | 160
| CB | 132 | 18 | 27 | 22 | 35 | 11 | 113 | 22.6 |  | IsolES | 649
| CB | 275 | 0 | 0 | 20 | 5 | 12 | 37 | 7.4 |  | VT | 358
| IsolES | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CT | 257
| IsolES | 66 | 0 | 0 | 31 | 0 | 0 | 31 | 6.2
| IsolES | 132 | 52 | 130 | 117 | 84 | 32 | 415 | 83
| IsolES | 275 | 0 | 0 | 116 | 26 | 61 | 203 | 40.6
| VT | 33 | 0 | 0 | 0 | 0 | 6 | 6 | 1.2
| VT | 132 | 37 | 96 | 46 | 67 | 20 | 266 | 53.2
| VT | 275 | 0 | 0 | 51 | 16 | 19 | 86 | 17.2
| CT | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CT | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CT | 132 | 9 | 78 | 51 | 9 | 0 | 147 | 29.4
| CT | 275 | 0 | 0 | 63 | 11 | 36 | 110 | 22
Summation of Adjustments to RIN Data
| Equipment | Voltage (kV)
CB | CB | 66 | 0 | 0 | -1 | 0 | 0 | -1 |  |  | CB | 2
CB | CB | 132 | 0 | -1 | 1 | 2 | 0 | 2 |  |  | IsolES | -44
CB | CB | 275 | 0 | 0 | 1 | 0 | 0 | 1 |  |  | VT | -20
IsolES | IsolES | 11 | 0 | 2 | 0 | 0 | 0 | 2 |  |  | CT | 13
IsolES | IsolES | 66 | 0 | 0 | 0 | 3 | 0 | 3
IsolES | IsolES | 132 | -6 | -58 | 0 | 10 | 0 | -54
IsolES | IsolES | 275 | 0 | 0 | 4 | 0 | 1 | 5
VT | VT | 33 | 0 | 0 | 0 | 0 | 0 | 0
VT | VT | 132 | 17 | -40 | 0 | 5 | 0 | -18
VT | VT | 275 | 0 | 0 | -3 | 0 | 1 | -2
CT | CT | 11 | 0 | 0 | 12 | 0 | 0 | 12
CT | CT | 66 | 0 | 0 | 0 | 0 | 0 | 0
CT | CT | 132 | 1 | 2 | -9 | 3 | 0 | -3
CT | CT | 275 | 0 | 0 | 0 | 1 | 3 | 4
Summation of Adjustments - Due to Equipment
| Equipment | Voltage (kV)
| CB | 66 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | CB | 0
| CB | 132 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | IsolES | 0
| CB | 275 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | VT | -12
| IsolES | 11 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | CT | -4
| IsolES | 66 | 0 | 0 | 0 | 0 | 0 | 0
| IsolES | 132 | 0 | 0 | 0 | 0 | 0 | 0
| IsolES | 275 | 0 | 0 | 0 | 0 | 0 | 0
| VT | 33 | 0 | 0 | 0 | 0 | 0 | 0
| VT | 132 | 0 | 0 | 0 | 0 | 0 | 0
| VT | 275 | 0 | 0 | -12 | 0 | 0 | -12
| CT | 11 | 0 | 0 | 0 | 0 | 0 | 0
| CT | 66 | 0 | 0 | 0 | 0 | 0 | 0
| CT | 132 | -2 | -2 | 0 | 0 | 0 | -4
| CT | 275 | 0 | 0 | 0 | 0 | 0 | 0
| Summation of Adjustments - Due to Deadtank CB / CTs | [9 empty] | old values
| Equipment | Voltage (kV)
| CB | 66 | 0 | 0 | 0 | 0 | 0 |  |  |  | CB
| CB | 132 | 0 | 0 | 0 | 0 | 0 |  |  |  | IsolES
| CB | 275 | 0 | 0 | 0 | 0 | 0 |  |  |  | VT
| IsolES | 11 | 0 | 0 | 0 | 0 | 0 |  |  |  | CT | 207
| IsolES | 66 | 0 | 0 | 0 | 0 | 0
| IsolES | 132 | 0 | 0 | 0 | 0 | 0
| IsolES | 275 | 0 | 0 | 0 | 0 | 0
| VT | 33 | 0 | 0 | 0 | 0 | 0
| VT | 132 | 0 | 0 | 0 | 0 | 0
| VT | 275 | 0 | 0 | 0 | 0 | 0
| CT | 11 | 0 | 0 | 0 | 0 | 0 | 0
| CT | 66 | 0 | 0 | 27 | 0 | 0 | 27
| CT | 132 | 33 | 12 | 24 | 72 | 33 | 174
| CT | 275 | 0 | 0 | 6 | 0 | 0 | 6
Adjusted Quantities - Including RIN adjustment, Deadtank CBs, not replacement plant
| Equipment | Voltage (kV)
| CB | 66 | 0 | 0 | 9 | 0 | 0 | 9 |  |  | CB | 162
| CB | 132 | 18 | 26 | 23 | 37 | 11 | 115 |  |  | IsolES | 605
| CB | 275 | 0 | 0 | 21 | 5 | 12 | 38 |  |  | VT | 326
| IsolES | 11 | 0 | 2 | 0 | 0 | 0 | 2 |  |  | CT | 473
| IsolES | 66 | 0 | 0 | 31 | 3 | 0 | 34
| IsolES | 132 | 46 | 72 | 117 | 94 | 32 | 361
| IsolES | 275 | 0 | 0 | 120 | 26 | 62 | 208
| VT | 33 | 0 | 0 | 0 | 0 | 6 | 6
| VT | 132 | 54 | 56 | 46 | 72 | 20 | 248
| VT | 275 | 0 | 0 | 36 | 16 | 20 | 72
| CT | 11 | 0 | 0 | 12 | 0 | 0 | 12
| CT | 66 | 0 | 0 | 27 | 0 | 0 | 27
| CT | 132 | 41 | 90 | 66 | 84 | 33 | 314
| CT | 275 | 0 | 0 | 69 | 12 | 39 | 120
Summation of Adjustments - Effect of Project Drivers (Non Condition Based)
Reporting_NonConditionDriverProjects | Equipment | Voltage (kV)
CB | CB | 66 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | CB | -20
CB | CB | 132 | 0 | -4 | -4 | -8 | 0 | -16 |  |  | IsolES | -87
CB | CB | 275 | 0 | 0 | -3 | -1 | 0 | -4 |  |  | VT | -50
IsolES | IsolES | 11 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | CT | -90
IsolES | IsolES | 66 | 0 | 0 | -31 | 0 | 0 | -31
IsolES | IsolES | 132 | 0 | -14 | -5 | -22 | 0 | -41
IsolES | IsolES | 275 | 0 | 0 | -13 | -2 | 0 | -15
VT | VT | 33 | 0 | 0 | 0 | 0 | 0 | 0
VT | VT | 132 | -12 | -13 | -1 | -19 | 0 | -45
VT | VT | 275 | 0 | 0 | -5 | 0 | 0 | -5
CT | CT | 11 | 0 | 0 | 0 | 0 | 0 | 0
CT | CT | 66 | 0 | 0 | -27 | 0 | 0 | -27
CT | CT | 132 | 0 | -18 | -9 | -21 | 0 | -48
CT | CT | 275 | 0 | 0 | -15 | 0 | 0 | -15
Adjusted Quantities
| Equipment | Voltage (kV)
| CB | 66 | 0 | 0 | 9 | 0 | 0 | 9 |  |  | CB | 142
| CB | 132 | 18 | 22 | 19 | 29 | 11 | 99 |  |  | IsolES | 518
| CB | 275 | 0 | 0 | 18 | 4 | 12 | 34 |  |  | VT | 276
| IsolES | 11 | 0 | 2 | 0 | 0 | 0 | 2 |  |  | CT | 383
| IsolES | 66 | 0 | 0 | 0 | 3 | 0 | 3
| IsolES | 132 | 46 | 58 | 112 | 72 | 32 | 320
| IsolES | 275 | 0 | 0 | 107 | 24 | 62 | 193
| VT | 33 | 0 | 0 | 0 | 0 | 6 | 6
| VT | 132 | 42 | 43 | 45 | 53 | 20 | 203
| VT | 275 | 0 | 0 | 31 | 16 | 20 | 67
| CT | 11 | 0 | 0 | 12 | 0 | 0 | 12
| CT | 66 | 0 | 0 | 0 | 0 | 0 | 0
| CT | 132 | 41 | 72 | 57 | 63 | 33 | 266
| CT | 275 | 0 | 0 | 54 | 12 | 39 | 105
Repex Model Calibration Quantities
CB | CB - All Voltages |  | 18 | 22 | 46 | 33 | 23 | 142 | 28.4 | 28.4
IsolES | IsolES - All Voltages |  | 46 | 60 | 219 | 99 | 94 | 518 | 103.6 | 103.6
VT | VT - All Voltages |  | 42 | 43 | 76 | 69 | 46 | 276 | 55.2 | 55.2
CT | CT - All Voltages |  | 41 | 72 | 123 | 75 | 72 | 383 | 76.6 | 76.6