## Annual Summary
2003/04
2003/04
2004/05
Transmission Network Service Provider |  | TNSP A |  |  |  |  | 2005/06
State |  | Qld |  |  |  |  | 2006/07
Summary for financial year |  | 2003/04 |  |  |  |  | 2007/08
2007/08
Service Standard | Applicable | Reliable data | Applicable Status | Reliabilty Status | Target | Performance Result | Collar $M | Cap $M | Incentive / (Penalty) $M
Circuit Availability (total) | TRUE | TRUE | 1 | 1 | 99.2 | 99.3 | -0.5 | 0.5 | 0.076923
Circuit Availability (critical)(peak) | TRUE | TRUE | 1 | 1 | 99.85 | 99.94 | -0.375 | 0.375 | 0.3375
Circuit Availability (non-critical)(peak) | TRUE | TRUE | 1 | 1 | 99.85 | 99.8 | -0.125 | 0.125 | -0.0096154
Circuit Availability (critical)(inter) | TRUE | TRUE | 1 | 1 | 99.85 | 99.83 | -0.125 | 0.125 | -0.0038462
Circuit Availability (non-critical)(inter) | TRUE | TRUE | 1 | 1 | 99.75 | 99.74 | -0.125 | 0.125 | -0.0025
Loss of Supply Event Frequency Index
> 0.2 minutes pa | TRUE | TRUE | 1 | 1 | 5 | 1 | -0.25 | 0.25 | 0.15625
> 1.0 minutes pa | TRUE | TRUE | 1 | 1 | 2 | 5 | -0.25 | 0.25 | -0.25
Average Outage Duration | TRUE | TRUE | 1 | 1 | 200 | 200 | -0.375 | 0.375 | 0
Average Outage Duration (lines) | TRUE | TRUE | 1 | 1 | 150 | 156.45 | -0.1875 | 0.1875 | -0.048375
Average Outage Duration (transformers) | TRUE | TRUE | 1 | 1 | 150 | 144 | -0.1875 | 0.1875 | 0
Transmission Constraints (intra-regional) | TRUE | TRUE | 1 | 0 | 0 | 0 | 0 | 0 | 0
Transmission Constraints (inter-regional) | TRUE | TRUE | 1 | 0 | 0 | 0 | 0 | 0 | 0
Market Measure 1 | FALSE | FALSE | 0 | 0
Market Measure 2 | FALSE | TRUE | 0 | 0
Market Measure 3 | FALSE | FALSE | 0 | 0
TOTAL | [6 empty] | -2.5 | 2.5 | 0.25634

## Data Entry
Service Standards Scheme for financial period beginning |  |  | 2003
Historical Data
Service Standard | 1996/97 | 1997/98 | 1998/99 | 1999/00 | 2000/01
Circuit Availability (total) | 99.41 | 99.46 | 99.19 | 99.54 | 99.49
Circuit Availability (critical)(peak) | 99.95 | 99.94 | 99.9 | 99.94 | 99.95
Circuit Availability (non-critical)(peak) | 99.93 | 99.9 | 99.75 | 99.97 | 99.96
Circuit Availability (critical)(inter) | 99.88 | 99.92 | 99.89 | 99.93 | 99.92
Circuit Availability (non-critical)(inter) | 99.74 | 99.81 | 99.89 | 99.77 | 99.93
Loss of Supply Event Frequency Index
> 0.2 minutes pa | 5 | 5 | 3 | 9 | 5
> 1.0 minutes pa | 3 | 2 | 0 | 2 | 1
Average Outage Duration | 478.2 | 411.4 | 165.4 | 141.8 | 282.6
Average Outage Duration (lines) | 94.8 | 362.1 | 216.9 | 112.8 | 96.15
Average Outage Duration (transformers) | 103.95 | 127.8 | 46.95 | 88.8 | 59.55
Transmission Constraints (intra-regional)
Transmission Constraints (inter-regional)
Market Measure 1
Market Measure 2
Market Measure 3
Performance Data
Service Standard | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | Average
Circuit Availability (total) | 99.3 |  |  |  |  | 99.3
Circuit Availability (critical)(peak) | 99.94 |  |  |  |  | 99.94
Circuit Availability (non-critical)(peak) | 99.8 |  |  |  |  | 99.8
Circuit Availability (critical)(inter) | 99.83 |  |  |  |  | 99.83
Circuit Availability (non-critical)(inter) | 99.74 |  |  |  |  | 99.74
Loss of Supply Event Frequency Index
> 0.2 minutes pa | 1 |  |  |  |  | 1
> 1.0 minutes pa | 5 |  |  |  |  | 5
Average Outage Duration | 200 |  |  |  |  | 200
Average Outage Duration (lines) | 156.45 |  |  |  |  | 156.45
Average Outage Duration (transformers) | 144 |  |  |  |  | 144
Transmission Constraints (intra-regional)
Transmission Constraints (inter-regional)
Market Measure 1
Market Measure 2
Market Measure 3
Performance Targets
Service Standard | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | Historical Average | Overall Average
Circuit Availability (total) | 99.2 | 99.2 | 99.2 | 99.2 | 99.2 | 99.418 | 99.3983
Circuit Availability (critical)(peak) | 99.85 | 99.85 | 99.85 | 99.85 | 99.85 | 99.936 | 99.9367
Circuit Availability (non-critical)(peak) | 99.85 | 99.85 | 99.85 | 99.85 | 99.85 | 99.902 | 99.885
Circuit Availability (critical)(inter) | 99.85 | 99.85 | 99.85 | 99.85 | 99.85 | 99.908 | 99.895
Circuit Availability (non-critical)(inter) | 99.75 | 99.75 | 99.75 | 99.75 | 99.75 | 99.828 | 99.8133
Loss of Supply Event Frequency Index
> 0.2 minutes pa | 5 | 5 | 5 | 5 | 5 | 5.4 | 4.6667
> 1.0 minutes pa | 2 | 2 | 2 | 2 | 2 | 1.6 | 2.1667
Average Outage Duration | 200 | 200 | 200 | 200 | 200 | 295.88 | 279.9
Average Outage Duration (lines) | 150 | 150 | 150 | 150 | 150 | 176.55 | 173.2
Average Outage Duration (transformers) | 150 | 150 | 150 | 150 | 150 | 85.41 | 95.175
Transmission Constraints (intra-regional)
Transmission Constraints (inter-regional)
Market Measure 1
Market Measure 2
Market Measure 3
Maximum Incentive Performance Values (cap)
Service Standard | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
Circuit Availability (total) | 99.85 | 99.85 | 99.85 | 99.85 | 99.85
Circuit Availability (critical)(peak) | 99.95 | 99.95 | 99.95 | 99.95 | 99.95
Circuit Availability (non-critical)(peak) | 99.95 | 99.95 | 99.95 | 99.95 | 99.95
Circuit Availability (critical)(inter) | 99.95 | 99.95 | 99.95 | 99.95 | 99.95
Circuit Availability (non-critical)(inter) | 99.95 | 99.95 | 99.95 | 99.95 | 99.95
Loss of Supply Event Frequency Index
> 0.2 minutes pa | 0 | 0 | 0 | 0 | 0
> 1.0 minutes pa | 0 | 0 | 0 | 0 | 0
Average Outage Duration | 175 | 175 | 175 | 175 | 175
Average Outage Duration (lines) | 125 | 125 | 125 | 125 | 125
Average Outage Duration (transformers) | 125 | 125 | 125 | 125 | 125
Transmission Constraints (intra-regional)
Transmission Constraints (inter-regional)
Market Measure 1
Market Measure 2
Market Measure 3
Maximum Penalty Performance Values (collar)
Service Standard | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
Circuit Availability (total) | 98.2 | 98.2 | 98.2 | 98.2 | 98.2
Circuit Availability (critical)(peak) | 99.4 | 99.4 | 99.4 | 99.4 | 99.4
Circuit Availability (non-critical)(peak) | 99.2 | 99.2 | 99.2 | 99.2 | 99.2
Circuit Availability (critical)(inter) | 99.2 | 99.2 | 99.2 | 99.2 | 99.2
Circuit Availability (non-critical)(inter) | 99.25 | 99.25 | 99.25 | 99.25 | 99.25
Loss of Supply Event Frequency Index
> 0.2 minutes pa | 12 | 12 | 12 | 12 | 12
> 1.0 minutes pa | 5 | 5 | 5 | 5 | 5
Average Outage Duration | 240 | 240 | 240 | 240 | 240
Average Outage Duration (lines) | 175 | 175 | 175 | 175 | 175
Average Outage Duration (transformers) | 205 | 205 | 205 | 205 | 205
Transmission Constraints (intra-regional)
Transmission Constraints (inter-regional)
Market Measure 1
Market Measure 2
Market Measure 3
Note on H47: Overall Average : Average value of historical and performance data

## Base Factors
Service Standards Scheme for period beginning |  |  |  |  | 2003
Transmission Network Service Provider | State |  | Annual Revenue ($M) |  |  |  |  | Total Revenue at Risk (% / $M)
|  |  | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 |  | 2004/05 |  | 2005/06 |  | 2006/07 |  | 2007/08
[9 empty] | - | + | - | + | - | + | - | + | - | bar: Annual Revenue ($M) 2003/04 to Total Revenue at Risk (% / $M) 2003/04
TNSP A | Qld |  | 250 | 250 | 250 | 250 | 250 | 1% | -1% | 1% | -1% | 1% | -1% | 1% | -1% | 1% | -1%
|  |  | Total Revenue at Risk (% / $M) 2003/04: 2.5 | -2.5 | 2.5 | -2.5 | 2.5 | -2.5 | 2.5 | -2.5 | 2.5 | -2.5
Performance measurement factors
Service Standard | Applicable | Reliable data | Annual Revenue ($M) 2003/04: Transition Factors; Total Revenue at Risk (% / $M) 2003/04: Weighting Factors |  |  |  |  | Impact Factors (Transition x Weighting) |  |  |  |  | Dead band Range (recommended maximum limits +/- 10%) | [9 empty] | Ramping Factors | [9 empty] | Interim (bonus) | Interim (penalty)
|  |  | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 |  | 2004/05 |  | 2005/06 |  | 2006/07 |  | 2007/08 |  | 2003/04 |  | 2004/05 |  | 2005/06 |  | 2006/07 |  | 2007/08
[19 empty] | - | + | - | + | - | + | - | + | - | Bonus | Penalty | Bonus | Penalty | Bonus | Penalty | Bonus | Penalty | Bonus | Penalty | bar: Transition Factors 2003/04 to Dead band Range (recommended maximum limits +/- 10%) 2003/04
Circuit Availability (total) | TRUE | TRUE | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.76923 | 0.5 | 0.76923 | 0.5 | 0.76923 | 0.5 | 0.76923 | 0.5 | 0.76923 | 0.5 | FALSE | FALSE
Circuit Availability (critical)(peak) | TRUE | TRUE | 1 | 1 | 1 | 1 | 1 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.75 | 0.83333 | 3.75 | 0.83333 | 3.75 | 0.83333 | 3.75 | 0.83333 | 3.75 | 0.83333 | FALSE | FALSE
Circuit Availability (non-critical)(peak) | TRUE | TRUE | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.25 | 0.19231 | 1.25 | 0.19231 | 1.25 | 0.19231 | 1.25 | 0.19231 | 1.25 | 0.19231 | FALSE | FALSE
Circuit Availability (critical)(inter) | TRUE | TRUE | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.25 | 0.19231 | 1.25 | 0.19231 | 1.25 | 0.19231 | 1.25 | 0.19231 | 1.25 | 0.19231 | FALSE | FALSE
Circuit Availability (non-critical)(inter) | TRUE | TRUE | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0.625 | 0.25 | 0.625 | 0.25 | 0.625 | 0.25 | 0.625 | 0.25 | 0.625 | 0.25 | FALSE | FALSE
Loss of Supply Event Frequency Index |  |  | Impact Factors (Transition x Weighting) 2003/04: 0; Impact Factors (Transition x Weighting) 2004/05: 0; Impact Factors (Transition x Weighting) 2005/06: 0; Impact Factors (Transition x Weighting) 2006/07: 0; Impact Factors (Transition x Weighting) 2007/08: 0
> 0.2 minutes pa | TRUE | TRUE | 1 | 1 | 1 | 1 | 1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 20% | -20% | 20% | -20% | 20% | -20% | 20% | -20% | 20% | -20% | -0.0625 | -0.041667 | -0.0625 | -0.041667 | -0.0625 | -0.041667 | -0.0625 | -0.041667 | -0.0625 | -0.041667 | TRUE | TRUE
> 1.0 minutes pa | TRUE | TRUE | 1 | 1 | 1 | 1 | 1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | -0.125 | -0.083333 | -0.125 | -0.083333 | -0.125 | -0.083333 | -0.125 | -0.083333 | -0.125 | -0.083333 | TRUE | TRUE
Average Outage Duration | TRUE | TRUE | 1 | 1 | 1 | 1 | 1 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 5% | -7% | 5% | -7% | 5% | -7% | 5% | -7% | 5% | -7% | -0.034091 | -0.0125 | -0.034091 | -0.0125 | -0.034091 | -0.0125 | -0.034091 | -0.0125 | -0.034091 | -0.0125 | FALSE | FALSE
Average Outage Duration (lines) | TRUE | TRUE | 1 | 1 | 1 | 1 | 1 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0% | -10% | 0% | -10% | 0% | -10% | 0% | -10% | 0% | -10% | -0.01875 | -0.0075 | -0.01875 | -0.0075 | -0.01875 | -0.0075 | -0.01875 | -0.0075 | -0.01875 | -0.0075 | FALSE | FALSE
Average Outage Duration (transformers) | TRUE | TRUE | 1 | 1 | 1 | 1 | 1 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 10% | -10% | 10% | -10% | 10% | -10% | 10% | -10% | 10% | -10% | -0.01875 | -0.0046875 | -0.01875 | -0.0046875 | -0.01875 | -0.0046875 | -0.01875 | -0.0046875 | -0.01875 | -0.0046875 | FALSE | FALSE
Transmission Constraints (intra-regional) | TRUE | FALSE | 1 | 1 | 1 | 1 | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | FALSE
Transmission Constraints (inter-regional) | TRUE | FALSE | 1 | 1 | 1 | 1 | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | FALSE
Market Measure 1 | FALSE | FALSE | 1 | 1 | 1 | 1 | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | [10 empty] | FALSE | FALSE
Market Measure 2 | FALSE | FALSE | 1 | 1 | 1 | 1 | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | [10 empty] | FALSE | FALSE
Market Measure 3 | FALSE | FALSE | 1 | 1 | 1 | 1 | 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | [10 empty] | FALSE | FALSE
TOTAL | 12 | 10 | [35 empty] | 2 | 2 | bar: Transition Factors 2003/04 to Dead band Range (recommended maximum limits +/- 10%) 2003/04
Service Standard | Applicable | Reliable data | Transition Factors 2003/04: Cap Asym Factor; Transition Factors 2004/05: Collar Asym Factor; Transition Factors 2005/06: Revenue at Risk ($M)
[5 empty] | 2003/04 |  | 2004/05 |  | 2005/06 |  | 2006/07 |  | 2007/08
|  |  | Cap Factor | Collar Factor | Cap | Collar | Cap | Collar | Cap | Collar | Cap | Collar | Cap | Collar
Circuit Availability (total) | 1 | 1 | 1 | 1 | 0.5 | -0.5 | 0.5 | -0.5 | 0.5 | -0.5 | 0.5 | -0.5 | 0.5 | -0.5
Circuit Availability (critical)(peak) | 1 | 1 | 1 | 1 | 0.375 | -0.375 | 0.375 | -0.375 | 0.375 | -0.375 | 0.375 | -0.375 | 0.375 | -0.375
Circuit Availability (non-critical)(peak) | 1 | 1 | 1 | 1 | 0.125 | -0.125 | 0.125 | -0.125 | 0.125 | -0.125 | 0.125 | -0.125 | 0.125 | -0.125
Circuit Availability (critical)(inter) | 1 | 1 | 1 | 1 | 0.125 | -0.125 | 0.125 | -0.125 | 0.125 | -0.125 | 0.125 | -0.125 | 0.125 | -0.125
Circuit Availability (non-critical)(inter) | 1 | 1 | 1 | 1 | 0.125 | -0.125 | 0.125 | -0.125 | 0.125 | -0.125 | 0.125 | -0.125 | 0.125 | -0.125
Loss of Supply Event Frequency Index | bar: Transition Factors 2003/04 to Transition Factors 2004/05
> 0.2 minutes pa | 1 | 1 | 1 | 1 | 0.25 | -0.25 | 0.25 | -0.25 | 0.25 | -0.25 | 0.25 | -0.25 | 0.25 | -0.25
> 1.0 minutes pa | 1 | 1 | 1 | 1 | 0.25 | -0.25 | 0.25 | -0.25 | 0.25 | -0.25 | 0.25 | -0.25 | 0.25 | -0.25
Average Outage Duration | 1 | 1 | 1 | 1 | 0.375 | -0.375 | 0.375 | -0.375 | 0.375 | -0.375 | 0.375 | -0.375 | 0.375 | -0.375
Average Outage Duration (lines) | 1 | 1 | 1 | 1 | 0.1875 | -0.1875 | 0.1875 | -0.1875 | 0.1875 | -0.1875 | 0.1875 | -0.1875 | 0.1875 | -0.1875
Average Outage Duration (transformers) | 1 | 1 | 1 | 1 | 0.1875 | -0.1875 | 0.1875 | -0.1875 | 0.1875 | -0.1875 | 0.1875 | -0.1875 | 0.1875 | -0.1875
Transmission Constraints (intra-regional) | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transmission Constraints (inter-regional) | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Market Measure 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Market Measure 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Market Measure 3 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL | 12 | 10 |  |  | 2.5 | -2.5 | 2.5 | -2.5 | 2.5 | -2.5 | 2.5 | -2.5 | 2.5 | -2.5

## Annual Performance
250
Annual Performance for 2003/04
Service Standard | Parameter | Applicable | Reliable data | Aplicable Status | Reliability Status | Performance Limit below dead band | Interim Value | Target - minimum dead band | Target | Target + maximum dead band | Interim Value | Performance Limit above dead band | Performance calculation (uncapped) | Performance bonus / penalty (capped) | Incremental Unit outside dead band | Incremental Penalty in $k | Incremental Incentive in $k
Circuit Availability (total) | 2003/04 Return in $M | TRUE | TRUE | 1 | 1 | -0.5 | -0.25 | 0 | 0 | 0 | 0.25 | 0.5 | 0.076923 | 0.076923 | 0.01 | 5 | 7.6923
| 2003/04 PI Profile |  |  |  |  | 98.2 | 98.7 | 99.2 | 99.2 | 99.2 | 99.525 | 99.85 | 99.3 | 99.3
Circuit Availability (critical)(peak) | 2003/04 Return in $M | TRUE | TRUE | 1 | 1 | -0.375 | -0.1875 | 0 | 0 | 0 | 0.1875 | 0.375 | 0.3375 | 0.3375 | 0.01 | 8.3333 | 37.5
| 2003/04 PI Profile |  |  |  |  | 99.4 | 99.625 | 99.85 | 99.85 | 99.85 | 99.9 | 99.95 | 99.94 | 99.94
Circuit Availability (non-critical)(peak) | 2003/04 Return in $M | TRUE | TRUE | 1 | 1 | -0.125 | -0.0625 | 0 | 0 | 0 | 0.0625 | 0.125 | -0.0096154 | -0.0096154 | 0.01 | 1.9231 | 12.5
| 2003/04 PI Profile |  |  |  |  | 99.2 | 99.525 | 99.85 | 99.85 | 99.85 | 99.9 | 99.95 | 99.8 | 99.8
Circuit Availability (critical)(inter) | 2003/04 Return in $M | TRUE | TRUE | 1 | 1 | -0.125 | -0.0625 | 0 | 0 | 0 | 0.0625 | 0.125 | -0.0038462 | -0.0038462 | 0.01 | 1.9231 | 12.5
| 2003/04 PI Profile |  |  |  |  | 99.2 | 99.525 | 99.85 | 99.85 | 99.85 | 99.9 | 99.95 | 99.83 | 99.83
Circuit Availability (non-critical)(inter) | 2003/04 Return in $M | TRUE | TRUE | 1 | 1 | -0.125 | -0.0625 | 0 | 0 | 0 | 0.0625 | 0.125 | -0.0025 | -0.0025 | 0.01 | 2.5 | 6.25
| 2003/04 PI Profile |  |  |  |  | 99.25 | 99.5 | 99.75 | 99.75 | 99.75 | 99.85 | 99.95 | 99.74 | 99.74
Loss of Supply Event Frequency Index
> 0.2 minutes pa | 2003/04 Return in $M | TRUE | TRUE | 1 | 1 | 0.25 | 0.0625 | 0 | 0 | 0 | -0.0625 | -0.25 | 0.15625 | 0.15625 | 1 | 41.6667 | 62.5
| 2003/04 PI Profile |  |  |  |  | 0 | 2 | 4 | 5 | 6 | 9 | 12 | 1 | 1
> 1.0 minutes pa | 2003/04 Return in $M | TRUE | TRUE | 1 | 1 | 0.25 | 0.0625 | 0 | 0 | 0 | -0.0625 | -0.25 | -0.25 | -0.25 | 1 | 83.3333 | 125
| 2003/04 PI Profile |  |  |  |  | 0 | 1 | 2 | 2 | 2 | 3.5 | 5 | 5 | 5
Average Outage Duration | 2003/04 Return in $M | TRUE | TRUE | 1 | 1 | 0.375 | 0.1875 | 0 | 0 | 0 | -0.1875 | -0.375 | 0 | 0 | 1 | 12.5 | 34.0909
| 2003/04 PI Profile |  |  |  |  | 175 | 180.5 | 186 | 200 | 210 | 225 | 240 | 200 | 200
Average Outage Duration (lines) | 2003/04 Return in $M | TRUE | TRUE | 1 | 1 | 0.1875 | 0.09375 | 0 | 0 | 0 | -0.09375 | -0.1875 | -0.048375 | -0.048375 | 1 | 7.5 | 18.75
| 2003/04 PI Profile |  |  |  |  | 125 | 130 | 135 | 150 | 150 | 162.5 | 175 | 156.45 | 156.45
Average Outage Duration (transformers) | 2003/04 Return in $M | TRUE | TRUE | 1 | 1 | 0.1875 | 0.09375 | 0 | 0 | 0 | -0.09375 | -0.1875 | 0 | 0 | 1 | 4.6875 | 18.75
| 2003/04 PI Profile |  |  |  |  | 125 | 130 | 135 | 150 | 165 | 185 | 205 | 144 | 144
Transmission Constraints (intra-regional) | 2003/04 Return in $M | TRUE | TRUE | 1 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 1 | #DIV/0! | #DIV/0!
| 2003/04 PI Profile |  |  |  |  | #DIV/0! | #DIV/0! | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0
Transmission Constraints (inter-regional) | 2003/04 Return in $M | TRUE | TRUE | 1 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 1 | #DIV/0! | #DIV/0!
| 2003/04 PI Profile |  |  |  |  | #DIV/0! | #DIV/0! | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0

## Measure 1
Measure 1 |  | Circuit Availability (total)
Definition |  | Actual circuit hours available for defined transmission circuits as a percentage of the total possible available hours
Calculation |  | [(Number of hours pa defined circuits available)/(total possible number of defined circuit hours)]*100
Applicable | Reliable Data | Historical % |  |  |  |  | Performance Result % |  |  |  |  | Target %
|  | 1996/97 | 1997/98 | 1998/99 | 1999/00 | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
FALSE | TRUE | 99.41 | 99.46 | 99.19 | 99.54 | 99.49 | 99.3 | 0 | 0 | 0 | 0 | 99.2 | 99.2 | 99.2 | 99.2 | 99.2
[5 empty] | Adjust Factor | Historical | Calculated Values |  |  |  |  | Manual Settings
[6 empty] | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
Linear Regression (linear trendline) slope of Historical data (q) |  |  |  |  | - | Historical 2000/01: 0.024; Calculated Values 2003/04: 0.024; Calculated Values 2004/05: -0.0031429; Calculated Values 2005/06: #VALUE!; Calculated Values 2006/07: #VALUE!; Calculated Values 2007/08: #VALUE!
Performance value - maximum incentive (cap) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 99.85; Calculated Values 2004/05: 99.85; Calculated Values 2005/06: 99.85; Calculated Values 2006/07: 99.85; Calculated Values 2007/08: 99.85
Performance value - maximum penalty (collar) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 98.2; Calculated Values 2004/05: 98.2; Calculated Values 2005/06: 98.2; Calculated Values 2006/07: 98.2; Calculated Values 2007/08: 98.2
Ramping factor - bonus |  | calc value to cap |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 0.76923; Calculated Values 2004/05: 0.76923; Calculated Values 2005/06: 0.76923; Calculated Values 2006/07: 0.76923; Calculated Values 2007/08: 0.76923
Ramping factor - penalty |  | calc value to collar |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 0.5; Calculated Values 2004/05: 0.5; Calculated Values 2005/06: 0.5; Calculated Values 2006/07: 0.5; Calculated Values 2007/08: 0.5
Interim Values in use |  | bonus |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: 0.76923; Calculated Values 2004/05: 0.76923; Calculated Values 2005/06: 0.76923; Calculated Values 2006/07: 0.76923; Calculated Values 2007/08: 0.76923
|  | penalty |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: 0.5; Calculated Values 2004/05: 0.5; Calculated Values 2005/06: 0.5; Calculated Values 2006/07: 0.5; Calculated Values 2007/08: 0.5
Circuit Availability (total) |  | Collar | Interim Value | Target - minimum dead band | Target | Historical 2000/01: Target + maximum dead band; Calculated Values 2003/04: Interim Value; Calculated Values 2004/05: Cap; Calculated Values 2005/06: Performance calculation (uncapped); Calculated Values 2006/07: Performance incentive / penalty (capped)
2003/04 Return in $M |  | -0.5 | -0.25 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.25; Calculated Values 2004/05: 0.5; Calculated Values 2005/06: 0.076923; Calculated Values 2006/07: 0.076923
2003/04 PI Profile |  | 98.2 | 98.7 | 99.2 | 99.2 | Historical 2000/01: 99.2; Calculated Values 2003/04: 99.525; Calculated Values 2004/05: 99.85; Calculated Values 2005/06: 99.3; Calculated Values 2006/07: 99.3
2004/05 Return in $M |  | -0.5 | -0.25 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.25; Calculated Values 2004/05: 0.5; Calculated Values 2005/06: -49.6; Calculated Values 2006/07: -0.5
2004/05 PI Profile |  | 98.2 | 98.7 | 99.2 | 99.2 | Historical 2000/01: 99.2; Calculated Values 2003/04: 99.525; Calculated Values 2004/05: 99.85; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2005/06 Return in $M |  | -0.5 | -0.25 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.25; Calculated Values 2004/05: 0.5; Calculated Values 2005/06: -49.6; Calculated Values 2006/07: -0.5
2005/06 PI Profile |  | 98.2 | 98.7 | 99.2 | 99.2 | Historical 2000/01: 99.2; Calculated Values 2003/04: 99.525; Calculated Values 2004/05: 99.85; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2006/07 Return in $M |  | -0.5 | -0.25 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.25; Calculated Values 2004/05: 0.5; Calculated Values 2005/06: -49.6; Calculated Values 2006/07: -0.5
2006/07 PI Profile |  | 98.2 | 98.7 | 99.2 | 99.2 | Historical 2000/01: 99.2; Calculated Values 2003/04: 99.525; Calculated Values 2004/05: 99.85; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2007/08 Return in $M |  | -0.5 | -0.25 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.25; Calculated Values 2004/05: 0.5; Calculated Values 2005/06: -49.6; Calculated Values 2006/07: -0.5
2007/08 PI Profile |  | 98.2 | 98.7 | 99.2 | 99.2 | Historical 2000/01: 99.2; Calculated Values 2003/04: 99.525; Calculated Values 2004/05: 99.85; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0

## Measure 1a
Measure 1a |  | Circuit Availability (critical)(peak)
Definition |  | Actual circuit hours available for critical transmission circuits as a percentage of the total possible available hours
Calculation |  | [(Number of hours pa critical circuits available)/(total possible number of defined circuit hours)]*100
Applicable | Reliable Data | Historical % |  |  |  |  | Performance Result % |  |  |  |  | Target %
|  | 1996/97 | 1997/98 | 1998/99 | 1999/00 | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
FALSE | TRUE | 99.95 | 99.94 | 99.9 | 99.94 | 99.95 | 99.94 | 0 | 0 | 0 | 0 | 99.85 | 99.85 | 99.85 | 99.85 | 99.85
[5 empty] | Adjust Factor | Historical | Calculated Values |  |  |  |  | Manual Settings
[6 empty] | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
Linear Regression (linear trendline) slope of Historical data (q) |  |  |  |  | - | Historical 2000/01: 0; Calculated Values 2003/04: 0; Calculated Values 2004/05: 0.00057143; Calculated Values 2005/06: #VALUE!; Calculated Values 2006/07: #VALUE!; Calculated Values 2007/08: #VALUE!
Performance value - maximum incentive (cap) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 99.95; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 99.95; Calculated Values 2006/07: 99.95; Calculated Values 2007/08: 99.95
Performance value - maximum penalty (collar) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 99.4; Calculated Values 2004/05: 99.4; Calculated Values 2005/06: 99.4; Calculated Values 2006/07: 99.4; Calculated Values 2007/08: 99.4
Ramping factor - bonus |  | calc value to cap |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 3.75; Calculated Values 2004/05: 3.75; Calculated Values 2005/06: 3.75; Calculated Values 2006/07: 3.75; Calculated Values 2007/08: 3.75
Ramping factor - penalty |  | calc value to collar |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 0.83333; Calculated Values 2004/05: 0.83333; Calculated Values 2005/06: 0.83333; Calculated Values 2006/07: 0.83333; Calculated Values 2007/08: 0.83333
Interim Values in use |  | bonus |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: 3.75; Calculated Values 2004/05: 3.75; Calculated Values 2005/06: 3.75; Calculated Values 2006/07: 3.75; Calculated Values 2007/08: 3.75
|  | penalty |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: 0.83333; Calculated Values 2004/05: 0.83333; Calculated Values 2005/06: 0.83333; Calculated Values 2006/07: 0.83333; Calculated Values 2007/08: 0.83333
Circuit Availability (critical)(peak) |  | Collar | Interim Value | Target - minimum dead band | Target | Historical 2000/01: Target + maximum dead band; Calculated Values 2003/04: Interim Value; Calculated Values 2004/05: Cap; Calculated Values 2005/06: Performance calculation (uncapped); Calculated Values 2006/07: Performance incentive / penalty (capped)
2003/04 Return in $M |  | -0.375 | -0.1875 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.1875; Calculated Values 2004/05: 0.375; Calculated Values 2005/06: 0.3375; Calculated Values 2006/07: 0.3375
2003/04 PI Profile |  | 99.4 | 99.625 | 99.85 | 99.85 | Historical 2000/01: 99.85; Calculated Values 2003/04: 99.9; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 99.94; Calculated Values 2006/07: 99.94
2004/05 Return in $M |  | -0.375 | -0.1875 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.1875; Calculated Values 2004/05: 0.375; Calculated Values 2005/06: -83.2083; Calculated Values 2006/07: -0.375
2004/05 PI Profile |  | 99.4 | 99.625 | 99.85 | 99.85 | Historical 2000/01: 99.85; Calculated Values 2003/04: 99.9; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2005/06 Return in $M |  | -0.375 | -0.1875 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.1875; Calculated Values 2004/05: 0.375; Calculated Values 2005/06: -83.2083; Calculated Values 2006/07: -0.375
2005/06 PI Profile |  | 99.4 | 99.625 | 99.85 | 99.85 | Historical 2000/01: 99.85; Calculated Values 2003/04: 99.9; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2006/07 Return in $M |  | -0.375 | -0.1875 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.1875; Calculated Values 2004/05: 0.375; Calculated Values 2005/06: -83.2083; Calculated Values 2006/07: -0.375
2006/07 PI Profile |  | 99.4 | 99.625 | 99.85 | 99.85 | Historical 2000/01: 99.85; Calculated Values 2003/04: 99.9; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2007/08 Return in $M |  | -0.375 | -0.1875 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.1875; Calculated Values 2004/05: 0.375; Calculated Values 2005/06: -83.2083; Calculated Values 2006/07: -0.375
2007/08 PI Profile |  | 99.4 | 99.625 | 99.85 | 99.85 | Historical 2000/01: 99.85; Calculated Values 2003/04: 99.9; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0

## Measure 1b
Measure 1b |  | Circuit Availability (non-critical)(peak)
Definition |  | Actual circuit hours available for non-critical transmission circuits as a percentage of the total possible available hours
Calculation |  | [(Number of hours pa non-critical circuits available)/(total possible number of defined circuit hours)]*100
Applicable | Reliable Data | Historical % |  |  |  |  | Performance Result % |  |  |  |  | Target %
|  | 1996/97 | 1997/98 | 1998/99 | 1999/00 | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
FALSE | TRUE | 99.93 | 99.9 | 99.75 | 99.97 | 99.96 | 99.8 | 0 | 0 | 0 | 0 | 99.85 | 99.85 | 99.85 | 99.85 | 99.85
[5 empty] | Adjust Factor | Historical | Calculated Values |  |  |  |  | Manual Settings
[6 empty] | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
Linear Regression (linear trendline) slope of Historical data (q) |  |  |  |  | - | Historical 2000/01: 0.013; Calculated Values 2003/04: 0.013; Calculated Values 2004/05: -0.0071429; Calculated Values 2005/06: #VALUE!; Calculated Values 2006/07: #VALUE!; Calculated Values 2007/08: #VALUE!
Performance value - maximum incentive (cap) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 99.95; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 99.95; Calculated Values 2006/07: 99.95; Calculated Values 2007/08: 99.95
Performance value - maximum penalty (collar) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 99.2; Calculated Values 2004/05: 99.2; Calculated Values 2005/06: 99.2; Calculated Values 2006/07: 99.2; Calculated Values 2007/08: 99.2
Ramping factor - bonus |  | calc value to cap |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 1.25; Calculated Values 2004/05: 1.25; Calculated Values 2005/06: 1.25; Calculated Values 2006/07: 1.25; Calculated Values 2007/08: 1.25
Ramping factor - penalty |  | calc value to collar |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 0.19231; Calculated Values 2004/05: 0.19231; Calculated Values 2005/06: 0.19231; Calculated Values 2006/07: 0.19231; Calculated Values 2007/08: 0.19231
Interim Values in use |  | bonus |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: 1.25; Calculated Values 2004/05: 1.25; Calculated Values 2005/06: 1.25; Calculated Values 2006/07: 1.25; Calculated Values 2007/08: 1.25
|  | penalty |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: 0.19231; Calculated Values 2004/05: 0.19231; Calculated Values 2005/06: 0.19231; Calculated Values 2006/07: 0.19231; Calculated Values 2007/08: 0.19231
Circuit Availability (non-critical)(peak) |  | Collar | Interim Value | Target - minimum dead band | Target | Historical 2000/01: Target + maximum dead band; Calculated Values 2003/04: Interim Value; Calculated Values 2004/05: Cap; Calculated Values 2005/06: Performance calculation (uncapped); Calculated Values 2006/07: Performance incentive / penalty (capped)
2003/04 Return in $M |  | -0.125 | -0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.0625; Calculated Values 2004/05: 0.125; Calculated Values 2005/06: -0.0096154; Calculated Values 2006/07: -0.0096154
2003/04 PI Profile |  | 99.2 | 99.525 | 99.85 | 99.85 | Historical 2000/01: 99.85; Calculated Values 2003/04: 99.9; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 99.8; Calculated Values 2006/07: 99.8
2004/05 Return in $M |  | -0.125 | -0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.0625; Calculated Values 2004/05: 0.125; Calculated Values 2005/06: -19.2019; Calculated Values 2006/07: -0.125
2004/05 PI Profile |  | 99.2 | 99.525 | 99.85 | 99.85 | Historical 2000/01: 99.85; Calculated Values 2003/04: 99.9; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2005/06 Return in $M |  | -0.125 | -0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.0625; Calculated Values 2004/05: 0.125; Calculated Values 2005/06: -19.2019; Calculated Values 2006/07: -0.125
2005/06 PI Profile |  | 99.2 | 99.525 | 99.85 | 99.85 | Historical 2000/01: 99.85; Calculated Values 2003/04: 99.9; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2006/07 Return in $M |  | -0.125 | -0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.0625; Calculated Values 2004/05: 0.125; Calculated Values 2005/06: -19.2019; Calculated Values 2006/07: -0.125
2006/07 PI Profile |  | 99.2 | 99.525 | 99.85 | 99.85 | Historical 2000/01: 99.85; Calculated Values 2003/04: 99.9; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2007/08 Return in $M |  | -0.125 | -0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.0625; Calculated Values 2004/05: 0.125; Calculated Values 2005/06: -19.2019; Calculated Values 2006/07: -0.125
2007/08 PI Profile |  | 99.2 | 99.525 | 99.85 | 99.85 | Historical 2000/01: 99.85; Calculated Values 2003/04: 99.9; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0

## Measure 1c
Measure 1c |  | Circuit Availability (critical)(inter)
Definition |  | Actual circuit hours available for defined transmission circuits as a percentage of the total possible available hours during peak periods
Calculation |  | [(Number of hours pa defined circuits available)/(total possible number of defined circuit hours)]*100
Applicable | Reliable Data | Historical % |  |  |  |  | Performance Result % |  |  |  |  | Target %
|  | 1996/97 | 1997/98 | 1998/99 | 1999/00 | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
FALSE | TRUE | 99.88 | 99.92 | 99.89 | 99.93 | 99.92 | 99.83 | 0 | 0 | 0 | 0 | 99.85 | 99.85 | 99.85 | 99.85 | 99.85
[5 empty] | Adjust Factor | Historical | Calculated Values |  |  |  |  | Manual Settings
[6 empty] | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
Linear Regression (linear trendline) slope of Historical data (q) |  |  |  |  | - | Historical 2000/01: 0.009; Calculated Values 2003/04: 0.009; Calculated Values 2004/05: -0.006; Calculated Values 2005/06: #VALUE!; Calculated Values 2006/07: #VALUE!; Calculated Values 2007/08: #VALUE!
Performance value - maximum incentive (cap) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 99.95; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 99.95; Calculated Values 2006/07: 99.95; Calculated Values 2007/08: 99.95
Performance value - maximum penalty (collar) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 99.2; Calculated Values 2004/05: 99.2; Calculated Values 2005/06: 99.2; Calculated Values 2006/07: 99.2; Calculated Values 2007/08: 99.2
Ramping factor - bonus |  | calc value to cap |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 1.25; Calculated Values 2004/05: 1.25; Calculated Values 2005/06: 1.25; Calculated Values 2006/07: 1.25; Calculated Values 2007/08: 1.25
Ramping factor - penalty |  | calc value to collar |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 0.19231; Calculated Values 2004/05: 0.19231; Calculated Values 2005/06: 0.19231; Calculated Values 2006/07: 0.19231; Calculated Values 2007/08: 0.19231
Interim Values in use |  | bonus |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: 1.25; Calculated Values 2004/05: 1.25; Calculated Values 2005/06: 1.25; Calculated Values 2006/07: 1.25; Calculated Values 2007/08: 1.25
|  | penalty |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: 0.19231; Calculated Values 2004/05: 0.19231; Calculated Values 2005/06: 0.19231; Calculated Values 2006/07: 0.19231; Calculated Values 2007/08: 0.19231
Circuit Availability (critical)(inter) |  | Collar | Interim Value | Target - minimum dead band | Target | Historical 2000/01: Target + maximum dead band; Calculated Values 2003/04: Interim Value; Calculated Values 2004/05: Cap; Calculated Values 2005/06: Performance calculation (uncapped); Calculated Values 2006/07: Performance incentive / penalty (capped)
2003/04 Return in $M |  | -0.125 | -0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.0625; Calculated Values 2004/05: 0.125; Calculated Values 2005/06: -0.0038462; Calculated Values 2006/07: -0.0038462
2003/04 PI Profile |  | 99.2 | 99.525 | 99.85 | 99.85 | Historical 2000/01: 99.85; Calculated Values 2003/04: 99.9; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 99.83; Calculated Values 2006/07: 99.83
2004/05 Return in $M |  | -0.125 | -0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.0625; Calculated Values 2004/05: 0.125; Calculated Values 2005/06: -19.2019; Calculated Values 2006/07: -0.125
2004/05 PI Profile |  | 99.2 | 99.525 | 99.85 | 99.85 | Historical 2000/01: 99.85; Calculated Values 2003/04: 99.9; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2005/06 Return in $M |  | -0.125 | -0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.0625; Calculated Values 2004/05: 0.125; Calculated Values 2005/06: -19.2019; Calculated Values 2006/07: -0.125
2005/06 PI Profile |  | 99.2 | 99.525 | 99.85 | 99.85 | Historical 2000/01: 99.85; Calculated Values 2003/04: 99.9; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2006/07 Return in $M |  | -0.125 | -0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.0625; Calculated Values 2004/05: 0.125; Calculated Values 2005/06: -19.2019; Calculated Values 2006/07: -0.125
2006/07 PI Profile |  | 99.2 | 99.525 | 99.85 | 99.85 | Historical 2000/01: 99.85; Calculated Values 2003/04: 99.9; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2007/08 Return in $M |  | -0.125 | -0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.0625; Calculated Values 2004/05: 0.125; Calculated Values 2005/06: -19.2019; Calculated Values 2006/07: -0.125
2007/08 PI Profile |  | 99.2 | 99.525 | 99.85 | 99.85 | Historical 2000/01: 99.85; Calculated Values 2003/04: 99.9; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0

## Measure 1d
Measure 1d |  | Circuit Availability (non-critical)(inter)
Definition |  | Actual circuit hours available for defined transmission circuits as a percentage of the total possible available hours during non-peak periods
Calculation |  | [(Number of hours pa defined circuits available)/(total possible number of defined circuit hours)]*100
Applicable | Reliable Data | Historical % |  |  |  |  | Performance Result % |  |  |  |  | Target %
|  | 1996/97 | 1997/98 | 1998/99 | 1999/00 | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
FALSE | TRUE | 99.74 | 99.81 | 99.89 | 99.77 | 99.93 | 99.74 | 0 | 0 | 0 | 0 | 99.75 | 99.75 | 99.75 | 99.75 | 99.75
[5 empty] | Adjust Factor | Historical | Calculated Values |  |  |  |  | Manual Settings
[6 empty] | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
Linear Regression (linear trendline) slope of Historical data (q) |  |  |  |  | - | Historical 2000/01: 0.034; Calculated Values 2003/04: 0.034; Calculated Values 2004/05: 0.0068571; Calculated Values 2005/06: #VALUE!; Calculated Values 2006/07: #VALUE!; Calculated Values 2007/08: #VALUE!
Performance value - maximum incentive (cap) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 99.95; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 99.95; Calculated Values 2006/07: 99.95; Calculated Values 2007/08: 99.95
Performance value - maximum penalty (collar) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 99.25; Calculated Values 2004/05: 99.25; Calculated Values 2005/06: 99.25; Calculated Values 2006/07: 99.25; Calculated Values 2007/08: 99.25
Ramping factor - bonus |  | calc value to cap |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 0.625; Calculated Values 2004/05: 0.625; Calculated Values 2005/06: 0.625; Calculated Values 2006/07: 0.625; Calculated Values 2007/08: 0.625
Ramping factor - penalty |  | calc value to collar |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 0.25; Calculated Values 2004/05: 0.25; Calculated Values 2005/06: 0.25; Calculated Values 2006/07: 0.25; Calculated Values 2007/08: 0.25
Interim Values in use |  | bonus |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: 0.625; Calculated Values 2004/05: 0.625; Calculated Values 2005/06: 0.625; Calculated Values 2006/07: 0.625; Calculated Values 2007/08: 0.625
|  | penalty |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: 0.25; Calculated Values 2004/05: 0.25; Calculated Values 2005/06: 0.25; Calculated Values 2006/07: 0.25; Calculated Values 2007/08: 0.25
Circuit Availability (non-critical)(inter) |  | Collar | Interim Value | Target - minimum dead band | Target | Historical 2000/01: Target + maximum dead band; Calculated Values 2003/04: Interim Value; Calculated Values 2004/05: Cap; Calculated Values 2005/06: Performance calculation (uncapped); Calculated Values 2006/07: Performance incentive / penalty (capped)
2003/04 Return in $M |  | -0.125 | -0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.0625; Calculated Values 2004/05: 0.125; Calculated Values 2005/06: -0.0025; Calculated Values 2006/07: -0.0025
2003/04 PI Profile |  | 99.25 | 99.5 | 99.75 | 99.75 | Historical 2000/01: 99.75; Calculated Values 2003/04: 99.85; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 99.74; Calculated Values 2006/07: 99.74
2004/05 Return in $M |  | -0.125 | -0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.0625; Calculated Values 2004/05: 0.125; Calculated Values 2005/06: -24.9375; Calculated Values 2006/07: -0.125
2004/05 PI Profile |  | 99.25 | 99.5 | 99.75 | 99.75 | Historical 2000/01: 99.75; Calculated Values 2003/04: 99.85; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2005/06 Return in $M |  | -0.125 | -0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.0625; Calculated Values 2004/05: 0.125; Calculated Values 2005/06: -24.9375; Calculated Values 2006/07: -0.125
2005/06 PI Profile |  | 99.25 | 99.5 | 99.75 | 99.75 | Historical 2000/01: 99.75; Calculated Values 2003/04: 99.85; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2006/07 Return in $M |  | -0.125 | -0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.0625; Calculated Values 2004/05: 0.125; Calculated Values 2005/06: -24.9375; Calculated Values 2006/07: -0.125
2006/07 PI Profile |  | 99.25 | 99.5 | 99.75 | 99.75 | Historical 2000/01: 99.75; Calculated Values 2003/04: 99.85; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2007/08 Return in $M |  | -0.125 | -0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: 0.0625; Calculated Values 2004/05: 0.125; Calculated Values 2005/06: -24.9375; Calculated Values 2006/07: -0.125
2007/08 PI Profile |  | 99.25 | 99.5 | 99.75 | 99.75 | Historical 2000/01: 99.75; Calculated Values 2003/04: 99.85; Calculated Values 2004/05: 99.95; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0

## Measure 2a
Measure 2a |  | Loss of Supply Event Frequency Index > 0.2 minutes pa
Definition
Calculation
Applicable | Reliable Data | Historical events |  |  |  |  | Performance Result events |  |  |  |  | Target events
|  | 1996/97 | 1997/98 | 1998/99 | 1999/00 | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
TRUE | TRUE | 5 | 5 | 3 | 9 | 5 | 1 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 5 | 5
[5 empty] | Adjust Factor | Historical | Calculated Values |  |  |  |  | Manual Settings
[6 empty] | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
Linear Regression (linear trendline) slope of Historical data (q) |  |  |  |  | - | Historical 2000/01: 0.4; Calculated Values 2003/04: 0.4; Calculated Values 2004/05: -0.4; Calculated Values 2005/06: #VALUE!; Calculated Values 2006/07: #VALUE!; Calculated Values 2007/08: #VALUE!
Performance value - maximum incentive (cap) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 0; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0; Calculated Values 2007/08: 0
Performance value - maximum penalty (collar) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 12; Calculated Values 2004/05: 12; Calculated Values 2005/06: 12; Calculated Values 2006/07: 12; Calculated Values 2007/08: 12
Ramping factor - bonus |  | calc value to cap |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: -0.0625; Calculated Values 2004/05: -0.0625; Calculated Values 2005/06: -0.0625; Calculated Values 2006/07: -0.0625; Calculated Values 2007/08: -0.0625
Ramping factor - penalty |  | calc value to collar |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: -0.041667; Calculated Values 2004/05: -0.041667; Calculated Values 2005/06: -0.041667; Calculated Values 2006/07: -0.041667; Calculated Values 2007/08: -0.041667
Interim Values in use |  | bonus |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: -0.09375; Calculated Values 2004/05: -0.09375; Calculated Values 2005/06: -0.09375; Calculated Values 2006/07: -0.09375; Calculated Values 2007/08: -0.09375
|  | penalty |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: -0.0625; Calculated Values 2004/05: -0.0625; Calculated Values 2005/06: -0.0625; Calculated Values 2006/07: -0.0625; Calculated Values 2007/08: -0.0625
Loss of Supply Event Frequency Index > 0.2 minutes pa |  | Cap | Interim Value | Target - minimum dead band | Target | Historical 2000/01: Target + maximum dead band; Calculated Values 2003/04: Interim Value; Calculated Values 2004/05: Collar; Calculated Values 2005/06: Performance calculation (uncapped); Calculated Values 2006/07: Performance incentive / penalty (capped)
2003/04 Return in $M |  | 0.25 | 0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.0625; Calculated Values 2004/05: -0.25; Calculated Values 2005/06: 0.15625; Calculated Values 2006/07: 0.15625
2003/04 PI Profile |  | 0 | 2 | 4 | 5 | Historical 2000/01: 6; Calculated Values 2003/04: 9; Calculated Values 2004/05: 12; Calculated Values 2005/06: 1; Calculated Values 2006/07: 1
2004/05 Return in $M |  | 0.25 | 0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.0625; Calculated Values 2004/05: -0.25; Calculated Values 2005/06: 0.25; Calculated Values 2006/07: 0.25
2004/05 PI Profile |  | 0 | 2 | 4 | 5 | Historical 2000/01: 6; Calculated Values 2003/04: 9; Calculated Values 2004/05: 12; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2005/06 Return in $M |  | 0.25 | 0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.0625; Calculated Values 2004/05: -0.25; Calculated Values 2005/06: 0.25; Calculated Values 2006/07: 0.25
2005/06 PI Profile |  | 0 | 2 | 4 | 5 | Historical 2000/01: 6; Calculated Values 2003/04: 9; Calculated Values 2004/05: 12; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2006/07 Return in $M |  | 0.25 | 0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.0625; Calculated Values 2004/05: -0.25; Calculated Values 2005/06: 0.25; Calculated Values 2006/07: 0.25
2006/07 PI Profile |  | 0 | 2 | 4 | 5 | Historical 2000/01: 6; Calculated Values 2003/04: 9; Calculated Values 2004/05: 12; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2007/08 Return in $M |  | 0.25 | 0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.0625; Calculated Values 2004/05: -0.25; Calculated Values 2005/06: 0.25; Calculated Values 2006/07: 0.25
2007/08 PI Profile |  | 0 | 2 | 4 | 5 | Historical 2000/01: 6; Calculated Values 2003/04: 9; Calculated Values 2004/05: 12; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0

## Measure 2b
Measure 2b |  | Loss of Supply Event Frequency Index > 1.0 minutes pa
Definition
Calculation
Applicable | Reliable Data | Historical events |  |  |  |  | Performance Result events |  |  |  |  | Target events
|  | 1996/97 | 1997/98 | 1998/99 | 1999/00 | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
TRUE | TRUE | 3 | 2 | 0 | 2 | 1 | 5 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 2
[5 empty] | Adjust Factor | Historical | Calculated Values |  |  |  |  | Manual Settings
[6 empty] | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
Linear Regression (linear trendline) slope of Historical data (q) |  |  |  |  | - | Historical 2000/01: -0.4; Calculated Values 2003/04: -0.4; Calculated Values 2004/05: 0.25714; Calculated Values 2005/06: #VALUE!; Calculated Values 2006/07: #VALUE!; Calculated Values 2007/08: #VALUE!
Performance value - maximum incentive (cap) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 0; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0; Calculated Values 2007/08: 0
Performance value - maximum penalty (collar) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 5; Calculated Values 2004/05: 5; Calculated Values 2005/06: 5; Calculated Values 2006/07: 5; Calculated Values 2007/08: 5
Ramping factor - bonus |  | calc value to cap |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: -0.125; Calculated Values 2004/05: -0.125; Calculated Values 2005/06: -0.125; Calculated Values 2006/07: -0.125; Calculated Values 2007/08: -0.125
Ramping factor - penalty |  | calc value to collar |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: -0.083333; Calculated Values 2004/05: -0.083333; Calculated Values 2005/06: -0.083333; Calculated Values 2006/07: -0.083333; Calculated Values 2007/08: -0.083333
Interim Values in use |  | bonus |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: -0.1875; Calculated Values 2004/05: -0.1875; Calculated Values 2005/06: -0.1875; Calculated Values 2006/07: -0.1875; Calculated Values 2007/08: -0.1875
|  | penalty |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: -0.125; Calculated Values 2004/05: -0.125; Calculated Values 2005/06: -0.125; Calculated Values 2006/07: -0.125; Calculated Values 2007/08: -0.125
Loss of Supply Event Frequency Index > 1.0 minutes pa |  | Cap | Interim Value | Target - minimum dead band | Target | Historical 2000/01: Target + maximum dead band; Calculated Values 2003/04: Interim Value; Calculated Values 2004/05: Collar; Calculated Values 2005/06: Performance calculation (uncapped); Calculated Values 2006/07: Performance incentive / penalty (capped)
2003/04 Return in $M |  | 0.25 | 0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.0625; Calculated Values 2004/05: -0.25; Calculated Values 2005/06: -0.25; Calculated Values 2006/07: -0.25
2003/04 PI Profile |  | 0 | 1 | 2 | 2 | Historical 2000/01: 2; Calculated Values 2003/04: 3.5; Calculated Values 2004/05: 5; Calculated Values 2005/06: 5; Calculated Values 2006/07: 5
2004/05 Return in $M |  | 0.25 | 0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.0625; Calculated Values 2004/05: -0.25; Calculated Values 2005/06: 0.25; Calculated Values 2006/07: 0.25
2004/05 PI Profile |  | 0 | 1 | 2 | 2 | Historical 2000/01: 2; Calculated Values 2003/04: 3.5; Calculated Values 2004/05: 5; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2005/06 Return in $M |  | 0.25 | 0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.0625; Calculated Values 2004/05: -0.25; Calculated Values 2005/06: 0.25; Calculated Values 2006/07: 0.25
2005/06 PI Profile |  | 0 | 1 | 2 | 2 | Historical 2000/01: 2; Calculated Values 2003/04: 3.5; Calculated Values 2004/05: 5; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2006/07 Return in $M |  | 0.25 | 0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.0625; Calculated Values 2004/05: -0.25; Calculated Values 2005/06: 0.25; Calculated Values 2006/07: 0.25
2006/07 PI Profile |  | 0 | 1 | 2 | 2 | Historical 2000/01: 2; Calculated Values 2003/04: 3.5; Calculated Values 2004/05: 5; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2007/08 Return in $M |  | 0.25 | 0.0625 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.0625; Calculated Values 2004/05: -0.25; Calculated Values 2005/06: 0.25; Calculated Values 2006/07: 0.25
2007/08 PI Profile |  | 0 | 1 | 2 | 2 | Historical 2000/01: 2; Calculated Values 2003/04: 3.5; Calculated Values 2004/05: 5; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0

## Measure 3
Measure 3 |  | Average Outage Duration
Definition |  | Average of the outage duration time for the period
Calculation |  | (Cummulative summation of the outage duration time for the period)/(number of outage events during the period)
Applicable | Reliable Data | Historical minutes |  |  |  |  | Performance Result minutes |  |  |  |  | Target minutes
|  | 1996/97 | 1997/98 | 1998/99 | 1999/00 | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
FALSE | TRUE | 478.2 | 411.4 | 165.4 | 141.8 | 282.6 | 200 | 0 | 0 | 0 | 0 | 200 | 200 | 200 | 200 | 200
[5 empty] | Adjust Factor | Historical | Calculated Values |  |  |  |  | Manual Settings
[6 empty] | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
Linear Regression (linear trendline) slope of Historical data (q) |  |  |  |  | - | Historical 2000/01: -66.08; Calculated Values 2003/04: -66.08; Calculated Values 2004/05: -51.4571; Calculated Values 2005/06: #VALUE!; Calculated Values 2006/07: #VALUE!; Calculated Values 2007/08: #VALUE!
Performance value - maximum incentive (cap) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 175; Calculated Values 2004/05: 175; Calculated Values 2005/06: 175; Calculated Values 2006/07: 175; Calculated Values 2007/08: 175
Performance value - maximum penalty (collar) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 240; Calculated Values 2004/05: 240; Calculated Values 2005/06: 240; Calculated Values 2006/07: 240; Calculated Values 2007/08: 240
Ramping factor - bonus |  | calc value to cap |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: -0.034091; Calculated Values 2004/05: -0.034091; Calculated Values 2005/06: -0.034091; Calculated Values 2006/07: -0.034091; Calculated Values 2007/08: -0.034091
Ramping factor - penalty |  | calc value to collar |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: -0.0125; Calculated Values 2004/05: -0.0125; Calculated Values 2005/06: -0.0125; Calculated Values 2006/07: -0.0125; Calculated Values 2007/08: -0.0125
Interim Values in use |  | bonus |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: -0.034091; Calculated Values 2004/05: -0.034091; Calculated Values 2005/06: -0.034091; Calculated Values 2006/07: -0.034091; Calculated Values 2007/08: -0.034091
|  | penalty |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: -0.0125; Calculated Values 2004/05: -0.0125; Calculated Values 2005/06: -0.0125; Calculated Values 2006/07: -0.0125; Calculated Values 2007/08: -0.0125
Average Outage Duration |  | Cap | Interim Value | Target - minimum dead band | Target | Historical 2000/01: Target + maximum dead band; Calculated Values 2003/04: Interim Value; Calculated Values 2004/05: Collar; Calculated Values 2005/06: Performance calculation (uncapped); Calculated Values 2006/07: Performance incentive / penalty (capped)
2003/04 Return in $M |  | 0.375 | 0.1875 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.1875; Calculated Values 2004/05: -0.375; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2003/04 PI Profile |  | 175 | 180.5 | 186 | 200 | Historical 2000/01: 210; Calculated Values 2003/04: 225; Calculated Values 2004/05: 240; Calculated Values 2005/06: 200; Calculated Values 2006/07: 200
2004/05 Return in $M |  | 0.375 | 0.1875 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.1875; Calculated Values 2004/05: -0.375; Calculated Values 2005/06: 6.3409; Calculated Values 2006/07: 0.375
2004/05 PI Profile |  | 175 | 180.5 | 186 | 200 | Historical 2000/01: 210; Calculated Values 2003/04: 225; Calculated Values 2004/05: 240; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2005/06 Return in $M |  | 0.375 | 0.1875 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.1875; Calculated Values 2004/05: -0.375; Calculated Values 2005/06: 6.3409; Calculated Values 2006/07: 0.375
2005/06 PI Profile |  | 175 | 180.5 | 186 | 200 | Historical 2000/01: 210; Calculated Values 2003/04: 225; Calculated Values 2004/05: 240; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2006/07 Return in $M |  | 0.375 | 0.1875 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.1875; Calculated Values 2004/05: -0.375; Calculated Values 2005/06: 6.3409; Calculated Values 2006/07: 0.375
2006/07 PI Profile |  | 175 | 180.5 | 186 | 200 | Historical 2000/01: 210; Calculated Values 2003/04: 225; Calculated Values 2004/05: 240; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2007/08 Return in $M |  | 0.375 | 0.1875 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.1875; Calculated Values 2004/05: -0.375; Calculated Values 2005/06: 6.3409; Calculated Values 2006/07: 0.375
2007/08 PI Profile |  | 175 | 180.5 | 186 | 200 | Historical 2000/01: 210; Calculated Values 2003/04: 225; Calculated Values 2004/05: 240; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0

## Measure 3a
Measure 3a |  | Average Outage Duration (lines)
Definition |  | Average of the outage duration time for the period
Calculation |  | (Cummulative summation of the outage duration time for the period)/(number of outage events during the period)
Applicable | Reliable Data | Historical minutes |  |  |  |  | Performance Result minutes |  |  |  |  | Target minutes
|  | 1996/97 | 1997/98 | 1998/99 | 1999/00 | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
FALSE | TRUE | 94.8 | 362.1 | 216.9 | 112.8 | 96.15 | 156.45 | 0 | 0 | 0 | 0 | 150 | 150 | 150 | 150 | 150
[5 empty] | Adjust Factor | Historical | Calculated Values |  |  |  |  | Manual Settings
[6 empty] | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
Linear Regression (linear trendline) slope of Historical data (q) |  |  |  |  | - | Historical 2000/01: -24.66; Calculated Values 2003/04: -24.66; Calculated Values 2004/05: -16.9629; Calculated Values 2005/06: #VALUE!; Calculated Values 2006/07: #VALUE!; Calculated Values 2007/08: #VALUE!
Performance value - maximum incentive (cap) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 125; Calculated Values 2004/05: 125; Calculated Values 2005/06: 125; Calculated Values 2006/07: 125; Calculated Values 2007/08: 125
Performance value - maximum penalty (collar) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 175; Calculated Values 2004/05: 175; Calculated Values 2005/06: 175; Calculated Values 2006/07: 175; Calculated Values 2007/08: 175
Ramping factor - bonus |  | calc value to cap |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: -0.01875; Calculated Values 2004/05: -0.01875; Calculated Values 2005/06: -0.01875; Calculated Values 2006/07: -0.01875; Calculated Values 2007/08: -0.01875
Ramping factor - penalty |  | calc value to collar |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: -0.0075; Calculated Values 2004/05: -0.0075; Calculated Values 2005/06: -0.0075; Calculated Values 2006/07: -0.0075; Calculated Values 2007/08: -0.0075
Interim Values in use |  | bonus |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: -0.01875; Calculated Values 2004/05: -0.01875; Calculated Values 2005/06: -0.01875; Calculated Values 2006/07: -0.01875; Calculated Values 2007/08: -0.01875
|  | penalty |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: -0.0075; Calculated Values 2004/05: -0.0075; Calculated Values 2005/06: -0.0075; Calculated Values 2006/07: -0.0075; Calculated Values 2007/08: -0.0075
Average Outage Duration (lines) |  | Cap | Interim Value | Target - minimum dead band | Target | Historical 2000/01: Target + maximum dead band; Calculated Values 2003/04: Interim Value; Calculated Values 2004/05: Collar; Calculated Values 2005/06: Performance calculation (uncapped); Calculated Values 2006/07: Performance incentive / penalty (capped)
2003/04 Return in $M |  | 0.1875 | 0.09375 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.09375; Calculated Values 2004/05: -0.1875; Calculated Values 2005/06: -0.048375; Calculated Values 2006/07: -0.048375
2003/04 PI Profile |  | 125 | 130 | 135 | 150 | Historical 2000/01: 150; Calculated Values 2003/04: 162.5; Calculated Values 2004/05: 175; Calculated Values 2005/06: 156.45; Calculated Values 2006/07: 156.45
2004/05 Return in $M |  | 0.1875 | 0.09375 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.09375; Calculated Values 2004/05: -0.1875; Calculated Values 2005/06: 2.5312; Calculated Values 2006/07: 0.1875
2004/05 PI Profile |  | 125 | 130 | 135 | 150 | Historical 2000/01: 150; Calculated Values 2003/04: 162.5; Calculated Values 2004/05: 175; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2005/06 Return in $M |  | 0.1875 | 0.09375 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.09375; Calculated Values 2004/05: -0.1875; Calculated Values 2005/06: 2.5312; Calculated Values 2006/07: 0.1875
2005/06 PI Profile |  | 125 | 130 | 135 | 150 | Historical 2000/01: 150; Calculated Values 2003/04: 162.5; Calculated Values 2004/05: 175; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2006/07 Return in $M |  | 0.1875 | 0.09375 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.09375; Calculated Values 2004/05: -0.1875; Calculated Values 2005/06: 2.5312; Calculated Values 2006/07: 0.1875
2006/07 PI Profile |  | 125 | 130 | 135 | 150 | Historical 2000/01: 150; Calculated Values 2003/04: 162.5; Calculated Values 2004/05: 175; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2007/08 Return in $M |  | 0.1875 | 0.09375 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.09375; Calculated Values 2004/05: -0.1875; Calculated Values 2005/06: 2.5312; Calculated Values 2006/07: 0.1875
2007/08 PI Profile |  | 125 | 130 | 135 | 150 | Historical 2000/01: 150; Calculated Values 2003/04: 162.5; Calculated Values 2004/05: 175; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0

## Measure 3b
Measure 3b |  | Average Outage Duration (transformers)
Definition |  | Average of the outage duration time for the period
Calculation |  | (Cummulative summation of the outage duration time for the period)/(number of outage events during the period)
Applicable | Reliable Data | Historical minutes |  |  |  |  | Performance Result minutes |  |  |  |  | Target minutes
|  | 1996/97 | 1997/98 | 1998/99 | 1999/00 | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
FALSE | TRUE | 103.95 | 127.8 | 46.95 | 88.8 | 59.55 | 144 | 0 | 0 | 0 | 0 | 150 | 150 | 150 | 150 | 150
[5 empty] | Adjust Factor | Historical | Calculated Values |  |  |  |  | Manual Settings
[6 empty] | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
Linear Regression (linear trendline) slope of Historical data (q) |  |  |  |  | - | Historical 2000/01: -12.78; Calculated Values 2003/04: -12.78; Calculated Values 2004/05: 1.0671; Calculated Values 2005/06: #VALUE!; Calculated Values 2006/07: #VALUE!; Calculated Values 2007/08: #VALUE!
Performance value - maximum incentive (cap) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 125; Calculated Values 2004/05: 125; Calculated Values 2005/06: 125; Calculated Values 2006/07: 125; Calculated Values 2007/08: 125
Performance value - maximum penalty (collar) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 205; Calculated Values 2004/05: 205; Calculated Values 2005/06: 205; Calculated Values 2006/07: 205; Calculated Values 2007/08: 205
Ramping factor - bonus |  | calc value to cap |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: -0.01875; Calculated Values 2004/05: -0.01875; Calculated Values 2005/06: -0.01875; Calculated Values 2006/07: -0.01875; Calculated Values 2007/08: -0.01875
Ramping factor - penalty |  | calc value to collar |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: -0.0046875; Calculated Values 2004/05: -0.0046875; Calculated Values 2005/06: -0.0046875; Calculated Values 2006/07: -0.0046875; Calculated Values 2007/08: -0.0046875
Interim Values in use |  | bonus |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: -0.01875; Calculated Values 2004/05: -0.01875; Calculated Values 2005/06: -0.01875; Calculated Values 2006/07: -0.01875; Calculated Values 2007/08: -0.01875
|  | penalty |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: -0.0046875; Calculated Values 2004/05: -0.0046875; Calculated Values 2005/06: -0.0046875; Calculated Values 2006/07: -0.0046875; Calculated Values 2007/08: -0.0046875
Average Outage Duration (transformers) |  | Cap | Interim Value | Target - minimum dead band | Target | Historical 2000/01: Target + maximum dead band; Calculated Values 2003/04: Interim Value; Calculated Values 2004/05: Collar; Calculated Values 2005/06: Performance calculation (uncapped); Calculated Values 2006/07: Performance incentive / penalty (capped)
2003/04 Return in $M |  | 0.1875 | 0.09375 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.09375; Calculated Values 2004/05: -0.1875; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2003/04 PI Profile |  | 125 | 130 | 135 | 150 | Historical 2000/01: 165; Calculated Values 2003/04: 185; Calculated Values 2004/05: 205; Calculated Values 2005/06: 144; Calculated Values 2006/07: 144
2004/05 Return in $M |  | 0.1875 | 0.09375 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.09375; Calculated Values 2004/05: -0.1875; Calculated Values 2005/06: 2.5312; Calculated Values 2006/07: 0.1875
2004/05 PI Profile |  | 125 | 130 | 135 | 150 | Historical 2000/01: 165; Calculated Values 2003/04: 185; Calculated Values 2004/05: 205; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2005/06 Return in $M |  | 0.1875 | 0.09375 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.09375; Calculated Values 2004/05: -0.1875; Calculated Values 2005/06: 2.5312; Calculated Values 2006/07: 0.1875
2005/06 PI Profile |  | 125 | 130 | 135 | 150 | Historical 2000/01: 165; Calculated Values 2003/04: 185; Calculated Values 2004/05: 205; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2006/07 Return in $M |  | 0.1875 | 0.09375 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.09375; Calculated Values 2004/05: -0.1875; Calculated Values 2005/06: 2.5312; Calculated Values 2006/07: 0.1875
2006/07 PI Profile |  | 125 | 130 | 135 | 150 | Historical 2000/01: 165; Calculated Values 2003/04: 185; Calculated Values 2004/05: 205; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2007/08 Return in $M |  | 0.1875 | 0.09375 | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: -0.09375; Calculated Values 2004/05: -0.1875; Calculated Values 2005/06: 2.5312; Calculated Values 2006/07: 0.1875
2007/08 PI Profile |  | 125 | 130 | 135 | 150 | Historical 2000/01: 165; Calculated Values 2003/04: 185; Calculated Values 2004/05: 205; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0

## Measure 4
Measure 4 |  | Transmission Constraints (intra-regional)
Definition |  | Aggregate number of hours pa that binding constraints exist on any part of the interconnected transmission system within a region
Calculation |  | Aggregate number of hours
Applicable | Reliable Data | Historical hours |  |  |  |  | Performance Result hours |  |  |  |  | Target hours
|  | 1996/97 | 1997/98 | 1998/99 | 1999/00 | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
FALSE | TRUE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Adjust Factor | Historical | Calculated Values |  |  |  |  | Manual Settings
[6 empty] | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
Linear Regression (linear trendline) slope of Historical data (q) |  |  |  |  | - | Historical 2000/01: #VALUE!; Calculated Values 2003/04: #VALUE!; Calculated Values 2004/05: #VALUE!; Calculated Values 2005/06: #VALUE!; Calculated Values 2006/07: #VALUE!; Calculated Values 2007/08: #VALUE!
Performance value - maximum incentive (cap) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 0; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0; Calculated Values 2007/08: 0
Performance value - maximum penalty (collar) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 0; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0; Calculated Values 2007/08: 0
Ramping factor - bonus |  | calc value to cap |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 0; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0; Calculated Values 2007/08: 0
Ramping factor - penalty |  | calc value to collar |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 0; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0; Calculated Values 2007/08: 0
Interim Values in use |  | bonus |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: #DIV/0!; Calculated Values 2005/06: #DIV/0!; Calculated Values 2006/07: #DIV/0!; Calculated Values 2007/08: #DIV/0!
|  | penalty |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: #DIV/0!; Calculated Values 2005/06: #DIV/0!; Calculated Values 2006/07: #DIV/0!; Calculated Values 2007/08: #DIV/0!
Transmission Constraints (intra-regional) |  | Cap | Interim Value | Target - minimum dead band | Target | Historical 2000/01: Target + maximum dead band; Calculated Values 2003/04: Interim Value; Calculated Values 2004/05: Collar; Calculated Values 2005/06: Performance calculation (uncapped); Calculated Values 2006/07: Performance incentive / penalty (capped)
2003/04 Return in $M |  | 0 | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2003/04 PI Profile |  | #DIV/0! | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: #DIV/0!; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2004/05 Return in $M |  | 0 | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2004/05 PI Profile |  | #DIV/0! | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: #DIV/0!; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2005/06 Return in $M |  | 0 | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2005/06 PI Profile |  | #DIV/0! | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: #DIV/0!; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2006/07 Return in $M |  | 0 | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2006/07 PI Profile |  | #DIV/0! | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: #DIV/0!; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2007/08 Return in $M |  | 0 | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2007/08 PI Profile |  | #DIV/0! | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: #DIV/0!; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0

## Measure 5
Measure 5 |  | Transmission Constraints (inter-regional)
Definition |  | Aggregate number of hours pa that binding constraints exist on an inter-regional interconnector.
Calculation |  | Aggregate number of hours against "importing" TNSP
Applicable | Reliable Data | Historical hours |  |  |  |  | Performance Result hours |  |  |  |  | Target hours
|  | 1996/97 | 1997/98 | 1998/99 | 1999/00 | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
FALSE | TRUE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Adjust Factor | Historical | Calculated Values |  |  |  |  | Manual Settings
[6 empty] | 2000/01 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08 | 2003/04 | 2004/05 | 2005/06 | 2006/07 | 2007/08
Linear Regression (linear trendline) slope of Historical data (q) |  |  |  |  | - | Historical 2000/01: #VALUE!; Calculated Values 2003/04: #VALUE!; Calculated Values 2004/05: #VALUE!; Calculated Values 2005/06: #VALUE!; Calculated Values 2006/07: #VALUE!; Calculated Values 2007/08: #VALUE!
Performance value - maximum incentive (cap) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 0; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0; Calculated Values 2007/08: 0
Performance value - maximum penalty (collar) |  |  |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 0; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0; Calculated Values 2007/08: 0
Ramping factor - bonus |  | calc value to cap |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 0; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0; Calculated Values 2007/08: 0
Ramping factor - penalty |  | calc value to collar |  |  | - | Historical 2000/01: -; Calculated Values 2003/04: 0; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0; Calculated Values 2007/08: 0
Interim Values in use |  | bonus |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: #DIV/0!; Calculated Values 2005/06: #DIV/0!; Calculated Values 2006/07: #DIV/0!; Calculated Values 2007/08: #DIV/0!
|  | penalty |  |  | 0.5 | Historical 2000/01: -; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: #DIV/0!; Calculated Values 2005/06: #DIV/0!; Calculated Values 2006/07: #DIV/0!; Calculated Values 2007/08: #DIV/0!
Transmission Constraints (inter-regional) |  | Cap | Interim Value | Target - minimum dead band | Target | Historical 2000/01: Target + maximum dead band; Calculated Values 2003/04: Interim Value; Calculated Values 2004/05: Collar; Calculated Values 2005/06: Performance calculation (uncapped); Calculated Values 2006/07: Performance incentive / penalty (capped)
2003/04 Return in $M |  | 0 | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2003/04 PI Profile |  | #DIV/0! | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: #DIV/0!; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2004/05 Return in $M |  | 0 | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2004/05 PI Profile |  | #DIV/0! | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: #DIV/0!; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2005/06 Return in $M |  | 0 | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2005/06 PI Profile |  | #DIV/0! | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: #DIV/0!; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2006/07 Return in $M |  | 0 | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2006/07 PI Profile |  | #DIV/0! | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: #DIV/0!; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2007/08 Return in $M |  | 0 | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: 0; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0
2007/08 PI Profile |  | #DIV/0! | #DIV/0! | 0 | 0 | Historical 2000/01: 0; Calculated Values 2003/04: #DIV/0!; Calculated Values 2004/05: #DIV/0!; Calculated Values 2005/06: 0; Calculated Values 2006/07: 0