## Data
ID | Outage ID | QAPR Reason | Outage Reason | IS IN QAPR | Failed Eq | Fault Clearance Time (msec) | Fault Type Complies with NER CCT | Notes | FeorNumber | Outage Group | AER Code | QTR | Sub | Failure Cause | Component_Type | Actual Start | Actual End | FEOR_Comment | Followup_Comments | FU Manual | Comment on Outage | Weather | SubEqCause | RegionC | VoltsC | Outage TypeC | CHECKED | Qapr Comment | AER Protection System Failure | AER Incorrect Isolation | Year | Explanation
1550 | 20928 | Unknown | Unknown | TRUE | TL |  |  |  | 2009-F-0003 | 962 Waratah West - Tomago 132 132kV Line | Z | 2009Q1 | WRH |  | TL | 2009-01-01 03:11 | 2009-01-01 03:11 | unable to identify 962 tl in the dropdown menu. Could only identify by calling it a cb. is this a bug? | [10 empty] | 0 | 0 | 2009
1548 | 20925 | HV Equipment | Sec Eqt Malfunction | TRUE | CB SF6 |  |  |  | 2009-E-0001 | No.1 Capacitor | Q | 2009Q1 | PMQ |  | CAP | 2009-01-01 04:38 | 2009-01-01 07:13 | SSMF Mr R Meeks carried out repairs due to low sf6 gas. rts @ 0713hrs est |  |  | SSMF Mr R Meeks carried out repairs due to low sf6 gas. | [7 empty] | 0 | 0 | 2009
1549 | 20927 | HV Equipment | Sec Eqt Malfunction | TRUE | SVC |  |  |  | 2009-F-0002 | No.1 Static Var Compensator | Z | 2009Q1 | KCR |  | SVC | 2009-01-01 11:58 | 2009-01-01 12:00 | SVC tripped during its daily automatic routine MVAR test. SVC restarted via Scada @ 1200 hrs |  |  | SVC tripped during its daily automatic routine MVAR test. SVC restarted via SCADA @ 1200 hrs | [7 empty] | 0 | 0 | 2009 | Unknown reason for SVC trip, no further info in QAPR/THEOS/Opslog
1551 | 20929 | Lightning/Storm | Unknown | TRUE | TL |  |  |  | 2009-F-0004 | 8L Dumaresq - Bulli Creek 330kV TL | Z | 2009Q1 | DMQ |  | TL | 2009-01-01 19:19 | 2009-01-01 19:19 | Protection details yet to be collected. Storm present at time of tripping |  |  | Protection details yet to be collected. Storm present at time of tripping | [7 empty] | 0 | 0 | 2009
1552 | 20964 | Unknown | Unknown | TRUE | TL |  |  |  | 2009-F-0009/1 | 2M Tuggerah - Munmorah 330kV TL | Z | 2009Q1 | MN1, TGH |  | TL | 2009-01-05 12:51 | 2009-01-05 12:51 |  |  |  | CB 2M2G at Munmorah did not auto re-close. Closed via SCADA. No bushfire or storm activity apparent at time of trip. Following the tripping, a ground patrol carried out the 5th of January 2009 indicated no evidence of any fault on the line. The precise lo | [7 empty] | 0 | 0 | 2009
1554 | 21109 | Instruction Error | Sec Eqt Staff Error | TRUE | Prev |  |  | No load or generation interrupted. | 2009-F-0016/1 | 330kV Generator Bus | Q | 2009Q1 | BAY |  | BB | 2009-01-08 12:49 | 2009-01-08 13:06 |  |  |  | At 12:49hrs Bayswater 330kV Generator Bus tripped, 73 Bayswater to Mt Piper tripped consequently. The trip occurred when No.2 Tie transformer 330kV CB 5422 was closed to energise No.2 Tie Transformer with temporary protection in place. Staff advised there | [7 empty] | 1 | 1 | 2009 | QAPR spreadsheet indicates this occurred due to error on switching instruction (failure to close BBP links)
1557 | 21157 | Contractor Error | Human Interference | TRUE | Prev |  |  |  | 2009-F-0018 | Spare Bay 4 Transformer CB 5242 | Q | 2009Q1 | BAY |  | CB | 2009-01-09 05:49 | 2009-01-09 09:53 | While contractors (UGI) were removing redundant cabling, new No. 4 Gen I/Z protection I/T rec was initiated. The redundant cable was disconnected from the inservice panel and bay returned to service. Bay closed at 10:53 | As proposed in detailed report on the incident. |  | While contractors (UGI) were removing redundant cabling, new No. 3 Gen I/Z protection I/T rec was initiated. The redundant cable was disconnected from the in-service panel and bay returned to service. Bay closed at 10:53. As proposed in detailed report on | [7 empty] | 1 | 1 | 2009 | Trip occurred while contractors were removing secondary cabling
1558 | 21160 | Unknown | Unknown | TRUE | TX |  |  |  | 2009-E-0004 | No.2 Transformer 132/66/11kV | E | 2009Q1 | MRE |  | TX | 2009-01-09 19:54 | 2009-01-10 00:42 | Buchholz alarm, staff 3+ hrs away. Tx taken o/s as precaution measure returned to load @ 0042hrs on 10/1/09 | NIL |  | Buchholz alarm, staff 3+ hrs away. Tx taken o/s as precaution measure returned to load @ 0042hrs on 10/1/09. The inspection of the Transformer prior to returning it into service has not indicated any gas or leakage of oil from the Buchholz Relay of the Tr | [7 empty] | 0 | 0 | 2009
1560 | 21469 | HV Equipment | Sec Eqt Malfunction | TRUE | CB |  |  |  | 2009-E-0005 | No.1 Generator 330kV CB 5212 | Q | 2009Q1 | ER0 |  | CB | 2009-01-10 03:32 | 2009-02-01 04:29 | CB taken off the system to allow replenishing of sf6 gas. RTS 0429 10/1 |  |  | CB taken off the system to allow replenishing of sf6 gas. RTS 0429 10/1 | [7 empty] | 0 | 0 | 2009
1561 | 21477 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0025 | O1 Upper Tumut - Canberra 330kV TL | Z | 2009Q1 | CA1, UT1 |  | TL | 2009-01-11 11:41 | 2009-01-11 11:41 | See FEOR 2009-F-0026, protection not reset between trips, storms in vicinity for both trips. DTF 12.03 km | No further action is required. |  | See FEOR 2009-F-0026, protection not reset between trips, storms in vicinity for both trips. DTF 12.03 km. A ground patrol in the area of the fault found no evidence of a fault. | Thunderstorm | [6 empty] | 0 | 0 | 2009
1562 | 21478 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0026 | O1 Upper Tumut - Canberra 330kV TL | Z | 2009Q1 | CA1, UT1 |  | TL | 2009-01-11 18:15 | 2009-01-11 18:15 | See FEOR 2009-F-0025, protection not reset between trips, storms in vicinity for both trips. DTF 12.03 km | No further action required. |  | See FEOR 2009-F-0025, protection not reset between trips, storms in vicinity for both trips. DTF 12.03 km | Thunderstorm | [6 empty] | 0 | 0 | 2009
1563 | 21488 | Animal/Bird | Animal/Bird | TRUE | Cap |  |  |  | 2009-F-0029 | No.3 Capacitor | Q | 2009Q1 | GRF |  | CAP | 2009-01-11 18:15 | 2009-01-12 09:54 | Dead bird found across a red phase can , causing can damage. Waiting for can replacement |  |  | Dead bird found across a red phase can , causing can damage. Waiting for can replacement | Fine | [6 empty] | 0 | 0 | 2009
1564 | 21612 | HV Equipment | HV Equipment Failure | TRUE | Cap |  |  |  | 2009-F-0030 | No.1 Capacitor | Z | 2009Q1 | SYN |  | CAP | 2009-01-14 18:22 | 2009-03-15 08:01 | Following requests by NEMMCO regarding availability of capacitors, Maintenance advised that No.1 Capacitor had neutral unbalance alarm issues but could be placed in service if required. Visual inspection carried out on site to confirm no obvious signs of | No further actions required |  | Following requests by NEMMCO regarding availability of capacitors, Maintenance advised that No.1 Capacitor had neutral unbalance alarm issues but could be placed in service if required. Visual inspection carried out on site to confirm no obvious signs of | [7 empty] | 0 | 0 | 2009
1565 | 21627 | Unknown | Unknown | TRUE | TL |  |  |  | 2009-F-0031 | 21 Sydney North - Tuggerah 330kV TL | Z | 2009Q1 | SYN, TGH |  | TL | 2009-01-15 12:43 | 2009-01-15 12:43 | Bushfire & Thunderstorm in area | NIL |  | "An aerial patrol of the line carried out on the 15th of January 2009 has not found any evidence fault on the line contributing the trip. Ground inspections in the vicinity of span 17T -18T have also found no cause for the fault." | Very Hot | [6 empty] | 0 | 0 | 2009
1566 | 21656 | Relay | LV/MECH/PROT Equipment Fail | TRUE | Prot |  |  |  | 2009-E-0007 | No.1 Transformer 132/66/11 kV | E | 2009Q1 | GNS |  | TX | 2009-01-16 23:37 | 2009-01-17 11:10 | Alarm 'No 1 Tx Prot 1 Fault' Tx taken o/s until investigated. Investigation revealed #1 protection "trouble light" illuminated. Tx rts & loaded @ 1110hrs 17/1/09 | NIL |  | Alarm 'No 1 Tx Prot 1 Fault' Tx taken o/s until investigated. Investigation revealed #1 protection "trouble light" illuminated. Tx RTS & loaded @ 1110hrs 17/1/09. Investigations have revealed that the alarm ‘No1 Tx Protection Fault’ was due to faulty No.1 protection relay. | [7 empty] | 1 | 0 | 2009
1567 | 21659 | HV Equipment | HV Equipment Failure | TRUE | Cap |  |  |  | 2009-F-0034 | No.2 Capacitor | Q | 2009Q1 | YA2 |  | CAP | 2009-01-18 19:27 | 2009-01-20 12:17 | Capacitor bank isolated on 18/01/2008. Capacitor repaired and RTS on 20/01/2009. |  |  | Capacitor bank isolated on 18/01/2008. Capacitor repaired (blown external fuses replaced) and RTS on 20/01/2009. | Fine | [6 empty] | 0 | 0 | 2009
1568 | 21708 | HV Equipment | HV Equipment Failure | TRUE | CVT |  |  |  | 2009-F-0037 | 96M Narrabri - Moree 132kV TL | Z | 2009Q1 | MRE, NB2 |  | TL | 2009-01-19 13:05 | 2009-01-19 23:31 | Line taken o/s due to suspect failing cvt at Narrabri end | Further testing will be carried out to try and determine the nature of fault. |  | CVT unbalance alarm was received from Narrabri Substation. As 96M CVT’s are in the 08/09 capital budget for replacement, all three CVT’s were replaced. The faulty CVT is a Tyree type 04/145/12 C2906/2. | [7 empty] | 0 | 0 | 2009
1569 | 21810 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0044 | O1 Upper Tumut - Canberra 330kV TL | Z | 2009Q1 | CA1, UT1 |  | TL | 2009-01-22 16:23 | 2009-01-22 16:23 | Storms in vicinity of UTSS CB012B Closed via SCADA DTF 68km from Canberra | No further action was required. |  | See FEOR 2009-F-0026, protection not reset between trips, storms in vicinity for both trips. DTF 12.03 km. A ground patrol in the area of the fault found no evidence of a fault. | [7 empty] | 0 | 0 | 2009
1570 | 21850 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0051 | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2009Q1 | GTH, MUR, GHI |  | TL | 2009-01-23 14:34 | 2009-01-23 15:58 | Lightning Storms in Area. RTS via SCADA 1558hrs | No further action required. <Duplicate Record> No further action is required. |  | Lightning Storms in Area. RTS via SCADA 1558hrs. Lightning Storms in Area. RTS via SCADA 1558hrs. A ground patrol in the area of the fault found no evidence of a fault. | [7 empty] | 0 | 0 | 2009
1571 | 21874 | HV Equipment | HV Equipment Failure | TRUE | TX |  |  |  | 2009-F-0054 | No.1 Transformer 330/132/11kV | Z | 2009Q1 | TGH |  | TX | 2009-01-23 21:12 | 2009-06-10 14:52 | Transformer Fire, was energised but not on load at the time of trip. | Refer Committee of Enquiry findings. |  | Transformer Fire, was energised on 132kV side but not on load at the time of trip. A Committee of Enquiry is investigating the cause of the failure of the Transformer. Action is being taken to replace the failed Transformer. | [7 empty] | 0 | 0 | 2009
1572 | 21878 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2009-E-0008 | 221 Sydney North - Kenthurst 132kV Line | Q | 2009Q1 | SYN |  | TL | 2009-01-24 20:55 | 2009-01-25 16:22 | After successful TAR on 221 Fdr, C.B.. 2212 went into error status @ SYN, @ SYN 132kV B Bus No.1 Section taken O/S to isolate C.B.. 2212. See FEOR 2009-F-0055 (221 Fdr) & 2009-E-0009 (132kV B1 Bus). |  |  | CB 6042 low SF6 condition. Isolated, topped up & RTS. Leak identification required (2 top ups since) FA4 | Very Windy | [6 empty] | 0 | 0 | 2009
1574 | 21973 | LV/MECH Fail | LV/MECH/PROT Equipment Fail | TRUE | TX |  |  |  | 2009-F-0057 | No.3 Transformer 132/66/11kV | Z | 2009Q1 | TA2 |  | TX | 2009-01-28 19:30 | 2009-01-28 21:25 | The Hot Oil Guage on the side of the Transformer worked its way loose, replaced and protection reset. |  |  | The rubber supporting mounts for the Hot Oil device separated resulting in the Hot Oil device coming away from the transformer and causing a Hot Oil trip. The Rubber Mounts were replaced and the transformer returned to service. | [7 empty] | 0 | 0 | 2009
1575 | 22014 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2009-E-0011 | No.1 Capacitor | E | 2009Q1 | CW2 |  | CAP | 2009-01-30 17:09 | 2009-01-30 20:47 | Low sf6, taken off the system for security reasons. SSMF advises that very close to lockout. | The leak was most likely introduced during maintenance conducted on 16/12/08. The job required the densimeter to be tested which involves that removal of the pipe work. This could lead to damage of th ¦ Plant branch to liase with supplier to get future CB |  | Low sf6, taken off the system for security reasons. SSMF advises that very close to lockout. The alarm was from the No1 Capacitor bank CB 3712 which is a ALSGL309F1-0. It was discovered the leak was from the pipe work connecting the densimeter to the pole | [7 empty] | 0 | 0 | 2009
1576 | 22015 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2009-E-0012 | No.1 Bus Coupler B CB 4012B | Q | 2009Q1 | BFD |  | CB | 2009-01-30 23:44 | 2009-01-31 02:40 | CB HP receiver relief valve leaking causing loss of SF6. CB opened before reaching lockout pressure. CB RTS after relief valve replaced. |  |  | CB HP receiver relief valve leaking causing loss of SF6. CB opened before reaching lockout pressure. CB RTS after relief valve replaced. | [7 empty] | 0 | 0 | 2009
1577 | 22023 | HV Equipment | Unknown | TRUE | CB SF6 |  |  |  | 2009-F-0060 | No.2 Capacitor | Z | 2009Q1 | DNT |  | CAP | 2009-01-31 10:36 | 2009-01-31 13:00 | Substation Miscellaneous Alarm & Command Failure Alarm received on SCADA when attempted to place I/S Placed I/S on Manual Voltage Control 1541hrs | Similar ALSTOM SF6 CB may fail to operate on command. ¦ All easily accessible terminal screws in the CB tightened, with similar ALSTOM CBs to be taken out of service and every factory connection check tightened. |  | Similar ALSTOM SF6 CB may fail to operate on command. ¦ All easily accessible terminal screws in the CB tightened, with similar ALSTOM CBs to be taken out of service and every factory connection check tightened. | [7 empty] | 0 | 0 | 2009
1578 | 22645 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0063 | 97K Cooma - Munyang tee Snowy Adit 132kV TL | Z | 2009Q1 | CMA, MNY |  | TL | 2009-02-02 18:47 | 2009-02-02 18:47 | Electrical Storms in Area, mainly around Munyang Guthega. A/R @ Munyang (RS) may have synchronised with C.E. Snowy Adit from Cooma via 82D, Cooma end manually closed by field staff 20:48 hrs. 82D did TAR between 18:47 - 20:48 hrs, unsure of actual tim | No further action required. |  | Electrical Storms in Area, mainly around Munyang Guthega. A/R @ Munyang (RS) may have synchronised with C.E. Snowy Adit from Cooma via 82D, Cooma end manually closed by field staff 20:48 hrs. 82D did TAR between 18:47 - 20:48 hrs, unsure of actual time, | Thunderstorm | [6 empty] | 0 | 0 | 2009
1767 | 93425 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2009-E-0013/2 | 9U9 Lismore 132 CB 9U92 | Q | 2009Q1 | LSM |  | CB | 2009-02-05 15:24 | 2009-02-05 15:45 |  |  |  | low sf6 blue phase | [7 empty] | 0 | 0 | 2009
1581 | 22890 | Relay Setting | LV/MECH/PROT Equipment Fail | TRUE | Prev |  |  | Action is in hand to model and analyse the worst case of inrush currents to determine whether the available setting on the RCL relay is sufficient or a point of wave circuit breaker will need to be installed on the No.2 Capacitor bank. | 2009-F-0082 | No.4 Capacitor | Z | 2009Q1 | PMQ |  | CAP | 2009-02-06 10:04 | 2009-02-06 11:05 | Tripped on close of No 2 Cap , Auto switched in after Protection reset | Action Taken Continued Protection Design advised increase the setting on the No1 Prot RCL relay to 300 Amps (approx 5 times the load) as an interim solution which is planned for the 10/3/09. ¦ Action is in hand to model and analyse the worst case of inrus |  | Tripped on close of No 2 Cap , Auto switched in after Protection reset. Investigation of the incident has revealed that the No1 protection RLC relay that operated has a filtered 50Hz pick up, and this has been progressively increasing based on switching i | [7 empty] | 1 | 0 | 2009
1582 | 23204 | Unknown | Unknown | TRUE | SVC |  |  |  | 2009-F-0099 | No.1 Static VAR Compensator | Z | 2009Q1 | AR1 |  | SVC | 2009-02-15 04:45 | 2009-02-15 12:16 | An investigation of the SVC equipment found no cause for the trip. RTS at 1316 HRS 15/2/09 (DST) |  |  | An investigation of the SVC equipment found no cause for the trip. | [7 empty] | 0 | 0 | 2009 | Unknown reason for trip, no further info in QAPR report, THEOS or Opslog
1583 | 23259 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0104/1 | 8M Dumaresq - Bulli Creek 330kV TL | Z | 2009Q1 | DMQ |  | TL | 2009-02-17 04:29 | 2009-02-17 04:29 |  |  |  | Blue phase single pole A/R only. | [7 empty] | 0 | 0 | 2009
1584 | 23399 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2009-E-0015 | Bay C Bay Coupler 330kV CB 5032 | Q | 2009Q1 | MTP |  | CB | 2009-02-19 09:27 | 2009-02-19 12:28 | Emergency outage to repair hydraulic oil leak on white phase. |  |  | Emergency outage to repair hydraulic oil leak on white phase. | [7 empty] | 0 | 0 | 2009
1585 | 23478 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2009-F-0120 | No.3 Generator 500kV CB 6232 | Q | 2009Q1 | ER0 |  | CB | 2009-02-23 02:27 | 2009-02-23 03:51 | R ph hydraulic oil contactor burnt out & timing relay not operating thus no CB abnormal alarms prior to trip, LV equipment replaced and CB RTS. |  |  | "R ph hydraulic oil contactor burnt out & timing relay not operating thus no CB abnormal alarms prior to trip, LV equipment replaced and CB RTS." | Fine | [6 empty] | 0 | 0 | 2009
1586 | 23480 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2009-E-0017 | No.2 Capacitor | Q | 2009Q1 | TRE |  | CAP | 2009-02-23 05:25 | 2009-02-23 05:59 | CB 2722 topped up with SF6 and made available @ 0559 hrs EST. |  |  | CB 2722 topped up with SF6 and made available @ 0559 hrs EST. | Fine | [6 empty] | 0 | 0 | 2009
1587 | 23506 | HV Equipment | HV Equipment Failure | TRUE | Other |  |  |  | 2009-E-0018/1 | 95N Newcastle - Waratah West 132kV TL | E | 2009Q1 | NEW, WRH |  | TL | 2009-02-23 10:54 | 2009-02-23 16:41 |  |  |  | Conductors broken line side of Isol 95N8. Repairs effected & RTS @ 1641 hrs EST. Investigation of the incident revealed that the cast aluminium palm installed on isolator 95N8 failed because of fatigue due to excessive tension in the vertical conductor co | [7 empty] | 0 | 0 | 2009
1588 | 23511 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0122/1 | 26 Munmorah - Sydney West 330kV TL | Z | 2009Q1 | MN1, SYW |  | TL | 2009-02-23 16:23 | 2009-02-23 16:25 |  |  |  | 26 didn't reclose at MPS, Main bus was O/S i.e. CB 262 open, CB 5032 closed via SCADA. At 16:23hrs 26 Sydney West to Munmorah 330 kV T/L tripped at both ends and reclosed at the Sydney West end only (Munmorah 330kV Main Bus O/S). Surge on system. Fault re | [7 empty] | 0 | 0 | 2009
1589 | 23613 | Staff Error | Sec Eqt Staff Error | TRUE | Prev |  |  |  | 2009-F-0126 | 33 Bayswater CB 332 | Q | 2009Q1 | LD1 |  | CB | 2009-02-25 12:31 | 2009-02-25 12:59 |  |  |  | At 12:31hrs CB 332 tripped at Liddell 330kV Switchyard resulting in the off loading of the 33 Liddell to Bayswater 330kV T/L (CB 5022 currently O/S for work). There was no surge at the time of the incident. Subsequent investigation found No 1 protection C | [7 empty] | 1 | 1 | 2009 | QAPR report indicates contractor inadvertently cutting a secondary cable
1591 | 23648 | External | Unknown | TRUE | TL |  |  |  | 2009-F-0128 | 96M Narrabri - Moree 132kV TL | Z | 2009Q1 | MRE, NB2 |  | TL | 2009-02-26 11:14 | 2009-02-26 11:14 | 96m previous open @ Moree for an earlier hvpri requirements | Action is in hand to follow up the incident with the aircraft operators to recover the costs from the incident. |  | Staff advised that trip was due to broken bond. 96M T/L was taken O/S to repair and RTS at 17:44hrs. At 19:55hrs Country Energy staff reported that on 96M T/L a part of a plane is hanging down from a conductor. Patrolman was sent to investigate and report | [7 empty] | 0 | 0 | 2009
1592 | 24612 | Lightning/Storm | Unknown | TRUE | Bus |  |  |  | 2009-F-0136 | 66kV Bus Section 1 | Q | 2009Q1 | NAM |  | BB | 2009-03-04 18:45 | 2009-03-04 20:55 |  |  |  | 66kV Bus section tripped at the same time as 751 Fdr including No 1 Tx, during a thunderstorm. Note line B-E bus W phase fault. No obvious fault found. Further investigations will be done in conjunction with Siemens for any CB issues (internal flashover) | [7 empty] | 0 | 0 | 2009
1596 | 24680 | Secondary Equipment | Sec Eqt Malfunction | TRUE | AC/DC |  |  |  | 2009-F-0140 | No.1 Static VAR Compensator | Z | 2009Q1 | AR1 |  | SVC | 2009-03-05 06:44 | 2009-03-05 07:11 | When taking No 1 Tx @ Armidale O/S the SVC tripped. Aux changeover at the SVC board failed. The SVC was RTS @ 0711 | The Substation AC Distribution Board supply CB's will be inspected and lubricated at the next available opportunity. Replacement option for the supply CB's (which are approximately 35 years old) will be investigated. |  | When taking No 1 Tx @ Armidale O/S the SVC tripped. Aux changeover at the SVC board failed. The SVC was RTS @ 0711. There are two 415V supplies to the SVC from the Substation AC distribution board. The SVC has a 415V change over system at the cooling plan | Fine | [6 empty] | 0 | 0 | 2009
1597 | 24716 | LV/MECH Fail | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | not available | 37 Macarthur - Kemps Ck 330kV TL | E | 2009Q1 | KCR, MAC |  | TL | 2009-03-06 03:49 | 2009-03-06 04:24 | [11 empty] | 0 | 0 | 2009
1598 | 24894 | Secondary Equipment | Sec Eqt Malfunction | TRUE | Cap |  |  |  | not available | No.1 Capacitor | Q | 2009Q1 | PMQ |  | CAP | 2009-03-12 01:19 | 2009-03-12 05:49 | [11 empty] | 0 | 0 | 2009
1599 | 24975 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0146 | 996 Wagga 330 - ANM 132kV TL | Z | 2009Q1 | ANM, WG1 |  | TL | 2009-03-14 14:18 | 2009-03-14 14:18 | Storms in area | An aerial patrol will be undertaken in November 2009. |  | An aerial patrol will be undertaken in November 2009. | Thunderstorm | [6 empty] | 0 | 0 | 2009
1602 | 24994 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2009-E-0019 | No.1 Transformer 132/33/11kV | E | 2009Q1 | TRE |  | TX | 2009-03-14 17:07 | 2009-03-15 16:23 |  |  |  | taken out of service due to low sf6 gas cb4412 | [7 empty] | 0 | 0 | 2009
1600 | 24981 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0151/1 | 36 Mt Piper - Marulan 330kV TL | Z | 2009Q1 | MRN, MTP |  | TL | 2009-03-14 23:59 | 2009-03-14 23:59 |  |  |  | 35 Tripped at the same time as 36 Line, but did not reclose at either end. It was manually closed at 0007hrs. There was lightning around both lines and 3 strikes on the line at the time. DTF 210 kM from Marulan. Reclose of 36 line induced a voltage on 35 | [7 empty] | 0 | 0 | 2009
1601 | 24986 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0151/1 | 35 Mt Piper - Marulan 330kV TL | Z | 2009Q1 | MRN, MTP |  | TL | 2009-03-14 23:59 | 2009-03-15 00:07 |  |  |  | 36 Line TAR at the same time a s 35 Line. 35 Tripped at the same time as 36 Line, but did not reclose at either end. It was manually closed at 0007hrs. There was lightning around both lines and 3 strikes on the line at the time. DTF 210 kM from Marulan. R | [7 empty] | 0 | 0 | 2009
1604 | 25062 | Secondary Equipment | Sec Eqt Malfunction | TRUE | SVC |  |  |  | 2009-F-0157 | No.1 Static VAR Compensator | Z | 2009Q1 | BKH |  | SVC | 2009-03-17 14:09 | 2009-03-17 14:27 | SVC tripped when energising No. 2 Transformer @ BKH. SVC placed I/S @ 1427 Hrs | LOCAL AREA |  | SVC tripped when energising No. 2 Transformer @ BKH. SVC placed I/S @ 1427 Hrs. SVC inspected. No.3 harmonic protection operated. | Fine | [6 empty] | 0 | 0 | 2009 | Unknown reason for SVC trip
1605 | 25181 | Switching error | Sec Eqt Staff Error | TRUE | Prev |  |  |  | 2009-F-0158/1 | 330kV Bus Section 3 | Q | 2009Q1 | AR1 |  | BB | 2009-03-18 06:59 | 2009-03-18 07:34 |  |  |  | At 0659hrs at Armidale the 330kV A Bus No3 Sect tripped due to inadvertent opening of incorrect BBP CT links during planned switching on CB5142. RTS at 0734hrs. Initial investigations revealed that a staff inadvertently opened No.1 Reactor BBP CT Links in | [7 empty] | 1 | 1 | 2009
1609 | 25735 | HV Equipment | Unknown | TRUE | TL |  |  |  | 2009-F-0176 | 875 Tamworth 132 - Gunnedah 66kV Line | Q | 2009Q1 | GN2, TA2 |  | TL | 2009-03-30 04:39 | 2009-03-31 12:13 | Returned to service at 13:13Hrs 31/03/09 | NIL |  | Ground patrol of the line on the 30th of May 2009, flashed insulators were found on blue phase at structure 9 (which lines up with the fault recorder location) and a loose bonding lead at structure 334 of the line. The flashed insulators were replaced and | [7 empty] | 0 | 0 | 2009
1610 | 26469 | Unknown | Unknown | TRUE | TL |  |  |  | not available | 5A3 Bayswater - Mt Piper 500kV TL | Z | 2009Q2 | BAY, MTP |  | TL | 2009-04-02 06:43 | 2009-04-02 06:43 |  |  |  | At 06:43hrs Delta Energy's Mt Piper PS Unit 2 tripped. At the same time 5A3 Bayswater to Mt Piper 330 kV T/L tripped and auto reclosed. No storms in the area, the cause in being investigated. Delta CEO has advised MPS unit 2 is holding steam and is requi | [7 empty] | 0 | 0 | 2009
1611 | 26604 | HV Equipment | Sec Eqt Malfunction | TRUE | CB SF6 |  |  |  | not available | No.2 330kV Generator CB 5222 | Q | 2009Q2 | MTP |  | CB | 2009-04-02 06:43 | 2009-04-02 10:41 |  |  |  | At 06:43hrs Delta Energy's Mt Piper PS Unit 2 tripped. At the same time 5A3 Bayswater to Mt Piper 330 kV T/L tripped and auto reclosed. No storms in the area, the cause in being investigated. Delta CEO has advised MPS unit 2 is holding steam and is requi | [7 empty] | 0 | 0 | 2009
1612 | 26672 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0193/1 | O60 Jindera - Wodonga 330kV TL | Z | 2009Q2 | JDA |  | TL | 2009-04-03 15:51 | 2009-04-03 18:12 |  |  |  | Storms stretching from Victoria to middle of NSW. When O60 T/L tripped @ Jindera, on TG SCADA O60 T/L still indicating closed @ Wodonga, V3 T/L also tripped at same time, interrupting supply to Wodonga. @ Wodonga B CB V32B O/S for maintenance, V3 T/L RTS | [7 empty] | 0 | 0 | 2009
1613 | 26675 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0194 | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2009Q2 | GTH, MUR, GHI |  | TL | 2009-04-03 17:40 | 2009-04-03 18:48 | Severe storms in vicinity at time of trip, supply interrupted to Guthega Bus, Units 1/2 & Jindabyne Pumps O/S at time of trip. 18:48 hrs @ Guthega 97G Geehi Tee C.B.. 97G2 - OPENED BY SCADA @ Murray 97G Geehi Tee C.B.. 97G2 - CLOSED BY SCADA @ Guthega 97G | No future action required. |  | Severe storms in vicinity at time of trip, supply interrupted to Guthega Bus, Units 1/2 & Jindabyne Pumps O/S at time of trip. 18:48 hrs @ Guthega 97G Geehi Tee C.B.. 97G2 - OPENED BY SCADA @ Murray 97G Geehi Tee C.B.. 97G2 - CLOSED BY SCADA @ Guthega 97 | Thunderstorm | [6 empty] | 0 | 0 | 2009
2245 | 26518 | Wiring Error |  | TRUE | Proc |  |  |  | not available | 5A3 Bayswater - Mt Piper 500kV TL |  | 2009Q2 | MTP |  |  | 2009-04-03 20:03 | 2009-04-03 20:03 |  |  |  | Investigations on the Interzone Protection Panels found the protection operated at the time of the 5A3 trip due to a loose wire connection on the panel wing of the No.2 Prot Interzone panel in the summated neutral CT circuit associated with CB 5222. After | [7 empty] | 1 | 0 | 2009
1615 | 26735 | Unknown | Unknown | TRUE | Proc |  |  |  | 2009-F-0200/1 | 5A3 Bayswater - Mt Piper 500kV TL | Z | 2009Q2 | BAY, MTP |  | TL | 2009-04-15 03:01 | 2009-04-15 07:00 |  |  |  | T/L tripped at Bayswater only. High voltage levels experienced at Mt Piper. ( no Mt Piper Generation in-service). An attempt at closing at Bayswater was unsuccessful. 5A3 T/L was de-energised at Mt Piper at 03:07hrs. 5A3 to remain out of service. 5a3 due | [7 empty] | 0 | 0 | 2009
1614 | 26734 | Windblown/object | Unknown | TRUE | TL |  |  |  | 2009-F-0199 | 97L Guthega - Jindabyne Pumps 132kV TL | Z | 2009Q2 | GTH |  | TL | 2009-04-15 10:33 | 2009-04-15 11:18 | Snowy Hydro staff on site at Guthega report strong winds in area at time of trip. No pumping at Jindabyne at time of trip. | No further action planned. |  | Snowy Hydro staff on site at Guthega report strong winds in area at time of trip. No pumping at Jindabyne at time of trip. No A/R installed on this line. | Very Windy | [6 empty] | 0 | 0 | 2009
1617 | 26899 | Bushfire | Bushfire | TRUE | TL |  |  |  | 2009-F-0205/1 | 66 Murray - Lower Tumut 330kV TL | Z | 2009Q2 | LT1, MUR |  | TL | 2009-04-21 15:58 | 2009-04-21 18:36 |  |  |  | T/L tripped at both ends. The line did not reclose. Lower Tumut end is normally non-auto reclose, however Murray end should have reclosed after 2 minutes. Cause of trip unknown until unconfirmed reports of fire near the line were received at 1630hrs. A pa | [7 empty] | 0 | 0 | 2009
1618 | 26902 | Relay | Bushfire | TRUE | Cont |  |  |  | 2009-F-0205/1 | 66 Lower Tumut 330kV A CB 662A | Q | 2009Q2 | MUR |  | CB | 2009-04-21 15:58 | 2009-04-21 18:36 |  |  |  | T/L tripped at both ends. The line did not reclose. Lower Tumut end is normally non-auto reclose, however Murray end should have reclosed after 2 minutes. Cause of trip unknown until unconfirmed reports of fire near the line were received at 1630hrs. A pa | [7 empty] | 0 | 0 | 2009
1619 | 27041 | HV Equipment | Sec Eqt Malfunction | TRUE | CB SF6 |  |  |  | 2009-E-0023 | 5A1 Kemps Creek 500kV CB 5A12 | Q | 2009Q2 | ER0 |  | CB | 2009-04-27 00:10 | 2009-04-27 02:23 | low sf6 gas on cb. topped up & rts |  |  | Low SF6 gas on CB. Topped up & RTS | [7 empty] | 0 | 0 | 2009
1620 | 27056 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2009-E-0021 | 96L Lismore 330 - Tenterfield tee Casino 132kV TL | E | 2009Q2 | LSM, TTF |  | TL | 2009-04-27 14:41 | 2009-04-27 14:55 | CB96L2 Blue phase low SF6. CB isolated, topped up and returned to service at 14:55hrs |  |  | CB96L2 Blue phase low SF6. CB isolated, topped up and returned to service at 14:55hrs | [7 empty] | 0 | 0 | 2009
1621 | 27058 | HV Equipment | Sec Eqt Malfunction | TRUE | CB SF6 |  |  |  | 2009-E-0022 | No.2 Capacitor | Q | 2009Q2 | TRE |  | CAP | 2009-04-28 00:26 | 2009-04-28 01:15 | cb 2722 low sf6 gas..topped up & rts |  |  | CB 2722 low SF6 gas topped up & RTS | [7 empty] | 0 | 0 | 2009
1622 | 27111 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2009-E-0024 | 96L Lismore 330 - Tenterfield tee Casino 132kV TL | E | 2009Q2 | LSM, TTF |  | TL | 2009-04-28 13:18 | 2009-04-28 15:08 | Low SF6 - taken O/S and leaking pressure gauge replaced, SF6 topped up. RTS at 1508. |  |  | Low SF6 - taken O/S and leaking pressure gauge replaced, SF6 topped up. RTS at 1508. | [7 empty] | 0 | 0 | 2009
1623 | 27134 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2009-E-0025 | No.3 Transformer 330kV CB 5432A | Q | 2009Q2 | TOM |  | CB | 2009-04-29 16:07 | 2009-04-30 14:04 |  |  |  | CB 5432A Nitrogen Accumulator leaked and needed replacement. Bus A and TL 95 out to facilitate isolation. 1607 - 1636 hrs No load loss as potlines transferred. CB 5432A out 1607 29/4 RTS 1404 30/4. The leaked Nitrogen Accumulator was repaired and the CB54 | [7 empty] | 0 | 0 | 2009
1628 | 27800 | Secondary Equipment | Sec Eqt Malfunction | TRUE | Sec |  |  |  | 2009-F-0211 | No.5 Capacitor | Z | 2009Q2 | SYW |  | CAP | 2009-05-04 07:34 | 2009-05-04 07:35 | CB4752 tripped on opening 932 Mt Druitt CB9322 |  |  | At Sydney West No.5 Cap CB 4752 TRIP (Tripped 3 secs after 38 Regentville T/L de-energised). Tripped when 932 T/L de-energised. Protection details: No.1 Prot. Neutral Unbalance Alarm Timing relay - reset OK. | [7 empty] | 0 | 0 | 2009 | Control system fault
1626 | 27717 | Unknown | Unknown | TRUE | TL |  |  |  | 2009-F-0210 | 963 Tomago 132 - Taree 132kV TL | Z | 2009Q2 | TRE, TGO |  | TL | 2009-05-04 15:53 | 2009-05-04 15:53 | No storms in the area at the time of tripping. EA's fault locator is not working. |  |  | No storms in the area at the time of tripping. EA's fault locator is not working. | [7 empty] | 0 | 0 | 2009
1629 | 27801 | Secondary Equipment | Sec Eqt Malfunction | TRUE | Cont |  |  |  | 2009-F-0212 | No.5 Capacitor | Z | 2009Q2 | SYW |  | CAP | 2009-05-05 06:37 | 2009-05-05 06:38 | CB4752 opened on Opening of 38 Regentvilee CB382. Has occurred on other occassions since. Still O/S |  |  | Tripped 3 secs after 38 Regentville T/L de-energised. Reason for trip being investigated | [7 empty] | 0 | 0 | 2009 | Control system fault
1630 | 27802 | Secondary Equipment | Sec Eqt Malfunction | TRUE | Cont |  |  |  | 2009-F-0213 | No.5 Capacitor | Q | 2009Q2 | SYW |  | CAP | 2009-05-06 07:45 | 2009-05-06 07:45 | CB4752 closed on closing No.2 capacitor CB4722 ( No.5 Capacitor CB4752 was Control Inhibited in SCADA at the time) |  |  | CB4752 closed on closing No.2 capacitor CB4722 ( No.5 Capacitor CB4752 was Control Inhibited in SCADA at the time). Appears control system is not functioning as intended. | [7 empty] | 0 | 0 | 2009 | Control system fault
1627 | 27787 | HV Equipment | HV Equipment Failure | TRUE | TX |  |  |  | 2009-F-0240 | No.2 Transformer 132/22kV | A | 2009Q2 | TTF |  | TX | 2009-05-06 11:33 | 2009-05-06 14:31 |  |  |  | Low Oil due to very cold temperature. | [7 empty] | 0 | 0 | 2009
2244 | 16 | Secondary Equipment |  | TRUE | Cont |  |  |  | IR 471 | No.5 Cap |  | 2009Q2 | SYW |  |  | 2009-05-07 16:46 | 2009-05-07 16:46 |  | When closing CB 2232 to RTS 223 Rooty Hill feeder, No.5 Cap CB 4752 closed 2 seconds later. Control system fault has been reported on previous occasions. | [9 empty] | 0 | 0 | 2009 | Control system fault
1631 | 28916 | Staff Error | Sec Eqt Staff Error | TRUE | Prev |  |  |  | 2009-F-0215 | No.1 Transformer 132/11/11kV | Z | 2009Q2 | GAD |  | TX | 2009-05-13 14:05 | 2009-05-13 14:23 | Staff installing/commissioning new control system inadvertently tripped CB due to incorrect wiring diagram. At time of trip VISY had major plant shutdown. Load indeterminate by trending. Tx available for service @ 1423. |  |  | Staff installing/commissioning new control system inadvertently tripped CB due to incorrect wiring diagram. (Wired to the wrong side of the link by contractor in 2000). At time of trip VISY had major plant shutdown. Load indeterminate by trending. Tx avai | [7 empty] | 1 | 0 | 2009 | Incorrect panel wiring due to design
1632 | 29048 | HV Equipment | HV Equipment Failure | TRUE | TL |  |  |  | 2009-F-0219/1 | 11 Dapto - Sydney South 330kV TL | Z | 2009Q2 | DPT, SYS |  | TL | 2009-05-16 05:27 | 2009-05-16 05:27 |  |  |  | Protection details same for both faults - TAR @ 05:30 hrs see FEOR 2009-F-0220, caused by optic fibre OHEW coming adrift, causing flashing over with Blue Phase during high winds. | [7 empty] | 0 | 0 | 2009
1633 | 29057 | HV Equipment | HV Equipment Failure | TRUE | TL |  |  |  | 2009-F-0220/1 | 11 Dapto - Sydney South 330kV TL | Z | 2009Q2 | DPT, SYS |  | TL | 2009-05-16 05:30 | 2009-05-16 18:37 |  |  |  | Protection details same for both faults - TAR @ 05:27 hrs see FEOR 2009-F-0219, caused by optic fibre OHEW coming adrift, causing flashing over with Blue Phase during high winds. RTS 18:37, required I.E. 33kV & 11kV U/X's O/S in Cleveland Rd. Dapto. | [7 empty] | 0 | 0 | 2009
1634 | 29085 | HV Equipment | Unknown | TRUE | TL |  |  |  | 2009-F-0221 | 96P Taree - Stroud 132kV TL | Z | 2009Q2 | TRE |  | TL | 2009-05-18 12:02 | 2009-05-18 12:02 | Weather light rain and little wind | It is proposed to restore the bonding connections on the poles and to replace insulators on this section of the line (which is within the Duralie Open Cut mine site), with the ones that are more resistant to pollution. |  | On Tuesday the 19th of May 2009 a ground patrol of the line from Stroud SS to Structure 387 was carried out. Broken bonding lead connections onto the earth wire and some burning of the wood pole in the vicinity of the pole's bonding strip were found on st | [7 empty] | 0 | 0 | 2009
1635 | 29090 | HV Equipment | Unknown | TRUE | Cap |  |  |  | 2009-F-0222 | No.2 Capacitor | Z | 2009Q2 | FB2 |  | CAP | 2009-05-18 17:11 | 2009-05-19 13:47 | Burnt smell around the capacitor cage. No2 Cap had been in service since 0743 rts 19/5 at 1347hrs | There are no more spares for this type of capacitor remaining. In the event of more can failures, the bank will be made serviceable by removing additional cans with the failed can to balance the bank. ¦ Stores to investigate if spares can be procured. If |  | Burnt smell around the capacitor cage. No2 Cap had been in service since 0743. Neutral Unbalance Protection up on both protections and a burnt smell around the Capacitor. The capacitor bank was investigated during the next day shift and four failed cans w | [7 empty] | 0 | 0 | 2009
1636 | 29157 | Secondary Equipment | Sec Eqt Malfunction | TRUE | SVC |  |  |  | 2009-F-0223 | No.2 Static Var Compensator | Z | 2009Q2 | KCR |  | SVC | 2009-05-20 09:43 | 2013-01-01 |  |  |  | At 09:42hrs No 2 SVC tripped at Kemps Creek. No impact on Market as a result of trip. No 2 SVC was isolated while reason for trip is investigated. Both the closed loop and open loop controls for the No.2 SVC have critically failed and cannot be repaired. |  | Secondary Equipment | [5 empty] | 0 | 0 | 2009
1770 | 93457 | HV Equipment | Sec Eqt Malfunction | TRUE | CB SF6 |  |  |  | 2009-E-0026/1 | 9J1 Blacktown 132kV CB 9J12 | Q | 2009Q2 | SYW |  | CB | 2009-05-24 14:16 | 2009-05-24 15:40 |  |  |  | Low SF6 Topped | [7 empty] | 0 | 0 | 2009
1637 | 29394 | Switching error | Operating Error | TRUE | Prev |  |  |  | 2009-F-0229 | 895 Forbes - Parkes 66kV Line | S | 2009Q2 | FB2 |  | TL | 2009-05-27 08:35 | 2009-05-27 08:50 | CB896 feeder was bypassed onto CB895 at Forbes. CB8952 TARTLO when 66kV Bus Section 1 VT was de-energised for planned switching. West Jemalong load of 6.5MW was lost. Load was restored at 08:50hrs. 895 Feeder is a stand-by Feeder to Parkes and was open a |  |  | CB896 feeder was bypassed onto CB895 at Forbes. CB8952 TARTLO when 66kV Bus Section 1 VT was de-energised for planned switching. West Jemalong load of 6.5MW was lost. Load was restored at 08:50hrs. 895 Feeder is a stand-by Feeder to Parkes and was open a | Fine | [6 empty] | 0 | 1 | 2009 | Incorrect isolation of VT
1638 | 29522 | HV Equipment | U/Volt Load Shed | TRUE | TX |  |  |  | 2009-F-0232 | No.3 Transformer 132/66/11kV | Z | 2009Q2 | CMA |  | TX | 2009-05-31 04:26 | 2009-07-14 13:43 | Auto Close scheme associated with No's 1 & 2 transformers failed to operate. No interruption to supply due to CE system arrangements. Transformer faulty and has been replaced with Spare from Molong | LOCAL AREA ¦ The damaged transformer has undergone limited testing by Aurecon while drained of oil, to determine its suitability for repair. An official report is yet to be produced. However, it was advised that the windings in the transformer appear to b |  | Tripped on both Differential and Buchholz Protection. No interruption to supply. Subsequent preliminary inspections have revealed no obvious cause or oil spillage. Auto Close scheme associated with No's 1 & 2 transformers failed to operate. No interruptio | [7 empty] | 0 | 0 | 2009
1639 | 30104 | HV Equipment | Sec Eqt Malfunction | TRUE | CB SF6 |  |  |  | 2009-E-0027 | No.2 Capacitor | E | 2009Q2 | SE1 |  | CAP | 2009-06-08 00:16 | 2009-06-08 00:38 |  |  |  | 132kv A Section 3-4 De-energised to allow isolation of Closed No.2 Capacitor CB4722 from system. Short Notice outage followed. | [7 empty] | 0 | 0 | 2009
1640 | 30108 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0239 | 96M Narrabri - Moree 132kV TL | Z | 2009Q2 | MRE, NB2 |  | TL | 2009-06-09 02:54 | 2009-06-09 02:54 | Distance to trip RANZA 25% from Narrabri |  |  | Investigations have revealed that the No1 protection at Moree SS operated correctly. Information entered in the FEOR is not correct. A ground patrol carried out on the 15th of June 2009, between Structure 117 & 160 and around the two major road crossings | [7 empty] | 0 | 0 | 2009
1641 | 30169 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2009-E-0028 | 24 Eraring 330kV GEN BUS CB 242G | Q | 2009Q2 | VP1 |  | CB | 2009-06-10 00:26 | 2009-06-10 01:26 |  |  |  |  | Fine | [6 empty] | 0 | 0 | 2009
1643 | 30211 | HV Equipment | HV Equipment Failure | TRUE | TX |  |  |  | 2009-F-0240 | No.2 Transformer 132/22kV | Z | 2009Q2 | TTF |  | TX | 2009-06-11 01:29 | 2009-06-11 13:15 | Low Oil due to very cold temperature | The oil leak will be monitored ahead of permanent repairs being undertaken. |  | Low Oil due to very cold temperature. Oil also topped up on Planned Notice outage 30604. Investigation of the incident has revealed that an oil leak from the transformer was noticed during the June 2009 FESS inspection at Tenterfield. Repairs were already | [7 empty] | 0 | 0 | 2009
1642 | 30207 | HV Equipment | HV Equipment Failure | TRUE | TX |  |  |  | 2009-F-0242 | No.2 Transformer 330/132/16kV | E | 2009Q2 | SE1 |  | TX | 2009-06-11 03:18 | 2009-06-11 03:42 |  |  |  | Cooling Fail alarm occurred 1913hrs. No.1 oil pump failed. Trip caused by No.2 Oil pump auto-stopping after run. RTS 1858hrs 12/6/09 with No.2 Oil Pump running on manual. Found open circuit winding on white phase No.1 Oil Pump. Pump has been isolated. The | [7 empty] | 0 | 0 | 2009
1645 | 30316 | HV Equipment | Sec Eqt Malfunction | TRUE | TL |  |  |  | 2009-E-0030 | No.1 Transformer 132/33/11kV | E | 2009Q2 | TRE |  | TX | 2009-06-12 16:07 | 2009-06-12 17:09 |  |  |  | cb 4412 low sf6 gas. topped up and rts | [7 empty] | 0 | 0 | 2009
1647 | 30376 | Unknown | Unknown | TRUE | TL |  |  |  | 2009-F-0243 | 96F Stroud - Beresfield 132kV TL | Z | 2009Q2 | SRD, BRF |  | TL | 2009-06-13 23:09 | 2009-06-13 23:13 | 96F tripped at 23:09hrs. 96F placed on load at Beresfield manually at 23:13hrs. No A/R installed at Beresfield. | The area of fault is noted for particular attention during the next aerial patrol of the line. |  | 96F tripped at 23:09hrs. 96F placed on load at Beresfield manually at 23:13hrs. No A/R installed at Beresfield. A ground patrol of the line between Structure 250 and 280 carried out on the 15th of June 2009 has indicated no evidence of any fault contribu | [7 empty] | 0 | 0 | 2009
1648 | 30504 | Unknown | Unknown | TRUE | TL |  |  |  | 2009-F-0245/1 | 948 Panorama - Orange 132kV TL | Z | 2009Q2 | ORG, PMA, ONO |  | TL | 2009-06-18 06:53 | 2009-06-18 06:53 |  |  |  | TAR No storms in the area | [7 empty] | 0 | 0 | 2009
1649 | 30607 | Staff Error | Sec Eqt Malfunction | TRUE | Prev |  |  |  | 2009-F-0246 | No.6 Broken Hill - Talc St -1 22kV Line | Q | 2009Q2 | BKH |  | TL | 2009-06-22 16:13 | 2009-06-22 16:13 | Staff removed & restored control +ve fuse on CB 62 to prove Scada alarm check, causing CB to TAR, no protection flags & no loss of load. Staff to follow up Thurs 23/6 during planned outage of Fdr. |  |  | Staff removed & restored control +ve fuse on CB 62 to prove SCADA alarm check, causing CB to TAR, no protection flags & no loss of load. Staff to follow up Thurs 23/6 during planned outage of Fdr. | [7 empty] | 0 | 1 | 2009 | Incorrect removal of fuse
1650 | 30672 | Contractor Error | Human Interference | TRUE | Prev |  |  |  | 2009-F-0250 | No.2 Transformer 330/132/11kV | Z | 2009Q2 | SYS |  | TX | 2009-06-24 11:51 | 2009-06-24 12:15 | Contractor working on No.1 Transformer installation inadvertantly placed a earth on BBP Initiate wiring of No.2 Transformer No.2 Prot causing the trip. | No further action required |  | Contractor working on No.1 Transformer installation inadvertently placed a earth on BBP Initiate wiring of No.2 Transformer No.2 Prot causing the trip. The Contractor reviewed its applicable SWMS and decided to make use of retractable tip test leads for s | Fine | [6 empty] | 1 | 1 | 2009 | Inadvertent placing of earth on BBP links
1652 | 30749 | Wiring Error | Sec Eqt Malfunction | TRUE | Proc |  |  | Load Lost 16.27MWh | 2009-F-0251 | 9W7 Nambucca - Boambee South 132kV TL | C | 2009Q2 | NAM, BOS |  | TL | 2009-06-24 23:53 | 2009-06-25 03:57 | RTS @ 03:57 on 25/6/09. No.2 TX energised only prior trip. CT ratio for CB 9W72 found incorrect. | Refer to the detailed report on the incident. |  | RTS @ 03:57 on 25/6/09. No.2 TX energised only prior trip. CT ratio for CB 9W72 found incorrect. A separate report on the incident will be prepared by the Projects Manager/ Northern Region | [7 empty] | 1 | 0 | 2009 | Incorrect CT ratio connection
1653 | 30902 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0252 | 994 Wagga 330 - Yanco 132kV TL | Z | 2009Q2 | WG1, YA2 |  | TL | 2009-06-26 14:30 | 2009-06-26 14:30 | Storms near Wagga. | An aerial patrol will be undertaken in November. |  | Storms near Wagga. An aerial patrol will be undertaken in November. | Thunderstorm | [6 empty] | 0 | 0 | 2009
1654 | 31015 | Secondary Equipment | LV/MECH/PROT Equipment Fail | TRUE | AC/DC |  |  |  | 2009-E-0031 | No.2 Transformer 132/66/11kV | E | 2009Q2 | AR1 |  | TX | 2009-06-30 21:58 | 2009-07-01 09:41 | Taken out of service to investigate earth fault on No.2 TX Bay controls. Fault found in Fire Prot cable (vermin). | NIL |  | Taken out of service to investigate earth fault on No.2 TX Bay controls. Fault found in Fire Prot cable (vermin). Investigations found the cause of the incident to be a fire protection cable chewed through by rabbits and damaged. The damaged cable was rep | [7 empty] | 0 | 0 | 2009
1663 | 31122 | HV Equipment | HV Equipment Failure | TRUE | CT |  |  | CB Low SF6 CB taken O/S, topped up & RTS | 2009-F-0262 | Spare Bay 4 Transformer CB 5242 | Q | 2009Q3 | BAY |  | CB | 2009-07-02 10:47 | 2009-07-02 16:45 | Explosive failure of CB 5042 CT in adjacent bay. |  |  | "Trip due to explosive failure of CB 5042 Blue phase CT. A Committee of Enquiry is investigating the details of the incident and the cause of the explosion." | [7 empty] | 0 | 0 | 2009
1664 | 31830 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2009-E-0033 | 22 SYDNEY NORTH 330KV GEN BUS CB 222G | Q | 2009Q3 | VP1 |  | CB | 2009-07-05 23:45 | 2009-07-06 00:38 | CB Low SF6 CB taken O/S, topped up & RTS |  |  | CB Low SF6 CB taken O/S, topped up & RTS | [7 empty] | 0 | 0 | 2009
1665 | 32403 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2009-E-0034 | 9J2 Sydney West - Blacktown 132kV Line | Q | 2009Q3 | SYW |  | TL | 2009-07-18 14:30 | 2009-07-18 15:18 | Low SF6 - Topped and RTS | The o-rings for these CB's have been stocklined. During future maintenance on this type of CB, if the gauge is removed for testing then the o-ring will be replaced with a new o-ring. |  | The o-rings for these CB's have been stocklined. During future maintenance on this type of CB, if the gauge is removed for testing then the o-ring will be replaced with a new o-ring. | [7 empty] | 0 | 0 | 2009
1667 | 32407 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2009-E-0035 | 37 Macarthur A CB 372A | Q | 2009Q3 | KCR |  | CB | 2009-07-18 20:10 | 2009-07-18 21:17 | Blue Phase pole stuck in semi closed position. Isolated on Log Entry. to allow Local operation. CB opened and freed . Opening and closing correctly. 37 T/L RTS at 2117hrs | This CB is planned for replacement by the Projects group in November 2009. |  | Blue Phase pole stuck in semi closed position. Isolated on Log Entry. to allow Local operation. CB opened and freed . Opening and closing correctly. 37 T/L RTS at 2117hrs | [7 empty] | 0 | 0 | 2009
1668 | 32409 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2009-E-0036 | 37 Macarthur A CB 372A | Q | 2009Q3 | KCR |  | CB | 2009-07-19 18:33 | 2009-07-19 19:26 | Low SF6 Blue phase CT, Topped and RTS 1926hrs | Gas levels in CT will be monitored during substation inspections in an event to prevent further emergency outages. In the event the CT requires action then a planned outage will occur for top-up implementation of suppliers advice. |  | Low SF6 Blue phase CT, Topped and RTS 1926hrs | [7 empty] | 0 | 0 | 2009
1669 | 32453 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2009-E-0037 | No.3 Capacitor | Q | 2009Q3 | PMQ |  | CAP | 2009-07-21 07:50 | 2009-07-21 09:05 | CB Low SF6. Capacitor taken O/S CB topped up & RTS OK |  |  | CB Low SF6. Capacitor taken O/S CB topped up & RTS OK | [7 empty] | 0 | 0 | 2009
1670 | 32719 | Relay Setting | Unknown | TRUE | Proc |  |  |  | 2009-F-0271/1 | No.4 Transformer 330/132/11kV | Z | 2009Q3 | DPT |  | TX | 2009-07-29 13:58 | 2009-07-29 18:04 |  |  |  | CB 5442 tripped on energising No.4 Transformer. No fault found. TX successfully energised @ 1804 hrs.Secondary Systems to implement Protection Design's advice to change the "g" setting from 20% to 40% and the "v" setting from 40% to 50%. This will aid the | [7 empty] | 1 | 0 | 2009 | Incorrect protection setting
1671 | 33762 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0273 | 94T Orange - Molong 132kV TL | Z | 2009Q3 | MOL, ORG, ONO |  | TL | 2009-08-11 06:30 | 2009-08-11 06:30 | Lightning in area at time of trip. | No further action required |  | Lightning in area at time of trip. | Thunderstorm | [6 empty] | 0 | 0 | 2009
1673 | 33798 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0277 | 97K Cooma - Munyang tee Snowy Adit 132kV TL | Z | 2009Q3 | CMA, MNY |  | TL | 2009-08-11 16:08 | 2009-08-11 16:08 | Storms in area |  |  | Storms in area. Aerial inspection staff advised of trip inspection to look for flash over. | Thunderstorm | [6 empty] | 0 | 0 | 2009
1672 | 33796 | Secondary Equipment | LV/MECH/PROT Equipment Fail | TRUE | TX |  |  |  | 2009-F-0276 | No.2 Transformer 330/132/11kV | Z | 2009Q3 | SYS |  | TX | 2009-08-12 12:12 | 2009-08-12 19:00 | No.2 oil Pump was running on manual & failed causing TX to trip. TX returned to service @ 1900 hrs on 12/08/09. |  |  | No.2 oil Pump was running on manual & failed causing TX to trip. TX returned to service @ 1900 hrs on 12/08/09. | Fine | [6 empty] | 0 | 0 | 2009
1674 | 33908 | Staff Error | LV/MECH/PROT Equipment Fail | TRUE | Prev |  |  |  | 2009-E-0039/2 | 32 Sydney West - Bayswater 330kV TL | E | 2009Q3 | BAY, SYW |  | TL | 2009-08-14 10:45 | 2009-08-14 10:45 |  |  |  | "32 TL off-loaded at 10:45.12hrs to tighten a CT secondary link associated with CB322, that was heard arcing when staff were nearby switchyard CT secondary marshalling kiosk. 32 T/L placed on load at 10:45.46hrs. Outage time was 34 seconds. Off-loading wa | [7 empty] | 0 | 0 | 2009
1675 | 33934 | HV Equipment | Sec Eqt Malfunction | TRUE | CT |  |  |  | 2009-E-0038 | No.1 Transformer 132/66/11kV | E | 2009Q3 | KLK |  | TX | 2009-08-16 14:39 | 2009-08-16 15:11 | No 1 Tx CT Low SF6. Tx taken OOS gas topped up & Tx RTS |  |  | No 1 Tx CT Low SF6. Tx taken OOS gas topped up & Tx RTS | [7 empty] | 0 | 0 | 2009
1680 | 34140 | Wiring Error | Sec Eqt Malfunction | TRUE | Prev |  |  |  | 2009-F-0286 | 96H Coffs Harbour - Koolkhan 132kV TL | Z | 2009Q3 | COF, KLK |  | TL | 2009-08-24 13:12 | 2009-08-24 13:20 | Protection staff report a cable fell from a lug opening a CT circuit while working on No 2 Tx ( Not Commissioned) . No load loss or overloads. | NIL | [9 empty] | 1 | 0 | 2009 | Cable falling off a lug
1681 | 34206 | Windblown/object | Wind | TRUE | Other |  |  |  | 2009-F-0288 | 330kV A Bus | Q | 2009Q3 | DNT |  | BB | 2009-08-24 23:24 | 2009-08-25 08:25 |  |  |  | Advised a flashover has occured between blue phase dropper to 63 line bypass ABS from 330KV bus & O/H strung bus Structure. The dropper to Bypass ABS is approx. 10M long & burn mark is about 3M from ABS, also a burn mark on the Str is seen. The dropper i | [7 empty] | 0 | 0 | 2009
1689 | 34327 | Relay Setting | Unknown | TRUE | Proc |  |  |  | 2009-F-0290 | No.1 Shunt Reactor | Q | 2009Q3 | BAY |  | RX | 2009-08-25 02:19 | 2009-08-27 10:53 | No.1 reactor tripped on closing CB2912. No.1 reactor isolated, pending further investigation. | NIL |  | No.1 reactor tripped on closing CB2912. No.1 reactor isolated, pending further investigation. Protection Design determined that a setting change was required to avoid the possibility of trip on closing the CB due to point on wave switching problems. This | [7 empty] | 1 | 0 | 2009 | Incorrect protection setting
1688 | 34325 | Switching error | Unknown | TRUE | Prev |  |  | "Generator Trip 540MW" | 2009-F-0289/1 | No.4 Generator Transformer Generator Bus 500kV CB 6242G | Q | 2009Q3 | BAY |  | CB | 2009-08-25 13:32 | 2009-08-26 18:54 |  |  |  | 1725hrs: Advises PCR have advised of a trip of the boiler on Unit4. 1750hrs: Advises TG prot staff have advised that insufficient isolations were taken during investigations and an inadvertant trip into the PS from the I/Z multitrip has caused the trip of | [7 empty] | 0 | 1 | 2009 | Incorrect isolation leading to intertrip. No info to suggest protection system fault.
1690 | 34328 | Relay Setting | Unknown | TRUE | Proc |  |  | "Load Lost 1.66MW" | 2009-F-0291 | 79C Griffith - Darlington Point 33kV Line | S | 2009Q3 | GRF |  | TL | 2009-08-25 14:22 | 2009-08-26 15:19 | Supply fully restored to customers via 79P Goolgowi Feeder @ 1706 hours. C.E. unable to provide any load loss statistics. Unable to determine from Transformer loading trends at Griffith. Attempted to return to service at 1424 hours. Feeder tripped on memo |  |  | "At 23:24hrs 79C Griffith to Darlington Point 33kV feeder tripped interrupting 4MW of load. High winds in the area. Feeder returned to Service at 06:50hrs At 03:539hrs 79C Griffith to Darlington Point 33kV feeder tripped interrupting 4MW of load. Storm in | [7 empty] | 1 | 0 | 2009 | QAPR report indicates incorrect protection setting
1687 | 34218 | Secondary Equipment | LV/MECH/PROT Equipment Fail | TRUE | Sec |  |  |  | not available | No.4 Generator Transformer Main Bus 500kV CB 6242M | Q | 2009Q3 | BAY |  | CB | 2009-08-25 16:08 | 2009-08-25 18:32 | [11 empty] | 0 | 0 | 2009 | Duplicate of outage ID 34325
1695 | 35273 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  | Generation Lost 25MW | 2009-F-0309 | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2009Q3 | GTH, MUR, GHI |  | TL | 2009-08-29 11:18 | 2009-08-29 13:01 | Storms in area at time of trip. Guthega generation 25 MW at time of trip.No protection details available. RTS @ 0101 30/08/09 | Climbing Inspection to check all insulators |  | At 11:18hrs 97G Murray to Guthega tee Geehi 132 kV T/L tripped interrupting 25MW of Guthega generation. Storm activity in the area. At 13:01hrs 97G was re-energised. Climbing Inspection to check all insulators | Thunderstorm | [6 empty] | 0 | 0 | 2009
1694 | 34526 | Windblown/object | Unknown | TRUE | TL |  |  |  | 2009-F-0303/1 | 14 Sydney North - Kemps Creek 330kV TL | Z | 2009Q3 | KCR, SYN |  | TL | 2009-08-29 16:39 | 2009-08-29 16:40 |  |  |  | At 16:39hrs 14 Kemps Creek to Sydney North 330 kV T/L tripped and auto reclosed. Strong winds in the area. W-E Fault unable to determine length of Fault due to fault recorder trace. | [7 empty] | 0 | 0 | 2009
1693 | 34517 | Staff Error | Sec Eqt Staff Error | TRUE | Prev |  |  | no lost load | 2009-F-0302 | 99X Wagga 330 - Wagga 132 132kV TL | Z | 2009Q3 | WG2, WG1 |  | TL | 2009-08-30 11:22 | 2009-08-30 11:40 | 99X T/L while being relocated to 132kV B1 Bus @ WG2 , when placed on load the 132kV B1 Bus tripped @ WG2. Cause found to be missing connections between 99X secondary C.T. links & associated BBP summation bus. @ WG2 132kV B1 Bus RTS @ 11:40hrs, No.2 Tx R |  |  | 99X T/L while being relocated to 132kV B1 Bus @ WG2 , when placed on load the 132kV B1 Bus tripped @ WG2. Cause found to be missing connections between 99X secondary C.T. Links & associated BBP summation bus. @ WG2 132kV B1 Bus RTS @ 11:40hrs, No.2 Tx RTS | Fine | [6 empty] | 1 | 0 | 2009 | Missing wiring from BBP links to CT
1696 | 35571 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2009-E-0041 | 37 Macarthur A CB 372A | Q | 2009Q3 | KCR |  | CB | 2009-09-12 18:15 | 2009-09-12 19:04 | Low SF6 Blue Phase CT assoc. with CB372A. | Gas levels in CT will be monitored during substation inspections in an event to prevent further emergency outages. In the event the CT requires action then a planned outage will occur for top-up implementation of suppliers advice. |  | CB Low SF6 CB taken O/S, topped up & RTS | [7 empty] | 0 | 0 | 2009
1711 | 36257 | HV Equipment | Unknown | TRUE | TX |  |  |  | 2009-E-0043 | No.3 Transformer 330/132/11kV | E | 2009Q3 | SYS |  | TX | 2009-09-17 18:54 | 2009-09-18 09:40 | No.3 Tx taken O/S after BHZ alarm, subsequent investigation found local alarm indicated it was Main Tank/OLTC oil level alarm, Main Tank level OK, T/C level over top mark, no gas from BHZ. Confirmed T/C had excess oil (was warm day when alarm occurred), 3 | Plant branch have been advised of the issues. No further action proposed. |  | No.3 Tx taken O/S after BHZ alarm, subsequent investigation found local alarm indicated it was Main Tank/OLTC oil level alarm, Main Tank level OK, T/C level over top mark, no gas from BHZ. Confirmed T/C had excess oil (was warm day when alarm occurred), 3 | Fine | [6 empty] | 0 | 0 | 2009
1697 | 35742 | Bushfire | Bushfire | TRUE | TL |  |  |  | 2009-F-0320/1 | 27 Sydney North - Sydney East 330kV TL | Z | 2009Q3 | SE1, SYN |  | TL | 2009-09-19 13:34 | 2009-09-19 13:34 |  |  |  | Hazard reduction Backburn in vicinity. Also TAR of 27 T/L at same time. EA Restored Berowra load 1432hrs. Returned to service after patrol by E.A. 1858hrs. | [7 empty] | 0 | 0 | 2009
1698 | 35745 | Bushfire | Bushfire | TRUE | TL |  |  | Load Lost 9.5MW | 2009-F-0321 | 250 Sydney North - Berowra 132kV Line | C | 2009Q3 | SYN |  | TL | 2009-09-19 13:34 | 2009-09-19 18:58 | Hazard reduction Backburn in vicinity. Also TAR of 27 T/L at same time. EA Restored Berowra load 1432hrs. Returned to service after patrol by E.A. 1858hrs. |  |  | Hazard reduction Backburn in vicinity. Also TAR of 27 T/L at same time. EA Restored Berowra load 1432hrs. Returned to service after patrol by E.A. 1858hrs. | Fine | [6 empty] | 0 | 0 | 2009
1700 | 35751 | Bushfire | Bushfire | TRUE | TL |  |  |  | 2009-F-0323/1 | 27 Sydney North - Sydney East 330kV TL | Z | 2009Q3 | SE1, SYN |  | TL | 2009-09-19 17:07 | 2009-09-19 19:21 |  |  |  | Controlled hazard reduction burn being carried out in the area. CB 272B at Sydney East closed by staff on site. | [7 empty] | 0 | 0 | 2009
1699 | 35746 | Unknown | Unknown | TRUE | TL |  |  |  | 2009-F-0322/1 | 5A3 Bayswater - Mt Piper 500kV TL | Z | 2009Q3 | BAY, MTP |  | TL | 2009-09-19 23:32 | 2009-09-20 15:18 |  |  |  | Helicopter patrol of 5A3 from Bayswater to STR 150, no cause of fault found. Weather fine and clear at time of trip. Reclose non-auto at time of trip. Line returned to service at 15:18hrs on 20/09/09. | [7 empty] | 0 | 0 | 2009
1701 | 35754 | Unknown | Unknown | TRUE | TL |  |  |  | 2009-F-0324/1 | 5A2 Eraring - Kemps Creek 500kV TL | Z | 2009Q3 | ER0, KCR |  | TL | 2009-09-21 00:52 | 2009-09-21 00:52 |  |  |  | "@ Kemps Creek 500kV Substation 5A2 Eraring to Kemps Creek 500 kV T/L TAR, no known cause, F/Rec operated @ SYW, SYN, Dapto, RGV, Kemps Creek, Vineyard, from SYW F/Rec fault duration 3.5 cycles, voltage depression R 4.2%, W 15.1%, B 1.5%. @ Kemps Ck & E | [7 empty] | 0 | 0 | 2009
1704 | 35950 | Windblown/object | Wind | TRUE | TL |  |  |  | 2009-F-0351/1 | X2 Buronga - Broken Hill 220kV TL | Z | 2009Q3 | BKH, BRG |  | TL | 2009-09-21 18:21 | 2009-09-29 18:10 | [11 empty] | 0 | 0 | 2009
1702 | 35912 | Pollution | Pollution | TRUE | SVC |  |  |  | 2009-F-0336 | No.1 Static VAR Compensator | Z | 2009Q3 | AR1 |  | SVC | 2009-09-23 21:53 | 2009-09-24 00:11 | Suspected flashover caused by dust pollution. Returned to service at 0011 HRS on 24/09/09 |  |  | Suspected flashover caused by dust pollution. | Fine | [6 empty] | 0 | 0 | 2009
1703 | 35913 | Pollution | Pollution | TRUE | SVC |  |  |  | 2009-F-0337 | No.1 Static VAR Compensator | Z | 2009Q3 | AR1 |  | SVC | 2009-09-24 02:15 | 2009-09-24 06:33 | Still out of service refer to Forced Outage 36945 for previous outage 2 hours earlier. | NIL ¦ NIL |  | Still out of service refer to Forced Outage 36945 for previous outage 2 hours earlier. Capicator associated with SVC replaced. | Fine | [6 empty] | 0 | 0 | 2009
1705 | 36045 | Pollution | Pollution | TRUE | TL |  |  |  | 2009-F-0345/2 | 5A2 Eraring - Kemps Creek 500kV TL | Z | 2009Q3 | ER0, KCR |  | TL | 2009-09-26 04:28 | 2009-09-26 04:28 |  |  |  | High wind & dust storm. CB 5A22A closed via Scada at Kemps Creek. | [7 empty] | 0 | 0 | 2009
1706 | 36059 | Staff Error | Sec Eqt Staff Error | TRUE | Prev |  |  |  | 2009-F-0350 | 132kV A Bus 2-3 Section CB 4122 | Q | 2009Q3 | SE1 |  | CB | 2009-09-27 16:07 | 2009-09-28 22:44 | Attempted RTS bus, C.B.'s 4102 & 4422A closed successfully, but as soon as an attempt to close C.B. 4122 was made bus immediately tripped. Bus RTS at 22:44hrs leaving C.B. 4122 isolated from the system. Subsequent investigation found Blind Spot IOC check |  |  | Attempted RTS bus, C.B.'s 4102 & 4422A closed successfully, but as soon as an attempt to close C.B. 4122 was made bus immediately tripped. Bus RTS at 22:44hrs leaving C.B. 4122 isolated from the system. Subsequent investigation found Blind Spot IOC check | Very Windy | [6 empty] | 1 | 1 | 2009 | QAPR report indicates blind spot IOC check link left open from previous work.
1764 | 42382 | Switching error | Operating Error | TRUE | Prev |  |  |  | 2009-F-0490 | 852 Beryl - Dunedoo 66kV Line | S | 2009Q4 | BER |  | TL | 2009-10-01 07:50 | 2009-10-01 07:54 | During switching for planned outage of 66kV Bus No.3 Section the 852 Dunedoo 66kV CB 8522 was opened prior to load transfer by Country Energy. 7MW interrupted from 0750hrs to 0754hrs (4 minutes). |  |  | During switching to isolate the Section 3 of the 66kV busbar load was inadvertently lost due to an ABS not being closed. | [5 empty] | Y |  | 0 | 1 | 2009 | Incorrect switching
1712 | 37565 | Unknown | Unknown | TRUE | TL |  |  |  | 2009-F-0354 | 99B Jindera - Albury 132kV TL | Z | 2009Q4 | ALB, JDA |  | TL | 2009-10-05 04:18 | 2009-10-05 04:18 |  |  |  | Aerial inspection staff advised of trip inspection to look for flash over. Inspection to occur second week of November. | Mild | Unexplained |  |  |  | y |  | 0 | 0 | 2009
1716 | 37593 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0361/1 | 13 Sydney South - Kemps Creek 330kV TL | Z | 2009Q4 | KCR, SYS |  | TL | 2009-10-05 14:38 | 2009-10-05 14:38 |  |  |  | C.B. 132B at Sydney South closed manually via SCADA. |  | External |  |  |  | y |  | 0 | 0 | 2009
1713 | 37572 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0356/1 | 22 Sydney North - Vales Point 330kV TL | Z | 2009Q4 | SYN, VP1 |  | TL | 2009-10-05 15:44 | 2009-10-05 15:45 |  |  |  | Storm between Sydney & Gosford |  | External |  |  |  | y |  | 0 | 0 | 2009
1714 | 37577 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0357/1 | 21 Sydney North - Tuggerah 330kV TL | Z | 2009Q4 | SYN, TGH |  | TL | 2009-10-05 16:12 | 2009-10-05 16:12 |  |  |  | Storm between Sydney & Gosford |  | External |  |  |  | y |  | 0 | 0 | 2009
1715 | 37581 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0358/1 | 5A2 Eraring - Kemps Creek 500kV TL | Z | 2009Q4 | ER0, KCR |  | TL | 2009-10-05 16:12 | 2009-10-05 16:12 |  |  |  | Storm between Sydney & Gosford, Follow up required for Kemps Creek |  | External |  |  |  | y |  | 0 | 0 | 2009
1717 | 37622 | Secondary Equipment | Sec Eqt Malfunction | TRUE | TX |  |  |  | 2009-F-0362 | No.2 Transformer 330/132/11kV | Z | 2009Q4 | SYS |  | TX | 2009-10-06 15:01 | 2009-10-06 16:45 | Transformer tripped while staff were investigating fault with No.2 pump control module. Pump stopped and started causing surge. (known issue) Module bypassed, pump started and Transformer RTS. | The soft starters will be replaced when the failed No.1 pump is replaced later this month. Plant Branch will to follow-up with Areva on inappropiate soft starters and pumps that trip the buchholz. |  | Transformer tripped while staff were investigating fault with No.2 pump control module. Pump stopped and started causing surge. (known issue) Module bypassed, pump started and Transformer RTS. Due to the past issues on this transformer, the No.2 pump was | Mild | Secondary Equipment |  |  |  | y |  | 0 | 0 | 2009
1718 | 37647 | Animal/Bird | Unknown | TRUE | TL |  |  |  | 2009-F-0363/2 | 5A3 Bayswater - Mt Piper 500kV TL | Z | 2009Q4 | BAY, MTP |  | TL | 2009-10-07 05:31 | 2009-10-07 05:31 |  |  |  | MtP indicated dist to fault 125.58 kms. bay indicated dtf 97kms. Line is being patrolled by helicopter from str 150 towards mtp. Previous line tripping 19/09/2009...guess what it was red ph to ground as well. In CB operations page, changed From Keeps Cree |  | External |  |  |  | y |  | 0 | 0 | 2009
1719 | 37700 | Animal/Bird | Unknown | TRUE | TL |  |  |  | 2009-F-0365/1 | 5A4 Bayswater - Wollar 500kV TL | Z | 2009Q4 | BAY, WOL |  | TL | 2009-10-09 05:35 | 2009-10-09 05:35 |  |  |  | "This Report covers FEORs 2009-F-0363/1, 2009-F-0365/1, 2009-F-0370/1 & 2009-F-0372/1. Aerial, ground and climbing patrols were carried out to establish the cause of continuing trip and recloses on the 5A3 and 5A4 lines as follows. 1. Bird droppings on so |  | External |  |  |  | y |  | 0 | 0 | 2009
1720 | 37787 | HV Equipment | HV Equipment Failure | TRUE | TL |  |  |  | 2009-F-0367 | 996 Wagga 330 - ANM 132kV TL | Z | 2009Q4 | ANM, WG1 |  | TL | 2009-10-13 15:24 | 2009-10-14 10:55 | Field Staff found hangar bracket on blue phase had failed @ Str. 123 (30-32kms from WG1). Repaired 14.10.09 & RTS 11:55 hrs, all times in EST. |  |  | Field Staff found hangar bracket on blue phase had failed @ Str. 123 (30-32kms from WG1). Outage taken and new insulator string installed. All other AE type structures in Southern checked for serviceability. All Ok. Eye bolt hanger corroded and sent for m | Rain and Very Windy |  |  |  |  | y |  | 0 | 0 | 2009
1721 | 37945 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2009-E-0044 | 83 LIDDELL 330kV A CB 832A | Q | 2009Q4 | MRK |  | CB | 2009-10-17 08:06 | 2009-10-17 08:48 | CB taken out of service to top up Blue phase SF6. RTS @ 0848hrs EST. |  |  | CB taken out of service to top up Blue phase SF6. RTS @ 0848hrs EST. Leak from Densimeter has been found. Repair being scheduled. |  | Oil/Gas Levels |  |  |  | Y |  | 0 | 0 | 2009
1722 | 38027 | Staff Error | Unknown | TRUE | Prev |  |  |  | 2009-F-0368/1 | 132kV B Bus Section 1 | Q | 2009Q4 | SE1 |  | BB | 2009-10-20 12:16 | 2009-10-20 15:28 |  |  |  | No.1 Capacitor out of service for maintenance work. Investigation by protection staff found when maintenance staff were preparing for DDF tests of No.1 capacitor CT's, initially the Metering and Indication core secondaries (Cores 5 & 6) were shorted and w | [5 empty] | Y |  | 1 | 1 | 2009 | CT terminals incorrectly shorted
1723 | 38063 | Animal/Bird | Unknown | TRUE | TL |  |  |  | 2009-F-0370/1 | 5A4 Bayswater - Wollar 500kV TL | Z | 2009Q4 | BAY, WOL |  | TL | 2009-10-21 05:12 | 2009-10-21 05:12 |  |  |  | "This Report covers FEORs 2009-F-0363/1, 2009-F-0365/1, 2009-F-0370/1 & 2009-F-0372/1. Aerial, ground and climbing patrols were carried out to establish the cause of continuing trip and recloses on the 5A3 and 5A4 lines as follows. 1. Bird droppings on so |  | External |  |  |  | y |  | 0 | 0 | 2009
1724 | 38218 | Animal/Bird | Unknown | TRUE | TL |  |  |  | 2009-F-0372/1 | 5A4 Bayswater - Wollar 500kV TL | Z | 2009Q4 | BAY, WOL |  | TL | 2009-10-23 05:31 | 2009-10-23 05:31 |  |  |  | "This Report covers FEORs 2009-F-0363/1, 2009-F-0365/1, 2009-F-0370/1 & 2009-F-0372/1. Aerial, ground and climbing patrols were carried out to establish the cause of continuing trip and recloses on the 5A3 and 5A4 lines as follows. 1. Bird droppings on so |  | External |  |  |  | y |  | 0 | 0 | 2009
1728 | 38272 | Unknown | Unknown | TRUE | SVC |  |  |  | 2009-F-0375/1 | No.1 Static VAR Compensator | Z | 2009Q4 | BKH |  | SVC | 2009-10-25 09:08 | 2009-10-25 10:59 |  |  |  | Storms in the area. |  | Unexplained |  |  |  | y |  | 0 | 0 | 2009
1725 | 38267 | HV Equipment | Unknown | TRUE | CT |  |  |  | 2009-F-0374 | 66kV Bus Section 1 | Q | 2009Q4 | KS2 |  | BB | 2009-10-25 18:48 | 2009-10-25 21:08 |  |  |  | Supply to Telegraph Point restored via Taree SS @ 2028hrs of 1.2MW's. Busbar energised @ 2021hrs via # 4 TX. # 5 TX loaded at 2108hrs. 864 remains o/s for CE visual patrol. Serve storms in the area at the time of tripping. Inspection of the 66kV Bus and t |  | Primary Equipment |  |  |  | y |  | 0 | 0 | 2009
1730 | 38424 | Unknown | Unknown | TRUE | Cap |  |  |  | 2009-F-0379 | No.1 Capacitor | Z | 2009Q4 | CA1 |  | CAP | 2009-10-28 10:38 | 2009-10-28 14:30 | Staff inspected bank, no sign of damage. Clearance given to RTS by Maintenance Manager |  |  | Staff inspected bank, no sign of damage. Clearance given to RTS by Maintenance Manager | Fine | Unexplained |  |  |  | Y |  | 0 | 0 | 2009
1731 | 38442 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0380 | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2009Q4 | GTH, MUR, GHI |  | TL | 2009-10-29 15:59 | 2009-10-29 17:32 | Lightning in vicinity. Attempted reclose at 1732hrs and Guthega Transferred to Murray 1748Hrs. |  |  | Lightning in vicinity. Attempted reclose at 1732hrs and Guthega Transferred to Murray 1748Hrs. Aerial inspection staff advised of trip inspection to look for flash over. Storms at time of trip. Aerial inspection due November 2009. A distance to fault loca |  | External |  |  |  | y |  | 0 | 0 | 2009
1732 | 38465 | AVC Scheme | Unknown | TRUE | Cont |  |  |  | 2009-F-0383 | No.2 Reactor & CB 4922 | Z | 2009Q4 | BFD |  | RX | 2009-10-30 06:44 | 2009-10-30 20:04 | No Protection operations. Possible cause of trip due to fault in AVC scheme. RTS with AVC N/A. RTS @ 2004 |  |  | No Protection operations. Possible cause of trip due to fault in AVC scheme. RTS with AVC N/A. RTS @ 2004. | Fine | Secondary Equipment |  |  |  | Y |  | 0 | 0 | 2009
1733 | 38466 | HV Equipment | HV Equipment Failure | TRUE | TL |  |  |  | 2009-E-0045 | 969 Tamworth 330 - Gunnedah 132kV TL | E | 2009Q4 | GN2, TA1 |  | TL | 2009-10-30 17:30 | 2009-10-30 20:10 | 969 TL was requested isolated and earthed for clearance to remove a conductor that had gave way from its anchor point on a new pole on a line under construction. The conductor dropped onto 11kV Country Energy under crossing causing it to trip. Both 969 T |  |  | 969 TL was requested isolated and earthed for clearance to remove a conductor that had gave way from its anchor point on a new pole on a line under construction. The conductor dropped onto 11kV Country Energy under crossing causing it to trip. Both 969 T | [5 empty] | y |  | 0 | 0 | 2009
1735 | 39159 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0391 | 999 Yass - Cowra 132kV TL | Z | 2009Q4 | CW2, YSN |  | TL | 2009-11-02 19:57 | 2009-11-02 19:57 | Refer to FEOR 2009-F-0392/1 for protection details. | No further action required. |  | T/L also tripped and reclose at 1957hrs EST. (refer FEOR 2009-F-0391/1) Protection details receive after both outages. | Thunderstorm | External |  |  |  | y |  | 0 | 0 | 2009
1736 | 39160 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0392 | 999 Yass - Cowra 132kV TL | Z | 2009Q4 | CW2, YSN |  | TL | 2009-11-02 19:59 | 2009-11-02 19:59 | T/L also tripped and reclose at 1957hrs EST. (refer FEOR 2009-F-0391/1) Protection details receive after both outages. | No further action required. |  | T/L also tripped and reclose at 1957hrs EST. (refer FEOR 2009-F-0391/1) Protection details receive after both outages. | Thunderstorm | External |  |  |  | y |  | 0 | 0 | 2009
1734 | 39087 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0388/1 | 5 Yass - Marulan 330kV TL | Z | 2009Q4 | MRN, YSN |  | TL | 2009-11-02 21:13 | 2009-11-02 21:13 |  |  |  | At Marulan, CB 5042 closed via SCADA at 21:16hrs. |  | External |  |  |  | y |  | 0 | 0 | 2009
1737 | 39172 | Secondary Equipment | LV/MECH/PROT Equipment Fail | TRUE | AC/DC |  |  | lost load 6MW | 2009-F-0393/2 | 132kV Bus | S | 2009Q4 | CLY |  | BB | 2009-11-04 07:30 | 2009-11-04 08:52 |  |  |  | AC/DC AC charger failed |  | Secondary Equipment |  |  |  | y |  | 0 | 0 | 2009
1740 | 39496 | Protection | LV/MECH/PROT Equipment Fail | TRUE | Prot |  |  |  | 2009-E-0046/1 | 3 Lower Tumut - Yass 330kV TL | E | 2009Q4 | LT1, YSN |  | TL | 2009-11-12 02:17 | 2009-11-12 09:39 |  |  |  | Faulty No2 Protection at Lower Tumut | [5 empty] | Y |  | 1 | 0 | 2009
1741 | 39540 | Relay Setting | Unknown | TRUE | Cont |  |  |  | 2009-F-0399 | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Z | 2009Q4 | AR1, COF |  | TL | 2009-11-12 04:45 | 2009-11-12 04:47 | Line reclosed at Coffs however was close via SCADA at Armidale | Replace the flashed string of insulators found on structure 378 of the line. <Duplicate Record> Follow up and instal new control database. |  | "Line reclosed at Coffs however was close via SCADA at Armidale. Investigation of the incident by Technical Services has indicated that the failure to reclose at AR1 was due to a mismatch of settings at AR1 (15 secs and dead line/dead bus) and COF (5 secs | Unknown |  |  |  |  | y |  | 0 | 0 | 2009 | Auto reclose failure is a control system failure, not protection
2019 | 39540 | HV Equipment | Unknown | TRUE | TL |  |  |  | 2009-F-0399 | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Z | 2009Q4 | AR1, COF |  | TL | 2009-11-12 04:45 | 2009-11-12 04:47 | Line reclosed at Coffs however was close via SCADA at Armidale | Replace the flashed string of insulators found on structure 378 of the line. <Duplicate Record> Follow up and instal new control database. |  | Line reclosed at Coffs however was close via SCADA at Armidale. An aerial patrol of the line between structures 360 and 380 has found flashed string of insulators at structure 378 of the line. There is not any significant road crossing near structure 378 | Unknown | Primary Equipment |  |  |  | y |  | 0 | 0 | 2009
1742 | 39641 | Animal/Bird | Animal/Bird | TRUE | Cap |  |  |  | 2009-F-0403 | No.1 Capacitor | Z | 2009Q4 | NEW |  | CAP | 2009-11-13 05:48 | 2009-11-13 12:50 | Magpie shorthed cap. Outage required to remove bird | NIL |  | Magpie shorted cap. Outage required to remove bird. No damage. |  | External |  |  |  | Y |  | 0 | 0 | 2009
1743 | 39710 | Contractor Error | Unknown | TRUE | Prev |  |  |  | 2009-F-0404 | No.3 Transformer 330/132/11kV | Z | 2009Q4 | WG1 |  | TX | 2009-11-16 12:49 | 2009-11-16 13:07 | Transformer RTS @ 1307. Protection to investigate. |  |  | Transformer tripped due to "external trip". No transformer protection operated. Protection Section investigating. Trip due to contrcators working in vicinity of BBP panel. | [5 empty] | y |  | 1 | 1 | 2009 | Protection staff working in the vicinity of the BBP panel, must have incorrectly isolated something.
1744 | 39979 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-E-0048/1 | 8C Armidale - Dumaresq 330kV TL | E | 2009Q4 | AR1, DMQ |  | TL | 2009-11-23 16:34 | 2009-11-23 16:34 |  |  |  | Storms in area. |  | External |  |  |  | y |  | 0 | 0 | 2009
1745 | 40142 | Bushfire | Bushfire | TRUE | TL |  |  |  | 2009-F-0420/1 | 94 Newcastle - Tomago 330 330kV TL | Z | 2009Q4 | NEW, TOM |  | TL | 2009-11-28 15:52 | 2009-11-28 16:10 |  |  |  | Bushfire near Newcastle SS. Weather hot & windy. Shortly after trip Pot lines 1 & 2 tripped at Hydro (200MW). |  | External |  |  |  | y |  | 0 | 0 | 2009
1763 | 42357 | Staff Error | Sec Eqt Malfunction | TRUE | Proc |  |  |  | 2009-F-0489 | 945 Wellington - Molong tee Well'n Town 132kV TL | Z | 2009Q4 | MOL, WL1 |  | TL | 2009-11-30 18:28 | 2009-11-30 21:18 | Staff found cubicle door open and rain water had affected electronic controls. CB returned to service at 21:18hrs 30/11/2009. |  |  | "Staff found cubicle door open and rain water had affected electronic controls. CB returned to service at 21:18hrs 30/11/2009." | [5 empty] | y |  | 0 | 0 | 2009
1746 | 40289 | HV Equipment | Unknown | TRUE | SVC |  |  |  | 2009-F-0428 | No.1 Static Var Compensator | Z | 2009Q4 | KCR |  | SVC | 2009-12-01 19:56 | 2009-12-01 21:15 | SVC trip while topping up cooling system for thyristors. Demineralised water level. Control system sensed low level of demineralised water RTS 21:15hrs est |  |  | SVC trip while topping up cooling system for thyristors. Demineralised water level. Control system sensed low level of demineralised water RTS 21:15hrs est. |  | Secondary Equipment |  |  |  | y |  | 0 | 0 | 2009
1747 | 40631 | Switching error | Sec Eqt Staff Error | TRUE | Prev |  |  |  | 2009-F-0429/1 | 2M Tuggerah - Munmorah 330kV TL | Z | 2009Q4 | MN1, TGH |  | TL | 2009-12-03 07:59 | 2009-12-03 09:20 |  |  |  | Initial investigation of the incident found that during LBU timer modifications to the 330kV Main Bus No.1 BBP panel at Munmorah, inadvertent contact was made to live wing terminals. This resulted in the operation of a CBF initiation into the 2M No.1 prot | [5 empty] | Y |  | 1 | 1 | 2009 | Inadvertent wiring contact resulting from incorrect isolation, causing incorrect operation of protection
1748 | 40784 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0438 | 96T Armidale - Glen Innes 132kV TL | Z | 2009Q4 | AR1, GNS |  | TL | 2009-12-08 15:24 | 2009-12-08 15:24 |  |  |  | The significant road crossings of the line patrolled on the 16th of December 2009 have indicated no evidence of any fault. The incident has been noted for next scheduled patrol of the line. | Thunderstorm | External |  |  |  | y |  | 0 | 0 | 2009
1749 | 40785 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0440 | 96T Armidale - Glen Innes 132kV TL | Z | 2009Q4 | AR1, GNS |  | TL | 2009-12-08 17:38 | 2009-12-08 17:38 |  | The incident has been noted for next scheduled patrol of the line. |  | Storms in area. | Thunderstorm | External |  |  |  | y |  | 0 | 0 | 2009
1750 | 40951 | Contractor Error | Unknown | TRUE | Prev |  |  |  | 2009-F-0448 | No.2 Transformer 330/132/11kV | Z | 2009Q4 | WG1 |  | TX | 2009-12-14 12:58 | 2009-12-15 14:33 |  |  |  | Tx blue phase tapchanger had been overfilled with oil during installation (failed to leave required air cushion) resulting in overpressure switch activation and trip of Tx. Oil level reduced in T/C and Tx RTS. | Fine |  |  |  |  | y |  | 0 | 0 | 2009
1751 | 40961 | Unknown | Unknown | TRUE | TL |  |  |  | 2009-F-0451 | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Z | 2009Q4 | AR1, COF |  | TL | 2009-12-15 03:18 | 2009-12-15 03:18 |  |  |  |  | Very Windy | Unexplained |  |  |  | y |  | 0 | 0 | 2009
1752 | 40976 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0452/1 | 8L Dumaresq - Bulli Creek 330kV TL | Z | 2009Q4 | DMQ |  | TL | 2009-12-15 18:41 | 2009-12-15 18:41 |  |  |  | Single pole (Red) re-close only. |  | External |  |  |  | y |  | 0 | 0 | 2009
1766 | 42385 | Switching error | Sec Eqt Staff Error | TRUE | Prev |  |  |  | 2009-F-0492 | 9W8 Boambee South - Coffs Harbour 132kV TL | Z | 2009Q4 | COF, BOS |  | TL | 2009-12-16 13:53 | 2009-12-16 15:26 | CB 9W82 tripped on temporary protection while CE doing commissioning checks at Boambee South with their No.1 & No.2 Txs energised. Suspect MVAr load exceeded temporary protection settings. Returned o service at 15:26hrs 16/12/2009 |  |  | CB 9W82 tripped on temporary protection while CE doing commissioning checks at Boambee South with their No.1 & No.2 Txs energised. Suspect MVAr load exceeded temporary protection settings. Returned o service at 15:26hrs 16/12/2009 | [5 empty] | y |  | 1 | 0 | 2009 | Temporary protection settings inadequate for MVAr load
1753 | 41077 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0454/1 | 62 Wagga 330 - Jindera 330kV TL | Z | 2009Q4 | JDA, WG1 |  | TL | 2009-12-17 13:54 | 2009-12-17 14:11 |  |  |  | 62 Line RTS at 1410hrs then at 1411hrs TAR. Hot Winds and storms in area, Bushfire under T/L near Jindera. Initial trip then reclosed at Jindera, but tripped again before Wagga could close. |  | External |  |  |  | y |  | 0 | 0 | 2009
2020 | 41138 | Unknown | Lightning or Storm | TRUE | Cont |  |  |  | 2009-F-0462 | 99L Deniliquin - Coleambally 132kV TL | Z | 2009Q4 | CLY, DN2 |  | TL | 2009-12-17 13:54 | 2009-12-19 14:21 | Storms in area at time of trip. Investigation required by Protection staff to determine whether C.B. 99L2 failed to reclose at Coleambally. No visibility of trip in Control Room. No SCADA alarm from Deniliquin and no alarms from Coleambally via dial up Fr | No further action required. |  | Storms in area at time of trip. Investigation required by Protection staff to determine whether C.B. 99L2 failed to reclose at Coleambally. No visibility of trip in Control Room. No SCADA alarm from Deniliquin and no alarms from Coleambally via dial up at | Thunderstorm |  |  |  |  | y |  | 0 | 0 | 2009
2021 | 41138 | Secondary Equipment | Lightning or Storm | TRUE | AC/DC |  |  |  | 2009-F-0462 | 99L Deniliquin - Coleambally 132kV TL | Z | 2009Q4 | CLY, DN2 |  | TL | 2009-12-17 13:54 | 2009-12-19 14:21 | Storms in area at time of trip. Investigation required by Protection staff to determine whether C.B. 99L2 failed to reclose at Coleambally. No visibility of trip in Control Room. No SCADA alarm from Deniliquin and no alarms from Coleambally via dial up Fr | No further action required. |  | Country Energy AC Charger found Failed and DC Supplies depleted. No1 Tx CB4412 Opened manually. Supply made available via No.2 TX. 99T Opened via SCADA at Darlington Point to allow manual closing of CB's at Coleambally. @ 0852 hrs. Supervisory and AC/DC | Thunderstorm | Secondary Equipment |  |  |  | y |  | 0 | 0 | 2009
1758 | 41138 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0462 | 99L Deniliquin - Coleambally 132kV TL | Z | 2009Q4 | CLY, DN2 |  | TL | 2009-12-17 13:54 | 2009-12-19 14:21 | Storms in area at time of trip. Investigation required by Protection staff to determine whether C.B. 99L2 failed to reclose at Coleambally. No visibility of trip in Control Room. No SCADA alarm from Deniliquin and no alarms from Coleambally via dial up Fr | No further action required. |  | Storms in area at time of trip. Investigation required by Protection staff to determine whether C.B. 99L2 failed to reclose at Coleambally. No visibility of trip in Control Room. No SCADA alarm from Deniliquin and no alarms from Coleambally via dial up at | Thunderstorm |  |  |  |  | y |  | 0 | 0 | 2009
1754 | 41080 | Bushfire | Bushfire | TRUE | TL |  |  |  | 2009-F-0455 | 996 Wagga 330 - ANM 132kV TL | Z | 2009Q4 | ANM, WG1 |  | TL | 2009-12-17 14:40 | 2009-12-17 15:11 | Bushfires in Vicinity. | No further action is required. |  | Bushfires in Vicinity. |  | External |  |  |  | y |  | 0 | 0 | 2009
1755 | 41081 | HV Equipment | HV Equipment Failure | TRUE | TL |  |  |  | 2009-F-0456 | 996 Wagga 330 - ANM 132kV TL | Z | 2009Q4 | ANM, WG1 |  | TL | 2009-12-17 17:07 | 2009-12-18 16:40 | Attempted reclose from Wagga 330 via SCADA to proove Line failed @1755hrs. Conductors down at str 350.. Repaired T/L RTS 1640hrs 18/12/09 | No further action required. |  | Storms in area at time of trip. Investigation required by Protection staff to determine whether C.B. 99L2 failed to reclose at Coleambally. No visibility of trip in Control Room. No SCADA alarm from Deniliquin and no alarms from Coleambally via dial up at | [5 empty] | y |  | 0 | 0 | 2009
1756 | 41083 | Secondary Equipment | Sec Eqt Malfunction | TRUE | SVC |  |  |  | 2009-F-0458 | No.1 Static VAR Compensator | Z | 2009Q4 | AR1 |  | SVC | 2009-12-17 17:10 | 2009-12-17 18:23 | 662 Walcha TAR during thunderstorm at 1709 hrs. Suspect voltage fluctuation caused SVC cooling aux equipment to fail & hence trip the SVC. | The suspect relays F301/1 and F301/2 in the Auxillary Supply Control Circuits will be replaced if found faulty. |  | 662 Walcha TAR during thunderstorm at 1709 hrs. Suspect voltage fluctuation caused SVC cooling aux equipment to fail & hence trip the SVC. SVC at Armidale Substation tipped due to loss of 415V Auxiliary Supply. Protection flagging indicated operation of F |  | Secondary Equipment |  |  |  | y |  | 0 | 0 | 2009
1757 | 41135 | Unknown | Unknown | TRUE | CB SF6 |  |  |  | 2009-F-0460 | 83 Muswellbrook CB 832 | Q | 2009Q4 | LD1 |  | CB | 2009-12-19 10:42 | 2009-12-19 12:45 | CB tripped for unknown reason. Nil protection operations. RTS at 1245hrs EST. | 1. Monitor the performance of CB832 for any further trips. 2. Make contact with the Macquarie Generation staff who were involved in the previous investigations and request a review of this incident. |  | CB tripped for unknown reason. Nil protection operations. RTS at 1245hrs EST. Has been investigated and no fault found. As a result of the investigations and monitoring in 2005, it was concluded that the trips on CB832 were likely to have been caused by d | Fine | Unexplained |  |  |  | Y |  | 0 | 0 | 2009
1765 | 42383 | Switching error | Sec Eqt Malfunction | TRUE | Prev |  |  |  | 2009-F-0491/1 | 99A Uranquinty - Finley 132kV TL | C | 2009Q4 | FNY, URQ |  | TL | 2009-12-19 12:31 | 2009-12-19 12:35 |  |  |  | T/L 99A was opened at Finley for a planned outage. All supply at Finley and Deniliquin S/S's was interrupted (20MW). All supply restored at 12:35hrs when 99A was closed at Finley. It was expected that supply to Deniliquin and Finley would remain on-load f | [5 empty] | Y |  | 0 | 1 | 2009 | QAPR report indicates incorrect switching
1987 | 8205 | Animal/Bird | Unknown | TRUE | SVC |  |  |  | 2012-F-0239 | No.1 Static Var Compensator | Z | 2009Q4 | KCR |  | SVC | 2009-12-21 15:47 | 2013-01-01 |  |  |  | Advised dead crow in 16kV area and was removed. There was no Protection LED indication for Trip only PLC printout indicating E\F trip high level. Receive clearance from OCE to place in-service. SVC1 tripped on closing and indicated No.1 & 2 Negative Phas |  | External |  |  |  | y |  | 0 | 0 | 2009
1759 | 41247 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CT |  |  |  | 2009-E-0049 | No.2 Generator Transformer CB 5222 | Q | 2009Q4 | BAY |  | CB | 2009-12-23 14:06 | 2009-12-23 15:25 | Low SF6 CB 5222 CT |  |  | Low SF6 CB 5222 CT. Damaged by Bayswater CT failure. Leak through fibreglass. Replacement being planned. |  | Primary Equipment |  |  |  | y |  | 0 | 0 | 2009
1761 | 41265 | Unknown | Unknown | TRUE | SVC |  |  |  | 2009-F-0479/1 | No.1 Static VAR Compensator | Z | 2009Q4 | BKH |  | SVC | 2009-12-27 10:17 | 2009-12-30 09:03 |  |  |  | No.1 SVC tripped at the same time that 42 Railway Town Feeder Tripped. see FEOR 2009-F-0478/1. Protection unable to reset. SVC isolated on bus Isolator till Transgrid staff can investigate. |  | Unexplained |  |  |  | y |  | 0 | 0 | 2009
1762 | 41272 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2009-F-0485 | 9U3 Gunnedah - Narrabri 132kV TL | Z | 2009Q4 | GN2, NB2 |  | TL | 2009-12-28 01:57 | 2009-12-28 01:57 | Severe storms at time of tripping |  |  | Severe storms at time of tripping |  | External |  |  |  | y |  | 0 | 0 | 2009
1333 | 41731 | Lightning/Storm | Unknown | TRUE | TL |  |  |  | 2010-F-0003 | 9U3 Gunnedah - Narrabri 132kV TL | Z | 2010Q1 | GN2, NB2 |  | TL | 2010-01-03 15:08 | 2010-01-04 12:32 | Lightning and rain at time of tripping. Reported from Country Energy of lightning strike near CE equipment @ Boggabri. CE staff also looked at TG's 132kV line , however unable to see any fault. | Replace the failed crossarm at Structure 616 of the line. |  | Lightning and rain at time of tripping. Reported from Country Energy of lightning strike near CE equipment @ Boggabri. CE staff also looked at TG's 132kV line , however unable to see any fault.. Mains Staff attended but were unable to gain access to all a | [7 empty] | 0 | 0 | 2010
1539 | 41918 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2010-E-0002/1 | 9W1 Lismore 330 - Lismore 132 132kV TL | P | 2010Q1 | LSM |  | TL | 2010-01-10 14:20 | 2010-01-10 14:52 | Taked o/s to top up CB SF6 |  |  | Taken O/S to top up CB SF6. Awaiting use of SF6 camera to locate the source of leaks | [7 empty] | 0 | 0 | 2010
1538 | 93491 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2010-E-0001/1 | 9U9 Lismore 132 CB 9U92 | Q | 2010Q1 | LSM |  | CB | 2010-01-10 14:30 | 2010-01-10 15:19 |  |  |  | Taken O/S to top up CB SF6. Awaiting use of SF6 camera to locate the source of leaks | [7 empty] | 0 | 0 | 2010
2247 | 93492 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | not available | 9W1 Lismore 132 CB 9W12 | Q | 2010Q1 | LSM |  | CB | 2010-01-10 15:20 | 2010-01-10 15:52 |  |  |  | Topped up SF 6 | [7 empty] | 0 | 0 | 2010
1334 | 42121 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0026/1 | 21 Sydney North - Tuggerah 330kV TL | Z | 2010Q1 | SYN, TGH |  | TL | 2010-01-13 23:24 | 2010-01-13 23:24 |  |  |  | No visible damage. | [7 empty] | 0 | 0 | 2010
1335 | 42176 | Relay | LV/MECH/PROT Equipment Fail | TRUE | Prot |  |  |  | 2010-F-0033 | 94C Wallerawang 132 (New) - Oberon 132kV Line | Q | 2010Q1 | WWS |  | TL | 2010-01-14 19:04 | 2010-01-14 23:44 | SO/CE advises no 132kV protection operated at Oberon, however tripped into 11kV Cb's feeding CSR & Carter Holt Harvey industries, an attempt to close CB 94C2 upon CE request caused CB 94C2 at Wang to trip, while CE were patrolling 94C at Oberon end, it b |  |  | At 19:29hrs Country Energy requested an attempt to close of 94C at Wallerawang. Tripped on closing. Country Energy will patrol the line. Staff called out to Wallerawang advised No.2 protection relay at Wallerawang will not reset, appears to be faulty. At | Thunderstorm | [6 empty] | 1 | 0 | 2010 | Faulty relay
1336 | 42212 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0036 | 2 Upper Tumut - Yass 330kV TL | Z | 2010Q1 | UT1, YSN |  | TL | 2010-01-16 13:58 | 2010-01-16 13:58 |  |  |  | Storms in vicinity at time of trip. The ground patrol was not carried out on this occasion. | [7 empty] | 0 | 0 | 2010
1338 | 42226 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0043 | 94U Parkes - Forbes 132kV TL | Z | 2010Q1 | FB2, PKS |  | TL | 2010-01-16 17:20 | 2010-01-16 17:20 | Protection details from Parkes SS added | The incident has been noted for the next scheduled patrol of the line. |  | Indji system was interrogated and found that the lightning stroke 1.8km from structure 131 was the closest stroke at time of the trip that was within Zone 1 of the protection that operated. No significant road crossings in the section of line that was aff | [7 empty] | 0 | 0 | 2010
1337 | 42216 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0038/1 | 22 Sydney North - Vales Point 330kV TL | Z | 2010Q1 | SYN, VP1 |  | TL | 2010-01-17 12:54 | 2010-01-17 12:54 |  |  |  | Indji system placed lightning strike in Jilliby State Conservation Area. There are crossing of significant roads by the line in this area. The locations of the fault has been noted for checking as part of the scheduled patrol. | [7 empty] | 0 | 0 | 2010
1339 | 42387 | Staff Error | HV Equipment Failure | TRUE | Prev |  |  |  | Not available | No.3 Transformer 330/132/11kV | E | 2010Q1 | WG1 |  | TX | 2010-01-21 14:56 | 2010-01-21 16:13 |  |  |  | 12:40 Projects have advised a bushing DLA point is open circuit, the transformer is required out to investigate and repair. Switching competed 1247 hrs. |  | Primary Equipment | [5 empty] | 0 | 0 | 2010
2234 | 42498 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0049/1 | 81 Newcastle - Liddell 330kV TL | Z | 2010Q1 | LD1, NEW |  | TL | 2010-01-27 18:18 | 2010-01-27 21:52 |  |  |  | T/L tripped at Newcastle and Liddell, reclosed at Newcastle but at Liddell indicated an attempted close on CB 812 and then a trip. An attempt to close the Bus coupler CB 5012 at Liddell failed. T/L was de-energised. Storms in the area. At 21:52hrs protect | [7 empty] | 0 | 0 | 2010
1340 | 42498 | Relay | Lightning or Storm | TRUE | Prot |  |  |  | 2010-F-0049/1 | 81 Newcastle - Liddell 330kV TL | Z | 2010Q1 | LD1, NEW |  | TL | 2010-01-27 18:18 | 2010-01-27 21:52 |  |  |  | T/L tripped at Newcastle and Liddell, reclosed at Newcastle but at Liddell indicated an attempted close on CB 812 and then a trip. An attempt to close the Bus coupler CB 5012 at Liddell failed. T/L was de-energised. Storms in the area. At 21:52hrs protect |  | External | [5 empty] | 1 | 0 | 2010 | QAPR report indicates faulty relay
2236 | 42550 | Secondary Equipment | Lightning or Storm | TRUE | Cont |  |  |  | 2010-F-0058/1 | 94B Beryl - Wellington 132kV TL | Z | 2010Q1 | BER, WL1 |  | TL | 2010-01-28 14:15 | 2010-01-28 14:17 | Line reclosed at Wellington OK however line failed to reclose at Beryl. CB 94B2 closed by SCADA at Beryl | The incident has been noted for next scheduled patrol of the line |  | "T/L tripped at Wellington and Beryl then reclosed at Wellington end only. Feeder was placed on load via SCADA at 14:17hrs. 4MW of load lost on voltage dip as a result of this trip. Storm in area. Closest strike is 388m from structure #200 where 94B cross | [7 empty] | 0 | 0 | 2010
1342 | 42550 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0058 | 94B Beryl - Wellington 132kV TL | Z | 2010Q1 | BER, WL1 |  | TL | 2010-01-28 14:15 | 2010-01-28 14:17 | Line reclosed at Wellington OK however line failed to reclose at Beryl. CB 94B2 closed by SCADA at Beryl | The incident has been noted for next scheduled patrol of the line |  | "T/L tripped at Wellington and Beryl then reclosed at Wellington end only. Feeder was placed on load via SCADA at 14:17hrs. 4MW of load lost on voltage dip as a result of this trip. Storm in area. Closest strike is 388m from structure #200 where 94B cross |  | External | [5 empty] | 0 | 0 | 2010
1343 | 42561 | Relay | Non TransGrid Reason | TRUE | Cont |  |  |  | 2010-F-0066 | 940 Wallerawang 132 (NEW) - Warimoo tee North Katoomba 132kV Line | S | 2010Q1 | WWS |  | TL | 2010-01-28 15:30 | 2010-01-29 13:38 | Line did not reclose at Wallerawang 132 SS (see assoc irreg) |  |  | Line did not reclose at Wallerawang 132 SS (see assoc irreg). Investigating trip and no reclose on 940 last night causing loss of supply at Warrimoo ( 11 MW for 1 Hr 12 mins ), interrogating relay, trip sequence was - CB 9402 trip, initiated MTM , A/R sta | [7 empty] | 0 | 0 | 2010 | Auto reclose failure is a control system failure, not protection
1341 | 42516 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0052 | 96L Lismore 330 - Tenterfield tee Casino 132kV TL | Z | 2010Q1 | LSM, TTF |  | TL | 2010-01-28 20:05 | 2010-01-28 20:05 | Unable to determine if line tripped @ Tenterfield. Will need on site staff to verify. Severe storms at time of tripping | The location of the fault has been noted for inclusion in the next scheduled patrol. |  | The location of the fault has been noted for inclusion in the next scheduled patrol. Unable to determine if line tripped @ Tenterfield. Will need on site staff to verify. Severe storms at time of tripping. The structures on either side of the Summerland W |  | External | [5 empty] | 0 | 0 | 2010
1344 | 42595 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0074 | 84 Liddell - Tamworth 330 330kV TL | Z | 2010Q1 | LD1, TA1 |  | TL | 2010-01-29 15:07 | 2010-01-29 15:07 |  |  |  | Distance to fault placed this incidcnt in the vi cinity of Structure 230. There are no crossings of significant roads in the vicinity of this structure. The location has been noted for checking as part of the next scheduled patrol. | Thunderstorm | External | [5 empty] | 0 | 0 | 2010
1345 | 42596 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0075 | 86 Tamworth 330 - Armidale 330kV TL | Z | 2010Q1 | AR1, TA1 |  | TL | 2010-01-29 15:10 | 2010-01-29 15:10 |  |  |  | Distance to fault placed this incident in approximately 11.5km from Tamworth 330kV SS. There are no crossings of any roads of significance in this area. The locations of the fault has been noted for checking as part of the next scheduled patrol. | Thunderstorm | External | [5 empty] | 0 | 0 | 2010
1346 | 42637 | Secondary Equipment | Non TransGrid Reason | TRUE | Cont |  |  |  | 2010-F-0079 | No.1 Balranald - Balranald 22kV Line | S | 2010Q1 | BRD |  | TL | 2010-02-01 20:42 | 2010-02-01 22:02 | Feeder did not reclose as per SCADA. Line patrolled by C.E Staff and requested by C.E to place in service at 2203hrs EST. |  |  | Feeder did not reclose as per SCADA. Line patrolled by C.E Staff and requested by C.E to place in service at 2203hrs EST. Investigation and A/R testing planned for 8th & 9th Feb | [7 empty] | 0 | 0 | 2010
1347 | 43239 | HV Equipment | Sec Eqt Malfunction | TRUE | CB SF6 |  |  |  | 2010-F-0080/1 | No.2 Tie Transformer 330kV CB 5422 |  | 2010Q1 | MTP |  | CB | 2010-02-03 13:44 | 2010-02-03 14:44 | Oil P/P's switched to manual, started to run & tripped tx | Risk of tripping transformer when more then two pumps operated simultaneously. ¦ ITEM ¦ Plant branch to advise. |  | Oil P/P's switched to manual, started to run & tripped Tx. Caused by switching from auto to manual mode on cooling. Causes all selected pumps to turn on. Interim procedure adopted to avoid this issue and modification of the control operation is being co |  | Secondary Equipment | [5 empty] | 0 | 0 | 2010
1348 | 43342 | Unknown | Unknown | TRUE | TL |  |  |  | 2010-F-0091 | 969 Tamworth 330 - Gunnedah 132kV TL | Z | 2010Q1 | GN2, TA1 |  | TL | 2010-02-06 05:30 | 2010-02-06 05:30 | 969T/L TAR during switching. TAR approx 60 secs after being off-loaded at Gunnedah but before 969 was de-energised at Tamworth. Line was isolated and earthed for planned switching. Line patrolled from structure 205 all the way to Gunnedah and no fault fou |  |  | 969T/L TAR during switching. TAR approx 60 secs after being off-loaded at Gunnedah but before 969 was de-energised at Tamworth. Line was isolated and earthed for planned switching. Line patrolled from structure 205 all the way to Gunnedah and no fault fou | [7 empty] | 0 | 0 | 2010
1362 | 45260 | Unknown | Backup Operation | TRUE | TL |  |  |  | 2010-F-0136 | 993 Wagga 330 - Gadara 132kV TL | Z | 2010Q1 | GAD, WG1 |  | TL | 2010-02-07 16:49 | 2010-02-07 18:38 | CB 9932 opened at Wagga 330 from Yass LOLS. CB closed via Scada at 1838hrs EST. |  |  | CB 9932 opened at Wagga 330 from Yass LOLS. CB closed via Scada at 1838hrs EST. There were high transfers south at the time. | Fine | [6 empty] | 0 | 0 | 2010
1349 | 43570 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0102 | 2 Upper Tumut - Yass 330kV TL | Z | 2010Q1 | UT1, YSN |  | TL | 2010-02-10 12:45 | 2010-02-10 12:45 |  |  |  | T/L tripped and auto reclosed. Storms in the area. The protection at Yass SS indicated that a phase to earth fault occurred at approximately 19.1km and 19.03 km from Yass SS, which corresponds to an area between structures 65 and 70. A visual inspection |  | External | [5 empty] | 0 | 0 | 2010
1354 | 43831 | Unknown | Unknown | TRUE | TL |  |  |  | 2010-F-0120 | No.4 Transformer 132/66KV | Z | 2010Q1 | ORG |  | TX | 2010-02-11 13:00 | 2010-02-11 14:58 | The LED is BBP CBF start but it is really BBP CBF trip. |  |  | The LED is BBP CBF start but it is really BBP CBF trip. | Fine | Unexplained | [5 empty] | 0 | 0 | 2010 | Unknown reason for trip, no further info in QAPR report, THEOS, or Opslog
1350 | 43611 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0109/1 | 72 Mt Piper - Wellington 330kV TL | Z | 2010Q1 | MTP, WL1 |  | TL | 2010-02-11 14:53 | 2010-02-11 14:54 |  |  |  | Manual close of CB 722A @ Wellington (A/R N/A at site) at 1454 hrs EST. Manual close of CB 5022 @ Mt Piper (as designed). Storms in area at time of trip. |  | External | [5 empty] | 0 | 0 | 2010
2235 | 43710 | Secondary Equipment | HV Equipment Failure | TRUE | Cont |  |  |  | 2010-E-0004/2 | 21 Sydney North 330kV B CB 212B | Q | 2010Q1 | TGH |  | CB | 2010-02-12 07:15 | 2010-02-12 11:32 | SF6 top up. |  |  | On the completion of SF6 top-up CB 212B failed to close via SCADA and local MITS but was able to be closed via CDS. Control issue also. | Fine | [6 empty] | 0 | 0 | 2010
1352 | 43710 | HV Equipment | HV Equipment Failure | TRUE | CB |  |  |  | 2010-F-0138 | 21 Sydney North 330kV B CB 212B | Q | 2010Q1 | TGH |  | CB | 2010-02-12 07:15 | 2010-02-12 11:32 | SF6 top up. |  |  | On the completion of SF6 top-up CB 212B failed to close via SCADA and local MITS but was able to be closed via CDS. Control issue also. | Fine | Oil/Gas Levels | [5 empty] | 0 | 0 | 2010
1351 | 43703 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0111/1 | 66 Murray - Lower Tumut 330kV TL | Z | 2010Q1 | LT1, MUR |  | TL | 2010-02-12 12:36 | 2010-02-12 12:37 |  |  |  | Tripped and Reclosed on CB 662B at MUR & LTSS. Mannual close back CB 662A at MUR & LTSS. |  | External | [5 empty] | 0 | 0 | 2010
1355 | 43927 | Secondary Equipment | Sec Eqt Malfunction | TRUE | Sec |  |  | lodt load 1.5MW | 2010-F-0123 | No.1 Transformer 220/22kV | C | 2010Q1 | BRD |  | TX | 2010-02-19 05:16 | 2010-02-19 10:50 | CB 2412 Tripped 0516hrs EST, CB 7412 Tripped 0620hrs EST. Load restored by County Energy 0751hrs EST. No.1 Trans RTS 1708hrs EST after inservice checks completed. (see Short Notice THEOS outage ID 45680) |  |  | CB 2412 Tripped 0516hrs EST, CB 7412 Tripped 0620hrs EST. Load restored by County Energy 0751hrs EST. No.1 Trans RTS 1708hrs EST after inservice checks completed. (see Short Notice THEOS outage ID 45680) | Fine | Secondary Equipment | [5 empty] | 1 | 0 | 2010 | QAPR report indicates faulty protection
1363 | 45262 | Unknown | Unknown | TRUE | Other |  |  |  | 2010-F-0139/1 | No.4 Generator Transformer Generator Bus 500kV CB 6242G | Q | 2010Q1 | BAY |  | CB | 2010-02-19 08:12 | 2010-02-19 12:45 |  |  |  | At 08:09hrs Bayswater No 4 Generator CB’s 6242M and 6242G tripped. Investigations were carried out. At 12:45hrs CB6242M and CB6242G were closed in preparation for No 4 Generator to be returned to service. This is a protection issue and is the subject of | [7 empty] | 1 | 0 | 2010 | QAPR report indicates faulty protection
1356 | 43952 | Unknown | Unknown | TRUE | TL |  |  |  | 2010-F-0124 | 976/1 Canberra - Queanbeyan/Spring Flat 132kV TL | Z | 2010Q1 | QBN |  | TL | 2010-02-22 07:41 | 2010-02-22 07:42 | Tripped and reclosed at Canberra, No protection flags at Queanbyan |  |  | Tripped and reclosed at Canberra, No protection flags at Queanbyan | [7 empty] | 0 | 0 | 2010
1509 | 61991 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2010-E-0032 | 22 SYDNEY NORTH 330KV GEN BUS CB 222G | Q | 2010Q1 | VP1 |  | CB | 2010-02-24 13:35 | 2010-02-24 15:44 | SF6 Top UP |  |  | SF6 Top UP | Unknown | [6 empty] | 0 | 0 | 2010
1357 | 44194 | Relay | Unknown | TRUE | Prot |  |  | Lost Load 1.5MW | 2010-F-0129 | 22kV Bus | Q | 2010Q1 | BRD |  | BB | 2010-02-27 22:57 | 2010-02-28 00:31 |  |  |  | Advised by J Parker that the BBP trip on 27-2-2010 was initiated from No.1 Protection (p142) on spare bay CB32. Initiated CB fail CB32 to BBP which tripped the 22kV Bus. Local relay screen is out of service ( no display) but healthy light was still on, th | [7 empty] | 1 | 0 | 2010 | QAPR report indicates faulty protection
1359 | 44205 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0131/2 | 26 Munmorah - Sydney West 330kV TL | Z | 2010Q1 | MN1, SYW |  | TL | 2010-02-28 16:13 | 2010-02-28 16:13 |  |  |  | Lightning and storm in vicinity | [7 empty] | 0 | 0 | 2010
1360 | 44228 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2010-E-0003 | 5A2 Kemps Creek 500kV CB 5A22 | Q | 2010Q1 | ER0 | o | CB | 2010-03-01 18:50 | 2010-03-01 20:33 | CB RTS after SF6 top up @ 2033 EST. |  |  | CB RTS after SF6 top up @ 2033 EST. Taken O/S to top up CB SF6. Leak located as B Ph line side density monitor o ring. Repair to be scheduled. | Rain | Oil/Gas Levels | [5 empty] | 0 | 0 | 2010
1361 | 45257 | HV Equipment | HV Equipment Failure | TRUE | Other |  |  |  | 2010-F-0135 | 822 Deniliquin - Moulamein tee Deniliquin 66kV SS 66kV Line | S | 2010Q1 | DN2 |  | TL | 2010-03-05 09:26 | 2010-03-05 18:21 | Landing span Blue phase dropper to CT/VT broken at clamp on Landing Span. Load restored via CE system 1027hrs EST. 822 TL RTS 1821hrs EST after repairs. |  |  | Landing span Blue phase dropper to CT/VT broken at clamp on Landing Span. Load restored via CE system 1027hrs EST. 822 TL RTS 1821hrs EST after repairs. Report has been prepared by Southern Region. Caused by corrosion involving dissimilar metals (alumini | [7 empty] | 0 | 0 | 2010
1364 | 45298 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB |  |  |  | 2010-E-0004 | 21 Sydney North 330kV B CB 212B | Q | 2010Q1 | TGH |  | CB | 2010-03-07 07:32 | 2010-03-07 10:10 | low sf6 gas. topped up by on site ssmf | Follow up with AREVA for the repairs of the Circuit Breaker. |  | Low SF6 gas. topped up by on site ssmf. AREVA model GL315. The location of the gas leak is suspected to be the fill point on the white phase of the Circuit Breaker. The Circuit Breaker is still under Warranty period. AREVA the manufacture of the Circuit B | [7 empty] | 0 | 0 | 2010
1366 | 45321 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0144 | 9R3 Finley - Deniliquin 132kV TL | Z | 2010Q1 | DN2, FNY |  | TL | 2010-03-07 14:17 | 2010-03-08 14:03 |  | No further action required. |  | T/L tripped, reclosed, tripped & locked out. Storms in the area. Nil interruption. Subsequent patrol of line reveal that two poles are tilted. Staff were called out and during their patrol of the 9R3 line, structure 161 was observed to be leaning. The str | Thunderstorm | [6 empty] | 0 | 0 | 2010
1365 | 45317 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0142 | 99L Deniliquin - Coleambally 132kV TL | Z | 2010Q1 | CLY, DN2 |  | TL | 2010-03-07 14:36 | 2010-03-07 14:36 | Storm in vicinity at time of fault | No further action is required. |  | Storm in vicinity at time of fault. T/L tripped and reclosed. The ground patrol was not carried out at this occasion. | Thunderstorm | [6 empty] | 0 | 0 | 2010
1367 | 45359 | Secondary Equipment | Sec Eqt Malfunction | TRUE | Sec |  |  |  | 2010-F-0147 | U7 Upper Tumut - Tumut 2 330kV TL | Z | 2010Q1 | UT1 |  | TL | 2010-03-09 11:57 | 2010-03-09 15:40 | Unit 7 inservice at time of trip. No.2 prot Intertrip receive relays and & Pilot changed. Cause of trip not determined. RTS time 1540hrs EST. |  |  | Unit 7 inservice at time of trip. No.2 prot Intertrip receive relays and & Pilot changed. Cause of trip not determined. RTS time 1540hrs EST. | Fine | [6 empty] | 1 | 0 | 2010 | Opslog implies protection faulty, excerpt: "16:04 hrs Prot repaired"
1379 | 47502 | Unknown | Unknown | TRUE | Cap |  |  |  | 2010-F-0182 | No.1 Capacitor | Q | 2010Q1 | BKH |  | CAP | 2010-03-25 14:05 | 2010-04-15 13:02 | No.1 Cap CB 2712 closed successfully 1302 hrs on 15/4 |  |  | Protections 1 & 2 neutral unbalance. | Fine | [6 empty] | 0 | 0 | 2010 | Unknown cause of trip, no info to indicate protection fault in QAPR report, THEOS or Opslog
1368 | 46209 | Unknown | Unknown | TRUE | TL |  |  |  | 2010-F-0153 | 970 Yass - Burrinjuck 132kV TL | Z | 2010Q1 | BUK, YSN |  | TL | 2010-03-26 06:27 | 2010-03-26 08:10 | Line failed to reclose at Burrinjuck. Line on load at 0910 hrs. DTF 5.39 km from Yass | Noted for an aerial patrol to be scheduled in September 2010. |  | Line failed to reclose at Burrinjuck. Line on load at 0910 hrs. DTF 5.39 km from Yass. Ground patrol found no issues. | Fine | [6 empty] | 0 | 0 | 2010
2227 | 46209 | Relay | Unknown | TRUE | Cont |  |  |  | 2010-F-0153/1 | 970 Yass - Burrinjuck 132kV TL | Z | 2010Q1 | BUK, YSN |  | TL | 2010-03-26 06:27 | 2010-03-26 08:10 | Line failed to reclose at Burrinjuck. Line on load at 0910 hrs. DTF 5.39 km from Yass | Noted for an aerial patrol to be scheduled in September 2010. |  | Line failed to reclose at Burrinjuck. Line on load at 0910 hrs. DTF 5.39 km from Yass. A ground patrol from Yass to structure 25 did not identify any reason for the fault. | Fine | [6 empty] | 0 | 0 | 2010
1546 | 93537 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2010-E-0034/1 | 9U9 Lismore 132 CB 9U92 | Q | 2010Q1 | LSM |  | CB | 2010-03-26 14:37 | 2010-03-26 15:03 |  |  |  | low SF6 | [7 empty] | 0 | 0 | 2010
1369 | 46234 | HV Equipment | Unknown | TRUE | TL |  |  |  | 2010-F-0154/1 | O1 Upper Tumut - Canberra 330kV TL | Z | 2010Q1 | CA1, UT1 |  | TL | 2010-03-27 18:18 | 2010-03-28 17:34 |  |  |  | White phase conductor on ground. A fault patrol identified a failed mid-span joint that had failed on structure 38. 64 LTSS - UTSS tripped at UTSS end only at the same time as 01. 19 Wind Generators tripped at Capital Wind Farm. White phase conductor on g | [7 empty] | 0 | 0 | 2010
1370 | 46237 | Relay | Unknown | TRUE | Prot |  |  |  | 2010-F-0155 | 64 Lower Tumut - Upper Tumut 330kV TL | Z | 2010Q1 | LT1, UT1 |  | TL | 2010-03-27 18:18 | 2010-03-27 19:15 | CB tripped at the same time as the 01 T/L. RTS via Scada. |  |  | At the same time 64 Upper Tumut to Lower Tumut 330kV T/L opened at Upper Tumut only. Nil interruption, No market impact. 64 T/L was placed on load at 1915hrs. 01 T/L was returned to service at 17:34hrs on Sunday 28/03/10. | Fine | [6 empty] | 1 | 0 | 2010
1371 | 46290 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2010-E-0006 | No.3 Generator 500kV CB 6232 | Q | 2010Q1 | ER0 |  | CB | 2010-03-30 05:28 | 2010-03-30 07:20 | Low SF6 Alarm CB isolated for top up. | NIL |  | Low SF6 Alarm CB isolated for top up. | Fine | [6 empty] | 0 | 0 | 2010
1510 | 62000 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2010-E-0035 | 5A1 Kemps Creek 500kV CB 5A12 | Q | 2010Q1 | ER0 |  | CB | 2010-03-30 16:11 | 2010-03-30 19:10 | Low SF6 |  |  | Low SF6 | Unknown | [6 empty] | 0 | 0 | 2010
1372 | 46314 | Animal/Bird | Animal/Bird | TRUE | TX |  |  |  | 2010-F-0163 | No.1 Transformer 132/66/11kV | Z | 2010Q1 | DN2 |  | TX | 2010-03-30 23:28 | 2010-03-31 02:36 | No.1 & 2 Transformers tripped at Finley 132 at the same time. No load lost at Deniliquin. |  |  | A bird came in contact with HV conductors. No load lost at Deniliquin. No.1 & 2 Transformers tripped at Finley 132 at the same time. No load lost at Deniliquin. | Fine | [6 empty] | 0 | 0 | 2010
1373 | 46315 | Staff Error | Unknown | TRUE | Proc |  |  | Lost Load 3MW | 2010-F-0164 | No.1 Transformer 132/66/11kV | C | 2010Q1 | FNY |  | TX | 2010-03-30 23:28 | 2010-03-31 03:10 | No.1 Transformer tripped at Deniliquin at the same time. No.2 Transformer tripped at Finley at the same time. Note: Load lost due to both Transformers tripping. (Total load 3MW) |  |  | No.1 Transformer tripped at Deniliquin at the same time. No.2 Transformer tripped at Finley at the same time. Note: Load lost due to both Transformers ripping. (Total load 3MW). CT connections reversed. No.2 Transformer tripped at Finley at the same time | Fine | [6 empty] | 1 | 0 | 2010 | Incorrect (reverse) CT connections
1374 | 46316 | Staff Error | Unknown | TRUE | Proc |  |  |  | 2010-F-0165 | No.2 Transformer 132/66/11kV | C | 2010Q1 | FNY |  | TX | 2010-03-30 23:28 | 2010-03-31 03:10 | No.1 Transformer tripped at Deniliquin at the same time. No.1 Transformer tripped at Finley at the same time. Total load lost at Finley recorded on FEOR for No.1 Transformer. |  |  | No.1 Transformer tripped at Deniliquin at the same time. No.2 Transformer tripped at Finley at the same time. Note: Load lost due to both Transformers ripping. (Total load 3MW). CT connections reversed. | Fine | [6 empty] | 1 | 0 | 2010 | Incorrect (reverse) CT connections
1375 | 47051 | HV Equipment | HV Equipment Failure | TRUE | SVC |  |  |  | 2010-F-0170 | No.1 Static VAR Compensator | Z | 2010Q2 | AR1 |  | SVC | 2010-04-03 19:38 | 2010-04-04 19:38 | ssmf attended to replace faulty cans | NIL |  | ssmf attended to replace faulty cans. Three cans on TSCB R-W leg of the SVC were found faulty and replaced. | [7 empty] | 0 | 0 | 2010
1385 | 48539 | Animal/Bird | Animal/Bird | TRUE | SVC |  |  |  | 2010-F-0193 | No.2 Static VAR Compensator | Z | 2010Q2 | BKH |  | SVC | 2010-04-07 06:59 | 2010-04-07 14:19 |  |  |  | A dead fox was found to be the cause of the trip. | [7 empty] | 0 | 0 | 2010
1376 | 47358 | Unknown | Unknown | TRUE | TX |  |  |  | 2010-F-0173 | No.1 Transformer 330/132/16kV | Z | 2010Q2 | SE1 |  | TX | 2010-04-09 19:01 | 2010-04-10 14:13 | No.1 Transformer Tripped . CB5412,CB4412A,CB4412B. on transfer of Auxilaries load from No.1 to No.2 TX in preparation for Outage of No. 1 TX for hot joint repairs. Hot joint repairs completed & TX available for Emergency use @ 2238 HRS. RTS 1413hrs 10/4 | Note for future. ¦ ITEM |  | Transformer tripped , on transfer of Auxiliaries load from No.1 to No.2 TX in preparation for Outage of No. 1 TX for hot joint repairs. Hot joint repairs completed & TX available for Emergency use @ 2238 HRS. RTS 1413hrs 10/4 after passing oil tests. Sus | Fine | [6 empty] | 0 | 0 | 2010
1378 | 47485 | HV Equipment | HV Equipment Failure | TRUE | CT |  |  |  | 2010-F-0180 | No.3 Transformer 132kV A CB 4432A | Q | 2010Q2 | SYW |  | CB | 2010-04-13 16:53 |  | Refer FEOR 2010-F-0174. CB 4432A CT exploded tripping No.3 TX. No.3 TX RTS on 13/4 @ 1652 hrs on CB 4432B only. CT replacement being carried out on CB 4432A CT's. |  |  | Refer FEOR 2010-F-0174. CB 4432A CT exploded tripping No.3 TX. No.3 TX RTS on 13/4 @ 1652 hrs on CB 4432B only. CT replacement being carried out on CB 4432A CT's. | [7 empty] | 0 | 0 | 2010
1540 | 93503 | HV Equipment | Sec Eqt Malfunction | TRUE | CB SF6 |  |  |  | 2010-E-0007/1 | 9U8 Lismore 132 CB9U82 | Q | 2010Q2 | LSM |  | CB | 2010-04-17 15:45 | 2010-04-17 16:36 |  |  |  | Low sf6 gas. Make ‘ABBHPL145’. The circuit breaker is being closely monitored for SF6 gas levels getting low in the past. Action is in hand to arrange the camera required to establish and repair the suspect gas leaks. | [7 empty] | 0 | 0 | 2010
1380 | 47599 | Unknown | Unknown | TRUE | TL |  |  |  | 2010-F-0185 | 969 Tamworth 330 - Gunnedah 132kV TL | Z | 2010Q2 | GN2, TA1 |  | TL | 2010-04-20 05:55 | 2010-04-20 05:55 | Fault recorder operated at Tamworth 330. Distance to fault from Tamworth 330 was 14.89kM | The incident has been noted for next scheduled aerial patrol. |  | No storms in area. Distance to fault from Tamworth 330 was 14.89km. The suspect section of the line between structures 52 and 76 was patrolled and no evidence of the possible cause was found. This is on the newly-constructed double circuit section of the | Fine | [6 empty] | 0 | 0 | 2010
1381 | 47777 | Design Ommission | Sec Eqt Staff Error | TRUE | Proc |  |  |  | 2010-F-0186 | No.1 Main Transformer 330/132/11kV | Z | 2010Q2 | WW2, WW1 |  | TX | 2010-04-22 14:47 | 2010-04-22 16:22 |  |  |  | During work by Wallerawang PS on the electrically not connected No 1A Tx a trip was sent to the in-service No 1 main Tx. Investigation shows that the wiring isolation was in accordance with the PMWI a fitter wired between the Tx panel and the power statio | [7 empty] | 1 | 1 | 2010 | QAPR report indicates incorrect isolation leading to incorrect protection operation
1511 | 62001 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2010-E-0036 | 96L Lismore 330 - Tenterfield tee Casino 132kV TL | E | 2010Q2 | LSM, TTF |  | TL | 2010-04-23 13:46 | 2010-04-23 14:36 | Low SF6 |  |  | low SF6 | Unknown | [6 empty] | 0 | 0 | 2010
1512 | 62003 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2010-E-0037 | No.2 Transformer 132/33/11kV | E | 2010Q2 | KS2 |  | TX | 2010-04-27 04:56 | 2010-04-27 06:09 |  |  |  | Low SF6 | [7 empty] | 0 | 0 | 2010
1382 | 48536 | Unknown | Unknown | TRUE | Prev |  |  |  | 2010-F-0190 | 18 Dapto - Kangaroo Valley 330kV TL | Z | 2010Q2 | DPT, KVS |  | TL | 2010-05-02 15:08 | 2010-05-02 15:11 | CB 182 tripped at 1508hrs 2/5/10. Staff where restoring control supplied to replacment CB 192 at KVSS about the time of the trip. CB 182 cliosed via Scada 1511hrs |  |  | CB 182 tripped at 1508hrs 2/5/10. Staff were restoring control supplied to replacement CB 192 at KVSS about the time of the trip. CB 182 closed via Scada 1511hrs | Fine | [6 empty] | 0 | 0 | 2010
1383 | 48537 | Unknown | Unknown | TRUE | Prev |  |  |  | 2010-F-0191 | 18 Dapto - Kangaroo Valley 330kV TL | Z | 2010Q2 | DPT, KVS |  | TL | 2010-05-02 15:56 | 2010-05-02 15:58 | Second trip on CB 182. No obvious cause found for trip. CB closed 1558hrs via Scada. Elcon Test Box removed from CB 182. Refer FEOR 190 for previous trip. |  |  | Second trip on CB 182. No obvious cause found for trip. CB closed 1558hrs via Scada. Elcon Test Box removed from CB 182. Refer FEOR 190 for previous trip. | Fine | [6 empty] | 0 | 0 | 2010
1384 | 48538 | Unknown | Unknown | TRUE | Prev |  |  |  | 2010-F-0192 | 18 Dapto - Kangaroo Valley 330kV TL | Z | 2010Q2 | DPT, KVS |  | TL | 2010-05-02 16:54 | 2010-05-02 16:57 | Cause of trip not determined. Trip occured when re-establishing isolation on CB 192. CB 182 closed via scada 1657hrs. Refer previous FEORs 190 & 191. |  |  | Cause of trip not determined. Trip occurred when re-establishing isolation on CB 192. CB 182 closed via scad 1657hrs. Refer previous FEORs 190 & 191. | Fine | [6 empty] | 0 | 0 | 2010
1386 | 48872 | HV Equipment | HV Equipment Failure | TRUE | Cap |  |  |  | 2010-F-0200 | No.2 Capacitor | Z | 2010Q2 | GN2 |  | CAP | 2010-05-03 21:50 | 2010-05-07 10:27 |  | NIL |  | Advises Cap tripped due to protection operation. Faulty can replaced. | Fine | [6 empty] | 0 | 0 | 2010
1387 | 48890 | Contractor Error | Human Interference | TRUE | Prev |  |  |  | 2010-F-0201 | 96P Taree - Stroud 132kV TL | Z | 2010Q2 | TRE |  | TL | 2010-05-10 13:32 | 2010-05-10 13:32 |  | NIL |  | The trip and auto-reclose on the line occurred as a result of a wind guy on structure 505 of the line struck by a small mulcher operated by Savco (Contractor working in the area at the time of the trip and reported the incident). The guy wire was temporar | Fine | [6 empty] | 0 | 0 | 2010
1388 | 48920 | HV Equipment | HV Equipment Failure | TRUE | Other |  |  |  | 2010-F-0202 | 81H Panorama - Stewart 66kV Line | Q | 2010Q2 | PMA |  | TL | 2010-05-11 08:54 | 2010-05-12 17:59 | Overhead earth wire failed on landing span within TG switchyard. CE advised no load interruption. Supply auto change over to 81G feeder |  |  | "Overhead earth wire failed on landing span within TG switchyard. CE advised no load interruption. Supply auto change over to 81G feeder" | [7 empty] | 0 | 0 | 2010
1392 | 48938 | Design Ommission | Unknown | TRUE | AC/DC |  |  |  | 2010-F-0203 | 711 Coffs Harbour - North Coffs Harbour 66kV Line | S | 2010Q2 | COF |  | TL | 2010-05-12 06:49 | 2010-05-12 07:04 | Load-shed initiated when staff were replacing No2 110V battery charger fuses. | The load shed system was designed when there were only two 132kV supplies to Coffs Harbour which now has effectively five supplies. A review of the need and/or inputs to the system will be carried out. |  | Load-shed initiated when staff were replacing No2 110V battery charger fuses. Investigations by staff at site determined that the load shed system had operated incorrectly. Investigations carried out by Technical Services staff found that the No.2 battery | Fine | [6 empty] | 0 | 0 | 2010 | Incorrect load shedding operation, not protection operation
1393 | 49011 | HV Equipment | Sec Eqt Malfunction | TRUE | CB |  |  |  | 2010-E-0008 | 83 LIDDELL 330kV A CB 832A | Q | 2010Q2 | MRK |  | CB | 2010-05-13 07:40 | 2010-05-13 09:33 | HV CB abnormal alarm received. Staff at Muswellbrook confirmed that CB 832A had a low SF6 alarm. | Repair the gas leaks. |  | HV CB abnormal alarm received. Staff at Muswellbrook confirmed that CB 832A had a low SF6 alarm. Make ‘M&G FA2’ (Contract No C2794/1). The CB has a minor leak from the blue phase SF6 Monitor. An outage to replace the leaking monitor has been planned. | Very Cold | [6 empty] | 0 | 0 | 2010
1394 | 49182 | Unknown | Unknown | TRUE | TX |  |  |  | 2010-F-0209 | 993 Wagga 330 - Gadara 132kV TL | Z | 2010Q2 | GAD, WG1 |  | TL | 2010-05-18 07:04 | 2010-05-18 07:04 | After 993 trip Gadara CB status indicated open (Wagga 330 indicated closed), when metering checks were carried out at Gadara & Wagga 330 it indicated line was actually back on load. After SCADA site refresh (occurs every 5 minutes) Gadara C.B. 9932 status | N/A ¦ No future actions are deemed neccessary. |  | After 993 trip Gadara CB status indicated open (Wagga 330 indicated closed), when metering checks were carried out at Gadara & Wagga 330 it indicated line was actually back on load. After SCADA site refresh (occurs every 5 minutes) Gadara C.B. 9932 statu | Fog | [6 empty] | 0 | 0 | 2010
1398 | 49577 | Animal/Bird | Animal/Bird | TRUE | TX |  |  |  | 2010-F-0216 | No.2 Transformer 132/33/11kV | Z | 2010Q2 | PMQ |  | TX | 2010-05-25 13:03 | 2010-05-25 18:04 | Site staff advised that a snake has caused a flash over on the No2 TX 33kV VT. No2 Transformer was isolated & Earthed for testing. | NIL |  | Site staff advised that a snake has caused a flash over on the No2 TX 33kV VT. The No2 Tx VT was tested on the 25th of May 2010 and found serviceable. There was no evidence of any damage to the Transformer. | Fine | [6 empty] | 0 | 0 | 2010
1396 | 49571 | Staff Error | Unknown | TRUE | Prev |  |  |  | 2010-F-0215 | No.1 Tie Transformer 500/330kV | Z | 2010Q2 | MTP |  | TX | 2010-05-25 13:07 | 2010-05-25 19:10 |  |  |  | Transformer tripped. No loss of load. (Impact on market) Staff on site are investigating. Advised that No1 Tie TX protection has operated again. Hue advised same protection as before. Both protection operations coincided with the fitters opening & closing | [7 empty] | 1 | 1 | 2010 | QAPR report indicates incorrect isolation of blue phase CT core leading to incorrect protection operation
1395 | 49555 | Lightning/Storm | Unknown | TRUE | TL |  |  |  | 2010-F-0212 | 945 Wellington - Molong tee Well'n Town 132kV TL | Z | 2010Q2 | MOL, WL1 |  | TL | 2010-05-26 06:57 | 2010-05-26 06:57 | Protection details at Molong still required. | The incident has been noted for the next scheduled patrol of the line. |  | A patrol of all road and rail crossings on line was undertaken and no cause for the trip was found. The incident has been noted for the next scheduled patrol of the line. Storms in the area. | Rain | [6 empty] | 0 | 0 | 2010
1399 | 49724 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2010-E-0010 | 5A1 Eraring A CB 5A12A | Q | 2010Q2 | KCR |  | CB | 2010-05-30 07:56 | 2010-05-30 12:47 | Low SF6 gas on Red phase CB 5A12A, but No.2 TX required to be taken O/S because unable to operate Disc 6427. No.2 TX O/S @ 0914 hrs. SF6 gas topped up, CB 5A12A closed @ 1247 hrs & No.2 TX I/S 1249 hrs. |  |  | Taken O/S at 2313 on 4/5/11 to top up White phase SF6. Returned to service at 0054 on 5/5/11. Leak located as B Ph line side density monitor o ring and repaired 15/9/10 but still leaking. Need to leak check again. FA4 | [7 empty] | 0 | 0 | 2010
1407 | 50054 | HV Equipment | HV Equipment Failure | TRUE | CT |  |  |  | 2010-F-0223 | 85 Tamworth 330 - Armidale 330kV TL | Z | 2010Q2 | AR1, TA1 |  | TL | 2010-06-01 17:23 | 2010-06-02 17:18 | [11 empty] | 0 | 0 | 2010
1408 | 50301 | Secondary Equipment | Animal/Bird | TRUE | TX |  |  |  | 2010-F-0224/ | No.2 Transformer 330/132/11kV | Z | 2010Q2 | VYD |  | TX | 2010-06-07 11:53 | 2010-06-07 16:59 |  |  |  | "No gas present when Buchholz Relay bled. Visual inspection of transformer showed no signs of damage or oil leaks. Low insulation resistance found on Buchholz Relay trip wiring. Water and mud found in Buchholz Relay termination box. Found spare cable glan | [7 empty] | 0 | 0 | 2010
1409 | 50565 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | Aux Tx |  |  |  | 2010-F-0226 | No.1 Transformer 330/132/11KV | Z | 2010Q2 | CA1 |  | TX | 2010-06-11 06:28 | 2010-06-11 12:22 | Low oil level in conservator |  |  | Unable to confirm oil level as sight glass dirty. No other damage apparent. Low oil level in conservator. Tx oil topped up & all alarms and protections reset. | Fine | [6 empty] | 0 | 0 | 2010
1410 | 50566 | HV Equipment | Sec Eqt Malfunction | TRUE | CB SF6 |  |  |  | not available | No.2 Tie Transformer 500/330/33kV | E | 2010Q2 | BAY |  | TX | 2010-06-12 09:40 | 2010-06-12 12:57 |  |  |  | Low SF6 CB6422. Make 'SIEMENS 3AP2FI-2' (Contract C1172). This CB has not been topped up before. The CB was installed in Jan 09 and is still covered by warranty. The leak will be referred to the manufacturer. | [7 empty] | 0 | 0 | 2010
1411 | 50602 | Relay Setting | Unknown | TRUE | Proc |  |  |  | 2010-F-0228 | No.1 150MVAr Shunt Reactor | Q | 2010Q2 | MTP |  | RX | 2010-06-13 14:21 | 2010-06-15 16:13 | No.1 reactor tripped on closing.............No.1 reactor returned to service at 16:14hrs on 15/6/10 after investigations carried out. | Plant branch to follow |  | Reactor tripped on closing and returned to service after investigations carried out. Issue has been investigated by Tech Services and Protection Design. The feedback is that the trip is due to CT saturation if CB close diff is >2ms. This is the case wit | [7 empty] | 1 | 0 | 2010 | Incorrect protection settings
1412 | 50615 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | Bus |  |  |  | not available | No.4 Transformer 330/132/16kV | E | 2010Q2 | NEW |  | TX | 2010-06-16 06:38 | 2010-06-16 08:45 |  |  |  | Low SF6 CB5442 | [7 empty] | 0 | 0 | 2010
1414 | 50678 | Secondary Equipment | Sec Eqt Malfunction | TRUE | Sec |  |  |  | 2010-F-0230 | 250 Sydney North - Berowra 132kV Line | Q | 2010Q2 | SYN |  | TL | 2010-06-17 13:00 | 2010-06-17 15:14 | Feeder tripped when 257 Galston U/C failed on Initial energisation from Sydney North. Tripped on thru fault. This has happened previousley. |  |  | Feeder tripped when 257 Galston U/C failed on Initial energisation from Sydney North. Tripped on thru fault. This has happened previousley. | [7 empty] | 0 | 0 | 2010 | 2010-F-0231 FEOR indicates Non-TransGrid reason (i.e. Must be Ausgrid's cable's fault)
1423 | 50749 | Staff Error | Backup Operation | TRUE | Prev |  |  | Lost Load 33MW | 2010-F-0234 | 0825 Koolkhan - Koolkhan PS 66kV Line | S | 2010Q2 | KLK |  | TL | 2010-06-17 15:40 | 2010-06-17 16:07 |  |  |  | Staff were working on the protection panel at the time. The incident occurred during the work involved with the installation of new Transformer at Koolkhan Substation. The Projects Manager Northern has investigated the incident and submitted a separate d | Fine | [6 empty] | 1 | 1 | 2010 | Staff working on the protection panel at the time, likely to have caused an incorrect isolation leading to an incorrect protection operation
1418 | 50737 | Staff Error | Unknown | TRUE | Prev |  |  | Lost Load 31MW | 2010-F-0233 | 0825 Koolkhan - Koolkhan PS 66kV Line | S | 2010Q2 | KLK |  | TL | 2010-06-17 17:12 | 2010-06-17 17:17 | Loss of Grafton load. | D2010/0620 ¦ Refer to the detailed investigation report of the incident. |  | D2010/0620 ¦ Refer to the detailed investigation report of the incident. | [7 empty] | 0 | 1 | 2010 | Opslog indicates switching error, excerpt: "Swticher (sic) was executing PRI 24976/2 Steps 23 to 31 and failed to coorectly carry out step 29 "check CB 3712 open". The bus bar tripped when an attempt was made to close bus isolator 3713"
1430 | 50763 | HV Equipment | Unknown | TRUE | TL |  |  |  | 2010-F-0237 | 967 Lismore 330 - Koolkhan 132kV TL | Z | 2010Q2 | KLK, LSM |  | TL | 2010-06-19 06:24 | 2010-06-19 06:24 |  | NIL |  | "The Line Team climbed structures 295 through to 335 of the line on the 29th of June 2010 and found a flashed over long rod insulator, at structure 314 (suspension top phase), which was replaced." | Fine | [6 empty] | 0 | 0 | 2010
1431 | 51446 | Unknown | Unknown | TRUE | TL |  |  |  | 2010-F-0243 | 96G Pt Macquarie - Kempsey 132kV TL | Z | 2010Q2 | KS2, PMQ |  | TL | 2010-06-30 14:01 | 2010-06-30 14:01 | no voltage depression or loss of load. CE reported no undue effect on their system | The incident has been noted for next scheduled Ground/Aerial Patrol. |  | No voltage depression or loss of load. CE reported no undue effect on their system. A ground patrol of the section of the line (between Structures 74 to 137) showed no evidence any damage to the line. | [7 empty] | 0 | 0 | 2010
1432 | 52290 | Secondary Equipment | Sec Eqt Malfunction | TRUE | SVC |  |  |  | 2010-F-0250 | No.1 Static VAR Compensator | Z | 2010Q3 | SYW |  | SVC | 2010-07-04 17:04 | 2010-07-06 17:04 | RTS 1704hrs 6/7/10 | ITEM |  | Control system defect fixed - computer motherboard failure. Spares being procured by SSE. | [7 empty] | 0 | 0 | 2010
1442 | 53141 | LV/MECH Fail | LV/MECH/PROT Equipment Fail | TRUE | Sec |  |  | "Return of various plant occurred over a period of time. Load Lost 76MW Load changed over instant-aneously 9MW" | 2010-F-0266 | 132kV A Bus No.1 Section | Q | 2010Q3 | SYN |  | BB | 2010-07-07 04:45 | 2010-07-07 20:55 | Trip due to cable trench fire near 132kV A1 and B1 BBP Summation Kiosk. Numerous control and protection cables damaged. No.2 Capacitor out of service at time of trip. 257 Galston 132kV Feeder isolated and earthed at time of trip. 132kV A Bus No.1 Section | LOCAL AREA |  | "At 0445hrs a series of a series of alarms and unusual SCADA indications occurred at Sydney North. At 0447hrs, The 132kV A and B busbars, No 1 and No 2 transformers, 251 Sydney North Pennant Hills and 250 Sydney North Berowra tripped interrupting about 14 | [7 empty] | 1 | 0 | 2010 | Protection cables (amongst others) burnt causing protection operation
1433 | 52383 | HV Equipment | HV Equipment Failure | TRUE | Cap |  |  |  | not availabe | No.2 Capacitor | Z | 2010Q3 | WL1 |  | CAP | 2010-07-07 13:34 | 2010-07-07 15:06 | [11 empty] | 0 | 0 | 2010
1434 | 52468 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2010-E-0013 | 2M Munmorah 330kV B CB 2M2B | Q | 2010Q3 | TGH |  | CB | 2010-07-08 07:15 | 2010-07-08 09:29 | CB taken out of service to top up SF6 then RTS. |  |  | CB taken out of service to top up SF6 then RTS. Leak appears to be CB watch transducer. CB fitted 28/11/08, 2yr warranty. Areva repaired 9/7/10. | Rain | [6 empty] | 0 | 0 | 2010
1435 | 52643 | Animal/Bird | Animal/Bird | TRUE | TX |  |  |  | 2010-F-0253 | No.1 Transformer 132/66kV | Z | 2010Q3 | ORG |  | TX | 2010-07-13 07:58 | 2010-07-13 10:40 | Birds nest on gantry above 66kV CB3412. Caused loss of AC supply to control room. No Aux TX on No4 TX. Generator was started manually to run during repair outage. | Availability of wire offcuts during construction work gives birds more material for building these types of nests. Some consideration to be given to storage of scrap during these works. ¦ ITEM |  | Birds nest mainly of metal wire on gantry above 66kV CB3412. Caused loss of AC supply to control room. No Aux TX on No4 TX. Generator was started manually to run during repair outage. Availability of wire off cuts during construction work gives birds more | [7 empty] | 0 | 0 | 2010
1514 | 62014 | HV Equipment | HV Equipment Failure | TRUE | TL |  |  |  | 2010-E-0038 | 5A2 Kemps Creek 500kV CB 5A22 | Q | 2010Q3 | ER0 |  | CB | 2010-07-14 07:51 | 2010-07-14 09:09 | Low SF6 |  |  |  | Unknown | [6 empty] | 0 | 0 | 2010
1436 | 52691 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2010-E-0014 | 24 Vales Point 330kV CB 242 | Q | 2010Q3 | ER0 |  | CB | 2010-07-15 06:28 | 2010-07-15 08:15 | RTS at 0815hrs after SF6 top up. |  |  | RTS at 0815hrs after SF6 top up. Leaky monitor - repairs planned for 20/10/10 | Fine | [6 empty] | 0 | 0 | 2010
1542 | 93520 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2010-E-0014 | 96G Kempsey 132kV CB 96G2 | Q | 2010Q3 | PMQ |  | CB | 2010-07-15 09:39 | 2010-07-15 10:40 |  |  |  | RTS at 1040hrs after CT SF6 top up. | [7 empty] | 0 | 0 | 2010
1523 | 62045 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CT |  |  |  | 2010-E-0046/1 | No.2 Transformer 330/132/11KV | E | 2010Q3 | SYN |  | TX | 2010-07-16 16:58 | 2010-07-20 16:50 |  |  |  | Transformer taken out of service due to reported damage to red & white phase metering C.T. Cores. C.B.. 4422B already out of service for other work. | [7 empty] | 0 | 0 | 2010
1438 | 52748 | Design Ommission | Unknown | TRUE | Prot |  |  |  | 2010-F-0258 | No.1 150MVAr Shunt Reactor | Q | 2010Q3 | MTP |  | RX | 2010-07-17 02:51 | 2010-07-17 09:16 | No.1 Reactor tripped on closing.........Clearance given by Mainetence Engineer to return to service No.1 Reactor. No.1 reactor made available for service 09:16hrs. | ITEM |  | No.1 Reactor tripped on closing.........Clearance given by Maintenance Engineer to return to service No.1 Reactor. No.1 reactor made available for service 09:16hrs. Known issue. Follow-up in progress with Plant/Protection Design. | Fine | [6 empty] | 1 | 0 | 2010
1439 | 52942 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2010-E-0033 | 78 Sydney South 330kV CB 782A | Q | 2010Q3 | ING |  | CB | 2010-07-24 11:41 | 2010-07-26 13:26 | Low SF6 on C.B. Taken out of service to top up. Found leaking isolation valve which required replacing. |  |  | When cap removed on CB filler to top up with SF6, the hole has been filled with a cork plug. On drilling out cork plug SF6 gas proceeded to leak from filler hole. SF6 main isolating valve on other side of filler was checked & is turned off, but is obvious | [7 empty] | 0 | 0 | 2010
1455 | 54374 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | Rx |  |  |  | 2010-E-0019 | No.6 Reactor | E | 2010Q3 | KCR |  | RX | 2010-07-29 01:54 | 2010-08-09 12:08 | Air Cell ruptured indicator. RX taken O/S.Water ingress in the alarm circuit. RTS 9/8/10 1208hrs |  |  | Air Cell ruptured indicator. RX taken O/S.Water ingress in the alarm circuit. | [7 empty] | 0 | 0 | 2010
1452 | 54072 | HV Equipment | Unknown | TRUE | TX |  |  |  | 2010-E-0017 | No.1 Transformer 132/33/11kV | E | 2010Q3 | YA2 |  | TX | 2010-08-11 23:10 | 2010-08-12 23:09 | Taken O/S due to Main Tank Buchholz alarm. Raining at time of alarm. |  |  | Taken O/S due to Main Tank Buchholz alarm. Raining at time of alarm. Advised oil sample of TX oil taken & to be tested. TX to remain I & E until result of oil sample. | [7 empty] | 0 | 0 | 2010
1453 | 54343 | HV Equipment | Sec Eqt Malfunction | TRUE | CB SF6 |  |  |  | 2010-E-0018 | No.1 Transformer 500/330/33kV | E | 2010Q3 | BBY |  | TX | 2010-08-12 14:09 | 2010-08-13 13:34 | 500kV internal CT Blue phase, 2 spare cores found open circuit with damage to terminal block on S/S inspection TX taken O/S. Repaired and RTS 1334 13/8/10 |  |  | 500kV internal CT Blue phase, 2 spare cores found open circuit with damage to terminal block on S/S inspection TX taken O/S. Repaired and RTS 1334 13/8/10 | [7 empty] | 1 | 0 | 2010 | Faulty CT protection terminals
1454 | 54364 | Unknown/Storm | Wind | TRUE | TL |  |  |  | 2010-F-0291 | 96M Narrabri - Moree 132kV TL | Z | 2010Q3 | MRE, NB2 |  | TL | 2010-08-13 01:01 | 2010-08-13 01:02 | Distance to Fault 9% | Have close look at the suspect area of the fault during next aerial patrol of the line. |  | Distance to Fault 9%. A ground patrol of the section of the line between Structures 14 to 75 was carried out on the 13th of August 2010. Section of the line between structures 44 and 50 could not be closely inspected because of wet conditions. However thi | [7 empty] | 0 | 0 | 2010
1456 | 54385 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | SVC |  |  |  | 2010-F-0292 | No.1 Static VAR Compensator | Z | 2010Q3 | LSM |  | SVC | 2010-08-13 16:30 | 2010-08-13 17:14 | No.1 pump failed when switched via duty cycle and tripped SVC, RTS at 1714 hrs on 13.08.2010 |  |  | No.1 pump failed when switched via duty cycle and tripped SVC. The SVC was taken out of service on the 17th of August for a close inspection of the pumps. A pocket of air was found in the No1 Pump system. All bleeding points on the system including the th | Fine | [6 empty] | 0 | 0 | 2010
1457 | 54387 | HV Equipment | Unknown | TRUE | TL |  |  |  | 2010-F-0293 | 99K Darlington Pt - Griffith 132kV TL | Z | 2010Q3 | DNT, GRF |  | TL | 2010-08-15 03:07 | 2010-08-15 03:07 |  | The insulator string at structure 382 could not be replaced and has been re-scheduled for replacement in October due to bad ground conditions. |  | The protection details at both ends suggest that a red-phase to earth fault caused the trip. Three insulator flashovers were identified at structures 332, 340 and 382. Nothing else was identified that could explain the fault. The insulator strings at stru | Rain | [6 empty] | 0 | 0 | 2010
1458 | 54391 | HV Equipment | HV Equipment Failure | TRUE | CT |  |  |  | 2010-E-0020 | Spare Bay 3 Transformer CB 5232 | Q | 2010Q3 | BAY |  | CB | 2010-08-15 12:24 | 2010-08-15 16:10 | Returned to service at 1610 HRS after topping up SF6 in C.B.. 5232 Blue phase C.T. |  |  | Returned to service at 1610 HRS after topping up SF6 in C.B.. 5232 Blue phase C.T. | [7 empty] | 0 | 0 | 2010
1459 | 54703 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2010-E-0021 | No.3 Capacitor | E | 2010Q3 | SYW |  | CAP | 2010-08-21 13:49 | 2010-08-21 14:57 | Low SF6 white phase CB4732 |  |  | Low SF6 white phase CB4732. First O rings replaced on ABB gauge, leak was still present, then gauge replaced and leak fixed (on 17/9/2010.) | [7 empty] | 0 | 0 | 2010
1460 | 54710 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2010-E-0022 | No.3 Capacitor | E | 2010Q3 | SYN |  | CAP | 2010-08-22 09:02 | 2010-08-22 10:14 | CB4732 Low SF6 white phase. Topped up and RTS 1014hrs |  |  | CB4732 Low SF6 white phase. Topped up and RTS 1014hrs. SF6 Gauge leaking, need to replace O rings to fix it. | [7 empty] | 0 | 0 | 2010
1461 | 54711 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2010-E-0023 | No.3 Transformer 330/132/11kV | E | 2010Q3 | SYS |  | TX | 2010-08-22 12:14 | 2010-08-22 13:48 |  |  |  | No.3 TX to Isolated to allow top up of SF6 on CB4432. RTS 1348hrs | [7 empty] | 0 | 0 | 2010
1508 | 61989 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2010-E-0031 | 37 Macarthur B CB 372B | Q | 2010Q3 | KCR |  | CB | 2010-08-25 22:56 | 2010-08-25 23:51 | Low SF6 on C.B. Taken out of service to top up. |  |  | Low SF6 on C.B. Taken out of service to top up. | [7 empty] | 0 | 0 | 2010
1463 | 54950 | Bushfire | Unknown | TRUE | TL |  |  |  | 2010-F-0298 | 87 Armidale - Coffs Harbour 330kV TL | Z | 2010Q3 | AR1, COF |  | TL | 2010-08-29 16:12 | 2010-08-29 16:12 |  |  |  | No storms or fires in the area at the time. Cause unknown. Fault recorders at Armidale and Coffs Harbour were triggered. No reports from the public via Country Energy of any flashovers. A ground patrol between structures 274 and 235 identified that a "bu | [7 empty] | 0 | 0 | 2010
1464 | 55677 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2010-E-0024 | 78 Sydney South 330kV CB 782A | Q | 2010Q3 | ING |  | CB | 2010-09-03 23:53 | 2010-09-04 00:55 | Taken out of service to top up low SF6 following receipt of alarm. |  |  | Taken out of service to top up low SF6 following receipt of alarm. WO 178540 raised to find source of leak. | Rain | [6 empty] | 0 | 0 | 2010
1465 | 55787 | Unknown | Unknown | TRUE | TL |  |  |  | 2010-F-0312 | 94X Wallerawang 132 (New) - Panorama 132kV TL | Z | 2010Q3 | PMA, WWS |  | TL | 2010-09-08 05:44 | 2010-09-08 05:44 |  |  |  | A patrol of all road and rail crossings on the line was undertaken and no cause for the trip was found | [7 empty] | 0 | 0 | 2010
1466 | 55900 | Instruction Error | Sec Eqt Staff Error | TRUE | Proc |  |  |  | 2010-F-0314 | No.2 Generator 330kV CB 5222 | Q | 2010Q3 | ER0 |  | CB | 2010-09-11 09:34 | 2010-09-11 10:43 |  |  |  | Switching Instruction was written without Intertrip link Isolation, so bay tripped on de-energisation of oil pumps. Isolation was taken and Protection reset. | [7 empty] | 0 | 1 | 2010 | Incorrect isolation
1543 | 93526 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2010-E-0026 | 9U9 Lismore 132 CB 9U92 | Q | 2010Q3 | LSM |  | CB | 2010-09-12 12:12 | 2010-09-12 13:09 |  |  |  | Low SF6 Alarm. CB 9U92 taken out of service topped up and returned to service. Known leak. Overhaul program is planned for the Lismore CBs | [7 empty] | 0 | 0 | 2010
1544 | 93527 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2010-E-0027 | 10 Avon 330kV TL CB 102 | Q | 2010Q3 | DPT |  | CB | 2010-09-15 15:46 | 2010-09-15 17:11 |  |  |  | @ Dapto C.B.. 102 red phase low SF6 gas, topped up & RTS 17:11 hrs. | [7 empty] | 0 | 0 | 2010
1468 | 56086 | Protection | Sec Eqt Malfunction | TRUE | Prot |  |  |  | 2010-F-0316 | 39 Sydney West - Bannaby 330kV TL | Z | 2010Q3 | SYW, BBY |  | TL | 2010-09-18 07:13 | 2010-09-18 07:19 | 61 T/L tripped @ BBY only. At time of trip 61 T/L selected to NAR both ends (line work on 35 & 36 T/L's). Line placed on load 0719 hrs. Suspect faulty No.1 Prot @ BBY, Prot staff to investigate | N/A ¦ No further action is deemed neccessary. |  | Faulty protection at Bannaby SS is suspected as the cause for the trip and protection design is presently investigating. | Fine | [6 empty] | 1 | 0 | 2010 | Faulty protection relay confirmed by QAPR report
1545 | 93528 | HV Equipment | HV Equipment Failure | TRUE | CBOil |  |  |  | 2010-F-0320 | 898 Trundle 66kV CB 8982 | Q | 2010Q3 | PKS |  | CB | 2010-09-22 05:54 | 2010-09-22 05:54 |  |  |  | When staff arrived after a CB alarm the spring charge motor was found burnt out. An outage was required to repair CB. Suspect one off problem with this old CB, installed 1993. more details in WO 179368. | [7 empty] | 0 | 0 | 2010
1469 | 56224 | HV Equipment | Unknown | TRUE | Cap |  |  |  | log report | No.2 Capacitor | E | 2010Q3 | NEW |  | CAP | 2010-09-23 14:58 | 2010-09-23 17:17 |  |  |  | No2 Cap has a Hot Joint that could cause damage if left in service. NCM advised. No2 Cap de-energised & command blocked. WO179370 for repair of the hot joint was completed on 24/9/10 | [7 empty] | 0 | 0 | 2010
1524 | 62049 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | Rx |  |  |  | 2010-E-0047 | No.2 Reactor | E | 2010Q4 | SYS |  | RX | 2010-10-03 17:44 | 2010-11-02 19:50 | Taken out of service on receipt of Pressure Relief Valve operated alarm. | ITEM |  | Taken out of service on receipt of Pressure Relief Valve operated alarm. | [7 empty] | 0 | 0 | 2010
1526 | 62133 | HV Equipment | HV Equipment Failure | TRUE | CB |  |  |  | Not available | No.3 Capacitor | E | 2010Q4 | WL1 |  | CAP | 2010-10-05 15:06 | 2010-10-06 09:33 |  |  |  | Low SF6, Faulty density monitor. | [7 empty] | 0 | 0 | 2010
1470 | 57458 | Animal/Bird | Unknown | TRUE | TL |  |  |  | 2010-F-0333 | 5A4 Bayswater - Wollar 500kV TL | Z | 2010Q4 | BAY, WOL |  | TL | 2010-10-13 04:46 | 2010-10-13 04:46 |  |  |  | A patrol of the line in the area of the fault (as determined by the Travelling Wave Fault Locators at Bayswater and Mt Piper Substations) was undertaken. Some bird nesting activity was noted on several structures. At structure 228, Red phase a corona ring | [7 empty] | 0 | 0 | 2010
1472 | 57654 | Animal/Bird | Unknown | TRUE | TL |  |  |  | 2010-F-0338 | 5A3 Bayswater - Mt Piper 500kV TL | Z | 2010Q4 | BAY, MTP |  | TL | 2010-10-15 06:31 | 2010-10-15 06:31 |  |  |  | A climbing line patrol has found evidence of a flashover on the corona ring at Structure 82 (on top phase) of the line. A bird’s nest found above the conductors on this structure. Climbing inspections of structures in the immediate vicinity are also bein | [7 empty] | 0 | 0 | 2010
1515 | 62015 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2010-E-0039 | No.3 Generator 500kV CB 6232 | Q | 2010Q4 | ER0 |  | CB | 2010-10-15 06:58 | 2010-10-15 12:42 | Low SF6 |  |  | SF6 Top up. Monitor is leaking with repair planned 16/2/11 | Unknown | [6 empty] | 0 | 0 | 2010
1471 | 57647 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0336 | 2 Upper Tumut - Yass 330kV TL | Z | 2010Q4 | UT1, YSN |  | TL | 2010-10-15 08:58 | 2010-10-15 08:58 |  |  |  | Heavy rain in area at time of TAR. A routine aerial inspection of the line was undertaken and no fault was identified to explain the line trip. | [7 empty] | 0 | 0 | 2010
1473 | 57692 | Unknown | Unknown | TRUE | TL |  |  |  | 2010-F-0343 | 992 Burrinjuck - Tumut 132kV TL | Z | 2010Q4 | BUK, TU2 |  | TL | 2010-10-16 15:54 | 2010-10-16 18:08 | Transmission line tripped at the same time as No.2 Transformer at Gadara. | N/A ¦ N/A |  | A routine aerial patrol of TL 992 had identified a flashed over string at structure 146. A/R failed to operate at BUK because A/R had been selected as non-auto on the Eraring Energy HMI. The EE HMI has now been removed from the A/R selection circuits for | Very Windy | [6 empty] | 0 | 0 | 2010
1474 | 57904 | Unknown | Unknown | TRUE | TL |  |  |  | 2010-F-0345 | 991 Wagga 132 - Murrumburrah 132kV TL | Z | 2010Q4 | MRU, WG2 |  | TL | 2010-10-18 05:52 | 2010-10-18 05:52 | No storms in area. | N/A ¦ Protection relay data from Wagga North has been sent to protection design and is presently being investigated. |  | Storms in area. No further action was deemed necessary on this occasion. N/A Transmission Line | Fine | [6 empty] | 0 | 0 | 2010
1475 | 57927 | Animal/Bird | Unknown | TRUE | TL |  |  |  | 2010-F-0347 | 5A3 Bayswater - Mt Piper 500kV TL | Z | 2010Q4 | BAY, MTP |  | TL | 2010-10-19 03:42 | 2010-10-19 03:42 |  |  |  | A climbing line patrol has found evidence of a flashover on the corona ring at Structure 82 (on top phase) of the line. A bird’s nest found above the conductors on this structure. Climbing inspections of structures in the immediate vicinity are also bein | [7 empty] | 0 | 0 | 2010
1476 | 57936 | Unknown | Unknown | TRUE | TL |  |  |  | 2010-F-0348 | 991 Wagga 132 - Murrumburrah 132kV TL | Z | 2010Q4 | MRU, WG2 |  | TL | 2010-10-19 05:08 | 2010-10-19 05:08 | DTF 118.8 KM from Wagga North | N/A ¦ Protection relay data from Wagga North has been sent to protection design and is presently being investigated. |  | Tripped and reclosed. Reason for trip being investigated. DTF 118.8 KM from Wagga North. | Mild | [6 empty] | 0 | 0 | 2010
1477 | 58061 | Animal/Bird | Animal/Bird | TRUE | SVC |  |  |  | 2010-F-0349 | No.2 Static VAR Compensator | Z | 2010Q4 | BKH |  | SVC | 2010-10-21 13:37 | 2010-10-22 09:43 |  |  |  | "Lizard found on Reactor core , no damage. SVC returned to service 0943 HRS on 22/10/10. At 07:51hrs on placing the SVC in service staff observed a hot joint on a Cable Pot Head. The SVC was taken O/S to repair." | [7 empty] | 0 | 0 | 2010
1479 | 58296 | Secondary Equipment | Unknown | TRUE | Sec |  |  |  | 2010-F-0354 | No.2 Transformer 330/132/11kV | Z | 2010Q4 | SYS |  | TX | 2010-10-27 07:54 | 2010-10-27 16:28 | No fault recorder operation or Buchholz alarm prior to trip. Gas Tests all Clear TX energised 1628hrs | ITEM ¦ Buchholz trip is suspected to be been a result of a surge created by the starting of a pump. A data logger is to be fitted to the pump circuit in order to confirm this suspicion. |  | Main tank buchholz has operated. Staff on site are investigating. No fault recorder operation. During invetigations of trips, a faulty soft starter relay was found on one set of pumps. This unit has been switched to operate on the other set of pumps unti | [7 empty] | 0 | 0 | 2010
1478 | 58254 | Switching error | Unknown | TRUE | Prev |  |  |  | 2010-F-0353 | No.1 Transformer 132/66/11kV | Z | 2010Q4 | NAM |  | TX | 2010-10-27 11:12 | 2010-10-27 11:25 | Transformer protection trip @ 1112 (both CBs.) Protection Tech. advised PMWI restoration on 66kV BS1 in progress at time, as probable cause of trip. Protection flags indicate CB fail trip only & consistent with verbal report of incident. TX & associated | Withdraw and replace the AVO Meters Model7 from service. |  | Transformer protection trip @ 1112 (both CBs.) Protection Tech. advised PMWI restoration on 66kV BS1 in progress at time, as probable cause of trip. Protection flags indicate CB fail trip only & consistent with verbal report of incident. TX & associated e | [7 empty] | 1 | 1 | 2010 | QAPR report indicates incorrect isolation caused by defective multimeter leading to incorrect protection operation
1480 | 58447 | Lightning/Storm | Unknown | TRUE | TL |  |  |  | 2010-F-0356 | 8C Armidale - Dumaresq 330kV TL | Z | 2010Q4 | AR1, DMQ |  | TL | 2010-10-28 18:09 | 2010-10-28 18:09 | [11 empty] | 0 | 0 | 2010
1516 | 62016 | HV Equipment | Sec Eqt Malfunction | TRUE | CT |  |  |  | 2010-E-0040 | No.2 Transformer 132/33/11kV | E | 2010Q4 | TRE |  | TX | 2010-10-30 19:42 | 2010-10-30 20:50 | low sf6 on CT, topped up. Date changed to 30/10/2010 from 30/12 please update your records |  |  | Low SF6. First top up. No leaks on monitor or pipe work. Further investigation being planned. | [7 empty] | 0 | 0 | 2010
1520 | 62022 | Lightning/Storm | Unknown | TRUE | TL |  |  |  | 2010-F-0440 | 998 Forbes - Cowra 132kV TL | Z | 2010Q4 | CW2, FB2 |  | TL | 2010-10-31 04:58 | 2010-10-31 04:58 | operators log book shows no indication of storms | The incident has b een noted for the next scheduled aerial patrol of the line. |  | A ground level patrol was undertaken of the line and no cause for the trip could be found. The line was scheduled for the next aerial patrol. | [7 empty] | 0 | 0 | 2010
1481 | 59328 | Animal/Bird | Unknown | TRUE | TL |  |  |  | 2010-F-0361 | 5A3 Bayswater - Mt Piper 500kV TL | Z | 2010Q4 | BAY, MTP |  | TL | 2010-11-07 08:46 | 2010-11-07 08:46 |  |  |  | A patrol of the line in the area of the fault (as determined by the Travelling Wave Fault Locators at Bayswater and Mt Piper Substations - structure 270) was undertaken. Some bird nesting activity was noted on several structures. | [7 empty] | 0 | 0 | 2010
1483 | 59334 | HV Equipment | Unknown | TRUE | SVC |  |  |  | 2010-F-0362 | No.2 Static VAR Compensator | Z | 2010Q4 | BKH |  | SVC | 2010-11-07 19:29 | 2010-11-08 20:06 | Dry electrical storm at time of trip. Advised by B Mills that Pulse card 5 had failed. SVC returned to service at 20:06 hrs 8-11-10 |  |  | Dry electrical storm at time of trip. Advised that Pulse card 5 had failed. | Thunderstorm | [6 empty] | 0 | 0 | 2010
1484 | 59337 | Lightning/Storm | Unknown | TRUE | TL |  |  |  | 2010-F-0363 | 96L Lismore 330 - Tenterfield tee Casino 132kV TL | Z | 2010Q4 | LSM, TTF |  | TL | 2010-11-08 06:18 | 2010-11-08 06:18 |  |  |  | T/L tripped and auto reclosed. Storms in area. No.1 TX returned to service on arrival of staff at site. A ground patrol around the three major road crossings between Lismore end and structure 339 of the line carried out on the 17th of November 2010, has i | [7 empty] | 0 | 0 | 2010
1486 | 59398 | Lightning/Storm | Unknown | TRUE | TL |  |  |  | 2010-F-0365 | 21 Sydney North - Tuggerah 330kV TL | Z | 2010Q4 | SYN, TGH |  | TL | 2010-11-08 20:45 | 2010-11-08 20:45 |  |  |  | Distance to fault identified as 30.67kM & 30.85kM. Storms in area at time of fault. | [7 empty] | 0 | 0 | 2010
1487 | 59469 | Secondary Equipment | LV/MECH/PROT Equipment Fail | TRUE | Sec |  |  |  | 2010-F-0367 | No.2 Transformer 330/132/11kV | Z | 2010Q4 | SYS |  | TX | 2010-11-10 10:09 | 2010-11-10 14:47 | Trip occurred during the installation of a data logger on the oil pumps. No.1 pump was stopped and No.2 Pump cut in even though the control was switched to off. No.2 Transformer RTS at 1447hrs 10/11/10 with No.1 oil pump available only. | ITEM |  | Trip occurred during the installation of a data logger on the oil pumps. No.1 pump was stopped and No.2 Pump cut in even though the control was switched to off. No.2 Transformer RTS at 1447hrs 10/11/10 with No.1 oil pump available only. Data logger was be | Fine | [6 empty] | 0 | 0 | 2010
1517 | 62017 | HV Equipment | Sec Eqt Malfunction | TRUE | CB SF6 |  |  |  | 2010-E-0041 | No.3 Reactor | E | 2010Q4 | LSM |  | RX | 2010-11-11 10:25 | 2010-11-11 11:28 | Low sf6 on CB 5932. topped up |  |  | SF6 Top up. 2.5 years since last top up. Repairs proposed for next HV outage with date to be advised. | [7 empty] | 0 | 0 | 2010
1488 | 59612 | HV Equipment | Unknown | TRUE | TX |  |  |  | 2010-F-0368 | No.2 Transformer 330/132/11kV | Z | 2010Q4 | SYS |  | TX | 2010-11-12 12:36 | 2010-11-12 15:08 | Transformer T/C high level oil alarm is incorrectly grouped with Buchholz alarm. Transformer taken O/S via SCADA due to Buchholz alarm by operator. Oil level has been reduced and Transformer returned to service via SCADA at 15:08hrs |  |  | Transformer T/C high level oil alarm is incorrectly grouped with Buchholz alarm. Transformer taken O/S via SCADA due to Buchholz alarm by operator. Oil level has been reduced and Transformer returned to service via SCADA at 15:08hrs. | [7 empty] | 0 | 0 | 2010
1489 | 59616 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0369 | 97K Cooma - Munyang tee Snowy Adit 132kV TL | Z | 2010Q4 | CMA, MNY |  | TL | 2010-11-13 19:04 | 2010-11-13 19:04 | Indji indicates a lightning strike between Munyang and Island Bend in the vicinity of the D/C section of 97K & 97L TL's. Refer FEOR 370 for a simultaneous trip occurred on 97L TL. Both Units tripped that were in-service at Guthega (60MW total generation l | N/A ¦ No future action is deemed necessary. |  | "No Auto reclose provide on this Line. Refer FEOR 369 for simultaneous trip occurred on 97K TL. Indji indicates a lightning strike between Munyang and Snowy Adit in the vicinity of the D/C section of 97K & 97L TL's. 97L RTS 0650hrs 14/11/10 after SHL rese | Thunderstorm | [6 empty] | 0 | 0 | 2010
1490 | 59617 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  | 60MW Generation lost | 2010-F-0370 | 97L Guthega - Jindabyne Pumps 132kV TL | Z | 2010Q4 | GTH |  | TL | 2010-11-13 19:04 | 2010-11-14 06:50 |  |  |  | No Auto reclose provide on this Line. Refer FEOR 369 for simultaneous trip occurred on 97K TL. Indji indicates a lightning strike between Munyang and Snowy Adit in the vicinity of the D/C section of 97K & 97L .TL's. 97L RTS 0650hrs 14/11/10 after SHL rese | [7 empty] | 0 | 0 | 2010
1492 | 59750 | Lightning/Storm | Unknown | TRUE | TL |  |  |  | 2010-F-0373 | 969 Tamworth 330 - Gunnedah 132kV TL | Z | 2010Q4 | GN2, TA1 |  | TL | 2010-11-14 04:34 | 2010-11-14 04:34 | Rain & storms in area | NIL |  | Rain & storms in area. A routine aerial patrol of TL 992 had identified a flashed over string at structure 146. Field staff have been sent to the site to assess access and plan the replacement works. An outage was booked on the 27th of October 2010 and th | [7 empty] | 0 | 0 | 2010
1491 | 59739 | Unknown | Unknown | TRUE | TL |  |  |  | 2010-F-0372 | 96M Narrabri - Moree 132kV TL | Z | 2010Q4 | MRE, NB2 |  | TL | 2010-11-17 04:56 | 2010-11-17 04:56 | Rain in area. Distance to fault reported as 76% from Narrabri. Unable to reset protection relays at Narrabri due to relay fault. | Technical Services will plan and repair the YTG relay in this week. |  | Rain in area. Distance to fault reported as 76% from Narrabri. Unable to reset protection relays at Narrabri due to relay fault. No evidence of any cause of the trip was identified following an inspection. | [7 empty] | 0 | 0 | 2010
1521 | 62030 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2010-E-0044 | 37 Macarthur B CB 372B | Q | 2010Q4 | KCR |  | CB | 2010-11-18 04:17 | 2010-11-18 07:11 | Low SF6 on C.B. Taken out of service to top up gas. |  |  | SF6 Top up. Monitor is leaking with repair planned 16/2/11 | [7 empty] | 0 | 0 | 2010
1527 | 62328 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2010-E-0049 | No.1 Capacitor | E | 2010Q4 | RGV |  | CAP | 2010-11-18 09:30 | 2011-10-21 14:57 | Due to defective SF6 pressure gauge, manfacturer recommended the cap remains unavailable until replaced. RTS after repairs. | 8/11/2011 8:30:00 AM ¦ Nil. ¦ Nil. |  | The incorrect SF6 gas gauge has been installed and CB is not to be operated. Due to defective SF6 pressure gauge, manfacturer recommended the cap remains unavailable until replaced. Internal inspection required by ABB due to operation at less than rated p | [7 empty] | 0 | 0 | 2010
1522 | 62031 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2010-E-0045 | No.2 Capacitor | E | 2010Q4 | WG1 |  | CAP | 2010-11-18 09:36 | 2010-11-18 12:15 | Low SF6 on C.B.. 4722. Taken out of service to top up. |  |  | Low SF6 on C.B.. 4722. Taken out of service to top up. FA1 CB with known leaks. Replacemen tplanned September 2011. | [7 empty] | 0 | 0 | 2010
1518 | 62018 | HV Equipment | Sec Eqt Malfunction | TRUE | CB SF6 |  |  |  | 2010-E-0042 | No.4 Bay Coupler CB 5042 | Q | 2010Q4 | MN1 |  | CB | 2010-11-20 03:34 | 2010-11-20 07:41 | low sf6 topped up and everyone was happy |  |  | CB 5042 topped up with SF6. Last topped up 20/11/10. (2 day duration between alarms). Please investigate leakage as frequency of top up is increasing. SF6 leak investigated and found in corroded section of SF6 gas pipe work at base of white phase pole. R | [7 empty] | 0 | 0 | 2010
1519 | 62019 | HV Equipment | Sec Eqt Malfunction | TRUE | CB SF6 |  |  |  | 2010-E-0043 | No.4 Bay Coupler CB 5042 | Q | 2010Q4 | MN1 |  | CB | 2010-11-22 05:27 | 2010-11-22 06:24 | cb 5042 topped up with sf6 |  |  | SF 6 | [7 empty] | 0 | 0 | 2010
1493 | 60136 | Animal/Bird | Animal/Bird | TRUE | Rx |  |  |  | 2010-F-0377 | No.4 Transformer Reactor | Z | 2010Q4 | DNT |  | RX | 2010-11-27 05:14 | 2010-11-27 13:22 | Advised very deceased black crow under 33kV insulator W ph. Slight arc mark on skirts of insulator. Protection Details CA01, CA02, Auto Voltage Control reset. Returned to service at 1322hrs 27-11-10 by SCADA |  |  | Advised very deceased black crow under 33kV insulator W ph. Slight arc mark on skirts of insulator. Protection Details CA01, CA02, Auto Voltage Control reset. Returned to service at 1322hrs 27-11-10 by SCADA. | [7 empty] | 0 | 0 | 2010
1525 | 62061 | Design Ommission | LV/MECH/PROT Equipment Fail | TRUE | Proc |  |  |  | 2010-E-0048 | No.2 Transformer 330/132/11kV | E | 2010Q4 | RGV |  | TX | 2010-11-30 15:02 | 2010-11-30 16:47 | CB lockout relay alarm & error status received from the Transformer 132kV C.B.. 4422 when being returned to service. Transformer taken out of service to investigate. | ITEM |  | CB lockout relay alarm & error status received from the Transformer 132kV C.B.. 4422 when being returned to service. Transformer taken out of service to investigate. No motor excess run timer installed. Timer purchased, installed & tested. | [7 empty] | 0 | 0 | 2010 | Not a protection failure, defective plant (CB missing timer)
1494 | 60626 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0386 | 999 Yass - Cowra 132kV TL | Z | 2010Q4 | CW2, YSN |  | TL | 2010-12-02 17:12 | 2010-12-02 17:12 |  | N/A ¦ No further action was deemed necessary on this occasion. |  | Storms in the area. | Thunderstorm | [6 empty] | 0 | 0 | 2010
1495 | 60629 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0389 | 970 Yass - Burrinjuck 132kV TL | Z | 2010Q4 | BUK, YSN |  | TL | 2010-12-02 22:23 | 2010-12-02 22:23 | Storms in area. | N/A ¦ No further action was deemed necessary on this occasion. |  | Storms in the area. | [7 empty] | 0 | 0 | 2010
1496 | 60669 | Lightning/Storm | Unknown | TRUE | TL |  |  |  | 2010-F-0394 | 947 Mt Piper 132 - Wellington tee Orange 132kV TL | Z | 2010Q4 | MPP, ORG, WL1, ONO |  | TL | 2010-12-05 15:04 | 2010-12-05 15:05 |  |  |  | Storms in the area. | Rain | [6 empty] | 0 | 0 | 2010
1497 | 60808 | HV Equipment | Sec Eqt Malfunction | TRUE | CT |  |  |  | 2010-E-0028 | No.6 Transformer 330/132/11kV | E | 2010Q4 | AR1 |  | TX | 2010-12-08 16:21 | 2010-12-08 19:36 | Alarm received No 6 Tx 446 CT SF6 Depleted Urgent alarm. Please make this a Non urgent alarm as there are two levels. The No 6 Tx was taken out and the CT SF6 level topped up. |  |  | Alarm received No 6 Tx 446 CT SF6 Depleted Urgent alarm. Please make this a Non urgent alarm as there are two levels. The No 6 Tx was taken out and the CT SF6 level topped up. Same type as Taree CT (outage ID 63840). Investigation to be arranged. | [7 empty] | 0 | 0 | 2010
1498 | 61119 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0409 | 9U3 Gunnedah - Narrabri 132kV TL | Z | 2010Q4 | GN2, NB2 |  | TL | 2010-12-15 02:15 | 2010-12-15 02:15 | Fault Locator 62.24km from Narrabri. Protection details for Gunnedah not available at this time. | NIL |  | Fault Locator 62.24km from Narrabri. Tar both ends. A ground patrol on ten structures on either side of Structure 489 of the line carried out on the 15th of December 2010 has indicated no evidence of any fault or damage to the line. Given that there are s | Fine | [6 empty] | 0 | 0 | 2010
1499 | 61120 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  | 30MW Generation lost | 2010-F-0410 | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2010Q4 | GTH, MUR, GHI |  | TL | 2010-12-15 16:51 | 2010-12-15 18:29 | Severe storms apparent in area. Guthega generation into NSW at time of incident. | N/A ¦ No further action was deemed necessary on this occasion. |  | Severe storms apparent in area. Guthega generation into NSW at time of incident. | [7 empty] | 0 | 0 | 2010
1501 | 61150 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2010-F-0414 | 4 Yass - Marulan 330kV TL | Z | 2010Q4 | MRN, YSN |  | TL | 2010-12-16 10:42 | 2010-12-16 10:42 |  |  |  | Storms are active in the area. | [7 empty] | 0 | 0 | 2010
1500 | 61148 | Switching error | Sec Eqt Staff Error | TRUE | Prev |  |  | Lost Load 6.45MWhrs | 2010-F-0412 | 234 Vineyard - Hawkesbury 132kV Line | S | 2010Q4 | VYD |  | TL | 2010-12-16 13:16 | 2010-12-16 13:21 | No auto reclose attempted. Reclose was selected off at the time of trip. 227 Fdr O/S for protection replacement @ VYD & Hawkesbury. |  |  | At 13:16: hrs Integral Energy's 234 Vineyard to Hawkesbury 132 kV T/L tripped and failed to reclose. Load restored at 1321hrs after a manual close was successful. Approximately 65Mwatts of load was interrupted for 5 minutes. No auto reclose attempted. Rec | Thunderstorm | [6 empty] | 0 | 0 | 2010 | Reclose failure is a control system failure, not protection
1502 | 61211 | External | Tree/Ground | TRUE | TL |  |  |  | 2010-F-0415 | 967 Lismore 330 - Koolkhan 132kV TL | Z | 2010Q4 | KLK, LSM |  | TL | 2010-12-18 05:45 | 2010-12-19 09:44 | A truck ran into pole 17 snapping at the base, to be replaced, hairline cracks found in Str 16 should be serviceable when conductors restrung. | None ¦ Recover the costs from Insurance. |  | Inspection found that the 30m single concrete pole structure was damaged as result of hitting by a private truck and needed replacement. There was a minimal damage to the conductors and fittings on the structure. Replacement of the 30m pole structure was | [7 empty] | 0 | 0 | 2010
1503 | 61240 | Tree/Ground | Wind | TRUE | TL |  |  |  | 2010-F-0429 | 9W3 Coffs Harbour - Raleigh 132kV TL | Z | 2010Q4 | COF, RAL |  | TL | 2010-12-20 12:17 | 2010-12-20 12:17 | Distance to fault from Coffs Harbour 18.4km Distance to fault from Raleigh 5.4km | None. ¦ NIL |  | Distance to fault from Coffs Harbour 18.4km. Distance to fault from Raleigh 5.4km. A ground patrol of the line on the 20th of December 2010 found an off easement tree (slim but fairly tall tree) had fallen on the midspan between structures 107 and 108 of | Very Windy | [6 empty] | 0 | 0 | 2010
1504 | 61467 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2010-E-0029 | No.3 Transformer 132kV A CB 4432A | Q | 2010Q4 | SYN |  | CB | 2010-12-23 17:21 | 2010-12-23 18:02 | Low SF6 Gas in CB, required top up. CB RTS 1802 hrs on 23/12/2010 |  |  | Low SF6 Gas in CB, required top up. Camera investigation completed in 2009 with nothing found. WO raised for follow up investigation. | Fine | [6 empty] | 0 | 0 | 2010
1505 | 61524 | LV/MECH Fail | LV/MECH/PROT Equipment Fail | TRUE | Seq Equ |  |  |  | 2010-F-0438 | No.2 Transformer 132/66/11kV | Z | 2010Q4 | NB2 |  | TX | 2010-12-28 16:32 | 2010-12-28 19:08 | Hot winding temperature box vibrated off the transformer | None. ¦ No further action required. |  | Hot winding temperature box vibrated off the transformer. Investigations of the incident identified that the Hot Winding Indicator box rubber mounting brackets were severely affected by transformer oil and weathering, which lead to their failure. The brac | [7 empty] | 0 | 0 | 2010
1506 | 61526 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2010-E-0030 | 78 Sydney South 330kV CB 782A | Q | 2010Q4 | ING |  | CB | 2010-12-29 09:30 | 2010-12-29 11:25 | CB taken O/S due to low SF6 gas level. SF6 gas topped up & CB RTS @ 1125 hrs ESTon 29/12/2010 |  |  | CB taken O/S due to low SF6 gas level. SF6 gas topped up. WO raised to investigate with camera - has had previous leak. | Fine | [6 empty] | 0 | 0 | 2010
1218 | 61549 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0001 | O7 Lower Tumut - Canberra 330kV TL | Z | 2011Q1 | CA1, LT1 |  | TL | 2011-01-01 21:42 | 2011-01-01 21:42 | [5 empty] | External | [5 empty] | 0 | 0 | 2011
1219 | 61945 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0004 | 84 Liddell - Tamworth 330 330kV TL | Z | 2011Q1 | LD1, TA1 |  | TL | 2011-01-02 22:40 | 2011-01-02 22:40 | Lightning between Str 178-180 at the time Protection details added | NONE ¦ The suspect fault noted for the next scheduled aerial patrol of the line. |  |  |  | External | [5 empty] | 0 | 0 | 2011
1220 | 62021 | Lightning/Storm | Unknown | TRUE | TL |  |  |  | 2011-F-0008 | 998 Forbes - Cowra 132kV TL | Z | 2011Q1 | CW2, FB2 |  | TL | 2011-01-06 04:43 | 2011-01-06 04:43 | Helicopter patrol of this line, found nothing | The incident has been noted for the next scheduled aerial and ground line patrols of this line. |  |  |  | External | [5 empty] | 0 | 0 | 2011
1771 | 62095 | Animal/Bird | Animal/Bird | TRUE | Cap |  |  |  | 2011-F-0011 | No.3 Capacitor | Z | 2011Q1 | DNT |  | CAP | 2011-01-08 11:51 | 2011-01-10 13:21 | CB trippped on closing via scada. Capacitor bay was inspected. No birds or animals but bay is covered in cobwebs including between phases. Capacitor was returned to service at 1321hrs 10/1/11 after clean down. |  |  |  | Fine | [6 empty] | 0 | 0 | 2011
1777 | 62101 | Staff Error | LV/MECH/PROT Equipment Fail | TRUE | Prev |  |  | Lost load 6MW | 2011-F-0012 | 887 Glen Innes - Glen Innes 66kV Line | S | 2011Q1 | GNS |  | TL | 2011-01-10 07:08 | 2011-01-10 07:20 |  |  |  | The incident occurred when an electrical fitter was tightening a cable tie within the 132kV BBP kiosk with both No1 and No2 Busbar protections in service. Whilst the Fitter did not physically touch the wire in question, the CT summation connection of the | [7 empty] | 1 | 0 | 2011 | QAPR report indicates loose wire connection, not caused by technician working on the panel at the time
1778 | 62233 | Animal/Bird | Animal/Bird | TRUE | TL |  |  |  | 2011-F-0029 | 861 Narrabri - Walgett 66kV Line | Q | 2011Q1 | NB2 |  | TL | 2011-01-15 05:46 | 2011-01-15 09:44 | CB8612 opened at 05:44hrs. Feeder remained alive in. 882 Wee Waa feeder picked up the load transfer. Caused appears to have been a frog that hopped across terminals 24, 25 & 26 on "Phase fault relay" at the back of 861 No.1 Protection panel B24 Top. Sig | None ¦ NIL |  | "CB8612 opened at 05:44hrs. Feeder remained alive in. 882 Wee Waa feeder picked up the load transfer. Caused appears to have been a frog that hopped across terminals 24, 25 & 26 on ""Phase fault relay"" at the back of 861 No.1 Protection panel B24 Top. S | Fine | [6 empty] | 0 | 0 | 2011
1779 | 62234 | Relay Setting | Sec Eqt Malfunction | TRUE | Prot |  |  |  | 2011-F-0030 | 237 Sydney West - ONESTEEL 132kV Line | S | 2011Q1 | SYW |  | TL | 2011-01-16 15:24 | 2011-01-16 15:24 | At 15:24hrs 237 Sydney West to Onesteel 132 kV T/L tripped and reclosed interrupting 65MW of load (One Steel). No surge on system. Load was progressively restored. The only protection that had operated was at Sydney West on No 1 protection indicating 3 ph |  |  | T/L tripped and reclosed interrupting 65MW of load (One Steel). No surge on system. Load was progressively restored. The only protection that had operated was at Sydney West on No 1 protection indicating 3 phase fault. Integral Energy advised no protectio | [7 empty] | 1 | 0 | 2011 | QAPR report indicates incorrect protection settings
1780 | 62273 | Animal/Bird | Animal/Bird | TRUE | SVC |  |  |  | 2011-F-0031 | No.1 Static VAR Compensator | Z | 2011Q1 | LSM |  | SVC | 2011-01-18 21:25 | 2011-01-19 13:58 | Advised by staff that a frog (dead) was found in the 7th harmonic filter cap bank. | None. ¦ NIL |  | Advised by staff that a frog (dead) was found in the 7th harmonic filter cap bank. | Fine | [6 empty] | 0 | 0 | 2011
1781 | 62314 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | SVC |  |  |  | 2011-F-0033 | No.1 Static VAR Compensator | Z | 2011Q1 | SYW |  | SVC | 2011-01-20 13:30 | 2011-01-20 14:12 | No.1 CW Pump failed to start. Started manually. SVC RTS 1412hrs | 8/11/2011 7:31:00 AM ¦ Nil ¦ Nil |  | No.1 CW Pump failed to start. Started manually. | [7 empty] | 0 | 0 | 2011
1782 | 62356 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0045 | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2011Q1 | GTH, MUR, GHI |  | TL | 2011-01-22 19:28 | 2011-01-22 20:14 |  |  |  | At 19:28hrs 97G Murray to Guthega tee Geehi 132 kV T/L tripped, interrupting supply to Guthega. No.1 & No2 Pumps at Jyndabyne tripped also, interrupting 70MW of pumping load. Storms in the area. At 1939hrs CB9792 was closed at Guthega via SCADA, restoring |  | External | [5 empty] | 0 | 0 | 2011
1873 | 93543 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0045 | 97G/1 Geehi Tee CB 97G2 | Z | 2011Q1 | MUR |  | CB | 2011-01-22 20:28 | 2011-01-22 21:14 | [11 empty] | 0 | 0 | 2011
913 | 62444 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2011-E-0001 | No.3 Capacitor | E | 2011Q1 | SYN |  | CAP | 2011-01-26 12:05 | 2011-01-26 12:51 | Made unavailable, Isolated to allow top up of CB4732 White phase SF6. Capacitor Available for service 1251hrs |  |  | Low SF6 White phase SF6. |  | Oil/Gas Levels | [5 empty] | 0 | 0 | 2011
914 | 62446 | Animal/Bird | Animal/Bird | TRUE | Cap |  |  |  | 2011-F-0046 | No.1 Capacitor | Z | 2011Q1 | SYN |  | CAP | 2011-01-26 17:01 | 2011-01-26 19:27 | Dead crow found on ground, area of contact healthy. No.1 Cap placed I/S 1927 hrs |  |  | Dead crow found on ground, area of contact healthy. | Very Hot | External | [5 empty] | 0 | 0 | 2011
1783 | 62461 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0047 | 96R Glen Innes - Tenterfield 132kV TL | Z | 2011Q1 | GNS, TTF |  | TL | 2011-01-27 13:11 | 2011-01-27 13:11 | Tripped during thunderstorm Indji shows only one stroke 14.9km from Glenn Innes, Prot flags added and CB ammended, No 2 Tx RTS, 1618 when staff arrived. | None ¦ The suspect fault has been noted for next scheduled patrol of the line. |  | Tripped during thunderstorm Indji shows only one stroke 14.9km from Glenn Innes. Major road crossings between structures 33 – 34, 76 – 77 and 80 – 81 of the line, visually inspected on the 01/02/11 have indicated no evidence of any damage. | [7 empty] | 0 | 0 | 2011
1784 | 62466 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0048 | 96M Narrabri - Moree 132kV TL | Z | 2011Q1 | MRE, NB2 |  | TL | 2011-01-27 20:23 | 2011-01-27 20:23 |  | None ¦ The fault has been noted for the next scheduled patrol of the line. |  | 98% of the line and the only road crossing at Moree end are strung with synthetic insulators and hence as per policy no immediate patrol of the line is required. | Thunderstorm | [6 empty] | 0 | 0 | 2011
1785 | 62523 | Unknown | Unknown | TRUE | TX |  |  |  | 2011-F-0053 | No.2 Transformer 330/132/11kV | Z | 2011Q1 | SYS |  | TX | 2011-01-31 13:38 | 2011-01-31 15:30 | Gas and Pumps tested all ok. RTS @ S. Singh request 1530hrs |  |  | Gas and Pumps tested all ok. RTS @ S. Singh request 1530hrs | [7 empty] | 0 | 0 | 2011
1786 | 62526 | Unknown | Unknown | TRUE | Prot |  |  |  | 2011-F-0055 | 237 Sydney West - ONESTEEL 132kV Line | Q | 2011Q1 | SYW |  | TL | 2011-02-01 01:49 | 2011-02-01 01:49 | Protection to follow up as has tripped on 2 occasions recently. |  |  | Protection to follow up as has tripped on 2 occasions recently. It is believed that the relay operated due to the Arc Furnace producing a distorted waveform. Protection Design and the relay manufacturer are still unable to find a definite cause for the r | Fine | [6 empty] | 1 | 0 | 2011 | Incorrect protection settings
919 | 62527 | HV Equipment | HV Equipment Failure | TRUE | Cap |  |  |  | Not Available | No.3 Capacitor | Z | 2011Q1 | DNT |  | CAP | 2011-02-01 10:46 | 2011-02-01 13:22 |  |  |  | Substation Misc. Equip Fail. Capacitor tripped on closing. request staff to attend 19:05 31/01/2011, F, CE/Staff, Laurie Bullock. No.3 Capacitor Prot'n Flags. No.1 Prot'n. Multitrip. No.2 Prot'n. Blue Phase 50N Trip. Reset. On Call Engineer messaged, Requ |  | Secondary Equipment | [5 empty] | 0 | 0 | 2011
1787 | 63440 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0067 | 977/1 Canberra - Queanbeyan 132kV TL | Z | 2011Q1 | CA1, SPR, QBY |  | TL | 2011-02-02 14:38 | 2011-02-03 11:55 | Line patrolled & no cause located, RTS 12:55hrs 3.2.2011. | N/A ¦ No further action is deemed neccessary. |  | Line patrolled & no cause located, storms in area. | Thunderstorm | [6 empty] | 0 | 0 | 2011
1809 | 65278 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0112 | 991 Wagga 132 - Murrumburrah 132kV TL | Z | 2011Q1 | MRU, WG2 |  | TL | 2011-02-04 15:58 | 2011-02-04 15:58 | Storms in area. | N/A ¦ Noted for the next scheduled aerial patrol. |  | Storms in the area. Line inspected between structure 280 to 330 for any obvious signs of insulator and conductor damage. Scheduled for next aerial patrol. | Thunderstorm | [6 empty] | 0 | 0 | 2011
1788 | 63524 | Staff Error | Unknown | TRUE | Prev |  |  | Lost load 20MW | 2011-F-0070 | 999 Yass - Cowra 132kV TL | C | 2011Q1 | CW2, YSN |  | TL | 2011-02-05 18:45 | 2011-02-07 15:08 | TARTLO @ Cowra. Refer Northern Ops Log. Left energised from Yass. Placed on load at Cowra on 7/2 at 15:08hrs EST | N/A ¦ No further action is deemed neccessary. |  | TThe trip wire for 999 No.2 protection was found to have been disconnected and pushed in behind the wiring loom between the 999 prot panels and the adjacent No.3 Tx panel. It is surmised that when contractors installed the No.3 Tx panel in Nov 2009, the 9 | Unknown | [6 empty] | 1 | 1 | 2011 | Incorrect isolation caused by technician dislodging trip wire, causing an incorrect protection operation
1798 | 63588 | Staff Error | Sec Eqt Staff Error | TRUE | Prev |  |  | Lost Load 18MW | 2011-F-0074 | 94U Parkes - Forbes 132kV TL | Z | 2011Q1 | FB2, PKS |  | TL | 2011-02-05 18:45 | 2011-02-05 20:59 | [11 empty] | 0 | 0 | 2011 | Emergency outage caused by forced outage of line 999, to prevent thermal overload on 94U
1874 | 93547 | Lightning/Storm | Unknown | TRUE | TL |  |  |  | 2011-F-0070 | 999 Yass CB 9992 | Q | 2011Q1 | CW2 |  | CB | 2011-02-05 19:45 | 2011-02-05 19:45 |  |  |  | TL tripped and autoreclosed at Yass SS, while it locked out at the Cowra SS. Lightning was observed in the area of the fault at the time of trip. | [7 empty] | 0 | 0 | 2011
1801 | 63736 | HV Equipment | HV Equipment Failure | TRUE | CBOil |  |  |  | 2011-F-0077 | No.2 Capacitor | Q | 2011Q1 | NB2 |  | CAP | 2011-02-07 14:34 | 2011-02-10 16:22 | Available 1722 hrs on 10/02/11. | NIL ¦ NIL |  | Advises 11kV CB Tripped Alarm at site plus protection flagging (NO alarms received on SCADA). BU alarms working OK. Obvious broken insulator. G.McIllveen advised. | Fine | [6 empty] | 0 | 0 | 2011
2241 | 15 | HV Equipment |  | TRUE | CB SF6 |  |  |  | IR7133 | CB 372B |  | 2011Q1 | KCR |  |  | 2011-02-08 00:34 | 2011-02-08 02:04 |  |  |  | 00:34 08/02/2011, F, SSO, K. Haigh Advised Red Phase CB 372B Low SF6 02:04 08/02/2011, F, SSO, K. Haigh Topped Up Ok Returned to Service | [7 empty] | 0 | 0 | 2011
1802 | 63796 | HV Equipment | Unknown | TRUE | CB SF6 |  |  |  | 2011-E-0002 | No.1 Transformer 330/132/11kV | E | 2011Q1 | LSM |  | TX | 2011-02-12 11:09 | 2011-02-12 11:57 | Investigation of CB 5412 abnormal alarm revealed low SF6 pressure B phase. No.1 TX off loaded and CB 5412 open & isolated for repairs. | None ¦ Monitor the SF6 gas levels in the circuit breaker and replace the gauge. |  | Preliminary investigations revealed low SF6 gas levels in the white phase of the circuit breaker (not the blue phase as indicated in the FEOR) and leakage of gas around spigot of the gauge on the circuit breaker. Further investigations has indicated that | [7 empty] | 0 | 0 | 2011
1804 | 63932 | Staff Error | Sec Eqt Staff Error | TRUE | Prev |  |  |  | 2011-F-0085 | Phase Shifting Transformer | L | 2011Q1 | AR1 |  | TX | 2011-02-18 06:57 | 2011-02-18 07:00 | PST TX / 965 TL offloaded. Restoration @ 0700 hrs EST. | Refer to the report on the incident. |  | A separate report that includes action items has been written on the incident by the Manager Technical Services. | Fine | [6 empty] | 1 | 1 | 2011 | Opslog indicates incorrect isolation due to wrong link opened, leading to incorrect protection operation, exerpt: "wrong linked opened..."
1805 | 64042 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | SVC |  |  |  | 2011-F-0087 | No.1 Static VAR Compensator | Z | 2011Q1 | AR1 |  | SVC | 2011-02-19 17:55 | 2011-02-19 20:27 | Cooling pumps changed over resulting in the o/s pump failing to start, call out staff manually started pump and SVC was RTS. | 186866 ¦ None ¦ NIL |  | Cooling pumps changed over resulting in the o/s pump failing to start, call out staff manually started pump and SVC was RTS. | Fine | [6 empty] | 0 | 0 | 2011
2240 | 14 | Unknown |  | TRUE | TX |  |  |  | IR7183 | No.1 Transformer 132/66/11kV |  | 2011Q1 | TA2 |  |  | 2011-02-20 23:09 | 2011-02-21 13:41 |  |  |  | Advises No.1 TX tripped on 11kV Neutral Earth Fault (D44 & CA01). No sign of debris/ animal around visible section of conductor. Advised. Will look at testing No.1 TX 11kV cable tomorrow. | [7 empty] | 0 | 0 | 2011
939 | 64174 | HV Equipment | Unknown | TRUE | Cap |  |  |  | 2011-F-0091 | No.2 Capacitor | Q | 2011Q1 | YA2 |  | CAP | 2011-02-22 06:17 | 2011-02-25 10:20 | C.E. staff advised found blown fuse. Possible fuse fatigue. Can fuse replaced. Cap tested & avail for service @ 1020 HRS on 25/2/2011 | 2/05/2012 9:15:00 AM |  | No2 Capacitor tripped at Yanco substation due to a blown fuse. The capacitor has been isolated pending further repairs. |  | Primary Equipment | [5 empty] | 0 | 0 | 2011
1806 | 64443 | Tree/Ground | Tree/Ground | TRUE | TL |  |  |  | Not available | 96G Pt Macquarie - Kempsey 132kV TL | C | 2011Q1 | KS2, PMQ |  | TL | 2011-03-01 17:18 | 2011-03-01 22:46 | [5 empty] | External | [5 empty] | 0 | 0 | 2011
1807 | 64446 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2011-E-0003 | No.4 Bay Coupler CB 6042 | Q | 2011Q1 | ER0 |  | CB | 2011-03-01 21:59 | 2011-03-01 23:23 | CB taken out of service to top up with SF6. RTS @ 2323 hrs EST. |  |  | CB taken out of service to top up with SF6. RTS @ 2323 hrs EST. | Fine | [6 empty] | 0 | 0 | 2011
1808 | 65183 | Lightning/Storm | Unknown | TRUE | TL |  |  |  | 2011-F-0107 | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Z | 2011Q1 | AR1, COF |  | TL | 2011-03-02 19:08 | 2011-03-02 19:09 | Storms in area Protection details added. Armidale DTF 49.9km Coffs Harbour DTF 93.5km | None. ¦ Fault noted for inspection during the next scheduled patrol of the line. |  | Storms in area. Protection Flagging indicated fault 49.7kms from Armidale end that works out to be around Structure 233 of the line. Indji system has indicated that there were lightning strikes near Structures 223 and 225 of the line. There are no major r | Thunderstorm | [6 empty] | 0 | 0 | 2011
1811 | 65522 | Instruction Error | Unknown | TRUE | Proc |  |  |  | 2011-F-0114 | No.2 Transformer 132/66/11kV | Z | 2011Q1 | NAM |  | TX | 2011-03-10 09:08 | 2011-03-10 09:14 | Possible operation of protection relay during planned manintenance. |  |  | Possible operation of protection relay during planned maintenance. The PMWI being used did not include isolation of direct tripping from the protection relay. In-service testing of the relay then caused the CB's to trip, offloading the transformer. | [7 empty] | 0 | 1 | 2011 | Incorrect isolation, protection operated during testing
1810 | 65517 | HV Equipment | HV Equipment Failure | TRUE | Rx |  |  |  | 2011-F-0113 | No.1 330kV Reactor | Z | 2011Q1 | AR1 |  | RX | 2011-03-10 11:54 |  | Local indication hot oil temp = 60 Deg cel., Hot Wdg = 97 deg cel. Local observation of reactor leaking oil from neutral bushing lid and conservator pipework. Oil spill contained & oil circulation pipework isolated. No report of personal or environmental | None ¦ Investigate and establish the possible cause of the failure of the Reactor. |  | Reactor make Parsons Peebles, year of manufacture 1975 failed internally and tripped. The failure caused a rupture of the 25mm equalising pipe at the top of the tank, and damaged the neutral bushing. This resulted in spilling of oil from the Conservator a | [7 empty] | 0 | 0 | 2011
1814 | 65654 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0125 | 8 Marulan - Dapto 330kV TL | Z | 2011Q1 | DPT, MRN |  | TL | 2011-03-12 16:02 | 2011-03-12 16:02 | [5 empty] | External | [5 empty] | 0 | 0 | 2011
1815 | 65734 | HV Equipment | HV Equipment Failure | TRUE | T/C |  |  |  | 2011-F-0127 | No.1 Transformer 330/132/11kV | Z | 2011Q1 | NEW |  | TX | 2011-03-16 07:40 | 2011-03-16 13:23 |  | 1. Replace the Tap Changer Overpressure Switch and restore the pressure switch trip links. 2. Check and correctly wire the Overpressure Switch on all the similar Units. 3. Technical Services should arrange the functional testing of the Overpressure Switch |  | Wednesday 16/03/2011 At 07:40hrs Newcastle No.1 Transformer tripped. No supply interruption. Newcastle No.4 Transformer was out of service for planned work, it has been recalled. 96G Port Macquarie to Kempsey 132kV T/L was out of service for planned work, | Fine | [6 empty] | 0 | 0 | 2011
1816 | 65794 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2011-E-0004 | No.2 Transformer 132kV A Bus CB 4422A | Q | 2011Q1 | NEW |  | CB | 2011-03-17 01:49 | 2011-03-17 03:00 | Taken O/S to top up low SF6 - Returned to service at 0400 HRS (DST) |  |  | Taken O/S to top up low SF6 | Rain | [6 empty] | 0 | 0 | 2011
1817 | 65812 | Unknown | Unknown | TRUE | TL |  |  |  | 2011-F-0129 | 994 Wagga 330 - Yanco 132kV TL | Z | 2011Q1 | WG1, YA2 |  | TL | 2011-03-17 07:24 | 2011-03-17 07:24 |  | N/A ¦ This has been noted for the next schedule aerial patrol. |  | This has been noted for the next schedule aerial patrol. | Fine | [6 empty] | 0 | 0 | 2011
2239 | 13 | Unknown |  | TRUE | TX |  |  |  | S 1 | No.1 Transformer 330/132/11kV |  | 2011Q1 | NEW |  |  | 2011-03-17 17:33 | 2011-03-17 21:48 |  |  |  | At 17:33hrs Newcastle No.1 Transformer tripped.. After inspection the transformer was returned to service at 2148hrs | [7 empty] | 0 | 0 | 2011
2238 | 12 | Unknown |  | TRUE | TX |  |  |  | SI 1 | No.1 Transformer 330/132/11kV |  | 2011Q1 | NEW |  | TX | 2011-03-18 10:35 | 2011-03-19 20:20 |  |  |  | 10:35 18/03/2011 No.1 Transformer at Newcastle tripped. Cause of trip is unknown. However, the same transformer tripped in a similar fashion yesterday. Attempts are being made to recall 96G Port Macquarie to Kempsey 132kV T/L. No load lost at this stage. | [7 empty] | 0 | 0 | 2011
2237 | 11 | HV Equipment |  | TRUE | CVT |  |  | no outage in Theos | IR 7284 | 968 Tamworth 330 - Narrabri 132kV TL |  | 2011Q1 | NB1 |  |  | 2011-03-21 15:19 | 2011-03-22 14:53 |  |  |  | "15:19 21/03/2011, F, Manager, G Francis Advised red phase sight glass leaking oil on CVT. Requires O/S for replacement tomorrow. NCM advised. Taken off the system @ 1519hrs. Essential Energy (Peter) advised tat there are no 66kV parallels between Tamwort | [7 empty] | 0 | 0 | 2011
1818 | 66107 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2011-E-0005 | No.2 Generator 330kV CB 5222 | Q | 2011Q1 | ER0 |  | CB | 2011-03-26 21:17 | 2011-03-26 23:31 | C.B.. 5222 taken out of service to top up low SF6 - RTS at 0031 HRS 27/03/11 |  |  |  | Mild | [6 empty] | 0 | 0 | 2011
1819 | 66219 | Unknown | Unknown | TRUE | TL |  |  |  | 2011-F-0134 | 990 Yass - Wagga 132 132kV TL | Z | 2011Q1 | WG2, YSN |  | TL | 2011-03-29 17:17 | 2011-03-29 18:00 | CB tripped through after closing via Scada 29/03/11 17:17 EST. Line was live in from Wagga 132. CB 9902 Closed after inpection 1800hrs EST. Note- Not all fields auto-filled |  |  |  | Fine | [6 empty] | 0 | 0 | 2011
1820 | 66373 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0140 | 9U2 Inverell - Moree 132kV TL | Z | 2011Q2 | INV, MRE |  | TL | 2011-04-01 20:15 | 2011-04-01 20:15 |  | NONE ¦ Close insoection of the area around structures 240 and 244 during the next scheduled aerial patrol of the line. |  | Close insoection of the area around structures 240 and 244 during the next scheduled aerial patrol of the line. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
1821 | 67023 | Unknown | Unknown | TRUE | TL |  |  |  | 2011-F-0142 | 944 Wallerawang 132 - Orange 132kV TL | Z | 2011Q2 | ORG, WW2, ONO |  | TL | 2011-04-02 11:28 | 2011-04-02 11:28 |  | The incident has been noted for the next scheduled aerial and ground line patrols of this line. |  | The incident has been noted for the next scheduled aerial and ground line patrols of this line. | Mild | Unexplained | [5 empty] | 0 | 0 | 2011
1822 | 67025 | Lightning/Storm | Unknown | TRUE | SVC |  |  |  | 2011-F-0144 | No.1 Static VAR Compensator | Z | 2011Q2 | LSM |  | SVC | 2011-04-02 18:35 | 2011-04-03 12:42 |  | Action is in hand to plan the testing of the Displacement relays to confirm the correct setting parameters. |  | Visual identified no obvious faults. The Lismore SVC was returned to service. Investigations of the incident reveal that the sequence of events on the SVC Control HMI shows that the No.2 Neutral Displacement relay operated to trip the SVC, and later the N | Thunderstorm | [6 empty] | 1 | 0 | 2011 | QAPR report indicates incorect operation of protection relays
1823 | 67026 | Relay | Unknown | TRUE | Prot |  |  |  | 2011-F-0145 | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Z | 2011Q2 | AR1, COF |  | TL | 2011-04-03 09:51 | 2011-04-03 12:42 |  |  |  | CB opened at Armidale only. The conditions were not met for an Auto reclose at Armidale as the incoming volts were 141kV whilst the Bus volts were 132kV. Appears to be a relay fault (OH1-311). Refer to outage 70908 below for follow-up. Relay sent to man | [7 empty] | 1 | 0 | 2011 | Faulty protection relay
1824 | 67077 | Relay | Unknown | TRUE | Prot |  |  |  | 2011-F-0146 | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Z | 2011Q2 | AR1, COF |  | TL | 2011-04-04 12:59 | 2011-04-04 13:02 | Suspect faulty relay. | None ¦ Investigate the faulty relay for possible cause the failure of the relay. |  | Initial investigations indicated the No1 protection Ohmega relay faulty. The line returned to service with only No2 protection in service. Following replacement of the faulty relay No1 protection was returned to service. The suspected faulty relay is be | [7 empty] | 1 | 0 | 2011 | Faulty protection relay
2054 | 8 | Switching error |  | TRUE | TL |  |  |  | SI | TL 965 | q | 2011Q2 | KS2 |  | TL | 2011-04-11 16:07 | 2011-04-11 16:16 |  |  |  | At 16:07hrs 965 Armidale to Kempsey 132 kV T/L was off loaded when staff inadvertently opened CB 9652 at Kempsey. SCADA was down at the time. The feeder was placed back on load at 1616hrs when SCADA became available again. There was no load interrupted or |  |  | Northern | 132 | Emergency |  |  | 0 | 1 | 2011 | Incorrect switching
1825 | 67249 | HV Equipment | HV Equipment Failure | TRUE | CB |  |  |  | 2011-E-0008 | No.4 Bay Coupler CB 6042 | Q | 2011Q2 | ER0 |  | CB | 2011-04-12 01:35 | 2011-04-12 03:20 | CB 6042 low SF6 condition. Isolated, topped up & RTS. |  |  | CB 6042 low SF6 condition. Isolated, topped up & RTS. Leak identification required (2 top ups since) FA4 | Fine | [6 empty] | 0 | 0 | 2011
1826 | 67250 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2011-E-0007 | No.2 Capacitor | Q | 2011Q2 | KS2 |  | CAP | 2011-04-12 03:33 | 2011-04-12 04:31 | CB 2822 low SF6 condition. Isolated, topped up & made available. |  |  | CB 2822 low SF6 condition. Isolated, topped up & made vailable. Region to arrange leak identification - one top up. | Fine | [6 empty] | 0 | 0 | 2011
1827 | 67366 | Design Ommission | Sec Eqt Malfunction | TRUE | Proc |  |  |  | 2011-E-0009 | 330kV C Bus | Q | 2011Q2 | CWF |  | BB | 2011-04-13 18:18 | 2011-04-14 00:32 | On energizing noticed smoke coming from CVT secondary kiosk. Bus de-energized . Isolation point damaged. RTS following checks and repairs 0032hrs 14/4/11 | 9/09/2011 11:07:00 AM |  | On energizing noticed smoke coming from CVT secondary kiosk. Bus de-energized . Isolation point damaged. RTS following checks and repairs 0032hrs 14/4/11. Drawings marked up. A new additional LV Marshalling Box was wired into the 330kV C Bus CVT to prov | [7 empty] | 0 | 0 | 2011 | Incorrect CVT earthing caused trip, not protection system
1829 | 67382 | Staff Error | LV/MECH/PROT Equipment Fail | TRUE | Prev |  |  |  | 2011-F-0153 | 9J2 Sydney West - Blacktown 132kV Line | Q | 2011Q2 | SYW |  | TL | 2011-04-14 10:46 | 2011-04-14 11:11 | Consequential outage. Refer to FEOR 2011-F-0152 (132kV B Bus No.1 Section) |  |  | "Commissioning checks being carried out on new 93J Camellia No.1 Protection. CBF operation occurred in Reyrolle Ohmega relay. CBF Trip link fitted to 93J No.1 Protection Panel incorrectly assembled by manufacturer and was electrically closed when link pla | Fine | [6 empty] | 1 | 0 | 2011 | Protection panel wiring error
1830 | 67523 | Unknown | Unknown | TRUE | TL |  |  |  | 2011-F-0157 | 976/1 Canberra - Queanbeyan/Spring Flat 132kV TL | Z | 2011Q2 | QBN |  | TL | 2011-04-19 06:27 | 2011-04-19 06:27 |  | N/A ¦ This has been noted for the next scheduled aerial patrol. |  | "Protection at both Substation detected a blue phase to earth fault. A patrol was carried on the 976/1 TL between structures 285 to 303 on the 19/04/2011. No irregularities were found. Scheduled for next aerial patrol." | Fog | [6 empty] | 0 | 0 | 2011
1831 | 67721 | Unknown | Unknown | TRUE | TL |  |  |  | 2011-F-0159 | 9U3 Gunnedah - Narrabri 132kV TL | Z | 2011Q2 | GN2, NB2 |  | TL | 2011-04-24 05:14 | 2011-04-24 05:14 | No storm activity apparent in vicinity of line at time of tripping. Point of fault was 47% x 100 klm line, patrolled from Narrabri to fault point + 70 structures towards Gunnedah and found no problems, patrolman advised line is presently under going plann |  |  | "No storm activity apparent in vicinity of line at time of tripping. Point of fault was 47% x 100 klm line, patrolled from Narrabri to fault point + 70 structures towards Gunnedah and found no problems, patrolman advised line is presently under going plan | Fine | [6 empty] | 0 | 0 | 2011
1832 | 67766 | Unknown | Unknown | TRUE | TL |  |  |  | 2011-F-0166 | 99F Uranqunity - Yanco 132kV TL | Z | 2011Q2 | YA2, URQ |  | TL | 2011-04-28 10:14 | 2011-04-28 10:14 |  | N/A ¦ This has been noted for the next scheduled aerial patrol. |  | A patrol was carried out between structures 125 to 180. It was found that between structures 147 to 149, 155 to 157 and 153 to 154 stubble had been burnt off which may have caused the trip. | Fine | [6 empty] | 0 | 0 | 2011
1833 | 67848 | Secondary Equipment | Sec Eqt Malfunction | TRUE | SVC |  |  |  | 2011-F-0168 | No.1 Static VAR Compensator | Z | 2011Q2 | BKH |  | SVC | 2011-04-29 10:36 | 2011-04-29 14:19 | Tripped simultaneously with No.3 South Feeder fault FEOR 2011-F-0167. SVC tripped due to Cooling water pump supply fault when Feeder fault occurred . |  |  | Tripped simultaneously with No.3 South Feeder fault FEOR 2011-F-0167. SVC tripped due to Cooling water pump supply fault when Feeder fault occurred. | Fine | [6 empty] | 0 | 0 | 2011
1834 | 68850 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2011-E-0010 | 5A2 Kemps Creek 500kV CB 5A22 | Q | 2011Q2 | ER0 |  | CB | 2011-05-04 23:13 | 2011-05-05 00:54 | Taken O/S at 2313 on 4/5/11 to top up White phase SF6. Returned to service at 0054 on 5/5/11 |  |  | Taken O/S at 2313 on 4/5/11 to top up White phase SF6. Returned to service at 0054 on 5/5/11. Leak located as B Ph line side density monitor o ring and repaired 15/9/10 but still leaking. Need to leak check again. FA4 | Mild | [6 empty] | 0 | 0 | 2011
2051 | 6 | HV Equipment |  | TRUE | CB SF6 |  |  |  | IR7455 | CB 5222 | q | 2011Q3 | ER0 | Plant (Subs) |  | 2011-05-06 05:48 | 2011-05-06 11:19 |  |  |  | Alarm received on SCADA - CB 5222 opened pending investigation. Taken O/S due to SF6 depleted alarm. AEMO adv per Opps Log. Monitor. Leak check planned. |  | Oil/Gas Levels | Northern | 330 | Emergency |  |  | 0 | 0 | 2011
1835 | 68972 | Secondary Equipment | LV/MECH/PROT Equipment Fail | TRUE | SVC |  |  |  | 2011-F-0173 | No.1 Static VAR Compensator | Z | 2011Q2 | BKH |  | SVC | 2011-05-06 12:55 | 2011-05-06 14:08 | SVC tripped @ same time as South Feeder (CB 32). Refer FEOR 2011-F-0171 for additional details. |  |  | SVC tripped @ same time as South Feeder (CB 32). Refer FEOR 2011-F-0171 for additional details. |  | Secondary Equipment | [5 empty] | 0 | 0 | 2011 | Unknown reason for SVC trip, no further info in QAPR/THEOS/Opslog
1836 | 68994 | Secondary Equipment | Sec Eqt Malfunction | TRUE | SVC |  |  |  | 2011-F-0175 | No.1 Static VAR Compensator | Z | 2011Q2 | BKH |  | SVC | 2011-05-07 10:12 | 2011-05-07 11:36 | SVC Tripped simultanously with South Feeder fault - refer FEOR 2011-F-0174. SVC RST 1136hrs |  |  | SVC Tripped simultanously with South Feeder fault - refer FEOR 2011-F-0174. SVC RST 1136hrs | Fine | Secondary Equipment | [5 empty] | 0 | 0 | 2011 | Unknown reason for SVC trip, no further info in QAPR/THEOS/Opslog
2052 | 69102 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2011-E-0011 | No.2 Capacitor | Q | 2011Q2 | TRE |  | CAP | 2011-05-10 10:07 | 2011-05-10 12:23 | CB taken out of service, topped up with SF6 (W phase low) & made available. |  |  | CB taken out of service, topped up with SF6 (W phase low) & made available. Has had repeated leaks. Filling point repaired in 2009. OSX36 | Rain and Very Windy | [6 empty] | 0 | 0 | 2011
1837 | 69117 | Fire | Unknown | TRUE | TL |  |  |  | 2011-F-0178 | 62 Wagga 330 - Jindera 330kV TL | Z | 2011Q2 | JDA, WG1 |  | TL | 2011-05-10 16:04 | 2011-05-10 16:04 | Significant hazard reduction burns in Jindera area at time of TAR. | N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Significant hazard reduction burns in Jindera area at time of TAR. A patrol of the 62 T/L from Str 196-171 found no damage or any indication of what could have caused the trip and reclose. However the property owners have recently burnt stubble paddocks o | Fine | [6 empty] | 0 | 0 | 2011
2055 | 9 | Protection |  | TRUE | Prot |  |  |  | SI | TL 990 | q | 2011Q2 | YS1 |  | TL | 2011-05-11 16:29 | 2011-05-11 17:35 |  |  |  | "Tripped on closing while attempting to restore the 132kV system between Yass and Wagga after an outage of 991 Wagga North to Murrumburrah T/L. After analysing protection details at Yass and as 990 T/L was still energised from Wagga132. Investigations fo |  | Secondary Equipment | Southern | 132 | Forced |  |  | 1 | 0 | 2011 | QAPR report indicates incorrect protection settings
1838 | 69499 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2011-E-0012 | 914 Sydney South - Bankstown 132kV Line | Q | 2011Q2 | SYS |  | TL | 2011-05-21 15:28 | 2011-05-21 16:15 | Top up low SF6. RTS 1615hrs |  |  | Top up low SF6. RTS 1615hrs. CB leak has been found, needs a complete pole replacement. Awaiting refurbished poles from ABB to action - defect in place. ABB LTB CB |  | Oil/Gas Levels | [5 empty] | 0 | 0 | 2011
1839 | 69503 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0183 | 99F Uranqunity - Yanco 132kV TL | Z | 2011Q2 | YA2, URQ |  | TL | 2011-05-22 16:53 | 2011-05-22 16:53 | Electrical Storms in Area |  |  | Electrical Storms in Area | [7 empty] | 0 | 0 | 2011
1840 | 69508 | Lightning/Storm | Unknown | TRUE | TL |  |  |  | 2011-F-0188 | 9U3 Gunnedah - Narrabri 132kV TL | Z | 2011Q2 | GN2, NB2 |  | TL | 2011-05-23 13:12 | 2011-05-23 13:12 | Flags found when Protection staff on site today Thunderstorms overnight, but unable to find time of trip on SCADA , local HMI or Narrabri end. |  |  | "Flags found when Protection staff on site today Thunderstorms overnight, but unable to find time of trip on SCADA , local HMI or Narrabri end." | [7 empty] | 0 | 0 | 2011
2056 | 10 | Relay |  | TRUE | Prot |  |  |  | IR7529 | CB O825 | q | 2011Q3 | KLK |  | CB | 2011-05-24 14:47 | 2011-05-24 14:47 |  |  |  | "Advised fault with No.2 protection relay cause of trip. Advised replacement relay not on site. Anticipated repair 1000 25/05/11. 0825 Fdr left in service on No.1 protection only after EsE (Bob Sullivan) request under current system conditions. (Within g |  | Primary Equipment | Northern | 66 | Forced |  |  | 1 | 0 | 2011 | Faulty protection relay
1841 | 69639 | HV Equipment | Sec Eqt Malfunction | TRUE | CB SF6 |  |  |  | 2011-E-0013 | No.3 Bay Coupler CB 5032 | Q | 2011Q2 | KCR |  | CB | 2011-05-27 07:33 | 2011-05-27 08:37 | Low SF6 on CB. Taken out of service to top up. |  |  |  | Fine | [6 empty] | 0 | 0 | 2011
1842 | 69697 | Animal/Bird | Unknown | TRUE | TL |  |  |  | 2011-F-0191 | 5A3 Bayswater - Mt Piper 500kV TL | Z | 2011Q2 | BAY, MTP |  | TL | 2011-05-29 03:29 | 2011-05-29 03:29 |  |  |  | Bird droppings have caused trip and auto-reclose events on this line in the past. The travelling wave fault locator identified this trip to be at structure 193. A climbing inspection was carried out 10/6. No nests were present in the tower, and a hole i | [7 empty] | 0 | 0 | 2011
1843 | 69852 | Secondary Equipment | Sec Eqt Malfunction | TRUE | SVC |  |  |  | 2011-F-0194 | No.1 Static VAR Compensator | Z | 2011Q2 | SYW |  | SVC | 2011-05-31 19:44 | 2011-06-01 16:05 | At time of trip staff were investigating cooling system fault alarm. Make up water pressure was varying between high & low. Pressure was low at time of trip. RTS @ 1605 1/06/2011 |  |  | At time of trip staff were investigating cooling system fault alarm. Make up water pressure was varying between high & low. Pressure was low at time of trip. RTS @ 1605 1/06/2011 | Rain | [6 empty] | 0 | 0 | 2011
1844 | 70341 | Wiring Error | Non TransGrid Reason | TRUE | Prev |  |  |  | 2011-F-0197 | 79F Griffith - Yenda 33kV Line | S | 2011Q2 | GRF |  | TL | 2011-06-02 22:36 | 2011-06-02 23:45 | Feeder energised at 23:45hrs. Load restored by 23:59hrs. |  |  | "Work has been carried out on 33kV Bus No.1 Section, planned outage 65145 1/6 to 2/6. When feeder returned to service and only winery loads restored on feeder. Investigations found that a loose connection in the Bus VT kiosk was the cause of the problem. | [7 empty] | 1 | 0 | 2011 | Loose VT secondary protection wiring
1845 | 70801 | Wiring Error | Unknown | TRUE | Prev |  |  |  | 2011-F-0198 | 79F Griffith - Yenda 33kV Line | S | 2011Q2 | GRF |  | TL | 2011-06-03 06:30 | 2011-06-03 08:16 | When feeder returned to service and only winery loads restored on feeder. |  |  | "Work has been carried out on 33kV Bus No.1 Section, planned outage 65145 1/6 to 2/6. When feeder returned to service and only winery loads restored on feeder. Investigations found that a loose connection in the Bus VT kiosk was the cause of the problem. | Fine | [6 empty] | 1 | 0 | 2011 | Loose VT secondary protection wiring
2053 | 7 | HV Equipment |  | TRUE | CB SF6 |  |  |  | OP Log Event 1553610 | CB 9J22 | q | 2011Q2 | SYW |  | CB | 2011-06-03 13:07 | 2011-06-03 14:13 |  |  |  | "3:33hrs Advised by Paul Williams LV CB Abnormal alarm is C.B.. 9J22 low SF6 white phase, requires to be topped up. Advised OK, advised SO/E.E. (Gary Carter) & C/T off-load. Confirmed Blacktown 132kV Bus solid. NCM advised & PRI prepared to top up SF6 gas |  |  | Central | 132 | Emergency |  |  | 0 | 0 | 2011
1846 | 70802 | Wiring Error | Unknown | TRUE | Prev |  |  |  | 2011-F-0199 | 79F Griffith - Yenda 33kV Line | S | 2011Q2 | GRF |  | TL | 2011-06-03 14:51 | 2011-06-03 23:09 | Attempt to close feeder @ 1542 and feeder tripped on closing. No.1 Protection R-E (Q11) and W-E (Q21) flags. Subsequent checks found discrepencies with V.T. Supply voltages to 79F Yenda No.1 Protection and 79C Darlington Point No.1 Protection. Voltages re |  |  | "Work has been carried out on 33kV Bus No.1 Section, planned outage 65145 1/6 to 2/6. When feeder returned to service and only winery loads restored on feeder. Investigations found that a loose connection in the Bus VT kiosk was the cause of the problem. | Fine | [6 empty] | 1 | 0 | 2011 | Loose VT secondary protection wiring
1849 | 70982 | Damaged Cable | HV Maintenance | TRUE | Prev |  |  |  | 2011-F-0209 | M7 Murray - Murray 1 330kV TL | Z | 2011Q2 | MUR |  | TL | 2011-06-04 17:41 | 2011-06-04 18:16 | M7 Murray to Murray 1 PS T/L was energised via 330kV A2 Bus with CBM72 closed, (due to issue with CBM72 & with SHL clearance to do so) CBM72 tripped, no apparent surge. SHL confirmed Tx prot. had operated, no issue with Tx & requested now CBM72 open if co |  |  | "Tripped when the Murray A2 330kV Bus section was energised via CB5102. (CBM72 had been left closed due to operational restrictions). The bus did not trip. No surge. Investigations found the CT cable form the white phas CT and the CT marshalling box had b | Mild | [6 empty] | 1 | 0 | 2011 | QAPR report indicates damaged CT marshalling box (which contains protection wiring)
1850 | 70983 | Damaged Cable | LV/MECH/PROT Equipment Fail | TRUE | Prev |  |  |  | 2011-F-0210 | M7 Murray - Murray 1 330kV TL | Z | 2011Q2 | MUR |  | TL | 2011-06-04 18:19 | 2011-06-05 15:36 |  |  |  | "Tripped when the Murray A2 330kV Bus section was energised via CB5102. (CBM72 had been left closed due to operational restrictions). The bus did not trip. No surge. Investigations found the CT cable form the white phas CT and the CT marshalling box had b | Mild | [6 empty] | 1 | 0 | 2011 | QAPR report indicates damaged CT marshalling box (which contains protection wiring)
1847 | 70943 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2011-E-0014 | 5A1 Eraring A CB 5A12A | Q | 2011Q2 | KCR |  | CB | 2011-06-05 09:18 | 2011-06-05 11:17 | Low SF6. Topped up and RTS at 11:17hrs. | 1/09/2011 12:10:00 PM ¦ Nil ¦ Replacement of Blue phase closing resistor TBA & re-investigation of Red phase CB pole. |  | Low SF6. Topped up and RTS at 11:17hrs. Blue phase had an SF6 top-up in April and Red phase closing resistor was found to be leaking - replaced in June 2011. Work Order raised to investigate leaks. No leak could be detected on Red phase but a leak was det | Fine | [6 empty] | 0 | 0 | 2011
1848 | 70944 | Unknown | Unknown | TRUE | TL |  |  |  | 2011-F-0200 | 96F Stroud - Tomago330 132kV TL | Z | 2011Q2 | TOM |  | TL | 2011-06-05 09:19 | 2011-06-05 09:19 | Dip on system at time of trip. Ausgrid advised of TAR. |  |  | Dip on system at time of trip. Ausgrid advised of TAR. | Fine | [6 empty] | 0 | 0 | 2011
2026 | 71022 | HV Equipment | HV Equipment Failure | TRUE | CVT |  |  |  | 2011-E-0015 | 132kV B Bus Section No.1 | Q | 2011Q2 | SYW |  | BB | 2011-06-07 11:52 | 2011-06-08 17:13 |  |  |  | Bus taken out of service due to Bus CVT Imbalance alarm and reported noise from secondary termination box. CVT found faulty and replaced. |  | Primary Equipment | [5 empty] | 0 | 0 | 2011 | Faulty CVT (primary equipment)
1866 | 92311 | Switching error | Sec Eqt Staff Error | TRUE | Prev |  |  |  | 2011-F-0230 | 250 Sydney North - Berowra 132kV Line | C | 2011Q2 | SYN |  | TL | 2011-06-07 16:57 | 2011-06-07 17:01 | During work at Sydney North 132kV B2 Busbar protection, an intertrip was sent to Ausgrid on 250 Sydney North Berowra, which was isolated at Berowra for the work. The intertrip caused a transformer and bus section to trip at Berowra. 27MVA load interrupted | 5/09/2011 9:48:00 AM ¦ Nil. ¦ Nil. |  | At 1657hrs during work at Sydney North 132kV B2 Busbar protection, an intertrip was sent to Ausgrid on 250 Sydney North Berowra, which was isolated at Berowra for the work. The intertrip caused a transformer and bus section to trip at Berowra. 27MVA load | Fine | [6 empty] | 1 | 1 | 2011 | QAPR report indicates incorrect isolation of intertrip signal leading to incorrect protection operation
1853 | 71188 | HV Equipment | HV Equipment Failure | TRUE | CVT |  |  |  | 2011-E-0017 | 14 Sydney North - Kemps Creek 330kV TL | E | 2011Q2 | KCR, SYN |  | TL | 2011-06-14 10:25 | 2011-06-15 18:16 | Staff on site observed bulge in CVT magnetic unit tank & discolouration of tank. T/L de-energised pending further action. | 23/06/2011 2:59:00 PM ¦ N/A ¦ Further investigation by Asset Performance initiated. |  | "Staff on site observed bulge in CVT magnetic unit tank & discolouration of tank. T/L de-energised pending further action. CVT Replaced - Follow up TWR in place for similar units for further investigation." | Rain | Primary Equipment | [5 empty] | 0 | 0 | 2011
1855 | 71226 | HV Equipment | Unknown | TRUE | TL |  |  |  | 2011-F-0207 | 21 Sydney North - Tuggerah 330kV TL | Z | 2011Q2 | SYN, TGH |  | TL | 2011-06-14 18:05 | 2011-06-15 11:32 | Distance to fault 17.3km from TGH 46.3km from SYN line length 64.5km | 13/07/2011 12:53:00 PM ¦ NIL ¦ Refer to the findings of the Task Force. |  | SO/Ausgrid advised that field staff have reported that conductors are down on 21 Sydney North to Tuggerah 330 kV T/L at Structure 75 (approx. 18km from Tuggerah.) | [7 empty] | 0 | 0 | 2011
1858 | 91301 | Secondary Equipment | Sec Eqt Malfunction | TRUE | Sec |  |  |  | 2011-E-0020 | No.3 Transformer 330/132/16kV | E | 2011Q2 | SE1 |  | TX | 2011-06-15 06:05 | 2011-06-15 16:35 | Tap Changer fault, Trans Group 1 Voltage off limits & SS Misc equipment fail alarms received 0529hrs. No.3 TX MW metering has gone to zero (over a one minute period) Metering error suspected. Scada Trends indicate No.3 Transformer actually went off load | 23/06/2011 3:50:00 PM ¦ N/A ¦ SCADA investigation ongoing. |  | Tap Changer fault, Trans Group 1 Voltage off limits & SS Misc equipment fail alarms received 0529hrs. No.3 TX MW metering has gone to zero (over a one minute period) Metering error suspected. Scada Trends indicate No.3 Transformer actually went off load a | Rain | [6 empty] | 0 | 0 | 2011
1856 | 91125 | HV Equipment | HV Equipment Failure | TRUE | TX |  |  |  | 2011-E-0019 | No.1 Transformer 330/132/11 kV | E | 2011Q2 | YSN |  | TX | 2011-06-18 16:10 | 2011-06-20 08:13 | On request from L. Smyth open No.1 TX @ Yass on CB, ( available in emergency) due to high Condition Monitor Alarms being received. No.1 TX to be isolated & earthed on Monday for investigation No.1 TX off loaded only on NAVC & O/L Tripping disabled via Sc | 27/09/2011 9:06:00 AM |  | On request from L. Smyth open No.1 TX @ Yass on CB, ( available in emergency) due to high Condition Monitor Alarms being received. No.1 TX to be isolated & earthed on Monday for investigation No.1 TX off loaded only on NAVC & O/L Tripping disabled via Sca | Fine | [6 empty] | 0 | 0 | 2011
1857 | 91153 | HV Equipment | Unknown | TRUE | CB SF6 |  |  |  | 2011-F-0214 | No.1 Transformer 330KV B CB 5412B | Q | 2011Q2 | SYN |  | CB | 2011-06-20 11:09 | 2011-08-10 15:48 | Prior to trip a CB pole discrepancy & CB abnormal alarms were generated. Inspection of CB carried out - all OK & no protection operations observed. 10/8/2011 - C.B. isolated on HVPRI 32181. Inspection carried out. No fault found. Advised C.B. is servicea | 16/08/2011 8:10:00 AM ¦ N/A ¦ Nil |  | Prior to trip a CB pole discrepancy & CB abnormal alarms were generated. Inspection of CB carried out - all OK & no protection operations observed. WO 193834 exists to investigate further - pole discrepancy. | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2011
1859 | 91973 | Secondary Equipment | Unknown | TRUE | Prot |  | No FR |  | 2011-F-0221 | No.1 Transformer 132/66/11kV | Z | 2011Q3 | AR1 | Protection | TX | 2011-07-01 11:59 | 2011-07-01 17:50 | No obvious fault although Fault recorder operated. No Load lost. No Protection fault found and Tx RTS successfuly at 1746hrs |  |  | No obvious fault although Fault recorder operated. No Load lost. No Protection fault found and Tx RTS successfully at 1746hrs. Now believed to be due to faulty Tapchanger O/P switch and possible interaction with RR3 relay. (Refer FEOR 2011-F-0323) | Fine | Secondary Equipment | [5 empty] | 0 | 0 | 2011 | Faulty tapchanger o/p switch
1860 | 91988 | Secondary Equipment | LV/MECH/PROT Equipment Fail | TRUE | Seq Equ |  | NA |  | 2011-E-0023 | No.5 Transformer 132kV B CB 4452B | Q | 2011Q3 | SYW |  | CB | 2011-07-02 03:21 | 2011-07-02 11:36 | Low IR on alarm cabling. Alarms wiring modified between BMK and C.T. Alarms tested through to SCADA OK. SF6 pressures confirmed OK on C.B. 4452B and associated C.T. | 13/07/2011 8:05:00 AM ¦ N/A ¦ Baiting for rabbits done in past 12 months at SYW, no further action to be taken. |  | Low IR on alarm cabling. Alarms wiring modified between BMK and C.T. Alarms tested through to SCADA OK. SF6 pressures confirmed OK on C.B. 4452B and associated C.T. On 02/07/2011 @ 0810 hrs a Low Gas Density Alarm initiated for No.5 Transformer CB Bay CB4 |  | Secondary Equipment | [5 empty] | 0 | 0 | 2011 | Poor condition cabling caused alarms leading to emergency outage
1861 | 92151 | Unknown/Storm | Unknown | TRUE | TL |  | No FR |  | 2011-F-0223 | 97K Cooma - Munyang tee Snowy Adit 132kV TL | C | 2011Q3 | CMA, MNY |  | TL | 2011-07-05 10:27 | 2011-07-05 16:21 | Tripped at same time as 97G Geehi Tee at Murray 330kV Substation (FEOR 2011-F-224). 18MW load loss at Munyang (Perisher load). Munyang load restored from Murray via Guthega @ 1038 hrs. 97K Cooma to Munyang 132kV T/L left out of service until patrol carrie | 2/08/2011 11:05:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Tripped at same time as 97G Geehi Tee at Murray 330kV Substation (FEOR 2011-F-224). 18MW load loss at Munyang (Perisher load). Munyang load restored from Murray via Guthega @ 1038 hrs. 97K Cooma to Munyang 132kV T/L left out of service until patrol carrie | Very Windy | Unexplained | [5 empty] | 0 | 0 | 2011
1862 | 92161 | Design Limitation | Unknown | TRUE | Proc |  | No FR |  | 2011-F-0224 | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2011Q3 | GTH, MUR, GHI |  | TL | 2011-07-05 10:27 | 2011-07-05 10:38 | 97G Geehi Tee tripped at the same time as 97K Cooma to Munyang 132kV T/L FEOR 2011-F-223). Line RTS via SCADA @ 1038 hours. Munyang load transferred onto Murray and fully restored @ 1049 hours. | 31/08/2011 1:41:00 PM ¦ N/A ¦ No further action is required. |  | 97G Geehi Tee tripped at the same time as 97K Cooma to Munyang 132kV T/L FEOR 2011-F-223). Line RTS via SCADA @ 1038 hours. Munyang load transferred onto Murray and fully restored @ 1049 hours. Queries on the operation of the auto-changeover scheme and t | Very Windy | [6 empty] | 1 | 0 | 2011 | QAPR report indicates incorrect protection settings
1863 | 92189 | Unknown/Storm | Wind | TRUE | TL | 265.31 | NA |  | 2011-F-0227 | 2 Upper Tumut - Yass 330kV TL | Z | 2011Q3 | UT1, YSN |  | TL | 2011-07-06 05:35 | 2011-07-06 05:36 | High winds in area | 2/08/2011 12:56:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Protection detected a blue phase to earth fault. High winds were reported in the area at the time of the trip. Due to weather conditions a patrol could not be carried out on the line. This has been noted for the next scheduled aerial patrol. | Very Windy | Unexplained | [5 empty] | 0 | 0 | 2011
1864 | 92232 | HV Equipment | Sec Eqt Malfunction | TRUE | SVC |  | No FR |  | 2011-F-0228 | No.1 Static VAR Compensator | Z | 2011Q3 | AR1 |  | SVC | 2011-07-06 13:08 | 2011-07-06 13:14 | SVC tripped on manual changeover of cooling pumps. | 12/07/2011 3:34:00 PM ¦ NIL ¦ In future, an outage of the SVC will be arranged for the replacement and testing of the cooling phase failure relays. |  | SVC tripped on manual changeover of cooling pumps. On 5/7/2011 at 1717 hrs, a 'Cooling Non Critical alarm' was initiated from the No1 SVC at Armidale Substation. On 6/7/2011, during investigations the phase failure relay on the TRC No1 Pump of the cooling | Fine | Secondary Equipment | [5 empty] | 0 | 0 | 2011 | QAPR report indicates cooling system fault
1865 | 92289 | HV Equipment | HV Equipment Failure | TRUE | TL |  | No FR |  | 2011-F-0229 | 993 Wagga 330 - Gadara 132kV TL | Z | 2011Q3 | GAD, WG1 |  | TL | 2011-07-06 17:16 | 2011-07-06 17:17 | Prior to trip Gadara was supplied radially via 993 line. 99P line was opened at Gadara due to system loadings. Loss of Visy load of 56 MW. Visy immediatley advised of TAR & to restore load as required. Weather conditions calm |  |  | Prior to trip Gadara was supplied radially via 993 line. 99P line was opened at Gadara due to system loadings. Loss of Visy load of 56 MW. Visy immediately advised of TAR & to restore load as required. | Very Cold | [6 empty] | 0 | 0 | 2011
1867 | 92714 | Switching error | Operating Error | TRUE | Prev |  | NA |  | 2011-F-0236 | 851 Beryl - Mudgee tee Gulgong 66kV Line | S | 2011Q3 | BER |  | TL | 2011-07-13 12:47 | 2011-07-13 12:47 | Whilst carrying out I.E test involving CB operations on scada at Beryl, incorrectly opened adjacent bay CB 8512 instead of CB 3812, resulting in 2.5MW of load interrupted for 11secs |  |  | Whilst carrying out I.E test involving CB operations on scada at Beryl, incorrectly opened adjacent bay CB 8512 instead of CB 3812, resulting in 2.5MW of load interrupted for 11secs. . The trip was due faulty pallets associated with the permissive trippin | Fine | [6 empty] | 0 | 1 | 2011 | Operator opened wrong CB
1184 | 92785 | HV Equipment | Non TransGrid Reason | TRUE | CB SF6 |  | NA |  | 2011-F-0237 | No.6 330kV GENERATOR TRANSFORMER CB 5262 | N | 2011Q3 | VP1 |  | CB | 2011-07-14 22:20 | 2011-07-16 14:32 | Delta requested CB opened due to issues when unit synchronised last (Blue phase 9.4 ms slower closing than other phases). Testing carried out on 16/7/11. CB RTS. Further investigations pending. |  |  | "Delta requested CB opened due to issues when unit synchronised last (Blue phase 9.4 ms slower closing than other phases). Testing carried out on 16/7/11. CB RTS. Further investigations pending. " | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2011
1868 | 92947 | Unknown | Unknown | TRUE | TL |  | No FR |  | 2011-F-0241 | 99H Jindera - ANM 132kV TL | Z | 2011Q3 | ANM, JDA |  | TL | 2011-07-20 14:15 | 2011-07-20 14:15 |  | 2/08/2011 11:22:00 AM ¦ N/A ¦ No further action is required. |  | A red-white phase fault was detected only on the No.1 protection at Jindera 330kV Substation. Queries on the protection operation have been referred to Technical Services and Protection Design. 99H forms part of a meshed network but only No.1 Prot at Jin |  | Unexplained | [5 empty] | 0 | 0 | 2011 | QAPR report indicates suspected wind blown debris
1186 | 93065 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  | NA |  | 2011-F-0243 | No.1 Transformer 330/132/33KV | Z | 2011Q3 | WL1 |  | TX | 2011-07-23 12:18 | 2011-07-23 13:35 | CB 5412 had low SF6 alarm. Transformer Isolated and CB topped-up. | 11/08/2011 8:22:00 AM ¦ Nil ¦ No.1 & No.2 Transformers are due for an outage in October. Repairs to leaks planned for this outage. |  | CB 5412 had low SF6 alarm. Transformer Isolated and CB topped-up. Investigations into the SF6 leak were performed in early August using an SF6 camera. The leak was detected in the White phase interrupter base breather, this means the main drive seal is le | Fine | Oil/Gas Levels | [5 empty] | 0 | 0 | 2011
1187 | 93066 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  | NA |  | 2011-E-0025 | No.2 Generator 330kV CB 5222 | Q | 2011Q3 | ER0 |  | CB | 2011-07-23 21:41 | 2011-07-23 22:56 | CB5222 SF6 top up. |  |  | SF6 top-up |  | Oil/Gas Levels | [5 empty] | 0 | 0 | 2011
1869 | 93181 | HV Equipment | Unknown | TRUE | Proc |  | No FR |  | 2011-F-0245 | No.1 Static VAR Compensator | Z | 2011Q3 | AR1 |  | SVC | 2011-07-26 09:33 | 2011-07-26 10:02 | Alarm fault being investigated at time of SVC shutdown. Field staff report reason for shutdown as being cooling water pump d.c. supply fail. All supplied checked as in service, alarm fault recitifed & SVC returned to service. | 8/08/2011 12:49:00 PM ¦ NIL ¦ In future, an outage of the SVC will be arranged for control relay replacement/testing. |  | The SVC tripped due to a Cooling Plant trip. At the time, staff investigating a Cooling Critical Alarm were replacing a suspect AC supply change over relay K4421. The suspect change over relay K4421 was replaced and the control circuits checked prior to r | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2011 | SVC trip due to cooling system
1871 | 93241 | Secondary Equipment | Unknown | TRUE | AC/DC |  | No FR |  | 2011-F-0248 | No.1 Transformer 330/132/11kV | Z | 2011Q3 | NEW | Plant (Subs) | TX | 2011-07-27 10:43 | 2011-07-28 18:08 | No.1 TX LBU into 330kV A Bus Section one. Bus section one rts leaving No. 1 TX o/s for further investigations Amendment rts at 1808hrs on 28/7/2011 | 18/08/2011 2:04:00 PM ¦ Replace the damaged 415V AC Bus Ring supply cable Investigate and prepare a detailed report of the incident and the circumstances leading to the damage of the 415V AC Bus Ring supply cable. |  | Protection flagging indicates 330kV Bus tripped due to No1 Transformer white phase differential protection operation, on No.1 protection only, plus CB 5412 local backup operation into the 330kV A1 bus. No1 transformer was isolated and the 330kV A1 bus ret | Very Cold | Secondary Equipment | [5 empty] | 1 | 0 | 2011 | QAPR report indicates poor cable condition resulted in 415 AC supply cable voltage causing current in the protection CT secondary cabling
1760 | 2 | Unknown | Unknown | TRUE | CB SF6 |  | NA |  | IR - 7776, IR7778 | CB 4712 | Z | 2011Q3 | Wl1 | Unknown | CB | 2011-07-28 06:05 | 2011-07-28 06:05 |  |  |  | CB 4712 opened immediately after closing. Please inspect & advise on protection details. Advised cannot find any issues with the capacitor. Visually inspected & no protection flag falls. I tried to pressurise the capacitor but failed to remain I/s. |  | Unexplained | Central | 132 | Forced |  |  | 0 | 0 | 2011 | Unknown reason for trip, no further info in QAPR/THEOS/Opslog
1915 | 3 | Wiring Error | Unknown | TRUE | Prev |  | NA |  | IR-7801 | 65 Upper Tumut - Murray 330kV TL | Z | 2011Q3 | MUR |  | TL | 2011-08-03 12:00 | 2011-08-03 12:00 |  |  |  | Advises has found wiring fault associated with A/R, T/L will not reclose @ Murray until rectified. A/R non-auto as a result of wiring changes associated with CB replacement. |  | Secondary Equipment | Southern | 330 | Forced |  |  | 0 | 0 | 2011
1331 | 5 | Design Ommission | Unknown | TRUE | Prev |  | NA |  | 2012-F-0239 | 64 Lower Tumut - Upper Tumut 330kV TL | Z | 2011Q3 | UT1 |  | Prev | 2011-08-03 12:31 | 2011-08-03 12:31 |  |  |  | Advises T/L failed to reclose due to changes to the A/R initiation wiring from the No.1 Protection following replacement of the No.2 Protection panel. |  | Maintenance | Southern | 330 | Forced |  |  | 0 | 0 | 2011
1875 | 94706 | Unknown | Unknown | TRUE | TL |  | No FR |  | 2011-F-0255 | 990 Yass - Wagga 132 132kV TL | Z | 2011Q3 | WG2, YSN |  | TL | 2011-08-12 06:35 | 2011-08-12 06:35 |  | 11/10/2011 9:32:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Tripped and reclosed. Reason unknown. Protection at both Yass and Wagga 132 detected a red phase fault. An inspection was carried out on the 990 from structures 60 to 75. No obvious signs of flashover were found. Minor damaged post insulators were found o | Fine | Unexplained | [5 empty] | 0 | 0 | 2011
1876 | 94717 | Secondary Equipment | Sec Eqt Malfunction | TRUE | Prot |  | No FR |  | 2011-F-0256 | 910 Sydney South - Chullora tee Canterbury 132kV Line | Q | 2011Q3 | SYS |  | TL | 2011-08-12 09:21 | 2011-08-12 10:51 | 910 TL tripped at Chullora and Canterbury. Ausgrid Protection, Chullora No.1 Prot only I/T REC & Multitrip. Canterbury No.1 Prot only, I/T REC & PW Diff. 10.51 hrs 910 TL No.1 Prot isolated and TL available for service on No2. Prot at SYS. SO/Ausgrid advi | 26/08/2011 9:54:00 AM ¦ Nil ¦ Nil |  | 910 TL tripped at Chullora and Canterbury. Ausgrid Protection, Chullora No.1 Prot only I/T REC & Multitrip. Canterbury No.1 Prot only, I/T REC & PW Diff. 10.51 hrs 910 TL No.1 Prot isolated and TL available for service on No2. Prot at SYS. SO/Ausgrid advi | Fine | Secondary Equipment | [5 empty] | 1 | 0 | 2011 | QAPR report indicates faulty relay power supply
1194 | 95606 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  | NA |  | 2011-E-0026 | No.1 Transformer 132/33/11kV | E | 2011Q3 | KS2 |  | TX | 2011-08-26 11:15 | 2011-08-26 15:49 | CB 4412 low SF6 Alarm. |  |  | CB 4412 low SF6 Alarm. | Fine | Oil/Gas Levels | [5 empty] | 0 | 0 | 2011
1877 | 95735 | Lightning/Storm |  | TRUE | TL | 95.2 | Yes |  | 2011-F-0269 | 965 Armidale - Kempsey 132kV TL | Z | 2011Q3 | AR1, KS2 |  | TL | 2011-08-30 15:40 | 2011-08-30 15:40 |  | 29/09/2011 9:44:00 AM ¦ NIL ¦ Plan and replace the flashed insulator string. |  | PST also out. Protection calculated distance to fault 132.4 km from Armidale Substation. The aerial inspection of the line carried out on the 13th of September 2011 has found a flashed insulator string on structure 370 of the line. Action is in hand to pl | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
1878 | 95804 | Lightning/Storm | Unknown | TRUE | TL |  | No FR |  | 2011-F-0271 | 96G Pt Macquarie - Kempsey 132kV TL | Z | 2011Q3 | KS2, PMQ |  | TL | 2011-08-31 11:20 | 2011-08-31 11:20 |  |  |  | See comments on outage 96261. | Fine | External | [5 empty] | 0 | 0 | 2011
1880 | 95956 | Condition Monitor |  | TRUE | TX |  | NA |  | 2011-F-0274 | No.3 Transformer 330/132/11kV | E | 2011Q3 | MTP | Plant (Subs) | TX | 2011-09-04 11:39 | 2011-09-05 18:11 | No3 Transformer main tank buchholz urgent alarm received at 0903. Staff called out to investigate. Transformer de-energised at 1139 for possible bushing fault. | 9/09/2011 7:34:00 AM ¦ Nil ¦ Asset Performance seeking advice from Bushing Monitor Manufacturer. |  | No3 Transformer main tank buchholz urgent alarm received at 0903. Staff called out to investigate and found a Bushing Monitor with "Red phase 330kV bushing severe % PF deterioration" alarm up. The Bushing Monitor Alarm had been paralleled with the Main Ta |  | Secondary Equipment | [5 empty] | 0 | 0 | 2011 | Emergency outage due to condition monitoring, not a protection operation
1881 | 96142 | Lightning/Storm | Lightning or Storm | TRUE | TL | 59.95 | Yes |  | 2011-F-0277 | 945 Wellington - Molong tee Well'n Town 132kV TL | Z | 2011Q3 | MOL, WL1 |  | TL | 2011-09-06 20:48 | 2011-09-06 20:48 | Customer advised that 4.8MW of load is radial at Wellington Town this was lost for reclose time only. Additional information provided from Molong. Fault duration 59.95ms Fault location from Molong 31.44km IA 221.3 A IB 1.396kA IC 96.99A Fault Resistance | 18/10/2011 3:32:00 PM ¦ Nil ¦ Line outage booked for 31/10/11 and 1/11/11 for insulator inspection and change (if required). |  | Line Tripped and Auto Reclosed. Duration of fault was 59.95 ms, weather at the time of fault was thunderstorms. Fault distance from Molong was 31.44 km. Essential Energy advised that 4.8MW of load is radial at Wellington Town this was lost for reclose ti | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
1882 | 96255 | Lightning/Storm | Lightning or Storm | TRUE | TL | 81.1 | Yes |  | 2011-F-0278 | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Z | 2011Q3 | AR1, COF |  | TL | 2011-09-08 16:01 | 2011-09-08 16:01 |  | 5/10/2011 1:28:00 PM ¦ NIL ¦ NIL |  | Aerial patrol carried out on the 13th of September 2011 in the area around structure 457 of the line has found no evidence of any damage to the line as consequence of the tripping. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
1883 | 96261 | Lightning/Storm | Unknown | TRUE | TL |  | No FR |  | 2011-F-0281 | 96G Pt Macquarie - Kempsey 132kV TL | Z | 2011Q3 | KS2, PMQ |  | TL | 2011-09-09 05:09 | 2011-09-09 05:09 | Note No 1 Protection only at Kempsey, Overcast but no rain | 29/09/2011 11:10:00 AM ¦ NIL ¦ NIL |  | Tripped and auto-reclosed on red phase earth fault at both ends. Earlier on the 31/8/11, the line also tripped and auto -reclosed at both ends on similar fault. On both the occasions the distance to the fault was calculated around 28 km from Kempsey Subst | Fine | External | [5 empty] | 0 | 0 | 2011
1884 | 96433 | Relay | Unknown | TRUE | Prot |  |  |  | 2011-F-0282 | 36 Marulan - Bannaby 330kV TL | Z | 2011Q3 | MRN, BBY |  | TL | 2011-09-14 19:01 | 2011-09-14 19:01 | 36 TL TAR at Bannaby end only, Line remained energised from Marulan. On call fitter requested to site for protection details at Bannaby and Marulan. Confirmed No CB or Protection operations at Marulan. No fault recorder operations. |  |  | 36 TL TAR at Bannaby end only, Line remained energised from Marulan. On call fitter requested to site for protection details at Bannaby and Marulan. Confirmed No CB or Protection operations at Marulan. No fault recorder operations. Faulty D60 relay. | Fine | Primary Equipment | [5 empty] | 1 | 0 | 2011 | Faulty protection relay
1885 | 96573 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CVT |  | NA |  | 2011-F-0283 | 21 Sydney North - Tuggerah 330kV TL | Z | 2011Q3 | SYN, TGH |  | TL | 2011-09-17 17:50 | 2011-09-18 17:24 | 21 line was energised @ SYN after CVT maintenance, when placed on load @ Tuggerah both CB's @ SYN tripped, leaving line energised from Tuggerah. At SYN found exposed CVT secondary wire which had shorted to earth causing both white & blue phase spark gaps | 28/09/2011 7:33:00 AM ¦ Nil ¦ Nil. |  | Line was returned to service after Trench 330kV CVT at SYN in accordance with TWR099., Both CBs 212A & 212B leaving 21 Line energised from Tuggerah. After inspection of the Blue Phase CVT it was found that a secondary wire had been shorted to earth causin | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2011 | QAPR report indicates secondary wire insulation damage at CVT
1204 | 96576 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  | NA |  | 2011-E-0028 | No.4 Bay Coupler CB 6042 | Q | 2011Q3 | ER0 |  | CB | 2011-09-18 23:49 | 2011-09-19 01:33 | CB6042 topped up with SF6 |  |  | CB5A22 white phase topped up with SF6. | Fine | Oil/Gas Levels | [5 empty] | 0 | 0 | 2011
2014 | 1 | Unknown | Unknown | TRUE | CBOil |  | NA |  | IR-7966 | CB 9672 | q | 2011Q3 | KLK | Plant (Subs) | CB | 2011-09-22 17:05 | 2011-09-22 17:05 |  |  |  | CB 9672 trip after 4 seconds on return to service of 967 TL. Line being energised at time as per normal operating procedure. No indication of protection operation. Bay & equipment inspected with no abnormalities observed. Kirk (SMF) reports similar equipm |  | Secondary Equipment | Northern | 132 | Forced |  |  | 0 | 0 | 2011 | Unknown reason for SVC trip, no further info in QAPR/THEOS/Opslog
1205 | 96825 | HV Equipment | Human Interference | TRUE | CB SF6 |  | NA |  | 2011-F-0289 | No.1 330kV Generator Transformer Group | Q | 2011Q3 | LD1 |  | TX | 2011-09-23 12:59 | 2011-09-23 16:36 | Substation maintenance fitter " dobbed a +ve " onto the trip link associated with CB 5212 with the view of opening this CB. Not only did CB 5212 open, in sympathy CB 5012 also opened thus tripping # 1 Generator Unit @ Liddell Power Station. CB's 5212 & | NIL ¦ Follow-up with the Power Station Staff for the replacement of the faulty Slave relay and test the No1 Generator control circuit. |  | Substation maintenance fitter " dabbed a +ve " onto the trip link associated with CB 5212 with the view of opening this CB. Not only did CB 5212 open, in sympathy CB 5012 also opened thus tripping # 1 Generator Unit @ Liddell Power Station. CB's 5212 & 50 | Fine | [6 empty] | 1 | 1 | 2011 | Incorrect isolation by dobbing a +ve supply onto the trip link, leading to an incorrect protection operation
1206 | 96827 | Unknown | Unknown | TRUE | CB SF6 |  | No FR |  | 2011-F-0291 | Station Transformer 1A 330kV CB 5412 | Q | 2011Q3 | MN1 |  | CB | 2011-09-24 20:39 | 2011-09-24 22:50 | Concurrent outage of 2B Station TX within Delta system resulted in loss of all 415V supply to Munmorah 330kV Switchyard for outage duration. Storms at time resulted in considerable interuption to Ausgrid services in area . Additional Protection details a |  |  | Concurrent outage of 2B Station TX within Delta system resulted in loss of all 415V supply to Munmorah 330kV Switchyard for outage duration. Storms at time resulted in considerable interruption to Ausgrid services in area. | Thunderstorm | [6 empty] | 0 | 0 | 2011 | Unknown reason for SVC trip, no further info in QAPR/THEOS/Opslog
1886 | 96830 | Unknown | Unknown | TRUE | TL | 53.8 | Yes |  | 2011-F-0294 | 5A4 Bayswater - Wollar 500kV TL | Z | 2011Q3 | BAY, WOL |  | TL | 2011-09-25 01:03 | 2011-09-25 01:03 | Concurrent operation of Fault Recorder at Mt Piper. No indication of storms via Indji Program, however system behaviour indicative of storms. |  |  | Concurrent operation of Fault Recorder at Mt Piper. No indication of storms via Indji Program, however system behaviour indicative of storms. | Unknown | Unexplained | [5 empty] | 0 | 0 | 2011
1887 | 96831 | Lightning/Storm | HV Maintenance | TRUE | TL |  | No FR |  | 2011-F-0295 | 96F Stroud - Tomago330 132kV TL | Z | 2011Q3 | TOM |  | TL | 2011-09-25 02:01 | 2011-09-25 02:01 |  |  |  |  | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
1888 | 96833 | Lightning/Storm | HV Maintenance | TRUE | TL |  | No FR |  | 2011-F-0297 | 968 Tamworth 330 - Narrabri 132kV TL | Z | 2011Q3 | NB2, TA1 |  | TL | 2011-09-25 05:02 | 2011-09-25 05:02 |  | 14/10/2011 1:38:00 PM ¦ NIL ¦ NI |  | TL tripped and auto-reclosed at both ends on red phase earth fault. Protection flagging indicated distance to the suspect fault between structures 87 and 101 of the line. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
1889 | 96834 | Lightning/Storm | HV Maintenance | TRUE | TL |  | No FR |  | 2011-F-0298 | 947 Mt Piper 132 - Wellington tee Orange 132kV TL | Z | 2011Q3 | MPP, ORG, WL1, ONO |  | TL | 2011-09-25 05:02 | 2011-09-25 05:03 | Burrendong Substation interrupted for reclose time - Essential Energy advised. | 18/10/2011 3:39:00 PM ¦ Nil ¦ Line outage on 13/10/11 for insulator replacement. |  | Burrendong Substation interrupted for reclose time. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
1890 | 96836 | Staff Error | Sec Eqt Malfunction | TRUE | Prev |  | NA |  | 2011-F-0300 | 132kV B Bus 1-2 Section CB 4112 | Q | 2011Q3 | SYN |  | CB | 2011-09-25 20:18 | 2011-09-26 17:56 | NOT A FORCED OUT - SHORT NOTICE OUTAGE |  |  | Abnormal alarms. Inspection found cabinet door open on C.B.. 4112, SF6 gas pressure OK, cabinet faces south (direction of rain) & the cabinet is full of water, will try & locate cause. Advised unsure which circuit(s) causing abnormal alarm, lighting poor, | Unknown | [6 empty] | 0 | 0 | 2011
1891 | 96871 | HV Equipment | HV Equipment Failure | TRUE | CVT |  | NA |  | Not Available | 25 Eraring - Vineyard 330kV TL | Z | 2011Q3 | ER0, VYD |  | TL | 2011-09-26 12:20 | 2011-09-28 18:18 |  |  |  | At 12:20hrs 25 Vineyard to Eraring 330kV T/L was taken out of service when staff advised of extreme concerns with the integrity of the C.V.T. at Vineyard. AEMO was advised and appropriate constraints invoked. Red & White CVT replaced 27/9. |  | Primary Equipment | [5 empty] | 0 | 0 | 2011
1892 | 96995 | Lightning/Storm | Lightning or Storm | TRUE | TL |  | No FR |  | 2011-F-0312 | X5/1 Darlington Point - Balranald 220kV TL | C | 2011Q3 | BRD, DNT |  | TL | 2011-09-28 16:20 | 2011-10-05 12:03 | Disconnector on X5/1 section of T/L (X5/11) locked open by TG Staff @ Balranald, supply restored to Balranald from Buronga on X5/3 section of T/L. 3 Str's replaced & line RTS 1203 hrs on 05/10/11 | 11/10/2011 3:27:00 PM ¦ N/A ¦ An investigation into the circumstances relating to the multiple structure collapse will be covered in a separate report. |  | At 16:19hrs X5 Buronga to Darlington Point tee Balranald 220 kV T/L tripped, reclosed, tripped and locked out. Severe thunderstorms & high winds in the area. 1.2 MW interrupted. Disconnector on X5/1 section of T/L (X5/11) locked open by TG Staff @ Balra | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
1893 | 96997 | Lightning/Storm | Lightning or Storm | TRUE | TL | 61.6 | Yes |  | 2011-F-0314 | 62 Wagga 330 - Jindera 330kV TL | Z | 2011Q3 | JDA, WG1 |  | TL | 2011-09-28 19:29 | 2011-09-28 19:29 |  | 31/10/2011 1:08:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | TL tripped and auto-reclosed successfully. Protection at Jindera detected a white phase to earth fault. Thunderstorms were reported in the area at the time of the trip. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
1896 | 97051 | Design Limitation | LV/MECH/PROT Equipment Fail | TRUE | Proc |  | No FR |  | 2011-F-0321 | No.2 Bus Coupler | Q | 2011Q3 | BFD |  | BB | 2011-09-29 10:42 | 2011-09-29 14:14 | 41 Cable, No.1 Transformer and No.2 Transformer out of service at time of trip. Protection staff working on 41 Cable 330kV Interzone protection. Protection staff advise they had completed work on 41 Cable 330kV Interzone protection and were in the process | 27/10/2011 2:47:00 PM ¦ Nil ¦ Protection Design investigating the maloperation of the relay with the manufacturer (Reyrlolle). |  | 41 Cable and No.1 Transformer and No.2 Transformer out of service at time of trip. Protection staff working on 41 Cable 330kV Interzone protection. Protection staff advise they had completed work on 41 Cable 330kV Interzone protection and were in the proc | Mild | [6 empty] | 1 | 0 | 2011 | QAPR report indicates incorrect protection relay earthing
321 | 97076 | Secondary Equipment | Unknown | TRUE | Prot |  | No FR |  | 2011-F-0323 | No.1 Transformer 132/66/11kV | Z | 2011Q3 | AR1 |  | TX | 2011-09-29 20:30 | 2011-09-30 16:04 |  | 18/10/2011 2:26:00 PM ¦ NIL ¦ Replace the Overpressure Switch and investigate the cause of the failure. |  | Suspect trip was caused by a earth fault in the negative of the TC overpressure trip cct. Trip link isolated and transformer made available for emergency use overnight on NAVC. Subsequent investigations found that the Tapchanger Overpressure switch is a d | Very Windy | Secondary Equipment | [5 empty] | 0 | 0 | 2011 | Faulty o/p switch
8 | 97368 | Unknown | Unknown | TRUE | TL | NA | NA |  | 2011-F-0331 | 999 Yass - Cowra 132kV TL | Z | 2011Q4 | CW2, YSN | Unknown Mains | TL | 2011-10-07 06:08 | 2011-10-07 06:08 | Distance to Fault from Yass- 40km, from Cawra 83.87km Overcast and drizzly. NCM and Rod White advised | 19/12/2011 11:05:00 AM ¦ N/A ¦ Noted for the next scheduled aerial patrol. |  | Distance to Fault from Yass- 40km, from Cawra 83.87km Overcast and drizzly. Ground inspection of 15 structures in the vicinity of the DTF did ot identify a cause for the fault. Noted for the next scheduled aerial patrol. | Rain | Unexplained | [5 empty] | 0 | 0 | 2011
11 | 97722 | Unknown | Unknown | TRUE | TL | NA | NA |  | 2011-F-0342 | 9U3 Gunnedah - Narrabri 132kV TL | Z | 2011Q4 | GN2, NB2 |  | TL | 2011-10-17 05:19 | 2011-10-17 05:19 | DTF 78.6 km from Narrabri | 19/10/2011 10:12:00 AM ¦ NIL ¦ Close inspection of the suspect fault area of the line during next scheduled patrol. |  | DTF 78.6 km from Narrabri. Ground inspection of the section of the line (between structures 400 and 418) that covers the highway road crossing structures 408-9 inspected and no fault found. Close inspection of the suspect fault area of the line during nex | Rain | Unexplained | [5 empty] | 0 | 0 | 2011
18 | 96933 | Protection |  | TRUE | Prot | NA | NA |  | 2011-F-0399 | No.3 Transformer 330/132kV | N | 2011Q4 | WW1, WWS |  | TX | 2011-10-17 06:00 | 2011-11-03 08:03 | This FEOR replaces 2011-F-0346/1 which has been withdrawn and is no longer available in the system. The transformer was not commissioned at the time of the trip, the transformer was commissioned later on 03/11/2011 at 09:03 hrs. The actual time of the tr |  |  | Trip occurred during commissioning soak of TX 3. CT unbalance for AUX TX attached. Commissioning delayed until 3/11/2011 due to lack of staff. This FEOR replaces 2011-F-0346/1 which has been withdrawn and is no longer available in the system. | Fine | [6 empty] | 0 | 0 | 2011
9 | 97795 | Fire | Unknown | TRUE | TL | NA | NA |  | 2011-F-0344 | 99F Uranqunity - Yanco 132kV TL | Z | 2011Q4 | YA2, URQ | Unknown Mains | TL | 2011-10-17 06:42 | 2011-10-17 06:42 | additional Info from URQ DTF = 33.84kM Fault duration 21.84 ms relay trip time 79.92ms Ia=66.85A Ib=52.49A Ic= 2.36KA Va=75.3 Vb= 76.43 Vc 60.56 Fault Resistance=853.83mohm Fitter call to site to get flag details | N/A ¦ Noted for the next scheduled aerial patrol. |  | Additional Info from URQ. Ground patrol the following day in the vicinity of the DTF there were indications of a very recent burn off. DTF = 33.84kM Fault duration 21.84 ms relay trip time 79.92ms. - Ia=66.85A - Ib=52.49A - Ic= 2.36KA - Va=75.3 - Vb= 76.4 | Fine | External | [5 empty] | 0 | 0 | 2011
7 | 97919 | Switching error | Operating Error | TRUE | Prev | NA | NA |  | 2011-F-0345 | 98F Dapto - Mt Terry 132kV Line | Q | 2011Q4 | DPT | Preventable Issues | TL | 2011-10-18 15:45 | 2011-10-18 16:09 | @ Dapto 330kV Substation 98F Dapto to Mt Terry 132 kV T/L energised on HVPRI 33536, when SO/E.E. closed 98F @ Mt. Terry, C.B.. 98F2 opened @ Dapto, no F/Rec. operation, weather fine. 98F fdr remained energised from Mt. Terry, SO/E.E. requested to de-ener |  |  | 98F fdr remained energised from Mt. Terry, SO/E.E. requested to de-energise while reason for trip investigated, possible switching issue. SO/E.E. advises 98F de-energised at TG request. Contacted Dapto switcher & he thought he may have left CVT sec. links | Fine | [6 empty] | 1 | 1 | 2011 | QAPR report indicates CVT links were left (incorrectly) isolated, leading to incorrect operation of protection
2 | 98003 | Animal/Bird | Unknown | TRUE | TL | 58.4 | YES |  | 2011-F-0347 | 5A4 Bayswater - Wollar 500kV TL | Z | 2011Q4 | BAY, WOL | Lightning Mains | TL | 2011-10-21 01:21 | 2011-10-21 01:21 |  | 26/10/2011 10:19:00 AM ¦ NIL ¦ Arrange climbing inspection and remove the bird-nests. |  | Arrange climbing inspection and remove the bird-nests. | Mild | External | [5 empty] | 0 | 0 | 2011
17 | 98136 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CT | NA | NA |  | 2011-E-0029 | No.2 Transformer 330/132/11kV | E | 2011Q4 | SYS | Plant (Subs) | TX | 2011-10-25 11:04 | 2011-10-25 15:27 | Staff on site observed a loud ringing noise coming from No.2 Transformer 330kV CT's. No.2 TX de-energised via Scada at 1104hrs EST. Open circuit found on metering C.T. core on No.2 Transformer. Protection staff confirmed wiring disturbed on White Phase of | 26/10/2011 1:37:00 PM ¦ Nil ¦ Nil |  | Staff on site observed a loud ringing noise coming from No.2 Transformer 330kV CT's. No.2 TX de-energised via Scada at 1104hrs EST. Open circuit found on metering C.T. Core on No.2 Transformer. Protection staff confirmed wiring disturbed on White Phase of | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2011 | Emergency outage, not a protection operation
12 | 98391 | Lightning/Storm | Lightning or Storm | TRUE | TL | NA | NA |  | 2011-F-0361 | 9U3 Gunnedah - Narrabri 132kV TL | Z | 2011Q4 | GN2, NB2 |  | TL | 2011-10-29 14:52 | 2011-10-29 14:52 |  | 8/11/2011 11:10:00 AM ¦ NIL ¦ The suspect fault has been noted for next scheduled patrol of the line. |  | The suspect fault has been noted for next scheduled patrol of the line. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
1 | 98393 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 | NA | NA |  | 2011-E-0030 | 5A2 Kemps Creek 500kV CB 5A22 | Q | 2011Q4 | ER0 | CB SF6s | CB | 2011-10-29 19:32 | 2011-10-29 21:30 | CB5A22 white phase topped up with SF6 |  |  | CB5A22 white phase topped up with SF6 |  | Oil/Gas Levels | [5 empty] | 0 | 0 | 2011
13 | 98401 | Lightning/Storm | Lightning or Storm | TRUE | SVC | NA | NA |  | Not Available | No.1 Static VAR Compensator | Z | 2011Q4 | LSM | u | SVC | 2011-10-30 18:50 | 2011-10-31 11:00 | [5 empty] | External | [5 empty] | 0 | 0 | 2011 | Unknown reason for SVC trip, no further info in QAPR/THEOS/Opslog
3 | 98791 | Relay | Sec Eqt Malfunction | TRUE | Prot | NA | NA |  | 2011-F-0367 | 5A6 Mt Piper 500kV - Bannaby 500kV TL | Z | 2011Q4 | MTP, BBY | Protection Eq | TL | 2011-11-05 18:08 | 2011-11-05 18:08 | Tripped at Bannaby end only and Auto reclosed on A CB only. CB 5A62B closed via scada. Protection staff attended and advised that the No.1 Protection relay had maloperated. Restored the Protection to service on advice of Team Leader. Further investigatio |  |  | Tripped at Bannaby end only and Auto reclosed on A CB only. CB 5A62B closed via scada. Protection staff attended and advised that the No.1 Protection relay had maloperated. Further investigations required after analysis of fault data from protection desig | Fine | Primary Equipment | [5 empty] | 1 | 0 | 2011
322 | 98953 | Staff Error | Unknown | TRUE | Prev | NA | NA |  | 2011-F-0372 | No.1 Capacitor | Z | 2011Q4 | FB2 |  | CAP | 2011-11-08 11:08 | 2011-12-02 13:41 |  |  |  | Refer to FEOR 2001-F-0372. It appears that the flashover may have occurred between the Live head of the CT, the loose HV conductor and the CT structure. Weather in the area on the day very windy with storms. Routine Maintenance was performed on No.1 Capac | [7 empty] | 0 | 0 | 2011
10 | 98912 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0375 | 99M Yass - Murrumburrah 132kV TL | Z | 2011Q4 | MRU, YSN |  | TL | 2011-11-08 16:13 | 2011-11-08 16:13 |  | 10/01/2012 8:55:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Protection at Yass and Murrumburrah detected a red phase to earth fault. The fault occurred approximately 62.46km from Yass Substation. Thunderstorms were reported in the area at the time of the trip. Noted for next aerial patrol. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
20 | 98965 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0376 | 996 Wagga 330 - ANM 132kV TL | Z | 2011Q4 | ANM, WG1 |  | TL | 2011-11-09 17:58 | 2011-11-09 17:58 | Storms in the area. | 9/01/2012 4:16:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Protection at Wagga and ANM detected a phase to phase and phase to earth fault. Storms were reported in the area at the time of the trip. Noted for next aerial patrol. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
19 | 99054 | Lightning/Storm | Lightning or Storm | TRUE | TL | 47.2 | YES |  | 2011-F-0379 | 66 Murray - Lower Tumut 330kV TL | Z | 2011Q4 | LT1, MUR |  | TL | 2011-11-09 19:29 | 2011-11-09 19:29 | T/L reclosed successfully on B C.B.'s both ends, both A C.B.'s closed by SCADA | N/A ¦ Noted for the next scheduled aerial patrol. |  | T/L reclosed successfully on B C.B.'s both ends, both A C.B.'s closed by SCADA. Noted for the next scheduled aerial patrol. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
4 | 98966 | Lightning/Storm | Lightning or Storm | TRUE | TL | NA | NA |  | 2011-F-0377 | 66 Murray - Lower Tumut 330kV TL | Z | 2011Q4 | LT1, MUR | Lightning Mains | TL | 2011-11-09 19:31 | 2011-11-09 19:31 | At 19:29:45hrs EST 66 Murray to Lower Tumut 330 kV T/L Tripped and Reclosed on CB 662B at LTSS & MUR Stoms and Lightning in area LTSS CB 662A close via SCADA MUR CB 662A close via SCADA |  |  | 66 Murray to Lower Tumut 330 kV T/L Tripped and Reclosed on CB 662B at LTSS & MUR. Stoms and Lightning in area. LTSS CB 662A close via SCADA. MUR CB 662A close via SCADA. No further action was deemed necessary on this occasion. Noted for next aerial patro | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
21 | 99613 | Lightning/Storm | Lightning or Storm | TRUE | TL | NA | NA |  | 2011-F-0383 | 992 Burrinjuck - Tumut 132kV TL | Z | 2011Q4 | BUK, TU2 |  | TL | 2011-11-10 08:20 | 2011-11-10 08:20 | Storms in vicinity, time unknown, outage occurred sometime on the evening of 09.11.2011. | 13/01/2012 11:20:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Storms in vicinity, time unknown, outage occurred sometime on the evening of 09.11.2011. Noted for next aerial patrol. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
22 | 99648 | Lightning/Storm | Lightning or Storm | TRUE | TL | NA | NA |  | 2011-F-0386 | 966 Armidale - Koolkhan 132kV TL | Z | 2011Q4 | AR1, KLK |  | TL | 2011-11-12 18:02 | 2011-11-12 18:02 |  |  |  | Storms in the area. TAR Only - No road crossings, patrol not required | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
23 | 99655 | Lightning/Storm |  | TRUE | TL | NA | NA |  | 2011-F-0392 | 968 Tamworth 330 - Narrabri 132kV TL | Z | 2011Q4 | NB2, TA1 |  | TL | 2011-11-13 09:10 | 2011-11-13 09:10 |  | 25/11/2011 10:02:00 AM ¦ NIL ¦ The suspect fault has been noted for the next scheduled patrol of the line. |  | The suspect fault has been noted for the next scheduled patrol of the line. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
24 | 99656 | Lightning/Storm | Lightning or Storm | TRUE | TL | 58.1 | YES |  | 2011-F-0393 | 96H Coffs Harbour - Koolkhan 132kV TL | Z | 2011Q4 | COF, KLK |  | TL | 2011-11-13 11:41 | 2011-11-13 11:41 |  | 25/11/2011 3:11:00 PM ¦ NIL ¦ The suspect fault has been noted for the next scheduled patrol of the line. |  | The suspect fault has been noted for the next scheduled patrol of the line. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
25 | 99663 | Lightning/Storm | Lightning or Storm | TRUE | TL | 58.9 | YES |  | 2011-F-0397 | 8E Armidale - Dumaresq 330kV TL | Z | 2011Q4 | AR1, DMQ |  | TL | 2011-11-13 18:48 | 2011-11-13 19:15 | This feor also caused a seperation from Queensland since cb's 5332 , 5322 , 5312 & 5342 opened. See seperate feor report for Dumaresq bus outage | 23/11/2011 1:34:00 PM ¦ NIL ¦ The Protection Design to analyse the protections on the lines. |  | This resulted in a separation between NSW and QLD since cb's 5332 , 5322 , 5312 & 5342 opened. See separate feor report for Dumaresq bus outage. There was 600MW flow south at the time of the trip. NSW system frequency dropped to 49.8Hz and recovered to > | Thunderstorm | External | [5 empty] | 0 | 0 | 2011 | Opslog indicates legitimate double circuit fault due to lightning, excerpt: ""Advised TG have been able to clearly identify an (sic) geniune double circuit fault"
26 | 100013 | Contractor Error | Pollution | TRUE | Prev | NA | NA |  | 2011-F-0410 | 11 Dapto - Sydney South 330kV TL | Z | 2011Q4 | DPT, SYS |  | TL | 2011-11-19 16:49 | 2011-11-19 16:49 | No storms in vicinity, T/L taken O/S 5 mins after TAR for further investigation, see EOR 2011-E-0033 for outcome. |  |  | No storms in vicinity, T/L taken O/S 5 mins after TAR for further investigation, see EOR 2011-E-0033 for outcome. | Fine | [6 empty] | 0 | 0 | 2011
27 | 100014 | Contractor Error | Pollution | TRUE | Prev | NA | NA |  | 2011-E-0033 | 11 Dapto - Sydney South 330kV TL | E | 2011Q4 | DPT, SYS |  | TL | 2011-11-19 17:54 | 2011-11-19 18:59 | 11 T/L taken O/S after TAR which occurred 2 min 12 secs after energising from 4 day continuous outage for contractors to grit blast & paint multiple towers along the line. TG staff discovered @ Str.63 a shielding cover on the ground used to protect insula | 29/11/2011 8:19:00 AM ¦ Nil. ¦ Moitoring of the corrective actions and reccomendations. |  | 11 T/L taken O/S after TAR which occurred 2 min 12 secs after energising from 4 day continuous outage for contractors to grit blast & paint multiple towers along the line. At Tower 63 it was found that there was several burnt/charred glass insulators visi | Fine | [6 empty] | 0 | 0 | 2011
28 | 100216 | Animal/Bird | Unknown | TRUE | TL |  |  |  | 2011-F-0417 | 5A3 Bayswater - Mt Piper 500kV TL | Z | 2011Q4 | BAY, MTP |  | TL | 2011-11-23 13:58 | 2011-11-23 13:58 | 5A3 TL bay equipment visually checked OK at both Bayswater & Mt Piper. Protection details attached to THEOS outage 100216. | 6/02/2012 1:04:00 PM ¦ NIL ¦ Arrange climbing inspection and remove the bird-nests. |  | 5A3 TL bay equipment visually checked OK at both Bayswater & Mt Piper. Fault locations identified by the Travelling Wave Fault Locator correlated with bird nests on inspection. Bird nests to be removed when bird deterants installed. | Rain | External | [5 empty] | 0 | 0 | 2011
29 | 100412 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0434 | 990 Yass - Wagga 132 132kV TL | Z | 2011Q4 | WG2, YSN |  | TL | 2011-11-29 20:12 | 2011-11-29 20:12 |  | 13/01/2012 9:54:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Storms in area. The fault occurred approximately 127.29km from Yass Substation. This works out to be around structure 94. An inspection on the line was completed on the 01/12/2011 between structures 90 to 115. No irregularities were found. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
30 | 100415 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0437 | 990 Yass - Wagga 132 132kV TL | Z | 2011Q4 | WG2, YSN |  | TL | 2011-11-29 20:58 | 2011-11-29 20:58 | Storms in area.990 TL tripped and reclosed at 20:58:12hrs and again at 20:58:52hrs. | 13/01/2012 10:01:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Storms in area. The fault occurred approximately 127.29km from Yass Substation. This works out to be around structure 94. An inspection on the line was completed on the 01/12/2011 between structures 90 to 115. No irregularities were found. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
1330 | 100422 | Relay | Lightning or Storm | TRUE | Cont |  |  |  | 2011-F-0444 | 992 Burrinjuck - Tumut 132kV TL | Z | 2011Q4 | BUK, TU2 |  | TL | 2011-11-29 21:31 | 2011-11-29 23:15 | Storms in area. Appears that 992 TL tripped and reclosed at Tumut and tripped only at Burrinjuck. Line closed at Burrinjuck after confirming Line volts incoming from Tumut. Unable to confirm Auto reclose operations at either end. | 10/01/2012 9:21:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. Line Interface relay fault at Burrinjuck requires follow-up. |  | Refer to outage 100422. Line Interface relay fault at Burrinjuck requires follow-up. | Thunderstorm | Primary Equipment | [5 empty] | 1 | 0 | 2011 | Faulty protection relay
31 | 100422 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0444 | 992 Burrinjuck - Tumut 132kV TL | Z | 2011Q4 | BUK, TU2 |  | TL | 2011-11-29 21:31 | 2011-11-29 23:15 | Storms in area. Appears that 992 TL tripped and reclosed at Tumut and tripped only at Burrinjuck. Line closed at Burrinjuck after confirming Line volts incoming from Tumut. Unable to confirm Auto reclose operations at either end. | 10/01/2012 9:21:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. Line Interface relay fault at Burrinjuck requires follow-up. |  | Storms in area. Appears that 992 TL tripped and reclosed at Tumut and tripped only at Burrinjuck. Line closed at Burrinjuck after confirming Line volts incoming from Tumut. Unable to confirm Auto reclose operations at either end. The fault occurred approx | Thunderstorm | External | [5 empty] | 0 | 0 | 2011 | Duplicate of outage ID 100422
32 | 100428 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0449 | 990 Yass - Wagga 132 132kV TL | Z | 2011Q4 | WG2, YSN |  | TL | 2011-11-29 22:40 | 2011-11-29 22:40 | Storms in area. | 13/01/2012 10:03:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Storms in area. The fault occurred approximately 127.29km from Yass Substation. This works out to be around structure 94. An inspection on the line was completed on the 01/12/2011 between structures 90 to 115. No irregularities were found. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
33 | 100431 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0452 | O1 Upper Tumut - Canberra 330kV TL | Z | 2011Q4 | CA1, UT1 |  | TL | 2011-11-30 00:40 | 2011-11-30 00:40 | Storms in area. CB 012B closed via scada at Canberra 0041hrs | 10/01/2012 10:58:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Storms in area. CB 012B closed via scada at Canberra 0041hrs. This has been noted for the next scheduled aerial patrol. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
323 | 100554 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0457 | 9U2 Inverell - Moree 132kV TL | Z | 2011Q4 | INV, MRE |  | TL | 2011-11-30 17:31 | 2011-11-30 17:31 |  | 7/12/2011 10:40:00 AM ¦ NIL ¦ The suspect fault has been noted for the next scheduled patrol of the line. |  | Storms in area. Line tripped and autoreclosed at both ends. The Indji lightning locator has indicated lightning strikes near structures 335 of the line at the time of the suspect. The ground patrol carried out on the section of the line between structures | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
324 | 100589 | HV Equipment | Unknown | TRUE | CBOil | NA | NA |  | 2011-F-0461 | 967 Lismore 330 - Koolkhan 132kV TL | Z | 2011Q4 | KLK, LSM |  | TL | 2011-12-01 14:27 | 2011-12-01 14:32 | CB 9672 @ KLK opened immediately after closing during return to service of 967 TL (planned daily outage). No protection operated. Visual inspection OK. CVT links intact. CB closed OK on 2nd attempt. | 19/12/2011 10:50:00 AM ¦ NIL ¦ Plan outage for the inspection and repairs to the mechanism box of the circuit breaker. |  | CB 9672 at KLK opened immediately after closing during return to service of 967 TL (planned daily outage). No protection operated. Visual inspection OK. CVT links intact. CB closed OK on 2nd attempt. This is a known issue for HLD circuit breakers that hav | Fine | Unexplained | [5 empty] | 0 | 0 | 2011 | Faulty CB not protection
325 | 100632 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 | NA | NA |  | 2011-F-0462 | 83 LIDDELL 330kV A CB 832A | Q | 2011Q4 | MRK | o | CB | 2011-12-02 01:28 | 2011-12-02 02:35 |  |  |  | Low SF6 condition. CB taken out of service, topped up then RTS. |  | Oil/Gas Levels | [5 empty] | 0 | 0 | 2011
326 | 100756 | Tree/Ground | Tree/Ground | TRUE | TL |  |  |  | 2011-F-0464 | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Z | 2011Q4 | AR1, COF |  | TL | 2011-12-04 00:55 | 2011-12-04 00:55 | Refer to IR#8315 possible tree foliage in close proximity to Essential Energy section of line. COF protection details added. AR1 protection added / unsure if details reflect recent outage on 4 January as protection detail record sheet not available. | 19/12/2011 10:56:00 AM ¦ NIL ¦ Close inspection of the suspect section of the line during next scheduled patrol of the line. |  | IR No. 8315 advises that a sycamore tree appears to be burnt between str's 63512 & 63513. Between str's 63510 & 63511 expected grown over the summer months would see foliage within proximity to the t/l. This could be a possible cause of the line's TAR yes | Mild | External | [5 empty] | 0 | 0 | 2011
327 | 101155 | Animal/Bird | Animal/Bird | TRUE | VT | NA | NA |  | 2011-F-0466 | No.5 Broken Hill - Talc St -2 22kV line | Q | 2011Q4 | BKH |  | TL | 2011-12-08 11:05 | 2011-12-08 11:05 | Dead Crow found on Line Isolator Structure. Has caused a flashover on the Line VT leaving layer of carbon on all three phases. Photos of equipment will be taken for appraisal by maintenance staff. |  |  | Dead Crow found on Line Isolator Structure. Has caused a flashover on the Line VT leaving layer of carbon on all three phases. Photos of equipment will be taken for appraisal by maintenance staff. | Fine | External | [5 empty] | 0 | 0 | 2011
328 | 101216 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0467 | 96M Narrabri - Moree 132kV TL | Z | 2011Q4 | MRE, NB2 |  | TL | 2011-12-10 03:01 | 2011-12-10 03:01 |  | 20/12/2011 10:10:00 AM ¦ NIL ¦ Close inspection of the suspect section of the line during next scheduled patrol of the line. |  | There is no road crossing in the suspect section of the line between Structured 250 – 286, and as such there is no need of an immediate inspection of the line. Close inspection of the suspect section of the line during next scheduled patrol of the line. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
329 | 101579 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0476 | X5/1 Darlington Point - Balranald 220kV TL | Z | 2011Q4 | BRD, DNT |  | TL | 2011-12-19 00:43 | 2011-12-19 00:43 | No information from DNT, no flags showing when inspected on 20/1/2012 | 13/01/2012 11:48:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | This has been noted for the next scheduled aerial patrol. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
1326 | 101610 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2011-F-0483 | 5A5 Wollar - Mt Piper 500kV TL | Z | 2011Q4 | MTP, WOL |  | TL | 2011-12-19 20:09 | 2011-12-19 20:09 | DTF- 50.61 KM from Wollar. | 10/01/2012 11:37:00 AM ¦ NA ¦ Work Order raised for replacement of the insulator string on next available outage. |  | Investigation on 21/12/2011 by Orange Mains staff observed damage to bottom phase insulator string on structure 371. Two Insulator discs were noted as damaged. Work Order raised for replacement of the insulator string on next available outage. | Thunderstorm | External | [5 empty] | 0 | 0 | 2011
1327 | 101723 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 | NA | NA |  | Not Available | No.3 Transformer 132kV B Bus CB 4432B | Q | 2011Q4 | NEW |  | CB | 2011-12-24 10:58 | 2011-12-24 12:09 |  |  |  | Found CB4432B blue phase low gas. CB removed from service and gassed up. |  | Oil/Gas Levels | [5 empty] | 0 | 0 | 2011
1328 | 101758 | HV Equipment | HV Equipment Failure | TRUE | SVC | NA | NA |  | 2011-F-0514 | No.1 Static VAR Compensator | Z | 2011Q4 | BKH |  | SVC | 2011-12-30 03:05 | 2012-01-04 09:23 | Lead Burnt off on Harmonic filter. Repaired on 4/1/12. | 7/06/2012 3:02:00 PM |  | Lead Burnt off on Harmonic filter. Repaired on 4/1/12. | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2011
1324 | 101772 | Unknown | Unknown | TRUE | TL | NA | NA |  | 2012-F-0001 | 994 Wagga 330 - Yanco 132kV TL | Z | 2012Q1 | WG1, YA2 |  | TL | 2012-01-02 05:20 | 2012-01-02 05:20 | No storms in area. | 26/04/2012 2:12:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol |  | No storms in area. This has been noted for the next scheduled aerial patrol | Fine | Unexplained | [5 empty] | 0 | 0 | 2012
1318 | 101773 | HV Equipment | Sec Eqt Malfunction | TRUE | Tx | No FR | NA |  | 2012-F-0002 | No.2 Transformer 330/132/11KV | Z | 2012Q1 | JDA |  | TX | 2012-01-02 14:38 | 2012-01-02 17:08 | Temperatures OK, Load low ( ANM low load), Possible Buchholz Surge on Cooling Pump Auto Start. | 12/06/2012 10:44:00 AM |  | Temperatures OK, Load low ( ANM low load), Possible Buchholz Surge on Cooling Pump Auto Start. | Fine | Secondary Equipment | [5 empty] | 0 | 0 | 2012
1319 | 101774 | HV Equipment | HV Equipment Failure | TRUE | CT | NA | NA |  | 2012-E-0001 | No.6 Transformer 330/132/11kV | E | 2012Q1 | AR1 |  | TX | 2012-01-02 17:25 | 2012-01-02 19:38 | Transformer returned to load @ 1937hrs after blue phase 132kV CT sf6 top-up |  |  | Transformer returned to load @ 1937hrs after blue phase 132kV CT sf6 top-up | Mild | Oil/Gas Levels | [5 empty] | 0 | 0 | 2012
1320 | 101816 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | T/C | NA | NA |  | Not Available | No.1 Transformer 330/132/11kV | E | 2012Q1 | NEW |  | TX | 2012-01-03 19:16 | 2012-01-04 08:41 |  |  |  | Identified No.1 TX No.1 Prot Blue phase OLTC O/P switch as the cause of the battery earth fault. The switch was very close to causing the protection to operate and suggests that No.1 TX is de-energised, available for emergency use. Blue phase OLTC O/P Tr |  | Secondary Equipment | [5 empty] | 0 | 0 | 2012
1325 | 101866 | Lightning/Storm | Lightning or Storm | TRUE | TL | No FR | NA |  | 2012-F-0005 | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Z | 2012Q1 | AR1, COF |  | TL | 2012-01-04 18:50 | 2012-01-04 18:50 | Protection details required | 10/01/2012 2:18:00 PM ¦ NIL ¦ Close inspection of the line in the area of the suspect fault. |  | There was intense lightning in the area at the time of the tripping. Protection Flaggings indicated 86.01Km from Armidale end and 55.63Km from Coffs Harbour end. The Indji lightning locator has confirmed lightning strike near structure 367 or 368 of line | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
1322 | 101893 | Lightning/Storm | Lightning or Storm | TRUE | TL | No FR | NA |  | 2012-F-0009 | 947 Mt Piper 132 - Wellington tee Orange 132kV TL | Z | 2012Q1 | MPP, ORG, WL1, ONO |  | TL | 2012-01-05 15:34 | 2012-01-05 15:34 | Approx MW of load was lost at Cadia mine (94G) during the voltage dip when 947 tripped. approx 10minutes after TAR load was not restored at Cadia. | 16/01/2012 7:40:00 AM ¦ NIL ¦ This structure and surrounding area will be inspected during the next scheduled patrol. |  | Load was lost at Cadia mine (94G) during the voltage dip when 947 tripped. Approx 10minutes after TAR load was not restored at Cadia. The Indji System was interrogated and indicated a lightning strike occurred on structure 594. This structure and surround | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
1323 | 101894 | Relay | Non TransGrid Reason | TRUE | Cont | No FR | NA |  | 2012-F-0010 | 8C1 Molong - Cumnock Tee Orange West 66kV Line | S | 2012Q1 | MOL |  | TL | 2012-01-05 15:47 | 2012-01-05 17:41 | Approx 890kW of load interrupted. 8C1 did not indicate that an auto reclose happened. Scada shows R/C control point is auto. Computer at Desk shows Auto Reclose Enabled and cyclo indicates no second shot. see package note for protection information. |  |  | Approx 890kW of load interrupted. 8C1 did not indicate that an auto reclose happened. Scada shows R/C control point is auto. Computer at Desk shows Auto Reclose Enabled and cyclo indicates no second shot. See package note for protection information. | Thunderstorm | Primary Equipment | [5 empty] | 0 | 0 | 2012 | Auto reclose failure is a control system failure, not protection
1329 | 101922 | Animal/Bird | Animal/Bird | TRUE | Cap | No FR | NA |  | 2012-F-0023 | No.3 Capacitor | Z | 2012Q1 | SYW |  | CAP | 2012-01-08 18:22 | 2012-01-09 11:04 | No.3 Capacitor was inspected. A small flash mark has been observed on one can which is suspected to be caused by a bird. Substations Team Leader advised that No.3 Capacitor is available for service. | 17/01/2012 1:54:00 PM ¦ Nil ¦ Nil |  | Both Neutral unbalance protections operated. On inspection, a small flash mark was observed on one can which was caused by a bird. | Fine | External | [5 empty] | 0 | 0 | 2012
1332 | 102038 | Bushfire | Bushfire | TRUE | TL | Y | 70.6 |  | 2012-F-0032 | 23 Munmorah - Vales Point 330kV TL | Z | 2012Q1 | MN1, VP1 |  | TL | 2012-01-11 16:14 | 2012-01-11 16:14 | There was a large bushfire burning just outside the switchyard fence at Munmorah end at the time of the TAR. | 13/01/2012 8:56:00 AM ¦ NIL |  | There was a large bushfire burning just outside the switchyard fence at Munmorah end at the time of the TAR. | Very Windy | External | [5 empty] | 0 | 0 | 2012
1898 | 102258 | Lightning/Storm | Lightning or Storm | TRUE | TL | No FR | NA |  | 2012-F-0056 | 944 Wallerawang 132 - Orange 132kV TL | Z | 2012Q1 | ORG, WW2, ONO |  | TL | 2012-01-21 13:06 | 2012-01-21 13:06 | Fault Location from Orange 52.98km Protection details required from Wallerawang 132. | 10/02/2012 7:45:00 AM ¦ Nil ¦ Trip noted for the next scheduled line patrol. |  | Fault Location from Orange 52.98km. Protection details required from Wallerawang 132. Trip noted for the next scheduled line patrol. | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
1900 | 102534 | Unknown | Unknown | TRUE | Cap | No FR | NA |  | 2012-F-0070 | No.3 Capacitor | Z | 2012Q1 | DNT |  | CAP | 2012-01-27 13:41 | 2012-01-27 16:46 | No.3 Capacitor tripped on scada close at 1341hrs. CB 4732 & Bank inspected and no sign of any damage. Maintenance Manager advised and Ok'ed attempt close. NCM. No.3 capacitor placed in successfully at 1646hrs. |  |  | No.3 Capacitor tripped on scada close at 1341hrs. CB 4732 & Bank inspected and no sign of any damage. No.3 capacitor returned to service at 1646hrs. | Fine | Unexplained | [5 empty] | 0 | 0 | 2012 | Unknown reason for trip, no further info in QAPR report, THEOS & Opslog
1901 | 102536 | Secondary Equipment | Sec Eqt Malfunction | TRUE | AC/DC | No FR | NA |  | 2012-F-0072 | No.2 Transformer 330/132/11kV | Z | 2012Q1 | SYS |  | TX | 2012-01-27 16:15 | 2012-01-27 17:16 | Staff were chasing a battery earth fault in wiring associated with No.2 Transformer at the time of the trip. A wiring loom was moved slightly in CB 5422 common cabinet. Ok'ed to investigate further for battery earth fault while transformer is out of servi | 1/02/2012 10:02:00 AM ¦ Nil ¦ Nil |  | Staff were chasing a battery earth fault in wiring associated with No.2 Transformer at the time of the trip. A wiring loom was moved slightly in CB 5422 common cabinet. Allowed to investigate further for battery earth fault while transformer is out of ser | Rain | Secondary Equipment | [5 empty] | 0 | 0 | 2012
1903 | 103182 | Switching error | Unknown | TRUE | Prev | No FR | NA |  | 2012-F-0077 | No.1 Tie Transformer 500/330kV | Z | 2012Q1 | MTP |  | TX | 2012-02-06 12:52 | 2012-02-06 12:56 | Tripped during oil sampling | 21/02/2012 2:52:00 PM ¦ Nil. ¦ Further Warning stickers are to be placed next to the Auto/Manual changeover switch. An investigation into wiring modifications and addition of locks on the switch is to be carried out. |  | Staff were taking an oil sample and inadvertently tripped No 1 Transformer by not following the procedure. They did not isolate 2 of the oil pumps before switching the pumps from auto to manual. All 4 oil pump turned on when switched to manual and the oil | Fine | Maintenance | [5 empty] | 0 | 1 | 2012 | Failure to isolate oil pumps during test caused protection operation
1917 | 103392 | Lightning/Storm | Lightning or Storm | TRUE | TL | NA - EF | 289.1 |  | 2012-F-0080 | O1 Upper Tumut - Canberra 330kV TL | Z | 2012Q1 | CA1, UT1 |  | TL | 2012-02-09 14:52 | 2012-02-09 14:52 | CB 012B manually closed via Scada @ Canberra 1453 HRS .DTF 11km's from UTSS | 27/04/2012 12:00:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | CB 012B manually closed via Scada @ Canberra 1453 HRS. DTF 11km's from UTSS. This has been noted for the next scheduled aerial patrol. |  | External | [5 empty] | 0 | 0 | 2012
1918 | 103395 | Lightning/Storm | Lightning or Storm | TRUE | TL | Y | 51.4 |  | 2012-F-0083 | 5A6 Mt Piper 500kV - Bannaby 500kV TL | Z | 2012Q1 | MTP, BBY |  | TL | 2012-02-09 22:16 | 2012-02-09 22:16 | Distance from MTP to fault 33.19km | 5/03/2012 3:31:00 PM ¦ Nil. ¦ Nil. |  | Distance from MTP to fault 33.19km | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
1905 | 103400 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 | NA | NA |  | 2012-F-0088 | No.2 Generator 330kV CB 5222 | Q | 2012Q1 | ER0 |  | CB | 2012-02-10 04:05 | 2012-02-10 05:50 | CB 5222 SF6 Depleted alarm CB opened via SCADA. |  |  | CB 5222 SF6 Depleted alarm CB opened via SCADA. | Mild | Oil/Gas Levels | [5 empty] | 0 | 0 | 2012
1906 | 103402 | Lightning/Storm | Lightning or Storm | TRUE | TL | No FR | NA |  | 2012-F-0090 | 999 Yass - Cowra 132kV TL | Z | 2012Q1 | CW2, YSN |  | TL | 2012-02-10 06:00 | 2012-02-10 06:00 | DTF 40.64km ex Yass, Storms at time of fault | 27/04/2012 1:58:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | DTF 40.64km ex Yass, Storms at time of fault. This has been noted for the next scheduled aerial patrol. |  | External | [5 empty] | 0 | 0 | 2012
1907 | 103498 | Lightning/Storm | Lightning or Storm | TRUE | TL | Y | 54.1 |  | 2012-F-0092 | 5A3 Bayswater - Mt Piper 500kV TL | Z | 2012Q1 | BAY, MTP |  | TL | 2012-02-10 14:09 | 2012-02-10 14:09 |  | 20/02/2012 11:11:00 AM ¦ NIL ¦ The suspect fault has been noted for next scheduled patrol of the line. |  | The Indji lightning locator has confirmed lightning strike in the area around structure 43 of the line. This is well clear of any road crossings and hence no action is required at this stage. However the suspect fault has been noted for next scheduled pat | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
1908 | 103503 | Lightning/Storm | Lightning or Storm | TRUE | TL | No FR | NA |  | 2012-F-0094 | 947 Mt Piper 132 - Wellington tee Orange 132kV TL | Z | 2012Q1 | MPP, ORG, WL1, ONO |  | TL | 2012-02-11 01:40 | 2012-02-11 01:40 |  | 14/02/2012 8:16:00 AM ¦ Nil ¦ Affected area noted for the next scheduled patrol. |  | Indji System indicated a lightning strike in the area of structures 660 - 662. No road corssings in this area. Affected area noted for the next scheduled patrol. | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
1920 | 103517 | Lightning/Storm | Unknown | TRUE | TL | No FR | NA |  | 2012-F-0104 | 9U3 Gunnedah - Narrabri 132kV TL | Z | 2012Q1 | GN2, NB2 |  | TL | 2012-02-12 05:16 | 2012-02-12 05:16 |  | 29/02/2012 8:56:00 AM ¦ NIL ¦ Close inspection of the line in the area of the suspect fault. |  | line tripped and autoreclosed at both ends on white phase earth fault. Distance to fault as 81km from Narrabri end which works out to be in the area around structure 392 of the line. Ground inspection of road crossings at structures 382 and 408 shows no e | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
1909 | 103516 | Lightning/Storm |  | TRUE | TL | Y | 81.4 |  | 2012-F-0103 | 16 Marulan - Avon 330kV TL | Z | 2012Q1 | AVS, MRN |  | TL | 2012-02-12 13:19 | 2012-02-12 13:19 | Lightning and Stoms in the area. | 20/02/2012 10:40:00 AM ¦ Nil. ¦ Area noted for the next scheduled patrol. |  | Lightning and Stoms in the area. Indji System indicated a lightning strike in the area of structures 159 - 160. No road crossings in this area. Area noted for the next scheduled patrol. | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
1910 | 103533 | Lightning/Storm | Lightning or Storm | TRUE | TL | Y | 105.6 |  | 2012-F-0107 | 71 Wallerawang - Mt Piper 330kV TL | Z | 2012Q1 | MTP, WW1 |  | TL | 2012-02-13 14:19 | 2012-02-13 14:19 | CB 5072 is not set up to A/R for a 71 T/L trip, thus was manually closed when the No.1 Gen TX group was returned to service | 14/03/2012 2:24:00 PM ¦ Nil ¦ Nil |  | CB 5072 is not set up to A/R for a 71 T/L trip, thus was manually closed when the No.1 Gen TX group was returned to service | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
1911 | 103554 | Lightning/Storm | Lightning or Storm | TRUE | TL | Y | 109.2 |  | 2012-F-0112 | O1 Upper Tumut - Canberra 330kV TL | Z | 2012Q1 | CA1, UT1 |  | TL | 2012-02-13 15:52 | 2012-02-13 15:52 | CB 012B at Canberra closed via SCADA. Lightning in area. Protection Details at CA1 No.1 Prot CAO1,30B BF613 No.2 Prot CAO2 30D BF623, 30F BF622, DTF 99% | 12/09/2012 9:20:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | CB 012B at Canberra closed via SCADA. Lightning in area. Protection Details at CA1 - No.1 Prot CAO1,30B BF613, No.2 Prot CAO2 30D BF623, 30F BF622, DTF 99%, Waiting on Protection Details for Upper Tumut. | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
1922 | 104203 | Lightning/Storm | Lightning or Storm | TRUE | TL | No FR | NA |  | 2012-F-0124 | 944 Wallerawang 132 - Orange 132kV TL | Z | 2012Q1 | ORG, WW2, ONO |  | TL | 2012-02-18 14:00 | 2012-02-18 14:00 | Storm activity at time of tripping | 6/03/2012 8:18:00 AM ¦ Nil. ¦ Patrol of the area of structures 40 - 45 being undertaken. |  | Storm activity at time of tripping Patrol of the area of structures 40 - 45 being undertaken. | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
1913 | 104211 | Lightning/Storm | Lightning or Storm | TRUE | TL | Y | 73.1 |  | 2012-F-0131 | 63 Wagga 330 - Darlington Point 330kV TL | Z | 2012Q1 | DNT, WG1 |  | TL | 2012-02-19 15:07 | 2012-02-19 15:07 | At Darlington Point CB'ers X52, 7442 & 7432 manually closed by SCADA. | 27/04/2012 3:37:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | At Darlington Point CB'ers X52, 7442 & 7432 manually closed by SCADA. This has been noted for the next scheduled aerial patrol. | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
1912 | 104208 | Lightning/Storm | Lightning or Storm | TRUE | TL | Y | 59.1 |  | 2012-F-0129 | 8E Armidale - Dumaresq 330kV TL | Z | 2012Q1 | AR1, DMQ |  | TL | 2012-02-19 17:41 | 2012-02-19 17:41 | Information from MITS events, white phase associated with both Cb's had single pole reclose at Dumaresq end. Storms were present at time of tripping AR1 - Mits log filled with alarms from SVC. Single Pole Fault white phase Distance to fault reading see | 5/03/2012 11:17:00 AM ¦ NIL ¦ Close inspection of the line in the area of the suspect fault. |  | Information from MITS events, white phase associated with both Cb's had single pole reclose at Dumaresq end. Storms were present at time of tripping. Close inspection of the line in the area of the suspect fault. | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
1924 | 104366 | HV Equipment | HV Equipment Failure | TRUE | Other | NA | NA |  | 2012-F-0137 | 804 Tamworth 132 - Nundle 66kV Line | Q | 2012Q1 | TA2 |  | TL | 2012-02-20 18:12 | 2012-02-20 22:39 | Broken jumper blue phase 8 metres from landing span. Also red phase 8 metres from landing span. Repairs carried out & rts |  |  | Broken jumper blue phase 8 metres from landing span. Also red phase 8 metres from landing span. Repairs carried out & rts | Thunderstorm | Primary Equipment | [5 empty] | 0 | 0 | 2012
1925 | 104538 | HV Equipment | Sec Eqt Malfunction | TRUE | SVC | No FR | NA |  | 2012-F-0138 | No.1 Static VAR Compensator | Z | 2012Q1 | BKH |  | SVC | 2012-02-23 10:41 | 2012-02-23 15:42 | Problem with blocked CW filter. RTS after cleaning filter. | 7/06/2012 2:52:00 PM |  | SVC tripped. Blocked water filter found. | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
1926 | 104558 | HV Equipment | Sec Eqt Malfunction | TRUE | SVC | No FR | NA |  | 2012-F-0139 | No.1 Static VAR Compensator | Z | 2012Q1 | BKH |  | SVC | 2012-02-23 21:19 | 2012-02-29 14:09 | Previous cooling system alarms cleared @ 2116. Pipe associated with thyristor cooling system ruptured 3 minutes later. RTS after repairs | 7/06/2012 2:57:00 PM |  | Cooling system alarms reset & filters swapped. However @ 2119 cooling water pipe associated with thyristors burst & spraying water over thyrisyors resulting in trip of SVC. |  | Primary Equipment | [5 empty] | 0 | 0 | 2012
1927 | 104996 | Unknown | Unknown | TRUE | TL | NA -EF | 247.2 |  | 2012-F-0149 | 2 Upper Tumut - Yass 330kV TL | Z | 2012Q1 | UT1, YSN |  | TL | 2012-03-01 14:58 | 2012-03-01 14:58 |  | 12/09/2012 9:54:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Rain | Rain | Unexplained | [5 empty] | 0 | 0 | 2012
1928 | 105297 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 | No FR | NA |  | 2012-F-0155 | 9NA Newcastle - Beresfield 132kV Line | Q | 2012Q1 | NEW |  | TL | 2012-03-06 17:13 | 2012-03-07 10:49 |  | 16/03/2012 2:14:00 PM ¦ NIL ¦ NIL |  | Loose link tigtened and attempt to close CB unsuccessful. However could hear close coil operation CB has a Mech problem. | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
1929 | 105350 | HV Equipment | Unknown | TRUE | CB SF6 |  |  |  | 2012-F-0156 | 18 Dapto 330kV CB 182 | Q | 2012Q1 | KVS |  | CB | 2012-03-07 12:31 | 2012-03-07 12:57 | @ Kangaroo Valley 330kV Switching Station C.B.. 182 & C.B.. 5432 - OPENED, on SCADA pole discrepancy alarms, TG staff working on C.B.. 5442 at time of trips, had received pole discr. alarm on this C.B. as well. Checked with staff on site & C.B.. 5442 woul | 18/06/2012 9:30:00 AM ¦ Nil ¦ Substations System Engineer notified and further investigation into these CB types underway. |  | Investigation carried out and identified a wiring problem that had both battery negatives paralleled through the pole discrepancy relay coils. TransGrid staff removed this wiring and restored supplies and CB 5442 was returned to service. Substations Syste | Fine | Unexplained | [5 empty] | 0 | 0 | 2012
1930 | 105357 | HV Equipment | Sec Eqt Malfunction | TRUE | CB SF6 | No FR | NA |  | 2012-F-0157 | Unit 3 Transformer 330kV CB 5432 | Q | 2012Q1 | KVS |  | CB | 2012-03-07 12:31 | 2012-03-07 12:58 | @ Kangaroo Valley 330kV Switching Station C.B.. 182 & C.B.. 5432 - OPENED, on SCADA pole discrepancy alarms, TG staff working on C.B.. 5442 at time of trips, had received pole discr. alarm on this C.B. as well. Checked with staff on site & C.B.. 5442 woul | 18/06/2012 9:32:00 AM ¦ As Above ¦ As Above |  | C.B 182 & C.B 5432 - OPENED, on SCADA pole discrepancy alarms, TG staff working on C.B.. 5442 at time of trips, had received pole discr. alarm on this C.B. as well. Investigation carried out and identified a wiring problem that had both battery negatives | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
1931 | 105821 | Animal/Bird | Unknown | TRUE | Cap | No FR | NA |  | 2012-F-0165 | No.1 Capacitor | Z | 2012Q1 | SYN |  | CAP | 2012-03-15 13:26 | 2012-03-16 09:31 | Dead crow found between red phase & earth 2nd bank from top. | 23/05/2012 9:39:00 AM ¦ Nil ¦ Nil |  | Dead crow found between red phase & earth 2nd bank from top. | Fine | External | [5 empty] | 0 | 0 | 2012
1932 | 105899 | HV Equipment | HV Equipment Failure | TRUE | Disc | NA | NA |  | 2012-E-0005 | No.7 Capacitor | E | 2012Q1 | SYW |  | CAP | 2012-03-17 16:34 | 2012-06-25 17:28 | Phil Baigent advises during switching to RTS 330kV B Bus No.1 Section at SYW, unable to fully close Red Phase of No.7 Capacitor Bus Disconnector.. 5773. Requested No.7 Capacitor Bus Disconnector.. 5773 be left LOCKED OPEN. | 23/05/2012 10:04:00 AM ¦ Nil ¦ Work Order raised to repair Disconnector. |  | During switching to RTS 330kV B Bus No.1 Section at SYW, unable to fully close Red Phase of No.7 Capacitor Bus Disconnector 5773. No.7 Capacitor Bus Disconnector 5773 left LOCKED OPEN. Work Order raised to repair Disconnector. | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
1933 | 106174 | Unknown | Unknown | TRUE | CB SF6 | No FR | NA |  | 2012-F-0171 | 37 Macarthur B CB 372B | Q | 2012Q1 | KCR |  | CB | 2012-03-21 18:04 | 2012-03-21 19:03 | Staff were working on the No.1 Capacitor C.B.. 5712 at the time. Advised that C.B.. 372B tripped at the same time as: - C.B.. 5712 Abnormal Al. - C.B.. 5712 POW relay fail Al. - L.V. C.B. or C.T. Abnormal Al. - Sub Misc Equip Fail Al. (battery earth) No | 18/06/2012 8:43:00 AM ¦ Nil ¦ Substations System Engineer notified and further investigation into these CB types underway. |  | Staff were working on the No.1 Capacitor C.B.. 5712 at the time. Advised that C.B.. 372B tripped at the same time as: - C.B.. 5712 Abnormal Al. - C.B.. 5712 POW relay fail Al. - L.V. C.B. or C.T. Abnormal Al. - Sub Misc Equip Fail Al. (battery earth) ¦ No | Fine | Unexplained | [5 empty] | 0 | 0 | 2012
1934 | 106271 | Switching error | Sec Eqt Staff Error | TRUE | Prev | No FR | NA |  | 2012-F-0177 | 42 Sydney South - Haymarket 330kV Cable | Z | 2012Q1 | HYM, SYS |  | UG | 2012-03-26 06:07 | 2012-03-26 06:14 | No.2 Transformer being taken out of service and 42 Cable on load at Haymarket via C.B. 5412B only. During switching on No.2 Transformer, 42 Cable V.T. secondary circuits were opened in error when carrying out step to isolate No.2 Transformer 330kV V.T. se |  |  | No.2 Transformer being taken out of service and 42 Cable on load at Haymarket via C.B. 5412B only. During switching on No.2 Transformer, 42 Cable V.T. Secondary circuits were opened in error when carrying out step to isolate No.2 Transformer 330kV V.T. Se | Fine | Maintenance | [5 empty] | 1 | 1 | 2012 | VT secondary circuits opened in error leading to incorrect protection operation
1936 | 106277 | HV Equipment | HV Equipment Failure | TRUE | Rx | NA | NA |  | 2012-F-0178 | No.2 330kV Reactor | Z | 2012Q1 | AR1 |  | RX | 2012-03-26 07:17 | 2012-04-15 15:21 | RX taken out of service due to Buchholz alarm. CB 5922 developed pole discrepency condition when open attempted (red phase still closed). | 27/06/2012 3:53:00 PM ¦ Nil. ¦ A report is being prepared by Substations/Northern with any future actions to be determined based on the recommendations of that report and in consultation with Substation Systems Engineer/Asset Performance. |  | RX taken out of service due to Buchholz alarm. CB 5922 developed pole discrepency condition when open attempted (red phase still closed). | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
1315 | 106277 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 | NA | No FR |  | 2012-F-0178 | No.2 330kV Reactor | Z | 2012Q1 | AR1 |  | RX | 2012-03-26 07:17 | 2012-04-15 15:21 | RX taken out of service due to Buchholz alarm. CB 5922 developed pole discrepency condition when open attempted (red phase still closed). | 27/06/2012 3:53:00 PM ¦ Nil. ¦ A report is being prepared by Substations/Northern with any future actions to be determined based on the recommendations of that report and in consultation with Substation Systems Engineer/Asset Performance. |  | RX No.1 Reactor was taken out of service due to Buchholz alarm. CB 5922 also developed pole discrepency condition when attempting to open. The pole discrepency in CB5922 caused overloading of the Neutral Earthing Reactor and resulted in the buchholz alarm | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
1935 | 106274 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 | NA | NA |  | 2012-E-0006 | 87 Armidale - Coffs Harbour 330kV TL | E | 2012Q1 | AR1, COF |  | TL | 2012-03-26 09:46 | 2012-03-26 09:53 | 87 TL required de-energised as CB 5922 (at Armidale) developed pole discrepency condition when open attempted (red phase still closed). | 27/06/2012 4:02:00 PM ¦ As above. ¦ As above. |  | 87 TL required de-energised as CB 5922 (at Armidale) developed pole discrepency condition when open attempted (red phase still closed). | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
1937 | 106281 | Lightning/Storm | Unknown | TRUE | TL | No FR | NA |  | 2012-F-0179 | 94X Wallerawang 132 (New) - Panorama 132kV TL | Z | 2012Q1 | PMA, WWS |  | TL | 2012-03-27 06:00 | 2012-03-27 06:00 | Outages of 944 & 947 TLs at time. Panorama made radial as pre contingent action. Panorama load interrupted for reclose time. Approximately 40MW (HIS data unavailable). | 24/05/2012 9:30:00 AM ¦ Nil. ¦ Nil. |  | Outages of 944 & 947 TLs at time. Panorama made radial as pre contingent action. Panorama load interrupted for reclose time. Approximately 40MW (HIS data unavailable). | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
1938 | 106306 | Lightning/Storm | Lightning or Storm | TRUE | TL | No FR | NA |  | 2012-F-0180 | 99M Yass - Murrumburrah 132kV TL | Z | 2012Q1 | MRU, YSN |  | TL | 2012-03-27 21:25 | 2012-03-27 21:25 |  | 27/04/2012 3:49:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Thunderstorm. This has been noted for the next scheduled aerial patrol. | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
1939 | 106341 | Unknown | Unknown | TRUE | TL | No FR | NA |  | 2012-F-0181 | 99A Uranquinty - Finley 132kV TL | Z | 2012Q1 | FNY, URQ |  | TL | 2012-03-28 10:18 | 2012-03-28 10:18 |  | 27/04/2012 4:06:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Weather Fine. No.1 Protection W-E Z1 DTF 40.91km, No.2 Protection W-E Z1. This has been noted for the next scheduled aerial patrol. | Fine | External | [5 empty] | 0 | 0 | 2012
1941 | 106389 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 | No FR | NA |  | 2012-F-0185 | 132kV B Bus 1-2 Section CB 4112 | S | 2012Q1 | SYW |  | CB | 2012-03-28 17:11 | 2012-03-29 03:57 |  |  |  | 132kV A2 Bus O/S for maintenance at time of trip, staff found C.B. 4112 failure issue & OHEW above C.B. came down, B1 & B2 Busbars I & E to remove OHEW, C.B. 4112 left isolated from system. Approx 170 MW of load interrupted due to fault. 36.9 MWh of load |  | Primary Equipment | [5 empty] | 0 | 0 | 2012
1944 | 106396 | Staff Error | Sec Eqt Malfunction | TRUE | Prev | No FR | NA |  | 2012-F-0186 | No.1 Transformer 330/132/11kV | Z | 2012Q1 | SYW |  | TX | 2012-03-29 01:14 | 2012-03-29 03:31 | Prior to trip 132kV Bus No.1 section had been energised via closing of No.2 TX CB 4422B. On closing No.1 TX CB 4412B, No.1 TX CB 5412, 4412A & CB 4412B tripped ( also No.2 TX CB 5422 & CB 4422B tripped, refer FEOR 2012-0187). Cause of tripping due to a co | 28/05/2012 10:59:00 AM ¦ Nil. ¦ Nil. |  | Prior to trip 132kV Bus No.1 section had been energised via closing of No.2 TX CB 4422B. On closing No.1 TX CB 4412B, No.1 TX CB 5412, 4412A & CB 4412B tripped ( also No.2 TX CB 5422 & CB 4422B tripped). Cause of tripping due to a contact latch pulsed up | Mild | Maintenance | [5 empty] | 1 | 0 | 2012 | FEOR 2012-F-0186/1 indicates faulty protection relay
1945 | 106397 | Staff Error | Sec Eqt Malfunction | TRUE | Prev | No FR | NA |  | 2012-F-0187 | No.2 Transformer 330/132/11kV | Z | 2012Q1 | SYW |  | TX | 2012-03-29 01:14 | 2012-03-29 03:30 | Refer FEOR 2012-0186 | 28/05/2012 11:01:00 AM ¦ As Above ¦ As Above |  | Prior to trip 132kV Bus No.1 section had been energised via closing of No.2 TX CB 4422B. On closing No.1 TX CB 4412B, No.1 TX CB 5412, 4412A & CB 4412B tripped ( also No.2 TX CB 5422 & CB 4422B tripped). Cause of tripping due to a contact latch pulsed up | Mild | Maintenance | [5 empty] | 1 | 0 | 2012 | FEOR 2012-F-0187/1 indicates faulty protection relay
1946 | 106398 | Unknown | Sec Eqt Malfunction | TRUE | Cont | No FR | NA |  | 2012-F-0188 | No.1 Static VAR Compensator | Z | 2012Q1 | SYW |  | SVC | 2012-03-29 01:14 | 2012-03-29 04:22 | SVC tripped due to loss of auxiliary supply when No.1 & No.2 TX's tripped ( refer FEOR 2012-0186 & 2012-0187). No.1 Aux TX was I/S prior to TX's tripping, No.3 Aux TX CB failed to close causing Diesel to start | 28/05/2012 12:56:00 PM ¦ Nil. ¦ Nil. |  | SVC tripped due to loss of auxiliary supply when No.1 & No.2 TX's tripped ( refer FEOR 2012-0186 & 2012-0187). No.1 Aux TX was I/S prior to TX's tripping, No.3 Aux TX CB failed to close causing Diesel to start | Mild | Secondary Equipment | [5 empty] | 0 | 0 | 2012
1947 | 106471 | Lightning/Storm | Non TransGrid Reason | TRUE | TL | Y | 57.3 |  | 2012-F-0190 | 32 Sydney West - Bayswater 330kV TL | Z | 2012Q1 | BAY, SYW |  | TL | 2012-03-29 13:42 | 2012-03-29 13:42 | Thunderstorms in area at time of incident | 30/04/2012 9:59:00 AM ¦ NIL ¦ Close inspection of the line in the area of the suspect fault. |  | Thunderstorms in area at time of incident. Close inspection of the line in the area of the suspect fault. | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
1974 | 106974 | Unknown | Unknown | TRUE | TL | No FR | NA |  | 2012-F-0204 | 99L Deniliquin - Coleambally 132kV TL | Z | 2012Q1 | CLY, DN2 |  | TL | 2012-03-29 17:48 | 2012-04-12 10:32 | CB 99L2 closed @ Coleambelly on Wed 12/4 following this trip. Auto reclose confirmed AUTO by staff on site | 12/09/2012 10:15:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Staff at Deniliquin had advised the SO/S on Thurs 12/04/12 that 99L Coleambally to Deniliquin 132kV T/L had a trip and reclose on 29/03/12. On investigation loadings on the SCADA indicated that 99L CB could still be open at Coleambally. Essential Energy w | Unknown | Unexplained | [5 empty] | 0 | 0 | 2012 | Reclose failure is a control system failure, not protection
1957 | 106974 | Relay | Unknown | TRUE | Cont | No FR | NA |  | 2012-F-0204 | 99L Deniliquin - Coleambally 132kV TL | Z | 2012Q1 | CLY, DN2 |  | TL | 2012-03-29 17:48 | 2012-04-12 10:32 | CB 99L2 closed @ Coleambelly on Wed 12/4 following this trip. Auto reclose confirmed AUTO by staff on site | 12/09/2012 10:15:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Staff at Deniliquin had advised the SO/S on Thurs 12/04/12 that 99L Coleambally to Deniliquin 132kV T/L had a trip and reclose on 29/03/12. On investigation loadings on the SCADA indicated that 99L CB could still be open at Coleambally. Essential Energy w | Unknown | Primary Equipment | [5 empty] | 0 | 0 | 2012 | Duplicate
1948 | 106481 | Unknown | Animal/Bird | TRUE | TL | No FR | NA |  | 2012-F-0191 | 94M Mt Piper 132 - Beryl tee Mudgee 132kV TL | Z | 2012Q1 | BER, MPP |  | TL | 2012-03-30 07:41 | 2012-03-30 07:41 | No1 Protection Pnl 6 b Relay Type (Optimho) F85 Tripping relay flag Z1 BN Fault duration 49mS Pre fault Va 78.65kV 0.0 phase degrees Vb 78.69kV - 120.3 phase degrees Vc 78.46 kV 119.7 degrees Ia 0.0499kA -177.8 degrees Ib 0.0462kA 60.8 degrees Ic 0.0451k | 24/05/2012 9:51:00 AM ¦ Nil. ¦ Nil. |  | Weather Fog. OpsLog: At 07:41:47hrs 94M Mt Piper 132 to Beryl tee Mudgee and Ilford 132 kV T/L tripped and reclosed. Cause unknown at this stage. 7 MWatts of load lost at Ulan Mine and approximately 15 Mwatts at Essential energy's zone substations. | Fog | Unexplained | [5 empty] | 0 | 0 | 2012
1952 | 106775 | HV Equipment | Unknown | TRUE | TX | NA |  |  | 2012-F-0197 | No.3 Transformer 132/66/11kV | Z | 2012Q2 | NB2 |  | TX | 2012-04-04 08:51 | 2012-04-04 18:51 | Low oil level reported in conservator by field staff. Evidence of approximately 50mm of oil observed within transformer bund. No alarms or indication of problem received in control room or locally. Transformer removed from service immediately & prepared f | 21/06/2012 2:16:00 PM ¦ Nil. ¦ Nil. |  | Low oil level reported in conservator by field staff. Evidence of approximately 50mm of oil observed within transformer bund. No alarms or indication of problem received in control room or locally. The oil was found to be leaking from a failed gasket on t | Fine | Oil/Gas Levels | [5 empty] | 0 | 0 | 2012
1953 | 106870 | Relay | Unknown | TRUE | Prot | NA |  |  | 2012-F-0198 | No.1 Taree - Council Bootawa 33kV Line | Q | 2012Q2 | TRE |  | TL | 2012-04-05 10:43 | 2012-04-05 12:47 | Customer advised that protection operation did not occur from within it's system. That is, trip occured from Taree 132kV Substation only. Subsequent action by customer resulted in opening No.1 Feeder within it's system to sectionalise. CB 12 successfully | 6/06/2012 3:36:00 PM ¦ Nil. ¦ Nil. |  | Protection operation did not occur from within customer's system. Customer opened feeder within it's system to sectionalise. CB 12 successfully closed at request of customer & placed on load. Similar alleged spurious protection operation on No.1 protectio | Fine | Primary Equipment | [5 empty] | 1 | 0 | 2012 | QAPR report indicates protection relay fault
1954 | 106885 | Unknown | Unknown | TRUE | TL | Yes | 60.5 |  | 2012-F-0199 | 5A6 Mt Piper 500kV - Bannaby 500kV TL | Z | 2012Q2 | MTP, BBY |  | TL | 2012-04-06 06:18 | 2012-04-06 06:18 | Distance to Fault from BBY 131.18 Distance to fault from Mount Piper 20.92 km's | 24/05/2012 11:07:00 AM ¦ Nil. ¦ Nil. |  | Distance to Fault from BBY 131.18. Distance to fault from Mount Piper 20.92 km's. No storms in the area at time of tripping. A patrol of the area was undertaken on 07/04/2012 from structures 51 - 63. No indication of flashover was noticed. Small birds and | Fine | Unexplained | [5 empty] | 0 | 0 | 2012
1955 | 106890 | Unknown/Storm | Unknown | TRUE | TL | No FR |  |  | 2012-F-0201 | 99K Darlington Pt - Griffith 132kV TL | Z | 2012Q2 | DNT, GRF |  | TL | 2012-04-09 17:22 | 2012-04-09 17:22 | Advised high wind in area | 12/09/2012 9:24:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Advised high wind in area | Fine | Unexplained | [5 empty] | 0 | 0 | 2012
1956 | 106914 | HV Equipment | HV Equipment Failure | TRUE | TX | NA |  |  | 2012-E-0007 | No.1 Transformer 132/66/11kV | E | 2012Q2 | INV |  | TX | 2012-04-10 21:48 | 2012-04-12 18:30 | TX taken out of service due to Buchholz alarm. Gas /oil tested OK. TX RTS. | 22/06/2012 3:45:00 PM ¦ Nil. ¦ Nil. |  | TX taken out of service due to Buchholz alarm. Gas /oil tested OK. TX RTS. Inspections revealed that the Transformer's external conservator bag was depleted of nitrogen. The transformer oil had recently been degassed and it is believed that this may have | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
1958 | 107140 | Fire | Unknown | TRUE | TL | No FR |  |  | 2012-F-0205 | 99F Uranqunity - Yanco 132kV TL | Z | 2012Q2 | YA2, URQ |  | TL | 2012-04-13 14:18 | 2012-04-13 14:18 | Staff advised that farmers were burning off in the area. | 27/04/2012 4:44:00 PM ¦ N/A. ¦ Communicate the likely nature of this fault to the relevant property owners. |  | Staff advised that farmers were burning off in the area. TG is communicating the likely hood of faults caused by burning to the relevant property owners. | Fine | External | [5 empty] | 0 | 0 | 2012
1959 | 107156 | Unknown | Unknown | TRUE | TL | No FR |  |  | 2012-F-0207 | 968 Tamworth 330 - Narrabri 132kV TL | Z | 2012Q2 | NB2, TA1 |  | TL | 2012-04-15 04:23 | 2012-04-15 04:23 |  | 29/05/2012 9:50:00 AM ¦ NIL ¦ Close inspection of the line during the next routine inspection. |  | Rain. Protection flagging indicated a blue phase fault to earth, with a distance to fault of between 36.9km and 49.7km from the Tamworth 330 end, which corresponds to a fault between structures 137-203. There is no Travelling Wave Fault Locator set up on | Rain | Unexplained | [5 empty] | 0 | 0 | 2012
1961 | 107220 | Relay | Lightning or Storm | TRUE | Prot | NA |  |  | 2012-F-0212 | No.1 Taree - Council Bootawa 33kV Line | Q | 2012Q2 | TRE |  | TL | 2012-04-16 10:00 | 2012-04-16 10:00 |  |  |  | TG Relay Fault. Only protection 2 operated: y-b , Zone 3. Essential Energy did not have a fault at their end of the line. No2 Prot YTG replaced on WO 211184 | Thunderstorm | Primary Equipment | [5 empty] | 1 | 0 | 2012 | QAPR report indicates protection relay fault
1962 | 107226 | Relay | Unknown | TRUE | Prot | NA |  |  | 2012-F-0213 | No.1 Taree - Council Bootawa 33kV Line | Q | 2012Q2 | TRE |  | TL | 2012-04-16 10:05 | 2012-04-16 10:05 |  |  |  | TG Relay Fault. Only protection 2 operated: y-b , Zone 3. Essential Energy did not have a fault at their end of the line. No2 Prot YTG replaced on WO 211184 | Thunderstorm | Primary Equipment | [5 empty] | 1 | 0 | 2012 | QAPR report indicates protection relay fault
1963 | 107227 | Relay | Unknown | TRUE | Prot | NA |  |  | 2012-F-0214 | No.1 Taree - Council Bootawa 33kV Line | Q | 2012Q2 | TRE |  | TL | 2012-04-16 10:07 | 2012-04-16 10:07 |  |  |  | TG Relay Fault. Only protection 2 operated: y-b , Zone 3. Essential Energy did not have a fault at their end of the line. No2 Prot YTG replaced on WO 211184 | Thunderstorm | Primary Equipment | [5 empty] | 1 | 0 | 2012 | QAPR report indicates protection relay fault
1964 | 107229 | Relay | Unknown | TRUE | Prot | NA |  |  | 2012-F-0215 | No.1 Taree - Council Bootawa 33kV Line | Q | 2012Q2 | TRE |  | TL | 2012-04-16 10:21 | 2012-04-16 19:41 | protection Tech investigating protn on #2 prot with the view of relay replacement Zero loss of load since this is a ring feed. Line successfully placed in service and on load after No.2 protection relay replacement at 1941. |  |  | TG Relay Fault. Only protection 2 operated: y-b , Zone 3. Essential Energy did not have a fault at their end of the line. Defect W/O 211184 created. Relay appeared to intermittently lose Zone 3 restraint & randomly trips. Relay replaced & tested OK. | Thunderstorm | Primary Equipment | [5 empty] | 1 | 0 | 2012 | QAPR report indicates protection relay fault
1960 | 107182 | HV Equipment | HV Equipment Failure | TRUE | TX | NA |  |  | 2012-E-0008 | No.3 Transformer 330/132/11kV | E | 2012Q2 | SYW |  | TX | 2012-04-16 11:29 | 2012-04-16 11:29 | Advised to off load and de-energise by P Hazletine. Suspect Bushing on Transformer. Condition Monitor Alarm L1 initiated. RTS 1008hrs 26/4/12 after bushing replacement. | 23/05/2012 3:41:00 PM ¦ Nil. ¦ Investigation underay into Trench type 132kV Bushings and methods of testing and eventual replacement of these Trench type bushings. |  | Advised to off load and de-energise by P Hazletine. Suspect Bushing on Transformer. Condition Monitor Alarm L1 initiated. Investigation underway into Trench type 132kV Bushings and methods of testing and eventual replacement of these Trench type bushings. | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
1965 | 107642 | Unknown | Unknown | TRUE | TL | No FR |  |  | 2012-F-0222 | 99T Darlington Pt - Coleambally 132kV TL | Z | 2012Q2 | CLY, DNT |  | TL | 2012-04-21 06:45 | 2012-04-21 08:30 | As no SCADA at Colembaly, Ess En staff called out to check CB 99T2 status following failure of CB 99L2 to close @ Colembaly a few weeks ago | 12/09/2012 10:18:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol |  | As no SCADA at Colembaly, Ess En staff called out to check CB 99T2 status following failure of CB 99L2 to close @ Colembaly a few weeks ago. Tech tested A/R to terminals on wing of panel as Fdr could not be removed from service due to faulty disconnector | Fine | Unexplained | [5 empty] | 0 | 0 | 2012
1971 | 108234 | Unknown | Unknown | TRUE | TL | No FR |  |  | 2012-F-0240 | 99L Deniliquin - Coleambally 132kV TL | Z | 2012Q2 | CLY, DN2 |  | TL | 2012-04-23 04:24 | 2012-04-23 04:24 | No fault recorded by Scada at this time. | 12/09/2012 9:42:00 AM ¦ N/A ¦ 20 Structures either side of DTF reading have been noted for the next scheduled aerial patrol. |  | No fault recorded by Scada at this time. | Unknown | Unexplained | [5 empty] | 0 | 0 | 2012
1967 | 107733 | HV Equipment | Unknown | TRUE | TX | NA |  |  | 2012-F-0230 | No.1 Transformer 220/22kV | C | 2012Q2 | BRD |  | TX | 2012-04-25 08:50 | 2012-04-25 09:45 | Buchholz Gas Accumulation alarm being investigated. Staff went to carry out low level bleed of Buchholz Relay and transformer tripped immediately bleed valve was opened. Field staff suspect issues with Buchholz Relay. Arrangements made after transformer R | 7/06/2012 2:20:00 PM ¦ Another outage is planned to investigate the airbag in the conservator to see if it is interferring with the oil flow between the conservator and main tank. This air bag is filled with air when the conservator is filled and then the |  | Buchholz Gas Accumulation alarm being investigated. Staff went to carry out low level bleed of Buchholz Relay and transformer tripped immediately after bleed valve was opened. Transformer taken out of service to carry out checks on Buchholz Relay. Relay O | Fine | Maintenance | [5 empty] | 0 | 0 | 2012
1970 | 108011 | Unknown | Unknown | TRUE | TL | No FR |  |  | 2012-F-0238 | 9U4 Glen Innes - Inverell 132kV TL | Z | 2012Q2 | GNS, INV |  | TL | 2012-05-02 06:19 | 2012-05-02 06:19 | No alarms received from Inverell Substation. Staff follow up required to confirm TAR and provide protection details. | 25/06/2012 1:01:00 PM ¦ Nil. ¦ Nil. |  | No alarms received from Inverell Substation. Protection flagging indicated a White phase to Earth fault, with the distance to fault calculated to be approximately 14.5km from the Inverell end, which corresponds to the area around structures 56 and 57. A c | Fog | Unexplained | [5 empty] | 0 | 0 | 2012
1914 | 112630 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 | NA | NA |  | 2012-E-0014 | 83 LIDDELL 330kV A CB 832A | Q | 2012Q2 | MRK |  | CB | 2012-05-06 02:50 | 2012-05-06 03:59 | CB topped up with SF6 |  |  | Low SF6 on CB832A at Muswellbrook clearance to take out of service to top up gas. | Unknown | Oil/Gas Levels | [5 empty] | 0 | 0 | 2012
1973 | 109246 | Relay | Sec Eqt Malfunction | TRUE | Cont | NA |  |  | 2012-E-0009 | No.1 Tie Transformer 500kV A Bus CB 6412A | Q | 2012Q2 | MTP |  | CB | 2012-05-13 14:40 | 2012-05-13 19:24 | Logica control unit (CPU) failed and replaced. CB isolated until repairs completed due to loss of alarm monitoring. | 24/05/2012 3:48:00 PM ¦ Nil. ¦ Nil. |  | Logica control unit (CPU) failed. Power supply replaced. CB was isolated until repairs completed due to loss of alarm monitoring. | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
2157 | 123520 | HV Equipment | HV Equipment Failure | TRUE | Cap |  |  |  | 2012-F-0508 | No.1 Capacitor | Z | 2012Q2 | SYS |  | CAP | 2012-05-17 06:09 | 2012-06-05 14:48 | CB inspected and found broken rod on No.1 Trip coil. |  |  | No.1 Capacitor at Sydney South 330kV Substation tripped on attempt to close. CB inspected and found broken rod on No.1 Trip coil. CB not available until repaired. | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
1975 | 109540 | Unknown | Unknown | TRUE | TL | No FR |  |  | 2012-F-0249 | 99K Darlington Pt - Griffith 132kV TL | Z | 2012Q2 | DNT, GRF |  | TL | 2012-05-17 15:13 | 2012-05-17 15:13 |  | 12/09/2012 10:08:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  |  | Fine | Unexplained | [5 empty] | 0 | 0 | 2012
1980 | 110123 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 | No FR |  |  | 2012-F-0259 | 76 Wallerawang - Sydney South 330kV TL | Z | 2012Q2 | SYS, WW1 |  | TL | 2012-05-21 13:55 | 2012-05-21 14:07 | C.B. 762 tripped when energising 76 Wallerawang to Sydney South 330kV T/L at SYS. Advised probable cause is a pole discrepency issue with C.B. 762 (i.e. protection may have operated correctly for system condition). 76 Wallerawang to Sydney South 330kV T/L | 8/08/2012 11:12:00 AM ¦ Nil. ¦ Nil. |  | C.B. 762 tripped when energising 76 Wallerawang to Sydney South 330kV T/L at SYS. Advised probable cause is a pole discrepency issue with C.B. 762 (i.e. protection has operated correctly for system condition). 76 Wallerawang to Sydney South 330kV T/L retu | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
1976 | 109651 | HV Equipment | Unknown | TRUE | T/C | No FR |  |  | 2012-F-0251 | No.1 Transformer 132/33/11kV | Z | 2012Q2 | TRE |  | TX | 2012-05-21 22:36 | 2012-05-24 18:56 | No significant events within customer system at time of trip. Lightning appears to be off the coast of TRE area. Bay inspected ok, nothing out of the ordinary noted. | 31/05/2012 4:39:00 PM ¦ Nil ¦ Future action to be determined in consultation with Substation Systems Engineer/Asset Performance. |  | No significant events within customer system at time of trip. Lightning appears to be off the coast of TRE area. Bay inspected ok, nothing out of the ordinary noted. It was confirmed that the Operation of the Multrip, the Transformer Diff Relay and the CB | Unknown | Secondary Equipment | [5 empty] | 0 | 0 | 2012
1978 | 110114 | Secondary Equipment | Sec Eqt Malfunction | TRUE | AC/DC | No FR |  | No Load Loss | 2012-F-0257 | No.2 Transformer 330/132/11kV | Z | 2012Q2 | TGH |  | TX | 2012-05-27 09:18 | 2012-05-27 15:33 | No fault recorders operated, no voltage dip or protection operated alarms. Just prior to trip fleeting Misc SS equipment alarms received on Scada. | 22/06/2012 3:12:00 PM ¦ All of the other outdoor distribution boards in the Northern Region (at Muswellbrook, Lismore and Coffs Harbour) will be inspected as they may be at risk of the same defect. ¦ Trip checks are to be carried out on the new No.1 Aux T |  | No fault recorders operated, no voltage dip or protection operated alarms. Just prior to trip fleeting Misc SS equipment alarms received on Scada. All of the other outdoor distribution boards in the Northern Region (at Muswellbrook, Lismore and Coffs Harb | Fine | Secondary Equipment | [5 empty] | 1 | 0 | 2012 | THEOS follow up report indicates AC on DC fault causing incorrect operation of No.2 protection for both transformers, exerpt: "The AC voltage on the No.2 110V DC supply indirectly resulted in the operation of a Repeat relay on each transformer's No.2 Protection schemes, which in turn operated each transformer's No.2 Protection Multitrip relays."
1979 | 110115 | Secondary Equipment | Sec Eqt Malfunction | TRUE | AC/DC | No FR |  | Expect Exclusion of load Loss | 2012-F-0258 | No.1 Transformer 330/132/11kV | C | 2012Q2 | TGH |  | TX | 2012-05-27 11:27 | 2012-05-27 15:31 | Entire central coast load interrupted except for Charmhaven. First load block restored, 123MW after 9 minutes, then remaining 17MW after 17 minutes from start of interruption. | 22/06/2012 3:22:00 PM ¦ As above. ¦ As above. |  | Entire central coast load interrupted except for Charmhaven. First load block restored, 123MW after 9 minutes, then remaining 17MW after 17 minutes from start of interruption. Estimated load lost was 18.1 MWhr or 0.077 System Minutes. It is expected that | Fine | Secondary Equipment | [5 empty] | 1 | 0 | 2012 | THEOS follow up report indicates AC on DC fault causing incorrect operation of No.2 protection for both transformers, exerpt: "The AC voltage on the No.2 110V DC supply indirectly resulted in the operation of a Repeat relay on each transformer's No.2 Protection schemes, which in turn operated each transformer's No.2 Protection Multitrip relays."
1981 | 110297 | Unknown | Unknown | TRUE | TL | No FR |  |  | 2012-F-0261 | 993 Wagga 330 - Gadara 132kV TL | Z | 2012Q2 | GAD, WG1 |  | TL | 2012-05-30 11:37 | 2012-05-30 11:41 | Advised of TAR on 993 Wagga 330 to Gadara 132 kV T/L at Wagga 330kV Substation and Gadara 132kV Substation. Also noting that on SCADA CB 9932 at Gadara took about 3 minutes to reclose, SCADA Sever switch over occurred during the Trip & Reclose operation. | 12/09/2012 9:44:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Advised of TAR on 993 Wagga 330 to Gadara 132 kV T/L at Wagga 330kV Substation and Gadara 132kV Substation. Also noting that on SCADA CB 9932 at Gadara took about 3 minutes to reclose, SCADA Sever switch over occurred during the Trip & Reclose operation. | Fine | Unexplained | [5 empty] | 0 | 0 | 2012
1982 | 110297 | Secondary Equipment | Unknown | TRUE | Cont | No FR |  |  | 2012-F-0261 | 993 Wagga 330 - Gadara 132kV TL | Z | 2012Q2 | GAD, WG1 |  | TL | 2012-05-30 11:37 | 2012-05-30 11:41 | Advised of TAR on 993 Wagga 330 to Gadara 132 kV T/L at Wagga 330kV Substation and Gadara 132kV Substation. Also noting that on SCADA CB 9932 at Gadara took about 3 minutes to reclose, SCADA Sever switch over occurred during the Trip & Reclose operation. | 12/09/2012 9:44:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Advised of TAR on 993 Wagga 330 to Gadara 132 kV T/L at Wagga 330kV Substation and Gadara 132kV Substation. Also noting that on SCADA CB 9932 at Gadara took about 3 minutes to reclose, SCADA Sever switch over occurred during the Trip & Reclose operation. | Fine | Secondary Equipment | [5 empty] | 0 | 0 | 2012
1984 | 110316 | Unknown | Unknown | TRUE | TL | No FR |  |  | 2012-F-0263 | 99L Deniliquin - Coleambally 132kV TL | Z | 2012Q2 | CLY, DN2 |  | TL | 2012-05-30 12:46 | 2012-05-30 12:46 |  | 12/09/2012 9:51:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  |  | Fine | Unexplained | [5 empty] | 0 | 0 | 2012
1985 | 110468 | Unknown | Unknown | TRUE | TL | No FR |  |  | 2012-F-0264 | 99F Uranqunity - Yanco 132kV TL | Z | 2012Q2 | YA2, URQ |  | TL | 2012-06-02 10:39 | 2012-06-02 10:39 | Cause of trip unknown. | 12/09/2012 10:04:00 AM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Cause of trip unknown. | Rain | Unexplained | [5 empty] | 0 | 0 | 2012
1986 | 110566 | HV Equipment | HV Equipment Failure | TRUE | Cap |  |  |  | 2012-F-0265 | No.5 Capacitor | Z | 2012Q2 | SYN |  | CAP | 2012-06-03 14:19 | 2012-06-25 08:13 |  | Nil. ¦ Nil. |  |  | Unknown | Primary Equipment | [5 empty] | 0 | 0 | 2012 | Unknown reason for trip, no information in QAPR report, THEOS, or Opslog
2003 | 111040 | HV Equipment | Unknown | TRUE | CBOil | No FR |  |  | 2012-F-0270 | 707 Port Macquarie - Boronia St No.2 33kV Line | Q | 2012Q2 | PMQ |  | TL | 2012-06-10 01:31 | 2012-06-10 12:59 | Reclose twice prior to lockout as per design at this location. Protection indicates object across feeder, cleared by reclose operation as line now energised into substation. It appears slow CB operation caused LBU operation onto Busbar which is now restor | 25/07/2012 2:12:00 PM ¦ Nil. ¦ A defect is to be raised for in service (first trip) timing checks to be carried out on CB7072 in 6 months time. |  | Reclose twice prior to lockout as per design at this location. Protection indicates object across feeder, cleared by reclose operation as line now energised into substation. It appears slow CB operation caused LBU operation onto Busbar which is now restor | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
2004 | 111044 | Unknown | Unknown | TRUE | TL | Yes | 58.44 |  | 2012-F-0271 | 86 Tamworth 330 - Armidale 330kV TL | Z | 2012Q2 | AR1, TA1 |  | TL | 2012-06-11 06:31 | 2012-06-11 06:31 | Fault recorder operated on TAR @ Armidale. Location in vicinity of Moombi as supported by distance to fault of 15.5 km from Tamworth, 104 km from Armidale. Fault appears to be Red Phase to Earth supported by protection relays at both ends. | 25/06/2012 1:57:00 PM ¦ Nil. ¦ Nil. |  | Fault recorder operated on TAR @ Armidale. Protection flagging indicated a Red phase to Earth fault, with the distance to fault calculated to be between structures 46 and 56. No lightning activity was recorded on the Indji system at the time of the incide | Rain | Unexplained | [5 empty] | 0 | 0 | 2012
2034 | 111082 | Staff Error | HV Equipment Failure | TRUE | Prev | No FR |  |  | 2012-E-0010 | 33kV Bus Section 3 | Q | 2012Q2 | PMQ |  | BB | 2012-06-12 10:37 | 2012-06-12 11:08 | Reported by SSMF performing routine substation maintenance inspection, CB 2122 CT is making an arcing noise from within. Busbar De-energised to allow staff safe approach to isolate CB 2122 CTs for suspected faulty CT. Log entry switching used to de-ene | 12/07/2012 1:12:00 PM ¦ Nil. ¦ A report is being prepared by Substations Northern, with any future actions to be determined based on the recommendations of that report. |  | De-energised after staff at site heard arcing from within one of the CB2122 CT's. An inspection of the CB2122 CT's revealed that the DLA link on the blue phase CT was open. CB2122 and the associated CT's were left out of service pending replacement of the | Fine | [6 empty] | 0 | 0 | 2012
2008 | 111109 | Unknown | Unknown | TRUE | TL | No FR |  |  | 2012-F-0273 | 96M Narrabri - Moree 132kV TL | Z | 2012Q2 | MRE, NB2 |  | TL | 2012-06-12 20:56 | 2012-06-12 20:56 | Line load reduction on reclose, approximately 4MW. Customer advised. | 25/06/2012 2:16:00 PM ¦ Nil. ¦ Nil. |  | Line load reduction on reclose, approximately 4MW. Customer advised. Protection flagging indicated a Red phase to Earth fault, with the distance to fault calculated to be in the vicinity of structure 412. There was no lightning activity recorded on the In | Unknown | Unexplained | [5 empty] | 0 | 0 | 2012
2009 | 111340 | HV Equipment | HV Equipment Failure | TRUE | T/C |  |  |  | 2012-E-0011 | No.1 Transformer 330/66/11kV | E | 2012Q2 | ING |  | TX | 2012-06-17 07:47 | 2012-06-17 14:13 | Buchholz alarms received 0747hrs. Transformer de-energised as a precaution at 0748hrs. Alarm caused by moisture ingress to the tap changer overpressure device wiring. Transformer returned to service at 1413hrs. | 19/07/2012 7:54:00 AM ¦ Nil. ¦ Ingleburn No.2 Transformer checked for same wiring. |  | Buchholz alarms received 0747hrs. Transformer de-energised as a precaution at 0748hrs. Alarm caused by moisture ingress to the tap changer overpressure device wiring. Tap Changer Overpressure devices have since been decommissioned. Ingleburn No.2 Transfor | Rain | Secondary Equipment | [5 empty] | 0 | 0 | 2012
2010 | 111589 | HV Equipment | Unknown | TRUE | Other | No FR |  | No lost Load | 2012-F-0279 | 97L Guthega - Jindabyne Pumps 132kV TL | Z | 2012Q2 | GTH |  | TL | 2012-06-22 01:43 | 2012-06-22 04:48 | Visual inspection carried out by SHL staff and no damaged evident from 132kV Bus out to first tower ex Guthega 132kV Switchyard. Line enegised via SCADA @ 0448 and remained in service. | 18/07/2012 9:22:00 AM ¦ Work order 215741 has been created to check the connections and droppers on the other phases of disconnector 97L1. Also to carry out a review to see if it is necessary that the clamped connections should be replaced with a crimped |  | Planned Outage 111606 taken at 14:57 to replace Blue phase dropper on line disconnector 97L1 on 97L JPS line | Very Windy | Primary Equipment | [5 empty] | 0 | 0 | 2012
2011 | 111590 | HV Equipment | Unknown | TRUE | Other |  |  | No lost Load | 2012-F-0280 | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2012Q2 | GTH, MUR, GHI |  | TL | 2012-06-22 05:42 | 2012-06-22 05:57 | 97G line tripped @ Murray at same time SHL were placing a Jindabyne pump in service on 97L line. | 18/07/2012 2:49:00 PM |  | See also Outage 111589 earlier in the day. Planned Outage 111606 taken at 14:57 to replace Blue phase dropper on line disconnector 97L1 on 97L JPS line | Snow or Ice | Primary Equipment | [5 empty] | 0 | 0 | 2012
2012 | 111643 | HV Equipment | HV Equipment Failure | TRUE | TX |  |  |  | 2012-F-0283 | No.3 Transformer 330/132/16kV | Z | 2012Q2 | NEW |  | TX | 2012-06-24 08:49 | 2012-06-24 15:37 |  | 12/07/2012 9:45:00 AM ¦ Nil. ¦ Investigate calibration of the conservator oil level indicator on red phase of No.3 Transformer. |  | Transformer tripped following receipt of a Buchholz alarm. there was no oil in the the buchholz relay, however the conservator oil level indicator indicated that the conservator did still contain oil. Further investigation revealed that the conservator o | Very Cold | Oil/Gas Levels | [5 empty] | 0 | 0 | 2012
2013 | 111644 | Condition Monitor | HV Equipment Failure | TRUE | TX | NA |  |  | 2012-F-0284 | No.1 Transformer 330/132/11kV | Z | 2012Q2 | NEW |  | TX | 2012-06-24 16:16 | 2012-06-25 14:33 | Requested to de-energise Transformer by G Francis due to Bushing monitor alarm. | 13/07/2012 10:50:00 AM ¦ Nil. ¦ Nil. |  | Transformer was de-energised following a request from the on-call engineer after a Transformer bushing DLA alarm was received. It was later available for emergency use only overnight. A review of the data from the Doble bushing monitor showed that the ala |  | Secondary Equipment | [5 empty] | 0 | 0 | 2012
2015 | 112491 | Unknown | Unknown | TRUE | TL |  |  |  | 2012-F-0290 | 96M Narrabri - Moree 132kV TL | Z | 2012Q2 | MRE, NB2 |  | TL | 2012-06-30 22:54 | 2012-06-30 22:54 |  | 23/07/2012 4:00:00 PM ¦ Nil. ¦ Nil. |  | Protection flagging indicated a Blue phase to Earth fault, with the distance to fault estimated at 84% from Narrabri, which is in the vicinity of structure 462. The Indji system did not record any lightning activity in the area at the time of the trip. A | Fine | Unexplained | [5 empty] | 0 | 0 | 2012
2016 | 112091 | Tree/Ground | Unknown | TRUE | TL | No FR | NA |  | 2012-F-0286 | 944 Orange North - Wallerawang 132kV (New) Line | Z | 2012Q3 | ONO, WWS |  | TL | 2012-07-02 16:06 | 2012-07-03 18:30 | WW2 reclose attempt failed (SOTF). Reclose from ONO not attempted due to check sync relay not detecting vaults Weather conditions - Cold and Cloudy, No rain Essential and Endeavour confirmed no known accidents or wires down. | 19/07/2012 9:06:00 AM ¦ Nil. ¦ The outside phase has pulled approximately 150mm towards structure 111 to be assessed. Clean up of the tree crown over the fence. 12 foot gate and assembly to be procured and installed and the fence be repaired. Check truck |  | WW2 reclose attempt failed (SOTF). Reclose from ONO not attempted due to check sync relay not detecting vaults Weather conditions - Cold and Cloudy, No rain Essential and Endeavour confirmed no known accidents or wires down. The outside phase has pulled | Mild | External | [5 empty] | 0 | 0 | 2012
2022 | 112530 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | Disc | Manual | Manual |  | 2012-F-0291 | No.6 330KV Generator Transformer Group | Q | 2012Q3 | VP1 |  | TX | 2012-07-02 20:09 | 2012-07-03 01:07 | Just prior to synchronising # 6 unit one of the last steps is to close then check closed gen tx isol 5261. SSMF advised operating shaft broken on isol 5261 with isol in the open position. LV access required. Tg's equipment was serviceable @ 0107hrs on 3/7 | 7/08/2012 7:47:00 AM ¦ Nil. ¦ A program will be arranged to replace the non stainless steel rod ends on other identical disconnectors. |  | Just prior to synchronising # 6 unit one of the last steps is to close then check closed gen tx isol 5261. SSMF advised operating shaft broken on isol 5261 with isol in the open position. LV access required. Tg's equipment was serviceable @ 0107hrs on 3/7 | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
2028 | 112607 | Contractor Error | Unknown | TRUE | Prev | Manual | Manual |  | 2012-E-0013 | 966 Armidale - Koolkhan 132kV TL | E | 2012Q3 | AR1, KLK |  | TL | 2012-07-09 12:15 | 2012-07-10 10:14 | A tree that Forestry tree trimming contractors loped has come in contact with what they believe is 966 TL str 349 which caused the insulator sting hook to jump out of hole allowing conductor to fall within 2.5 m of ground. Location is Blue Rock Rd , acc | 24/07/2012 4:03:00 PM ¦ Nil. ¦ Nil. |  | A tree that Forestry tree trimming contractors loped has come in contact with what they believe is 966 TL str 349 which caused the insulator sting hook to jump out of hole allowing conductor to fall within 2.5 m of ground. Location is Blue Rock Rd , acce | Fine | External | [5 empty] | 0 | 0 | 2012
2029 | 112631 | Secondary Equipment | Unknown | TRUE | Sec | No FR | NA |  | 2012-F-0293 | No.2 Transformer 330/132/16kV | Z | 2012Q3 | NEW |  | TX | 2012-07-09 21:38 | 2012-07-11 16:30 | No additional external tripping device activation. Alarms associated with loss of Aux's. | 9/08/2012 7:31:00 AM ¦ Nil. ¦ Nil. |  | No additional external tripping device activation. An inspection of the No.2 Transformer revealed that the insulation on the wiring associated with the blue phase tank's Buchholz relay had deteriorated. Insulation Resistance tests were carried out on the | Unknown | Secondary Equipment | [5 empty] | 0 | 0 | 2012
2033 | 114186 | HV Equipment | HV Equipment Failure | TRUE | CT | No FR | NA |  | 2012-F-0308 | No.4 Capacitor | Q | 2012Q3 | BKH |  | CAP | 2012-07-20 17:46 | 2012-08-22 13:24 | Essential Energy staff investigated on 23/07/12 and advised of burnt off bridging leads associated with the Neutral Unbalance CT. Russell Ubrihien advised and spoke to Essential Energy staff. Capacitor bank removed from service. | 4/03/2013 2:30:00 PM |  | Essential Energy staff investigated on 23/07/12 and advised of burnt off bridging leads associated with the Neutral Unbalance CT. Capacitor bank removed from service. Bird proofing is installed which includes a conduit over the star point lead. Conduit f | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
2036 | 114319 | Animal/Bird | Animal/Bird | TRUE | Bus | No FR | NA |  | 2012-F-0311 | 33kV Bus No.1 Section | S | 2012Q3 | GRF |  | BB | 2012-07-26 17:28 | 2012-07-26 19:45 | Darlington Point supplied from Coleambally at time of incident | 22/08/2012 9:01:00 AM |  | On arrival field staff located a dead bird across the 33kV Bus No.1 Section busbar. | Fine | External | [5 empty] | 0 | 0 | 2012
2038 | 115198 | HV Equipment | Unknown | TRUE | TX | Manual | Manual |  | 2012-E-0015 | No.2 Transformer 330/132/16kV | E | 2012Q3 | NEW |  | TX | 2012-08-04 22:14 | 2012-08-28 17:29 | TX taken out of service after receiving a Buchholz alarm. Further investigations pending. | 31/08/2012 10:18:00 AM ¦ Nil. ¦ As the transformer is no longer required for service, no further action is required to address the tapchanger issue. |  | The transformer remains out of service pending its scheduled replacement, as it has been confirmed by System Planning that it is not required in the meantime. Oil samples were taken from the blue phase tank, and the results indicated that the issue was re | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
2039 | 115312 | Bushfire | Non TransGrid Reason | TRUE | TL | No FR | NA |  | 2012-F-0316 | 932 Sydney West - Mt Druitt 132kV TL | Z | 2012Q3 | SYW |  | TL | 2012-08-06 17:48 | 2012-08-06 21:20 | Endeavour Energy advise of bushfire at rear of Mt Druitt directly below T/L. Will patrol line to confirm fire cause of trip. | 8/08/2012 11:56:00 AM ¦ Nil. ¦ Nil. |  | Endevour Energy advise of a fire outside their substation and a flashover reported by the Fire Brigade. | Fine | External | [5 empty] | 0 | 0 | 2012
2041 | 115490 | Unknown | Unknown | TRUE | TL | No FR | NA |  | 2012-F-0318 | 992 Burrinjuck - Tumut 132kV TL | Z | 2012Q3 | BUK, TU2 |  | TL | 2012-08-08 06:50 | 2012-08-08 06:50 |  | 6/11/2012 5:34:00 PM ¦ N/A ¦ LOCAL AREA ¦ No further action required. |  | Advised Protection details for TAR on 992 Tumut to Burrinjuck 132 kV T/L at Tumut 132 S/S No.1 prot: Zone 1, R - E and DTF 9.48km. No.2 prot: Zone 1, R- E and DTF 35.6km. No1 & No2 Protections DTF at 42kM during commissioning. | Fine | Unexplained | [5 empty] | 0 | 0 | 2012
2048 | 115458 | HV Equipment | HV Equipment Failure | TRUE | CBOil | Manual | Manual |  | 2012-E-0016/3 | 95U Muswellbrook 330 - Singleton 132kV Line | Q | 2012Q3 | MRK |  | TL | 2012-08-08 07:43 | 2012-08-08 12:00 |  |  |  | 132kV Bus section 1 at Muswellbrook 330 was off-loaded then 95U singleton Bus Isol 95U3 locked open. Staff are working to repair CB 95U2. The circuit breaker is an ASEA HLR type breaker. A detailed inspection of the circuit breaker's operating mechanism r |  | Primary Equipment | [5 empty] | 0 | 0 | 2012
2042 | 115502 | Animal/Bird | Animal/Bird | TRUE | Cap | No FR | NA |  | 2012-F-0319 | No.5 Capacitor | Z | 2012Q3 | TRE |  | CAP | 2012-08-08 14:05 | 2012-08-08 16:31 | Advised by Contract staff that a bird was on the ground under No5 Cap. Capacitor came out of service when volts were around 139kV (Normal control switchout voltage). Staff sent to site due to information from contractor. |  |  | Advised by Contract staff that a bird was on the ground under No5 Cap. Capacitor came out of service when volts were around 139kV (Normal control switchout voltage). Staff sent to site due to information from contractor. | Fine | External | [5 empty] | 0 | 0 | 2012
2046 | 115668 | HV Equipment | Unknown | TRUE | Cap | No FR | NA |  | 2012-F-0320 | No.2 Capacitor | Z | 2012Q3 | NEW |  | CAP | 2012-08-09 23:58 | 2012-08-17 11:47 |  | 31/08/2012 2:28:00 PM ¦ Nil. ¦ A 415V AC injection test is to be carried out by Substations/Newcastle to allow a more accurate balance to be carried out on No.2 Capacitor. |  | See outage 115978. A 415V AC injection test is to be carried out by Substations/Newcastle to allow a more accurate balance to be carried out on No.2 Capacitor. | Fine | Unexplained | [5 empty] | 0 | 0 | 2012
2049 | 115669 | HV Equipment | HV Equipment Failure | TRUE | Cap | Manual | Manual |  | 2012-E-0017 | No.1 Capacitor | Q | 2012Q3 | PMQ |  | CAP | 2012-08-10 11:59 | 2012-08-13 11:45 | On return of No.1 capacitor to service a neutral unbalance alarm was initiated. Capacitor subsequently taken out of service pending repairs. | 22/08/2012 9:55:00 AM ¦ Nil. ¦ Nil. |  | The Capacitor Bank had been in service for approximately 30 minutes following final commissioning checks and initial energisation of the bank when the unbalance alarm initiated. Cans replaced. | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
2043 | 115674 | Bushfire | Bushfire | TRUE | TL | No FR | NA |  | 2012-F-0321 | 11 Dapto - Sydney South 330kV TL | Z | 2012Q3 | DPT, SYS |  | TL | 2012-08-10 17:10 | 2012-08-10 17:55 | Bushfire near conductors on section of line between structures 79 to 84 at time of trip. | 3/09/2012 11:42:00 AM ¦ Nil. ¦ Nil |  | Bushfire near conductors on section of line between structures 79 to 84 at time of trip. The line was patrolled after staff were able to enter area. No damage could be found due the fire. | Very Windy | External | [5 empty] | 0 | 0 | 2012
2044 | 115685 | Bushfire | Bushfire | TRUE | TL | FEOR not yet issued |  |  | 2012-F-0322 | 11 Dapto - Sydney South 330kV TL | Z | 2012Q3 | DPT, SYS |  | TL | 2012-08-11 02:11 | 2012-08-11 02:11 | At 02:11hrs 11 Dapto to Sydney South 330 kV T/L Tripped and reclosed TAR. Report from RFS Richard Petch 42568432 that the Transmission line is arcing. There are fires in the area and very windy. Advised NCM and requuest staff to investigate B Fultcher c | As Above. ¦ As Above. |  | T/L Tripped and reclosed TAR. Report from RFS that the Transmission line is arcing. There are fires in the area and very windy. Advised NCM and request staff to investigate. Advised on site, fire is out of control, have advised RFS not to get under TX lin | Rain and Very Windy | External | [5 empty] | 0 | 0 | 2012
2058 | 115952 | HV Equipment | HV Equipment Failure | TRUE | Cap | No FR | NA |  | 2012-F-0328 | No.1 Capacitor | Z | 2012Q3 | WL1 |  | CAP | 2012-08-13 20:23 | 2012-08-16 15:16 |  | 12/09/2012 1:34:00 PM ¦ Nil. ¦ Nil. |  | Advised cap was observed opening with < 140kV (AVC set to 142.5 kV). No.1 Cap No.1 Protection multitrip alarm found on MITS. Cap command blocked on SCADA. Further investigations required. A closer inspection of No.1 Capacitor and found leaking Capacitor C | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
2050 | 115801 | Unknown | Unknown | TRUE | TL | No FR | NA |  | 2012-F-0324 | 969 Tamworth 330 - Gunnedah 132kV TL | Z | 2012Q3 | GN2, TA1 |  | TL | 2012-08-15 10:57 | 2012-08-15 10:57 | no storms in the area | 21/08/2012 10:10:00 AM ¦ Nil. ¦ Nil. |  | Protection flagging indicated a White phase to Blue phase fault, approximately 6km from Tamworth 330kV substation. This corresponds to a fault between structures 15 and 18 of the line. White and Blue phases are arranged as the bottom and middle phases on | Fine | Unexplained | [5 empty] | 0 | 0 | 2012
2060 | 115829 | HV Equipment | HV Equipment Failure | TRUE | CT | No FR | NA |  | 2012-F-0325 | 37 Macarthur A CB 372A | Q | 2012Q3 | KCR |  | CB | 2012-08-15 17:31 | 2012-08-15 19:00 | CB 372A low SF6 gas alarm. Topped up by field staff. | Nil. ¦ Nil. |  | Isolated to top up SF6 Blue phase C.T. | Fine | Oil/Gas Levels | [5 empty] | 0 | 0 | 2012
2057 | 115830 | HV Equipment | HV Equipment Failure | TRUE | CT | FEOR not yet issued |  |  | 2012-F-0326 | No.2 Transformer 330/132/16kV | Z | 2012Q3 | SE1 |  | TX | 2012-08-15 18:25 | 2012-08-15 22:27 | Top up low SF6 gas in 330kV CB 5422. | Nil. ¦ Nil. |  | Investigate CB abnormal alarm. Top up C.T SF6 assoc. CB5422 Blue Phase. | Fine | Oil/Gas Levels | [5 empty] | 0 | 0 | 2012
2059 | 115978 | HV Equipment | HV Equipment Failure | TRUE | Cap | No FR | NA |  | 2012-F-0330 | No.2 Capacitor | Z | 2012Q3 | NEW |  | CAP | 2012-08-17 11:47 | 2013-01-23 10:01 | Tripped on energising. | 31/08/2012 2:52:00 PM ¦ As above. ¦ As above. |  | A detailed inspection of the Capacitor bank was carried out on Thursday 16/08/12. The inspection did not reveal any issues with the bank. On the same day, measurements were taken of the capacitance of each leg of the bank, along with measurements of the c | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
2065 | 117156 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 | FEOR not yet issued |  |  | 2012-F-0344 | No.3 330kV Reactor | Z | 2012Q3 | AR1 |  | RX | 2012-08-18 06:22 | 2012-08-18 06:22 | Failed to close due to pole discrepency. | 11/01/2013 10:10:00 AM ¦ Nil. ¦ The auxiliary switches on red and white phases are to be replaced within the next three months once spare switches are obtained from a spare circuit breaker at Vales Point. |  | this has been an issue for a number of years, the cause is presently unknown. CM testing has identified no issues. One pole has had auxilliaries and pallets replaced, alternate 2 poles require another outage. This is being planned. 3AQ2 CB identified | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
2064 | 116432 | Secondary Equipment | Non TransGrid Reason | TRUE | Cont | No FR | NA |  | 2012-F-0333 | 863 Ingleburn - Minto 66kV Line | Q | 2012Q3 | ING |  | TL | 2012-08-23 14:15 | 2012-08-23 14:15 | CB 8632A did not auto reclose. Repaired & returned to service at 21:19hrs. |  |  | CB 8632A did not auto reclose. Customer reported pole top fire on line near Ingleburn. C.B. 8632A reclose set to auto but SCADA event log did not record C.B. reclosing. Later attempt to close C.B. 8632A failed (both locally and via SCADA). Short Notice ou | Rain and Very Windy | Secondary Equipment | [5 empty] | 0 | 0 | 2012
2063 | 116440 | Secondary Equipment | Non TransGrid Reason | TRUE | Cont | No FR | NA |  | 2012-F-0333 | 863 Ingleburn - Minto 66kV Line | Q | 2012Q3 | ING |  | TL | 2012-08-23 14:44 | 2012-08-23 22:44 | Customer reported pole top fire on line near Ingleburn. C.B. 8632A reclose set to auto but SCADA event log did not record C.B. reclosing. Later attempt to close C.B. 8632A failed (both locally and via SCADA). Short Notice outage created for C.B 8632A. |  |  | Customer reported pole top fire on line near Ingleburn. C.B. 8632A reclose set to auto but SCADA event log did not record C.B. Reclosing. Later attempt to close C.B. 8632A failed (both locally and via SCADA). Short Notice outage created for C.B 8632A. Rel | Rain and Very Windy | Secondary Equipment | [5 empty] | 0 | 0 | 2012
2061 | 116734 | Relay | Sec Eqt Malfunction | TRUE | Prot | Manual | Manual |  | 2012-E-0018 | L5 Lower Tumut - Tumut 3 330kV TL | E | 2012Q3 | LT1 |  | TL | 2012-08-30 05:18 | 2012-08-30 09:40 | L5 group line taken O/S pending further protection investigation. Protection Staff investigated, relays OK, indication is CVT unbalance alarm caused issue, L5 line RTS for further monitoring. | 15/05/2013 9:39:00 AM |  | L5 group line taken O/S pending further protection investigation. Protection Staff investigated, relays OK, indication is CVT unbalance alarm caused issue, L5 line RTS for further monitoring. Suspect CVT unbalance relay. Have installed a Hioki recorder lo | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012 | Faulty CVT unbalance relay, not part of the protection system.
2062 | 116757 | HV Equipment | Unknown | TRUE | Prev | No FR | NA |  | 2012-F-0343 | 963 Tomago 330 - Taree 132kV TL | Z | 2012Q3 | TRE, TOM |  | TL | 2012-08-30 10:27 | 2012-08-30 18:26 | Initial reports indicate earth wire adrift from line impacting 11kV Essential Energy Fdr @ or near 107 Wingham Rd Taree NSW. Distance to fault readings at Tomago indicate 101kM from site. Line owned by Ausgrid to structure 184 from Tomago. No known impac | 25/09/2012 3:32:00 PM ¦ Nil. ¦ The two failed spans of OHEW will be replaced at a future date when outages can be coordinated with Essential Energy and required road closures. A report is being prepared for Asset Performance regarding the asset manageme |  | Initial reports indicate earth wire adrift from line impacting 11kV Essential Energy Fdr @ or near 107 Wingham Rd Taree NSW. The incident occurred when a mulcher operated by Savco, TransGrid's vegetation maintenance contractor, broke a guy wire on structu | Fine | External | [5 empty] | 0 | 0 | 2012
2066 | 117783 | HV Equipment | HV Equipment Failure | TRUE | CT | Manual | Manual |  | 2012-E-0019 | 232 Regentville - Glenmore Park 132kV Line | Q | 2012Q3 | RGV |  | TL | 2012-09-09 15:18 | 2012-09-09 17:00 |  | Nil. ¦ Nil. |  | Replaced CT O ring associated with SF6 pressure gauge and replenished gas. | Fine | Oil/Gas Levels | [5 empty] | 0 | 0 | 2012
2067 | 117892 | Staff Error | Sec Eqt Staff Error | TRUE | Prev | No FR | NA |  | 2012-F-0359 | No.2 Transformer 330/132/11kV | Z | 2012Q3 | SYS |  | TX | 2012-09-11 10:41 | 2012-09-11 11:23 | protection staff were carrying out panel wiring mods which caused the trip. | 12/09/2012 2:38:00 PM ¦ Nil. ¦ Nil. |  | Protection staff were carrying out panel wiring mods which caused the trip. The trip was caused as a result of a building wire that was being stripped coming into contact with the No.2 Transformer trip fuse and the other end of the building wire coming in | Fine | External | [5 empty] | 1 | 1 | 2012 | Incorrect isolation by protection staff resulting in an incorrect protection operation
2069 | 118295 | Lightning/Storm | Lightning or Storm | TRUE | TL | No FR | NA |  | 2012-F-0369 | 99A Uranquinty - Finley 132kV TL | Z | 2012Q3 | FNY, URQ |  | TL | 2012-09-18 09:27 | 2012-09-18 09:27 | Finley DTF 82.3 km Uranquinty DTF 75.32 km | 6/11/2012 5:04:00 PM ¦ N/A ¦ LOCAL AREA ¦ This has been noted for the next scheduled aerial patrol. |  | A patrol by easement staff did not find anything indicating that a trip and reclose had occurred. A follow up on the INJI system indicated that there was a lightening strike at 09:27am on Tuesday 18th September at approximately 500m from Structure 454. | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
2071 | 118365 | HV Equipment | Unknown | TRUE | CB SF6 | Manual | Manual |  | 2012-E-0021 | 5 Yass 330kV CB 52 | Q | 2012Q3 | MRN |  | CB | 2012-09-19 15:15 | 2012-09-19 17:26 | CB Failed to close due lock out caused excess run time on CB hydraulic pump. | 4/03/2013 3:31:00 PM |  | CB Failed to close due to lock out causing excess run time on CB hydraulic pump. Issue has occured a number of times this year. The Nitrogen gauge has been replaced as has the hydraulic pump control timer. Ther alarm is a loss of nitrogen alarm. The pu | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
2070 | 118368 | Staff Error | Unknown | TRUE | Proc | Manual | Manual |  | 2012-E-0022 | No.1 Transformer 132/66/11kV | E | 2012Q3 | KLK |  | TX | 2012-09-19 18:57 | 2012-09-21 17:19 | Transformer taken out of service following receipt of Urgent Buchholz alarm. | 11/01/2013 9:21:00 AM ¦ Nil. ¦ Nil. |  | Transformer taken out of service following receipt of Urgent Buchholz alarm. Gas evident in Gas Receiver, but lost when bled by fitter. Aux transformer. Buchholz isolated for maintenance and lower valve left closed. During heating and cooling of aux Tx, | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
2073 | 118400 | Wiring Design | Unknown | TRUE | Proc | No FR | NA |  | 2012-F-0380 | 80R Beryl - Ulan 66kV Line | S | 2012Q3 | BER |  | TL | 2012-09-20 12:42 | 2012-09-20 12:49 |  |  |  | A wiring design fault was found for the new CB8512. This directly tripped the bus-section and resulted in a loss of 17MW load for 7 minutes. CB Control Cabinet pallet wiring was used for wiring termination, this did not appear on the schematic. Design ha |  | Primary Equipment | [5 empty] | 1 | 0 | 2012 | Incorrect wiring within CB, not protection system
2074 | 118425 | HV Equipment | Sec Eqt Malfunction | TRUE | SVC | No FR | NA |  | 2012-F-0381 | No.2 Static VAR Compensator | Z | 2012Q3 | BKH | Preventable | SVC | 2012-09-20 14:44 | 2012-09-20 16:50 | On return to service of 22kV Bus No.2 Section, No.2 SVC failed to start either remotely or locally (C.B.. 2V22 didn't close), SVC isolated & investigation found loose control wiring, rectified fully tested both locally & remotely & RTS 16:50hrs | 4/03/2013 2:24:00 PM |  | On return to service of 22kV Bus No.2 Section, No.2 SVC failed to start either remotely or locally (C.B.. 2V22 didn't close), SVC isolated & investigation found loose control wiring, rectified fully tested both locally & remotely & RTS 16:50hrs. All wirin | Mild | Secondary Equipment | [5 empty] | 0 | 0 | 2012 | Loose control wiring
2075 | 118433 | HV Equipment | Unknown | TRUE | Rx | Manual | Manual |  | 2012-E-0023 | No.2 Reactor | E | 2012Q3 | SYS |  | RX | 2012-09-21 00:02 | 2012-09-27 19:58 | Reactor taken out of service following receipt of Condition Monitor L1 alarm. | Nil ¦ Nil. |  | Reactor taken out of service following receipt of Condition Monitor L1 alarm. | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
2077 | 118476 | Lightning/Storm | Lightning or Storm | TRUE | TL | No FR | NA |  | 2012-F-0382 | 96R Glen Innes - Tenterfield 132kV TL | Z | 2012Q3 | GNS, TTF |  | TL | 2012-09-21 13:18 | 2012-09-21 13:18 | Protection details required. | 9/11/2012 10:53:00 AM ¦ Nil. ¦ Nil. |  |  | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
2078 | 118514 | Unknown | Unknown | TRUE | TL | No FR | NA |  | 2012-F-0383 | 966 Armidale - Koolkhan 132kV TL | Z | 2012Q3 | AR1, KLK |  | TL | 2012-09-23 16:52 | 2012-09-23 16:52 | cause unknown, no storms. | 26/10/2012 11:40:00 AM ¦ Nil. ¦ Nil. |  | Cause unknown, no storms. | Fine | Unexplained | [5 empty] | 0 | 0 | 2012
2079 | 118515 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | SVC | No FR | NA |  | 2012-F-0384 | No.1 Static VAR Compensator | Z | 2012Q3 | SYW |  | SVC | 2012-09-23 19:13 | 2012-09-23 21:30 | MITS Event Log shows Cooling System Trip occurred following changeover of cooling pumps. Cooling system checled OK and SVC returned to service at 2130 hours. | 6/11/2012 11:14:00 AM ¦ Nil. ¦ Nil. |  | MITS Event Log shows Cooling System Trip occurred following changeover of cooling pumps. Cooling system checled OK and SVC returned to service at 2130 hours. Fault occurs within the ABB provided control system. Issue being followed up with ABB under war | Fine | Secondary Equipment | [5 empty] | 0 | 0 | 2012 | Trip caused by cooling system fault
2080 | 118767 | Tree/Ground | Tree/Ground | TRUE | TL | FEOR not yet issued |  | Lost generation 67MW | 2012-F-0391 | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2012Q3 | GTH, MUR, GHI |  | TL | 2012-09-28 15:11 | 2012-09-30 16:37 |  |  |  | Helicopter patrol of line has found tree across two phases of T/L approx. 9.5kms from Murray SS, is attempting to organise TG staff to attend delayed due to saftey. Trip interrupted 64MW of Guthega generation. At 16:21hrs the 132kV bus was returned to ser | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
2082 | 118801 | Relay | Unknown | TRUE | Cont | FEOR not yet issued |  |  | 2012-F-0394 | 97G/3 Geehi Tee CB 97G2 | Q | 2012Q3 | GTH |  | CB | 2012-09-30 16:37 | 2012-10-01 06:49 |  |  |  | Unable to close 97G2 CB at Guthega. Sync relay fail alarm. TG maint fitter to investigate. Geehi Dam now taken supply via TL 97G. AYDM10 sync relay is the problem. The relay was moved behind the panel to provide more room. Since being done, sync issues |  | Primary Equipment | [5 empty] | 0 | 0 | 2012 | Reclose failure is a control system failure, not protection
2083 | 119064 | Bushfire | Bushfire | TRUE | TL | Yes | 79.84 |  | 2012-F-0398 | 24 Vales Point - Eraring 330kV TL | Z | 2012Q4 | ER0, VP1 |  | TL | 2012-10-04 12:15 | 2012-10-04 12:15 | CB 242M manually closed, no reclose even though selected. | 19/04/2013 8:35:00 AM ¦ Nil. ¦ Actions are being taken in accordance with the recommendations in the TransGrid investigation report prepared by Mains Manager/Northern. |  | This follow up report covers the following FEOR's: 2012-F-0398 to 2012-F-0402 inclusive; and 2012-F-0404. On Thursday 4/10/12 at 12:15hrs, the 330kV 24TL from Vales Point to Eraring tripped and auto-reclosed at both ends of the line. Auto-reclose at Vales | Fine | External | [5 empty] | 0 | 0 | 2012
2085 | 119079 | Switching error | LV/MECH/PROT Equipment Fail | TRUE | Proc | Yes | 79.84 |  | 2012-F-0399 | 24 Eraring 330kV MAIN BUS CB 242M | Q | 2012Q4 | VP1 |  | CB | 2012-10-04 12:15 | 2012-10-04 12:15 |  |  |  | CB 242M manually closed, no reclose even though selected. Field investigations discovered that the AR was not set to ON. |  | Secondary Equipment | [5 empty] | 0 | 0 | 2012 | Reclose failure
2084 | 119077 | Bushfire | Bushfire | TRUE | TL | Yes | 79.84 |  | 2012-F-0399 | 24 Vales Point - Eraring 330kV TL | Z | 2012Q4 | ER0, VP1 |  | TL | 2012-10-04 13:00 | 2012-10-04 13:00 | CB 242M left open, no reclose even though selected. | 19/04/2013 8:51:00 AM ¦ As above. ¦ As above. |  | CB 242M left open, no reclose even though selected. | Fine | External | [5 empty] | 0 | 0 | 2012 | Reclose failure
2086 | 119090 | Switching error | LV/MECH/PROT Equipment Fail | TRUE | Proc | Yes | 79.53 |  | 2012-F-0400 | 24 Eraring 330kV MAIN BUS CB 242M | Q | 2012Q4 | VP1 |  | CB | 2012-10-04 13:00 | 2012-10-04 13:00 |  |  |  | No reclose even though selected. CB 242M left open, no reclose even though selected. Field investigations discovered that the AR was not set to ON. |  | Secondary Equipment | [5 empty] | 0 | 0 | 2012 | Reclose failure
2087 | 119091 | Bushfire | Bushfire | TRUE | TL | Yes | 79.53 |  | 2012-F-0400 | 24 Vales Point - Eraring 330kV TL | Z | 2012Q4 | ER0, VP1 |  | TL | 2012-10-04 13:02 | 2012-10-04 13:02 | CB 242M left open. | 19/04/2013 8:52:00 AM ¦ As above. ¦ As above. |  | CB 242M left open. | Fine | External | [5 empty] | 0 | 0 | 2012 | Reclose failure
2088 | 119094 | Bushfire | Bushfire | TRUE | TL | Yes | 72.66 |  | 2012-F-0401 | 24 Vales Point - Eraring 330kV TL | Z | 2012Q4 | ER0, VP1 |  | TL | 2012-10-04 13:05 | 2012-10-04 13:05 | CB 242M left open. | 19/04/2013 8:53:00 AM ¦ As above. ¦ As above. |  | CB 242M left open. | Fine | External | [5 empty] | 0 | 0 | 2012 | Reclose failure
2089 | 119102 | Bushfire | Bushfire | TRUE | TL | Yes | 78.75 |  | 2012-F-0402 | 24 Vales Point - Eraring 330kV TL | Z | 2012Q4 | ER0, VP1 |  | TL | 2012-10-04 13:13 | 2012-10-04 15:22 | CB 242M closed, CB 242G opened prior trip. A/R disabled prior tripping. Fire cleared from easement , line RTS. | 19/04/2013 8:54:00 AM ¦ As above. ¦ As above. |  | See 119064. CB 242M closed, CB 242G opened prior trip. A/R disabled prior tripping. Fire cleared from easement , line RTS. | Fine | External | [5 empty] | 0 | 0 | 2012 | Reclose failure
2090 | 119166 | Bushfire | Bushfire | TRUE | TL | Yes | 80.16 |  | 2012-F-0404 | 24 Vales Point - Eraring 330kV TL | Z | 2012Q4 | ER0, VP1 |  | TL | 2012-10-05 13:56 | 2012-10-05 13:59 | Bushfire under 24 TL is out of control. TL Tripped and reclose occured at VP1 CB 242G only. | 19/04/2013 8:55:00 AM ¦ As above. ¦ As above. |  | See 119064. Bushfire under 24 TL is out of control. TL tripped and reclose occured at VP1 CB 242G only. | Very Hot | External | [5 empty] | 0 | 0 | 2012 | Reclose failure
2091 | 119170 | HV Equipment | HV Equipment Failure | TRUE | TX | NA | NA |  | 2012-E-0025 | No.3 Transformer 132/66/11kV | E | 2012Q4 | TA2 |  | TX | 2012-10-05 14:34 | 2012-10-05 18:27 | Reported from SSMF, Transformer has developed an oil leak coming from the neutral bushing 66kV side. All oil is being contained in the bunded area. Top Cap of Bushing was found to be loose on inspection. It was tightened and oil leak stopped. It will con |  |  | Reported from SSMF, Transformer has developed an oil leak coming from the neutral bushing 66kV side. All oil is being contained in the bunded area. Top Cap of Bushing was found to be loose on inspection. It was tightened and oil leak stopped. It will cont | Unknown | Oil/Gas Levels | [5 empty] | 0 | 0 | 2012
2093 | 119200 | Relay | Lightning or Storm | TRUE | TL | No FR | No FR | Lost generation 60MW | 2012-F-0408 | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2012Q4 | GTH, MUR, GHI |  | TL | 2012-10-06 19:07 | 2012-10-06 20:44 | Guthega Units 1& 2 I/S at time of trip of 97G, both units tripped. See IR 9513 for more details. | 7/04/2013 6:12:00 PM ¦ N/A ¦ No further action required. |  | Guthega Units 1& 2 I/S at time of trip of 97G, both units tripped. See IR 9513 for more details. 60 MW generation. The auto synch check relay (line bay interface 97G) was locking up. This had to be powered down and reset. There is a known lock up issue. N | Thunderstorm | [6 empty] | 0 | 0 | 2012 | Reclose failure
2094 | 119211 | HV Equipment | HV Equipment Failure | TRUE | Cap | No FR | No FR |  | 2012-F-0410 | No.4 Capacitor | L | 2012Q4 | CMA |  | CAP | 2012-10-07 04:48 | 2012-10-07 04:48 | Actual time of trip unknown. CB 3742 command blocked on SCADA. AVC made non auto. | 4/03/2013 2:43:00 PM |  | Actual time of trip unknown. CB 4742 command blocked on SCADA. AVC made non auto. | Unknown | Primary Equipment | [5 empty] | 0 | 0 | 2012
2097 | 119489 | Condition Monitor | HV Equipment Failure | TRUE | TX | NA | NA |  | 2012-E-0026 | No.1 Transformer 330/132/11kV | E | 2012Q4 | WRH |  | TX | 2012-10-11 01:10 | 2012-10-11 09:07 |  |  |  | Tx was taken out of service following the initiation of fleeting L1 condition monitoring alarm. Inspections revealed that the alarms were being generated by the Tapguard condition monitoring system and were associated with measured temperatures exceeding |  | Primary Equipment | [5 empty] | 0 | 0 | 2012 | Condition monitoring alarms
2098 | 119591 | HV Equipment | Unknown | TRUE | TL | No FR | No FR |  | 2012-F-0415 | 96M Narrabri - Moree 132kV TL | Z | 2012Q4 | MRE, NB2 |  | TL | 2012-10-12 04:04 | 2012-10-12 04:04 |  | 9/11/2012 11:24:00 AM ¦ Nil. ¦ Nil. |  | An aerial patrol carried out on Friday reported evidence of damaged longrod insulators at structure 503. The damage appeared to have been caused by birds eating away the polymer sheds on post and longrod insulators. Damaged insulators were subsequently re | Rain | Primary Equipment | [5 empty] | 0 | 0 | 2012
2099 | 119654 | Switching error | Sec Eqt Staff Error | TRUE | Prev | No FR | No FR |  | 2012-F-0423 | No.1 Transformer 330/132/33KV | Z | 2012Q4 | WL1 |  | TX | 2012-10-12 14:37 | 2012-10-12 14:50 |  |  |  | No.2 Protection was replaced and a balance was being performed on the No.2 Protection. The isolations included the 132kV & 330kV BBP Summation, No.1 Protection Differential & Indication Circuits. The balance was completed succesfully and the isolations we |  | External | [5 empty] | 1 | 1 | 2012 | QAPR report indicates incorrect restoration of links leading to incorrect protection operation
2102 | 119696 | Wiring Error | Unknown | TRUE | Proc | No FR | No FR |  | 2012-F-0423 | No.1 Transformer 330/132/33KV | Z | 2012Q4 | WL1 |  | TX | 2012-10-14 16:06 | 2012-10-14 20:55 | Alarms initiated - 132kV No.1 TX 4412 CB Unsolicited Operation; 330kkV No.1 TX 5412 CB Unsolicited Operation; 330kV No.1 Auxiliary Transfer CB Trip. Note - No.3 Capacitor closing check relay fault alarm and 132 No.1 Cap 4712 CB Motor supply initiation | 27/11/2012 2:17:00 PM ¦ As Above ¦ As Above |  | Alarms initiated - 132kV No.1 TX 4412 CB Unsolicited Operation; 330kkV No.1 TX 5412 CB Unsolicited Operation; 330kV No.1 Auxiliary Transfer CB Trip. Note - No.3 Capacitor closing check relay fault alarm and 132 No.1 Cap 4712 CB Motor supply initiation at | Fine | External | [5 empty] | 1 | 0 | 2012 | QAPR report indicates incorrect protection operation due to wire between open link and relay
2104 | 119757 | Relay | Unknown | TRUE | Prot | No FR | No FR |  | 2012-F-0425 | No.1 Transformer 330/132/33KV | Z | 2012Q4 | WL1 |  | TX | 2012-10-15 20:56 | 2012-10-16 13:08 |  | 27/11/2012 2:13:00 PM ¦ Nil. ¦ Nil. |  | Advised tripped. Likely to be operation of possibly faulty No.2 prot, known issue. Advises No.2 Prot operation only, same as yesterday (high speed trip on Matrix RMS type plus red LED 2nd up from bottom, left side red indication on ,no description, spare | Fine | Primary Equipment | [5 empty] | 1 | 0 | 2012 | QAPR report indicates faulty protection relay
2106 | 119959 | Animal/Bird | Animal/Bird | TRUE | Other | No FR | No FR |  | 2012-F-0430 | 7R2 Kempsey - North St tee Smithtown 33kV Line | Q | 2012Q4 | KS2 |  | TL | 2012-10-19 01:52 | 2012-10-19 01:52 | Advise from site staff that there is a dead Owl on the ground on the line side of the line isolator. There is also some fresh burn marks near the earth switch. FEOR update. |  |  | Advise from site staff that there is a dead Owl on the ground on the line side of the line isolator. There is also some fresh burn marks near the earth switch. | Fine | External | [5 empty] | 0 | 0 | 2012
2105 | 119948 | HV Equipment | HV Equipment Failure | TRUE | Disc | Not reviewed | Not reviewed |  | 2012-F-0429 | 5A2 Eraring B CB 5A22B | Q | 2012Q4 | KCR |  | CB | 2012-10-19 07:18 | 2012-12-15 13:47 |  | Nil. ¦ WO raised to repair Disconnector 5A28. |  | Investigation by TransGrid staff found accumulators on red phase with low Nitrogen. During switching to get access to the CB, Disconnector 5A28 failed during opening. The limit switch failed and the mechanism travelled past its limits and was seized open. |  | Primary Equipment | [5 empty] | 0 | 0 | 2012
2188 | 119948 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 | Not reviewed | Not reviewed |  | 2012-F-0429 | 5A2 Eraring B CB 5A22B | Q | 2012Q4 | KCR |  | CB | 2012-10-19 07:18 | 2012-12-15 13:47 |  | Nil. ¦ WO raised to repair Disconnector 5A28. |  | Investigation by TransGrid staff found accumulators on red phase with low Nitrogen. During switching to get access to the CB, Disconnector 5A28 failed during opening. The limit switch failed and the mechanism travelled past its limits and was seized open. |  | Oil/Gas Levels | [5 empty] | 0 | 0 | 2012
2107 | 119972 | Unknown | Unknown | TRUE | TL | No FR | No FR |  | 2012-F-0431 | 998 Forbes - Cowra 132kV TL | Z | 2012Q4 | CW2, FB2 |  | TL | 2012-10-20 06:26 | 2012-10-20 06:26 |  |  |  |  | Unknown | Unexplained | [5 empty] | 0 | 0 | 2012
2108 | 119973 | Bushfire | Bushfire | TRUE | TL | Yes | 69.38 |  | 2012-F-0432 | 5A2 Eraring - Kemps Creek 500kV TL | Z | 2012Q4 | ER0, KCR |  | TL | 2012-10-20 13:07 | 2012-10-20 14:19 | Fault recorder suggested DTF - 76Klm, indji web site approx 76.6 klm, B.Fraser advised and clearance given to RTS 5A2 T/L. (St By prot'n at both ends of line indicated B-E also) | 6/11/2012 12:36:00 PM ¦ Nil. ¦ Nil. |  | Fault recorder suggested DTF - 76Klm, indji web site approx 76.6 klm, B.Fraser advised and clearance given to RTS 5A2 T/L. (St By prot'n at both ends of line indicated B-E also). Patrol of the area conducted on 26/10/2012. Evidence of fire found below str | Fine | External | [5 empty] | 0 | 0 | 2012
2109 | 120305 | Unknown | Unknown | TRUE | TL | No FR | No FR |  | 2012-F-0437 | 99X Wagga 330 - Wagga 132 132kV TL | Z | 2012Q4 | WG2, WG1 |  | TL | 2012-10-26 13:28 | 2012-10-26 13:52 | Feeder remained in service at Wagga 330. |  |  | Feeder remained in service at Wagga 330. | Fine | Unexplained | [5 empty] | 1 | 0 | 2012 | Opslog indicates only one protection operated at Wagga132, so likely to be a protection relay fault. No further info in QAPR report, THEOS or Opslog
2110 | 120846 | Staff Error | Unknown | TRUE | Prev | No FR | No FR |  | 2012-F-0439 | 132kV Bus Section 1 | Q | 2012Q4 | LSM |  | BB | 2012-10-31 12:19 | 2012-10-31 12:26 | Staff report inadvertant protection operation whilst undertaking functional testing of No.1 Transformer trip circuitry. No loss of load. Restoration completed after visual equpment inspection completed and protection reset. |  |  | Staff report inadvertant protection operation whilst undertaking functional testing of No.1 Transformer trip circuitry. No loss of load. Restoration completed after visual equpment inspection completed and protection reset. The use of link barrieers are b | Fine | External | [5 empty] | 1 | 1 | 2012 | Incorrect isolation by staff causing incorrect protection operation
2114 | 120959 | HV Equipment | HV Equipment Failure | TRUE | Cap | NA | NA |  | 2012-E-0028 | No.3 Capacitor | E | 2012Q4 | NEW |  | CAP | 2012-11-01 16:14 | 2012-11-02 09:40 | 01/11/12 Receipt of Substation Misc Equip fault & 132 No 3 Cap Neutral Imbalance. No 3 Cap in service. Prot tech onsite confirmed relay 62B NUB in alarm. Trip relay 62A not activated. Due to availability of other Capacitors and increased risk to system se | 19/12/2012 3:34:00 PM ¦ Nil. ¦ The No.3 Capacitor will be inspected and rebalanced following the rebalancing of the No.2 Capacitor Bank at Newcastle, which is scheduled for 22/01/2013. |  | Receipt of Substation Misc Equip fault & 132 No 3 Cap Neutral Imbalance. No 3 Cap in service. Prot tech onsite confirmed relay 62B NUB in alarm. Trip relay 62A not activated. Due to availability of other Capacitors and increased risk to system security Ca | Very Hot | Secondary Equipment | [5 empty] | 0 | 0 | 2012
2116 | 121066 | HV Equipment | HV Equipment Failure | TRUE | Aux Tx | Not reviewed | Not reviewed |  | 2012-F-0442 | No.3 Aux Transformer 33000/415V | Q | 2012Q4 | KCR |  | TX | 2012-11-04 04:29 | 2012-11-04 08:35 |  |  |  | Receipt of a Buchholz alarm on No.3 Auxiliary Transformer 33kV/415V. The Auxiliary transformer was isolated and No 3 Transformer 500/330/33kV was returned to service |  | Primary Equipment | [5 empty] | 0 | 0 | 2012
2117 | 121079 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 | Not reviewed | Not reviewed |  | 2012-F-0445 | U7 Tumut 2 330kV CB U72 | Q | 2012Q4 | UT1 |  | CB | 2012-11-04 19:21 | 2012-12-15 18:48 | Failed to Close after SHL opened due to SCADA issues. White Phase has suspected faulty operating rod. U7 T/L unavailable on Reserve bus | 4/03/2013 2:54:00 PM |  | Failed to Close after SHL opened due to SCADA issues. White Phase has suspected faulty operating rod. U7 T/L unavailable on Reserve bus | Unknown | Primary Equipment | [5 empty] | 0 | 0 | 2012
2118 | 121467 | Condition Monitor | Unknown | TRUE | TX | NA | NA |  | 2012-E-0029 | No.2 Transformer 330/132/11kV | E | 2012Q4 | SYS |  | TX | 2012-11-10 12:01 | 2012-11-13 19:52 | Condition Monitor L1 urgent alarm generated, confirmed alarm on HMI, Tx had been RTS for 27min after outage to connect new alarm cabling, including wiring to Doble. There was an alarm up on the Doble after work, but reset as thought alarm initated during | 10/12/2012 12:45:00 PM ¦ Nil. ¦ Replace Doble bushing monitor with a new Treetech bushing monitor. |  | Shortly after being returned to service a Condition Monitoring L1 alarm was recieved via SCADA. Transformer taken out of service for offline bushng tests. Bushing test results within Condition Monitoring limits and indicated no signs of bushing deteriorat | Mild | Secondary Equipment | [5 empty] | 0 | 0 | 2012 | Condition monitoring alarm
2123 | 121718 | Staff Error | Unknown | TRUE | Prev | NA | NA |  | 2012-E-0030 | No.3 Transformer 500/330/33kV | E | 2012Q4 | KCR |  | TX | 2012-11-11 00:01 | 2012-11-11 10:12 |  |  |  | Aux tx disconnector 2433 is locked open. Aux TX Buchholz alarm has been isolated. No.3 Tx buchholz alarm on SCADA will only be main transformer. Alarms have been seperated from the No.3 Aux TX Buchholz. No.3 Tx Buchholz alarm on SCADA will only be Main Tr |  | Primary Equipment | [5 empty] | 0 | 0 | 2012
2121 | 121694 | HV Equipment | Unknown | TRUE | TX | NA | NA |  | 2012-E-0031 | No.3 Transformer 330/132/11kV | E | 2012Q4 | WG1 |  | TX | 2012-11-15 13:12 | 2012-11-25 13:43 |  |  |  | Bushing being replaced. | Unknown | Primary Equipment | [5 empty] | 0 | 0 | 2012
2122 | 121702 | Lightning/Storm | Unknown | TRUE | TL | Yes | 59.38 |  | 2012-F-0454 | 5A4 Bayswater - Wollar 500kV TL | Z | 2012Q4 | BAY, WOL |  | TL | 2012-11-16 03:54 | 2012-11-16 03:54 | Protection details to be followed up |  |  |  | Rain | Primary Equipment | [5 empty] | 0 | 0 | 2012
2124 | 121770 | Lightning/Storm | Lightning or Storm | TRUE | TL | Yes | 59.22 |  | 2012-F-0458 | 8E Armidale - Dumaresq 330kV TL | Z | 2012Q4 | AR1, DMQ |  | TL | 2012-11-18 04:17 | 2012-11-18 04:17 | single pole reclose DMQ distance to Fault 119km AR1 distance to fault 50km site incident record sheets attached to outage protection details updated. | 18/01/2013 9:52:00 AM ¦ Nil. ¦ Nil. |  | Single phase (white) trip and reclose. Protection flagging indicated a white phase fault to earth. The distance to fault was indicated as being 119km from Dumaresq substation, which is in the vicinity of structures 412 to 413. There were no interruptions | Thunderstorm | Primary Equipment | [5 empty] | 0 | 0 | 2012
2125 | 121912 | HV Equipment | Unknown | TRUE | CBOil |  |  |  | Not Available | 96N Armidale - Inverell 132kV TL | Z | 2012Q4 | AR1, INV |  | TL | 2012-11-21 17:36 | 2012-11-21 18:26 |  |  |  | CB failed to close. |  | Primary Equipment | Northern |  |  |  |  | 0 | 0 | 2012
2126 | 121982 | Animal/Bird | HV Equipment Failure | TRUE | Other | NA | NA |  | 2012-E-0033 | No.3 Transformer 132/66/11kV | E | 2012Q4 | COF |  | TX | 2012-11-23 11:55 | 2012-11-23 15:34 |  | 5/02/2013 3:44:00 PM ¦ Nil. ¦ Nil. |  | The fitter requested the outage to enable an inspection of the red phase VT in the No.3 Transformer Bay, as he could hear an unusual noise originating from it. The inspection revealed that the noise was coming from a cricket, which was found inside one of | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
2127 | 121999 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 | NA | NA |  | 2012-E-0035 | No.1 Capacitor | E | 2012Q4 | VYD |  | CAP | 2012-11-25 14:47 | 2012-11-29 15:37 | Alarms received. #1 Cap CB abnormal, #1 Cap Voltage Control Non Auto, #1 Cap Control Locked Out and #1 Cap Voltage Control Inop alarms. Capacitor was in service at the time. Taken out of service. | Nil. ¦ Follow up with Control Systems re: database change. |  | Alarms received. #1 Cap CB abnormal, #1 Cap Voltage Control Non Auto, #1 Cap Control Locked Out and #1 Cap Voltage Control Inop alarms. Capacitor was in service at the time and was taken out of service. The excess run timer was replaced and timeing checks | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
2128 | 122021 | Lightning/Storm | Lightning or Storm | TRUE | TL | No FR | No FR |  | 2012-F-0467 | 83 Liddell - Muswellbrook 330kV TL | Z | 2012Q4 | LD1, MRK |  | TL | 2012-11-26 18:50 | 2012-11-26 18:50 | CB 5042 @ LD1 manually closed OK. CB 832B @ MRK isolated (No.2 TX outage) at time of tripping. MRK protection details added and attached to outage 122021. | 18/01/2013 1:33:00 PM ¦ Nil. ¦ A climbing inspection of the road and rail crossings is to be arranged. A close inspection of the line will be carried out during the next routine aerial patrol of the line. |  | The Indji system indicated several lightning strikes along the length of the line (17km) around the time of the trip. The outage has been noted for close inspection of the line during the next routine aerial patrol. | Thunderstorm | Primary Equipment | [5 empty] | 0 | 0 | 2012
2129 | 122022 | Lightning/Storm | Lightning or Storm | TRUE | TL | No FR | No FR |  | 2012-F-0468 | 82 Liddell - Tomago 330kV TL | Z | 2012Q4 | LD1, TOM |  | TL | 2012-11-26 19:36 | 2012-11-26 19:36 |  | 18/01/2013 1:08:00 PM ¦ Nil. ¦ Close inspection of the line during the next routine aerial patrol. |  | The Indji system indicated several lightning strikes in the area between structures 14 and 30 around the time of the trip. The outage has been noted for close inspection during the next routine aerial patrol of the line. | Thunderstorm | Primary Equipment | [5 empty] | 0 | 0 | 2012
2130 | 122523 | Lightning/Storm | Lightning or Storm | TRUE | TL | No FR | No FR |  | 2012-F-0470 | 990 Yass - Wagga 132 132kV TL | Z | 2012Q4 | WG2, YSN |  | TL | 2012-11-27 12:13 | 2012-11-27 12:13 |  | 7/04/2013 6:16:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | INDJI indicates 30 lightening strikes in close proximity to the 990 TL in a 15minute window either side of 1:13pm. The lightening strike that correlates best with the recorded trip time occurred approximately 520m from the line between spans 143 and 144 a | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
2131 | 122536 | Lightning/Storm | Unknown | TRUE | TL | No FR | No FR |  | 2012-F-0471 | 991 Wagga North - Murrumburrah 132kV TL | Z | 2012Q4 | MRU, WGN |  | TL | 2012-11-27 14:05 | 2012-11-27 14:05 |  | 7/04/2013 6:19:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | INDJI indicates 31 lightening strikes in close proximity to the 991 TL in a 15minute window either side of 15:05pm. The closest Lightening strike occurred approximately 15m from 991 TL between spans 313 and 314. Due to Thunderstorms and the knowledge that | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
2132 | 122558 | Lightning/Storm | Lightning or Storm | TRUE | TL | No FR | No FR |  | 2012-F-0475 | 945 Wellington - Molong tee Well'n Town 132kV TL | Z | 2012Q4 | MOL, WL1 |  | TL | 2012-11-28 16:27 | 2012-11-28 16:27 |  | 9/01/2013 9:47:00 AM ¦ Nil. ¦ Nil. |  | Protection flagging indicated a fault 31.67km from Molong Substation. Storms reported in the area. A visual inspection of the area (Structures 107 - 112) found no signs of damage. | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
2142 | 122756 | Staff Error | HV EQT Staff Error | TRUE | Prev | No FR | No FR |  | 2012-F-0487 | 132kV A Bus No.1 Section | Q | 2012Q4 | VYD |  | BB | 2012-11-30 08:56 | 2012-11-30 09:39 | Trip occurred when carrying out testing of No.1 Capacitor C.T. and a set of earths were left in place in error. This has resulted in current being passed through the 132kV BBP C.T. cores unintentionally and the operation of the BBP. | 9/01/2013 10:58:00 AM ¦ Nil. ¦ Nil. |  | Trip occurred when carrying out testing of No.1 Capacitor C.T. and a set of earths were left in place in error. This has resulted in current being passed through the 132kV BBP C.T. cores unintentionally and the operation of the BBP. | Fine | External | [5 empty] | 1 | 1 | 2012 | Earthing error during maintenance leading to incorrect protection operation
2134 | 122763 | HV Equipment | HV Equipment Failure | TRUE | CT | NA | NA |  | 2012-E-0037 | 969 Tamworth 330 - Gunnedah 132kV TL | E | 2012Q4 | GN2, TA1 |  | TL | 2012-11-30 17:42 | 2012-11-30 18:55 | CT SF6 low pressure alarm. |  |  | CT SF6 low pressure alarm. |  | Oil/Gas Levels | [5 empty] | 0 | 0 | 2012
2143 | 123086 | Lightning/Storm | Lightning or Storm | TRUE | TL | No FR | No FR |  | 2012-F-0501 | 999 Yass - Cowra 132kV TL | Z | 2012Q4 | CW2, YSN |  | TL | 2012-11-30 18:40 | 2012-11-30 18:40 |  | 9/01/2013 9:54:00 AM ¦ Nil. ¦ Nil. |  | No storms reported at the time of trip. Proection flagging indicated a distance to fault 49.35km from Cowra substation (around str 172). Inspections completed on structures 169 - 176 with no damage found. | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
2136 | 122774 | HV Equipment | HV Equipment Failure | TRUE | Rx | NA | NA |  | 2012-E-0038 | No.2 330kV Reactor | E | 2012Q4 | AR1 |  | RX | 2012-11-30 22:02 | 2012-12-01 10:22 | Hot Winding urgent alarm recieved at 2155 30/11/12 RX taken out of service at 2202 30/11/12 Hot winding alarm reset at 0008 01/12/12 please note these times are in EST. | 19/12/2012 3:31:00 PM ¦ Nil. ¦ Nil. |  | The on call fitter and protection tech. both attended site in the morning on Saturday 01/12/12 and confirmed that the winding temperature settings were as per the RTI. The buchholz was also inspected and there was no evidence of any gas accumulation in th |  | Primary Equipment | [5 empty] | 0 | 0 | 2012
2137 | 122806 | Animal/Bird | Lightning or Storm | TRUE | TL | Yes | 51.09 |  | 2012-F-0490 | 5A4 Bayswater - Wollar 500kV TL | Z | 2012Q4 | BAY, WOL |  | TL | 2012-12-02 01:30 | 2012-12-02 01:30 | Storms in area. | 18/01/2013 1:57:00 PM ¦ Nil. ¦ A close insection of the line will be carried out during the next routine aerial patrol. |  | Protection flagging indicated a blue phase fault to earth at a distance of 61.9km from Bayswater and 47.1km from Wollar. This is in the vicinity of structures 145-160. Although there were thunderstorms in the area at the time, no lightning activity was re | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
2141 | 122953 | HV Equipment | HV Equipment Failure | TRUE | Rx | NA | NA |  | 2012-E-0040 | No.2 330kV Reactor | E | 2012Q4 | AR1 |  | RX | 2012-12-03 04:05 | 2012-12-03 11:56 | RX taken out of service due to Hot Winding & Hot Oil alarms. Temp around 90 deg. 600L drained from RX and made available. | 19/12/2012 3:33:00 PM ¦ Nil. ¦ Nil. |  | An inspection revealed that the oil level indicator on the conservator was showing the conservator oil was at its maximum level. Subsequently, approx. 600L of oil was taken out of the reactor. All the valves in the oil convection path that could be inspec | Mild | Oil/Gas Levels | [5 empty] | 0 | 0 | 2012
2138 | 122881 | HV Equipment | Unknown | TRUE | TL | No FR | No FR |  | 2012-F-0494 | 944 Orange North - Wallerawang 132kV (New) Line | Z | 2012Q4 | ONO, WWS |  | TL | 2012-12-03 04:36 | 2012-12-03 04:36 |  | 9/01/2013 11:08:00 AM ¦ Nil. ¦ Upcoming outage of 944 Line for replacement of insulators. |  | Patrol of the area (Str 179 - 185) was undertaken and found burnt insulators on str 183. Upcoming outage of 944 Line for replacement of insulators. | Unknown | Primary Equipment | [5 empty] | 0 | 0 | 2012
2139 | 122927 | Lightning/Storm | Lightning or Storm | TRUE | TL | No FR | No FR |  | 2012-F-0495 | 84 Liddell - Tamworth 330 330kV TL | Z | 2012Q4 | LD1, TA1 |  | TL | 2012-12-03 08:34 | 2012-12-03 19:36 | AR1 SVC set to low gain 88 TL A/R made non auto at MRK. 964 T/L A/R made non auto a TRE 96G T/L A/R made non auto a KS2 9W T/L A/R made non auto a KS2 as per OM521. | 5/12/2012 3:21:00 PM ¦ Nil. ¦ The two insulator strings on white and blue phases will be replaced and returned for detailed inspection when another outage can be arranged. |  | Protection flagging indicated a red phase fault to earth at a distance of 122.5km from the Tamworth end of the line, which is in the vicinity of structure 36. The Indji system showed a heavy lightning strike near structure 31 at the same time as the fault | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
2140 | 122951 | Condition Monitor | HV Equipment Failure | TRUE | TX | NA | NA |  | 2012-E-0039 | No.3 Transformer 330/132/11kV | E | 2012Q4 | WRH |  | TX | 2012-12-03 11:07 | 2012-12-03 11:08 | TX de-energised on receiving a Condition Monitoring L1 alarm. | 7/02/2013 3:33:00 PM ¦ Nil. ¦ Nil. |  | TX de-energised on receiving a Condition Monitoring L1 alarm. The alarm was traced back to the Doble bushing monitoring system, which was indicating an issue with one of the 330kV bushings. Dirana tests of the 330kV and the 132kV bushings were carried out | Rain | Primary Equipment | [5 empty] | 0 | 0 | 2012 | Condition monitoring alarm
2146 | 123521 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 | Not reviewed | Not reviewed |  | 2012-F-0509 | No.1 Reactor | Z | 2012Q4 | SYS |  | RX | 2012-12-07 05:48 | 2012-12-13 13:12 | No.1 Rx at Sydney South No.1 Rx CB..5912 failed still closed on R phase. HVPRI 41795 created to Isolate & Earth No.1 Rx and No.1 Rx CB..5912. | As Above ¦ As Above |  | CB 5912 failed to open on red phase. As a result 41 (Sydney South - Beaconsfield West) 330kV Cable tripped as did BFS No.3 Transformer. TransGrid staff called to site and investigations revealed damage to red phase mechanism aswell as damage to the closin | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2012
2158 | 123574 | Staff Error | Unknown | TRUE | Prev | No FR | No FR |  | 2012-F-0515 | 330kV B Bus Section No.1 | S | 2012Q4 | SYW |  | BB | 2012-12-10 10:02 | 2012-12-10 11:02 | Work being carried out in H.V. Switchyard by contractors at 1F Spare Bypass Disconnector 1F4. Control cabling was being cut and a positive supply was applied through to the 330kV B Bus No.1 Section No.1 Protection Multitrip relays. Investigatiion by prote | 9/01/2013 3:49:00 PM ¦ Nil. ¦ Nil. |  | Work being carried out in H.V. Switchyard by contractors at 1F Spare Bypass Disconnector 1F4. Control cabling was being cut and a positive supply was applied through to the 330kV B Bus No.1 Section No.1 Protection Multitrip relays. Investigatiion by prote | Mild | External | [5 empty] | 1 | 1 | 2012 | Incorrect cable cut leading to incorrect protection operation
2152 | 124084 | HV Equipment | Unknown | TRUE | TL | Not reviewed | Not reviewed | Lost load 3 MW | 2012-F-0516 | X5/3 Baranald - Buronga 220kV TL | Z | 2012Q4 | BRD, BRG |  | TL | 2012-12-12 12:54 | 2012-12-14 16:47 |  |  |  | 3MW load interrupted at Balranald. Staff have found wire on the ground about 5 kilometres west of Balranald (towards Buronga). Essential Energy advise customer load was restored at 15:30hrs. X5/1 Darlington Point to Balranald T/L RTS at 18:42hrs to restor |  | Primary Equipment | [5 empty] | 0 | 0 | 2012
2151 | 124014 | HV Equipment | HV Equipment Failure | TRUE | CT | NA | NA |  | 2012-E-0042 | No.2 Shunt Reactor | Q | 2012Q4 | ER0 |  | RX | 2012-12-15 11:55 | 2012-12-19 10:43 | Faulty CT replaced. | 1/02/2013 1:19:00 PM ¦ Nil. ¦ The faulty CT was transported to the NRC workshop, where it will be inspected to determine the likely cause of the arcing across the DLA link. A report will be prepared following the inspection. |  | Reactor was from service following an arcing sound coming from the 66kV red phase CB2922 CT associated with No.2 Reactor. The CT was inspected and evidence of arcing was found across the CT's DLA link. The CT's on white and blue phases were also inspected |  | Primary Equipment | [5 empty] | 0 | 0 | 2012
2159 | 124166 | Relay | Backup Operation | TRUE | Prot | Yes | 278.28 (LBU) |  | 2012-F-0519 | No.5 Transformer 330/132/11kV | Z | 2012Q4 | SYW |  | TX | 2012-12-18 05:14 | 2012-12-18 15:08 | Faulty IOC relay - inital trip caused by explosive failure 1-2 A bus section CB..4102 | 9/01/2013 2:51:00 PM ¦ As Above. ¦ As Above. |  | Faulty IOC relay - inital trip caused by explosive failure 1-2 A bus section CB..4102. Faulty relay contact was the cause. | Fine | Primary Equipment | [5 empty] | 1 | 0 | 2012 | Faulty protection relay
2165 | 124204 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 | Yes | 278.28 (LBU) | Lost Load 82.20MWhr | 2012-F-0521 | 132kV A Bus 1-2 Section CB 4102 | S | 2012Q4 | SYW |  | CB | 2012-12-18 05:14 | 2013-01-09 11:08 |  |  |  | Explosive failure 1-2 A bus section CB..4102. Due to explosion an overhead earth wire fell on 132kV Bus A2 causing tripping of both Busbars A1 and A2. Loss of load 82.2MWhrs on Endeavour Energy feeders 217 and 218. Load lost. |  | Primary Equipment | [5 empty] | 0 | 0 | 2012
2166 | 124388 | Unknown | Unknown | TRUE | TL | No FR | No FR |  | 2012-F-0537 | 96T Armidale - Glen Innes 132kV TL | Z | 2012Q4 | AR1, GNS |  | TL | 2012-12-23 03:55 | 2012-12-23 03:55 | Distance to Fault 93.47km from Armidale Glen Innes Protection details added. Distance to Fault 7.03km from Glen Innes | 21/01/2013 3:42:00 PM ¦ Nil. ¦ Nil. |  | Protection flagging indicated a white phase fault to earth at a distance of 93.47km from Armidale substation. This is in the vicinity of structure 377, north of the Gwydir Highway crossing. A climbing inspection carried out on 08/01/13 between structures | Fine | Unexplained | [5 empty] | 0 | 0 | 2012
2167 | 124390 | Lightning/Storm | Lightning or Storm | TRUE | TL | Not reviewed | Not reviewed |  | 2012-F-0539 | 8 Marulan - Dapto 330kV TL | Z | 2012Q4 | DPT, MRN |  | TL | 2012-12-23 14:39 | 2012-12-23 14:39 | Protection details to be collected. |  |  |  | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
2168 | 124398 | Lightning/Storm | Lightning or Storm | TRUE | TL | No FR | No FR |  | 2012-F-0546 | 63 Wagga 330 - Darlington Point 330kV TL | Z | 2012Q4 | DNT, WG1 |  | TL | 2012-12-23 20:32 | 2012-12-23 20:32 | At 20:32hrs 63 Wagga to Darlington Point 330 kV T/L tripped and reclosed operating the X5 tripping scheme. CBs 7442, 7432 and X52 opened. No.3 Capacitor opened manually at Darlington point at 20:33hrs No.4 and No.3 Transformer RTS at 2056hrs. X5 closed at | 7/04/2013 7:09:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | At 20:32hrs 63 Wagga to Darlington Point 330 kV T/L tripped and reclosed operating the X5 tripping scheme. CBs 7442, 7432 and X52 opened. No.3 Capacitor opened manually at Darlington point at 20:33hrs. No.4 and No.3 Transformer RTS at 2056hrs. X5 closed a | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
2169 | 124403 | Lightning/Storm | Lightning or Storm | TRUE | TL | Yes | 73.13 |  | 2012-F-0550 | 5 Yass - Marulan 330kV TL | Z | 2012Q4 | MRN, YSN |  | TL | 2012-12-23 20:47 | 2012-12-23 20:47 |  | 7/04/2013 6:57:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | Protection details indicate C phase to earth fault in the middle 60% of the line where Zone 1 protection exists however no distance to fault was recorded. INDJI doesn’t show any lightening strikes at the time of the trip and reclose. Due to Thunderstorms | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
2170 | 124426 | Lightning/Storm | Lightning or Storm | TRUE | TL | Not reviewed | Not reviewed |  | 2012-F-0555 | 993 Wagga 330 - Gadara 132kV TL | Z | 2012Q4 | GAD, WG1 |  | TL | 2012-12-24 15:36 | 2012-12-24 15:36 | storms in area, ncm adv. |  |  | storms in area, ncm adv. | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
2171 | 124427 | Lightning/Storm | Lightning or Storm | TRUE | TL | Yes | 50.16 |  | 2012-F-0556 | 2 Upper Tumut - Yass 330kV TL | Z | 2012Q4 | UT1, YSN |  | TL | 2012-12-24 16:02 | 2012-12-24 16:02 |  | 7/04/2013 5:59:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  |  | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
2172 | 124428 | Lightning/Storm | Lightning or Storm | TRUE | TL | Not reviewed | Not reviewed |  | 2012-F-0557 | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2012Q4 | GTH, MUR, GHI |  | TL | 2012-12-24 16:21 | 2012-12-24 16:27 | 97G was earlier transferred to cooma on SHL request. 97G CB open at Guthega. 97G was energised via SCADA at Murray S.S. at 16:27hrs 24-12-2012 Requested by NCM |  |  | 97G was earlier transferred to cooma on SHL request. 97G CB open at Guthega. 97G was energised via SCADA at Murray S.S. at 16:27hrs 24-12-2012 Requested by NCM | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
2173 | 124435 | Lightning/Storm | Lightning or Storm | TRUE | TL | Yes | 71.56 |  | 2012-F-0561 | 24 Vales Point - Eraring 330kV TL | Z | 2012Q4 | ER0, VP1 |  | TL | 2012-12-24 21:14 | 2012-12-24 23:25 | 24 T/L tripped and appeared to have failed a R/C attempt, RTS via SCADA after prot'n details gathered and HMI at VPPS indicated 242M failed to R/C, B.Fraser gave clearance to RTS | 21/01/2013 3:15:00 PM ¦ Nil. ¦ Nil. |  | T/L tripped and appeared to have failed a R/C attempt, RTS via SCADA. Protection flagging indicated a red phase fault to earth. A detailed inspection was carried out on Wednesday 02/01/2013 between structures 35 and 40. No evidence of a flashover or any o | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
2189 | 124435 | Relay | Lightning or Storm | TRUE | Cont | Yes | 71.56 |  | 2012-F-0561 | 24 Vales Point - Eraring 330kV TL | Z | 2012Q4 | ER0, VP1 |  | TL | 2012-12-24 21:14 | 2012-12-24 23:25 | 24 T/L tripped and appeared to have failed a R/C attempt, RTS via SCADA after prot'n details gathered and HMI at VPPS indicated 242M failed to R/C, B.Fraser gave clearance to RTS | 21/01/2013 3:15:00 PM ¦ Nil. ¦ Nil. |  | An inspection of the auto reclose scheme revealed a loose ribbon cable between the Controller Output, Interface Block and Close Pulse Follower Relays caused the failed Auto Close Pulse to the Circuit Breaker, which prevented auto reclosing of the breaker. | Thunderstorm | Primary Equipment | [5 empty] | 0 | 0 | 2012 | Reclose failure, not protection
2174 | 124460 | Lightning/Storm | Lightning or Storm | TRUE | TL | Yes | 58.28 |  | 2012-F-0576 | 5A3 Bayswater - Mt Piper 500kV TL | Z | 2012Q4 | BAY, MTP |  | TL | 2012-12-25 14:26 | 2012-12-25 14:26 |  | 23/01/2013 3:48:00 PM ¦ Nil. ¦ A close inspection of the line in the vicinity of structure 27 will be carried out during the next routine patrol. |  | The Indji system recorded a lightning strike in the vicinity of structure 27 at the time of the trip. The trip has been noted for a close inspection of the line to be carried out in the vicinity of structure 27 during the next routine patrol. | Thunderstorm | External | [5 empty] | 0 | 0 | 2012
2176 | 124872 | HV Equipment | Non TransGrid Reason | TRUE | Disc |  |  |  | 2013-F-0004 | U7 Upper Tumut - Tumut 2 330kV TL | Y | 2013Q1 | UT1 |  | TL | 2013-01-03 11:03 | 2013-01-05 14:17 | SHL advises Guard Gate trip of Units 7 and 8. SHL staff required to be called out to reset protections at Tumut 2 PS and UTSS. C.B. 5012 closed at 1417 hours. |  |  | While carrying out PRI to place C.B U72 on bypass, disconnector U76 failed to close fully, remaining open for 30cms on all phases. U76 was closed manually by hand with the Reserve Bus de-energised & U7 fully O/S. | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2013
2177 | 124958 | Unknown | Unknown | TRUE | TX |  |  |  | 2013-F-0016 | No.2 Transformer 330/132/11KV | Z | 2013Q1 | JDA |  | TX | 2013-01-05 14:58 | 2013-01-05 17:30 |  | 17/05/2013 10:33:00 AM |  | Main Tank Buchholz operated on #2 transformer. No gas detected from Buchholz. Apparently a known issue. Very thoroughly investigated and no cause found. Has been two trips in very hot humid weather. Pump start up has been ruled out - pumps did not operat | Very Hot | Unexplained | [5 empty] | 0 | 0 | 2013
2179 | 124978 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0018 | 990 Yass - Wagga 132 132kV TL | Z | 2013Q1 | WG2, YSN |  | TL | 2013-01-05 22:19 | 2013-01-05 22:19 | Follow up of protection details required. Check C.B. 9902 cyclo at Wagga 132 as no visibility of C.B. operation via SCADA. WG2 prot details obtained 22.1.2013, 1 CB & 1 A/R operation. | 7/04/2013 6:43:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | A white phase to earth fault occurred approximately 91.12km out of the Yass Z/S around structure 228 (Calculated from TAMIS). INDJI indicates that lightening strike occurred approximately 320m from structure 309 at 11:19:45pm. Due to Thunderstorms and the | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2178 | 124976 | HV Equipment | Unknown | TRUE | Cap |  |  |  | 2013-E-0001 | No.4 Capacitor | E | 2013Q1 | NEW |  | CAP | 2013-01-05 22:58 | 2013-01-10 13:07 | Neutral Imbalance alarm received via SCADA @ 2257 hours. Alarm reset when No.4 Capacitor taken out of service. | 10/01/2013 3:33:00 PM ¦ Nil. ¦ Nil. |  | Neutral Imbalance alarm received via SCADA at 2257 hours. Alarm reset when No.4 Capacitor was taken out of service. 4 cans were found faulty. No common cause found with other can failures at Newcastle. Affects all 4 banks. 1982/84 plus 1999/00. No co | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2013
2180 | 125079 | Bushfire | Bushfire | TRUE | TL |  |  |  | 2013-F-0024 | 6 Canberra - Capital Wind Farm 330kV TL | Z | 2013Q1 | CA1, CWF |  | TL | 2013-01-08 13:46 | 2013-01-08 13:46 | 6 T/L tripped at the same time as 3W T/L and the 330kV C Bus at Capital Wind Farm. | 7/04/2013 6:38:00 PM ¦ N/A ¦ Continue to monitor during next climbing inspections. This has been noted for the next scheduled aerial patrol. |  | 3W Kangaroo Valley to Capital Wind Farm 330 kV T/L tripped and auto reclosed. The Capital Wind Farm S/S 330kV C Bus also tripped, interrupting 127MW generation at Capital Wind Farm PS. 3W T/L remains on load via CB 3W2B and 6 T/L. Staff have been called o |  | External | [5 empty] | 0 | 0 | 2013
2194 | 125253 | Bushfire | Bushfire | TRUE | TL |  |  |  | 2013-F-0030 | 3W Capital Wind Farm - Kangaroo Valley 330kV TL | Z | 2013Q1 | KVS, CWF |  | TL | 2013-01-08 13:46 | 2013-01-08 13:46 | Also refer to FEOR's 0023 & 0029 | As Above. ¦ As Above. <Duplicate Record> 7/04/2013 6:22:00 PM ¦ N/A ¦ Continue to monitor during next climbing inspections. This has been noted for the next scheduled aerial patrol. |  | Also refer to FEOR's 0023 & 0029. FEOR-0023/2 comment - The 330kV C Bus tripped at the same time as the 3W T/L had tripped and reclosed. (3W2B had only closed) 6 T/L Canberra to Capital had also tripped at the same time. Capital P.S ( Greg 0408092552) has | Very Hot | External | [5 empty] | 0 | 0 | 2013
2181 | 125081 | Bushfire | Bushfire | TRUE | TL |  |  |  | 2013-F-0024 | 3W Capital Wind Farm - Kangaroo Valley 330kV TL | Z | 2013Q1 | KVS, CWF |  | TL | 2013-01-08 14:06 | 2013-01-10 16:56 | Refer to FEOR 0023/1 and 0030 | Nil. ¦ WO raised to replace marker ball. <Duplicate Record> 7/04/2013 6:32:00 PM ¦ N/A ¦ Continue to monitor during next climbing inspections. This has been noted for the next scheduled aerial patrol. |  | The T/L tripped, reclosed, tripped and locked out due to bushfire. Aerial inspection carried out on 10/01/2013 and line given all clear to return to service. Transmission Line was patrolled on the 22/1/2013, the fire has burnt along the easement from stru | Very Hot | External | [5 empty] | 0 | 0 | 2013
2182 | 125091 | HV Equipment | HV Equipment Failure | TRUE | CT |  |  | Lost load 11MW | 2013-F-0026 | 22kV Bus No.1 Section | S | 2013Q1 | BKH |  | BB | 2013-01-09 02:50 | 2013-01-09 04:29 | Railway Town CT failed taking out No.1 Transformer, No.1 SVC, 22kV Bus Section 1, GT's, No.1 &3 Capacitors, South Fdr, Railway Town Fdr & Talc St 2 Fdr. | 4/03/2013 3:49:00 PM |  | A cat climbing up the red phase CT on Railway town feeder caused shorting of the HV conductor and the main tank of the CT, and causing the bus to trip. After the fault a visual inspection revealed negligible damage to the CT. The CT was cleaned and DDF/m |  | Primary Equipment |  |  |  |  | Lost load 11MW. | 0 | 0 | 2013
2190 | 125235 | Switching error | Sec Eqt Staff Error | TRUE | Prev |  |  |  | 2013-F-0028 | No.2 Transformer 500/330/33kV | Z | 2013Q1 | BBY |  | TX | 2013-01-10 08:17 | 2013-01-10 08:46 | Staff were testing Transformer fans and pumps, inadvertently left two out of four pumps 'Auto' on white phase when all should have been selected to manual before testing commenced. Pumps shut down, protection reset anf Transformer RTS. | 4/03/2013 4:05:00 PM |  | While testing the transformer fans and pumps, staff inadvertently left two out of four pumps in 'Auto' on white phase when all should have been selected to 'Manual' before testing commenced. This caused the pumps to shut down. Test instructions are in pla | Fine | External | [5 empty] | 0 | 1 | 2013 | Incorrect isolation of transformer pumps
2191 | 125279 | Protection | Unknown | TRUE | Prot | TBA | TBA | lost load 0.5MW | 2013-F-0032 | 66kV Bus Section 3 | Q | 2013Q1 | MRE |  | BB | 2013-01-11 05:45 | 2013-01-11 09:28 | Slow operation or protection relay problem with CB 7222 under investigation. CB 7222 isolated for timing checks at time of report. | 12/02/2013 11:32:00 AM ¦ Nil. ¦ Nil. |  | An inspection of CB7222 did not reveal any issues. Contact Resistance, Insulation Resistance and Timing Tests were also carried out on CB7222. All results were acceptable. Inspections were then carried out on the associated protection schemes. The fault r | Fine | [5 empty] | lost load 0.5MW. | 1 | 0 | 2013 | According to THEOS followup report a design fault in the protection scheme, excerpt: "The fault record (sic) information indicated a spurious signal, 25ms in duration, coming into the No.1 Feeder Prot relay via the BBP trip input"
2196 | 125349 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0043 | 84 Liddell - Tamworth 330 330kV TL | Z | 2013Q1 | LD1, TA1 |  | TL | 2013-01-13 16:16 | 2013-01-13 16:16 |  | 13/02/2013 8:14:00 AM ¦ Nil. ¦ Carry out a close inspection of this section of the line during the next routine inspection. |  | Protection flagging indicated a blue phase fault to earth around 40km from Liddell substation. The Indji system indicated lightning activity in the vicinity of structure 71 around the time of the fault. After confirming that there are no major road crossi | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2197 | 125350 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0044 | 9U3 Gunnedah - Narrabri 132kV TL | Z | 2013Q1 | GN2, NB2 |  | TL | 2013-01-13 17:02 | 2013-01-16 14:11 |  | 13/02/2013 2:10:00 PM ¦ Nil. ¦ A committee of enquiry has been arranged to further investigate this incident. |  | Upon inspection, 4 wooden H-pole suspension structures (str's 688, 791, 792 and 793) were found to have failed. Replacement of the failed structures commenced on Monday 14/01/13 and the line was subsequently returned to service. | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2198 | 125351 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0045 | 968 Tamworth 330 - Narrabri 132kV TL | Z | 2013Q1 | NB2, TA1 |  | TL | 2013-01-13 17:11 | 2013-01-15 08:34 |  | 13/02/2013 9:57:00 AM ¦ Nil. ¦ A committee of enquiry has been arranged to further investigate this incident. |  | Upon inspection, 1 wooden H-pole structure and 1 concrete structure (str's 739 and 740) were found to have failed. Replacement of the failed structures commenced on Monday 14/01/13 and the line was subsequently returned to service on Tuesday 15/01/13 | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2199 | 125365 | Lightning/Storm | Lightning or Storm | TRUE | TL | N/A | N/A |  | 2013-F-0053 | 96M Narrabri - Moree 132kV TL | Z | 2013Q1 | MRE, NB2 |  | TL | 2013-01-13 17:33 | 2013-01-13 17:33 | Loss of SCADA services at Narrabri and Moree. Time of outage derived from SCADA load trends on 96N Inverell 132kV T/L at Armidale. | 21/03/2013 2:07:00 PM ¦ Nil. ¦ Nil. |  | Loss of SCADA services at Narrabri and Moree. Time of outage derived from SCADA load trends on 96N Inverell 132kV T/L at Armidale. Protection flagging indicated a zone 1, red and white phase fault to earth. There were severe storms around Narrabri around | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2200 | 125366 | Lightning/Storm | Unknown | TRUE | TL |  |  | Lost load 18MW | 2013-F-0054 | 96M Narrabri - Moree 132kV TL | C | 2013Q1 | MRE, NB2 |  | TL | 2013-01-13 17:34 | 2013-01-13 19:04 | Trip occurred at Moree only following a successful TAR operation at 1733 hours (refer to FEOR 2013-F-0053). Total loss of supply to Narrabri 132kV Substation due to earlier TARTLO of 968 Tamworth to Narrabri 132kV T/L and 9U3 Gunnedah to Narrabri 132kV T/ | 21/03/2013 2:08:00 PM ¦ Nil. ¦ Nil. |  | Trip occurred at Moree only following a successful TAR operation at 1733 hours (refer to FEOR 2013-F-0053). Total loss of supply to Narrabri 132kV Substation due to earlier TARTLO of 968 Tamworth to Narrabri 132kV T/L and 9U3 Gunnedah to Narrabri 132kV T/ | Thunderstorm | External |  |  |  |  | Lost load 18MW. | 0 | 0 | 2013
2206 | 125414 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0055 | 9U4 Glen Innes - Inverell 132kV TL | Z | 2013Q1 | GNS, INV |  | TL | 2013-01-13 21:28 | 2013-01-13 21:28 | Distance to fault 30.39km From Inverell Distance to fault 35.19km from Glen Innes Glen Innes Protection details added and outage time corrected. Site incident record sheets added to notes of outage ID 125414. Please note that time and date on the protect | 13/02/2013 3:40:00 PM ¦ Nil. ¦ Nil. |  | The Indji system indicated a lightning strike in the vicinity of structure 113 around the time of the fault. A ground patrol found no evidence of a fault or any damage from lightning or storms. Distance to fault 30.39km From Inverell and 35.19km from Glen | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2207 | 125646 | Relay Setting | Unknown | TRUE | Prot | TBA | TBA |  | 2013-F-0057 | No.4 Transformer 330/132kV | Z | 2013Q1 | WW1, WWS |  | TX | 2013-01-18 13:41 | 2013-01-22 15:09 | Extremely hot day. Trip occurred whilst re-energising transformer following 3 day continuous outage for maintenance. | 5/02/2013 9:45:00 AM ¦ Nil. ¦ Nil. |  | Trip occurred whilst re-energising transformer following 3 day continuous outage for maintenance. 2nd harmonic inrush current caused the No.1 11kV overcurrent protection to operate. A setting change to the No.1 Protection was completed on 21/01/2013 to fi | Fine | Primary Equipment | [5 empty] | 1 | 0 | 2013 | Incorrect protection settings
2249 | 125641 | HV Equipment | HV Equipment Failure | TRUE | Rx |  |  |  | 2013-E-0002/2 | No.2 330kV Reactor | E | 2013Q1 | AR1 |  | RX | 2013-01-18 13:48 | 2013-01-25 12:51 | Staff at site advised internal noise from Red phase and no2 RX required out of service. | 20/02/2013 3:03:00 PM ¦ Nil. ¦ There is ongoing discussion between Northern Region Substations group and Asset Performance regarding this reactor. Any future actions will be determined based on these discussions. |  | Staff at site advised internal noise from Red phase and No.2 RX required out of service. The reactor was manufactured by GEC under Contract 4165. An external inspection of the reactor was carried out, however no issues were found. High voltage testers wer |  | Primary Equipment | [5 empty] | 0 | 0 | 2013
2208 | 125647 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2013-E-0003 | No.3 Transformer 330kV CB 5432A | Q | 2013Q1 | TOM |  | CB | 2013-01-18 15:56 | 2013-01-18 18:06 |  | 20/02/2013 2:45:00 PM ¦ Nil. ¦ Nil. |  | Hydraulic pump pressure low and falling and pump running CB required open before it goes into lockout. NCM advised CB opened. The CB is a Siemens 3AQ2 model, purchased under Contract 3937 and commissioned in 1992. The CB was bled and pumped back up to pre |  | Oil/Gas Levels | [5 empty] | 0 | 0 | 2013
2209 | 125661 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0060 | 8M Dumaresq - Bulli Creek 330kV TL | Z | 2013Q1 | DMQ |  | TL | 2013-01-19 17:57 | 2013-01-19 17:57 | 8M Tripped and Reclosed at Dumaresq. 8M did not syncronse at Bulli Creek. Power link placed on load via SCADA. | 13/02/2013 1:59:00 PM ¦ Nil. ¦ Close inspection of the line during the next routine inspection. |  | 8M Tripped and Reclosed at Dumaresq. 8M did not syncronse at Bulli Creek. Power link placed on load via SCADA. The Indji system indicated lightning around the time of the trip in the vicinity of Structures 52-53 & 117-118. The insulators used on this line | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2210 | 125867 | Contractor Error | HV EQT Staff Error | TRUE | Prev |  |  |  | 2013-F-0068 | No.2 Capacitor | Q | 2013Q1 | BFD |  | CAP | 2013-01-23 08:31 | 2013-01-25 10:03 | Staff arranged to investigate tripping of Beaconsfield North No.2 Cap CB 4722A and found Contracting Staff under access testing for faulty Cap Cans on the No.2 Bank inadvertently injected current into NUB CT's | 8/02/2013 11:04:00 AM ¦ Nil. ¦ Nil. |  | Testing of the capacitor was being carried out by a contractor. The testing device used was not a passive instrument and the capacitor cans had been left connected resulting in a trip during testing. | Fine | External | [5 empty] | 0 | 1 | 2013 | Incorrect isolation of capacitor cans when performing current injection into NUB CT
2211 | 125898 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0069 | 965 Armidale - Kempsey 132kV TL | Z | 2013Q1 | AR1, KS2 |  | TL | 2013-01-23 16:23 | 2013-01-23 16:23 |  | 13/02/2013 1:52:00 PM ¦ Nil. ¦ Close inspection of this section of the line will be carried out during the next routine inspection. |  | Protection flagging indicated a red and white phase fault to earth, with a distance to fault of 25.4km from Armidale substation in the vicinity of structure 110. There were 2 lightning strikes in the vicinity of structure 100 around the time of the fault. | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2212 | 126009 | Bushfire | Bushfire | TRUE | TL |  |  |  | 2013-F-0073 | 77 Wallerawang - Ingleburn 330kV TL | Z | 2013Q1 | ING, WW1 |  | TL | 2013-01-25 13:28 | 2013-01-25 13:28 | Indication of CB 772 & 5012 at Wallerawang 330 Failed to show open on SCADA and the local HMI indicated invalid state. No1 Prot details from WW1 continue:- 8 times F85 Multi Trips:- 199DR Multitrip D No1 Relay,199DW Multitrip D No1 Relay, 199DB Multitrip | 5/02/2013 8:19:00 AM ¦ Nil. ¦ Nil. |  | Bushfire reported in the area of 76/77 Line. Transmission Line 76/77 was patrolled on the 25/01/2013 as well as the 04/02/2013. Minor pitting marks on both bottom phases approximately 50 metres from structure 329 heading towards 330 were found. This is a | Fine | External | [5 empty] | 0 | 0 | 2013
2214 | 126011 | Bushfire | Bushfire | TRUE | TL |  |  |  | 2013-F-0075 | 76 Wallerawang - Sydney South 330kV TL | Z | 2013Q1 | SYS, WW1 |  | TL | 2013-01-25 13:28 | 2013-01-25 13:28 | Indication of CB 762 & 5022 at Wallerawang 330 Failed to show open on SCADA and the local HMI indicated invalid state. | 5/02/2013 8:36:00 AM ¦ As Above. ¦ As Above. |  | Bushfire reported in the area of 76/77 Line. Transmission Line 76/77 was patrolled on the 25/01/2013 as well as the 04/02/2013. Minor pitting marks on both bottom phases approximately 50 metres from structure 329 heading towards 330 were found. This is a | Mild | External | [5 empty] | 0 | 0 | 2013
2216 | 126039 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0078 | 990 Yass - Wagga 132 132kV TL | Z | 2013Q1 | WG2, YSN |  | TL | 2013-01-26 13:58 | 2013-01-26 13:58 | At 13:58hrs 990 Yass to Wagga 132 132 kV T/L Tripped and reclosed | 7/04/2013 6:25:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | T/L Tripped and reclosed. INDJI indicates 7 lightening strikes in close proximity to the 990 TL in a 15minute window either side of 2:58pm. The lightening strike that correlates best with the recorded trip time and is in closest proximity to the 990 TL oc | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2215 | 126038 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0077 | 3 Lower Tumut - Yass 330kV TL | Z | 2013Q1 | LT1, YSN |  | TL | 2013-01-26 15:34 | 2013-01-26 15:34 | At 15:34hrs 3 Yass to Lower Tumut 330 kV T/L Tripped and Reclosed. CB 32A @ LT1 closed via SCADA SHL advised | 7/04/2013 6:36:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. |  | T/L Tripped and Reclosed. Circuit Breaker 32A at Lower Tumut was closed via SCADA and SHL were advised. INDJI indicates 19 lightening strikes in close proximity to the 3 TL in a 15minute window either side of 4:34pm. Due to Thunderstorms and the knowledge | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2217 | 126044 | Relay | Lightning or Storm | TRUE | Prot | TBA | TBA |  | 2013-F-0083 | No.2 Transformer 500/330/33kV | Z | 2013Q1 | BBY | Protection | TX | 2013-01-26 16:43 | 2013-01-28 16:09 |  |  |  | T60 relay failed. The Tx was RTS following protection relay repairs. | Thunderstorm | Primary Equipment | [5 empty] | 1 | 0 | 2013
2218 | 126063 | HV Equipment | HV Equipment Failure | TRUE | Disc |  |  |  | 2013-F-0088 | 41 Sydney South - Beaconsfield West 330kV Cable | Z | 2013Q1 | BFD, SYS |  | TL | 2013-01-27 05:39 | 2013-01-28 16:17 | RTS 16:15hrs 28.1.2013, fault located on Disc.. 5421 cable side. | 22/03/2013 3:46:00 PM ¦ Nil. ¦ Nil. |  | Cause of trip was a flashover of the spark gap on White Phase Disconnector 5421. Suspect pollution build up from industrial area and heavy rain. | Rain | Primary Equipment | [5 empty] | 0 | 0 | 2013
2219 | 126097 | Unknown/Storm | Unknown | TRUE | TL |  |  |  | 2013-F-0094 | 964 Pt Macquarie - Taree Tee Herons Creek 132kV TL | Z | 2013Q1 | PMQ, TRE |  | TL | 2013-01-29 03:47 | 2013-01-29 03:47 | No Distance to fault details provided. | 7/03/2013 2:25:00 PM ¦ Nil. ¦ Close inspection of the line during the next routine patrol. |  | Protection flagging indicated a zone 1, white phase fault to earth. There is currently no distance to fault information available. There were strong winds and rain in the area at the time of the trip. No lightning activity was recorded in the vicinity of | Rain and Very Windy | External | [5 empty] | 0 | 0 | 2013
2220 | 126102 | HV Equipment | Sec Eqt Malfunction | TRUE | Aux Tx | TBA | TBA |  | 2013-F-0096 | No.2 Transformer 330/132/11KV | Z | 2013Q1 | SYN |  | TX | 2013-01-29 05:30 | 2013-01-29 08:04 | Checks on Auxiliary Transformer Buchholz Relay cabling found low insulation resistance on the bakelite terminal block in the Buchholz relay. Terminal block was cleaned and insulation resistance increased to acceptable value (6 MΩ). | 26/03/2013 3:43:00 PM ¦ Nil. ¦ Nil. |  | Checks on Auxiliary Transformer Buchholz Relay cabling found low insulation resistance on the bakelite terminal block in the Buchholz relay. Terminal block was cleaned and dried and resistance returned to normal. | Rain | Secondary Equipment | [5 empty] | 0 | 0 | 2013 | Failure of bucholz relay terminals
2221 | 126642 | HV Equipment | Unknown | TRUE | Cap |  |  |  | 2013-F-0115 | No.2 Capacitor | Z | 2013Q1 | GN2 |  | CAP | 2013-02-03 10:59 | 2013-02-04 13:28 | No visible evidence of damage to equipment. No operation of earthfault or overcurrent protection. Capacitor isolated at bus pending testing / repair. | 4/02/2013 4:01:00 PM ¦ Nil. ¦ Nil. |  | No visible evidence of damage to equipment. No operation of earthfault or overcurrent protection. Capacitor isolated at bus pending testing / repair. The trip setting of the neutral unbalance relay is 800mA. A visual inspection of the bank revealed no iss | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2013 | THEOS followup indicates faulty cap can, excerpt: "one faulty can being identified on blue phase"
2225 | 127334 | Lightning/Storm | Lightning or Storm | TRUE | TL | N/A | N/A |  | 2013-F-0134 | 72 Mt Piper - Wellington 330kV TL | Z | 2013Q1 | MTP, WL1 |  | TL | 2013-02-10 18:16 | 2013-02-10 18:16 | @ MTP, Bay Coupler C.B.. 5022 closed via Scada. At the same time that 72 T/L tripped, @ WW1, Bay Coupler C.B.. 5042 tripped. Closed via Scada. | 27/03/2013 2:08:00 PM ¦ Nil. ¦ Protection Design liaising with Delta with regards to No.8 Generator. |  | At the same time of this TAR, Wallerawang 330kV Bay Coupler CB 5042 also tripped and closed by SCADA. Normally this CB is tripped by the bay feeder or No.8 Generator at Wallerawang Power Station. 72 Line was patrolled from Structure 15 - Structure 25 on 0 | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2224 | 127333 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0133 | 94M Mt Piper 132 - Beryl tee Mudgee 132kV TL | Z | 2013Q1 | BER, MPP |  | TL | 2013-02-10 18:36 | 2013-02-10 18:36 | S.O./Essential Energy and Endeavour Energy advised. Ilford load transferred to 828 Fdr. |  |  | S.O./Essential Energy and Endeavour Energy advised. Ilford load transferred to 828 Fdr. | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2226 | 127356 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0138 | 86 Tamworth 330 - Armidale 330kV TL | Z | 2013Q1 | AR1, TA1 |  | TL | 2013-02-10 23:43 | 2013-02-10 23:43 | DTF from AR1 - 141kM DTF from TA1 - 10.25km | 20/02/2013 11:36:00 AM ¦ Nil. ¦ The local patrol officer will carry out a patrol of all road crossings between structures 20 and 35 and report his findings to the Northern Region Mains Support team. Any additional actions required will be determined base |  | Protection flagging indicated a blue phase fault to earth. The Indji system indicated lightning in the vicinity of structure 20 around the time of the trip. The local patrol officer will carry out a patrol of all road crossings between structures 20 and 3 | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2228 | 127541 | HV Equipment | Lightning or Storm | TRUE | CB SF6 |  |  |  | 2013-F-0145 | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2013Q1 | GTH, MUR, GHI |  | TL | 2013-02-14 13:11 | 2013-02-14 14:21 | Thunderstorms around Guthega at the time of trip and 97G was open at the Guthega end. Suspect slow CB 97G2 at Murray resulting in concurrent No.1/No.2 transformer trip. | 15/05/2013 8:54:00 AM <Duplicate Record> 7/04/2013 6:30:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. | 7/04/2013 6:30:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. | Slow operation tripped TX 1 & 2 at Murray and 11kV supplies out of Murray. Load not lost due alternate automatic 11kV supply from reactor at power station. INDJI indicates that lightening strike occurred approximately 400m from structure 72 at 2:11:54pm. | Thunderstorm | Primary Equipment | [5 empty] | 0 | 0 | 2013
2229 | 127543 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0145/1 | 97G/1 Geehi Tee CB 97G2 | Q | 2013Q1 | MUR |  | CB | 2013-02-14 13:11 | 2013-02-14 14:21 |  |  | 7/04/2013 6:30:00 PM ¦ N/A ¦ This has been noted for the next scheduled aerial patrol. | Thunderstorms around Guthega at the time of trip and 97G was open at the Guthega end. Suspect slow CB 97G2 at Murray resulting in concurrent No.1/No.2 transformer trip. Timing checks will be done in late May/early June to CB 97G2 to determine cause of slo |  | External | [5 empty] | 0 | 0 | 2013
2233 | 127646 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | TX |  |  |  | 2013-F-0151 | No.2 Transformer 132/66/11 kV | Z | 2013Q1 | GNS |  | TX | 2013-02-17 12:11 | 2013-02-18 15:13 | Remote MITS interrogation indicates operation of No.1 protection only. To be confirmed when staff attend site anticipated approximately 1.5 hours. Protection details provided indicate TC Buchholz trip. No visible sign of damage to equipment. NCM advised. | 18/03/2013 1:49:00 PM ¦ Nil. ¦ The overpressure switch will be replaced with a new switch during an outage scheduled for 17/05/2013. The faulty contacts can then be inspected to determine the cause of failure. |  | Inspection revealed that the tapchanger overpressure switch's trip contacts were faulty. The overpressure switch has a spare set of contacts which tested ok. As the spare contacts of this switch were used, the switch could not be dismantled to determine t | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2013 | Faulty o/p switch
2250 | 127738 | HV Equipment | HV Equipment Failure | TRUE | TX | N/A | N/A |  | 2013-E-0004 | No.3 Transformer 330/132/11kV | E | 2013Q1 | HYM |  | TX | 2013-02-18 11:04 | 2013-02-18 17:52 | CB5422BDisconnector 5438 low SF6. Staff investigating advised alarm indication incorrect and No.2 Transformer 330kV SGD was the actual cause of the low gas alarm. SGD was topped up with SF6 gas. Further investigation required on site to confirm other al | 25/03/2013 10:52:00 AM ¦ Nil. ¦ Follow up with Substation Systems to ensure the Functional Specification has requirements for individual alarms at the HMI or SCADA level for critical low gas alarms, so that Operators can isolate the correct equipment. |  | Staff investigating advised alarm indication was incorrect and No.2 Transformer 330kV SGD was the actual cause of the low gas alarm. SGD was topped up with SF6 gas. Further investigation required on site to confirm that other alarm indications are correc | Fine | Oil/Gas Levels | [5 empty] | 0 | 0 | 2013
2251 | 127988 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0155 | 96R Glen Innes - Tenterfield 132kV TL | Z | 2013Q1 | GNS, TTF |  | TL | 2013-02-22 20:46 | 2013-02-22 20:46 | No staff called to Tenterfield to confirm if CB4422 reclosed as no CB trip alarm received on Scada or BU alarms, so therefore it was considered that 4422 reclosed successfully. | 7/03/2013 2:47:00 PM ¦ Nil. ¦ A close inspection of this section of the line will be carried out during the next routine patrol. The earthing of the structures in this section of the line will also be investigated at the same time. |  | 96R line from Glen Innes to Tenterfield tripped and auto-reclosed at both ends of the line. Protection flagging indicated a three phase fault to earth, with the distance to fault calculated to be 37-38km from Tenterfield substation. This corresponds to an | Rain and Very Windy | External | [5 empty] | 0 | 0 | 2013
2252 | 127997 | Windblown/object | Unknown | TRUE | TL |  |  |  | 2013-F-0157 | 966 Armidale - Koolkhan 132kV TL | Z | 2013Q1 | AR1, KLK |  | TL | 2013-02-23 10:14 | 2013-02-26 12:40 | DTF from AR1 :- 115.3km DTF from KLK :- 40.41km | 7/03/2013 3:41:00 PM ¦ Nil. ¦ Nil. |  | Protection indicated a white and blue phase fault to earth, with the distance to fault calculated as being 115.3km from AR1. Weather rainy, with very high winds. Ground patrols unable to find the fault. Aerial patrol of the Clouds Creek area revealed a la | Rain and Very Windy | External | [5 empty] | 0 | 0 | 2013
2253 | 128017 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0162 | 8 Marulan - Dapto 330kV TL | Z | 2013Q1 | DPT, MRN |  | TL | 2013-02-24 20:23 | 2013-02-24 20:23 |  | 27/03/2013 2:15:00 PM ¦ Nil. ¦ A full climbing inspection will be conducted from Structures 39 – 46 in the near future. This inspection could not have been done around the time of incident due to wet weather. |  | An inspection of the line was carried out and a broken insulator disc was discovered on Structure 40. A full climbing inspection will be conducted from Structures 39 – 46 in the near future. This inspection could not have been done around the time of inci | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2254 | 128027 | Animal/Bird | Unknown | TRUE | Cap |  |  |  | 2013-F-0163 | No.5 Capacitor | Z | 2013Q1 | SYW |  | CAP | 2013-02-25 07:49 | 2013-02-28 15:08 |  | 27/03/2013 2:25:00 PM ¦ Nil. ¦ Nil. |  | Inspection of the capacitor bank revealed a dead bird. After the bird was removed the capacitor passed testing and was returned to service. | Mild | External | [5 empty] | 0 | 0 | 2013
2255 | 128250 | Condition Monitor | Sec Eqt Malfunction | TRUE | TX |  |  |  | 2013-F-0169 | No.1 Transformer 330/132/11kV | Z | 2013Q1 | WDL |  | TX | 2013-02-28 06:44 | 2013-02-28 11:09 | received No.1 Transformer condition monitor L1 Urgent alarm via SCADA at Williamsdale 330kV Substation. No.1 Transformer take out of service as per instruction. An internal relay in the Hydran monitor unit (relay removed from alarm cct in other substati | 4/03/2013 11:25:00 AM ¦ Investigate internal alarm in Hyran monitor unit to be done in March 2013 . Investigate 415 volt auxiliary supply changeover circuit to be done by Projects/Substation staff. |  | Received No.1 Transformer condition monitor L1 Urgent alarm via SCADA. Transformer taken out of service as per instruction. No.1 Transformer condition monitor L1 Urgent alarm was initiated by an internal alarm within the Hydran monitor unit. On initial in | Rain | Secondary Equipment | [5 empty] | 0 | 0 | 2013 | Condition monitoring fault, not protection
2256 | 128278 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0170 | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Z | 2013Q1 | AR1, COF |  | TL | 2013-02-28 18:22 | 2013-02-28 18:22 | Added COFs protection details DTF = 1.45 km Added AR1 protection details DTF = 149.1 km | 7/03/2013 1:38:00 PM ¦ Nil. ¦ Nil. |  | Tripped and auto-reclosed at both ends of the line. Protection flagging indicated a red phase fault to earth, with a distance to fault of 1.45km from Coffs Harbour substation. There were storms in the area around the time of the trip, however the Indji sy | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2261 | 128303 | HV Equipment | Sec Eqt Malfunction | TRUE | CB SF6 |  |  |  | 2013-E-0007 | No.4 Transformer 132kV A CB 4442A | Q | 2013Q1 | SE1 |  | CB | 2013-02-28 23:26 | 2013-03-01 17:31 | Low SF6 gas alarm received. CB opened via Scada. | 25/03/2013 11:18:00 AM ¦ Nil. ¦ Nil. |  | Low SF6 gas alarm received. CB opened via Scada. The alarm was found to be initiated by water ingress into a densimeter which was causing the alarm contacts to short and send through false alarms. | Rain | External | [5 empty] | 0 | 0 | 2013
2262 | 128338 | Animal/Bird | Animal/Bird | TRUE | Sec |  |  |  | 2013-F-0174 | Misc LV (Wellington Substation) | Q | 2013Q1 | WL1 |  | LV | 2013-03-01 07:03 | 2013-03-01 10:54 | Dead mouse across Y - B phase supervision relay. |  |  | Dead mouse across Y - B phase supervision relay. | Rain and Very Windy | External | [5 empty] | 0 | 0 | 2013
2257 | 128422 | HV Equipment | HV Equipment Failure | TRUE | Disc |  |  |  | 2013-E-0008 | 132kV A Bus Section No.1 | Q | 2013Q1 | SYW |  | BB | 2013-03-03 12:06 | 2013-03-03 13:12 | When the 132kV A Bus No.1 Section was returned to service and placed on load (HVPRI 42996), arcing was noticed on all 3 phases of one of the 132kV disconnectors (later identifed as No.1 Transformer 132kV A Bus Disconnector 4415). The 132kV A Bus No.1 Sect | 27/03/2013 2:49:00 PM ¦ Nil. ¦ Repair of Disconnector when spares become available. |  | When Bus No.1 Section was returned to service and placed on load (HVPRI 42996), arcing was noticed on all 3 phases of one of the 132kV disconnectors (later identifed as No.1 Transformer 132kV A Bus Disconnector 4415). The Bus Section was de-energised @ 12 | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2013
2263 | 128841 | HV Equipment | HV Equipment Failure | TRUE | TX |  |  |  | 2013-E-0009 | No.1 Transformer 330/132/11kV | E | 2013Q1 | SYS |  | TX | 2013-03-07 12:13 | 2013-03-20 15:34 | Saiyaz Dean Reported bushing oil sample has returned high gas levels. The No.1 transformer is required out of service pending further investigation. | 25/03/2013 9:29:00 AM ¦ Nil ¦ Replacement of the Corona shields on all new 132kV bushings. |  | Bushings replaced with Micafil RIP bushings, however Siemens has advised that these particular bushings may not be suitable for their transformers with regard to the Corona shield on the bushings. New Corona shields have been ordered for replacement. This |  | Primary Equipment | [5 empty] | 0 | 0 | 2013
2267 | 128873 | Bushfire | Unknown | TRUE | TL |  |  |  | 2013-F-0180 | 994 Wagga 330 - Yanco 132kV TL | Z | 2013Q1 | WG1, YA2 |  | TL | 2013-03-08 05:55 | 2013-03-08 05:55 | Protection details to be added | 7/04/2013 6:14:00 PM ¦ N/A ¦ No further action required. |  | The 994 TL was patrolled approximately 1 week after the fault and evidence of a stubble fire was noticed at structure 168. | Fine | External | [5 empty] | 0 | 0 | 2013
2264 | 129020 | Unknown | Unknown | TRUE | Sec | TBA | TBA |  | 2013-F-0181 | No.3 Capacitor | Z | 2013Q1 | DNT |  | CAP | 2013-03-08 18:19 | 2013-03-09 07:48 | No.3 Capacitor tripped when No.2 Capacitor was taken out of service. |  |  | No.3 Capacitor tripped when No.2 Capacitor was taken out of service. Trip was on Neutral Unbalance one protection only. No.3 Cap tripped due to real neutral current flowing. It is suspected that the CB on No.2 Cap had a restrike as classic phase to phase | Unknown | Secondary Equipment | [5 empty] | 0 | 0 | 2013
2265 | 129061 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0183 | 96R Glen Innes - Tenterfield 132kV TL | Z | 2013Q1 | GNS, TTF |  | TL | 2013-03-10 04:11 | 2013-03-10 04:11 |  | 19/04/2013 9:48:00 AM ¦ Nil. ¦ A close inspection of the line will be carried out during the next aerial inspection. |  | The 132kV 96R TL from Glen Innes to Tenterfield tripped and auto-reclosed at both ends of the line. Protection flagging from Glen Innes indicated a zone 1 blue phase fault to earth. The distance to fault was calculated at 61.22km from Glen Innes substatio | Unknown | Unexplained | [5 empty] | 0 | 0 | 2013
2268 | 129161 | LV/MECH Fail | Unknown | TRUE | Other |  |  |  | 2013-E-0010 | No.3 Tie | Q | 2013Q1 | BFD |  | BB | 2013-03-12 09:07 | 2013-03-13 09:15 | Received advice from SSMF there is a loud noise and vibration emanating from No.3 132kV Bus Tie in the cable basement of Beaconsfield south GIS building Received request from T/L Maint that No.3 132kV Bus Tie be taken out of service. Projects Alfred Gun | 27/03/2013 3:01:00 PM ¦ Nil. ¦ Report being prepared by ABB. |  | Received advice from SSMF of a loud noise and vibration emanating from No.3 132kV Bus Tie in the cable basement of Beaconsfield south GIS building. No.3 132kV Bus Tie be was taken out of service. No issues found by ABB after checking the Bus Tie. Later i | Fine | Unexplained | [5 empty] | 0 | 0 | 2013
2266 | 129454 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0190 | 945 Wellington - Molong tee Well'n Town 132kV TL | Z | 2013Q1 | MOL, WL1 |  | TL | 2013-03-14 17:37 | 2013-03-14 17:37 | Protection details required | 27/03/2013 3:09:00 PM ¦ Nil. ¦ Nil. |  | The Indji System indicated lightning strikes near structure 113. Line patrolled between structures 112 and 118 and no cause for trip could be found. | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2269 | 17 | RTU/MITS/PLC |  | TRUE | Cont | TBA | TBA |  | IR10362 | No.4 Capacitor | E | 2013Q1 | SE1 |  | CAP | 2013-03-18 21:43 |  |  |  |  | No fault found with RTU. Investigation showed this fault was external to the RTU. Attempts to clear the alarm by powering down then powering up the bay controller failed. In consultation with NCM, log entry switching was carried out and CB 5742 was opened | Fine | Primary Equipment | Central | 330 | Emergency |  |  | 0 | 0 | 2013
2271 | 130288 | Unknown | Unknown | TRUE |  |  |  |  | 2013-F-0205 | 96M Narrabri - Moree 132kV TL | Z | 2013Q1 | MRE, NB2 |  | TL | 2013-03-26 20:28 | 2013-03-26 20:28 | No storm activity could be seen to Indji |  |  | No storm activity could be seen to Indji | Unknown | [6 empty] | 0 | 0 | 2013
2272 | 131184 | Switching error | Operating Error | TRUE | Prev |  |  |  | 2013-F-0209 | No.3 Transformer 330/132/11kV | Z | 2013Q2 | MTP | HV Equipment (Mains) | TX | 2013-04-05 14:15 | 2013-04-05 16:15 | No 3 Transformer 330kV bay (CBs 5432 & 5032) tripped during restoration see PRI 43655. | 8/05/2013 8:19:00 AM ¦ Nil. ¦ Nil. |  | CB 5432 & 5032 tripped during switching as a result of the protection not being reset before switching of No.3 Tx 330/132kV. the Transformer required draining and refilling and as a result a tap changer overpressure trip signal was sent to the Transforme | Fine | External | [5 empty] | 0 | 1 | 2013 | Incorect isolation of protection from overpressure trip signal, whilst refilling the transformer
2274 | 131216 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0211 | 2 Upper Tumut - Yass 330kV TL | Z | 2013Q2 | UT1, YSN |  | TL | 2013-04-07 15:39 | 2013-04-07 15:39 | @ UTSS from OPTIMHO pre voltage levels Va 197kV, Vb 197.1kV, Vc 196.3kV - Fault Va 111.7kV, Vb 116.0 kV, Vc 182.5kV @ Yass Va 89kV, Vb 92kV, Vc 195kV SOrms in the vicinity of Yass at time of TAR. | 19/04/2013 1:53:00 PM ¦ Nil. ¦ A close inspection of the line will be carried out during the next aerial inspection. |  | TL tripped and auto-reclosed at both ends of the line. Protection flagging from Upper Tumut indicated zone 1-2, phase to phase & phase to earth faults. Protection flagging from Yass also indicated a zone 1 fault. The distance to fault was calculated at 1 | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2275 | 131242 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2013-E-0012 | 87 Coffs Harbour 330kV CB 872A | Q | 2013Q2 | AR1 |  | CB | 2013-04-08 13:07 | 2013-04-11 15:15 | During Protection trip checks for 330kV B/S 3 CB 872A caught on fire. | 17/04/2013 10:53:00 AM ¦ D2013/04984 ¦ Nil. ¦ A detailed report is being prepared by Substations/Northern Region, with any future actions to be determined based on the recommendations of that report. |  | The 330kV 872A circuit breaker's central cubicle at Armidale Substation caught fire. The circuit breaker was open at the time of the fire, as Tech Services staff were on site carrying out trip checks on 330kV Bus Section 3, which includes CB872A. The circ | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2013
2276 | 131452 | Staff Error | Sec Eqt Staff Error | TRUE | Prev |  |  | Generation lost 150MW | 2013-F-0213 | M5 Murray - Murray 1 330kV TL | Z | 2013Q2 | MUR | Preventable | TL | 2013-04-11 10:52 | 2013-04-11 11:12 | M5 T/L Trip was caused by TG protection tech contacting a DC supply while working on M9 protection. SHL SMCC operator advised they lost 2 units and a total generation of 150MW |  |  | Protection staff error. M5 T/L Trip was caused by TG protection tech contacting a DC supply while working on M9 protection. SHL SMCC operator advised they lost 2 units and a total generation of 150MW. | Fine | External |  |  |  |  | Generation lost 150MW | 1 | 1 | 2013 | An excerpt from Opslog: "A protection technician working on other protection panel work inadvertently contacted live panel links receiving a small electric shock and causing the trip of M5 T/L"
2277 | 131534 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0214 | 94X Wallerawang 132 (New) - Panorama 132kV TL | Z | 2013Q2 | PMA, WWS |  | TL | 2013-04-13 07:00 | 2013-04-13 07:00 | no storms. cause unknown. | 8/05/2013 2:21:00 PM ¦ Nil. ¦ Nil. |  | No storms in the area at the time. A patrol of 94X was undertaken from Wallerawang to structure 52 (500kV undercrossing), no defects on the line were detected. There are no trees close to this section of line. | Fine | Unexplained | [5 empty] | 0 | 0 | 2013
2278 | 131613 | Communications | Unknown | TRUE | Com |  |  |  | 2013-F-0216 | 810 Cooma - Brown Mountain tee Bombala 66kV Line | Q | 2013Q2 | CMA |  | TL | 2013-04-15 12:42 | 2013-04-15 12:42 | No alarms received via TransGrid SCADA. Problem found with alarm cabling on 810 Feeder at Cooma after incident. TAR time assumed to be when Essential Energy received numerous alarms in their system which gave indication of a TAR operation on 810 Feeder. |  |  | Communication of alarms did not occur due to fault on alarm cabling. Essential Energy received numerous alarms in their system which gave indication of a TAR operation on 810 Feeder. | Rain | Secondary Equipment | [5 empty] | 0 | 0 | 2013
2279 | 131845 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2013-E-0013 | O51 Lower Tumut 330kV CB 0512 | Q | 2013Q2 | WG1 |  | CB | 2013-04-20 06:06 | 2013-04-20 09:37 | Low SF6 gas top up. | 22/08/2013 3:52:00 PM |  | CB 0512 low SF6 - R Phase, requires topping up | Fine | [6 empty] | 0 | 0 | 2013
2284 | 132068 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  |  | 78 Ingleburn - Sydney South 330kV TL | E | 2013Q2 | ING, SYS |  | TL | 2013-04-27 08:48 | 2013-04-27 09:34 |  |  |  | 330kV B Bus No.2 Section was de-energised to allow isolation of faulty 78 Ingleburn CB782. | [7 empty] | 0 | 0 | 2013
2283 | 132027 | HV Equipment | HV Equipment Failure | TRUE | Disc |  |  |  | 2013-F-0224/1 | 78 Ingleburn - Sydney South 330kV TL | E | 2013Q2 | ING, SYS |  | TL | 2013-04-28 17:47 | 2013-04-29 00:02 |  |  |  | Hot joint noticed on 78 bus disconnector. | [7 empty] | 0 | 0 | 2013
2288 | 132226 | Staff Error | Backup Operation | TRUE | Prev |  |  |  | 2013-F-0225 | No.1 Transformer 132/33/11kV | Z | 2013Q2 | YA2 | Preventable | TX | 2013-05-02 10:11 | 2013-05-02 11:21 | Notes from the fitter on site: Oil level checked before taking oil sample from the Aux Tx Appeared 1/2 full but optical illusion Aux Tx topped up with 10 Liters of oil. | 15/05/2013 8:50:00 AM |  | Auxiliary transformer and No.1 transformer tripped while oil samples were taken from the auxiliary transformer. Oil level checked before taking oil sample from the Aux Tx. Appeared 1/2 full but optical illusion. Aux Tx topped up with 10 Liters of oil. Pre | Fine | External | [5 empty] | 0 | 0 | 2013
2289 | 138127 | Staff Error | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2013-E-0015 | No.1 Tie Transformer 500/330/33kV | E | 2013Q2 | BAY | Preventable | TX | 2013-05-08 12:30 | 2013-05-08 12:43 | A Spring Discharge alarm occured on CB 6412 after Transformer returned to service from a planned maintenance outage. Fitter on site requested Transformer to be deenergised for reparis to be carried out. | 28/05/2013 3:26:00 PM ¦ Nil. ¦ Nil. |  | A Spring Discharge alarm occured on the 500kV No.1 Tie Transformer CB 6412 after the tie transformer was returned to service from a planned maintenance outage. The fitter on site requested the transformer to be de-energised to investigate the initiation o | Fine | External | [5 empty] | 0 | 0 | 2013
2290 | 138161 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0226 | 9U3 Gunnedah - Narrabri 132kV TL | Z | 2013Q2 | GN2, NB2 |  | TL | 2013-05-09 03:42 | 2013-05-09 03:42 | light rain in the area at the time. |  |  | light rain in the area at the time. | Rain | [6 empty] | 0 | 0 | 2013
2291 | 138425 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2013-E-0016 | No.5 Reactor | E | 2013Q2 | KCR | HV Equipment (Mains) | RX | 2013-05-12 21:47 | 2013-05-17 14:49 | Tripped on closing. Appears to be pole discrepency. See IR 10557. Further investigations & repairs required. | 14/06/2013 3:29:00 PM ¦ Nil. ¦ Nil. |  | The No.5 Reactor CB5952 tripped on closing. Auxiliary contact block found to be faulty. The cores were rewired into spare contact block and the CB was made available for service. | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2013
2295 | 138926 | Staff Error | LV/MECH/PROT Equipment Fail | TRUE | Prev |  |  |  | 2013-E-0017 | 96H Coffs Harbour - Koolkhan 132kV TL | E | 2013Q2 | COF, KLK |  | TL | 2013-05-18 10:53 | 2013-05-18 11:22 | CVT Imbalance alarm. Advises No.1 Prot Sec volts of 83.2 V (R), 79.0 V (W) & 75.3 V (B). Similar readings from No.2 Prot.TL de-energised. Neutral link found loose in CVT secondary cabinet, now tightened. TL RTS. Alarms cleared, sec volts OK. | 12/06/2013 8:52:00 AM ¦ Nil. ¦ Nil. |  | A CVT unbalance alarm was received and 96H was taken out of service. At the CVT marshalling cubicle the fitter found a loose screw on one end of the neutral link cartridge in the CVT marshalling cubicle. The screw was tightened and the line was returned |  | External | [5 empty] | 0 | 0 | 2013
2296 | 138974 | Staff Error | Sec Eqt Staff Error | TRUE | Prev |  |  |  | 2013-F-0229 | C1 Munmorah - Colongra 330kV TL | Q | 2013Q2 | MN1 |  | TL | 2013-05-20 12:22 | 2013-05-20 12:46 | Temporary protection operation occurred during balance between Calongra Units via C1 and CB 5052 C.T.s Protection details Red Phase overcurrent element operated. Faulty test lead identified as cause of protection operation. Fault rectified and equipment r |  |  | Temporary protection operation occurred during balance between Calongra Units via C1 and CB 5052 CTs. Protection details Red Phase overcurrent element operated. Faulty test lead identified as cause of protection operation. Fault rectified and equipment re | Fine | External | [5 empty] | 1 | 0 | 2013 | Faulty test lead in temporary protection implementation
2297 | 139384 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2013-E-0018 | 330kV B Bus 1-2 Section CB 5112 | Q | 2013Q2 | SE1 | HV Equipment (Mains) | CB | 2013-05-26 15:24 | 2013-05-31 13:59 | When returning the 330kV B Bus No.1 Section to Service on HVPRI 44738, unable to close C.B. 5112 via SCADA. Requested Steve McLeod to close locally. Unable to close locally at site. | 14/06/2013 3:47:00 PM ¦ Nil. ¦ Further Investigation into reason for spring tension. |  | When returning the 330kV B Bus No.1 Section to Service, C.B. 5112 was unable to be closed via SCADA or locally. Investigation revealed that the CB drive mechanism on the Blue Phase had failed. Investigations revealed that the spring had been overtensioned | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2013
2298 | 139518 | Bushfire | Bushfire | TRUE | TL |  |  |  | 2013-F-0234 | 96F Stroud - Tomago330 Tee Brandy Hill 132kV TL | Z | 2013Q2 | TOM | HV Equipment (Mains) | TL | 2013-05-28 13:17 | 2013-05-28 13:17 | -fault duration 51.65mS -fault location 42.37km -fault current 2.494kA | 30/05/2013 9:31:00 AM ¦ Nil. ¦ No further action required. |  | A patrol found evidence of a recent grass fire between structures 250 and 251, directly below 96F TL. This fire is believed to be the cause of the trip. No other issues were found. Protection flagging indicated a zone 1 blue phase fault to earth. The dist | Unknown | External | [5 empty] | 0 | 0 | 2013
2299 | 139722 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2013-F-0239 | No.4 Transformer 132kV A CB 4442A | Q | 2013Q2 | SE1 |  | CB | 2013-06-02 13:57 | 2013-06-05 17:22 | CB 4442A taken out of service to investigate and top up SF6 |  |  | CB 4442A taken out of service to investigate and top up SF6 | Rain | Oil/Gas Levels | [5 empty] | 0 | 0 | 2013
2301 | 139800 | LV/MECH Fail | HV Equipment Failure | TRUE | Other |  |  | Lost load 6MW | 2013-F-0241 | 66kV Bus 1-2 Section CB 3102 | S | 2013Q2 | MRU |  | CB | 2013-06-04 08:47 | 2013-06-05 13:59 | Murrumburrah 66kV Bus No.1 Section and No.1 Transformer tripped. Dispatched staff to investigate. Initially found nothing wrong and no signs of damage on the switchgear. Reset the protections and energised the 66kV No.1 section via No.1 Transformer. Resto | 26/07/2013 10:36:00 AM |  | Murrumburrah 66kV Bus No.1 Section and No.1 Transformer tripped. The trip was caused by faulty summation links which burned out, on CB3102 CT Primary BBP summation circuit. Initially staff found nothing wrong and no signs of damage on the switchgear. The | Fine | Secondary Equipment | [5 empty] | 1 | 0 | 2013
2310 | 140754 | HV Equipment | HV Equipment Failure | TRUE | Disc |  |  |  | 2013-E-0020 | No.3 Transformer 330kV CB 5432A | Q | 2013Q2 | TOM |  | CB | 2013-06-06 19:21 | 2013-07-31 15:01 | Disc 5437 unable to be closed on RTS of 330kV A Bus. Disc 5437 left locked open. Disc 5437 repaired & returned to service 31/7/13. | 24/06/2013 10:41:00 AM ¦ Nil. ¦ Consideration will be given to the long term serviceability of this isolator. Any future actions will be decided accordingly in consultation with Asset Performance. |  | Disconector 5437 was unable to be closed on the return to service switching of 330kV A Bus. The disconector was left locked open. Staff inspecting the isolator and found that its reduction gearbox assembly had seized due to corrosion. The seals and end ca | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2013
2306 | 140516 | External | Human Interference | TRUE | TL |  |  | Lost Load 6MW | 2013-F-0245/2 | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | C | 2013Q2 | AR1, COF |  | TL | 2013-06-09 13:48 | 2013-06-10 15:54 | DTF from Armidale 120.5km Greg from Fire & rescue reported that they have cut a dead tree down. Doug Esse SO reported that due to a failed CB at Dorrigo that thay were unable to restore load until staff arrived at 1521. | 24/06/2013 9:23:00 AM ¦ Nil. ¦ Nil. |  | Emergency services reported that they have cut a dead tree down. The patrolman called out to respond to the outage found that the tree had fallen onto the white phase conductor around 15m west of structure 463. The steel crossarm on structure 463 was foun | Fine | [6 empty] | 0 | 0 | 2013
2307 | 140722 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0251 | 9U4 Glen Innes - Inverell 132kV TL | Z | 2013Q2 | GNS, INV |  | TL | 2013-06-12 17:13 | 2013-06-12 17:13 |  |  |  |  | Thunderstorm | [6 empty] | 0 | 0 | 2013
2308 | 140724 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0252 | 9U4 Glen Innes - Inverell 132kV TL | Z | 2013Q2 | GNS, INV |  | TL | 2013-06-12 17:15 | 2013-06-12 17:15 |  |  |  |  | Thunderstorm | [6 empty] | 0 | 0 | 2013
2309 | 140725 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2013-E-0019 | 5A2 Kemps Creek 500kV CB 5A22 | Q | 2013Q2 | ER0 |  | CB | 2013-06-13 02:29 | 2013-06-13 09:26 | H.V. C.B. Abnormal alarm received @ 0223 hours. C.B. opened via SCADA at 0229 hours. | 14/06/2013 11:49:00 AM ¦ Nil. ¦ An SF6 camera survey of the breaker will be carried out on Friday 14/06/2013 to locate the source of the leak. Repairs will be arranged based on the results of the camera survey. |  | The 500kV circuit breaker 5A22 was manually removed from service following the initiation of the circuit breaker's CB abnormal alarm. It was found that the alarm was caused by low SF6 pressure on the blue phase line side pole of CB 5A22. The pole was topp | Unknown | Primary Equipment | [5 empty] | 0 | 0 | 2013
2311 | 140915 | Staff Error | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2013-F-0253 | U3 Tumut 1 330kV CB U32 | Q | 2013Q2 | UT1 |  | CB | 2013-06-14 19:16 | 2013-06-14 23:53 | CB in an indeterminate state after attempt to close (synchronise). Confirmed visually that red phase is open whilst white & blue phases remain closed. CB isolated & exercised OK. CB deemed servicable. | 26/07/2013 10:35:00 AM ¦ Work Order 304069 created to replace pole discrepancy and spring discharged alarm relays. |  | The CB was in an indeterminate state after an attempt to close (synchronise). It was confirmed visually that the red phase is open whilst the white & blue phases remain closed. The CB was isolated & exercised OK. Faulty pole discrepancy and spring dischar | Very Cold | External | [5 empty] | 0 | 0 | 2013
2313 | 141238 | Contractor Error |  | TRUE | Prev |  |  | Lost load 8MW. Does not qualify for 2013 STPIS inclusion. New 2014 STPIS would include these outages. System minutes 0.183 | >24hr Notice | 94C Wallerawang 132 (New) - Oberon 132kV Line |  | 2013Q2 | WWS |  | TL | 2013-06-18 16:09 | 2013-06-18 21:24 |  |  |  | At 16:10 hrs 18 June 2013, 132kV transmission line 94C from Wallerawang to Oberon substation was taken out of service due to a faulty voltage transformer in the Wallerawang line bay owned by TransGrid. 1h 9m notice was given to Essential Energy that the |  | Maintenance | [5 empty] | 0 | 0 | 2013
2314 | 141302 | HV Equipment | HV Equipment Failure | TRUE | CT |  |  |  | 2013-E-0021 | 86 Tamworth 330 - Armidale 330kV TL | E | 2013Q2 | AR1, TA1 |  | TL | 2013-06-19 16:27 | 2013-06-20 18:22 | 86 TL removed from service due to suspect CT at Tamworth 330 reported by Maintenance Engineer. | 24/06/2013 10:29:00 AM ¦ Nil. ¦ Nil. |  | De-energised following report of dangerous levels of gas in oil samples on red phase CT at Tamworth 330kV substation. The CT was replaced on 20/06/2013. Following the replacement of the CT, the line was returned to service. NCM advised outage impacting o | Unknown | Primary Equipment | [5 empty] | 0 | 0 | 2013
2321 | 141728 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2013-E-0023 | No.4 Transformer 132kV A CB 4442A | Q | 2013Q2 | SE1 |  | CB | 2013-06-23 12:38 | 2013-06-23 13:51 | Low SF6 alarm received on Scada. C.B. taken out of service to allow staff to top up SF6. | 5/12/2013 1:42:00 PM ¦ Nil ¦ Nil |  | Low SF6 alarm received on Scada. C.B. taken out of service to allow staff to top up SF6. | Rain | Oil/Gas Levels | [5 empty] | 0 | 0 | 2013
2322 | 141553 | HV Equipment | Non TransGrid Reason | TRUE | MVT |  |  | Lost load 6MW | 2013-F-0258 | 723 Moree - Wenna tee Wathagar 66kV Line | S | 2013Q2 | MRE |  | TL | 2013-06-25 05:18 | 2013-06-25 09:39 |  |  |  | Feeder 723 tripped and locked out due to a VT fault. 6MW of load was lost. Supply was restored to the affected areas at 0717 hrs. | Rain | Primary Equipment | [5 empty] | 0 | 0 | 2013
2324 | 141702 | Relay | HV Equipment Failure | TRUE | Cont |  |  |  | 2013-F-0259 | 66kV Bus Section 1 | S | 2013Q2 | MRE |  | BB | 2013-06-25 09:43 | 2013-06-25 10:45 | 723 Wenna Tee Wathagar VT explosive failure. | 23/07/2013 1:54:00 PM ¦ Nil. ¦ A report on the incident is being prepared by Substations/Northern Region. The report will investigate possible causes of the failure. Any additional actions will be determined based on the findings of the report, in consul |  | At 1044 hrs a close was requested by SCADA and CB 8812 tripped. Line 881 - Moree to Garah tee Ashley remained out of service until 1132 hrs. | Rain | [6 empty] | 0 | 0 | 2013 | Explosive VT failure, not protection
2317 | 141702 | HV Equipment | HV Equipment Failure | TRUE | MVT |  |  | Lost load 10MW. Sys. min. 0.0784 | 2013-F-0259 | 66kV Bus Section 1 | S | 2013Q2 | MRE |  | BB | 2013-06-25 09:43 | 2013-06-25 10:45 | 723 Wenna Tee Wathagar VT explosive failure. | 23/07/2013 1:54:00 PM ¦ Nil. ¦ A report on the incident is being prepared by Substations/Northern Region. The report will investigate possible causes of the failure. Any additional actions will be determined based on the findings of the report, in consul |  | The white phase VT on the 66kV 723 Feeder Bay failed causing the busbar to trip. Further inspection of the bay revealed that a palm on the white phase CT in the 723 Feeder Bay had been damaged during the VT failure. The damage resulted in an oil leak from | Rain | Primary Equipment | [5 empty] | 0 | 0 | 2013
2323 | 142232 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0262 | 991 Wagga North - Murrumburrah 132kV TL | Z | 2013Q3 | MRU, WGN |  | TL | 2013-07-01 11:03 | 2013-07-01 11:03 | No storms in vicinity at time of trip. |  |  | Trip and reclose. No storms in vicinity at the time of the trip. Distance to fault recorded at 3.2km. Line patrol did not identify the cause of the trip. | Mild | Unexplained | [5 empty] | 0 | 0 | 2013
2325 | 142788 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2013-E-0024 | 5A2 Kemps Creek 500kV CB 5A22 | Q | 2013Q3 | ER0 |  | CB | 2013-07-07 04:42 | 2013-07-07 06:36 | CB 5A22 low SF6 topped up and returned to service. | 12/07/2013 4:10:00 PM ¦ Nil. ¦ Replacement of the resistor is planned for Wednesday 17/07/2013. |  | A low SF6 alarm was received. The CB was taken out of service, topped up, then returned to service. The location of the leak was on the resistor associated with the blue phase line side pole. The resistor was replaced. | Fine | Oil/Gas Levels | [5 empty] | 0 | 0 | 2013
2326 | 142987 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0270 | 966 Armidale - Koolkhan 132kV TL | Z | 2013Q3 | AR1, KLK |  | TL | 2013-07-10 02:10 | 2013-07-10 02:10 |  |  |  | Trip and reclose operation. The cause is unknown. | Unknown | Unexplained | [5 empty] | 0 | 0 | 2013
2328 | 143079 | HV Equipment | LV/MECH/PROT Equipment Fail | TRUE | CB SF6 |  |  |  | 2013-E-0025 | No.2 Transformer 132/33/11kV | E | 2013Q3 | MNY |  | TX | 2013-07-10 15:07 | 2013-07-10 18:49 |  |  |  | Low SF6 alarm received (0.2 bar above lockout limit) on transformer no.2 CB-4422. A faulty O-Ring was found on the filling point of the CB. The O-Ring was replaced and the CB was returned to service. |  | Oil/Gas Levels | [5 empty] | 0 | 0 | 2013
2329 | 143173 | Contractor Error | LV/MECH/PROT Equipment Fail | TRUE | Prev |  |  |  | 2013-F-0271 | 97A Tamworth 330 - Tamworth 132 132kV TL | Z | 2013Q3 | TA2, TA1 |  | TL | 2013-07-10 17:34 | 2013-07-10 18:46 | I/T cable damaged by contractor staff in field.TL offloaded at TA2 only. Temp prots now installed. | 19/07/2013 3:20:00 PM ¦ Nil. ¦ Following the repair of the cables, commissioning checks will be carried out, the temporary protections will be decommissioned and the pilot cable protections will be reinstated for both TLs. |  | Two pilot cables that run between the two substations were both severed by an external party that was installing cable in a paddock between the two sites. The pilot cables are both used for the No.1 Protections for the 132kV 97A and 97B TLs. After isolati | Fine | External | [5 empty] | 1 | 1 | 2013 | Pliot cables excavated and damaged (incorrect isolation), causing incorrect protection operation
2330 | 143283 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0272 | 96M Narrabri - Moree 132kV TL | Z | 2013Q3 | MRE, NB2 |  | TL | 2013-07-13 02:47 | 2013-07-13 02:47 |  |  |  | Trip and reclose operation. The cause is unknown. | Unknown | Unexplained | [5 empty] | 0 | 0 | 2013
2331 | 143301 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2013-E-0026 | No.3 Capacitor | E | 2013Q3 | WL1 | HV Equipment (Mains) | CAP | 2013-07-13 13:29 | 2013-07-13 18:27 | CB 4732 SF6 Low alarm received from site and CB was taken out of service. | 5/12/2013 4:06:00 PM ¦ Nil ¦ Address SF6 leak during next planned outage. |  | A low SF6 alarm was received. The CB was taken out of service. The gas pressure was topped up the same day at 13:30 hrs. The leak could not be detected with a sniffer. The densimeter needle was noted as being "sticky". A digital gauge used to take final | Fine | Oil/Gas Levels | [5 empty] | 0 | 0 | 2013
2333 | 143310 | Protection | Unknown | TRUE | TL |  |  |  | 2013-F-0276 | 94 Newcastle - Tomago 330 330kV TL | Z | 2013Q3 | NEW, TOM | Protection | TL | 2013-07-14 15:15 | 2013-07-14 15:15 | No CB operations at Newcastle end. No voltage dips or alarm at the time. No fault recorder operations at the time. CB 942A opened for 2.520 secs CB 942B opened for 2.463 secs | 19/07/2013 3:16:00 PM ¦ Nil. ¦ The relay's firmware and setting file will be updated from V5.5 to V5.9 on Monday 22/07/2013. A review of the other protection schemes that use the D60 relay is being carried out by Protection Design. Any additional action |  | The line tripped and reclosed at the Tomago end only. Protection flagging indicated a zone 1, three phase fault to earth on the No.1 Protection at Tomago only. There were no fault recorder operations, voltage dips or alarms recorded at the time of the tri | Fine | Secondary Equipment | [5 empty] | 1 | 0 | 2013 | Protection relay firmware fault
2334 | 143554 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0277 | 4 Yass - Marulan 330kV TL | Z | 2013Q3 | MRN, YSN |  | TL | 2013-07-16 11:54 | 2013-07-16 11:54 |  |  |  | The TL tripped and auto reclosed. The weather was clear. The fault recorders operated at Bannaby and Yass. Patrol of the line has been arranged. No follow up to date. | Rain | Unexplained | [5 empty] | 0 | 0 | 2013
2335 | 144081 | Staff Error | HV Equipment Failure | TRUE | Sec |  |  |  | 2013-E-0027 | 967 Lismore 330 - Koolkhan 132kV TL | E | 2013Q3 | KLK, LSM | Preventable | TL | 2013-07-25 22:40 | 2013-07-26 08:48 |  | 15/08/2013 11:54:00 AM ¦ Nil. ¦ Nil. |  | A CVT phase imbalance alarm was received on the line at Lismore substation. The line was taken out of service for investigation. A visual inspection did not indicate any problems. A measurement of the secondary voltages from inside the Control Room indica | Unknown | External | [5 empty] | 0 | 0 | 2013
2336 | 144186 | LV/MECH Fail | LV/MECH/PROT Equipment Fail | TRUE | SVC |  |  |  | 2013-F-0285 | No.1 SVC | Z | 2013Q3 | SYW | Plant (Subs) | SVC | 2013-07-27 18:46 | 2013-07-27 18:54 | Tripped during planned 415V changeover due to 415V CB not latching. | 5/12/2013 4:40:00 PM ¦ Nil ¦ Nil |  | 415V supply change over did not occur within the loss of supply condition for the SVC cooling system. Sustained loss of cooling supply resulted in a trip of CB 5V12, offloading the No.1 SVC. Loss of 415V supply to the SVC was due to a 415V contactor fail | Fine | Secondary Equipment | [5 empty] | 0 | 0 | 2013
2337 | 144191 | Bushfire | Unknown | TRUE | TL |  |  |  | 2013-F-0286 | 96L Lismore 330 - Tenterfield tee Casino 132kV TL | Z | 2013Q3 | LSM, TTF |  | TL | 2013-07-28 07:30 | 2013-07-28 07:30 | TTF DTF info from No 2 Prot only - 118.2km LSM DTF info from fault recorder - 12km | 1/08/2013 3:23:00 PM ¦ Nil. ¦ No further action required. |  | Ground patrols found evidence of a recent grass fire between structures 402 and 405. The TL tripped and auto-reclosed due to a white phase to earth fault. The distance to the fault was 12km from Lismore SS (structure 405). No storms were recorded in the a | Fine | External | [5 empty] | 0 | 0 | 2013
2338 | 144848 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0292 | 96M Narrabri - Moree 132kV TL | Z | 2013Q3 | MRE, NB2 |  | TL | 2013-08-03 23:07 | 2013-08-03 23:07 | Moree protection details added. |  |  | Trip and reclose operation. Cause unknown | Unknown | Unexplained | [5 empty] | 0 | 0 | 2013
2339 | 144911 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0293 | 5A4 Bayswater - Wollar 500kV TL | Z | 2013Q3 | BAY, WOL |  | TL | 2013-08-05 07:08 | 2013-08-05 07:08 | Wollar protection details added. | 23/12/2013 3:43:00 PM ¦ Nil ¦ Nil |  | Trip and reclose operation. Fault recorders operated at numerous locations and indicate a blue phase to earth fault. The reason for the trip is being investigated. DTF - 93km from Bayswater. | Fine | [6 empty] | 0 | 0 | 2013
2340 | 145002 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0295 | 970 Yass - Burrinjuck 132kV TL | Z | 2013Q3 | BUK, YSN |  | TL | 2013-08-05 23:55 | 2013-08-05 23:55 |  |  |  | Trip and reclose operation, cause unknown. | Fine | Unexplained | [5 empty] | 0 | 0 | 2013
2342 | 145642 | Bushfire | Unknown | TRUE | TL |  |  |  | 2013-F-0307 | 96L Lismore 330 - Tenterfield tee Casino 132kV TL | Z | 2013Q3 | LSM, TTF |  | TL | 2013-08-14 11:16 | 2013-08-14 11:16 | Rural fire service confirmed no reports of active fires in area | 30/08/2013 8:07:00 AM ¦ Nil. ¦ No further action required. |  | Protection flagging indicated a blue phase fault to earth. A ground patrol found evidence of a sugar cane fire between structures 415 and 416. | Fine | External | [5 empty] | 0 | 0 | 2013
2343 | 145760 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2013-E-0028 | 330kV B Bus 1-2 Section CB 5112 | E | 2013Q3 | SE1 |  | CB | 2013-08-15 17:00 | 2013-08-15 19:09 | CB 5112 low on SF6 (R-Ph). Topped up |  |  | Outage to top up low SF6 in CB 5112. | Fine | Oil/Gas Levels | [5 empty] | 0 | 0 | 2013
2344 | 145950 | HV Equipment | Unknown | TRUE | TX |  |  |  | 2013-F-0310 | No.1 Transformer 330/132/11kV | Z | 2013Q3 | BFD |  | TX | 2013-08-20 04:25 | 2013-08-21 15:02 |  | Nil ¦ Nil |  | Tripped on main tank Buchholtz. | Fine | Oil/Gas Levels | [5 empty] | 0 | 0 | 2013
2345 | 146039 | HV Equipment | Unknown | TRUE | CVT |  |  |  | 2013-E-0029 | 89 Coffs Harbour - Lismore 330 330kV TL | E | 2013Q3 | COF, LSM |  | TL | 2013-08-21 07:56 | 2013-08-22 17:01 | 89 TL deenergised due to CVT Phase Imbalance Alarm. | 3/09/2013 11:44:00 AM ¦ Nil. ¦ An investigation will be carried out by Substations/Northern Region. Any additional actions will be determined based on the findings of the investigation, in consultation with Asset Performance. |  | The transmission line was manually removed from service following the initiation of the CVT unbalance alarm at Lismore Substation. The 89 Feeder Bay was left out of service pending replacement of the VT. The VT was replaced with a spare after which the 89 | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2013
2346 | 146081 | HV Equipment | HV Equipment Failure | TRUE | Rx |  |  |  | 2013-E-0030 | No.1 Reactor | E | 2013Q3 | LSM |  | RX | 2013-08-22 00:33 | 2013-08-22 16:21 | Buchholz alarm received. | 19/09/2013 11:19:00 AM |  | The reactor was manually removed from service following the initiation of a Buchholz alarm. The Buchholz alarm was initiated due to low oil in the reactor. This was a result of the No.1 Reactor being de-energised as the 330kV 89 TL from Lismore to Coffs H | Fine | Oil/Gas Levels | [5 empty] | 0 | 0 | 2013
2348 | 146237 | HV Equipment | HV Equipment Failure | TRUE | CB SF6 |  |  |  | 2013-E-0031 | No.6 Transformer 330/132/11kV | E | 2013Q3 | AR1 | HV Equipment (Mains) | TX | 2013-08-25 17:10 | 2013-08-25 18:48 | CB4462 Blue phase CT SF6 replenished |  |  | Outage to top up low SF6 in CB. | Fine | Oil/Gas Levels | [5 empty] | 0 | 0 | 2013
2349 | 146350 | HV Equipment | Unknown | TRUE | CB SF6 |  |  |  | 2013-E-0032 | No.1 Capacitor | Q | 2013Q3 | TRE | HV Equipment (Mains) | CAP | 2013-08-27 18:08 | 2013-09-10 11:37 | Smoke observed from C.B. control cubicle when closed as part of 33kV Bus Section 1 restoration as reported by SMF. C.B. 2712 opened via SCADA. Irregularity issued. Log entry PRI instigated to provide security isolation. | 19/09/2013 3:14:00 PM ¦ Nil ¦ No further action required |  | The capacitor was manually removed from service following initiation of CB Abnormal alarm and smoke being observed inside the CB Control Cubicle. As the Circuit Breaker was still under warranty, Schneider attended site to investigate the problem. The moto | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2013
2351 | 146802 | Switching error | HV EQT Staff Error | TRUE | Prev |  |  | Load lost 9MW for 9min | 2013-F-0319 | No.5 Orange - Orange North 66kV Line | S | 2013Q3 | ORG | Preventable | TL | 2013-09-03 08:02 | 2013-09-03 08:11 | During planned PRI execution to isolate & Earth 807 - Orange West tee Orange South TL. Field switching error resulted in No.5 Tx feeder to be off-loaded. Load restored following consultation with market participant. |  |  | During planned PRI execution to isolate & Earth 807 - Orange West tee Orange South TL. Field switching error resulted in No.5 Tx feeder to be off-loaded. 9MW of load was lost for 9 minutes. Load was restored following consultation with market participant. | Fine | External | [5 empty] | 0 | 1 | 2013 | Incorrect HV switching
2353 | 147591 | Bushfire | Unknown | TRUE | TL |  |  |  | 2013-F-0321 | 32 Sydney West - Bayswater 330kV TL | Z | 2013Q3 | BAY, SYW |  | TL | 2013-09-10 15:17 | 2013-09-10 15:18 | Grassfires in area | 23/12/2013 3:51:00 PM ¦ Nil ¦ Nil |  | Grassfires in area | Fine | External | [5 empty] | 0 | 0 | 2013
2354 | 147674 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0323 | 9U3 Gunnedah - Narrabri 132kV TL | Z | 2013Q3 | GN2, NB2 |  | TL | 2013-09-12 05:44 | 2013-09-12 05:44 |  |  |  | Trip and reclose operation. Cause unknown | Fine | Unexplained | [5 empty] | 0 | 0 | 2013
2355 | 147732 | Switching error | Unknown | TRUE | Prev |  |  | Lost load 55MW for 55min | 2013-F-0324 | 132kV Bus Section 3 | S | 2013Q3 | TA1 | Preventable | BB | 2013-09-12 09:00 | 2013-09-12 09:48 | 132kV busbar trip. Protection operation resulting in approximately 51MW load lost to Tamworth area. No1 transformer switching in progress at time of trip. |  |  | Approximately 55MW load lost to Tamworth area. The 132kV busbar sections 3 to 5 tripped due to a switching error. All load was restored 55 minutes later at 0955hrs. | Fine | External | [5 empty] | 0 | 1 | 2013 | Incorrect HV switching
2358 | 147899 | Animal/Bird | Unknown | TRUE | TL |  |  |  | 2013-F-0328 | 5A4 Bayswater - Wollar 500kV TL | Z | 2013Q3 | BAY, WOL |  | TL | 2013-09-14 22:42 | 2013-09-14 22:42 | 49% voltage depression for 3 cycles at Bayswater 500kV Switchyard. | 9/10/2013 2:11:00 PM ¦ Nil. ¦ No further action required. |  | Trip and reclose operation. A routine aerial inspection was carried out on 23/09/13 and found evidence of bird activity on structure 132. No damage was observed during this routine inspection. The distance to fault was calculated as being 55.8km from Bays | Unknown | External | [5 empty] | 0 | 0 | 2013
2359 | 148075 | Animal/Bird | Unknown | TRUE | TL |  |  |  | 2013-F-0332 | 5A4 Bayswater - Wollar 500kV TL | Z | 2013Q3 | BAY, WOL |  | TL | 2013-09-17 07:32 | 2013-09-17 07:32 | Distance to fault recorded as 73.7 from Bayswater / No.1 Protection. Distance to fault recorded as 73.74 from Bayswater / No.2 Protection. Blue phase (lower conductor) to earth. Note - Previous trip and reclose recorded on Saturday 14th September appears | 9/10/2013 2:12:00 PM ¦ Nil. ¦ No further action required. |  | A ground patrol identified a bird nest on structure 177 on the blue phase wing. A routine aerial inspection was conducted and found no further evidence of flash over. No damage was observed during this routine inspection. Protection indicated a blue phase | Fine | External | [5 empty] | 0 | 0 | 2013
2361 | 148237 | Unknown | Unknown | TRUE | SVC |  |  |  | 2013-F-0335 | No.1 SVC | Z | 2013Q3 | SYW |  | SVC | 2013-09-18 07:23 | 2013-09-18 12:24 | 330 No.1 SVC at Sydney West 330kV Substation tripped. Alarms received on SCADA as follows Syw No.1 SVC 5V1 KV - entered Zero Syw No.1 SVC 5V12 CB - Opened Syw 018 No.1 SVC - started OFF Syw 018 No.1 SVC - Stop Seq inittiated ON Syw 018 |  |  | Cause unknown. All SVC control logs to be forwarded to ABB for follow up. | Fine | Unexplained | [5 empty] | 0 | 0 | 2013 | Unknown reason for SVC trip, no further info in QAPR/THEOS/Opslog
2360 | 148234 | Contractor Error | Human Interference | TRUE | Prev |  |  |  | 2013-F-0334 | No.3 Transformer 330/132/11kV | Z | 2013Q3 | SYW | Preventable | TX | 2013-09-18 07:43 | 2013-09-18 10:25 | No.3 Transformer 330 C.B.. 5432 has Opened with out any control in put or protection operation. No.3 Transformer remained energised from the 132kV and was still supplying 415V auxiliaries. through an investigation it was discovered from Powercore site |  |  | A civil contractor inadvertently opened No.3 Transformer 330kV CB 5432 via the local manual trip button. | Fine | External | [5 empty] | 0 | 1 | 2013 | Incorrect manual CB operation
2362 | 148275 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0336 | O1 Upper Tumut - Canberra 330kV TL | Z | 2013Q3 | CA1, UT1 |  | TL | 2013-09-18 18:00 | 2013-09-18 18:00 |  |  |  | Storms in the area |  | External | [5 empty] | 0 | 0 | 2013
2365 | 148906 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0348 | 5A3 Bayswater - Mt Piper 500kV TL | Z | 2013Q4 | BAY, MTP |  | TL | 2013-10-01 05:38 | 2013-10-01 05:38 | Fault recorders operated at Wollar, Bannaby, Mt Piper. Noticeable dip on control room lights. Mount Piper DTF 105.78 Bayswater DTF 101.88 |  |  | Fault recorders operated at Wollar, Bannaby, Mt Piper. Noticeable dip on control room lights. Mount Piper DTF 105.78 Bayswater DTF 101.88 | Fine | Unexplained | [5 empty] | 0 | 0 | 2013
2368 | 149129 | Staff Error | Unknown | TRUE | VT |  |  |  | 2013-F-0354 | 18 Dapto - Kangaroo Valley 330kV TL | Z | 2013Q4 | DPT, KVS |  | TL | 2013-10-03 08:40 | 2013-10-03 11:45 |  |  |  | Transmission line tripped at only Dapto end due to loose K4L VT fuse on the blue phase. | Unknown | Unexplained | [5 empty] | 0 | 0 | 2013 | Loose VT fuse is the cause of the trip
2366 | 149289 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0357 | 96T Armidale - Glen Innes 132kV TL | Z | 2013Q4 | AR1, GNS |  | TL | 2013-10-08 05:02 | 2013-10-08 05:02 | DTF from Glen Innes = 41.92 km |  |  | DTF from Glen Innes = 41.92 km | Fine | Unexplained | [5 empty] | 0 | 0 | 2013
2367 | 149395 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0360 | 96T Armidale - Glen Innes 132kV TL | Z | 2013Q4 | AR1, GNS |  | TL | 2013-10-10 04:52 | 2013-10-10 04:52 |  | 1/11/2013 10:35:00 AM ¦ Nil. ¦ No further action required. |  | The transmission line tripped and auto-reclosed at both ends of the line due to a red phase to earth fault. A similar auto-reclose event occurred on 8/10/13 at 06:02hrs in a similar location. Ground patrols did not find any damage or cause for the trip. | Fine | Unexplained | [5 empty] | 0 | 0 | 2013
2369 | 149539 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0362 | 99W Wagga 330 - Wagga 132 132kV TL | Z | 2013Q4 | WG2, WG1 |  | TL | 2013-10-12 09:13 | 2013-10-12 09:13 |  |  |  |  | Fine | Unexplained | [5 empty] | 0 | 0 | 2013
2370 | 149543 | Animal/Bird | Non TransGrid Reason | TRUE | TL |  |  |  | 2013-F-0363 | 5A3 Bayswater - Mt Piper 500kV TL | Z | 2013Q4 | BAY, MTP |  | TL | 2013-10-13 01:30 | 2013-10-13 01:30 | Unit 7 at Wallerawang tripped at the same time. | 13/12/2013 9:20:00 AM ¦ Nil. ¦ No further action required. |  | The suspected cause of the trip is due to bird activity which has caused tripping of lines using similar towers in the past. Unit 7 at Wallerawang tripped at the same time. EnergyAustralia found that Wallerawang Unit 7 tripped on Restricted Earth Fault ( | Fine | External | [5 empty] | 0 | 0 | 2013
2371 | 149560 | Bushfire | Non TransGrid Reason | TRUE | TL |  |  |  | 2013-F-0372 | 963 Tomago330 - Taree T Hawksnest 132kV TL | Y | 2013Q4 | TRE, TOM |  | TL | 2013-10-13 19:46 | 2013-10-13 19:46 | 9632 TAR coincided with Trip of 98A T/L. | 30/10/2013 3:43:00 PM ¦ Nil. ¦ No further action required. |  | 963 TAR coincided with the trip of Ausgrid's 132kV 98A feeder at Tomago 330kV Substation (refer to FEOR 2013-F-0371). The distance to fault indicates that the fault occurred on the Ausgrid owned section of the 963 line. The fault records indicate a Blue p | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2372 | 149562 | Bushfire | Non TransGrid Reason | TRUE | TL |  |  |  | 2013-F-0373 | 963 Tomago330 - Taree T Hawksnest 132kV TL | Y | 2013Q4 | TRE, TOM |  | TL | 2013-10-13 21:29 | 2013-10-13 21:29 | Coincided with trip of 9F4. | 30/10/2013 3:42:00 PM ¦ Nil. ¦ No futher action required. |  | 963 TAR coincided with the trip of Ausgrid's 132kV 9A4 feeder at Tomago 330kV Substation (refer to FEOR 2013-F-0374). The distance to fault was calculated as being 4.9km - 6.4km from Tomago 330kV Substation. This indicates that the fault occurred on the A | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2374 | 149565 | Lightning/Storm | Unknown | TRUE | TL |  |  | Lost load 13MW for 1 hour 11 minutes | 2013-F-0376 | 96L Lismore 330 - Tenterfield tee Casino 132kV TL | C | 2013Q4 | LSM, TTF | HV Equipment (Mains) | TL | 2013-10-13 22:05 | 2013-10-14 18:38 | fault recorder on 96L at LSM indicated B and W phases. Returned to service at 18:38hrs. | 31/10/2013 4:07:00 PM ¦ Nil. ¦ No further action required. |  | Thunderstorms were present in the area. 13MW of load was lost. The transmission line tripped, auto-reclosed, tripped and then locked out at both the Lismore and Tenterfield ends of the line. Protection details indicated a red phase to earth fault. An aeri | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2433 | 149827 | Windblown/object | Wind | TRUE | Bus |  |  |  | 2013-F-0381 | 132kV Bus No.1 Section | Q | 2013Q4 | WW2 |  | BB | 2013-10-17 10:54 | 2013-10-17 11:53 |  | 23/12/2013 4:16:00 PM ¦ Nil ¦ Nil |  | Strong wind caused a copper earthing strap installed along an original concrete support structure of a decommissioned bay had come lose and made contact with the adjacent line bay equipment. The strong caused fatigue and eventual failure of the fasteners | Very Windy | External | [5 empty] | 0 | 0 | 2013
2379 | 149852 | Unknown/Storm | Non TransGrid Reason | TRUE | TL |  |  |  | 2013-F-0383 | 32 Sydney West - Bayswater 330kV TL | Z | 2013Q4 | BAY, SYW |  | TL | 2013-10-17 14:34 | 2013-10-17 14:35 |  |  |  |  | Very Windy | Unexplained | [5 empty] | 0 | 0 | 2013
2380 | 149855 | Unknown/Storm | Non TransGrid Reason | TRUE | TL |  |  |  | 2013-F-0384 | 32 Sydney West - Bayswater 330kV TL | Z | 2013Q4 | BAY, SYW |  | TL | 2013-10-17 14:57 | 2013-10-17 14:57 | Protection details also refer to FEOR 2013-F-0383 |  |  |  | Very Windy | Unexplained | [5 empty] | 0 | 0 | 2013
2381 | 149864 | Lightning/Storm | Wind | TRUE | TL |  |  |  | 2013-F-0385 | 6 Canberra - Capital Wind Farm 330kV TL | Z | 2013Q4 | CA1, CWF |  | TL | 2013-10-17 15:48 | 2013-10-18 14:12 | Very Strong Winds at Capital Wind Farm. DTF from CA1 - 53.7km DTF from CWF - 9.69km |  |  | Very Strong Winds at Capital Wind Farm. A crossarm on an emergency structure has come loose. DTF from CA1 - 53.7km DTF from CWF - 9.69km |  | External | [5 empty] | 0 | 0 | 2013
2382 | 149865 | Unknown | Bushfire | TRUE | TL |  |  |  | 2013-F-0386 | 31 Regentville - Bayswater 330kV TL | Z | 2013Q4 | BAY, RGV |  | TL | 2013-10-17 17:02 | 2013-10-17 17:02 |  |  |  |  | Very Windy | Unexplained | [5 empty] | 0 | 0 | 2013
2383 | 149962 | Lightning/Storm | Non TransGrid Reason | TRUE | TL |  |  |  | 2013-F-0388 | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Z | 2013Q4 | AR1, COF | HV Equipment (Mains) | TL | 2013-10-18 12:16 | 2013-10-18 12:16 |  |  |  | Lightning storms were present in the area | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2384 | 150158 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0392 | 991 Wagga North - Murrumburrah 132kV TL | Z | 2013Q4 | MRU, WGN |  | TL | 2013-10-22 09:46 | 2013-10-22 09:46 | Note. SCADA did not indicate CB operation at Murrumburrah |  |  | Storms in the area | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2385 | 150268 | Bushfire | Non TransGrid Reason | TRUE | TL |  |  |  | 2013-F-0394 | 95 Newcastle - Tomago 330kV TL | Z | 2013Q4 | NEW, TOM | HV Equipment (Mains) | TL | 2013-10-23 11:48 | 2013-10-23 11:48 | Newcastle - Distance to fault - 8.2km Tomago - Distance to fault - 17.55km | 11/11/2013 3:03:00 PM ¦ Nil. ¦ Further inspection of the line will be carried out at the next routine inspection. |  | The fault is consistent with the fire being blown across the line, from vegetation adjacent to the easement. Further inspection of the line will be carried out at the next routine inspection. | Fine | External | [5 empty] | 0 | 0 | 2013
2386 | 150408 | Bushfire | Unknown | TRUE | TL |  |  |  | 2013-F-0395 | 31 Regentville - Bayswater 330kV TL | Z | 2013Q4 | BAY, RGV |  | TL | 2013-10-25 13:11 | 2013-10-25 13:11 | Bush Fires in close proximity of dual circuit transmission lines 31 & 32 |  |  | Bush Fires in close proximity of dual circuit transmission lines 31 & 32 | Fine | External | [5 empty] | 0 | 0 | 2013
2387 | 150426 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0397 | 990 Yass - Wagga 132 132kV TL | Z | 2013Q4 | WG2, YSN |  | TL | 2013-10-27 06:35 | 2013-10-27 06:35 | Protection details required. Unsure if CB 9902 at WG2 operated due to lack of alarms at WG2 and voltage indication at YSN did not appear to change. |  |  | Protection details required. Unsure if CB 9902 at WG2 operated due to lack of alarms at WG2 and voltage indication at YSN did not appear to change. | Fine | Unexplained | [5 empty] | 0 | 0 | 2013
2388 | 150485 | Relay | Sec Eqt Malfunction | TRUE | Prot |  |  |  | 2013-F-0399 | 8 Marulan - Dapto 330kV TL | Z | 2013Q4 | DPT, MRN |  | TL | 2013-10-28 07:24 | 2013-10-28 07:32 | Note Only No.1 protection Operated and only CB..82 at operated at Dapto there were no alarms or CB operations at Marulan sub. Protection tech at Dapto believes a firm wear fault on the No.1 Protection relay caused the trip of CB..82 at Dapto | 24/12/2013 9:47:00 AM ¦ Nil ¦ Nil |  | Only No.1 protection Operated and only CB82 operated at Dapto there were no alarms or CB operations at Marulan sub. Protection tech at Dapto believes a firm wear fault on the No.1 Protection relay caused the trip of CB82 at Dapto The cases of mal-operatio | Fine | Secondary Equipment | [5 empty] | 1 | 0 | 2013 | Protection relay firmware fault
2391 | 150854 | Secondary Equipment | LV/MECH/PROT Equipment Fail | TRUE | Cond |  |  |  | 2013-E-0035 | No.7 330/132/11kV Transformer | E | 2013Q4 | TOM |  | TX | 2013-11-03 09:34 | 2013-11-03 11:25 | Taken out of service in response to Urgent Condition Monitoring alarm. Hydran unit found faulty. TX RTS. | 28/11/2013 3:32:00 PM ¦ Nil. ¦ The unit is to be repaired under warranty by the manufacturer. |  | Taken out of service in response to Urgent Condition Monitoring alarm. The Hydran unit was found to be faulty. The unit will be repaired by the manufacturer as it is under warranty. The unit is a Hydran 201 supplied by Toshiba. The Transformer was returne |  | Secondary Equipment | [5 empty] | 0 | 0 | 2013
2392 | 151296 | Animal/Bird | Unknown | TRUE | TL |  |  |  | 2013-F-0409 | 5A4 Bayswater - Wollar 500kV TL | Z | 2013Q4 | BAY, WOL |  | TL | 2013-11-07 04:09 | 2013-11-07 04:10 |  | 4/12/2013 8:41:00 AM ¦ Nil. ¦ No further action required. |  | An inspection found two previously reported bird nests and an additional bird's nest on the middle phase of 5A4. Evidence of a recent flashover was found on the middle phase of 5A4 TL as well as a recently deceased bird under the 5A4 TL side of the tower | Unknown | External | [5 empty] | 0 | 0 | 2013
2393 | 151585 | HV Equipment | Sec Eqt Malfunction | TRUE | TX |  |  |  | 2013-F-0411 | No.1 Transformer 330/132/11kV | Z | 2013Q4 | NEW |  | TX | 2013-11-08 14:52 | 2013-11-08 17:41 | CB 5412 tripped immediately on enerigising after routine maintenance. | 4/12/2013 9:46:00 AM ¦ Nil. ¦ In the future, DC testing will not be conducted as the last test before the transformer is returned to service. This will allow any residual magnetism to discharge before the Transformer is energised. |  | The 330kV 5412CB at Newcastle Substation tripped immediately upon energisation of the No.1 330/132/11kV Transformer. The Transformer was being energised following a routine maintenance. Protection flagging indicated a lowset differential trip. The trip wa |  | Maintenance | [5 empty] | 0 | 0 | 2013
2394 | 151615 | HV Equipment |  | TRUE | Disc |  |  |  |  | No.1 Transformer 330/132/11kV | Z | 2013Q4 | SYW | Plant (Subs) | TX | 2013-11-09 17:00 | 2013-11-17 15:20 |  |  |  | No.1 Transformer was out for a planned outage. The 330kV Bus Disc 5413 failed to close fully while switching under HVPRI 47987. No FEOR - see IR 11262 |  | Unexplained | [5 empty] | 0 | 0 | 2013
2395 | 151626 | Unknown/Storm | Unknown | TRUE | TL |  |  |  | 2013-F-0418 | No.2 Tie Wallerawang 132 - Wallerawang 132 (New) 132kV TL | Z | 2013Q4 | WW2, WWS |  | TL | 2013-11-10 15:22 | 2013-11-10 18:00 | No auto reclose on TL. |  |  | No auto reclose available on TL. OPSLog entry indicated bay and line inspection but does not indicate any findings. | Thunderstorm | Unexplained | [5 empty] | 0 | 0 | 2013
2451 | 151628 | Staff Error | Non TransGrid Reason | TRUE | Cont |  |  |  | 2013-F-0420 | 0896 Koolkhan - Maclean 66kV Line | Q | 2013Q4 | KLK | Preventable | TL | 2013-11-10 18:06 | 2013-11-10 18:52 | no reclose, Scada selected to auto reclose. Confirmed no reclose event on local control system. Needs further investigation. Feeder returned to service at 18:52 at Essential Energy request. | 6/12/2013 8:15:00 AM ¦ Nil. ¦ No further action required. |  | The auto-reclose switch on the 0896 feeder Control Panel was in the non-auto position, preventing the feeder from auto-reclosing. The status of this switch is not visible via SCADA, thus it appeared to the operator that auto-reclose was enabled. As part | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2396 | 151698 | Unknown/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0425 | 966 Armidale - Koolkhan 132kV TL | Z | 2013Q4 | AR1, KLK |  | TL | 2013-11-11 14:55 | 2013-11-11 14:55 |  |  |  | Trip and reclose | Thunderstorm | [6 empty] | 0 | 0 | 2013
2397 | 151700 | Fire | Unknown | TRUE | TL |  |  |  | 2013-F-0426 | 967 Lismore 330 - Koolkhan 132kV TL | Z | 2013Q4 | KLK, LSM | HV Equipment (Mains) | TL | 2013-11-11 16:20 | 2013-11-11 16:45 | Cane fire under line at time of trip. Cane farmer confirmed flash over at time of trip. | 4/12/2013 8:56:00 AM ¦ Nil. ¦ The established approval and reporting process for cane fires worked as intended, and no change is considered necessary. |  | A cane farmer 3.5km from Lismore Substation notified a TransGrid Easement Officer that he would start a cane fire and said that the fire would be a low level fire. The System Operator was advised of the proposed fire. Following the TARTLO, the Easement Of | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2399 | 151811 | Unknown/Storm | Non TransGrid Reason | TRUE | TL |  |  |  | 2013-F-0436 | 96T Armidale - Glen Innes 132kV TL | Z | 2013Q4 | AR1, GNS |  | TL | 2013-11-12 09:50 | 2013-11-12 09:50 |  |  |  | Trip and reclose | Thunderstorm | [6 empty] | 0 | 0 | 2013
2398 | 151803 | Lightning/Storm | Non TransGrid Reason | TRUE | TL |  |  |  | 2013-F-0434 | 9U4 Glen Innes - Inverell 132kV TL | Z | 2013Q4 | GNS, INV |  | TL | 2013-11-12 11:23 | 2013-11-12 11:23 | Trip and successful auto reclose during period of heavy storm activity in area. |  |  | Trip and reclose | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2400 | 151818 | Staff Error | HV Equipment Failure | TRUE | TX |  |  |  | 2013-E-0036 | No.3 Transformer 330/132/11kV | E | 2013Q4 | SYS | Preventable | TX | 2013-11-12 11:52 | 2013-12-18 11:35 | 0950hrs T/TECH Albert El Souri - Advised of No.3 Tx Low Oil Alarm at Sydney South 330kV Substation. Request investigate. 0957hrs F/TECH Albert El Souri - Advises Oil levels seem correct and comparable to other in service Tx's. 1047hrs F/TL Paul Hazelti | 24/12/2013 10:14:00 AM ¦ Nil ¦ Nil |  | The transformer was de-energised after receiving a L1 bushing alarm. A further inspection by Substation Maintenance on the 18/12/13 of the Doble IDD bushing tap connections found wiring issues. The tap connections were repaired and modified after which t | Rain | External | [5 empty] | 0 | 0 | 2013
2401 | 152362 | HV Equipment | HV EQT Staff Error | TRUE | Disc |  |  |  | 2013-F-0451 | 29 Sydney West - Vineyard 330KV TL | Z | 2013Q4 | SYW, VYD | Plant (Subs) | TL | 2013-11-17 06:40 | 2013-11-17 08:41 | 29 Sydney west to Vineyard 330kV T/L tripped as a fault on 330kV A2 Bus R-Ph at SYW. | 20/12/2013 4:33:00 PM ¦ Nil ¦ Nil |  | T/L tripped as a fault on 330kV A2 Bus R-Ph at SYW. Tech services confirmed protection flagging 'switch on to fault' trip - the relays were in this mode in error. Tech services investigation detremined the cause to be 330kV AEM disconnector pallets being | Rain | Secondary Equipment | [5 empty] | 0 | 0 | 2013 | Disconnector pallets faulty
2405 | 152395 | Switching error | HV EQT Staff Error | TRUE | Bus |  |  |  | 2013-F-0456 | 330kV A Bus Section No.2 | Q | 2013Q4 | SYW | Preventable | BB | 2013-11-17 06:40 | 2013-11-17 08:41 | SYW 330kV A Bus No.2 section tripped due to switching error |  |  | Tripped due to switching error. | Rain | External | [5 empty] | 0 | 1 | 2013 | Switching error, excerpt from Opslog: "Earth Switch 5120/1 was operated incorrectly"
2404 | 152368 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0454 | 99K Darlington Pt - Griffith 132kV TL | Z | 2013Q4 | DNT, GRF |  | TL | 2013-11-18 05:01 | 2013-11-18 05:01 | At 05:01hrs 99K Darlington Point to Griffith 132 kV T/L tripped and Reclosed at Darlington Point and Griffith SS. Cause Unknown |  |  | Cause Unknown | Fine | Unexplained | [5 empty] | 0 | 0 | 2013
2410 | 152647 | HV Equipment | LV Maintenance | TRUE | CB SF6 |  |  |  |  | No.3 Capacitor | E | 2013Q4 | WL1 |  | CAP | 2013-11-20 15:10 | 2013-11-20 18:18 |  |  |  | CB SF6 top up as per RFA 2013-10056 and OPSLog entry. |  | Oil/Gas Levels | [5 empty] | 0 | 0 | 2013
2411 | 152805 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0463 | 77 Wallerawang - Ingleburn 330kV TL | Z | 2013Q4 | ING, WW1 |  | TL | 2013-11-21 17:47 | 2013-11-21 17:50 | Initial trip and reclose from Ingleburn only. No.2 Transformer out of service at Ingleburn with 77 Wallerawang B C.B.. 772B open and reclose disabled. Reclose selected non-auto at Wallerawang 330 at the time of outage due to impending return to service of |  |  | The line auto-reclosed at Ingleburn only. The Wallerawang side was selected as non-auto due to preparation for the return to service of No.7 Generator at Wallerawang Power Station. The TL was returned to service following manual closing of one of its brea | Thunderstorm | External | [5 empty] | 0 | 0 | 2013 | Reclose failure, not a protection failure
2412 | 152914 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0468 | 97K Cooma - Munyang tee Snowy Adit 132kV TL | Z | 2013Q4 | CMA, MNY |  | TL | 2013-11-22 10:05 | 2013-11-22 10:05 | [5 empty] | External | [5 empty] | 0 | 0 | 2013
2413 | 152974 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0484 | 966 Armidale - Koolkhan 132kV TL | Z | 2013Q4 | AR1, KLK |  | TL | 2013-11-23 15:42 | 2013-11-23 15:42 |  | 24/12/2013 11:08:00 AM ¦ Nil. ¦ No further action required. |  | Protection flagging indicated a 3 phase to earth fault. The distance to fault was calculated as being 61.5km from Armidale, which equates to structures 208 - 209. INDJI indicated that multiple lightning strikes occurred in the vicinity of structure 210. A | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2414 | 152976 | Lightning/Storm | Lightning or Storm | TRUE | TL |  |  |  | 2013-F-0485 | 9W6 Macksville - Nambucca 132kV TL | Z | 2013Q4 | NAM, MVL |  | TL | 2013-11-23 16:45 |  |  | 13/12/2013 9:07:00 AM ¦ Nil. ¦ No further action required. |  | Thunderstorms were present at the time of the trip. An inspection was carried out and found the OHEW had failed mid span between structures 282 and 101, which is the second span out from Macksville Substation. 9W5 and 9W6 are run on double circuit towers | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2455 | 152986 | HV Equipment | LV Maintenance | TRUE | CB SF6 |  |  |  |  | No.4 Bay Coupler CB 6042 | Q | 2013Q4 | ER0 | Plant (Subs) | CB | 2013-11-24 21:52 | 2013-11-24 23:22 |  |  |  | Outage to top up SF6 (RFA 2013-10138) |  | Oil/Gas Levels | [5 empty] | 0 | 0 | 2013
2415 | 153397 | HV Equipment | HV Equipment Failure | TRUE | Rx |  |  |  | 2013-E-0038 | No.2 330kV Reactor | E | 2013Q4 | AR1 | Plant (Subs) | RX | 2013-11-29 21:53 | 2013-12-04 14:00 | Buchholz alarm received. No.2 reactor de-energised. Buchholz relay indicating oil level OK and no gas. Further investigation to be carried out during daylight hours. Investigation indicates hydran condition monitoring unit alarm initiates buchholz alarm | 13/12/2013 9:37:00 AM ¦ Nil. ¦ The Reactor oil will be sampled every 6 months to ensure the rate of change of gas in the oil remains stable. |  | Investigation indicates that the hydran condition monitoring unit alarm initiates the buchholz alarm. Analysis indicated elevated hydrogen levels. | Rain | Oil/Gas Levels | [5 empty] | 0 | 0 | 2013
2416 | 153524 | HV Equipment | Defect | TRUE | CB SF6 |  |  |  |  | No.7 Transformer 330kV B CB 5472B | Q | 2013Q4 | TOM | Plant (Subs) | CB | 2013-12-02 07:11 | 2013-12-02 08:07 |  |  |  | CB SF6 top-up. (RFA 2013-10318) |  | Oil/Gas Levels | [5 empty] | 0 | 0 | 2013
2417 | 153692 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0494 | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Z | 2013Q4 | AR1, COF |  | TL | 2013-12-04 02:56 | 2013-12-04 02:56 |  | 13/12/2013 9:09:00 AM ¦ Nil. ¦ No further action required. |  | A ground patrol found no evidence of a fault. The trip was likely associated with humid, low temperature weather conditions. There were no storms in the area at the time of the trip. Protection flagging indicated a blue phase to earth fault. The distance | Fine | Unexplained | [5 empty] | 0 | 0 | 2013
2418 | 154078 | Unknown | Unknown | TRUE | TL |  |  |  | 2013-F-0502 | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2013Q4 | GTH, MUR, GHI |  | TL | 2013-12-05 10:11 | 2013-12-05 15:32 | 97G Geehi Tee open at Guthega at time of trip. No.2 Transformer out of service at time of trip. Trip of No.1 Transformer initiated by CBF trip from 97G Geehi Tee No.2 Protection. No.1 Transformer returned to service at |  |  | 97G Geehi Tee was open at Guthega at the time of the trip. No.2 Transformer out of service at time of trip. Trip of No.1 Transformer initiated by CBF trip from 97G Geehi Tee No.2 Protection. | Rain | [6 empty] | 1 | 0 | 2013 | Caused by loose wiring in Guthega No.2 Prot Panel for Line 97G, excerpt from THEOS followup: "The wire 3430 was found loose in the DEF module"
2480 | 154078 | Unknown | Unknown | TRUE | CB |  |  |  | 2013-F-0502 | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2013Q4 | GTH, MUR, GHI |  | TL | 2013-12-05 10:11 | 2013-12-05 15:32 | 97G Geehi Tee open at Guthega at time of trip. No.2 Transformer out of service at time of trip. Trip of No.1 Transformer initiated by CBF trip from 97G Geehi Tee No.2 Protection. No.1 Transformer returned to service at |  |  | 97G Geehi Tee was open at Guthega at the time of the trip. No.2 Transformer out of service at time of trip. Trip of No.1 Transformer initiated by CBF trip from 97G Geehi Tee No.2 Protection. | Rain | [6 empty] | 0 | 0 | 2013 | Duplicate
2419 | 154325 | Animal/Bird | Animal/Bird | TRUE | Cap |  |  |  | 2013-F-0512 | No.3 Capacitor | Z | 2013Q4 | BER |  | CAP | 2013-12-08 05:40 | 2013-12-11 13:21 | Bay inspection revealled birds nesting within Capacitor bank. Substantial amount of nesting material present. |  |  | Bay inspection revealled birds nesting within the capacitor bank. Substantial amount of nesting material was present. | Fine | External | [5 empty] | 0 | 0 | 2013
2434 | 154443 | Unknown | Unknown | TRUE | Cont |  |  |  | 2013-F-0517 | 973 Yass - Cowra 132kV TL | Z | 2013Q4 | CW2, YSN |  | TL | 2013-12-10 00:30 | 2013-12-10 00:30 | 973 T/L reclosed at Yass end but not at Cowra end. 973 closed at Cowra end via Scada. |  |  | 973 T/L reclosed at Yass end but not at Cowra end. 973 closed at Cowra end via Scada. | Rain | Unexplained | [5 empty] | 0 | 0 | 2013
2436 | 154532 | Lightning/Storm | Unknown | TRUE | TL |  |  | Lost load 7.2MW for 21 minutes | 2013-F-0519 | 964 Pt Macquarie - Taree Tee Herons Creek 132kV TL | C | 2013Q4 | PMQ, TRE | HV Equipment (Mains) | TL | 2013-12-10 15:18 | 2013-12-11 14:49 | Essential Energy report 11kV conductor fault in area of Landsdown occurring at time TAROLO of 964 T/L. Distance to fault indication also places fault in area of Landsdown. Awaiting results of line patorl at time of this report. | 24/12/2013 11:07:00 AM ¦ Nil. ¦ No further action required. |  | There were thunderstorms in the area at the time of the trip. A ground patrol was carried out and found the outer right (Blue) phase conductor approx 33m east of the centreline, resting in the crown of a 35m high tree. No obvious damage to the conductor | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2437 | 154696 | Staff Error | Operating Error | TRUE | Bus |  |  |  | 2013-F-0520 | 330kV A Bus No.1 Section | Q | 2013Q4 | UT1 | Preventable | BB | 2013-12-11 07:42 | 2013-12-11 10:36 | Also Tripped Reserve bus. |  |  | Incorrect HVPRI was the cause of the incident. 137MW generation was lost. |  | External | [5 empty] | 0 | 1 | 2013 | Incorrect switching instructions (HVPRI)
2438 | 154702 | Lightning/Storm | Unknown | TRUE | SVC |  |  |  | 2013-F-0521 | No.1 Static VAR Compensator | Z | 2013Q4 | LSM | Plant (Subs) | SVC | 2013-12-11 14:23 | 2013-12-11 17:11 |  | 24/12/2013 11:37:00 AM ¦ Nil. ¦ No further action required. |  | There were thunderstorms in the area at the time of the trip. It is noted that a similar outage occurred on this SVC on 30/10/11. Protection flagging indicated a neutral displacement trip and also a transformer differential operation. A close inspection o | Thunderstorm | External | [5 empty] | 0 | 0 | 2013
2442 | 154862 |  | Unknown | TRUE |  |  |  |  | 2013-F-0526 | No.2 Transformer 330/132/11kV | Z | 2013Q4 | VP1 |  | TX | 2013-12-14 07:50 | 2013-12-14 10:10 | Appears protection operation resulting from possible slow C.B. operation. Equipment inspected and returned to service successfully. | 24/12/2013 11:13:00 AM |  | The No.4 station transformer tripped No.2 transformer. TransGrid are currently in consultation with Delta to confirm details of the protection operations of the No.4 Station Transformer. | Fine | [6 empty] | 1 | 0 | 2013
2605 | 154883 | HV Equipment | HV Equipment Failure | TRUE | VT |  |  | Lost load 0.164MW for 16 hours 29 mins | 2013-E-0039 | 300 Parkes - North Parkes 132kV Line | P | 2013Q4 | PKS |  | TL | 2013-12-16 01:15 | 2013-12-16 17:44 | TAR occurred @ 0110 hours (FEOR 2013-F-0258) and 0111 hours (FEOR 2013-F-0259). C.V.T. Imbalance alarm active when both incidents occurred. Clearance requested from Essential Energy to de-energise T/L due to concerns over integrity of Line C.V.T. Staff |  |  | Parkes Line 300 tripped and auto-reclosed twice (a minute apart) followed by a CVT Imbalance alarm being raised, prompting the operator to manually take the line of out of service. Site staff subsequently found the CVT failed explosively and was on fire. | Fine | Primary Equipment | [5 empty] | 0 | 0 | 2013
2443 | 154950 | Lightning/Storm | Unknown | TRUE | TL |  |  |  | 2013-F-0535 | 978 Williamsdale - Cooma 132kV TL | Z | 2013Q4 | CMA, WDL |  | TL | 2013-12-16 16:18 | 2013-12-16 16:18 | Tripped 240V De-Ion CB for 120V Battery Charger "A" on 415V AC distribution panel Requires protection details when next available on site. |  |  | At 16:18hrs 978 Williamsdale to Cooma 132 kV T/L tripped and auto reclosed. Storms in the area. |  | External | [5 empty] | 0 | 0 | 2013
2458 | 155298 | Unknown | HV Maintenance | TRUE | CB |  |  |  |  | No.1 Capacitor | E | 2013Q4 | SYW |  | CAP | 2013-12-26 17:28 | 2014-01-13 14:10 |  |  |  | Outage to replace control cable and perform CB trip checks (see RFA 2013-10293 and RFA 2014-108) |  | Secondary Equipment | [5 empty] | 0 | 0 | 2013
2446 | 155299 | HV Equipment | Defect | TRUE | CB SF6 |  |  |  |  | No.1 Transformer 132/66/11kV | E | 2013Q4 | NB2 | Plant (Subs) | TX | 2013-12-26 20:05 | 2013-12-26 20:23 |  |  |  | Outage to top up SF6 |  | Oil/Gas Levels | [5 empty] | 0 | 0 | 2013

## Results
Year: | Prot Fail | Incorrect Isolation
2009 | 21 | 14
2010 | 18 | 6
2011 | 26 | 8
2012 | 20 | 7
2013 | 11 | 10