## QAPR Comment on Outage
Outage ID | QAPR Reason | Failed Eq | Outage Group | AER Code | QTR | Sub | Component_Type | Actual Start | Actual End | FEOR_Comment | Followup_Comments | Comment on Outage | VoltsC | Asset Mgr Comments | AER Fault/Forced Outage | Year:
-3 | Communications | Com | Black Mountain Radio Repeater |  | 2015Q1 |  | Comms | 2015-01-02 17:30 | 2015-01-03 17:30 | MWLink-0059 Sagem SLF Radio system failure, causing loss of comms (SCADA, BAS, OTS, CDN, SSZ) to QBY. |  | MWLink-0059 Sagem SLF Radio system failure, causing loss of comms (SCADA, BAS, OTS, CDN, SSZ) to QBY. IDU subsequently replaced and services restored. |  |  |  | 2015
-2 | External | TL |  |  | 2014Q4 |  | TL | 2014-11-08 19:11 | 2014-11-08 19:11 |  |  | Advised Ausgrid had received reports of children (approx 3) climbing a transmission tower. They were spotted 35 metres from the ground. Ausgrid DEO in attendance confirmed it was a TransGrid structure. Police were called but just as the police arrived children climbed down and left. (possibly sighted police coming). Ausgrid DEO confirmed the barbbed wire was not cut but there appears to be a dog leg in the way it's attached and quite easily climbed around. |  | Richard Archer to send Bruce Fraser a request to install anti-climber. Investigation ongoing. Update 30/09/2015: Anti-climber can be bypassed. Need work request raised with maintenance to improve anti-climber. [Update 15/12/2015] Internal Works Request (IWR) being raised for design solution and implementation by Field Services. [Update 28/01/2016] IWR has been issued. [Update 09/05/2016] Designer still reviewing. [20/07/2016] Steve Stavropoulos advised can be closed. W/O issued to design & field services to rectify anti climber non compliance. |  | 2014
-1 | Communications | Com | 51 Lower Tumut - Wagga 330 OPGW |  | 2014Q2 | LTS | Comms | 2014-05-02 00:30 | 2014-05-02 13:00 | Faulty Optical Line Equipment on the Multiplexer at Lower Tumut meant loss of SCADA Communications to Wagga 330, Wagga Nth, Murrumburah, Finley, Gadara, Yanco, Tumut 132, Urinquinty, Deniliquin and Coleambally sites |  | Faulty Optical Line Equipment on the Multiplexer at Lower Tumut meant loss of SCADA Communications to Wagga 330, Wagga Nth, Murrumburah, Finley, Gadara, Yanco, Tumut 132, Urinquinty, Deniliquin and Coleambally sites |  | Work ongoing |  | 2014
92373 | [11 empty] | SF6 top-up FEOR cancelled to make short notice |  |  |  | 1900
102540 | [11 empty] | FEOR Cancelled as available for emergency use. Advises doble alarm is 64 again, from bushing diagram in cabinet appears indicating problem is (6) 132kV R phase bushing & (4) indicates "critical deterioration detected", cleared again. Advised OK, will O/S #1 Transformer, OCE (Martin) & NCM (Max) advised. Available for emergency use |  |  |  | 1900
109228 |  |  | 8L Dumaresq - Bulli Creek 330kV TL | X | 2014Q4 | DMQ | TL | 2014-10-13 07:28 | 2014-10-17 11:02 |  |  |  | 330 |  |  | 2014
109229 |  |  | 8M Dumaresq - Bulli Creek 330kV TL | X | 2014Q3 | DMQ | TL | 2014-07-01 11:40 | 2014-07-06 14:38 |  |  |  | 330 |  |  | 2014
110093 | [11 empty] | Cause being investigated |  |  |  | 1900
150673 |  |  | M13 Murray - Murray 2 330kV TL | X | 2014Q2 | MUR | TL | 2014-05-18 10:16 | 2014-05-18 13:03 |  |  |  | 330 |  |  | 2014
155087 |  |  | M13 Murray - Murray 2 330kV TL | X | 2014Q2 | MUR | TL | 2014-06-01 09:11 | 2014-06-01 12:25 |  |  |  | 330 |  |  | 2014
155098 |  |  | U3 Upper Tumut - Tumut 1 330kV TL | X | 2014Q1 | UT1 | TL | 2014-03-16 07:29 | 2014-03-16 11:35 |  |  |  | 330 |  |  | 2014
155099 |  |  | U5 Upper Tumut - Tumut 2 330kV TL | X | 2014Q1 | UT1 | TL | 2014-03-16 07:29 | 2014-03-16 11:35 |  |  |  | 330 |  |  | 2014
155100 |  |  | L5 Lower Tumut - Tumut 3 330kV TL | X | 2014Q1 | LT1 | TL | 2014-03-16 07:29 | 2014-03-16 11:35 |  |  |  | 330 |  |  | 2014
155101 |  |  | 64 Lower Tumut - Upper Tumut 330kV TL | X | 2014Q1 | LT1, UT1 | TL | 2014-03-16 07:26 | 2014-03-16 11:35 |  |  |  | 330 |  |  | 2014
155109 |  |  | L5 Lower Tumut - Tumut 3 330kV TL | X | 2014Q1 | LT1 | TL | 2014-03-23 08:01 | 2014-03-23 13:49 |  |  |  | 330 |  |  | 2014
155113 |  |  | 64 Lower Tumut - Upper Tumut 330kV TL | X | 2014Q1 | LT1, UT1 | TL | 2014-03-23 07:34 | 2014-03-23 11:55 |  |  |  | 330 |  |  | 2014
155114 |  |  | U5 Upper Tumut - Tumut 2 330kV TL | X | 2014Q1 | UT1 | TL | 2014-03-23 08:00 | 2014-03-23 13:48 |  |  |  | 330 |  |  | 2014
155115 |  |  | U3 Upper Tumut - Tumut 1 330kV TL | X | 2014Q1 | UT1 | TL | 2014-03-23 07:52 | 2014-03-23 13:48 |  |  |  | 330 |  |  | 2014
155539 |  |  | 96F Stroud - Tomago 330 132kV TL | X | 2014Q1 | TOM | TL | 2014-01-13 05:36 | 2014-01-13 16:15 |  |  |  | 132 |  |  | 2014
155543 |  |  | 96F Stroud - Tomago 330 132kV TL | X | 2014Q1 | TOM | TL | 2014-01-15 05:11 | 2014-01-15 18:04 |  |  |  | 132 |  |  | 2014
155613 | Unknown | Disc | No.4 Tenterfield - Council (TSC 22/11kV SS) 22kV Line | Q | 2014Q1 | TTF | TL | 2014-01-08 22:14 | 2014-01-09 03:49 |  |  | Outage to repair Disconnector 44 | 22 | Subs Asset Mgr advises can be closed |  | 2014
155616 | Lightning/Storm | TL | 963 Tomago330 - Taree T Hawksnest 132kV TL | Q | 2014Q1 | TRE, TOM | TL | 2014-01-04 01:15 | 2014-01-04 01:15 | Customer load restored via auto reclose | 4/02/2014 1:52:00 PM ¦ follow up required ¦ Nil. ¦ No future action required. | On Saturday 04/01/2014 at 02:15hrs, the 132kV 963 TL from Tomago to Taree tripped and auto-reclosed at both ends of the line. Protection flagging indicated a red phase fault to earth. The fault location was calculated as being approx 12km from Tomago Substation, which puts the fault in the AusGrid owned section of the line | 132 |  |  | 2014
155635 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2014Q1 | GRF | TL | 2014-01-04 10:21 | 2014-01-04 10:21 |  | follow up required |  | 33 |  |  | 2014
155652 |  |  | 82K/1 Bungendore tee Sutton CB 82K2 |  | 2014Q1 | QBY | CB | 2014-01-05 07:33 | 2014-01-05 07:33 | Tripped and Reclosed. Essential Energy advised. | follow up required |  | 66 |  |  | 2014
155653 | LV/MECH Fail | CB | 5A4 Bayswater 500kV A CB 5A42A | Q | 2014Q1 | WOL | CB | 2014-01-05 11:46 | 2014-01-06 10:38 |  |  | Advised of earth fault indication from No.1 DC Battery. Appears to be DC negative to earth fault in control circuitry of CB. When control box accessed "burning smell" observed. CB requested O/S for integrity check and investigation. Fault located in CB No.1 trip circuit No.1 Trip negative link. Secondary Systems Asset Manager indicates no further investigation required. | 500 |  |  | 2014
155657 |  |  | 29 Sydney West - Vineyard 330kV TL | E | 2014Q1 | SYW, VYD | TL | 2014-01-05 14:23 | 2014-01-05 15:51 |  | follow up required |  | 330 |  | Forced | 2014
155658 |  |  | 26 Munmorah - Sydney West 330kV TL | E | 2014Q1 | MN1, SYW | TL | 2014-01-05 13:45 | 2014-01-05 15:50 | Request to de-energise line and prepare for isolation and earthing via Network Control Manager. Concurrent outage of 29 T/L. Line placed in service and on load at request of Network Control Manager. | follow up required |  | 330 |  | Forced | 2014
155659 |  |  | 26 Munmorah - Sydney West 330kV TL |  | 2014Q1 | MN1, SYW | TL | 2014-01-05 13:45 | 2014-01-05 15:50 | Line de-energised due to person on tower | follow up required |  | 330 |  |  | 2014
155663 | Condition Monitor | TX | No.3 Transformer 330/132/11kV | E | 2014Q1 | AR1 | TX | 2014-01-06 03:04 | 2014-01-06 10:13 | Transformer taken out of service following receipt of Condition Monitor L1 alarm. | 30/01/2014 2:21:00 PM ¦ follow up required ¦ Nil. ¦ Any future action will be based on consultation by Asset Performance with the manufacturer of the oil monitoring device. | On Monday 06/01/2014 at 04:04hrs, the 330/132/11kV No.3 Transformer at Armidale Substation was manually removed from service following the initiation of a condition monitoring L1 alarm. The L1 alarm was initiated by an internal fan failure in the Calisto online Oil Monitoring device. This alarm had been incorrectly grouped with the transformer's L1 alarms. The alarm was accepted and the Calisto's general alarm output was isolated from the L1 alarm group. The Transformer was returned to service on 06/01/2014 at 11:13hrs. Secondary Systems Asset Manager advises no further investigation required. | 330 |  | Forced | 2014
155721 | HV Equipment | CB | 330KV A Bus 1-2 Section CB 5102 | Q | 2014Q1 | NEW | CB | 2014-01-07 01:06 | 2014-01-07 02:37 |  |  | CB SF6 topup | 330 |  |  | 2014
155809 |  |  | No.2 Capacitor | B | 2014Q1 | CMA | CAP | 2014-01-08 11:32 | 2014-01-08 12:54 |  |  |  | 66 |  | Forced | 2014
155812 |  |  | 932 Sydney West - Mt Druitt 132kV Line | X | 2014Q1 | SYW | TL | 2014-02-06 05:47 | 2014-02-07 16:36 |  |  |  | 132 |  |  | 2014
155963 | HV Equipment | CB | 5A2 Eraring A CB 5A22A | Q | 2014Q1 | KCR | CB | 2014-01-10 06:07 | 2014-01-10 12:30 |  |  | Advises low hydraulic oil level on blue phase of 5A2 Eraring A C.B. 5A22A. Hydraulic oil pump had been continually running. Pump shut down. Will require outage of 5A2 Eraring A C.B. 5A22A to top up hydraulic oil and bleed hydraulic system on C.B. | 500 |  |  | 2014
156016 |  |  | No.2 Generator |  | 2014Q1 | MPS, MTP | G | 2014-01-10 14:05 | 2014-01-10 15:52 |  |  |  | 23 |  |  | 2014
156017 |  |  | No.2 330kV Generator Transformer Group |  | 2014Q1 | MTP | TX | 2014-01-10 14:05 | 2014-01-10 15:52 |  | follow up required |  | 330 |  |  | 2014
156031 | External | TL | 963 Tomago330 - Taree T Hawksnest 132kV TL | Q | 2014Q1 | TRE, TOM | TL | 2014-01-12 03:28 | 2014-01-12 03:28 | At 03:28 963 Tomago to Taree tee Hawks Nest 132kV T/L tripped, Reclosed, Tripped and Locked out at Taree. 963 Tomago to Taree tee Hawks Nest 132kV T/L tripped and Reclosed at Tomago. Approx. 2MW Load Interupted during reclose time Essential Energy advised. Closed via SCADA at Taree. DTF from Taree 159.97kM | 4/02/2014 3:23:00 PM ¦ follow up required ¦ Nil. ¦ No future action required. | As the fault was located in the AusGrid owned section of the line, TransGrid was not required to patrol the line. The TARTLO at Taree was investigated initially but was not pursued as the protection scheme has operated as expected on subsequent trips (Refer FEORs 2014-F-0012 and 2014-F-0025). | 132 |  |  | 2014
156034 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2014Q1 | GRF | TL | 2014-01-12 08:43 | 2014-01-12 08:43 |  | follow up required |  | 33 |  |  | 2014
156035 |  |  | 893/5 Forbes - Payten's Bridge 66kV Line |  | 2014Q1 | FB2 | TL | 2014-01-12 10:19 | 2014-01-12 10:19 |  | follow up required |  | 66 |  |  | 2014
156038 |  |  | 9E4 Sydney East - Willoughby tees Castle Cove & Mosman 132kV Line |  | 2014Q1 | SE1 | TL | 2014-01-12 23:06 | 2014-01-13 00:58 | Ausgrid advised that they found a Possum in a transformer at Castle Cove. | follow up required |  | 132 |  |  | 2014
156087 | External | TL | 963 Tomago330 - Taree T Hawksnest 132kV TL | Q | 2014Q1 | TRE, TOM | TL | 2014-01-14 04:42 | 2014-01-14 04:42 | DTF from Taree 159.97kM | 4/02/2014 2:58:00 PM ¦ follow up required ¦ Nil. ¦ Nil. | As the fault was located in the AusGrid owned section of the line, TransGrid was not required to patrol the line. TransGrid's System Operator advised AusGrid's System Operator that the fault location had been calculated as being in AusGrid's section of the line. AusGrid confirmed that it would arrange for a patrol of its section of the line. | 132 |  |  | 2014
156108 | HV Equipment | Cap | No.1 Capacitor | Z | 2014Q1 | NEW | CAP | 2014-01-14 06:42 | 2014-01-18 11:54 | Substation Misc Equip Fail Alarm received on SCADA followed by No1 Capacitor CB 4712 opening. Capacitor cans replaced and capacitor returned to service. | 30/01/2014 10:12:00 AM ¦ follow up required ¦ Nil. ¦ No further action required. | Testing was carried out on the capacitor bank on Saturday 18/01/2014, which revealed a faulty capacitor can. There were no other signs of damage in the switchbay. The capacitor can is an ABB CHF102, purchased under Contract 3153. The faulty capacitor can was replaced. The bank was successfully re-tested and then returned to service on 18/01/2014 at 12:54hrs. | 132 |  | Fault | 2014
156153 | Wiring/Testing Error | T/C | No.2 Transformer 330/132/11kV | Z | 2014Q1 | WG1 | TX | 2014-01-14 13:45 | 2014-01-14 20:06 |  | 8/04/2014 8:14:00 AM ¦ follow up required | No.2 Transformer at Wagga 330kV Substation tripped. NCM advised. Called Russel Ubrehien to dispatch staff to investigate. 14:05 Will Kroker on site. Advises will investigate and advise back. Received following protection details: No.1 Protection - 86 Relay - MultiTrip 87 Tx Diff relay Flag - T/C Overpressure B-Phase Trip - Flag Alarm - Flag No.2 Protection - Nil Byron Mills requests for HV access to investigate further. Suspects over presure device activation on B-Ph Tap Changer may have cause the trip. On investigation a damaged wire was found in the Tap Change Over Pressure switch which was caused by being clamped when cover Re-Fitted following Maintenance. Wire has been replaced and pressure switch tested OK. Transformer returned to service. | 330 |  | Fault | 2014
156158 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2014Q1 | MRE | TL | 2014-01-14 17:03 | 2014-01-14 17:03 | No storms in the area. Cause unkown. | follow up required |  | 66 |  |  | 2014
156199 | HV Equipment | VT | 973 Yass - Cowra 132kV TL | E | 2014Q1 | CW2, YSN | TL | 2014-01-15 10:14 | 2014-01-15 12:11 |  |  | Advises 973 Yass Line C.V.T. checked at Cowra 132kV Substation and O.K. to remain in service. 973 Yass placed on load at Cowra and requests reclose made auto at Yass. At Yass :- 973 Cowra C.B.. 9732 - PLACED ON AUTO RECLOSE VIA SCADA @ 1212 hours. S.O./N and NCM advised. | 132 |  | Forced | 2014
156207 | HV Equipment | Cap | No.1 Static VAR Compensator | Z | 2014Q1 | AR1 | SVC | 2014-01-15 12:49 | 2014-01-15 17:46 | 3 load bangs heard by staff working in yard. | 20/01/2014 9:41:00 AM ¦ follow up required ¦ Nil. ¦ No further action required. | Upon investigation, a faulty capacitor can was found in the Blue phase - Red phase leg of TSCB. The capacitor can is an ABB CHD780 purchased under Contract 1020. The capacitor can was replaced and the SVC returned to service on 15/01/2014 at 18:46hrs. | 330 |  | Fault | 2014
156215 | LV/MECH Fail | CB | No.1 Capacitor | Z | 2014Q1 | VYD | CAP | 2014-01-15 17:19 | 2014-01-16 18:43 |  |  | Advises no protection operation on No.1 Capacitor. Inspection of C.B. 4712 OK. Attempted to close C.B. 4712 via SCADA. C.B. failed to close. Requested Stuart to attempt to close C.B. 4712 via site HMI. C.B. failed to close and SCADA logged a C.B. CLOSE and C.B. OPEN event. NCM advised and THEOS package 57365 created to investigate control of C.B. 4712. Advised by Stuart Cameron over the telephone that after having checked and tightened some mechanical parts on the CB, it was subsequently serviceable. CB shooting through on site. High heat day >40 degC. With CB isolated from system, CB closed ok, when system reconnected, CB operated ok. Open close indicator lose but not fouling - was tightened but not thought to contribute to op issue. Erraneous operation which could not be identified and has not repeated since.This may need follow up. ABBLTB type CB. There has been an issue raised on this type with bearing problems - related? | 132 | Known ongoing problem with this model of CB. Subs Asset Mgr advises to be closed. | Fault | 2014
156230 |  |  | 96F Stroud - Tomago 330 132kV TL | X | 2014Q1 | TOM | TL | 2014-01-19 07:00 | 2014-01-19 17:13 |  |  |  | 132 |  |  | 2014
156268 |  |  | No.1 & No.2 Gas Turbines 22kV CB 2212 |  | 2014Q1 | BKH | G | 2014-01-16 17:21 | 2014-01-16 18:10 | Trip initiated by No.2 Gas Turbine overvoltage protection at Essential Energy's Broken Hill Gas Turbine Station. | follow up required |  | 11 |  |  | 2014
156269 |  |  | No.1 Gas Turbine |  | 2014Q1 | BKH | G | 2014-01-16 17:21 | 2014-01-16 18:10 |  |  |  | 11 |  |  | 2014
156270 |  |  | No.2 Gas Turbine |  | 2014Q1 | BKH | G | 2014-01-16 17:21 | 2014-01-16 18:10 |  |  |  | 11 |  |  | 2014
156271 |  |  | No.1 & No.2 Gas Turbines 22kV CB 2212 |  | 2014Q1 | BKH | G | 2014-01-16 18:28 | 2014-01-16 18:28 | Trip caused by overvoltage protection on No.2 Gas Turbine. | follow up required |  | 11 |  |  | 2014
156272 |  |  | No.1 Gas Turbine |  | 2014Q1 | BKH | G | 2014-01-16 18:28 | 2014-01-16 18:28 |  |  |  | 11 |  |  | 2014
156273 |  |  | No.2 Gas Turbine |  | 2014Q1 | BKH | G | 2014-01-16 18:28 | 2014-01-16 18:28 |  |  |  | 11 |  |  | 2014
156282 |  |  | M5 Murray - Murray 1 330kV TL | X | 2014Q1 | MUR | TL | 2014-01-23 07:46 | 2014-01-23 11:14 |  |  |  | 330 |  |  | 2014
156317 | Staff Error | Bus | 66kV Bus No.1 Section | Q | 2014Q1 | WW2 | BB | 2014-01-18 10:06 | 2014-01-18 12:35 | Trip was caused by 800 Railway feeder overhead earth wire dropping on to busbar below during cut over from Old Wallerawang to New Wallerawang. | 31/01/2014 9:47:00 AM ¦ follow up required ¦ Nil ¦ Nil | Advised that the cause of the trip was the overhead being cut away had dropped onto busbar below. No one is hurt. I advised Mark to ensure staff remain well clear of area until bus is isolated and earthed to allow safe removal of earth wire. Mark confirm earth wire was blown off by the phase it contacted but still resting on other two phases, so HV access required. The incident is under investigation and is being followed up through an INS. | 66 |  |  | 2014
156318 |  |  | 800 Wallerawang 132 - Railway 66kV Line |  | 2014Q1 | WWS | TL | 2014-01-18 10:06 | 2014-01-18 12:35 |  |  |  | 66 |  |  | 2014
156319 |  |  | 823 Wallerawang 132 - Portland 66kV Line |  | 2014Q1 | WWS | TL | 2014-01-18 10:06 | 2014-01-18 12:35 |  |  |  | 66 |  |  | 2014
156320 |  |  | 856 Wallerawang 132 - Oberon Tee Lillyvale 66kV Line |  | 2014Q1 | WWS | TL | 2014-01-18 10:06 | 2014-01-18 12:35 |  |  |  | 66 |  |  | 2014
156321 |  |  | 857 Wallerawang 132 - Lithgow 66kV Line |  | 2014Q1 | WWS | TL | 2014-01-18 10:06 | 2014-01-18 12:35 |  |  |  | 66 |  |  | 2014
156322 | Lightning/Storm | TL | O1 Upper Tumut - Canberra 330kV TL | Q | 2014Q1 | CA1, UT1 | TL | 2014-01-18 17:38 | 2014-01-18 17:38 | Indji application showing significant lightning activity in the vicinity of Tower 182. | 17/03/2014 3:28:00 PM ¦ follow up required ¦ Nil. ¦ A close inspection of the line section will be carried out in the next aerial inspection. | On Saturday 18/01/2014 at 18:38hrs, the 330kV No.1 transmission line from Upper Tumut to Canberra tripped and reclosed at both ends of the line. Thunderstorms were reported at the time of the trip. The Indji system recorded a lightning strike at 18:39hrs near structure 183 and several other lightning strikes around the time of the trip between structures 172 and 184. No protection details or DTF information was recorded. | 330 |  |  | 2014
156346 | Bushfire | TL | 3 Lower Tumut - Yass 330kV TL | Z | 2014Q1 | LT1, YSN | TL | 2014-01-18 20:20 | 2014-01-20 09:22 | Protection details include flagging for FEORs 2014-F-0023 and 2014-F-0024. Indji application showing fire at Sturgess Trail and Snubba Road (~ 4.5 km NE of Batlow) in near vicinity of T/L. Re-issue FEOR as 3 T/L Returned to service. | 17/03/2014 4:32:00 PM ¦ follow up required ¦ Nil. ¦ Nil. | On Saturday 18/01/2014 at 21:20hrs, the 330kV No.3 transmission line from Lower Tumut to Yass tripped, reclosed, tripped and locked out at both ends of the line. Protection at Lower Tumut 330kV Substation indicated a zone 1 phase to earth fault while protection at Yass 330kV Substation indicated a zone 4 phase to earth fault. The distance to fault was calculated to be between 19.36km and 32.06km from Lower Tumut 330kV Substation which is between structures 53 and 80. Bushfires were present in the area at the time of the trip in proximity to the line. The Indji application indicated a fire at Sturgess Trail and Snubba Road (~ 4.5 km NE of Batlow) in near vicinity of the transmission line. The weather was reported as very windy. An aerial patrol of the line was conducted and no evidence of damage was observed. | 330 |  | Fault | 2014
156348 |  |  | 828 Tumut - Gundagai 66kV Line |  | 2014Q1 | TU2 | TL | 2014-01-18 20:46 | 2014-01-18 20:46 | Essential Energy field staff reported flash over on 828 Tumut to Gundagai 66kV Feeder T/L in area where fires burning. | follow up required |  | 66 |  |  | 2014
156349 | Bushfire | TL | 3 Lower Tumut - Yass 330kV TL | Q | 2014Q1 | LT1, YSN | TL | 2014-01-18 19:38 | 2014-01-18 19:38 | Protection details include flagging for FEORs 2014-F-0021 and 2014-F-0024. C.B. 32A closed via SCADA at Lower Tumut following successful reclose of C.B. 32B. Indji application showing fire at Sturgess Trail and Snubba Road (~ 4.5 km NE of Batlow) in near vicinity of T/L. | 8/04/2014 10:34:00 AM ¦ follow up required ¦ Nil. ¦ Nil. | On Saturday 18/01/2014 at 20:38hrs, the 330kV No.3 transmission line from Lower Tumut to Yass tripped and reclosed at both ends of the line. Protection at Lower Tumut 330kV Substation indicated a zone 1 phase to earth fault while protection at Yass 330kV Substation indicated a zone 4 phase to earth fault. The distance to fault was calculated to be between 19.36km and 32.06km from Lower Tumut 330kV Substation which is between structures 53 and 80. Bushfires were present in the area at the time of the trip in proximity to the line. The Indji application indicated a fire at Sturgess Trail and Snubba Road (~ 4.5 km NE of Batlow) in near vicinity of the transmission line. The weather was reported as very windy. An aerial patrol of the line was conducted and no evidence of damage was observed. | 330 |  |  | 2014
156350 | Bushfire | TL | 3 Lower Tumut - Yass 330kV TL | Q | 2014Q1 | LT1, YSN | TL | 2014-01-18 18:56 | 2014-01-18 18:56 | Protection details include flagging for FEORs 2014-F-0021 and 2014-F-0023. C.B. 32A closed via SCADA at Lower Tumut following successful reclose of C.B. 32B. Indji application showing fire at Sturgess Trail and Snubba Road (~ 4.5 km NE of Batlow) in near vicinity of T/L. | 8/04/2014 10:35:00 AM ¦ follow up required ¦ Nil. ¦ Nil. | On Saturday 18/01/2014 at 19:56hrs, the 330kV No.3 transmission line from Lower Tumut to Yass tripped and reclosed at both ends of the line. Protection at Lower Tumut 330kV substation indicated a zone 1 phase to earth fault while protection at Yass 330kV substation indicated a zone 4 phase to earth fault. The distance to fault was calculated to be between 19.36km and 32.06km from Lower Tumut 330kV Substation which is between structures 53 and 80. Bushfires were present in the area at the time of the trip in proximity to the line. The Indji application indicated a fire at Sturgess Trail and Snubba Road (~ 4.5 km NE of Batlow) in near vicinity of the transmission line. The weather was reported as very windy. An aerial patrol of the line was conducted and no evidence of damage was observed. | 330 |  |  | 2014
156351 | External | TL | 963 Tomago330 - Taree T Hawksnest 132kV TL | Q | 2014Q1 | TRE, TOM | TL | 2014-01-19 04:43 | 2014-01-19 04:43 | DTF - 159.26km from Taree DTF - 9.3km from Tomago | 4/02/2014 3:51:00 PM ¦ follow up required ¦ Nil. ¦ No future action required. | As the fault was located within the AusGrid owned section of the line, TransGrid was not required to carry out a patrol. AusGrid's System Operator advised that a patrol of it's section of the line had been carried out following earlier outages of this line (refer FEORs 2014-F-0001, 2014-F-0008 and 2014-F-0025), but failed to find a cause of the previous outages. The AusGrid Operator confirmed that another patrol would be arranged as a result of this latest outage. | 132 |  |  | 2014
156364 | Unknown | Cap | No.2 Capacitor | Q | 2014Q1 | YA2 | CAP | 2014-01-19 18:31 | 2014-01-20 14:09 | Essential Energy staff attended SS and it appears No.2 Cap has tripped on phase unbalance TG staff investigated and No2 Cap has been returned to service. | 31/01/2014 2:31:00 PM ¦ follow up required ¦ Protection to check relays in near future. | Essential Energy staff attended SS and it appears No.2 Cap has tripped on phase unbalance TG staff investigated and No2 Cap has been returned to service. Protection to check relays in near future. 415v injection done to cap. Measured values: Red Phase 1.128A @ 237.0V White Phase 1.137A @ 239.6V Blue Phase 1.134A @ 239.4V Capacitance of bank for each limb was measured: R-E = 15.0uF W-E= 15.1uF B-E= 15.4uF No problems identified with balance so bank was restored to service and we got: 35.7°C No.1 Protection: R = 179.3mA W= 179.1mA B= 179.3mA No.2 Protection: R = 179.7mA W= 179.5mA B= 180.0mA Note the RTI says the phase unbalance is 150mA after 6 seconds delay. Protection Design reports that the trip was due to system transients. No revision to protection settings required. | 33 |  |  | 2014
156387 |  |  | 94J Wellington - Dubbo 132kV Line |  | 2014Q1 | WL1 | TL | 2014-01-20 10:14 | 2014-01-20 19:53 | Essential Energy request 94J to be deenergised due to severly leaking CVT at Dubbo. | follow up required |  | 132 |  |  | 2014
156438 |  |  | U1 Upper Tumut - Tumut 1 330kV TL | X | 2014Q1 | UT1 | TL | 2014-01-30 06:28 | 2014-01-31 13:52 |  |  |  | 330 |  |  | 2014
156474 |  |  | 963 Tomago330 - Taree T Hawksnest 132kV TL | X | 2014Q1 | TRE, TOM | TL | 2014-01-22 06:48 | 2014-01-22 14:24 |  |  |  | 132 |  |  | 2014
156476 |  |  | 84B Finley - Finley 66 66kV Line |  | 2014Q1 | FNY | TL | 2014-01-21 14:20 | 2014-01-21 17:59 | Micom relay - Alarm Led's on 99A Uranquinty, 9R4 Mulwala and 9R3 Deniliquin feeders also. John Hicks advised of protection details advised ok to return to service | 30/01/2014 4:20:00 PM ¦ follow up required |  | 66 |  |  | 2014
156477 | Bushfire | TL | 3 Lower Tumut - Yass 330kV TL | Z | 2014Q1 | LT1, YSN | TL | 2014-01-21 18:04 | 2014-01-22 12:51 | Site Incident record sheet added to notes in outage. | follow up required ¦ Nil. ¦ The outage has been noted for close inspection during the next routine aerial patrol of the line. | Advises aerial patrol of 3 Yass to Lower Tumut 330 kV T/L around DTF appears to be normal and no obvious signs of fault. T/L can return to service. Prot Tech John Hicks investigating Yass 330kV Substation 3TL Prot Stub mode operated alarm. Reason. Unknown reason why auto-reclose was not attempted. Secondary Systems Asset Manager advises no further investigation required. | 330 |  | Fault | 2014
156478 |  |  | No.4 330kV Generator Transformer Group |  | 2014Q1 | LD1 | TX | 2014-01-21 20:13 | 2014-01-23 22:49 |  | follow up required |  | 330 |  |  | 2014
156479 |  |  | No.5 Taree - Council Kanangra Drive 33kV Line |  | 2014Q1 | TRE | TL | 2014-01-22 03:27 | 2014-01-22 03:27 |  | follow up required |  | 33 |  |  | 2014
156521 |  |  | No.9 Transformer 132/66/11kV | N | 2014Q1 | WW2 | TX | 2014-01-18 10:06 | 2014-01-18 12:35 |  |  |  | 132 |  |  | 2014
156586 |  |  | L1 Lower Tumut - Tumut 3 330kV TL | X | 2014Q1 | LT1 | TL | 2014-02-04 07:01 | 2014-02-07 09:22 |  |  |  | 330 |  |  | 2014
156656 |  |  | OX1 Buronga - Red Cliffs 220kV TL | X | 2014Q1 | BRG | TL | 2014-02-15 06:11 | 2014-02-15 20:59 |  |  |  | 220 |  |  | 2014
156762 |  |  | M5 Murray - Murray 1 330kV TL | X | 2014Q1 | MUR | TL | 2014-02-04 06:55 | 2014-02-04 11:04 |  |  |  | 330 |  |  | 2014
156777 |  |  | 8C1 Molong - Cumnock Tee Orange West 66kV Line |  | 2014Q1 | MOL | TL | 2014-01-26 05:05 | 2014-01-26 05:05 | SCADA Alarm Protection Relays Operated alarm from Molong only. CB indication did not change. Customer advised that reclosers have operated on 8C1. Protection flagging added. | follow up required |  | 66 |  |  | 2014
156787 | Condition Monitor | TX | No.3 Transformer 330/132/11kV | E | 2014Q1 | WDL | TX | 2014-01-27 08:13 | 2014-01-27 10:13 | Condition Monitor L1 Alarm received on SCADA. Oil levels checked OK by field staff. Alarms reset OK. OCE OK'd RTS of TX. | 31/01/2014 7:57:00 AM ¦ follow up required | Protection relays checked and not alarming or operated. Condition monitoring devices checked: Hydran- 28ppm not alarming Luxtron- Decommissioned Dobel IDD- no alarms Tx temps WTI-LV 37 max 56 WTI-HV 38 max 57 Oil 37 max 52 Main tank oil level 50% = 60deg Tapchanger oil level 25% = 35deg Tapchanger on tap 8 Range min 6 max 13 All alarms reset on scada and Tx returned to service. Condition monitored for 1 hour with no obvious change to temps or oil levels. | 330 |  | Forced | 2014
156788 | HV Equipment | CB | 93L Sydney West - Guildford 132kV Line | Q | 2014Q1 | SYW | TL | 2014-01-27 16:11 | 2014-01-27 17:39 |  |  | CB SF6 Topup | 132 |  |  | 2014
156818 |  |  | 963 Tomago330 - Taree T Hawksnest 132kV TL | X | 2014Q1 | TRE, TOM | TL | 2014-01-30 06:26 | 2014-01-30 15:14 |  |  |  | 132 |  |  | 2014
156833 | Unknown | TL | 944 Orange North - Wallerawang 132kV Line | Z | 2014Q1 | ONO, WWS | TL | 2014-01-28 14:43 | 2014-01-29 16:17 | Distance to fault 86.08km from Orange North CB operation at WWS: 14:42:53 CB 9442 -OPENED- 14:42:57 CB 9442 -CLOSED- 14:42:57 CB 9442 -OPENED- 14:43:00 CB 9442 -CLOSED- 14:43:00 CB 9442 -OPENED- | 17/06/2014 10:42:00 AM ¦ follow up required ¦ Nil ¦ The final report of the investigating commitee provides recommendations on follow up actions. Action items will be raised and tracked through IMS. | On 28/1/2014 at14:42, feeder 944 tripped out of service due to a pole failure (structure 74) ~30km from Wallerawang 132kV Substation (NEW). CB 9442 at Orange North 132kV Substation tripped and remained out of service. CB 9442 at Wallerawang 132kV Substation (NEW) sequence TARTLO - followed by an additional close and trip. A committee has been convened to investigate and provide a report on the incident - outcome pending. Follow up required to determine the failure of the anti-pumping circuit and use of Serck CB routine. | 132 |  | Fault | 2014
156919 |  |  | No.10 Yanco - Kamarah (No.10 Council) |  | 2014Q1 | YA2 | TL | 2014-01-29 18:05 | 2014-01-29 19:06 | EsE staff utilised in restoration. | follow up required |  | 33 |  |  | 2014
156920 |  |  | 893/1 Cowra - Grenfell 66kV Line |  | 2014Q1 | CW2 | TL | 2014-01-29 21:28 | 2014-01-29 21:28 | Distance to fault 140.9m | follow up required |  | 66 |  |  | 2014
156939 |  |  | No.5 Reactor | B | 2014Q1 | KCR | RX | 2014-01-31 05:27 | 2014-01-31 15:36 |  |  |  | 330 |  | Forced | 2014
157095 |  |  | 836 Murrumburrah - Cootamundra 66kV Line |  | 2014Q1 | MRU | TL | 2014-02-01 05:05 | 2014-02-01 05:05 |  | follow up required |  | 66 |  |  | 2014
157148 |  |  | 963 Tomago330 - Taree T Hawksnest 132kV TL | Y | 2014Q1 | TRE, TOM | TL | 2014-02-01 18:51 | 2014-02-02 15:12 | Essential energy lost 4.5MW of customer load at their Hawks Nest Sub station at 18:51 hrs load restored via back feed at 20:15 hrs HVPRI created to I&E 963 Ausgrid Advised 963 Isolated and earthed at 22:07 Hrs 22:48 hrs Ausgrid advised a pole head had failed at Str 157 and repairs would take several hours TL returned to service at 15:12 HRS EST on 02/02/14 following repairs within Ausgrid system. Reclose operation at Taree requires further investigation (Ireg 11689) | 6/02/2014 1:43:00 PM ¦ follow up required ¦ Nil. ¦ No future action required. |  | 132 |  |  | 2014
157198 | Protection | Prot | 5A2 Eraring - Kemps Creek 500kV TL | E | 2014Q1 | ER0, KCR | TL | 2014-02-03 00:31 | 2014-02-03 02:13 | T/L offloaded itself at Kemps creek end only. T/L remained alive in to Kemps Creek. T/L was de-energised during preliminary investigation. T/L returned to service at 02:13hrs. Further investigation of No.1 protection required. | follow up required | T/L offloaded itself at Kemps creek end only. T/L remained alive in to Kemps Creek. T/L was de-energised during preliminary investigation. T/L returned to service at 02:13hrs. Further investigation of No.1 protection required. Microhmo Relay Faulty and replaced under Work Order 317561. Spares still available. | 500 | Sec Systems Asset Mgr advises may be closed due to faulty relay being replaced | Forced | 2014
157242 |  |  | 882 Narrabri - Wee Waa 66kV Line |  | 2014Q1 | NB2 | TL | 2014-02-03 13:39 | 2014-02-03 13:39 | No Loss of load recorded. Parallel supply via the 879 Wee Waa Feeder | follow up required |  | 66 |  |  | 2014
157247 | LV/MECH Fail | CB | 966 Armidale - Koolkhan 132kV TL | Q | 2014Q1 | AR1, KLK | TL | 2014-02-03 14:17 | 2014-02-03 16:38 |  |  | CB at Armidale end failed to close via SCADA. Requested CB closed locally via CDS switch. Failed to close via CDS switch. Further investigations locally, fault finding a latched positive on the trip coil at the CB, led to CB closing. Not requested by SO and not intended by the Staff on site. CB deemed serviceable with further investigations to be carried out during planned outage tomorrow. NCM Advised Team Leader Advised. After speaking with staff advised that he would like the CB to be taken OS for further testing to be carried out. Team Leader will speak with his Manager and inform him of situation. Graham Francis confirmed cb to come out of service for further testing. NCM advised See pack 57874 for next outage. Graham Francis advised CB has been returned to service. Need to follow up with Northern | 132 | Sec Systems Asset Mgr advises needs further testing. Now resolved. |  | 2014
157253 |  |  | 712 Port Macquarie - Rocks Ferry 33kV Line |  | 2014Q1 | PMQ | TL | 2014-02-03 20:45 | 2014-02-03 20:45 |  | follow up required |  | 33 |  |  | 2014
157460 | Relay Setting | Prot | No.3 Capacitor | Z | 2014Q1 | DNT | CAP | 2014-02-04 12:18 | 2014-02-04 13:04 | No sign of cause of trip, all gear OK, when protection reset relay 51B/60 indicated IO >> trip 54% 0.01s, discussed with maintenance regarding attempt to place I/S, done successfully. Requires protection follow up. | 12/03/2014 10:38:00 AM ¦ follow up required | Protection settings reviewed. New RTI's issued and completed with the following comments. DNTC132-3-1.S03 Calculated Io Highset [Io>>] time delay revised to 0.10 seconds to desensitise protection element due to CB restrike/failure. DNTC132-3-2.S04 Calculated Io Highset [50N-2] time delay revised to 0.10 seconds to desensitise protection element due to CB restrike/failure. Time clock left at internal clock. Secondary Systems Asset Manager advises no further investigation required. | 132 |  | Fault | 2014
157461 |  |  | 828 Tumut - Gundagai 66kV Line |  | 2014Q1 | TU2 | TL | 2014-01-18 19:50 | 2014-01-18 19:50 |  | follow up required |  | 66 |  |  | 2014
157462 | LV/MECH Fail | CB | M7 Murray - Murray 1 330kV TL | Z | 2014Q1 | MUR | TL | 2014-02-03 07:44 | 2014-02-04 10:20 | C.B.. M72 made RFS with limited operation after pole discrepancy issue on red phase, M7 Murray to Murray 1 P.S. synchronised with Unit 7/8 via C.B.. M72 & then M7 T/L left energised with temporary cooling on SHL Unit 7/8 Transformers until further notice. | 12/03/2014 10:52:00 AM ¦ follow up required ¦ CBM72 To be replaced 18/3/14-4/4/14. | CBM72 found to have worn latching mechanism. | 330 |  | Fault | 2014
157463 | Animal/Bird | Reg | No.1 Transformer 132/66/11kV | Z | 2014Q1 | CMA | TX | 2014-02-04 22:05 | 2014-02-06 10:46 |  | 8/04/2014 8:25:00 AM ¦ follow up required | On investigation a Rat was found across No1 Regulator 11kV terminals. A full set of diagnostic test were performed, all OK. Transformer returned to service. | 132 |  | Fault | 2014
157464 | Relay Setting | Prot | No.3 Capacitor | Z | 2014Q1 | DNT | CAP | 2014-02-04 20:07 | 2014-02-09 09:20 | No.3 Capacitor tripped when taking No.2 Capacitor out of service. No.3 Capacitor tripped earlier in the day and was later returned to service (refer to FEOR 2014-F-0039/1). Clearance given to make No.3 Capacitor available for service at 0920 hours on 09/02/2014. | 12/03/2014 11:50:00 AM ¦ follow up required | Protection settings reviewed. New RTI's issued and completed with the following comments. DNTC132-3-1.S03 Calculated Io Highset [Io>>] time delay revised to 0.10 seconds to desensitise protection element due to CB restrike/failure. DNTC132-3-2.S04 Calculated Io Highset [50N-2] time delay revised to 0.10 seconds to desensitise protection element due to CB restrike/failure. Time clock left at internal clock See follow up 2014-F-0039-802/1. Secondary Systems Asset Manager advises no further investigation required. | 132 |  | Fault | 2014
157519 |  |  | Broken Hill - Cockburn 22kV Line |  | 2014Q1 | BKH | TL | 2014-02-05 08:06 | 2014-02-05 09:06 | Fault caused by bird strike | follow up required |  | 22 |  |  | 2014
157605 |  |  | No.1 Transformer 132/66/11kV | B | 2014Q1 | MRU | TX | 2014-02-19 09:52 | 2014-02-19 11:03 |  |  |  | 132 |  | Forced | 2014
157612 |  |  | No.3 Transformer 330/132/16kV | B | 2014Q1 | CA1 | TX | 2014-02-07 07:21 | 2014-02-07 08:38 |  |  |  | 330 |  | Forced | 2014
157667 | HV Equipment | SD | No.2 Capacitor | Q | 2014Q1 | GRF | CAP | 2014-02-06 13:12 | 2014-05-06 16:11 | NO.2 Capacitor - Blue Phase 33kV SGD failed catastrophically. No other damaged observed to adjacent HV plant | 12/03/2014 12:02:00 PM ¦ follow up required | Blue Phase 33kV Surge Diverter replaced. Meggered OK. Returned to service 7/2/14. | 33 |  |  | 2014
157757 |  |  | U5 Upper Tumut - Tumut 2 330kV TL | X | 2014Q4 | UT1 | TL | 2014-10-07 07:02 | 2014-11-12 15:17 |  |  |  | 330 |  |  | 2014
157821 |  |  | 999 Yass - Cowra 132kV TL | E | 2014Q1 | CW2, YSN | TL | 2014-02-08 10:38 | 2014-03-10 06:09 |  |  | Received request from SO North to De-energise 999 Cowra to Yass 132 kV T/L at Yass 330kV Substation , due to temperature restrictions on 999 Cowra line. 999 Cowra C.B..9992 - OPEN via SCADA - completed at 10:39 hrs | 132 |  | Forced | 2014
157834 | LV/MECH Fail | Cont | 890 Murrumburrah - Young 66kV Line | Q | 2014Q1 | MRU | TL | 2014-02-10 11:41 | 2014-02-10 19:19 |  |  | Request carry out following log entry switching: 890 Young C.B.. 8902 - CHECK OFF LOAD, OPEN Advises operated CDS switch to open C.B. Advised indicating C.B.. 8902 still closed, request inspect C.B.. 8902 & confirm status. 08:02hrs Advised by Kai C.B.. 8902 still closed locally. Advised OK, will call out SSMF to assist. Advised NCM & Gary Morgan, no staff in today. Advised OK, will call S/by fitter. 08:07hrs Contacted Broughton Webb to attend, during conversation received No.110V Battery Earth & No.1 110V Batt. Chgr Fuse alarms. Checked with Kai & he had attempted another open on C.B.. 8902 via CDS. Requested inspect C.B. Control cabinet for possible burnt out trip coil. 08:15hrs Kai advises No.1 Trip coil & assoc. Wiring severly damaged. Broughton advised & will require at least 1 trip coil. 10:15hrs Advised by Broughton on site, discussed & will open C.B.. 8902 locally, reuested check no load & open. Advises done. During RTS of 890 Murrumburrah to Young 66kV Feeder C.B.. 8902 by local operation C.B. Indicated on SCADA closed, open, closed & opened. Confirmed no protection operation, was actually caused by staff closing a second time after C.B. Didn't latch. NCM & SO/E.E. Advised. 18:25hrs Requested Broughton carry out following log entry switching: 890 Young C.B.. 8902 Reclose - PLACE ON N/A 890 Young C.B.. 8902 - CHECK OPEN 890 Young Bus Isol. 8903 - O & LO 890 Young Line Isol. 8901 - O & LO & investigate cause. 18:59hrs Broughton advised a defective supervisory relay held trip signal on cintiously and was causing the 890 Young C.B.. 8902 to Trip on closing. Supervisory Link has been Isolated no SCADA operation of 890 Young C.B.. 8902 available. 19:04hrs Requested Broughton carry out following log entry switching: 890 Young C.B.. 8902 - CHECK OPEN 890 Young Bus Isol. 8903 - UL & C 890 Young Line Isol. 8901 - UL & C 890 Young C.B.. 8902 Reclose - PLACE ON Auto Advised completed 19:17 Secondary Systems Asset Manager advises no further investigation required. | 66 |  |  | 2014
157841 |  |  | U5 Upper Tumut - Tumut 2 330kV TL | X | 2014Q1 | UT1 | TL | 2014-02-20 07:00 | 2014-02-25 11:29 |  |  |  | 330 |  |  | 2014
157851 | HV Equipment | CT | 83A Murrumburrah - Murrumburrah 66kV 66kV Line | Q | 2014Q1 | MRU | TL | 2014-02-10 17:09 | 2014-02-11 13:09 | 83A Fdr taken O/S due to noise eminating from white phase C.T., found issue with DDF test link, repaired, C.T. tested OK & now available for service. | 12/03/2014 1:01:00 PM ¦ follow up required ¦ Check other similar CTs as per Maintenance Alert for DLA Links Following Problem at Eraring. | DDF link found to be badly burnt. Link replaced, terminals cleaned and CT tested OK. Other phases checked with no problems. | 66 |  |  | 2014
157852 | HV Equipment | CT | 66kV Bus Section 3 | Q | 2014Q1 | BER | BB | 2014-02-10 21:35 | 2014-02-10 23:31 | P/TL John confirmed protection details indicated a genuine bus bar fault and the protection had operated correctly. Confirmed with SSMF Ken that he had completed several visiual inspections on No.3 section 66 busbar and was unable to find a cause for the bus fault. All Essential energy load was restored No.3 section 66 busbar | 17/06/2014 11:08:00 AM ¦ follow up required ¦ Nil ¦ The final report of the Commitee of Enquiry will provide recommendations on follow up actions. Action items will be raised and tracked through IMS. | Protection flagging indicated a red phase to ground fault. An invesigation of the bus section and connected bays found no conclusive evidence of a fault. Possible flashover identified on red phase upper treminal of arc gaps associated with No.3 Capacitor bank disconnector. Outage planned for closer inspection and measurement of the rod gap identified no sign of arcing on the lower arc gap terminal. An invesitgation of POW operation of the capacitor bank was planned with an outage on 23/5, followed by in-service testing on the same day. See W/O 319099. During in-service testing, the red phase CT failed explosive. A Commitee of Equiry has been convened by NP&P/AP/Substation Systems to investigate and report on the Cap CT failure. | 66 |  |  | 2014
157853 |  |  | No.3 Transformer 132/66/11kV | Z | 2014Q1 | BER | TX | 2014-02-10 21:35 | 2014-02-10 23:31 |  |  |  | 132 |  | Fault | 2014
157854 |  |  | 66kV Bus Section CB 3122 |  | 2014Q1 | BER | CB | 2014-02-10 21:35 | 2014-02-10 23:31 |  |  |  | 66 |  |  | 2014
157855 |  |  | No.3 Capacitor | Z | 2014Q1 | BER | CAP | 2014-02-10 21:35 | 2014-02-10 23:31 |  |  |  | 66 |  | Fault | 2014
157856 |  |  | 80U Beryl - Ulan 66kV Line |  | 2014Q1 | BER | TL | 2014-02-10 21:35 | 2014-02-10 23:31 |  |  |  | 66 |  |  | 2014
157857 |  |  | 852 Beryl - Dunedoo 66kV Line | S | 2014Q1 | BER | TL | 2014-02-10 21:35 | 2014-02-10 23:31 |  |  |  | 66 |  |  | 2014
157969 |  |  | 250 Sydney North - Berowra 132kV Line | X | 2014Q1 | SYN | TL | 2014-02-17 16:19 | 2014-02-18 16:10 |  |  |  | 132 |  |  | 2014
158090 |  |  | 828 Mt Piper 132 - Portland tee BCSC 66kV Line |  | 2014Q1 | MPP | TL | 2014-02-13 17:29 | 2014-02-13 17:29 |  | follow up required |  | 66 |  |  | 2014
158198 |  |  | 912 Sydney South - Port Hacking 132kV Line |  | 2014Q1 | SYS | TL | 2014-02-15 05:18 | 2014-02-15 12:31 | protection flags added | follow up required |  | 132 |  |  | 2014
158206 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2014Q1 | CW2 | TL | 2014-02-15 06:13 | 2014-02-15 13:48 |  | follow up required |  | 66 |  |  | 2014
158207 | Animal/Bird | Cap | No.1 Capacitor | Z | 2014Q1 | TOM | CAP | 2014-02-15 09:16 | 2014-02-19 10:23 | Cap RTS after investigation. | 21/02/2014 8:36:00 AM ¦ follow up required ¦ Nil. ¦ No future action is required. | Maintenance staff carried out an inspection of the Capacitor Bank on Wednesday 19/02/2014. The outage was found to have been caused by a flashover on the white phase of Capacitor Bank 1A due to bird activity. A dead bird was found in the area, which was subsequently removed. Capacitance measurements were taken to confirm that the Capacitor Bank was adequately balanced, then the Capacitor Bank was returned to service at 11:23hrs. | 330 |  | Fault | 2014
158208 |  |  | 845 Queanbeyan - Fyshwick 66kV Line |  | 2014Q1 | QBY | TL | 2014-02-15 09:41 | 2014-02-15 09:46 |  | follow up required |  | 66 |  |  | 2014
158218 |  |  | 887 Glen Innes - Glen Innes 66kV Line |  | 2014Q1 | GNS | TL | 2014-02-15 23:54 | 2014-02-15 23:54 |  | follow up required |  | 66 |  |  | 2014
158228 | Lightning/Storm | TL | 87 Armidale - Coffs Harbour 330kV TL | Q | 2014Q1 | AR1, COF | TL | 2014-02-16 18:28 | 2014-02-16 18:28 | D/L was tripped, (SCADA trip time was 18.28.25secs) Armidale Distance to Fault No.2 Protection 70.05km Coffs Harbour Distance to Fault No.1 Protection 82.4km. No.2 Protection 79.42km | follow up required | Line 87 tripped & auto-reclosed. | 330 |  |  | 2014
158229 |  |  | No.2 330kV Reactor |  | 2014Q1 | AR1 | RX | 2014-02-16 18:28 | 2014-02-16 18:28 |  |  |  | 330 |  |  | 2014
158390 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2014Q1 | MRE | TL | 2014-02-18 15:58 | 2014-02-18 17:45 |  | follow up required |  | 66 |  |  | 2014
158420 |  |  | No.2 Transformer 330/132/11kV | X | 2014Q1 | LP1 | TX | 2014-03-20 19:25 | 2014-03-21 15:20 |  |  |  | 330 |  |  | 2014
158433 |  |  | 877 Gunnedah - Keepit PS 66kV Line |  | 2014Q1 | GN2 | TL | 2014-02-18 21:32 | 2014-02-18 21:32 |  | follow up required |  | 66 |  |  | 2014
158447 |  |  | 896 Forbes - West Jemalong 66kV Line |  | 2014Q1 | FB2 | TL | 2014-02-19 13:44 | 2014-02-19 13:44 |  | follow up required |  | 66 |  |  | 2014
158448 |  |  | 82B Queanbeyan - High St 66kV Line |  | 2014Q1 | QBY | TL | 2014-02-19 14:02 | 2014-02-19 16:34 | Weather is Stormy | follow up required |  | 66 |  |  | 2014
158459 | HV Equipment | CT | 96H Coffs Harbour - Koolkhan 132kV TL | E | 2014Q1 | COF, KLK | TL | 2014-02-19 22:12 | 2014-02-20 00:49 | SF6 Lockout alarm received via SCADA. Site HMI indicates SF6 Depleted alarm. C.T. de-energised until staff arrive on site to investigate. THEOS package 58349 created and SF6 gas topped up and line returned to service at 0049 hours on 20/02/2014. | 20/03/2014 3:05:00 PM ¦ follow up required ¦ Nil. ¦ An inspection of the CT with the SF6 camera is planned for Friday 11/04/2014 to identify the location of the leak. Once the location is identified, arrangements will then be made to carry out repairs to eliminate the leak. | Staff responding to the alarm confirmed low SF6 level on the blue phase current transformer. The CT was topped up with SF6 and the line was returned to service at 00:49hrs on 20/02/2014. The CT is a Trench SAS 145/1G, purchased on Contract Q3/99A and installed in September 2002. On Wednesday 19/02/2014 at 23:13hrs, the 132kV 96H TL from Coffs Harbour to Koolkhan was manually removed from service following the initiation of an SF6 lockout alarm from the CB 96H2 current transformers at Koolkhan. | 132 |  | Forced | 2014
158528 |  |  | No.1 Static VAR Compensator | B | 2014Q1 | AR1 | SVC | 2014-02-21 06:36 | 2014-02-21 09:56 |  |  |  | 330 |  | Forced | 2014
158534 | HV Equipment | CT | 92 Newcastle CB 922 | Q | 2014Q1 | VP1 | CB | 2014-02-20 17:14 | 2014-02-20 18:18 |  |  | CT SF6 Topup | 330 |  |  | 2014
158547 |  |  | No.1 Transformer 330/132/11kV | B | 2014Q1 | WRH | TX | 2014-02-21 11:43 | 2014-02-21 14:20 |  |  |  | 330 |  | Forced | 2014
158554 |  |  | 963 Tomago330 - Taree T Hawksnest 132kV TL | X | 2014Q1 | TRE, TOM | TL | 2014-03-10 07:03 | 2014-03-10 17:27 |  |  |  | 132 |  |  | 2014
158604 |  |  | No.3 Capacitor | E | 2014Q1 | BER | CAP | 2014-02-23 05:40 | 2014-12-11 14:00 |  |  |  | 66 |  | Forced | 2014
158630 |  |  | L3 Lower Tumut - Tumut 3 330kV TL | X | 2014Q1 | LT1 | TL | 2014-03-20 07:07 | 2014-03-20 15:09 |  |  |  | 330 |  |  | 2014
158632 | Animal/Bird | TL | 964 Pt Macquarie - Taree Tee Herons Creek 132kV TL | Q | 2014Q1 | PMQ, TRE | TL | 2014-02-24 11:13 | 2014-02-24 11:13 |  | 20/03/2014 11:13:00 AM ¦ follow up required ¦ Nil. ¦ It has been noted that a detailed inspection of the structure is to be carried out during the next routine aerial patrol. | As no obvious explanation for the outage could be determined, it was decided that a fault patrol should be carried out. It was reported to the patrol staff that a member of the public had observed a bird flying between the centre phase and earthwire at pole 242, with several locals apparently seeing a flashover occur. Inspection of pole 242 from the ground identified burn marks on the centre phase insulator. | 132 |  |  | 2014
158659 | Unknown | TL | 966 Armidale - Koolkhan 132kV TL | Q | 2014Q1 | AR1, KLK | TL | 2014-02-25 04:27 | 2014-02-25 04:27 | SCADA time 04:27:40 EST. | follow up required |  | 132 |  |  | 2014
158748 |  |  | 822 Deniliquin - Moulamein tee Deniliquin 66kV SS 66kV Line |  | 2014Q1 | DN2 | TL | 2014-02-25 16:58 | 2014-02-25 18:00 |  | follow up required |  | 66 |  |  | 2014
158749 | Lightning/Storm | TL | X5/3 Baranald - Buronga 220kV TL | Q | 2014Q1 | BRD, BRG | TL | 2014-02-25 17:20 | 2014-02-25 17:20 |  | 16/05/2014 12:55:00 PM ¦ follow up required ¦ Nil. ¦ A close inspection of the line section will be carried out in the next aerial inspection. |  | 220 |  |  | 2014
158750 |  |  | X5/3 Reactor |  | 2014Q1 | BRG | RX | 2014-02-25 17:20 | 2014-02-25 17:20 |  |  |  | 220 |  |  | 2014
158751 |  |  | 264 Beaconsfield West - Kingsford 132kV Line |  | 2014Q1 | BFD | TL | 2014-02-25 16:44 | 2014-02-25 19:52 | Requested by AusGrid to Open CB 2642 after Protection issue at Kingsford. | follow up required |  | 132 |  |  | 2014
158757 |  |  | No.5 Yanco - Whitton (No.5 Council) 33kV Line |  | 2014Q1 | YA2 | TL | 2014-02-25 23:39 | 2014-02-26 01:15 |  | follow up required |  | 33 |  |  | 2014
158834 |  |  | 893/5 Forbes - Payten's Bridge 66kV Line |  | 2014Q1 | FB2 | TL | 2014-02-26 15:50 | 2014-02-26 15:50 |  | follow up required |  | 66 |  |  | 2014
158835 |  |  | 888/1 Cooma - Rhine Falls 66kV Line |  | 2014Q1 | CMA | TL | 2014-02-26 14:00 | 2014-02-26 14:00 |  | follow up required |  | 66 |  |  | 2014
158836 |  |  | 840 Wagga 132 - Lockhart 66kV Line |  | 2014Q1 | WG2 | TL | 2014-02-26 14:00 | 2014-02-26 14:00 |  |  |  | 66 |  |  | 2014
158837 |  |  | 840 Wagga 132 - Lockhart 66kV Line |  | 2014Q1 | WG2 | TL | 2014-02-26 14:00 | 2014-02-26 14:00 |  | follow up required |  | 66 |  |  | 2014
158838 |  |  | No.2 Wagga 132 - Forest Hill 66kV Line |  | 2014Q1 | WG2 | TL | 2014-02-26 14:00 | 2014-02-26 14:00 |  | follow up required |  | 66 |  |  | 2014
158840 |  |  | 893/5 Forbes - Payten's Bridge 66kV Line |  | 2014Q1 | FB2 | TL | 2014-02-26 16:02 | 2014-02-26 16:02 |  | follow up required |  | 66 |  |  | 2014
158841 |  |  | 896 Forbes - West Jemalong 66kV Line |  | 2014Q1 | FB2 | TL | 2014-02-26 16:12 | 2014-02-26 16:12 |  | follow up required |  | 66 |  |  | 2014
158846 |  |  | 888/1 Rhine Falls CB 888/12 |  | 2014Q1 | CMA | CB | 2014-02-26 18:05 | 2014-02-26 18:33 |  | follow up required |  | 66 |  |  | 2014
158847 | HV Equipment | CVT | 5A2 Eraring - Kemps Creek 500kV TL | E | 2014Q1 | ER0, KCR | TL | 2014-02-26 22:51 | 2014-02-28 17:03 | Red phase CVT at Eraring end failed. Secondary volts on red phase were 69V W and B phases were 63V. | 24/03/2014 10:31:00 AM ¦ follow up required ¦ Nil. ¦ An investigation is being carried out by Substations/Northern Region to try to determine the cause of the fault of both the red and white phase CVTs. Future actions will be determined based on the findings of this investigation. | The on-call fitter attending the Eraring site measured the secondary voltage of the CVTs and found red phase voltage to be higher than white and blue phases. A visual inspection of the red phase CVT revealed a small amount of oil leaking down the porcelain, consistent with the oil expansion chamber having been punctured due to over-pressurisation. The red phase CVT was replaced on Friday 28/02/2014. During the initial energisation test, smoke was observed from the white phase CVT (refer to FEOR 2014-E-0010/1 and its follow-up report). Both the CVTs are Trench TEHM 500 model, purchased under Contract 3059. Following replacement of white phase CVT and the successful HV testing of all three phases, 5A2 TL was returned to service on Friday 07/03/2014 at 16:56hrs. | 500 | Subs Asset Mgr advises can be closed due to being replaced | Forced | 2014
158871 |  |  | U5 Upper Tumut - Tumut 2 330kV TL | X | 2014Q2 | UT1 | TL | 2014-04-11 14:05 | 2014-04-14 09:42 |  |  |  | 330 |  |  | 2014
158876 |  |  | U3 Upper Tumut - Tumut 1 330kV TL | X | 2014Q2 | UT1 | TL | 2014-05-02 12:21 | 2014-05-05 10:17 |  |  |  | 330 |  |  | 2014
158921 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2014Q1 | BER | TL | 2014-02-27 23:21 | 2014-02-27 23:21 |  | follow up required |  | 66 |  |  | 2014
158936 |  |  | 99N Darlington Point - Hillston 132kV Line |  | 2014Q1 | DNT | TL | 2014-02-28 05:59 | 2014-02-28 05:59 |  | follow up required |  | 132 |  |  | 2014
158983 |  |  | M9 Murray - Murray 1 330kV TL | X | 2014Q1 | MUR | TL | 2014-03-03 06:31 | 2014-03-19 15:25 |  |  |  | 330 |  |  | 2014
158984 |  |  | 879 Narrabri - Wee Waa 66kV Line |  | 2014Q1 | NB2 | TL | 2014-02-28 08:17 | 2014-02-28 16:19 | Distance to fault - 31.2km | follow up required |  | 66 |  |  | 2014
158987 | HV Equipment | CVT | 5A2 Eraring - Kemps Creek 500kV TL | E | 2014Q1 | ER0, KCR | TL | 2014-02-28 17:04 | 2014-03-07 15:56 | When carrying out an Initial Energisation Test on replacement Red phase C.V.T. on 5A2 Kemps Creek at Eraring, smoke was noticed coming from the secondary terminal box of C.V.T. and abnormally high volts were being recorded on White phase of the C.V.T. 5A2 Kemps Creek to Eraring T/L was de-energised at Kemps Creek and later isolated and earthed to allow replacement of White phase of the C.V.T. | 20/03/2014 1:44:00 PM ¦ follow up required ¦ Nil. ¦ An investigation is being carried out by Substations/Northern Region to try to determine the cause of the fault of both the red and white phase CVTs. Future actions will be determined based on the findings of this investigation. | On Friday 28/02/2014 at 18:04hrs, during the initial energisation test on the replacement red phase CVT in the 500kV 5A2 TL Bay at Eraring Substation, the 500kV 5A2 TL from Eraring to Kemps Creek was de-energised at Kemps Creek after some abnormalities were observed on the white phase CVT. The CVT is a Trench TEHM 500 model, purchased under Contract 3059. The white phase CVT was replaced and high voltage tests were then successfully carried out on all three CVTs on Friday 07/03/2014. 5A2 TL was then returned to service at 16:56hrs. | 500 |  | Forced | 2014
159137 |  |  | No.1 Capacitor | B | 2014Q1 | INV | CAP | 2014-03-05 07:43 | 2014-03-05 09:34 |  |  |  | 66 |  | Forced | 2014
159186 |  |  | Broken Hill - West 22kV Line |  | 2014Q1 | BKH | TL | 2014-03-04 13:08 | 2014-03-04 13:08 |  | follow up required |  | 22 |  |  | 2014
159188 |  |  | Broken Hill - West 22kV Line |  | 2014Q1 | BKH | TL | 2014-03-04 14:03 | 2014-03-04 14:03 |  | follow up required |  | 22 |  |  | 2014
159246 | Lightning/Storm | TL | 5A1 Eraring - Kemps Creek 500kV TL | Q | 2014Q1 | ER0, KCR | TL | 2014-03-05 12:03 | 2014-03-05 12:03 | Fault locator indicated 37 Kms from Kemps Creek and 104 Kms from Eraring. Storms in the Sydney area. | 15/07/2014 11:16:00 AM ¦ follow up required ¦ Nil ¦ Nil |  | 500 |  |  | 2014
159256 |  |  | 5A1 Eraring - Kemps Creek 500kV TL |  | 2014Q1 | ER0, KCR | TL | 2014-03-05 12:03 | 2014-03-05 12:08 |  | 15/07/2014 11:19:00 AM ¦ follow up required ¦ Nil ¦ Nil |  | 500 |  |  | 2014
159268 |  |  | 81L Panorama - Raglan 66kV Line |  | 2014Q1 | PMA | TL | 2014-03-05 14:13 | 2014-03-05 14:13 |  | follow up required |  | 66 |  |  | 2014
159275 |  |  | 893/5 Forbes - Payten's Bridge 66kV Line |  | 2014Q1 | FB2 | TL | 2014-03-05 15:06 | 2014-03-05 16:45 | Distance to fault = 48.69km | follow up required |  | 66 |  |  | 2014
159330 |  |  | 23 Munmorah - Vales Point 330kV TL | X | 2014Q2 | MN1, VP1 | TL | 2014-05-06 10:07 | 2014-05-06 17:00 |  |  |  | 330 |  |  | 2014
159363 | LV/MECH Fail | CB | 828 Mt Piper 132 - Portland tee BCSC 66kV Line | S | 2014Q1 | MPP | TL | 2014-03-06 16:10 | 2014-03-06 20:17 |  | 15/07/2014 3:56:00 PM ¦ follow up required ¦ Nil ¦ Nil | Issy advises burning smell coming from mech box. She confirmed that close coil was melted. Request CB control fuse be removed to confirm if battery earth fault clears.done....split was 60-0-60, when fuses restored split 80-0-40, fuses removed again. Request she contact her teamleader to arrange replacement close coil. CB subsequently repaired and feeder returned to service. Secondary Systems Asset Manager indicates no further investigation required. | 66 |  |  | 2014
159364 | Lightning/Storm | TL | 86 Tamworth 330 - Armidale 330kV TL | Q | 2014Q1 | AR1, TA1 | TL | 2014-03-06 17:34 | 2014-03-06 17:35 | Distance to Fault 26.82 / 26.08 km from Tamworth 330kv Switchyard. | follow up required |  | 330 |  |  | 2014
159374 |  |  | 94X Wallerawang 132 - Panorama 132kV TL | X | 2014Q1 | PMA, WWS | TL | 2014-03-21 07:08 | 2014-03-21 14:49 |  |  |  | 132 |  |  | 2014
159405 |  |  | 817 Wallerawang 132 - Meadow Flat 66kV Line |  | 2014Q1 | WWS | TL | 2014-03-07 12:24 | 2014-03-07 12:24 |  | follow up required |  | 66 |  |  | 2014
159407 |  |  | 875 Wallerawang 132 - Oakey Park 66kV Line |  | 2014Q1 | WWS | TL | 2014-03-07 12:40 | 2014-03-07 15:40 | Concurrent Trip of 800 Railway Fdr via intertrip from within customer system. | follow up required |  | 66 |  |  | 2014
159412 |  |  | 800 Wallerawang 132 - Railway 66kV Line |  | 2014Q1 | WWS | TL | 2014-03-07 12:40 | 2014-03-07 15:23 | Concurrent trip of 875 Oakey Park 66kV Fdr. Fault appears to be generated from transformer intertrip within Sydney Trains system No attempted reclose. Staff in attendance at site. Sydney Trains undertaking patrols of equipment at time of report. | follow up required |  | 66 |  |  | 2014
159427 |  |  | 8C1 Molong - Cumnock Tee Orange West 66kV Line |  | 2014Q1 | MOL | TL | 2014-03-07 16:11 | 2014-03-07 16:11 | Distance to Fault 14.2km | follow up required |  | 66 |  |  | 2014
159428 |  |  | 879 Narrabri - Wee Waa 66kV Line |  | 2014Q1 | NB2 | TL | 2014-03-07 17:48 | 2014-03-07 17:48 |  | follow up required |  | 66 |  |  | 2014
159464 |  |  | 83F Wagga North - Junee 66kV Line |  | 2014Q1 | WGN | TL | 2014-03-08 16:33 | 2014-03-08 17:24 | Storms in vicinity at time of trip. | follow up required |  | 66 |  |  | 2014
159465 | HV Equipment | CB | 330kV B Bus 1-2 Section CB 5112 | Q | 2014Q1 | SE1 | CB | 2014-03-08 18:08 | 2014-03-08 18:32 |  |  | CB SF6 Topup | 330 |  |  | 2014
159466 |  |  | 83F Wagga North - Junee 66kV Line |  | 2014Q1 | WGN | TL | 2014-03-08 17:35 | 2014-03-08 17:49 |  | follow up required |  | 66 |  |  | 2014
159467 |  |  | 837 Murrumburrah - Jugiong 66kV Line |  | 2014Q1 | MRU | TL | 2014-03-08 19:05 | 2014-03-08 19:05 |  | follow up required |  | 66 |  |  | 2014
159468 |  |  | 837 Murrumburrah - Jugiong 66kV Line |  | 2014Q1 | MRU | TL | 2014-03-08 19:33 | 2014-03-09 16:11 | flags caused by earlier TAR and then masked by TARTLO. | follow up required |  | 66 |  |  | 2014
159469 | Lightning/Storm | TL | 3J Gullen Range - Yass 330kV TL | Z | 2014Q1 | YSN, GUR | TL | 2014-03-08 21:02 | 2014-03-09 09:43 | Confirmed all Protection Reset at Yass note: still on Yass SCADA 330Gullen RG 3J Stub Mode Operated was unable to Close either 3J Gullen Range CB's at yass Via SCADA or the HMI control systems at Yass 330 Needed to by-pass 3J sync check and close 3J Gullen Range C.B..3J2 Via CDS switch on the control panel and then the No.3 Bay Coupler C.B..5032 was able to closed Via SCADA at Yass 330 Note: Yass SCADA 330Gullen RG 3J Stub Mode Operated -reset on closing of 3J Gullen Range C.B..3J2 Via CDS switch on the control panel. | 17/03/2014 5:23:00 PM ¦ follow up required ¦ Nil. ¦ Nil. | On Saturday 08/03/2014 at 22:02hrs, the 330kV No.3J transmission line from Gullen Range to Yass tripped at both ends of the line. Protection indicated a red phase to ground fault at both Yass and Gullen Range substations. The distance to fault at Yass 330kV substation was calculated as being 7.46km from the substation, which is in the vicinity of structures 18 and 19. Thunderstorms were present at the time of the trip. Indji recorded multiple lightning strikes in the Yass region around the time of the trip. A patrol was immediately initiated between structures 16 and 21 and nothing untoward was found. The line was returned to service on 09/03/2014 at 10:43hrs. Auto reclose not attempted. Secondary Systems Asset Manager advises no further investigation required. | 330 |  | Fault | 2014
159522 |  |  | C1 Munmorah - Colongra 330kV TL |  | 2014Q1 | MN1 | TL | 2014-03-10 08:48 | 2014-03-10 09:53 | Delta Staff inadvertently operated protection whilst doing prelim works for upcoming fault recorder installation - Was not expected to malgrade protections hence no notifictaion to TG recieved | follow up required |  | 330 |  |  | 2014
159638 | Lightning/Storm | TL | 64 Lower Tumut - Upper Tumut 330kV TL | Q | 2014Q1 | LT1, UT1 | TL | 2014-03-11 16:11 | 2014-03-11 16:11 | DTF 41Km from Upper Tumut | 16/05/2014 12:53:00 PM ¦ follow up required ¦ Nil. ¦ A close inspection of the line section will be carried out in the next aerial inspection. |  | 330 |  |  | 2014
159639 |  |  | 64 UPPER TUMUT 330KV A BUS CB BAY |  | 2014Q1 | LT1 | CB | 2014-03-11 16:11 | 2014-03-11 16:11 |  |  |  | 330 |  |  | 2014
159640 |  |  | 64 UPPER TUMUT 330KV B BUS CB BAY |  | 2014Q1 | LT1 | CB | 2014-03-11 16:11 | 2014-03-11 16:11 |  |  |  | 330 |  |  | 2014
159660 |  |  | No.2 Tie Transformer 500/330/33kV | B | 2014Q1 | BAY | TX | 2014-03-12 10:34 | 2014-03-12 12:18 |  |  |  | 500 |  | Forced | 2014
159664 |  |  | No.3 330kV Generator Transformer Group |  | 2014Q1 | LD1 | TX | 2014-03-12 10:46 |  |  |  |  | 330 |  |  | 2014
159685 |  |  | No.2 Transformer 330/132/11kV | X | 2014Q1 | VP1 | TX | 2014-03-10 11:29 | 2014-03-12 19:29 |  |  |  | 330 |  |  | 2014
159688 | HV Equipment | CB | No.3 Transformer 132kV B CB 4432B | Q | 2014Q1 | SYW | CB | 2014-03-13 00:31 |  |  |  | CB SF6 Topup | 132 |  |  | 2014
159689 |  |  | 807 Orange - Orange West T Orange South 66kV Line |  | 2014Q1 | ORG | TL | 2014-03-13 05:42 | 2014-03-13 12:47 | load disturbed for auto changeover time onto feeder 8C2 in Essential Energy's system. | follow up required |  | 66 |  |  | 2014
159735 |  |  | 81C Panorama - Blayney 66kV Line |  | 2014Q1 | PMA | TL | 2014-03-13 15:27 | 2014-03-13 15:27 |  | follow up required |  | 66 |  |  | 2014
159738 |  |  | 823 Wallerawang 132 - Portland 66kV Line |  | 2014Q1 | WWS | TL | 2014-03-13 17:06 | 2014-03-13 17:06 |  | follow up required |  | 66 |  |  | 2014
159739 |  |  | 823 Wallerawang 132 - Portland 66kV Line |  | 2014Q1 | WWS | TL | 2014-03-13 17:17 | 2014-03-13 17:17 |  | follow up required |  | 66 |  |  | 2014
159770 |  |  | U7 Upper Tumut - Tumut 2 330kV TL | X | 2014Q2 | UT1 | TL | 2014-04-11 14:05 | 2014-04-14 09:42 |  |  |  | 330 |  |  | 2014
159771 |  |  | U7 Upper Tumut - Tumut 2 330kV TL | X | 2014Q2 | UT1 | TL | 2014-04-23 07:50 | 2014-06-13 18:32 |  |  |  | 330 |  |  | 2014
159779 |  |  | U1 Upper Tumut - Tumut 1 330kV TL | X | 2014Q2 | UT1 | TL | 2014-05-02 12:21 | 2014-05-05 10:02 |  |  |  | 330 |  |  | 2014
159791 |  |  | No.3 Transformer 330/132/11kV | B | 2014Q1 | SYS | TX | 2014-03-14 12:42 | 2014-03-14 14:51 |  |  |  | 330 |  | Forced | 2014
159795 |  |  | 828 Mt Piper 132 - Portland tee BCSC 66kV Line |  | 2014Q1 | MPP | TL | 2014-03-14 12:02 | 2014-03-14 12:02 |  | follow up required |  | 66 |  |  | 2014
159807 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2014Q1 | CW2 | TL | 2014-03-14 13:27 | 2014-03-14 13:27 |  | follow up required |  | 66 |  |  | 2014
159812 |  |  | 828 Mt Piper 132 - Portland tee BCSC 66kV Line |  | 2014Q1 | MPP | TL | 2014-03-14 13:18 | 2014-03-14 13:18 |  | follow up required |  | 66 |  |  | 2014
159857 |  |  | 847 Murrumburrah - Boorowa 66kV Line |  | 2014Q1 | MRU | TL | 2014-03-14 15:08 | 2014-03-14 15:08 | Protection Flags required when next on site. | follow up required |  | 66 |  |  | 2014
159860 |  |  | 81C Panorama - Blayney 66kV Line |  | 2014Q1 | PMA | TL | 2014-03-14 14:20 | 2014-03-14 14:20 |  | follow up required |  | 66 |  |  | 2014
159861 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2014Q1 | CW2 | TL | 2014-03-14 14:26 | 2014-03-14 14:26 |  | follow up required |  | 66 |  |  | 2014
159862 |  |  | 856 Wallerawang 132 - Oberon Tee Lillyvale 66kV Line |  | 2014Q1 | WWS | TL | 2014-03-14 14:33 | 2014-03-14 14:33 |  | follow up required |  | 66 |  |  | 2014
159863 |  |  | 828 Mt Piper 132 - Portland tee BCSC 66kV Line |  | 2014Q1 | MPP | TL | 2014-03-14 15:03 | 2014-03-14 15:03 |  | follow up required |  | 66 |  |  | 2014
159864 |  |  | 817 Wallerawang 132 - Meadow Flat 66kV Line |  | 2014Q1 | WWS | TL | 2014-03-14 16:50 | 2014-03-14 16:50 | protection flagging added | follow up required |  | 66 |  |  | 2014
159865 |  |  | 8C1 Molong - Cumnock Tee Orange West 66kV Line |  | 2014Q1 | MOL | TL | 2014-03-14 17:00 | 2014-03-14 17:00 |  | follow up required |  | 66 |  |  | 2014
159866 |  |  | 8C1 Molong - Cumnock Tee Orange West 66kV Line |  | 2014Q1 | MOL | TL | 2014-03-14 17:14 | 2014-03-14 17:14 |  | follow up required |  | 66 |  |  | 2014
159869 |  |  | 8C1 Molong - Cumnock Tee Orange West 66kV Line |  | 2014Q1 | MOL | TL | 2014-03-14 18:46 | 2014-03-14 18:46 |  | follow up required |  | 66 |  |  | 2014
159870 |  |  | 8C1 Molong - Cumnock Tee Orange West 66kV Line |  | 2014Q1 | MOL | TL | 2014-03-14 19:20 | 2014-03-14 19:20 | protection flagging added | follow up required |  | 66 |  |  | 2014
159901 |  |  | 837 Murrumburrah - Jugiong 66kV Line |  | 2014Q1 | MRU | TL | 2014-03-15 21:52 | 2014-03-15 21:52 |  | follow up required |  | 66 |  |  | 2014
159902 | Lightning/Storm | TL | 999 Yass - Cowra 132kV TL | Q | 2014Q1 | CW2, YSN | TL | 2014-03-15 22:45 | 2014-03-15 22:45 |  | 31/03/2014 12:01:00 PM ¦ follow up required ¦ Nil. ¦ A close inspection of the line section will be carried out in the next aerial inspection. |  | 132 |  |  | 2014
159906 | Lightning/Storm | TL | 998 Forbes - Cowra 132kV TL | Q | 2014Q1 | CW2, FB2 | TL | 2014-03-16 06:03 | 2014-03-16 06:03 | Indji clear of storm activity, however customer reports lightning activity and loss of other 11kV assets within it's system. Irregularity issued to provide protection details when staff next at site. | 10/07/2014 10:11:00 AM ¦ follow up required ¦ Nil ¦ Nil |  | 132 |  |  | 2014
159919 | Lightning/Storm | TL | 83 Liddell - Muswellbrook 330kV TL | Q | 2014Q1 | LD1, MRK | TL | 2014-03-16 13:00 | 2014-03-16 13:00 | Heavy storm activity in area. Accompanied by fault recorder operation at Wolar, Mt Piper, Muswellbrook, Lismore, Waratah West and Bayswater. Significant surge. C.B. 5042 at Liddell reclosed via SCADA. (Normally selected non auto at this site) | follow up required |  | 330 |  |  | 2014
159920 | Lightning/Storm | TL | 96F Stroud - Tomago 330 132kV TL | Q | 2014Q1 | TOM | TL | 2014-03-16 13:43 | 2014-03-16 13:43 | Essential Energy advised. Reported 11kV or 33kV conductors down at or near Stroud area. | follow up required |  | 132 |  |  | 2014
159921 |  |  | No.2 Transformer 132/33/11kV | Y | 2014Q1 | MNY | TX | 2014-03-16 10:51 | 2014-03-16 13:42 |  |  |  | 132 |  |  | 2014
159925 | Lightning/Storm | TL | 963 Tomago330 - Taree T Hawksnest 132kV TL | Q | 2014Q1 | TRE, TOM | TL | 2014-03-16 13:57 | 2014-03-16 13:57 | Interruption to Hawks Nest (Essential Energy) for reclose time only. Ausgrid advised. (shared line ownership to str. 184 from Tomago 330kV Switchyard) Taree No.1 Prot - Distance to fault Fault report 152. 84.5km No.2 Prot - Distance to fault 132.29 km | follow up required |  | 132 |  |  | 2014
159926 | Lightning/Storm | TL | 963 Tomago330 - Taree T Hawksnest 132kV TL | Q | 2014Q1 | TRE, TOM | TL | 2014-03-16 14:00 | 2014-03-16 14:00 | Interruption to Hawks Nest (Essential Energy) for reclose time only. Ausgrid advised. (shared line ownership to str. 184 from Tomago 330kV Switchyard) Previous TAR at 1357 during heavy storm activity. | follow up required |  | 132 |  |  | 2014
159927 | Lightning/Storm | TL | 963 Tomago330 - Taree T Hawksnest 132kV TL | Q | 2014Q1 | TRE, TOM | TL | 2014-03-16 14:07 | 2014-03-16 14:07 | Interruption to Hawks Nest (Essential Energy) for reclose time only. Ausgrid advised. (shared line ownership to str. 184 from Tomago 330kV Switchyard) Previous TAR at 1357 & 1400 during heavy storm activity. | 10/04/2014 11:43:00 AM ¦ follow up required ¦ Nil ¦ No further action required. |  | 132 |  |  | 2014
159928 | Tree/Ground | TL | 964 Pt Macquarie - Taree Tee Herons Creek 132kV TL | C | 2014Q1 | PMQ, TRE | TL | 2014-03-16 14:19 | 2014-03-17 11:29 | Distance to fault from Port Macquarie - Protection 1 = 83.36km Protection 2 = 73.63km On Call Engineer / Mains Team Leader advised with view to patrol. Note - Essential Energy customer restoration completed 1438 from within Essential Energy system. Large tree found on TL 3 km out of Taree. Removal & repairs completed. | 10/04/2014 11:42:00 AM ¦ follow up required ¦ Nil ¦ No further action required. | Large tree found on TL 3 km out of Taree. Removal & repairs completed. Damaged earthwire was repaired and the TL was returned to service on Monday 17/03/2014 at 12:29hrs. Secondary Systems/Technical Services confirmed that all of the protections operated correctly for the given fault conditions. | 132 |  | Fault | 2014
159929 |  |  | 7G2 Taree - Council Harrington tee Coopernook 33kV Line |  | 2014Q1 | TRE | TL | 2014-03-16 14:19 | 2014-03-16 14:19 |  | follow up required |  | 33 |  |  | 2014
159930 |  |  | 861 Taree - Whitbread St Zone SS 66kV Line |  | 2014Q1 | TRE | TL | 2014-03-16 14:17 | 2014-03-16 15:09 | Restoration by closing C.B. 8612 at request of customer after inspection completed within its system. | follow up required |  | 66 |  |  | 2014
159931 |  |  | 863 Taree - Whitbread St Zone SS 66kV Line |  | 2014Q1 | TRE | TL | 2014-03-16 14:17 | 2014-03-16 15:09 | Supply restored by closing C.B 8632 at request of Essential Energy after patrol undertaken within it's system. | follow up required |  | 66 |  |  | 2014
159932 |  |  | 0896 Koolkhan - Maclean 66kV Line |  | 2014Q1 | KLK | TL | 2014-03-16 14:56 | 2014-03-16 14:56 |  | follow up required |  | 66 |  |  | 2014
159973 | HV Equipment | CB | 78 Sydney South A CB 782A | Q | 2014Q1 | ING | CB | 2014-03-17 09:43 | 2014-03-17 11:03 |  | 10/07/2014 11:30:00 AM ¦ follow up required ¦ Nil ¦ SF6 leak to be identified and repaired. | CB SF6 Topup | 330 |  |  | 2014
159981 |  |  | No.3 Transformer 132/66/11kV | B | 2014Q1 | NB2 | TX | 2014-03-17 12:35 | 2014-03-17 16:09 |  |  |  | 132 |  | Forced | 2014
159993 |  |  | 807 Orange - Orange West T Orange South 66kV Line |  | 2014Q1 | ORG | TL | 2014-03-13 05:42 | 2014-03-13 05:42 |  | follow up required |  | 66 |  |  | 2014
159998 | Unknown | TX | No.1 Transformer 330/132/11kV | Z | 2014Q1 | SYS | TX | 2014-03-14 12:45 | 2014-03-17 19:21 | No.1 Tx tripped on Buchholz after Aux Tx changeover, oil samples taken, nil fault recorder operations indicated. Advised by Sachin Singh Tx may return to service 17/03/14 at 1810hrs Transformer Returned to service at 1921hrs 17/03/14 | 18/07/2014 3:47:00 PM ¦ follow up required ¦ Nil ¦ Nil | No.1 Tx tripped on Buchholz after Aux Tx changeover, oil samples taken, nil fault recorder operations indicated. Advised by Sachin Singh Tx may return to service 17/03/14 at 1810hrs Transformer Returned to service at 1921hrs 17/03/14 Auxilliary supply changeover caused a brief interruption of cooling supply to No.2 Transformer. Approx 32 seconds after auxilliary supply was retored, No.2 Transformer tripped on buccholz. The trip was attributed to a cooling pump surge. The cooling soft start relay appeared fault free and the event could not be replicated with subsequent auxilliary change over attempts. The transformer was returned to service at 1921hrs on 17/03/14. | 330 |  | Fault | 2014
160024 |  |  | No.1 Transformer 330/132/11KV | X | 2014Q1 | LP1 | TX | 2014-03-18 05:30 | 2014-03-18 17:27 |  |  |  | 330 |  |  | 2014
160032 |  |  | L5 Lower Tumut - Tumut 3 330kV TL | X | 2014Q2 | LT1 | TL | 2014-04-15 08:09 | 2014-04-15 15:46 |  |  |  | 330 |  |  | 2014
160180 |  |  | 5A6 Mt Piper 500kV - Bannaby 500kV TL | B | 2014Q1 | MTP, BBY | TL | 2014-03-20 06:18 | 2014-03-20 15:59 |  |  |  | 500 |  | Forced | 2014
160189 |  |  | 964 Pt Macquarie - Taree Tee Herons Creek 132kV TL | X | 2014Q1 | PMQ, TRE | TL | 2014-03-25 07:27 | 2014-03-25 11:11 |  |  |  | 132 |  |  | 2014
160197 | Unknown | Proc | No.3 Transformer 330kV CB 5432 | Q | 2014Q1 | VYD | CB | 2014-03-19 10:44 | 2014-03-19 10:51 | No.3 TX CB 5432 opened and due to 25tl outage No.2 Transformer was off-loaded. Staff at site confirmed no protection operation and battery earth faults for both the No.1 & 2 Batteries occurred when CB 5432 opened. | 15/07/2014 4:24:00 PM ¦ follow up required ¦ Nil ¦ Completion of TWR107 | Asked why CB 5432 opened could not explain as they were working on DC circuits at the time that could not operate the CB. Both No.1 & Batteries had a earth fault at the time CB 5432 opened. NCM advised. CB was closed when staff confirmed that there was no protection operation. Secondary Systems Asset Manager advises no further investigation required. | 330 |  |  | 2014
160223 |  |  | 723 Wenna Tee Wathagar 66kV CB 7232 |  | 2014Q1 | MRE | CB | 2014-03-19 17:27 | 2014-03-19 17:27 |  | follow up required |  | 66 |  |  | 2014
160224 | Lightning/Storm | TL | 5A7 Mt Piper 500kV - Bannaby 500kV TL | Q | 2014Q1 | MTP, BBY | TL | 2014-03-19 17:52 | 2014-03-19 17:52 | Simultaneous trip of No.4 Generator at Bayswater. C.B. 5A72B O/S at time of trip and reclose. MTP distance to fault = 41.88km | 10/07/2014 10:13:00 AM ¦ follow up required ¦ Nil ¦ Nil |  | 500 |  |  | 2014
160225 | Non Transgrid | Prot | No.4 500kV Generator Transformer Group | Q | 2014Q1 | BAY | TX | 2014-03-19 17:53 | 2014-03-21 16:51 | Generator trip and bay open at same time as trip and auto reclose of 5A7 Mt Piper to Banaby 500kV T/L. Staff en route to site at time of report. Initial indication by customer indicates generator transformer differential protection operation has occurred. | follow up required | Advised that engineering staff have advised there may be a protection fault and is to be investigated on Thursday 20/03/14. Advised Greg that No.4 500kV Generator Transformer Group would have to be Isolated so the I/T rec links could be isolated at Bayswater 500 Note No RIA has been sent from Mac Gen Email sent to AEMO: After speaking with the protection technician on duty the day of the incident I can confirm circuit breakers 6242G and 6242M at the Transgrid Bayswater substation operated due to an inter-zone signal received from Bayswater Power Stations No.4 Generator Transformer groups differential protection scheme. All our protections operated normally as designed. The trip of the generator transformer group appears to be an issue within the Power Station, and an intertrip was received at the TransGrid end. Investigation pinpoints the fault in Generator Zone Protection. TG to follow up to understand corrective action from Mac Gen. | 500 | AEMO report produced, only action items are for Macquarie Generation investigations. Closed from TransGrid's point of view. |  | 2014
160285 |  |  | No.2 Transformer 330/132/11kV | Z | 2014Q1 | VYD | TX | 2014-03-19 10:44 | 2014-03-19 10:51 |  |  | Consequential outage to 160197 | 330 |  | Fault | 2014
160425 | Lightning/Storm | TL | O1 Upper Tumut - Canberra 330kV TL | Q | 2014Q1 | CA1, UT1 | TL | 2014-03-21 18:11 | 2014-03-21 18:11 | A/R selected to A CB at CA1. CB 012B closed via SCADA. | 4/04/2014 3:46:00 PM ¦ follow up required ¦ Nil. ¦ No further action required. |  | 330 |  |  | 2014
160426 |  |  | No.9 Yanco - Leeton (No.9 Council) 33kV Line |  | 2014Q1 | YA2 | TL | 2014-03-21 19:58 | 2014-03-21 20:40 | EsE staff called out to RTS. No loss of load. | follow up required |  | 33 |  |  | 2014
160427 | Lightning/Storm | TL | 96M Narrabri - Moree 132kV TL | Q | 2014Q1 | MRE, NB2 | TL | 2014-03-22 03:11 | 2014-03-22 03:11 | No sign of storms on Indji. | follow up required |  | 132 |  |  | 2014
160446 |  |  | 7R4 Kempsey - Munga 33kV Line |  | 2014Q1 | KS2 | TL | 2014-03-22 13:44 | 2014-03-22 14:25 | No auto reclose was attempted. | follow up required |  | 33 |  |  | 2014
160459 | Unknown | Cont | 8C1 Molong - Cumnock Tee Orange West 66kV Line | Q | 2014Q1 | MOL | TL | 2014-03-22 15:29 | 2014-03-22 15:29 | CB indication did not change on SCADA. | follow up required | CB indication did not change on SCADA during trip and auto reclose. Secondary Systems Asset Manager advises no further investigation required. | 66 |  |  | 2014
160466 | Unknown | TL | 998 Forbes - Cowra 132kV TL | Q | 2014Q1 | CW2, FB2 | TL | 2014-03-23 06:03 | 2014-03-23 06:03 |  | 10/07/2014 10:18:00 AM ¦ follow up required ¦ Nil ¦ Nil |  | 132 |  |  | 2014
160482 | Condition Monitor | Cond | No.1 Transformer 330/132/11kV | E | 2014Q1 | WDL | TX | 2014-03-23 07:24 | 2014-03-27 09:53 | No.1 Transformer de-energised on receipt of L1 condition monitoring alarm. Staff called to site and confirmed condition monitoring indicated elevated gas levels to 500ppm. No.1 TX isolated pending oil sample test results. Advised alarm caused by faulty Hydran. Alarm wires disconnected. Clearance to return to service 09:53 27/03/2014 - No.1 Transformer RTS NCM advised | 27/03/2014 8:15:00 AM ¦ follow up required ¦ Hydran confirmed faulty by manufacturer. Unit to be replaced. | Hydran confirmed faulty by manufacturer. Unit to be replaced. | 330 |  | Forced | 2014
160490 | Non Transgrid | TL | 9R6 Wagga 132 - Wagga North 132kV TL | Q | 2014Q1 | WG2, WGN | TL | 2014-03-23 11:45 | 2014-03-23 11:45 | no storms in the area at the time. Updated protection flagging and cause of trip. Human interference leading to fatality. | 28/04/2014 5:22:00 PM ¦ follow up required ¦ Nil. ¦ Nil. | no storms in the area at the time. Updated protection flagging and cause of trip. Human interference leading to fatality. An inspection of the tower was conducted and no evidence of damage was found. | 132 | Issued a board paper on anti-climbers. Coroner's report in progress. |  | 2014
160497 |  |  | 851 Mudgee Tee Gulgong 66kV CB 8512 |  | 2014Q1 | BER | CB | 2014-03-23 16:16 | 2014-03-23 16:16 |  | follow up required |  | 66 |  |  | 2014
160535 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2014Q1 | CW2 | TL | 2014-03-24 23:21 | 2014-03-24 23:21 |  | follow up required |  | 66 |  |  | 2014
160536 | Condition Monitor | TX | No.1 Transformer 330/132/11kV | E | 2014Q1 | SYS | TX | 2014-03-25 01:04 | 2014-03-26 18:21 | Received Condition Monitor L1 Urgent alarm on No.1 Transformer at Sydney South 330kV Substation. No.1 Transformer De-energised immediately (Open CBs Only). NCM advised. | 17/06/2014 3:18:00 PM ¦ follow up required ¦ Nil ¦ Nil | Received Condition Monitor L1 Urgent alarm on No.1 Transformer at Sydney South 330kV Substation. No.1 Transformer De-energised immediately (Open CBs Only). NCM advised. | 330 |  | Forced | 2014
160621 |  |  | 83F Wagga North - Junee 66kV Line |  | 2014Q1 | WGN | TL | 2014-03-25 21:50 | 2014-03-26 15:29 |  | follow up required |  | 66 |  |  | 2014
160718 |  |  | No.1 Transformer 330/132/11kV | B | 2014Q1 | SYS | TX | 2014-03-27 11:38 | 2014-03-29 13:40 |  |  |  | 330 |  | Forced | 2014
160916 |  |  | U1 Upper Tumut - Tumut 1 330kV TL | X | 2014Q2 | UT1 | TL | 2014-04-08 08:43 | 2014-04-09 12:33 |  |  |  | 330 |  |  | 2014
160917 |  |  | U3 Upper Tumut - Tumut 1 330kV TL | X | 2014Q2 | UT1 | TL | 2014-04-09 12:42 | 2014-04-10 17:23 |  |  |  | 330 |  |  | 2014
160970 |  |  | Broken Hill - Railway Town 22kV Line |  | 2014Q1 | BKH | TL | 2014-03-29 08:52 | 2014-03-29 09:57 | Essential Energy advise fault in their system, Sectionalised and place back in service at 0957hrs. | follow up required |  | 22 |  |  | 2014
160971 |  |  | 845 Queanbeyan - Fyshwick 66kV Line |  | 2014Q1 | QBY | TL | 2014-03-29 09:29 | 2014-03-29 11:58 | Full patrol of T/L carried out by ACTEW staff. Requested by ACTEW operator to make reclose N/A and place in-service. at 11:58hrs 845 Fysfwick was energised by SCADA and reclose made auto. | follow up required |  | 66 |  |  | 2014
160972 | Relay | Cont | 94 Tomago 330 A Bus CB 942A | Q | 2014Q1 | NEW | CB | 2014-03-29 15:17 | 2014-04-06 12:10 |  |  | Unable to close CB812A via scada. CB sync check in progress lamp on control panel. CB was in sync. Sync check bypassed and CB closed via CDS. Secondary Systems Asset Manager advises no further investigation required. | 330 |  |  | 2014
161026 |  |  | 876 Moree - Moree Solar Farm 66kV Line |  | 2014Q1 | MRE | TL | 2014-03-30 03:27 | 2014-03-30 03:27 |  | follow up required |  | 66 |  |  | 2014
161037 |  |  | 7R2 Kempsey - North St tee Smithtown 33kV Line |  | 2014Q1 | KS2 | TL | 2014-03-22 13:44 | 2014-03-22 14:25 | No auto reclose attempted. This FEOR replaces FEOR 2014-F-0136/2 that was issued on the wrong equipment. | 28/04/2014 3:36:00 PM ¦ follow up required ¦ Nil ¦ Essential Energy is investigating why its downstream protection didn't clear the fault before TransGrid's protection operated. |  | 33 |  |  | 2014
161038 |  |  | 82G Queanbeyan - Captains Flat 66kV Line |  | 2014Q1 | QBY | TL | 2014-03-30 13:51 | 2014-03-30 13:51 |  | follow up required |  | 66 |  |  | 2014
161043 | Lightning/Storm | TL | 35 Marulan - Bannaby 330kV TL | Q | 2014Q1 | MRN, BBY | TL | 2014-03-30 17:01 | 2014-03-30 17:01 |  | 6/05/2014 5:06:00 PM ¦ follow up required ¦ Nil. ¦ A close inspection of the line section will be carried out in the next aerial inspection. |  | 330 |  |  | 2014
161046 | Unknown | TL | 949 Orange North - Mt Piper 132kV Line | Q | 2014Q1 | MPP, ONO | TL | 2014-03-31 06:04 | 2014-03-31 06:04 | ONO DTF - 19.15km | 16/07/2014 2:31:00 PM ¦ follow up required ¦ Nil ¦ Nil |  | 132 |  |  | 2014
161047 |  |  | 99N Darlington Point - Hillston 132kV Line |  | 2014Q1 | DNT | TL | 2014-03-31 06:18 | 2014-03-31 06:18 | Fault Locator Showing 38% Weather - Fine | follow up required |  | 132 |  |  | 2014
161052 | Condition Monitor | TX | No.1 Transformer 330/132/11kV | E | 2014Q1 | SYS | TX | 2014-03-29 14:02 | 2014-04-02 09:29 | 1341hrs received L1 Condition Monitoring alarm associated with No.1 Tx. Transformer taken out of service via SCADA at 1402hrs. NCM Advised Steve Cunningham advised. Advises Bushings are OK and Tx available for emergency use only until further investigation takes place. 02/04/2014 - No.1 Transformer Returned to Service on advice from Sachin Singh | 17/06/2014 2:41:00 PM ¦ follow up required ¦ Nil ¦ Nil | 1341hrs received L1 Condition Monitoring alarm associated with No.1 Tx. Transformer taken out of service via SCADA at 1402hrs. NCM Advised Steve Cunningham advised. Advises Bushings are OK and Tx available for emergency use only until further investigation takes place. 02/04/2014 - No.1 Transformer Returned to Service on advice from Sachin Singh On 25/3/14, Sydney South No.1 Tx Doble IDD bushing monitoring device indicated a L1 Condition Monitoring Alarm (FEOR 2014-F-142). Review of OLCM data indicated that HV A phase bushing connection may have water ingress. An outage was taken on the 29th-30th of March to replace the bushing tap connector. The transformer was returned to service on the 29/3/2014 however the due to the accumulated trend history, a level 1 urgent alarm persisted. The alarm history was effectively cleared on the 1/4/2014 and the transformer returned to service on 2/4/2014 | 330 |  | Forced | 2014
161095 | Condition Monitor | TX | No.1 Tie Transformer 500/330kV | E | 2014Q2 | MTP | TX | 2014-04-01 03:43 | 2014-04-01 14:23 | Taken out of service after Condition Monitor L1 ALARM | 10/07/2014 1:34:00 PM ¦ follow up required ¦ Nil ¦ Nil | Advise Sachin of Condition Monitor L1 ALARM received again after placing the Tx back in service at 14:23 and received clearance from Sachin to take out of service No.1 Tie Transformer at Mt Piper 500kV Substation. Advise NCM of above alarm and receive clearance to take out of service No.1 Tie Transformer at Mt Piper 500kV Substation. Request Huw Greenhill to investigate alarm. 14:35 Receive advice from Huw Condition Monitor reset Receive advice from Sachin that Condition Monitor equipment has been reset and No.1 Tie Tx can be returned to service Advise NCM NCM given Clearance to RTS No.1 Tie Tx at Mt Piper 500/330kV Substation | 500 |  | Forced | 2014
161169 |  |  | No.3 Capacitor | E | 2014Q2 | SYN | CAP | 2014-04-01 11:08 | 2014-04-01 11:42 |  |  |  | 132 |  | Forced | 2014
161190 |  |  | M13 Murray - Murray 2 330kV TL | X | 2014Q2 | MUR | TL | 2014-04-07 13:14 | 2014-04-15 15:21 |  |  |  | 330 |  |  | 2014
161192 | Condition Monitor | TX | No.1 Tie Transformer 500/330kV | E | 2014Q2 | MTP | TX | 2014-04-01 14:57 | 2014-04-01 16:42 | Taken out of service after Condition Monitor L1 ALARM | 10/07/2014 1:36:00 PM ¦ follow up required ¦ Nil ¦ Nil | 1454 - Received Condition Monitor L1 Urgent alarm. Confirmed with Sachin requirement to O/S. Transformer taken out of service. Advised No.1 Tie Transformer Condition Monitor has been reset and transformer is serviceable. Clearance received from Sachin Singh to RTS. 16:42hrs - Transformer RTS. | 500 |  | Forced | 2014
161198 | Pollution | TL | 99K Darlington Pt - Griffith 132kV TL | Q | 2014Q2 | DNT, GRF | TL | 2014-04-01 20:02 | 2014-04-01 20:02 | Burning off activities in area surrounding Griffith at time of TAR | 15/05/2014 2:12:00 PM ¦ follow up required ¦ Nil. ¦ Nil. | On Tuesday 01/04/2014 at 21:02hrs, the 132kV No.99K transmission line from Darlington Point to Griffith tripped and reclosed at both ends of the line. Protection details at Darlington Point indicated a blue phase to earth fault, while protection details at Griffith indicated a zone 1 blue phase to earth fault. No distance to fault information was recorded. The weather was fine at the time of the event. Burning activities were reported in the Griffith area. | 132 |  |  | 2014
161216 | HV Equipment | CB | 330KV A Bus 1-2 Section CB 5102 | Q | 2014Q2 | NEW | CB | 2014-04-02 07:36 | 2014-04-02 12:56 |  |  | SF6 Topup Leak on shaft seal - repairs planned 17/6/14 type and history SIE - 3AS2 First leak 8/1/14 - around operating rod | 330 |  |  | 2014
161260 | HV Equipment | CB | 932 Sydney West - Mt Druitt 132kV Line | E | 2014Q2 | SYW | TL | 2014-04-02 13:15 | 2014-04-02 13:44 |  |  | SF6 Topup Gauge not yet replaced - planned for 8/2014. type and history ABB - HPL145 red phase leak back to 3/5/12 - red phase gauge was replaced? | 132 |  | Forced | 2014
161487 | Unknown | Cap | No.1 Capacitor | Z | 2014Q2 | SYN | CAP | 2014-04-03 08:20 |  | Capacitor tripped when attempting to place in service. | 16/07/2014 14:23:00 ¦ Follow up ¦ Nil ¦ Nil | No.1 Capacitor tripped when closing for voltage control. System operator advised. Further investigation required. A Central/Substations fitter attended site on the same day to investigate the No.1 Capacitor Bank trip. Protection flagging indicated a NUB trip associated with the 'B' bank. An initial visual inspection of the capacitor bank and associated circuit breaker identified no cause of the fault. A follow up investigation is planned to be completed in conjunction with routine maintenance. | 132 | Queried Planning about whether the capacitor banks can be partially/fully removed, awaiting response. Tony Gray of the opinion that this capacitor bank should be removed, to escalate the case. Andrew Kingsmill to raise during the next SPPRWG. Tony Gray suggests the capacitor to be mothballed. [Update 16/12/2015] Capacitor to be removed, needs statement created. | Fault | 2014
161581 |  |  | 828 Mt Piper 132 - Portland tee BCSC 66kV Line |  | 2014Q2 | MPP | TL | 2014-04-04 14:05 | 2014-04-04 14:05 |  | follow up required |  | 66 |  |  | 2014
161587 |  |  | 703 Port Macquarie - Boronia St No.1 33kV Line |  | 2014Q2 | PMQ | TL | 2014-04-05 01:11 | 2014-04-05 01:11 |  | follow up required |  | 33 |  |  | 2014
161640 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2014Q2 | MRE | TL | 2014-04-05 15:12 | 2014-04-05 15:12 | Multiple TAR in short period of time. See (x2) associated FEORs. | follow up required |  | 66 |  |  | 2014
161641 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2014Q2 | MRE | TL | 2014-04-05 15:22 | 2014-04-05 15:22 | Multiple TAR in short period of time. See (x2) associated FEORs. | follow up required |  | 66 |  |  | 2014
161642 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2014Q2 | MRE | TL | 2014-04-05 15:24 | 2014-04-05 15:24 | Multiple TAR in short period of time. See (x2) associated FEORs. | follow up required |  | 66 |  |  | 2014
161643 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2014Q2 | MRE | TL | 2014-04-05 16:34 | 2014-04-05 16:34 |  | follow up required |  | 66 |  |  | 2014
161644 | LV/MECH Fail | CB | 5A4 Wollar 500kV CB 5A42 | Q | 2014Q2 | BAY | CB | 2014-04-06 05:13 | 2014-04-06 09:49 |  |  | Advised CB 5A42 opened immediately on closing whilst restoring bay. Looks to be pole discrepancy. LV isolation required. BAY 5A42 CB mal operation on 6/4/14 was caused by a loose wiring connection plug on an auxiliary switch. He check all similar plugs and they seemed OK. Most likely the plug was not fitted correctly at installation but he also thinks some of the looms are a bit tight which may contribute. He thinks he sent Graham a short report at the time. If he find it I will forward it to you. | 500 |  |  | 2014
161667 |  |  | O51 Lower Tumut - Wagga 330kV TL | B | 2014Q2 | LT1, WG1 | TL | 2014-04-07 09:49 | 2014-04-07 11:03 |  |  |  | 330 |  | Forced | 2014
161668 |  |  | No.1 Transformer 330/132/11kV | E | 2014Q2 | TA1 | TX | 2014-04-05 15:00 | 2014-04-08 14:55 |  |  |  | 330 |  | Forced | 2014
161892 |  |  | No.1 Transformer 132/66/11kV | B | 2014Q2 | CMA | TX | 2014-04-11 09:03 | 2014-04-11 11:15 |  |  |  | 132 |  | Forced | 2014
161931 |  |  | 707 Port Macquarie - Boronia St No.2 33kV Line |  | 2014Q2 | PMQ | TL | 2014-04-10 21:20 | 2014-04-11 00:14 | Essential Energy advised at the time of the trip a loud bang and flash of light occurred on the 33kV street mains adjacent to their Port Macquarie Control room. Feeder patrolled and no fault found. Line returned to service at 00:14hrs | follow up required |  | 33 |  |  | 2014
161932 | Unknown | TL | 92Z Sydney North - Sydney East tee Mt Colah 132kV TL | Q | 2014Q2 | SE1, SYN | TL | 2014-04-11 04:30 | 2014-04-11 04:30 |  | follow up required | At 04:30hrs AusGrid's 92Z Sydney North to Sydney East tee Mt Colah 132 kV T/L trijpped and reclosed. No interruption to supply. | 132 |  |  | 2014
161933 |  |  | 92Z Sydney North tee Mt Colah 132kV CB 92Z2 |  | 2014Q2 | SE1 | CB | 2014-04-11 04:30 | 2014-04-11 04:30 |  |  |  | 132 |  |  | 2014
161934 |  |  | 92Z Sydney East tee Mt Colah CB 92Z2 |  | 2014Q2 | SYN | CB | 2014-04-11 04:30 | 2014-04-11 04:30 |  |  |  | 132 |  |  | 2014
162013 |  |  | 824 Yass - Yass Town 66kV Line |  | 2014Q2 | YSN | TL | 2014-04-11 20:28 | 2014-04-11 20:28 |  | follow up required |  | 66 |  |  | 2014
162014 |  |  | No.3 Transformer 132/66/11kV |  | 2014Q2 | YSN | TX | 2014-04-11 20:28 | 2014-04-11 20:28 |  |  |  | 132 |  |  | 2014
162101 |  |  | 896 Forbes - West Jemalong 66kV Line |  | 2014Q2 | FB2 | TL | 2014-04-14 11:29 | 2014-04-14 15:11 | Customer reports incident within it's system whilst undertaking live line work as probable reason for trip from service. Feeder selected and tagged for non auto reclose at time of event as planned and requested by customer. Subsequent I&E requested by customer for repairs. | follow up required |  | 66 |  |  | 2014
162216 |  |  | 97L Guthega - Jindabyne Pumps 132kV TL | Y | 2014Q2 | GTH | TL | 2014-04-15 09:09 | 2014-04-15 13:55 | Weather - Fine/Overcast Jindabyne pumps were not generating at time. Advised by Russell Solomon (SHL) that trip signal from SHL protection to 97L2 via Intertrip, staff working on Jindabyne pumps units at time of trip. | follow up required |  | 132 |  |  | 2014
162403 |  |  | No.3 Transformer 500/330/33kV | B | 2014Q2 | KCR | TX | 2014-04-22 07:52 | 2014-04-22 08:07 |  |  |  | 500 |  | Forced | 2014
162404 |  |  | No.3 Transformer 500/330/33kV | B | 2014Q2 | KCR | TX | 2014-04-22 12:20 | 2014-04-22 12:40 |  |  |  | 500 |  | Forced | 2014
162439 |  |  | M11 Murray - Murray 2 330kV TL | X | 2014Q2 | MUR | TL | 2014-04-30 10:06 | 2014-05-02 16:03 |  |  |  | 330 |  |  | 2014
162445 | HV Equipment | CB | No.3 Capacitor | E | 2014Q2 | WL1 | CAP | 2014-04-23 15:16 | 2014-04-23 16:36 |  |  | SF6 Topup Blue phase leak found - interrupter to mechanism. Repair planned for September. type and history ABBLTB145 leaks start 1/10/2010. Leak found and repair planned 9/2014 | 132 |  | Forced | 2014
162488 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2014Q2 | MRE | TL | 2014-04-24 12:14 | 2014-04-24 12:14 |  | follow up required |  | 66 |  |  | 2014
162495 | LV/MECH Fail | T/C | No.1 Transformer 132/66/11kV | Z | 2014Q2 | MRU | TX | 2014-04-24 15:17 | 2014-05-01 15:33 |  | 18/03/2015 1:54:00 PM ¦ follow up required | De-energised on request of maintenance due to tap changer issue. Is available for service if required on fixed tap 5 and auto close is auto. | 132 | Subs Asset Mgr advises can be closed | Fault | 2014
162503 |  |  | 662 Armidale - Walcha 66kV Line |  | 2014Q2 | AR1 | TL | 2014-04-24 21:42 | 2014-04-24 21:42 |  | follow up required |  | 66 |  |  | 2014
162504 |  |  | 868 Taree - Bohnock Tee Hallidays Point 66kV Line |  | 2014Q2 | TRE | TL | 2014-04-25 05:57 | 2014-04-25 05:57 |  | follow up required |  | 66 |  |  | 2014
162505 |  |  | 868 Taree - Bohnock Tee Hallidays Point 66kV Line |  | 2014Q2 | TRE | TL | 2014-04-25 06:25 | 2014-04-25 06:25 |  | follow up required |  | 66 |  |  | 2014
162506 |  |  | 868 Taree - Bohnock Tee Hallidays Point 66kV Line |  | 2014Q2 | TRE | TL | 2014-04-25 06:29 | 2014-04-25 06:29 |  | follow up required |  | 66 |  |  | 2014
162512 |  |  | 867 Taree - OCC Failford 66kV Line |  | 2014Q2 | TRE | TL | 2014-04-25 08:46 | 2014-04-25 08:46 |  | follow up required |  | 66 |  |  | 2014
162513 |  |  | 662 Armidale - Walcha 66kV Line |  | 2014Q2 | AR1 | TL | 2014-04-25 15:19 | 2014-04-25 15:19 |  | follow up required |  | 66 |  |  | 2014
162526 |  |  | 824 Yass - Yass Town 66kV Line |  | 2014Q2 | YSN | TL | 2014-04-26 16:32 | 2014-04-26 16:32 | No singn of storms in vicinity at time of trip. | follow up required |  | 66 |  |  | 2014
162527 |  |  | No.3 Transformer 132/66/11kV |  | 2014Q2 | YSN | TX | 2014-04-26 16:32 | 2014-04-26 16:32 |  |  |  | 132 |  |  | 2014
162528 |  |  | 33kV Bus No.1 Section | Q | 2014Q2 | GRF | BB | 2014-04-27 06:31 | 2014-04-27 14:11 | Essential Energy restored all load via parallels in their 33kV system at 0927 hours (partial load restored at 0910 hours). | 4/06/2014 10:19:00 AM ¦ follow up required |  | 33 |  |  | 2014
162529 |  |  | No.1 Bus VT |  | 2014Q2 | GRF | VT | 2014-04-27 06:31 | 2014-04-27 14:11 |  |  |  | 33 |  |  | 2014
162530 |  |  | EE Frequency Injection 33kV CB 2842 |  | 2014Q2 | GRF | CB | 2014-04-27 06:31 | 2014-04-27 14:11 |  |  |  | 33 |  |  | 2014
162531 |  |  | 79G Griffith - Griffith West 33kV Line |  | 2014Q2 | GRF | TL | 2014-04-27 06:31 | 2014-04-27 14:11 |  |  |  | 33 |  |  | 2014
162532 |  |  | 79J Griffith - Griffith Zone Standby 33kV Line |  | 2014Q2 | GRF | TL | 2014-04-27 06:31 | 2014-04-27 14:11 |  |  |  | 33 |  |  | 2014
162533 |  |  | 33kV Bus Section 1-2 CB 2102 |  | 2014Q2 | GRF | CB | 2014-04-27 06:31 | 2014-04-27 14:11 |  |  |  | 33 |  |  | 2014
162534 | Animal/Bird | Bus | No.1 Transformer 132/33/11kV | Z | 2014Q2 | GRF | TX | 2014-04-27 06:31 | 2014-04-27 14:11 |  |  | Fault on 33kv busbar section 1-2 due to birds landing on arching horn adjacent to Disconnector 2107. Confirmed no damage to High Voltage Equipment. Returned to service. Essential Energy restored all load via parallels in their 33kV system at 0927 hours (partial load restored at 0910 hours). Further investigation as to why CB 2412 failed to close via SCADA required. Further investigation into why CB 2412 failed to close found close latch pawl to be quite sticky. Mechanism cleaned and greased. CB operated OK during all test operations. CB to be replaced June 2014. | 132 | Subs Asset Mgr advises can be closed | Fault | 2014
162535 |  |  | No.1 Capacitor |  | 2014Q2 | GRF | CAP | 2014-04-27 06:31 | 2014-04-27 14:11 |  |  |  | 33 |  |  | 2014
162536 |  |  | 79F Griffith - Yenda 33kV Line | S | 2014Q2 | GRF | TL | 2014-04-27 06:31 | 2014-04-27 14:11 |  |  |  | 33 |  |  | 2014
162537 |  |  | 79C Griffith - Darlington Point 33kV Line | S | 2014Q2 | GRF | TL | 2014-04-27 06:31 | 2014-04-27 14:11 |  |  |  | 33 |  |  | 2014
162572 |  |  | No.2 Reactor |  | 2014Q2 | YSN | RX | 2014-04-28 11:05 | 2014-04-28 15:33 | Contractors found Neutral connections to Reactor Differential relay dislodged from relay terminal. Reactor to be isolated for Protection staff to rectify Advised by Prot staff wiring rectified. | 30/04/2014 3:12:00 PM ¦ follow up required ¦ WO 322725 created check No1 Reactor protections. |  | 330 |  |  | 2014
162578 |  |  | 96Z Newcastle - Maryland 132kV Line |  | 2014Q2 | NEW | TL | 2014-04-28 13:08 | 2014-04-28 21:07 | AusGrid advises that an 11kV pole top transformer sharing structures with 96Z has failed explosively and is the like cause of the trip. | follow up required |  | 132 |  |  | 2014
162585 |  |  | No.4 Transformer 330/132/11kV | B | 2014Q2 | NEW | TX | 2014-04-29 07:17 | 2014-04-29 17:27 |  |  |  | 330 |  | Forced | 2014
162636 |  |  | U5 Upper Tumut - Tumut 2 330kV TL | X | 2014Q2 | UT1 | TL | 2014-04-30 13:11 | 2014-04-30 16:32 |  |  |  | 330 |  |  | 2014
162678 |  |  | M3 Murray - Murray 1 330kV TL | X | 2014Q2 | MUR | TL | 2014-05-06 12:21 | 2014-05-12 15:49 |  |  |  | 330 |  |  | 2014
162780 | HV Equipment | CVT | No.2 Transformer 330/132/11kV | E | 2014Q2 | LSM | TX | 2014-04-30 18:21 | 2014-05-02 14:33 |  |  | Advised CVT Phase-Phase Volts indicating R-B = 112V, B-W = 79 V, and R-W = 54V. No CVT unbalance alarms initiated. 18:13, F, G Francis - Requested TX be taken OS for further investigations. Pre outage arrangements completed and TX switched on open CB. Transformer Offloaded at 18:21. G Francis advised TX OS with further investigations to be carried out. Essential Energy SO Advised. 1850 - Advises white phase CVT tank hot to touch. Other phases cool. Secondary wiring appears OK. 52 ppm moisture. Insulation failed in magnetic unit This event suggests that moisture ingress may be an issue in these failures? Condtion of capacitor unit seal? Cork type or rubber o ring? May need to do some more moisture sampling? | 330 | Sec Systems Asset Mgr advised CVT unbalance functionality needs testing. Now resolved. | Forced | 2014
162802 |  |  | 876 Moree - Moree Solar Farm 66kV Line |  | 2014Q2 | MRE | TL | 2014-05-01 08:50 | 2014-05-01 08:50 |  | follow up required |  | 66 |  |  | 2014
162807 |  |  | L1 Lower Tumut - Tumut 3 330kV TL | X | 2014Q2 | LT1 | TL | 2014-05-08 07:47 | 2014-05-08 12:15 |  |  |  | 330 |  |  | 2014
162810 |  |  | L5 Lower Tumut - Tumut 3 330kV TL | X | 2014Q2 | LT1 | TL | 2014-05-13 07:33 | 2014-05-15 15:17 |  |  |  | 330 |  |  | 2014
162891 |  |  | 99J Yanco - Griffith 132kV TL | B | 2014Q2 | GRF, YA2 | TL | 2014-05-02 08:51 | 2014-05-02 14:45 |  |  |  | 132 |  | Forced | 2014
162892 |  |  | 330kV B Bus Section 1 | Q | 2014Q2 | NEW | BB | 2014-05-01 15:28 | 2014-05-01 16:43 | 330kV B Bus Section 1 Tripped on Initial energisation of CB 5422 & No.2 Transformer at Newcastle 330 kV Substation via No.2 Transformer No.1 protection | 21/05/2014 8:50:00 AM ¦ follow up required ¦ Nil. ¦ A detailed report is being prepared by Technical Services/Protection and Metering Group. Any future actions will be determined in this report. |  | 330 |  |  | 2014
162893 |  |  | 330kV Bus Section 1 Bus Coupler CB 5012 |  | 2014Q2 | NEW | CB | 2014-05-01 15:28 | 2014-05-01 16:43 |  |  |  | 330 |  |  | 2014
162894 |  |  | No.2 Transformer 330/132/11kV | Z | 2014Q2 | NEW | TX | 2014-05-01 15:28 | 2014-05-01 16:43 |  |  |  | 330 |  | Fault | 2014
162895 |  |  | 90 Eraring B Bus CB 902B |  | 2014Q2 | NEW | CB | 2014-05-01 15:28 | 2014-05-01 16:43 |  |  |  | 330 |  |  | 2014
162896 |  |  | 330KV B Bus 1-2 Section CB 5122 |  | 2014Q2 | NEW | CB | 2014-05-01 15:28 | 2014-05-01 16:43 |  |  |  | 330 |  |  | 2014
162897 | Protection | Prot | 93 Eraring - Newcastle 330kV TL | Z | 2014Q2 | ER0, NEW | TL | 2014-05-01 15:28 | 2014-05-01 16:43 |  |  | 330kV B Bus Section 1 Tripped on Initial energisation of CB 5422 & No.2 Transformer at Newcastle 330 kV Substation via No.2 Transformer No.1 protection The inrush currents on the No.2 Transformer during initial energisation were being measured via the No.2 Transformer No.1 Protection differential relay's oscillography. A binary input (P7A) on the relay was selected and assigned the function of triggering the oscilliography upon the detection of a DC Voltage from the Control Panel 330kV CB5442 closing signal. A review of the event records downloaded from the No.2 Transformer No.1 Protection relay following the trip revealed that the input used to trigger the oscillography was actually assigned to the CBF start function of the relay. While this input was marked as a spare on the protection schematic diagram and also in the Binary Input Assignments Table of the RTI, it was subsequently identified in another section of the RTI as being assigned to the function "CB1 CBF Start". As a result, the CB 5442 closing signal input was removed from this binary input and 330kV B Bus Section 1 was then returned to service at 16:43 hrs. The oscillography trigger was then re-assigned to the "Test" binary input (H7A) on the No.2 Transformer No.1 Protection relay, and the transformer was re-energised successfully at 17:42 hrs. A detailed report is being prepared by Technical Services/Protection and Metering Group. Any future actions will be determined in this report. | 330 | Following a review, this procedure is no longer required to be performed by Tech Services. Sec Systems Asset Mgr advises can be closed | Fault | 2014
162935 | LV/MECH Fail | CB | Unit 3 Transformer | Q | 2014Q2 | KVS | CB | 2014-05-02 10:53 | 2014-05-02 10:58 | Tripped on Pole discrepancy - Known issue at KVS. | follow up required | Tripped on Pole discrepancy - Known issue at KVS. | 330 | Subs Asset Mgr advises this item has a TWR, may be closed. |  | 2014
163037 | LV/MECH Fail | CB | No.1 Transformer 132/33/11kV | Z | 2014Q2 | GRF | TX | 2014-05-03 14:46 | 2014-05-03 17:02 | CB failed to Close on restoration switching HVPRI 51671. | 5/08/2014 1:28:00 PM ¦ follow up required | Further investigation into why CB 2412 failed to close found close latch pawl to be quite sticky. Mechanism cleaned and greased. CB operated OK during all test operations. CB to be replaced June 2014. | 132 |  | Fault | 2014
163038 | Unknown | TX | No.1 Transformer 330/132/11kV | E | 2014Q2 | NEW | TX | 2014-05-03 20:52 | 2014-05-06 12:37 | No.1 Transformer Tap Changer Low Oil alarm. Transformer taken out of service until staff arrive on site to check. Confirmed low oil. Oil to be topped up on Tuesday 06/05/2014. Transformer available for emergency service. | 21/05/2014 1:17:00 PM ¦ follow up required ¦ Nil. ¦ No future action is required. | Staff called out to site confirmed the low oil level in the diverter conservator tank. A top up and inspection of the diverter's conservator was arranged. The top up and inspection was carried out on Tuesday 06/05/2014, and the 330kV No.1 Transformer was returned to service at 12:37hrs. The tapchanger on this transformer is only ever operated during routine maintenances. Because of the infrequent tapchanger operation, the gas cushion at the top of each diverter switch has been slowly absorbed over time. This has led to a drop in oil level in the diverter conservator tank (this tank only has a small capacity). This drop in oil level combined with the low ambient temperature at the time of the outage was sufficient to initiate the low oil alarm. | 330 |  | Forced | 2014
163170 |  |  | 37 Macarthur - Kemps Ck 330kV TL | X | 2014Q2 | KCR, MAC | TL | 2014-05-14 07:07 | 2014-05-14 17:26 |  |  |  | 330 |  |  | 2014
163171 |  |  | 37 Macarthur - Kemps Ck 330kV TL | X | 2014Q2 | KCR, MAC | TL | 2014-05-15 06:13 | 2014-05-15 16:37 |  |  |  | 330 |  |  | 2014
163183 |  |  | No.3 Transformer 132/66/11kV | B | 2014Q2 | TRE | TX | 2014-05-06 06:01 | 2014-05-06 16:10 |  |  |  | 132 |  | Forced | 2014
163217 |  |  | No.3 Transformer 132/66/11kV | B | 2014Q2 | TRE | TX | 2014-05-07 06:08 | 2014-05-07 14:01 |  |  |  | 132 |  | Forced | 2014
163246 |  |  | No.2 Transformer 330/132/11kV | X | 2014Q2 | VP1 | TX | 2014-05-06 10:22 | 2014-05-06 17:00 |  |  |  | 330 |  |  | 2014
163250 |  |  | No.2 Capacitor | X | 2014Q2 | VP1 | CAP | 2014-05-06 10:22 | 2014-05-06 17:00 |  |  |  | 330 |  |  | 2014
163251 |  |  | 957 Vales Pt - Ourimbah tee Morisset 132kV Line | X | 2014Q2 | VP1 | TL | 2014-05-06 10:22 | 2014-05-06 17:00 |  |  |  | 132 |  |  | 2014
163373 |  |  | No.1 Transformer 132/66/11kV | B | 2014Q2 | AR1 | TX | 2014-05-08 10:47 | 2014-05-08 17:01 |  |  |  | 132 |  | Forced | 2014
163480 |  |  | L3 Lower Tumut - Tumut 3 330kV TL | X | 2014Q2 | LT1 | TL | 2014-05-20 08:04 | 2014-05-22 13:46 |  |  |  | 330 |  |  | 2014
163595 |  |  | 13 Sydney South - Kemps Creek 330kV TL | X | 2014Q2 | KCR, SYS | TL | 2014-05-26 09:03 | 2014-05-26 18:59 |  |  |  | 330 |  |  | 2014
163596 |  |  | 13 Sydney South - Kemps Creek 330kV TL | X | 2014Q2 | KCR, SYS | TL | 2014-05-27 09:02 | 2014-05-27 16:46 |  |  |  | 330 |  |  | 2014
163607 | LV/MECH Fail | SVC | No.1 Static VAR Compensator | Z | 2014Q2 | SYW | SVC | 2014-05-08 15:09 | 2014-05-08 21:17 | SVC tripped when No.4 Transformer was de-energised while staff investigating Transformer AVR fault. Subs advise faulty mechanism on No.2 supply 415V CB. Further repairs required tomorrow. Currently on No.1 supply only. SVC RTS at 2117 hrs. | 18/07/2014 11:37:00 AM ¦ follow up required ¦ Nil ¦ Nil | SVC tripped when No.4 Transformer was de-energised while staff investigating Transformer AVR fault. Subs advise faulty mechanism on No.2 supply 415V CB. Further repairs required tomorrow. Currently on No.1 supply only. SVC RTS at 2117 hrs. When No.4 Transformer was deenergised, the SVC was supplied from the No.4 Transformer Auxilliary supply. Upon loss of 415 supply, the SVC failed to change over to alternate supply. Prolonged loss of 415 supply prevents operation of SVC cooling equipment, which results in a trip of the SVC. A faulty change over relay was identified and replaced. The SVC was RTS at 2117hrs on the same day. | 330 | Subs Asset Mgr advises can be closed | Fault | 2014
163714 |  |  | No.1 Static VAR Compensator | B | 2014Q2 | SYW | SVC | 2014-05-09 12:18 | 2014-05-09 16:20 |  |  |  | 330 |  | Forced | 2014
163936 | Protection | Prot | No.1 Transformer 132/66/11kV | Z | 2014Q2 | MRE | TX | 2014-05-12 19:41 | 2014-05-14 17:15 |  | 17/06/2014 2:53:00 PM ¦ follow up required ¦ Nil. ¦ No future action is required. | Upon arrival, No.2 Prot'n diff has operated only, site inspection revealed nothing, on call engineer B.Fraser advised and concluded, TX to remain O/S tonight, awaiting further investigations tomorrow, however is available to be placed into service or at least attempted for the loss of No.2, and No.2 to be placed on fixed tap, all has been arranged with Steve Adams and NCM advised. The on call fitter attended site and found no visible sign of any issues. Substations Maintenance staff carried out tests on the No.1 Transformer windings and bushings as well as other associated HV equipment; and found no issue. Secondary Systems/Technical Services staff tested the No.1 & No.2 Protection Differential relays and found a slightly high pick-up current on the No.1 Protection Differential relay; however, this is not believed to have contributed to this outage. The pick-up current was adjusted and the No.1 Protection Differential relay was found to operate correctly. The No.2 Protection Differential relay was also throughly tested and no issues were found. Following reviewing of all the test results, the No.1 Transformer at Moree 132kV Substation was returned to service on 14/05/2014 at 17:15hrs The on call fitter attended site and found no visible sign of any issues. Substations Maintenance staff carried out tests on the No.1 Transformer windings and bushings as well as other associated HV equipment; and found no issue. Secondary Systems/Technical Services staff tested the No.1 & No.2 Protection Differential relays and found a slightly high pick-up current on the No.1 Protection Differential relay; however, this is not believed to have contributed to this outage. The pick-up current was adjusted and the No.1 Protection Differential relay was found to operate correctly. The No.2 Protection Differential relay was also throughly tested and no issues were found. Following reviewing of all the test results, the No.1 Transformer at Moree 132kV Substation was returned to service on 14/05/2014 at 17:15hrs. | 132 | Transformer has returned without further incident. Source of Trip could not be definitively located. Issue closed. | Fault | 2014
163996 |  |  | 876 Moree - Moree Solar Farm 66kV Line |  | 2014Q2 | MRE | TL | 2014-05-13 11:30 | 2014-05-13 11:30 | Distance to Fault No 1 Prot - 6km No 2 Prot - 6.3km | follow up required |  | 66 |  |  | 2014
164028 | HV Equipment | CVT | 967 Lismore 330 - Koolkhan 132kV TL | E | 2014Q2 | KLK, LSM | TL | 2014-05-13 13:55 | 2014-05-14 16:48 | CVT Phase Unbalance alarm received on SCADA. Verified by staff on site. | 13/06/2014 12:52:00 PM ¦ follow up required ¦ Nil. ¦ The faulty 967 TL W phase CVT is scheduled to be inspected thoroughly on Thursday 26/06/2014 to find out the likely cause of the failure. | Staff called out to site confirmed that the 967 TL W ph CVT at Lismore 330kV Substation had become faulty. Faulty CVT Details (967 TL W phase): • Manufacturer and type: Trench TEM 138 • Contract: 4163/7 The W phase CVT was replaced on Wednesday 14/05/2014. New CVT Details (967 TL W phase): • Manufacturer and type: Trench TEM 138 • Contract: 4163/7 Following replacement of white phase CVT, 967 TL was returned to service on Wednesday 14/05/2014 at 16:48hrs. Has not been stripped. 57 ppm water. Lots of combustible gasses. This event suggests that moisture ingress may be an issue in these failures? Condtion of capacitor unit seal? Cork type or rubber o ring? May need to do some more moisture sampling? | 132 |  | Forced | 2014
164080 |  |  | M9 Murray - Murray 1 330kV TL | X | 2014Q2 | MUR | TL | 2014-05-23 08:15 | 2014-06-04 18:56 |  |  |  | 330 |  |  | 2014
164164 | Unknown | Prot | 96 Newcastle - Waratah West 330KV TL | Q | 2014Q2 | NEW, WRH | TL | 2014-05-15 08:00 | 2014-05-15 08:00 | Cuircuit Breakers open & auto reclose from one end only. Fault within zone 1 seen by No.1 protection only at Waratah West 330kV Substation. Staff on site at Waratah confirm C.B. operation & supported by SCADA data. Nil protection operation at Newcastle. No surging or other anomalies observed at time of C.B. operation. | 13/06/2014 3:29:00 PM ¦ follow up required ¦ Nil. ¦ Secondary Systems/Technical Services is carrying out further testing of the faulty VT and CT modules to find out the likely cause of the defect. | At 08:00hrs 96 Newcastle to Tomago 330 kV T/LTripped and reclosed at Waratah West only. Reason for trip at one end only being investigated. Secondary Systems/Technical Services found that No.1 protection relay on the 330kV 96TL at Waratah West 330kV Substation tripped due to an intermittent faulty analogue to digital VT input card giving an incorrect signal to the relay's comparator. Analysis of the event logs in the No.1 protection relay indicated a distorted ac voltage waveform at the time of tripping which caused the comparator to operate tripping the line. The existing VT & CT modules of the 96TL at Waratah West 330kV Substation were found faulty and replaced. | 330 | GE D60 Relay Failed - 3.5 years old. Sec Systems Asset Mgr advises can be closed |  | 2014
164356 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2014Q2 | BER | TL | 2014-05-17 06:36 | 2014-05-17 06:36 | DTF - 21.68km | follow up required |  | 66 |  |  | 2014
164387 |  |  | M1 Murray - Murray 1 330kV TL | X | 2014Q2 | MUR | TL | 2014-05-18 10:14 | 2014-05-18 13:03 |  |  |  | 330 |  |  | 2014
164394 |  |  | M7 Murray - Murray 1 330kV TL | X | 2014Q2 | MUR | TL | 2014-05-18 10:16 | 2014-05-18 13:03 |  |  |  | 330 |  |  | 2014
164410 |  |  | 97L Guthega - Jindabyne Pumps 132kV TL | X | 2014Q2 | GTH | TL | 2014-05-18 09:47 | 2014-05-18 13:14 |  |  |  | 132 |  |  | 2014
164411 | LV/MECH Fail | SVC | No.2 Static VAr Compensator | Z | 2014Q2 | BKH | SVC | 2014-05-18 14:49 | 2014-05-18 16:33 | Advised by Essential Energy staff lead pump fail alarm reset and pump started all alarms clear and SVC restarted. | 19/05/2014 1:34:00 PM ¦ follow up required | 14:49 18/5/14 No2 SVC Tripped. Essential Energy staff called out to investigate. Found Lead cooling pump failed. Reset all OK. Returned to service 16:33 18/5/14. | 22 | Subs Asset Mgr advises can be closed | Fault | 2014
164418 | LV/MECH Fail | SVC | No.2 Static VAr Compensator | Z | 2014Q2 | BKH | SVC | 2014-05-18 23:28 | 2014-05-22 16:04 | No.2 SVC manually taken out of service (No protection operation) due to Thyr Cooling System Fault alarm. The same SVC has previously tripped today at 14:54 hrs on same alarm. | 19/05/2014 1:35:00 PM ¦ follow up required ¦ Outage planned 09:00 20/5/14 to replace pump/contactor. <Duplicate Record> 23/05/2014 1:36:00 PM ¦ follow up required | 23:08 18/5/14 No2 SVC2 Thyr Cooling System Fault alarm. Taken out of service 23:28 18/5/14. Cooling flow Rate Transducer impeller found to be very worn. Staff on site were unable to source replacements so parts have been refurbished or manufactured. SVC returned to service 22/5/14. | 22 | Subs Asset Mgr advises can be closed | Fault | 2014
164425 |  |  | 947 Wellington - Orange North tee Burrendong 132kV Line | X | 2014Q2 | WL1, ONO | TL | 2014-06-30 09:43 | 2014-06-30 11:07 |  |  |  | 132 |  |  | 2014
164426 |  |  | 947 Wellington - Orange North tee Burrendong 132kV Line | X | 2014Q3 | WL1, ONO | TL | 2014-07-11 14:22 | 2014-07-11 14:44 |  |  |  | 132 |  |  | 2014
164460 |  |  | 932 Sydney West - Mt Druitt 132kV Line | B | 2014Q2 | SYW | TL | 2014-05-19 16:10 | 2014-05-19 17:07 |  |  |  | 132 |  | Forced | 2014
164720 | Switching error | Proc | 85 Tamworth 330 - Armidale 330kV TL | Z | 2014Q2 | AR1, TA1 | TL | 2014-05-22 14:50 | 2014-05-22 14:57 | Amdt 1 - Weather and service fixed Incorrect CB opened during HVPRI execution | follow up required | Operating error occured during execution of HVPRI at Armidale (incorrect CB opened at Tamworth) Advised by NCM of situation. N Buggy came from the cell to rectify situation. Report sent to NCM. This operating error resulted in a separation in the 330kV main system between Tamworth and Armidale. | 330 | Project initiated to install sync check relays at Tamworth 330, issue closed. | Fault | 2014
164721 |  |  | 82K/1 Queanbeyan - Bungendore tee Sutton 66kV Line |  | 2014Q2 | QBY | TL | 2014-05-22 10:07 | 2014-05-22 10:07 |  | follow up required |  | 66 |  |  | 2014
164724 | Unknown | TL | 23 Munmorah - Vales Point 330kV TL | Z | 2014Q2 | MN1, VP1 | TL | 2014-05-23 07:16 | 2014-05-23 19:37 | DTF from MN1 - P1 - 3.8km P2 - 4.78km DTF from VP1 - P1 - 5.7km P2 - 4.5km | 13/06/2014 10:33:00 AM ¦ follow up required ¦ Nil. ¦ Installation of new spacers and replacement of a mid-span joint on R phase is scheduled to occur on 14 June 2014. An investigation is being carried out by Mains/Northern to find out the likely cause of the failure. | On Friday 23/05/2014, Mains line workers arrived at site and identified a mid span joint on one of the Red phase conductors at span 13-16 failed and the conductor was on the ground. The repair work carried out were as follows: 1. A new section of conductor was inserted 2. Two new mid span joints were installed 3. Repair rods were installed where conductor had been damaged 4. Broken conductor spacers were removed 5. A chain block was put across the other Red phase mid span joint as it showed signs of deterioration The 23TL was returned to service on Friday 23/05/2014 at 19:37hrs. Installation of new spacers and replacement of a mid-span joint on R phase is scheduled to occur on 14 June 2014. An investigation is being carried out by Mains/Northern to find out the likely cause of the failure. | 330 | Report from metallurgist received. | Fault | 2014
164802 | Relay Setting | Prot | No.2 Transformer 330/132/11kV | Z | 2014Q2 | SYS | TX | 2014-05-23 17:52 | 2014-05-26 20:00 |  | 18/07/2014 12:05:00 PM ¦ follow up required ¦ Nil ¦ Nil | Attempted to close No.2 Transformer C.B.. 5422 under HVPRI 51174. C.B..5422 closed and opened Staff on site advise Diff trip (A&B phase), No.1 Protection. Requested to check switchgear. Staff advise Multitrips confirmed reset prior to switching. NCM advised 18:08 - Staff advise switchgear appears ok. No fault recorder operations or other indications to indicate fault. 18:25 - Sachin Singh advised of No.2 Transformer tripping on energisation. Requested to provide further instruction. 18:50 - Sachin requests No.2 Transformer to remain OOS. Protection staff arranged to attend first thing on Monday 26/5/14. No.2 Transformer to be isolated from system under log entry switching Investigation into the trip on energisation identified that the No.1 Protection relay tripped in error on inrush during energisation. A setting change was required to correct the inrush inhibit mode. Setting changes were made on 26/05/14 and the transformer RTS at 2000hrs | 330 | An older standard of T60 settings for preventing inrush tripping on transformer energisation likely contributed to the trip. These have been updated to the current standard and work is ongoing to determine whether any other sites still have the old standard for settings in service. | Fault | 2014
164806 | Condition Monitor | TX | No.3 Transformer 330/132/11kV | E | 2014Q2 | BFD | TX | 2014-05-24 11:42 | 2014-05-30 18:09 | Received No.3 Transformer condition monitor L1 Urgent - Alarm at Beaconsfield South, No.3 Transformer taken out of service. Note : No.3 Transformer was energised on std-by only prior to the condition monitor L1 Urgent - Alarm and then been taken out of service. | 18/07/2014 10:32:00 AM ¦ follow up required ¦ Nil ¦ Amend control system database to appropriately map OLCM alarms from TapGuard. | Advises received No.3 Transformer condition monitor L1 Urgent Alarm at Beaconsfield South Advised NCM No.3 Transformer required OOS No.3 Transformer - PLACE ON NON-AUTO VOLTAGE CONTROL No.3 Transformer 132kv CB..4432 - CHECK OPEN No.3 Transformer 132kv CB..5432 - OPEN via SCADA completed 11:44 hrs 11:48 advised maintenance staff training at Holroyd and requested someone to confirmed auxiliary supply changed over correctly. 12:00 advised on call engineer Saiyaz Dean, who advised would arrange staff on Monday 26/05/14 to follow up. | 330 |  | Forced | 2014
164823 | Unknown | SVC | No.1 Static VAR Compensator | Z | 2014Q2 | LSM | SVC | 2014-05-26 07:23 | 2014-05-26 09:38 | SVC was returned to service then 30 sec later when the 5th filter load maker switch closed the SVC tripped. Refer to FEOR 2014-F-0193 for second trip. | 17/06/2014 11:50:00 AM ¦ follow up required ¦ Nil. ¦ No future action is required. | Thyristor Controlled Reactor (TCR) gate control panel failure alarm up. AVR No.2 Tripped CB, AVR No.1 still powered (Normal). Biased Diff relay all 3 phases tripped. MTR Trip. TX Diff and restricted E/Fault relay FNG1 AB&C operated. Advised that he has spoken to N Robertson and believes that the Diff restricted E/Fault relay was not the cause of the trip and that the loss of power to the AVR No.2 was the cause. On Monday 26/05/2014, the on call fitter attended the site and couldn't find any reason behind the trip. On Monday 26/05/2014 at 09:38hrs, during an attempt to put the No.1 SVC at Lismore 330kV Substation back on service, the No.1 SVC tripped again (refer to FEOR 2014-F-0193/2 and its follow-up report). Further investigation suggested that a faulty power supply unit of No.2 AVR causing the mal-operation of the TCR gate control resulting in a SVC trip. The faulty power supply unit was replaced and the No.1 SVC at Lismore 330kV Substation was returned to service on 27/05/2014 at 13:44hrs. | 132 | Subs Asset Mgr advises can be closed | Fault | 2014
164836 | Unknown | SVC | No.1 Static VAR Compensator | Z | 2014Q2 | LSM | SVC | 2014-05-26 09:38 | 2014-05-27 13:44 | SVC was returned to service then 30 sec later when the 5th filter load maker switch 2V12A closed the SVC tripped. Repairs completed 27/05/14 | 17/06/2014 1:32:00 PM ¦ follow up required ¦ Nil. ¦ No future action is required. | Graham Francis informed SO/N the SVC tripped when the Power Supply to the #2 AVR control panel tripped. All relays and signals reset and permission requested and given to return the SVC to service. The SVC tripped on energising at 09:38hrs. Further investigation on cause of trip required. Investigations indicated that a faulty power supply unit caused the mal-operation of the Thyristor Controlled Reactor (TCR) gate control; resulting in the SVC trip. The faulty power supply unit was replaced and the No.1 SVC at Lismore 330kV Substation was returned to service on 27/05/2014 at 13:44hrs | 132 | Subs Asset Mgr advises can be closed | Fault | 2014
164968 |  |  | M1 Murray - Murray 1 330kV TL | X | 2014Q4 | MUR, MP1 | TL | 2014-10-27 07:05 | 2014-11-14 12:08 |  |  |  | 330 |  |  | 2014
164976 | Lightning/Storm | TL | O1 Upper Tumut - Canberra 330kV TL | Q | 2014Q2 | CA1, UT1 | TL | 2014-05-27 18:24 | 2014-05-27 18:24 |  | 9/07/2014 1:03:00 PM ¦ follow up required ¦ Nil. ¦ A close inspection of the line section will be carried out in the next aerial inspection. |  | 330 |  |  | 2014
164977 |  |  | 82B Queanbeyan - High St 66kV Line |  | 2014Q2 | QBY | TL | 2014-05-27 20:48 | 2014-05-27 20:48 |  | follow up required |  | 66 |  |  | 2014
165038 |  |  | No.3 Transformer 330/132/11kV | B | 2014Q2 | SYS | TX | 2014-05-29 09:48 | 2014-06-10 14:39 |  |  |  | 330 |  | Forced | 2014
165039 |  |  | 330kV A Bus No.1 Section | Q | 2014Q2 | SYS | BB | 2014-05-29 07:03 | 2014-05-29 08:09 | CB5432 failed to open correctly. | 16/07/2014 3:06:00 PM ¦ follow up required ¦ Nil ¦ Nil |  | 330 |  |  | 2014
165040 | LV/MECH Fail | CB | No.3 Transformer 330/132/11kV | E | 2014Q2 | SYS | TX | 2014-05-29 07:03 | 2014-05-29 08:09 |  |  | Advises No.3 Transformer 330kV CB 5432 has opened on Red and Blue phases only. Smoke coming from Circuit Breaker cabinet. Possible faulty trip coil. NCM Advised. Request clear Substation to facilitate outage of 330kV A1 Bus section at Sydney South 330kV Substation. 1 phase found to be in intermittent position (neither open nor closed). This is due to slippage of clutch in mech box on this pole. This is not a maintenance item and so goes unchecked. Clutch tightened and RTS. Returning to check other phases. WO 325589 Service instruction may need to be amended to include additional checks. This needs follow up with Central. A Central/Substation Fitter attended site to investigate. White phase pole found to be in intermittent position (neither open nor closed) triggering a pole discrepency alarm. The mechanical failure is due to slippage of clutch in mechanism box on this pole. The clutch was tightened and the CB RTS at 0809 on the same day. A follow up investigation to check the condition of the other phases is planned under WO 325589. The circuit breaker is a Sprecher & Schuh HGF215. This model has been identified for staged replacement in PAD-0504 for completion by 2029, with CB 5432 identified in the 2014/15-2018/19 regulatory period. | 330 |  | Forced | 2014
165041 |  |  | No.2 Transformer 330/132/11kV | E | 2014Q2 | SYS | TX | 2014-05-29 07:03 | 2014-05-29 08:09 |  |  |  | 330 |  | Forced | 2014
165042 |  |  | 13 Kemps Creek A CB 132A |  | 2014Q2 | SYS | CB | 2014-05-29 07:03 | 2014-05-29 08:09 |  |  |  | 330 |  |  | 2014
165043 |  |  | 330kV A Bus 1-2 Section CB 5102 |  | 2014Q2 | SYS | CB | 2014-05-29 07:03 | 2014-05-29 08:09 |  |  |  | 330 |  |  | 2014
165044 |  |  | 41 Beaconsfield West Series Reactor | E | 2014Q2 | SYS | RX | 2014-05-29 07:03 | 2014-05-29 08:09 |  |  |  | 330 |  | Forced | 2014
165045 |  |  | 11 Dapto - Sydney South 330kV TL | E | 2014Q2 | DPT, SYS | TL | 2014-05-29 07:03 | 2014-05-29 08:09 |  |  |  | 330 |  | Forced | 2014
165221 |  |  | No.2 Transformer 132/33/11kV | X | 2014Q2 | MNY | TX | 2014-05-30 11:32 | 2014-05-30 13:36 |  |  |  | 132 |  |  | 2014
165280 |  |  | M1 Murray - Murray 1 330kV TL | X | 2014Q2 | MUR | TL | 2014-06-24 08:06 | 2014-06-24 10:51 |  |  |  | 330 |  |  | 2014
165286 |  |  | M1 Murray - Murray 1 330kV TL | X | 2014Q2 | MUR | TL | 2014-06-24 11:11 | 2014-06-24 12:39 |  |  |  | 330 |  |  | 2014
165287 |  |  | M1 Murray - Murray 1 330kV TL | X | 2014Q2 | MUR | TL | 2014-06-24 12:59 | 2014-06-24 16:22 |  |  |  | 330 |  |  | 2014
165289 |  |  | L5 Lower Tumut - Tumut 3 330kV TL | X | 2014Q2 | LT1 | TL | 2014-06-19 08:55 | 2014-06-19 11:02 |  |  |  | 330 |  |  | 2014
165290 |  |  | L5 Lower Tumut - Tumut 3 330kV TL | X | 2014Q2 | LT1 | TL | 2014-06-19 11:33 | 2014-06-19 13:52 |  |  |  | 330 |  |  | 2014
165295 | Condition Monitor | TX | No.3 Transformer 330/132/11kV | E | 2014Q2 | BFD | TX | 2014-05-30 18:09 | 2014-06-12 12:01 | Advised Sachin Singh of L1 Condition Monitoring alarm on energisation of No.3 Transformer at Beaconsfield. P.Baigent to attend and advise | 18/07/2014 10:36:00 AM ¦ follow up required ¦ Nil ¦ See follow up 870. | Advised hydran is within 31ppm, Dobel has no alerts. L1 alarm seems to be caused by tap guard red message alert "oil sample due 24/5/14" | 330 |  | Forced | 2014
165305 | HV Equipment | CB | 330KV A Bus 1-2 Section CB 5102 | Q | 2014Q2 | NEW | CB | 2014-05-31 08:19 | 2014-05-31 09:31 |  |  | Advised SF6 low. Outage arranged for top up. Leak on shaft seal - repairs planned 17/6/14 | 330 |  |  | 2014
165315 |  |  | Broken Hill - West 22kV Line |  | 2014Q2 | BKH | TL | 2014-05-31 17:38 | 2014-05-31 17:38 |  | follow up required |  | 22 |  |  | 2014
165317 |  |  | 97L Guthega - Jindabyne Pumps 132kV TL | X | 2014Q2 | GTH | TL | 2014-06-01 09:07 | 2014-06-01 12:54 |  |  |  | 132 |  |  | 2014
165330 |  |  | M1 Murray - Murray 1 330kV TL | X | 2014Q2 | MUR | TL | 2014-06-01 09:11 | 2014-06-01 12:25 |  |  |  | 330 |  |  | 2014
165331 |  |  | M7 Murray - Murray 1 330kV TL | X | 2014Q2 | MUR | TL | 2014-06-01 09:11 | 2014-06-01 12:25 |  |  |  | 330 |  |  | 2014
165333 |  |  | Broken Hill - Cockburn 22kV Line |  | 2014Q2 | BKH | TL | 2014-06-01 09:40 | 2014-06-01 09:40 | Both the No.8 Cockburn and No.7 West 22kV Lines TAR at the same time. | follow up required |  | 22 |  |  | 2014
165334 |  |  | Broken Hill - West 22kV Line |  | 2014Q2 | BKH | TL | 2014-06-01 09:40 | 2014-06-01 09:40 | Both the No.8 Cockburn and No.7 West 22kV Lines TAR at the same time. | follow up required |  | 22 |  |  | 2014
165377 |  |  | 330kV A Bus Section 1 |  | 2014Q2 | HLD | BB | 2014-06-02 13:50 | 2014-06-02 18:24 |  | 11/07/2014 9:13:00 AM ¦ follow up required ¦ Nil ¦ Nil |  | 330 |  |  | 2014
165378 |  |  | Spare 5X1 CB 5X12 |  | 2014Q2 | HLD | CB | 2014-06-02 13:50 | 2014-06-02 18:24 |  |  |  | 330 |  |  | 2014
165379 |  |  | 43 Rookwood Rd CB 432 |  | 2014Q2 | HLD | CB | 2014-06-02 13:50 | 2014-06-02 18:24 |  |  |  | 330 |  |  | 2014
165380 |  |  | 1F Sydney West CB 1F2 |  | 2014Q2 | HLD | CB | 2014-06-02 13:50 | 2014-06-02 18:24 |  |  |  | 330 |  |  | 2014
165407 | Relay Setting | Prot | 850 Tumut - Talbingo tee Jounama Dam 66kV Line | S | 2014Q2 | TU2 | TL | 2014-06-02 14:42 | 2014-06-02 14:52 | Transgrid conducting inservice on-load checks on 850 Talbingo fdr after SSB cutover with temporary protections, SHL then commenced generation at Jounama PS the generation exceeded Temporary O/C levels Essential customer load lost 1MW Generation lost 9MW | follow up required |  | 66 | Trip occurred during commissioning procedure on temporary protection. Temporary Protection Settings were not implemented according to Temporary Protection RTI. Sec Sys Asset Mgr advises can be closed |  | 2014
165473 | HV Equipment | Other | No.1 Transformer 330/132/11kV | E | 2014Q2 | HLD | TX | 2014-06-02 13:50 | 2014-06-02 18:24 |  |  | GIS Equipment SF6 Low on Red Phase. SF6 topped up. | 330 |  | Forced | 2014
165622 |  |  | 863 Cowra - Canowindra 66kV Line |  | 2014Q2 | CW2 | TL | 2014-06-05 07:35 | 2014-06-05 07:35 |  | follow up required |  | 66 |  |  | 2014
165703 | Unknown | TL | 945 Wellington - Molong tee Well'n Town 132kV TL | Q | 2014Q2 | MOL, WL1 | TL | 2014-06-06 07:15 | 2014-06-06 07:15 |  | follow up required |  | 132 |  |  | 2014
165717 |  |  | 79C Griffith - Darlington Point 33kV Line |  | 2014Q2 | GRF | TL | 2014-06-07 10:46 | 2014-06-07 10:46 |  | follow up required |  | 33 |  |  | 2014
165726 |  |  | No.1 & No.2 Gas Turbines 22kV CB 2212 |  | 2014Q2 | BKH | G | 2014-06-09 06:32 | 2014-06-09 12:07 | C.B. tripped due to Buchholz Low Oil Trip on Essential Energy's Unit 1 Transformer at Broken Hill Gas Turbine Station. Transformer isolated on HVPRI 52566 to allow Essential Energy to top up oil in transformer. C.B. 2212 returned to service at 1207 hours. | follow up required |  | 11 |  |  | 2014
165727 |  |  | No.1 Gas Turbine |  | 2014Q2 | BKH | G | 2014-06-09 06:32 | 2014-06-09 12:07 |  |  |  | 11 |  |  | 2014
165728 |  |  | No.2 Gas Turbine |  | 2014Q2 | BKH | G | 2014-06-09 06:32 | 2014-06-09 12:07 |  |  |  | 11 |  |  | 2014
165741 |  |  | 950 Newcastle - Jesmond 132kV Line |  | 2014Q2 | NEW | TL | 2014-06-10 10:04 | 2014-06-10 16:43 | Noticeable surge on system. Customer line patrol in progress at time of report. | follow up required |  | 132 |  |  | 2014
165837 |  |  | 97G Murray - Guthega tee Geehi 132kV TL | B | 2014Q2 | GTH, MUR, GHI | TL | 2014-06-12 10:05 | 2014-06-12 13:51 |  |  |  | 132 |  | Forced | 2014
166004 |  |  | 957 Vales Pt - Ourimbah tee Morisset 132kV Line |  | 2014Q2 | VP1 | TL | 2014-06-12 11:38 | 2014-06-12 14:50 |  | follow up required |  | 132 |  |  | 2014
166020 |  |  | 97L Guthega - Jindabyne Pumps 132kV TL | X | 2014Q2 | GTH | TL | 2014-06-17 09:10 | 2014-06-17 11:05 |  |  |  | 132 |  |  | 2014
166067 |  |  | 99N Hillston CB 99N2 |  | 2014Q2 | DNT | CB | 2014-06-14 03:15 | 2014-06-14 03:15 |  | follow up required |  | 132 |  |  | 2014
166097 |  |  | No.3 330kV Generator Transformer Group |  | 2014Q2 | LD1 | TX | 2014-06-16 08:13 | 2014-06-19 18:10 |  | follow up required |  | 330 |  |  | 2014
166125 |  |  | 83G Wagga North - Bomen 66kV Line |  | 2014Q2 | WGN | TL | 2014-06-16 12:52 | 2014-06-16 12:52 |  | follow up required |  | 66 |  |  | 2014
166132 |  |  | No.3 Transformer 132/66/11kV | B | 2014Q2 | NB2 | TX | 2014-06-17 08:50 | 2014-06-17 09:38 |  |  |  | 132 |  | Forced | 2014
166156 |  |  | 96P Taree - Stroud 132kV TL | X | 2014Q2 | TRE | TL | 2014-06-20 06:09 | 2014-06-20 17:08 |  |  |  | 132 |  |  | 2014
166166 |  |  | 9C5 Tomago330 - Brandy Hill 132kV TL | X | 2014Q2 | TOM, BRH | TL | 2014-06-30 06:53 | 2014-07-17 15:09 |  |  |  | 132 |  |  | 2014
166329 |  |  | 79L Griffith - Beelbangera 33kV Line |  | 2014Q2 | GRF | TL | 2014-06-19 15:10 | 2014-06-19 17:00 | Staff working at site advise that they noticed a flashover on the second pole outside the sub. DTF 0.72kM. | follow up required |  | 33 |  |  | 2014
166400 |  |  | 7G2 Taree - Council Harrington tee Coopernook 33kV Line |  | 2014Q2 | TRE | TL | 2014-06-21 01:02 | 2014-06-21 01:02 |  | follow up required |  | 33 |  |  | 2014
166457 |  |  | 38 Sydney West - Regentville 330kV TL | B | 2014Q2 | RGV, SYW | TL | 2014-06-21 12:04 | 2014-06-21 14:06 |  |  |  | 330 |  | Forced | 2014
166461 |  |  | No.3 330kV Generator Transformer Group |  | 2014Q2 | LD1 | TX | 2014-06-22 05:11 | 2014-06-23 14:48 |  |  |  | 330 |  |  | 2014
166464 | Unknown | Cap | No.2 Capacitor | Q | 2014Q2 | BKH | CAP | 2014-06-22 12:28 | 2014-06-23 14:05 |  | 11/09/2014 2:09:00 PM ¦ follow up required | At 12:28hrs No.2 Capacitor Tripped. Neutral Unbalance and M/T operated. CB 2722 closed when M/T reset. Opend by Operator and Capacitor bank Isolated. Further Investigation Required. Visual inspection carried out following week by protection staff on site. No obvious signs of failure. Cap in service at this time and protection requested to tong spill current of NUB CT. Measured and found well below alarm trip level in RTI. | 22 |  |  | 2014
166652 |  |  | 98W Dapto - Mt Terry 132kV Line |  | 2014Q2 | DPT | TL | 2014-06-24 23:18 | 2014-06-25 00:27 | SO/Endeavour Energy advised that the OHEW on 98W Mt Terry 132kV Feeder has broken and is laying on the ground. The feeder was off-loaded by Endeavour and then requestd TG to De-Energise at Dapto. SO/Endeavour Energy (Peter) advises that 98W Dapto - Mt Terry 132kV Line was actually incorrectly located as a faulty feeder where as the fault is on 98U feeder out of Mt Terry. 98W Dapto - Mt Terry 132kV Line is absolutely fine and fully operational and can be returned to service. Requests to Energise 98W Dapto - Mt Terry 132kV Line at DPT. NCM advised. 00:27 98W Mt Terry CB 98W2 CLOSED. | follow up required |  | 132 |  |  | 2014
166653 | Unknown | TL | 96M Narrabri - Moree 132kV TL | Q | 2014Q2 | MRE, NB2 | TL | 2014-06-25 04:22 | 2014-06-25 04:22 |  | follow up required |  | 132 |  |  | 2014
166750 |  |  | 82B Queanbeyan - High St 66kV Line |  | 2014Q2 | QBY | TL | 2014-06-24 10:04 | 2014-06-24 10:04 | Essential Energy advised patrol of line identified conductors clashing on line where conductors transition from vertical to delta configuration. Auto Reclose requested to be made non auto and advised outage to be arranged on feeder later in week. Refer to FEOR 2014-F-0218 for subsequent TAR event @ 1316 hours. | follow up required |  | 66 |  |  | 2014
166751 |  |  | 82B Queanbeyan - High St 66kV Line |  | 2014Q2 | QBY | TL | 2014-06-24 13:16 | 2014-06-24 13:16 | Essential Energy advised patrol of line identified conductors clashing on line where conductors transition from vertical to delta configuration. Auto Reclose requested to be made non auto and advised outage to be arranged on feeder later in week. Refer to FEOR 2014-F-0217 for earlier TAR event @ 1004 hours. | follow up required |  | 66 |  |  | 2014
166883 | HV Equipment | Cap | No.1 Capacitor | Z | 2014Q2 | CA1 | CAP | 2014-06-26 18:10 | 2014-07-11 12:55 | Visual inspection of gear ok. Slight smell from Capacitor Bank (PCB). Will have another inspection in the morning (27/6/14) CB 4712 command blocked | 25/05/2015 9:33:00 AM ¦ follow up required ¦ Cap bank currently being replaced by southern construction group | Defect work order 327797 created and completed on 10/7/14. Replaced faulty can on white phase in group 71 of bank. replaced two cans on white phase and done a 415v balance. Bank balance was good | 132 |  | Fault | 2014
166925 |  |  | 97L Guthega - Jindabyne Pumps 132kV TL | X | 2014Q3 | GTH | TL | 2014-07-03 08:42 | 2014-07-03 16:41 |  |  |  | 132 |  |  | 2014
166934 |  |  | 43 Holroyd - Rookwood Rd 330kV Cable |  | 2014Q2 | HLD, RWR | UG | 2014-06-27 15:43 | 2014-07-04 11:48 | 43 Rookwood Rd Line Disconnector 431 is open and 43 Rookwood Rd is not connected. Alarms; 43 No.1 line prot CBF I/T Rec - OPTD 43 No.1 line prot Trip ( software) - ON 43 No.1 line prot - OPTD | follow up required |  | 330 |  |  | 2014
166957 |  |  | 804 Tamworth 132 - Nundle 66kV Line |  | 2014Q2 | TMW | TL | 2014-06-28 13:59 | 2014-06-28 19:32 | No SCADA from site. Staff in attendance at time of report to provide protection and conduct bay inspection. Essential Energy reports interruption to customers and has initiated line patrol. | follow up required |  | 66 |  |  | 2014
166958 |  |  | 83G Wagga North - Bomen 66kV Line |  | 2014Q2 | WGN | TL | 2014-06-28 10:48 | 2014-06-28 10:48 |  | follow up required |  | 66 |  |  | 2014
166959 |  |  | 927 Sydney North - Homebush Bay tee Carlingford 132kV Line |  | 2014Q2 | SYN | TL | 2014-06-28 16:04 | 2014-06-29 00:16 | Actual outage time 28/06/2014 16:04 Ausgrid Line patrol did not find anything. | follow up required |  | 132 |  |  | 2014
166960 |  |  | 927 Sydney North tee Homebush Bay CB 15979 |  | 2014Q2 | CFL | CB | 2014-06-28 04:22 | 2014-06-29 00:16 |  |  |  | 132 |  |  | 2014
166961 |  |  | 927 Sydney North tee Carlingford 132kV CB 9272 |  | 2014Q2 | HOM | CB | 2014-06-28 04:22 | 2014-06-29 00:16 |  |  |  | 132 |  |  | 2014
166962 |  |  | 927 Homebush Bay tee Carlingford CB 9272 |  | 2014Q2 | SYN | CB | 2014-06-28 04:22 | 2014-06-29 00:16 |  |  |  | 132 |  |  | 2014
167080 |  |  | No.4 Station Transformer |  | 2014Q3 | VP1 | TX | 2014-07-01 17:18 | 2014-08-02 14:08 | Emergency Outage of Delta Electricity Station Transformer 4 due to severe arcing of Transformer | follow up required |  | 132 |  |  | 2014
167102 | LV/MECH Fail | T/C | No.4 Transformer 330/132/11kV | B | 2014Q3 | DPT | TX | 2014-07-03 08:45 | 2014-07-03 13:37 |  |  | Investigate tap changer fault LV testing of circuits | 330 |  | Forced | 2014
167121 |  |  | 79C Griffith - Darlington Point 33kV Line |  | 2014Q3 | GRF | TL | 2014-07-02 12:17 | 2014-07-02 12:17 | Distance to Fault 8.5km Calculated 7MW load lost Cause of Fault - Downed conductors in Essential Energy Network. 79C de-energised at request Essential Energy. Weather - Fine | follow up required |  | 33 |  |  | 2014
167124 | HV Equipment | CB | 5A1 Eraring A CB 5A12A | Q | 2014Q3 | KCR | CB | 2014-07-03 07:15 | 2014-07-03 13:24 |  |  | SF6 topup | 500 |  |  | 2014
167130 |  |  | 96F Stroud - Tomago 330 132kV TL | X | 2014Q3 | TOM | TL | 2014-07-09 09:39 | 2014-07-09 15:48 |  |  |  | 132 |  |  | 2014
167157 | HV Equipment | CB | No.2 Capacitor | B | 2014Q3 | GN2 | CAP | 2014-07-03 12:59 | 2014-07-03 13:44 |  |  | CB SF6 Topup | 66 |  | Forced | 2014
167459 | HV Equipment | TL | 97G Murray - Guthega tee Geehi 132kV TL | E | 2014Q3 | GTH, MUR, GHI | TL | 2014-07-04 16:30 | 2014-09-25 17:35 | 97G Murray - Guthega tee Geehi 132kV TL isolated & Earthed Saturday 05/0714 on HVPRI 52996, Bonds were removed at Str117 between Murray and Geehi tee, 97G Guthega tee Geehi 132kV TL was the energised from Guthega 132 Mains T/L advised of failed crossarm on 97G Murray - Guthega tee Geehi 132kV TL and line required out of service. M T/L advised was arranging staff for switchnig at Murray330 and Guthega 132kV. | 10/10/2014 3:14:00 PM ¦ follow up required ¦ Nil. ¦ Nil. | On Friday 04/07/2014 at 16:30hrs, the 132kV 97G transmission line from Guthega to Murray substation was taken out of service following a defect that was discovered by Snowy Hydro staff. The Southern Mains team leader was advised of a failed (bent) crossarm on structure 139. The line was immediately taken out of service. Staff attended site on Saturday 05 July 2014 to assess the defect and commence planning to rectify the issue. An aerial patrol was also conducted on Tuesday 15 July 2014 with no other defects on the 97G failure area observed. The crossarm was replaced on Thursday 18/09/2014 and the line was returned to service on Thursday 25/09/2014. | 132 | Crossarms replaced. | Forced | 2014
167460 |  |  | 97G/3 Geehi Tee CB 97G2 |  | 2014Q3 | GTH | CB | 2014-07-04 16:30 | 2014-09-25 17:35 |  |  |  | 132 |  |  | 2014
167461 |  |  | 97G/1 Geehi Tee CB 97G2 |  | 2014Q3 | MUR | CB | 2014-07-04 16:30 | 2014-09-25 17:35 |  |  |  | 132 |  |  | 2014
167462 | HV Equipment | CT | 132kV Bus No2 Sect Bus Coupler CB 4022 | Q | 2014Q3 | WWS | CB | 2014-07-04 16:33 | 2014-08-08 12:17 |  |  | Advised todays testing has identified a high resistance joint on the No1 BBP CT contribution internal to the apparatus. Sachin Singh and Tim Barnes have been made aware the equipment is not serviceable and have decided the equipment is not to return to service. Switching has been modified to allow 132kV A Bus Section 2 and 941 TL to return to service whilst maintaining the isolation and earthing for future works on CB 4022. | 132 | SSE advises CT replaced, investigation complete. |  | 2014
167464 | HV Equipment | CB | 7R1 Kempsey - Prince St 33kV Line | Q | 2014Q3 | KS2 | TL | 2014-07-05 02:48 | 2014-07-05 03:48 |  |  | SF6 topup | 33 |  |  | 2014
167535 | HV Equipment | CB | No.3 Transformer 132/66/11kV | E | 2014Q3 | NB2 | TX | 2014-07-06 07:54 | 2014-07-06 08:44 |  |  | CB3432 (66kV) SF6 topup | 132 |  | Forced | 2014
167593 | HV Equipment | CB | No.1 Transformer 132/66/11kV | B | 2014Q3 | NB2 | TX | 2014-07-08 07:15 | 2014-07-08 08:03 |  |  | CB SF6 Topup | 132 |  | Forced | 2014
167601 | HV Equipment | Rx | No.1 330kV Reactor | B | 2014Q3 | AR1 | RX | 2014-07-08 08:10 | 2014-07-08 16:13 |  |  | Outage to top up oil and check oil gauge accuracy, in response to oil level alarm. | 330 |  | Forced | 2014
167651 | Unknown | Cont | 90 Eraring A Bus CB 902A | Q | 2014Q3 | NEW | CB | 2014-07-08 14:36 | 2014-07-08 16:28 |  |  | C.B. failed to open via SCADA during planned switching. Gav Wood requested to investigate. C.B. again failed to open from local MITS. C.B then opened via CDS from control panel. Irregularity issued. | 330 | SSA - No further comment. Issue resolved. |  | 2014
167848 |  |  | 79F Griffith - Yenda 33kV Line |  | 2014Q3 | GRF | TL | 2014-07-09 16:25 | 2014-07-09 16:25 | Protections Reset OK No.3 Buchholz alarm grouped with trip - voltage sensing off 415 board changeover. | follow up required |  | 33 |  |  | 2014
167849 | HV Equipment | CB | No.3 Capacitor | B | 2014Q3 | WL1 | CAP | 2014-07-10 08:10 | 2014-07-10 12:38 |  |  | SF6 Topup | 132 |  | Forced | 2014
167974 | HV Equipment | CB | 806 Goddard Lane 66kV CB 8062 | Q | 2014Q3 | TMW | CB | 2014-07-11 08:46 | 2014-07-11 11:02 |  |  | Inspect oil leak and topup. | 66 |  |  | 2014
167975 | HV Equipment | CB | 22kV Bus Section 1-2 CB 2112 | Q | 2014Q3 | BKH | CB | 2014-07-11 12:19 | 2014-07-11 14:38 |  |  | SF6 topup following alarm. | 22 |  |  | 2014
167994 | HV Equipment | Disc | No.4 Transformer 330/132/11KV | B | 2014Q3 | SYN | TX | 2014-07-11 16:19 | 2014-07-11 18:35 |  |  | Inspect and align disconnector contacts | 330 |  | Forced | 2014
168075 |  |  | No.2 330KV Capacitor |  | 2014Q3 | WOTS | CB | 2014-07-13 15:43 | 2014-07-18 15:43 |  | follow up required |  | 330 |  |  | 2014
168089 | Condition Monitor | T/C | No.3 Transformer 330/132/11kV | E | 2014Q3 | WRH | TX | 2014-07-14 07:35 | 2014-07-14 11:23 | Alarms Received - Waratah West No.3 Tx Tap Changer Fault & Condition Monitor L1 Urgent alarm. Maintenance Manager advised tap changer fault alarm generated the Condition Monitor L1 Urgent alarm, Transformer ok to be returned to service. | 23/07/2014 2:14:00 PM ¦ follow up required ¦ Nil. ¦ A work request has been submitted to the Control Systems Group to have the No.3 Transformer tap changer L1 urgent alarms modified. | The L1 alarm was initiated by the tap changer fault. This alarm had been incorrectly grouped with the transformer’s L1 urgent alarms. The tap changer fault alarm output was isolated from the L1 alarm group. The No.3 Transformer On-Load Tap Changer (OLTC) was tested and operated successfully on 14/07/2014. The No.3 Transformer was returned to service on 14/07/2014 at 11:23hrs. | 330 |  | Forced | 2014
168125 |  |  | 97L Guthega - Jindabyne Pumps 132kV TL | X | 2014Q3 | GTH | TL | 2014-07-17 15:49 | 2014-07-17 16:06 |  |  |  | 132 |  |  | 2014
168156 |  |  | 963 Tomago330 - Taree T Hawksnest 132kV TL | X | 2014Q3 | TRE, TOM | TL | 2014-08-06 07:50 | 2014-08-06 17:54 |  |  |  | 132 |  |  | 2014
168228 |  |  | No.3 Transformer 132/33/11kV | B | 2014Q3 | WG2 | TX | 2014-07-16 08:47 | 2014-07-16 14:08 |  |  |  | 132 |  | Forced | 2014
168231 |  |  | 99W Wagga 330 - Wagga 132 132kV TL | B | 2014Q3 | WG2, WG1 | TL | 2014-07-16 08:47 | 2014-07-16 14:08 |  |  |  | 132 |  | Forced | 2014
168270 |  |  | 804 Tamworth 132 - Nundle 66kV Line |  | 2014Q3 | TMW | TL | 2014-07-16 08:06 | 2014-07-16 08:06 | 804 Nundle Feeder overhead earth wire low to phase wires. Stunned bird on ground under feeder. | follow up required |  | 66 |  |  | 2014
168281 | HV Equipment | CVT | No.2 Transformer 330/132/16kV | E | 2014Q3 | CA1 | TX | 2014-07-16 19:07 | 2014-07-18 16:46 |  |  | At 18:52hrs the 330kV B1 Bus was taken out of service at Canberra on advice received from field staff of a suspect C.V.T. following reciept of a "C.V.T. unbalance" alarm. | 330 |  | Forced | 2014
168285 | Animal/Bird | TL | 9U2 Inverell - Moree 132kV TL | Q | 2014Q3 | INV, MRE | TL | 2014-07-16 19:58 | 2014-07-16 19:58 | Mick Tarbert was at MRE investigating a control system fault and was able to provide MRE prot'n details Distance to fault from Inverell - 109.7 | 5/08/2014 12:49:00 PM ¦ follow up required ¦ Nil. ¦ Nil. | On Wednesday 16/07/2014 at 19:58hrs, the 132kV 9U2TL from Inverell 132kV Substation to Moree 132kV Substation tripped and auto-reclosed both at Inverell 132kV Substation and Moree 132kV Substation. Protection flagging indicated a zone 1, W phase to B phase fault. The fault location was indicated as being 109.7 km from Inverell 132kV Substation. No lightning activity was observed during the time of the incident. On Thursday 17/07/2014, an initial inspection was carried out from structure 460-480 and found no evidence of fault. On Friday 25/07/2014, during a routine ground inspection, a dead pelican was found in the mid span between structure 502 and 503. The bird had a burn hole in its back. The top phase conductor showed signs of arcing but no damage to conductor was found. | 132 |  |  | 2014
168303 | HV Equipment | CB | 78 Sydney South A CB 782A | Q | 2014Q3 | ING | CB | 2014-07-17 10:42 | 2014-07-17 13:13 |  |  | SF6 topup | 330 |  |  | 2014
168321 | HV Equipment | SVC | No.1 Static VAr Compensator | Z | 2014Q3 | BKH | SVC | 2014-07-17 13:20 | 2014-07-19 14:35 | visual inspection found 7th harmonic filter has failed | 11/09/2014 2:46:00 PM ¦ follow up required | Visual inspection found 7th harmonic filter has failed No 1 SVC Tripped out on 17/07/14 due to a melted joint on the 7th harmonic filter star point conductor. Conductor was repaired using 40 x 2.5 copper strap, brazing the legs of the phases to the strap. Section was re-birdproofed. Capacitance measured on cans and all OK. | 22 |  | Fault | 2014
168349 | HV Equipment | VT | Phase Shifting Transformer | B | 2014Q3 | AR1 | TX | 2014-07-18 13:08 | 2014-07-18 14:37 |  |  | OIL SAMPLE 132 KV CVT'S | 132 |  | Forced | 2014
168380 | Unknown | TL | 97L Guthega - Jindabyne Pumps 132kV TL | Z | 2014Q3 | GTH | TL | 2014-07-18 07:47 | 2014-07-18 18:11 | Aerial Patrol advises no obvious defects observed. Local conditions are Snow, Ice and Very Windy. | follow up required | At 07:47hrs 97G Murray to Guthega tee Geehi 132 kV T/L & 97L Guthega to Jindabyne Pumps 132 kV T/L both tripped. Advises no defects inspected at Guthega 132kV Switching Station. Switchgear and incomings T/L's appear OK. Advises will perform an aerial patrol of both 97G & 97L T/L's. Request inspect 97G first, and the first 10% of the line out of Guthega 132kV Switching Station. Aerial Patrol advises no obvious defects observed. Local conditions are Snow, Ice and Very Windy. | 132 | Need to investigate protection settings. Resolved. | Fault | 2014
168381 | Unknown | TL | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2014Q3 | GTH, MUR, GHI | TL | 2014-07-18 07:47 | 2014-07-18 15:48 | Aerial Patrol advises no obvious defects observed. Local conditions are Snow, Ice and Very Windy. | 10/10/2014 2:14:00 PM ¦ follow up required ¦ Nil. ¦ Nil. | At 07:47hrs 97G Murray to Guthega tee Geehi 132 kV T/L & 97L Guthega to Jindabyne Pumps 132 kV T/L both tripped. Advises no defects inspected at Guthega 132kV Switching Station. Switchgear and incomings T/L's appear OK. Advises will perform an aerial patrol of both 97G & 97L T/L's. Request inspect 97G first, and the first 10% of the line out of Guthega 132kV Switching Station. Aerial Patrol advises no obvious defects observed. Local conditions are Snow, Ice and Very Windy. | 132 | Need to investigate protection settings. Resolved. | Fault | 2014
168382 |  |  | 97G/3 Geehi Tee CB 97G2 |  | 2014Q3 | GTH | CB | 2014-07-18 07:47 | 2014-07-18 15:48 |  |  |  | 132 |  |  | 2014
168383 |  |  | 97G/1 Geehi Tee CB 97G2 |  | 2014Q3 | MUR | CB | 2014-07-18 07:47 | 2014-07-18 15:48 |  |  |  | 132 |  |  | 2014
168449 | HV Equipment | CB | No.3 Transformer 132/66/11kV | B | 2014Q3 | NB2 | TX | 2014-07-21 12:41 | 2014-07-21 13:43 |  |  | TOPUP CB 3432 WITH SF6 GAS | 132 |  | Forced | 2014
168471 |  |  | 92Z Sydney North tee Mt Colah 132kV CB 92Z2 |  | 2014Q3 | SE1 | CB | 2014-07-22 05:05 | 2014-07-22 05:05 | Calculated 8MW load lost. | follow up required |  | 132 |  |  | 2014
168495 | LV/MECH Fail | T/C | No.2 Transformer 132/66/11kV | B | 2014Q3 | CMA | TX | 2014-07-23 09:47 | 2014-07-23 13:00 |  |  | Tapchanger - repair and operate Dial switch refurbishment to rectify misalignment issues. | 132 |  | Forced | 2014
168506 | HV Equipment | Rx | No.3 Transformer Reactor | Q | 2014Q3 | DNT | RX | 2014-07-22 10:36 | 2014-07-24 13:19 | Flashover damage internally on B phase air core reactor one leg to earth. | 18/03/2015 2:32:00 PM ¦ follow up required | Advises Trip caused by Flashover of No.3 Air Cooled reactor. Signs to suggest both internal and external flashover Blue phase to earth. Russell Ubrihien reports the air cooled reactor showed signs of external and internal flashovers on Blue phase to earth. An outage will be arranged to replace the reactor with an on site spare. NOS entry will be arranged when Package created. | 33 |  |  | 2014
168516 | HV Equipment | CB | No.1 Capacitor | E | 2014Q3 | SYW | CAP | 2014-07-22 13:30 | 2014-07-22 17:03 |  |  | SF6 topup | 132 |  | Forced | 2014
168518 | HV Equipment | TL | 26 Munmorah - Sydney West 330kV TL | B | 2014Q3 | MN1, SYW | TL | 2014-07-22 16:53 | 2014-07-23 15:07 |  |  | Replacement of insulators | 330 |  | Forced | 2014
168519 |  |  | U5 Upper Tumut - Tumut 2 330kV TL | X | 2014Q3 | UT1 | TL | 2014-08-05 08:59 | 2014-08-05 15:39 |  |  |  | 330 |  |  | 2014
168733 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2014Q3 | CW2 | TL | 2014-07-24 14:47 | 2014-07-24 14:47 |  | follow up required |  | 66 |  |  | 2014
168754 | HV Equipment | CT | 80C Tamworth 132 - Goddard Lane 66kV Line | Q | 2014Q3 | TMW | TL | 2014-07-25 13:01 | 2014-07-29 15:53 |  |  | 80C De-energised due to CT gas leak to be repaired Monday. | 66 |  |  | 2014
168759 | HV Equipment | CT | 97R Cooma - Steeple Flat 132kV Line | Q | 2014Q3 | CMA | TL | 2014-07-25 17:54 | 2014-07-25 18:56 |  |  | SF6 topup | 132 |  |  | 2014
168763 | Animal/Bird | TX | No.3 Transformer 132/66kV | E | 2014Q3 | ORG | TX | 2014-07-25 15:11 | 2014-07-25 17:41 | Bird nesting on Gantry above Transformer. Wire hanging down more than half the length of the insulator string. | 27/08/2014 11:09:00 AM ¦ follow up required ¦ Nil ¦ Nil | Huw Greenhill advised Bird nesting on Gantry above Transformer. Wire hanging down encroaching minimum clearances. The wire was associated with a bird nesting in the gantry structure and was bridging across more than half a string insulator. An outage was taken of No.3 Transformer at 15:11 to remove the wire and bird nest. No.3 Transformer was returned to service at 17:41hrs on the same day. | 132 |  | Forced | 2014
168769 |  |  | 850 Tumut - Talbingo tee Jounama Dam 66kV Line |  | 2014Q3 | TU2 | TL | 2014-07-25 17:31 | 2014-07-26 13:28 | Approx 1 MW of customer load lost @ 17:31 and restored via T3 reactor supply at 20:34 7MW of Generation lost | follow up required |  | 66 |  |  | 2014
168774 |  |  | 66kV Bus No.3 Section | Q | 2014Q3 | ORG | BB | 2014-07-26 13:48 | 2014-07-26 18:25 | No.4 Tx was O/S at the time of trip on open CB's and suspect Blue phase centre pivot on No.4 Tx 66kV Bus ABS 3443,(visable burn marks at top of insulator and on steel work support structure) thought to have caused trip of Sect 3 66kV BB, however collapsed contacts of No.1 prot'n IOC relay caused No.2 66kV sect BB to trip. | 27/08/2014 11:07:00 AM ¦ follow up required ¦ Nil ¦ Nil |  | 66 |  |  | 2014
168775 |  |  | No.3 Transformer 132/66kV | Z | 2014Q3 | ORG | TX | 2014-07-26 13:48 | 2014-07-26 18:25 |  |  |  | 132 |  | Fault | 2014
168776 |  |  | 66kV Bus No.2-3 Section CB 3112 |  | 2014Q3 | ORG | CB | 2014-07-26 13:48 | 2014-07-26 18:25 |  |  |  | 66 |  |  | 2014
168777 |  |  | No.4 Transformer 132/66KV | Z | 2014Q3 | ORG | TX | 2014-07-26 13:48 | 2014-07-26 18:25 |  |  |  | 132 |  | Fault | 2014
168778 |  |  | 8M2 Orange - Orange Industrial 66kV Line |  | 2014Q3 | ORG | TL | 2014-07-26 13:48 | 2014-07-26 18:25 |  |  |  | 66 |  |  | 2014
168779 |  |  | No.7 Orange - Orange North 66kV Line | S | 2014Q3 | ORG | TL | 2014-07-26 13:48 | 2014-07-26 18:25 |  |  |  | 66 |  |  | 2014
168780 |  |  | 8C2 Orange - Orange West 66kV Line | S | 2014Q3 | ORG | TL | 2014-07-26 13:48 | 2014-07-26 18:25 |  |  |  | 66 |  |  | 2014
168781 |  |  | 8W2 Orange - Orange West Frequency Injection |  | 2014Q3 | ORG | TL | 2014-07-26 13:48 | 2014-07-26 18:25 |  |  |  | 66 |  |  | 2014
168782 |  |  | 66kV Bus No.2 Section | Q | 2014Q3 | ORG | BB | 2014-07-26 13:48 | 2014-07-26 15:49 | Suspect Blue phase centre pivot on ABS 3443,(visable burn marks at top of insulator and on steel work support structure) thought to have caused trip of Sect 3 66kV BB, however welded close contacts of No.1 prot'n IOC relay caused No.2 66kV sect BB to trip. | 27/08/2014 11:08:00 AM ¦ follow up required ¦ Nil ¦ Nil |  | 66 |  |  | 2014
168783 |  |  | No.1 Capacitor | Z | 2014Q3 | ORG | CAP | 2014-07-26 13:48 | 2014-07-26 15:49 |  |  |  | 66 |  | Fault | 2014
168784 |  |  | 66kV Bus No.2-3 Section CB 3112 |  | 2014Q3 | ORG | CB | 2014-07-26 13:48 | 2014-07-26 15:49 |  |  |  | 66 |  |  | 2014
168785 |  |  | 66kV Bus No.1-2 Section CB 3102 |  | 2014Q3 | ORG | CB | 2014-07-26 13:48 | 2014-07-26 15:49 |  |  |  | 66 |  |  | 2014
168786 |  |  | 807 Orange - Orange West T Orange South 66kV Line | S | 2014Q3 | ORG | TL | 2014-07-26 13:48 | 2014-07-26 15:49 |  |  |  | 66 |  |  | 2014
168787 | HV Equipment | Prot | No.5 Orange - Orange North 66kV Line | S | 2014Q3 | ORG | TL | 2014-07-26 13:48 | 2014-07-26 15:49 |  |  | Suspect Blue phase centre pivot on ABS 3443,(visable burn marks at top of insulator and on steel work support structure) thought to have caused trip of Sect 3 66kV BB, however welded close contacts of No.1 prot'n IOC relay caused No.2 66kV sect BB to trip | 66 | Relay replaced, resolved. |  | 2014
168788 |  |  | No.6 Orange - Orange North 66kV Line | S | 2014Q3 | ORG | TL | 2014-07-26 13:48 | 2014-07-26 15:49 |  |  |  | 66 |  |  | 2014
168789 |  |  | 8C1 Molong - Cumnock Tee Orange West 66kV Line |  | 2014Q3 | MOL | TL | 2014-07-26 15:06 | 2014-07-26 15:16 |  | follow up required |  | 66 |  |  | 2014
168815 |  |  | 96M Narrabri - Moree 132kV TL | X | 2014Q3 | MRE, NB2 | TL | 2014-07-31 08:54 | 2014-07-31 09:14 |  |  |  | 132 |  |  | 2014
168832 |  |  | No.3 Transformer 132/66kV | B | 2014Q3 | ORG | TX | 2014-07-29 08:50 | 2014-07-29 13:27 |  |  |  | 132 |  | Forced | 2014
168834 |  |  | No.2 Munyang - Perisher 33kV Line |  | 2014Q3 | MNY | TL | 2014-07-28 15:34 | 2014-07-28 19:02 | Essential Energy requested feeder Isolated and Earthed due to broken drop out fuse assembly in the customer system. | follow up required |  | 33 |  |  | 2014
168835 |  |  | No.2 Transformer 132/33/11kV | Y | 2014Q3 | MNY | TX | 2014-07-28 15:34 | 2014-07-28 19:02 |  |  |  | 132 |  |  | 2014
168887 | Relay | Prot | No.1 Transformer 132/33/11kV | Z | 2014Q3 | KS2 | TX | 2014-07-29 17:00 | 2014-07-29 17:35 | Advised of trip on energising. Advises issue was TC overpressure had operated MTR previously. Relay reset and nil volts checked across link on RTS. Protection now reset via pushbutton on panel and No.1 TX RTS. | follow up required ¦ Nil. ¦ A defect work order (331076) has been created by Secondary Systems Group to have the similar relays modified. <Duplicate Record> 28/08/2014 1:14:00 PM ¦ follow up required ¦ Nil. ¦ A defect work order (331076) has been created by Secondary Systems Group to have similar relays modified. | Advised of trip on energising. Advises issue was TC overpressure had operated MTR previously. Relay reset and nil volts checked across link on RTS. Protection now reset via pushbutton on panel and No.1 TX RTS. The tap changer pressure relief device had been inadvertently operated during the Substation routine maintenance work and although a check of the Tx multitrip relays was carried out at the end of the maintenance work, the No.1 Multitrip relay had operated despite showing no flag. Following the second trip, further investigations by Protection staff found that the multitrip flag was jamming due to lifting of the red indication paper attached to the flag facia. The paper was removed and the facia was painted with red paint. The No.2 Multitrip relay showed signs of the same problem and was also repaired. | 132 | SSA - First time occurrence of this type of fault. Not thought to be a major issue. Issue closed. | Fault | 2014
168916 |  | CB | 26 Munmorah B CB 262B | Q | 2014Q3 | SYW | CB | 2014-07-30 10:43 | 2014-07-30 13:02 |  |  | Advises unable to close 26 Sydney West to Munmorah CB 262B at Sydney West 330kV Substation via SCADA. Request SMF/Mick Simms to close 26 Sydney West to Munmorah CB 262B via CDS. Advises unable to close. 0714hrs T/TL Paul Hazeltine - Request staff investigate CB failure to close. RFA submitted and HVPRI to be prepare to investigate. | 330 | Pole discrepancy alarm was missing (not wired through). Now is wired, SSE advises investigation closed. |  | 2014
168922 |  |  | M7 Murray - Murray 1 330kV TL | X | 2014Q3 | MUR | TL | 2014-08-12 08:00 | 2014-08-22 13:50 |  |  |  | 330 |  |  | 2014
168923 |  |  | M9 Murray - Murray 1 330kV TL | X | 2014Q3 | MUR | TL | 2014-08-12 09:48 | 2014-08-12 15:02 |  |  |  | 330 |  |  | 2014
168957 |  |  | No.2 Transformer 132/33/11kV | Y | 2014Q3 | MNY | TX | 2014-07-29 18:04 | 2014-07-30 12:02 |  |  |  | 132 |  |  | 2014
168969 |  |  | 132kV B Bus No.2 Section |  | 2014Q3 | CA1 | BB | 2014-07-30 13:53 | 2014-07-30 18:06 | Wire from birds nest on bus gantry fell across underslung insulator | 11/09/2014 2:53:00 PM ¦ follow up required |  | 132 |  |  | 2014
168970 |  |  | No.3 Transformer 132kV B CB 4432B |  | 2014Q3 | CA1 | CB | 2014-07-30 13:53 | 2014-07-30 18:06 |  |  |  | 132 |  |  | 2014
168971 |  |  | No.4 Transformer 132kV BCB 4442B |  | 2014Q3 | CA1 | CB | 2014-07-30 13:53 | 2014-07-30 18:06 |  |  |  | 132 |  |  | 2014
168972 |  |  | 132kV B Bus 1-2 Section CB 4112 |  | 2014Q3 | CA1 | CB | 2014-07-30 13:53 | 2014-07-30 18:06 |  |  |  | 132 |  |  | 2014
168973 | Animal/Bird | Cap | No.3 Capacitor | Z | 2014Q3 | CA1 | CAP | 2014-07-30 13:53 | 2014-07-30 18:06 |  |  | Wire from birds nest on bus gantry fell across underslung insulator 132kV No2 Section B bus at Canberra tripped due to flashover caused by crows nest. Crows nest was made up of assortment of wires. Underslung insulator and conductor inspected and cleaned, All OK. Remaining nest removed. R.Cox | 132 |  | Fault | 2014
168974 |  |  | No.3 Canberra - Gold Creek 132kV Line |  | 2014Q3 | CA1 | TL | 2014-07-30 13:53 | 2014-07-30 18:06 |  |  |  | 132 |  |  | 2014
168986 |  |  | 828 Tumut - Gundagai 66kV Line |  | 2014Q3 | TU2 | TL | 2014-07-30 14:59 | 2014-07-30 14:59 |  | follow up required |  | 66 |  |  | 2014
169014 |  |  | No.3 Coleman St 66kV CB 32 |  | 2014Q3 | WG2 | CB | 2014-07-31 08:14 | 2014-07-31 08:56 |  | follow up required |  | 66 |  |  | 2014
169020 | Condition Monitor | TX | No.6 330/132/11kV Transformer | E | 2014Q3 | TOM | TX | 2014-07-31 09:24 | 2014-07-31 11:48 | Condition Monitoring Urgent Alarm Received - Transformer removed from service pending investigation | 6/08/2014 3:06:00 PM ¦ follow up required ¦ Nil. ¦ Nil. | Condition Monitoring Urgent Alarm Received - Transformer removed from service. Received advice from Ken Wiper That analysis of condition monitoring clears No.6 Tx from any bushing fault further analysis to continue and request to energise Transformer and endorsed by asset owner Graham francis. Receive clearance from Tony Grey (asset owner) and endorsed by Graham francis to return No.6 Tx and to command block Condition Monitoring Urgent alarm for 24 hours until condition monitoring unit has recalibrated over 24 hours then command block lifted. The L1 alarm was initiated by the Doble Bushing Monitor device. Further investigation suggested that the alarm was false and the condition of the bushings was normal. The No.6 Transformer was returned to service on Thursday 31/07/2014 at 11:48hrs. | 330 | Investigation ongoing. | Forced | 2014
169022 |  |  | O97B Tumut - Blowering 132kV TL | X | 2014Q3 | TU2 | TL | 2014-08-05 09:37 | 2014-08-07 09:31 |  |  |  | 132 |  |  | 2014
169074 |  |  | 82B Queanbeyan - High St 66kV Line |  | 2014Q3 | QBY | TL | 2014-07-31 12:53 | 2014-07-31 12:53 | TAR on 82B High Street feeder. High winds reported in the area. | follow up required |  | 66 |  |  | 2014
169077 |  |  | 82B Queanbeyan - High St 66kV Line |  | 2014Q3 | QBY | TL | 2014-07-31 13:15 | 2014-07-31 13:15 | TAR on 82B High Street 66kV Feeder at Queanbeyan 132kV Substatiion. High winds in the area reported. | follow up required |  | 66 |  |  | 2014
169083 | HV Equipment | Bus | No.2 Transformer 330/132/16kV | E | 2014Q3 | CA1 | TX | 2014-07-31 14:57 | 2014-07-31 15:07 |  |  | Field staff advised of a wire hanging down partially across insulator. Required O/S to take service to effect repairs. | 330 |  | Forced | 2014
169085 |  |  | No.2 Capacitor | E | 2014Q3 | CA1 | CAP | 2014-07-31 14:57 | 2014-07-31 15:07 |  |  |  | 132 |  | Forced | 2014
169087 |  |  | 976/1 Canberra - Queanbeyan/Spring Flat 132kV TL | E | 2014Q3 | QBN | TL | 2014-07-31 14:57 | 2014-07-31 15:07 |  |  |  | 132 |  | Forced | 2014
169089 |  |  | 82B Queanbeyan - High St 66kV Line |  | 2014Q3 | QBY | TL | 2014-07-31 11:27 | 2014-07-31 11:27 |  | follow up required |  | 66 |  |  | 2014
169090 |  |  | 82B Queanbeyan - High St 66kV Line |  | 2014Q3 | QBY | TL | 2014-07-31 12:05 | 2014-07-31 12:05 |  | follow up required |  | 66 |  |  | 2014
169091 |  |  | 82B Queanbeyan - High St 66kV Line |  | 2014Q3 | QBY | TL | 2014-07-31 12:32 | 2014-07-31 12:32 |  | follow up required |  | 66 |  |  | 2014
169095 | Wiring Design | Aux Tx | No.3 Transformer 330/132/11kV | B | 2014Q3 | MN1 | TX | 2014-08-01 10:02 | 2014-08-01 15:37 |  |  | Correct phasing of Aux Transformer | 330 |  | Forced | 2014
169178 |  |  | No.3 Tenterfield - Council (Timbarra Mine) 22kV Line |  | 2014Q3 | TTF | TL | 2014-08-01 14:22 | 2014-08-01 17:09 | Windy weather conditions. | follow up required |  | 22 |  |  | 2014
169215 | HV Equipment | TX | No.3 Transformer 330/132/16kV | B | 2014Q3 | CA1 | TX | 2014-08-02 10:59 | 2014-08-04 15:30 |  |  | Top Up Oil | 330 |  | Forced | 2014
169224 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2014Q3 | GRF | TL | 2014-08-02 10:37 | 2014-08-02 10:37 |  | follow up required |  | 33 |  |  | 2014
169225 | HV Equipment | CB | 79J Griffith - Griffith Zone Standby 33kV Line | Q | 2014Q3 | GRF | TL | 2014-08-03 05:04 | 2014-08-03 10:36 |  |  | SF6 topup | 33 |  |  | 2014
169226 | HV Equipment | CB | No.2 Capacitor | Q | 2014Q3 | YA2 | CAP | 2014-08-03 13:48 | 2014-08-03 16:26 |  |  | SF6 topup | 33 |  |  | 2014
169289 |  |  | M9 Murray - Murray 1 330kV TL | X | 2014Q3 | MUR | TL | 2014-08-19 08:04 | 2014-08-19 16:46 |  |  |  | 330 |  |  | 2014
169290 | LV/MECH Fail | CB | U7 Tumut 2 CB U72 | Q | 2014Q3 | UT1 | CB | 2014-08-04 11:53 | 2014-08-04 17:37 |  |  | Received advice from SHL that attempted to close U7 twice but CB U72 failed to close. SCADA only indicates one attempt to close. Staff to investigate. 14:20 SMF Nathan advises CB..U72 failure to close caused by closing spring not charged and no alarms were received on the HMI or SCADA. 16:00 SMF Nathan advises CB..U72 testing completed and CB..U72 tested OK. 16:18 SHL Mick advises U7 Tumut 2 PS CB.. U72 Ready for service and SHL OK to attempt to place U7 Tumut 2 PS CB.. U72 into service. 16:25 SHL Mick advised U7 Tumut 2 PS CB.. U72 failed to close and Units 7 & 8 shut down. 17:18 SMF Nathan advises found an alarm on SHL's 7/8 Group auto synchronizer located in relay room and alarm reset when acknowledged. 17:25 SHL Mick advised of alarm on SHL's 7/8 Group auto synchronizer and alarm reset 17:30 SHL Mick advises will attempt to place U7 Tumut 2 PS CB.. U72 into service. 17:33 SHL Mick advises U7 Tumut 2 PS CB.. U72 closed and Units 7 & 8 in-service | 330 | There have been no further issues with the CB since this was completed on 26/8/14. The basic detail is that the spring charge motors were all running simultaneously once a close was initiated and on the 120v supply system this was dropping the battery operating voltage to around 120v approx 10v less than float. Adjustments were made to the spring mechanisms to prevent future occurrence of this issue. SSE advises investigation closed. |  | 2014
169534 | Condition Monitor | TX | No.6 330/132/11kV Transformer | E | 2014Q3 | TOM | TX | 2014-08-06 11:49 | 2014-08-07 14:40 | Condition Monitoring alarm received, TX taken out of service. | 26/09/2014 3:11:00 PM ¦ follow up required ¦ Nil. ¦ Nil. | Condition Monitoring alarm received, TX taken out of service. | 330 |  | Forced | 2014
169600 | Unknown | TL | 973 Yass - Cowra 132kV TL | Q | 2014Q3 | CW2, YSN | TL | 2014-08-07 06:40 | 2014-08-07 06:40 | No sign of storms on Indji. | 8/09/2014 1:05:00 PM ¦ follow up required ¦ Nil. ¦ A close inspection of the line section will be carried out in the next aerial inspection. |  | 132 |  |  | 2014
169609 | HV Equipment | CB | No.1 Capacitor | Q | 2014Q3 | TRE | CAP | 2014-08-07 13:11 | 2014-08-07 14:46 |  |  | Investigate CB fail to operate | 33 |  |  | 2014
169759 |  |  | 847 Murrumburrah - Boorowa 66kV Line |  | 2014Q3 | MRU | TL | 2014-08-10 08:50 | 2014-08-10 08:50 |  | follow up required |  | 66 |  |  | 2014
169780 |  |  | U1 Upper Tumut - Tumut 1 330kV TL | X | 2014Q3 | UT1 | TL | 2014-08-20 08:24 | 2014-08-22 16:22 |  |  |  | 330 |  |  | 2014
169820 |  |  | No.1 Transformer 132/11/11kV |  | 2014Q3 | GAD | TX | 2014-08-11 14:20 | 2014-08-11 17:21 | No.1 Transformer tripped due to an apparant fault in the 11kV network at VISY Mill. | 25/05/2015 9:04:00 AM ¦ follow up required |  | 132 |  |  | 2014
169835 |  |  | 996 Wagga 330 - ANM tee Morven 132kV TL | X | 2014Q3 | ANM, WG1 | TL | 2014-08-12 10:21 | 2014-08-12 16:17 |  |  |  | 132 |  |  | 2014
169854 | HV Equipment | CB | 81 Newcastle CB 812 | Q | 2014Q3 | LD1 | CB | 2014-08-15 07:36 | 2014-08-15 11:57 |  |  | CB SF6 Topup | 330 |  |  | 2014
170016 |  |  | U3 Upper Tumut - Tumut 1 330kV TL | X | 2014Q3 | UT1 | TL | 2014-08-26 08:14 | 2014-08-28 16:10 |  |  |  | 330 |  |  | 2014
170102 |  |  | No.3 Transformer Reactor |  | 2014Q3 | DNT | RX | 2014-08-15 08:50 | 2014-08-15 11:24 | Suspect caused by loss of DC supplies during DC Switching operations. Reason for Trip unknown | 11/09/2014 3:50:00 PM ¦ follow up required |  | 33 |  |  | 2014
170115 | HV Equipment | CB | No.2 Transformer 132/66/11kV | E | 2014Q3 | PKS | TX | 2014-08-15 15:19 | 2014-08-15 16:58 |  |  | SF6 Topup | 132 |  | Forced | 2014
170140 |  |  | 79L Griffith - Beelbangera 33kV Line |  | 2014Q3 | GRF | TL | 2014-08-16 10:46 | 2014-08-16 10:46 |  | follow up required |  | 33 |  |  | 2014
170170 |  |  | 841 Yanco - Narrandera 66kV Line |  | 2014Q3 | YA2 | TL | 2014-08-18 10:20 | 2014-08-18 10:20 | Distance to fault 16km. | follow up required |  | 66 |  |  | 2014
170171 |  |  | No.4 Transformer 66/33/11kV |  | 2014Q3 | YA2 | TX | 2014-08-18 10:20 | 2014-08-18 10:20 |  |  |  | 66 |  |  | 2014
170194 | LV/MECH Fail | Meter | No.3 Transformer 132/33/11kV | E | 2014Q3 | GRF | TX | 2014-08-18 14:53 | 2014-08-26 09:32 |  |  | Blue phase metering CT faulty. | 132 | SSA - Contractor issue. Blue phase CT wiring was not terminated despite producing records indicating it had ben checked. Defect not picked up during commissioning but during post energisation checks. CB operation was manual not trip. Wiring issue resolved. | Forced | 2014
170261 | Staff Error | Proc | No.4 Transformer 66/33/11kV | S | 2014Q3 | YA2 | TX | 2014-08-19 11:00 | 2014-08-19 11:10 | Protection Tech advised that No.4 Transformer (841 Narrendra) tripped while wiring work was being carried out on 33kV Bus Bar Protection panel. Cause of the trip is under investigation and they have reset the protection. No.4 Transformer (841 Narrendra) restored with clearance from Essential Energy. | 18/09/2014 4:20:00 PM ¦ follow up required | Protection Tech advised that No.4 Transformer (841 Narrendra) tripped while wiring work was being carried out on 33kV Bus Bar Protection panel. Cause of the trip is under investigation and they have reset the protection. No.4 Transformer (841 Narrendra) restored with clearance from Essential Energy. Upon investigation it was found tha a phoenix link had been installed upside down which caused a trip when new wiring was laid down. Link removed and installed correctly. | 66 | SSA - Blanking plate was ommitted from design, will raise issue with Design to prevent future re-occurrence. |  | 2014
170262 |  |  | 841 Yanco - Narrandera 66kV Line | Q | 2014Q3 | YA2 | TL | 2014-08-19 11:00 | 2014-08-19 11:10 |  |  |  | 66 |  |  | 2014
170283 | Unknown | Cap | No.5 Capacitor | E | 2014Q3 | SYW | CAP | 2014-08-19 13:10 | 2015-05-13 14:15 |  | Follow up ¦ Nil ¦ Nil | At 13:11hrs Sydney West 330kV Substation #5 Cap de-energised after receiving "Neutral Unbalance" alarm at Sydney West 330kV Substation. NOTE: Unbalance was to alarm limit but not trip limit. Alarm not received via SCADA but was detected by staff working in Relay Room, who requested Control Room staff to de-energise capacitor bank. Staff to investigate neutral unbalance and lack of SCADA alarm. AEMO notified #5 Cap unavailable. | 132 | SSA - Potential database issue causing alarm not to go through to SCADA. Further testing required to determine root cause. Staff looked into issue on 4th-5th September, no issues found. SSE considers investigation complete. | Forced | 2014
170414 |  |  | U7 Upper Tumut - Tumut 2 330kV TL | X | 2014Q3 | UT1 | TL | 2014-09-01 09:04 | 2014-09-08 16:54 |  |  |  | 330 |  |  | 2014
170431 | Pollution | TL | 967 Lismore 330 - Koolkhan 132kV TL | Q | 2014Q3 | KLK, LSM | TL | 2014-08-20 18:43 | 2014-08-20 18:43 | trip apparantly caused by burn at a sugarcane farm in the vacinity of 967 T/L. | 25/09/2014 1:55:00 PM ¦ follow up required ¦ Nil. ¦ A detailed inspection of this area of the line will be carried out during upcoming aerial patrols. | Trip apparently caused by burning at a sugarcane farm in the vicinity of 967 T/L. A maintenance fitter inspected the area the following day and found no signs of any damage. Protection maintenance group investigated the trip sequence and determined that everything operated as expected for the given fault conditions | 132 |  |  | 2014
170452 | HV Equipment | CB | 78 Sydney South A CB 782A | Q | 2014Q3 | ING | CB | 2014-08-21 15:31 | 2014-08-21 18:11 |  |  | SF6 Topup. | 330 |  |  | 2014
170490 | HV Equipment | CB | 932 Sydney West - Mt Druitt 132kV Line | B | 2014Q3 | SYW | TL | 2014-08-21 19:25 | 2014-08-21 20:51 |  |  | Top up low SF6 | 132 |  | Forced | 2014
170547 | LV/MECH Fail | CB | No.4 Bay Coupler CB 5042 | Q | 2014Q3 | MRN | CB | 2014-08-23 10:30 | 2014-08-29 13:02 |  |  | Advises problem with hydraulic control circuit and pressure switch. Enough hydraulic pressure to close C.B. and C.B. will trip OK. May be issue with further attempts to close C.B. NCM advised and No.4 Bay Coupler C.B.. 5042 to be left open. | 330 | Defective CB circuitry was repaired. SSE advises investigation closed. |  | 2014
170551 | HV Equipment | CB | No.3 Capacitor | E | 2014Q3 | WL1 | CAP | 2014-08-24 14:59 | 2014-08-24 17:07 | CB 4732 isolated & topped up with SF6. Now RTS. | 14/11/2014 10:30:00 AM ¦ follow up required ¦ Nil ¦ Nil | SF6 Topup | 132 |  | Forced | 2014
170587 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2014Q3 | GRF | TL | 2014-08-25 06:55 | 2014-08-25 06:55 |  | follow up required |  | 33 |  |  | 2014
170597 | Lightning/Storm | TL | 5 Yass - Marulan 330kV TL | Z | 2014Q3 | MRN, YSN | TL | 2014-08-25 16:01 | 2014-08-25 18:30 | Storms in area. | 8/09/2014 12:07:00 PM ¦ follow up required ¦ Nil ¦ A close inspection of the line section will be carried out in the next aerial inspection. | At 15:43hrs 5 Yass to Marulan 330 kV T/L tripped. No reclose attempted. Fault recorder operated at Yass, Marulan and Bannaby. Storms in the area. Staff to be called out to investigate. The auto-reclose issue at Yass was rectified and a ground patrol was conducted at targeted areas between structures 160 and 205 to assess any damage on the line or potential cause of the trip. Nothing untoward was found. | 330 | Database updated to fix the auto-reclose issue. | Fault | 2014
170598 |  |  | M13 Murray - Murray 2 330kV TL | Y | 2014Q3 | MUR | TL | 2014-08-25 23:20 | 2014-08-26 16:19 | SHL confirms operation of Unit 13 & 14 Gennerator Transformer "B" Differential Protection at Murray 2 Power Station | follow up required |  | 330 |  |  | 2014
170599 |  |  | M13 Murray 2 A CB M132A |  | 2014Q3 | MUR | CB | 2014-08-25 23:20 | 2014-08-26 16:19 |  |  |  | 330 |  |  | 2014
170600 |  |  | M13 Murray 2 B CB M132B |  | 2014Q3 | MUR | CB | 2014-08-25 23:20 | 2014-08-26 16:19 |  |  |  | 330 |  |  | 2014
170609 | HV Equipment | CB | No.2 Capacitor | Q | 2014Q3 | TRE | CAP | 2014-08-26 12:20 | 2014-08-26 14:52 |  |  | Carry out CB Timing Checks as required. | 33 |  |  | 2014
170617 | HV Equipment | CB | U7 Tumut 2 CB U72 | Q | 2014Q3 | UT1 | CB | 2014-08-26 13:21 | 2014-08-26 15:29 |  |  | Investigate CB U72 close failure. | 330 |  |  | 2014
170633 | Unknown | TX | No.2 Transformer 330/132/11kV | Z | 2014Q3 | SYW | TX | 2014-08-26 13:22 | 2014-08-28 10:04 | Clearance from Asset Owner to RTS | 7/11/2014 2:53:00 PM ¦ follow up required ¦ Nil ¦ Nil | No.2 Transformer Tripped at Sydney West 330kV Substation. NCM advised M.Simms requested to attend and advise. 11:40 - M.Simms advised Switchgear appears ok. No protection flags present T.Moss advised and requested to investigate 12:00 - T.Moss advises No.1 Prot M/T on events page present. No M/T flag dropped. Downloading Events log from relay. (possible glitch with GE P60 Relay) NCM advised Advised by Protection Staff no fault found. Will talk to asset owner and advise Permission from Asset owner required to RTS FEOR created | 330 | SSA - No further comment. Resolved. | Fault | 2014
170717 |  |  | 712 Port Macquarie - Rocks Ferry 33kV Line |  | 2014Q3 | PMQ | TL | 2014-08-27 08:16 | 2014-08-27 10:03 | DTF 5.86km Tree found on conductors | follow up required |  | 33 |  |  | 2014
170726 |  |  | No.2 Transformer 330/132/11kV | X | 2014Q3 | VP1 | TX | 2014-08-27 09:53 | 2014-08-28 22:51 |  |  |  | 330 |  |  | 2014
170772 |  |  | 79F Griffith - Yenda 33kV Line |  | 2014Q3 | GRF | TL | 2014-08-27 15:48 | 2014-08-27 17:57 |  | follow up required |  | 33 |  |  | 2014
170779 | Relay Setting | Prot | No.3 Transformer 330/132/11kV | Z | 2014Q3 | WRH | TX | 2014-08-27 16:04 | 2014-08-27 18:07 | No.3 Tx Tripped on Energizing from CB 962B following maintenance | 30/09/2014 2:08:00 PM ¦ follow up required ¦ Nil. ¦ Nil. | No.3 Transformer tripped on energising. No.1 Protection Low Set Diff Blue phase. Protection design and Asset Manager advised. It was determined that the trip was not caused by a genuine transformer fault but instead was due to the occurrence of inrush currents upon energisation of the transformer. The inrush inhibit settings on the Tx differential protection relay were subsequently amended to minimise the risk of future recurrence. The No.3 transformer was then returned to service on 27/08/2014 at 18:07hrs | 330 | SSA - Known issue with T60 settings currently subject of a TWR to rectify across the network. TWR issued, issue closed. | Fault | 2014
170788 |  |  | No.1 Transformer 132/33/11kV | B | 2014Q3 | KS2 | TX | 2014-08-28 09:12 | 2014-08-28 15:42 |  |  |  | 132 |  | Forced | 2014
170866 | HV Equipment | CB | 330kV B Bus 1-2 Section CB 5112 | Q | 2014Q3 | SE1 | CB | 2014-08-28 19:29 | 2014-08-28 20:37 |  |  | SF6 Topup. | 330 |  |  | 2014
171033 |  |  | M9 Murray - Murray 1 330kV TL | X | 2014Q3 | MUR | TL | 2014-08-30 11:37 | 2014-08-30 15:31 |  |  |  | 330 |  |  | 2014
171039 | Condition Monitor | TX | No.2 Transformer 132/66kV | E | 2014Q3 | MPP | TX | 2014-08-30 15:32 | 2014-08-31 10:50 | No.2 Transformer de-energised due to condition monitoring L1 alarm. | follow up required | Advises that an oil Sample has been taken from No.2 Transformer at Mount Piper 132 kV Substation and he has arranged for it to be tested at the Lab tomorrow morning. | 132 |  | Forced | 2014
171070 | HV Equipment | Other | No.3 Capacitor | Q | 2014Q3 | YA2 | CAP | 2014-09-01 09:10 |  |  | Follow up | Advises cable pot head on one phase of No.3 Capacitor has failed with majority of porcelain at base of structure and smaller pieces scattered up to 30m away. Capacitor has remained in service and confirmed no protection flagging. | 33 |  |  | 2014
171164 | HV Equipment | CB | 132kV B Bus Section 1 | Q | 2014Q4 | DPT | BB | 2014-10-01 06:37 | 2014-10-01 17:18 |  |  | CB 4112 stuck closed. | 132 |  |  | 2014
171214 |  |  | No.2 Transformer 330/132/11kV | Y | 2014Q3 | VP1 | TX | 2014-09-01 14:12 | 2014-09-01 16:14 | Note Alarms received - Tx 2 No.2 Protection tripped, Station Transformer 4 Protection operated. Duncan Marks (PPO) advised work within PS on 6.6kV Station Services Board initiated trip and is cause of interruption. Site staff confirm relevant protection details consistent with information received. Visual inspection of equipment failed to reveal any further anomalies. NCM & asset owner advised of above. Clearance obtained to return No.2 Transformer and 957 T/L to service. Report from customer pending and will be pursued by asset owner G Francis. | follow up required |  | 330 |  |  | 2014
171220 | HV Equipment | Disc | 99X Wagga 330 - Wagga 132 132kV TL | E | 2014Q3 | WG2, WG1 | TL | 2014-09-01 17:33 | 2014-09-02 10:23 | Advised by field staff 99X Wagga Line Isolator 99X1 arcing badly at Wagga 330kV Substation and needs to be off loaded. NCM advised. Clearance given to off load 99X Wagga 330 to Wagga 132 kV T/L at Wagga 330kV Substation. C.B. 99X opened at Wagga 330kV Substation @ 1733 hours. | 18/03/2015 3:31:00 PM ¦ follow up required | Advised by field staff 99X Wagga Line Isolator 99X1 arcing badly at Wagga 330kV Substation and needs to be off loaded. NCM advised. Clearance given to off load 99X Wagga 330 to Wagga 132 kV T/L at Wagga 330kV Substation. C.B. 99X opened at Wagga 330kV Substation @ 1733 hours. Defect created to maintain and repair Disconnector. Completed on 2/9/14 Extremely hot connection on Line disconnector B Ph Bus Side.Moving contact appears to have not rolled at end of closing operation.Both fixed and moving contacts were replaced and contact alignment checked OK.All contacts cleaned and lubricated and operation proved OK | 132 |  | Forced | 2014
171461 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2014Q3 | GRF | TL | 2014-09-03 12:09 | 2014-09-03 13:50 | Failed Regulator Can in Essential Energy System | follow up required |  | 33 |  |  | 2014
171590 |  |  | 997/1 Albury - Corowa 132kV Line |  | 2014Q3 | ALB | TL | 2014-09-04 12:45 | 2014-09-04 19:45 | Essential Energy fault, now repaired. | follow up required |  | 132 |  |  | 2014
171628 |  |  | 84A Jerilderie CB 84A2 |  | 2014Q3 | FNY | CB | 2014-09-04 12:01 | 2014-09-04 14:59 | Fault Earth switch operated in Essential system at Jerilderie S/S Essential energy was unable to advise size of load lost at the time, was unable to see load change on transformer loadings at T/G's finley 132 sub | follow up required |  | 66 |  |  | 2014
171629 | HV Equipment | SVC | No.1 Static VAR Compensator | Z | 2014Q3 | AR1 | SVC | 2014-09-04 23:31 | 2014-09-05 12:09 | Further investigations today. | 25/09/2014 1:12:00 PM ¦ follow up required ¦ Nil. ¦ Nil. | Maintenance staff carried out an inspection of TSC B and observed a capacitor can that was bulging on all sides. The faulty capacitor can was replaced with a spare and the SVC was subsequently returned to service on Friday 05/09/2014 at 12:09hrs | 330 |  | Fault | 2014
171892 |  |  | 828 Tumut - Gundagai 66kV Line |  | 2014Q3 | TU2 | TL | 2014-09-06 09:07 | 2014-09-06 09:07 | Successful TAR on 828 Gundagai 66kV Feeder at Tumut 132. Protection details awaited. | follow up required |  | 66 |  |  | 2014
171893 |  |  | 79C Griffith - Darlington Point 33kV Line |  | 2014Q3 | GRF | TL | 2014-09-06 11:51 | 2014-09-06 11:51 | Successful TAR on 79C Darlington Point 33kV Feeder at Griffith. Protection details awaited. | follow up required |  | 33 |  |  | 2014
171896 | Unknown | TL | 5A2 Eraring - Kemps Creek 500kV TL | Q | 2014Q3 | ER0, KCR | TL | 2014-09-07 01:04 | 2014-09-07 01:04 | CB 5A22A failed to reclose at Kemps Creek, fault recorder is indicating genuine fault on "W" phase | 3/11/2014 11:39:00 AM ¦ follow up required ¦ Nil ¦ Bird nest to be removed under WO 00335819 | CB 5A22A did not reclose at Kemps Creek, fault recorder is indicating genuine fault on "W" phase. | 500 |  |  | 2014
172123 | HV Equipment | CB | No.8 330/132/11kV Transformer | B | 2014Q3 | TOM | TX | 2014-09-09 18:04 | 2014-09-09 18:52 |  |  | SF6 TOPUP | 330 |  | Forced | 2014
172124 |  |  | No.6 Deniliquin - Moama 66kV Line |  | 2014Q3 | DN2 | TL | 2014-09-09 17:05 | 2014-09-09 17:05 |  | follow up required |  | 66 |  |  | 2014
172125 | Lightning/Storm | TL | 62 Wagga - Jindera 330kV TL | Q | 2014Q3 | JDA, WG1 | TL | 2014-09-09 22:05 | 2014-09-09 22:05 |  | 25/09/2014 4:40:00 PM ¦ follow up required ¦ Nil. ¦ Nil. | An aerial inspection of the line was conducted on Thursday 11/09/2014 to assess any damage on the line. No evidence of damage was observed. | 330 |  |  | 2014
172126 |  |  | 97G/3 Geehi Tee CB 97G2 |  | 2014Q3 | GTH | CB | 2014-09-09 23:57 | 2014-09-10 14:07 | Returned to service 1407 hrs via SCADA | 26/09/2014 9:51:00 AM ¦ follow up required ¦ Nil. ¦ Nil. |  | 132 |  |  | 2014
172127 |  |  | 850 Tumut - Talbingo tee Jounama Dam 66kV Line |  | 2014Q3 | TU2 | TL | 2014-09-10 00:33 | 2014-09-10 00:33 |  | follow up required |  | 66 |  |  | 2014
172133 |  |  | 963 Tomago330 - Taree T Hawksnest 132kV TL | X | 2014Q4 | TRE, TOM | TL | 2014-10-10 07:12 | 2014-10-10 15:58 |  |  |  | 132 |  |  | 2014
172144 |  |  | 996 Wagga 330 - ANM tee Morven 132kV TL | X | 2014Q4 | ANM, WG1 | TL | 2014-10-01 07:03 | 2014-10-01 07:33 |  |  |  | 132 |  |  | 2014
172150 |  |  | 823 Wallerawang 132 - Portland 66kV Line |  | 2014Q3 | WWS | TL | 2014-09-10 09:13 | 2014-09-10 12:58 | Heavy rain night before | follow up required |  | 66 |  |  | 2014
172188 |  |  | O60 Jindera - Wodonga 330kV TL | X | 2014Q4 | JDA | TL | 2014-10-22 05:49 | 2014-10-22 22:47 |  |  |  | 330 |  |  | 2014
172189 |  |  | O60 Jindera - Wodonga 330kV TL | X | 2014Q4 | JDA | TL | 2014-10-24 05:48 | 2014-10-24 22:03 |  |  |  | 330 |  |  | 2014
172393 |  |  | 963 Tomago330 - Taree T Hawksnest 132kV TL | X | 2014Q4 | TRE, TOM | TL | 2014-10-09 06:43 | 2014-10-09 15:33 |  |  |  | 132 |  |  | 2014
172446 | Lightning/Storm | TL | 9U4 Glen Innes - Inverell 132kV TL | Q | 2014Q3 | GNS, INV | TL | 2014-09-15 00:23 | 2014-09-15 00:23 |  | 2/10/2014 2:19:00 PM ¦ follow up required ¦ Nil. ¦ Nil. |  | 132 |  |  | 2014
172516 | Lightning/Storm | TL | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Q | 2014Q3 | AR1, COF | TL | 2014-09-15 11:36 | 2014-09-15 11:36 | Essential Energy advise no loss of load (Dorrigo). | 2/10/2014 2:57:00 PM ¦ follow up required ¦ Nil. ¦ Nil. |  | 132 |  |  | 2014
172571 | Unknown | Other | 83 Muswellbrook CB 832 | Q | 2014Q3 | LD1 | CB | 2014-09-15 16:59 | 2014-09-15 23:59 | Unexplained CB operation accompanied by numerous disconnector thermal O/L alarms via SCADA. Mick Stemmer called out to investigate at time of report. Suspect d.c. circuit fault. | 29/09/2014 2:14:00 PM ¦ follow up required ¦ Nil. ¦ The trip circuit will be monitored and further investigation carried out to try to determine the source of the spurious signal. | Unexplained CB operation accompanied by numerous disconnector thermal O/L alarms via SCADA. Mick Stemmer called out to investigate at time of report. Suspect d.c. circuit fault. Substation maintenance staff investigating the cause of the trips initially measured a spurious 130V AC signal across the No.2 trip coil associated with CB832. It is believed that this spurious signal is also related to the initiation of the disconnector thermal overload alarms. The spurious signal was not present during subsequent investigation, so the source of the spurious signal could not be confirmed. The investigation did not reveal any issues with the No.2 trip circuit. A monitor has been left connected to the No.2 trip coil to capture the spurious signal if it does reoccur, to assist with investigations. | 330 | SSA - Due to fleeting AC on DC faults. Investigation closed. |  | 2014
172572 |  |  | U7 Upper Tumut - Tumut 2 330kV TL | X | 2014Q3 | UT1 | TL | 2014-09-25 08:50 | 2014-09-25 13:55 |  |  |  | 330 |  |  | 2014
172575 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2014Q3 | MRE | TL | 2014-09-16 04:47 | 2014-09-16 04:47 |  | follow up required |  | 66 |  |  | 2014
172752 | HV Equipment | CT | No.2 Transformer 330/132/11kV | E | 2015Q2 | SYS | TX | 2015-06-01 08:06 | 2015-06-01 12:13 |  |  | OIL SAMPLE CTs FOR DGA + WATER | 330 |  | Forced | 2015
172826 | HV Equipment | TX | No.1 Transformer 132/66/11kV | B | 2014Q3 | GN2 | TX | 2014-09-17 13:02 | 2014-09-17 14:30 |  |  | NO 1 TX REVIEW LID LEAK. | 132 |  | Forced | 2014
172955 | HV Equipment | TL | 96T Armidale - Glen Innes 132kV TL | B | 2014Q3 | AR1, GNS | TL | 2014-09-19 07:42 | 2014-09-19 11:22 |  |  | Wooden OHEW replacement | 132 |  | Forced | 2014
172978 | Unknown | Other | 83 Muswellbrook CB 832 | Q | 2014Q3 | LD1 | CB | 2014-09-18 20:10 | 2014-09-19 14:39 | Unexplained C.B. operation similar to event reported in FEOR 2014-F-0280. | follow up required ¦ Refer to Follow Up report 2014-F-0280-895 ¦ Refer to Follow Up report 2014-F-0280-895 | Unexplained CB operation accompanied by numerous disconnector thermal O/L alarms via SCADA. Mick Stemmer called out to investigate at time of report. Suspect d.c. circuit fault. Substation maintenance staff investigating the cause of the trips initially measured a spurious 130V AC signal across the No.2 trip coil associated with CB832. It is believed that this spurious signal is also related to the initiation of the disconnector thermal overload alarms. The spurious signal was not present during subsequent investigation, so the source of the spurious signal could not be confirmed. The investigation did not reveal any issues with the No.2 trip circuit. A monitor has been left connected to the No.2 trip coil to capture the spurious signal if it does reoccur, to assist with investigations. | 330 | SSA - No further comment. Investigation onging. |  | 2014
172979 |  |  | 971 Yass - Goulburn tee Cullerin Range tee Gunning 132kV Line |  | 2014Q3 | YSN | TL | 2014-09-19 04:21 | 2014-09-19 09:28 | No generation at Gunning or Cullerin Range at the time of the trip. Essential Energy carried out patrol of T/L and no defect found. Line returned to service @ 0928 hours on 19/09/2014. | follow up required |  | 132 |  |  | 2014
173036 | Unknown | Other | 83 Muswellbrook CB 832 | Q | 2014Q3 | LD1 | CB | 2014-09-19 17:30 | 2014-09-20 11:38 | Recurrence of intermittent fault related to d.c. control circuit or induction probable. Transgrid staff called out to investigate. | 29/09/2014 2:15:00 PM ¦ follow up required ¦ Refer to Follow Up report 2014-F-0280-895. ¦ Refer to Follow Up report 2014-F-0280-895. | Unexplained CB operation accompanied by numerous disconnector thermal O/L alarms via SCADA. Mick Stemmer called out to investigate at time of report. Suspect d.c. circuit fault. Substation maintenance staff investigating the cause of the trips initially measured a spurious 130V AC signal across the No.2 trip coil associated with CB832. It is believed that this spurious signal is also related to the initiation of the disconnector thermal overload alarms. The spurious signal was not present during subsequent investigation, so the source of the spurious signal could not be confirmed. The investigation did not reveal any issues with the No.2 trip circuit. A monitor has been left connected to the No.2 trip coil to capture the spurious signal if it does reoccur, to assist with investigations. | 330 |  |  | 2014
173070 | Animal/Bird | TL | 969 Tamworth 330 - Gunnedah 132kV TL | Q | 2014Q3 | GN2, TA1 | TL | 2014-09-21 05:35 | 2014-09-21 05:35 |  | 2/10/2014 3:09:00 PM ¦ follow up required ¦ Nil. ¦ Nil. | A routine aerial patrol identified that the bottom (blue) phase insulators on structure 52 had been badly damaged by birds. It appears that morning dew on these damaged insulators caused a flashover to the concrete pole. The damaged insulators were replaced on Monday 29/09/2014 | 132 |  |  | 2014
173079 | HV Equipment | CB | No.5 Transformer 330/132/11kV | E | 2014Q3 | SYN | TX | 2014-09-21 15:49 | 2014-09-21 17:09 |  |  | CB SF6 TOPUP | 330 |  | Forced | 2014
173111 | HV Equipment | TX | No.1 Bus Coupler | Q | 2014Q3 | BFD | BB | 2014-09-22 21:53 | 2014-09-22 23:32 | No.1 Transformer Out of service due to Maintenance activities, No1 Transformer Main tank Buchholtz Opened due to low oil and No.1 Bus Coupler closed. | 6/11/2014 11:23:00 AM ¦ follow up required ¦ Nil ¦ Nil | No.1 Transformer Out of service due to Maintenance activities, No1 Transformer Main tank Buchholtz Opened due to low oil and No.1 Bus Coupler closed. On 22/9/14, Beaconsfield No.1 Transformer was taken OOS to allow overhaul of the 330kV CB 5412 poles under TWR 098. The 132kV bus coupler associated with No.1 Transformer remained in service (CB 4012A & 4012B closed). On the first evening of the outage, No.1 Transformer oil dropped to the buchholz low oil alarm level at 2130hrs, then to the buchholz low oil trip level at 2153 hours resulting in a trip of CB 4012A & 4012B. The buchholz trip links were isolated and the bus coupler was returned to service at 2332hrs. No.1 Transformer oil was topped up to service level on 23/9/14. | 132 | Work order No. 334901 was created on 23/09/2014 to fix this issue. Oil topped up and work order closed. Another work order (No. 345054) was created on 10/04/2015 with the same low oil issue. 600l of new oil was added to tx. These leaks require further investigations. |  | 2014
173169 |  |  | 9E3 Sydney East - Willoughby 132kV Line |  | 2014Q3 | SE1 | TL | 2014-09-23 10:01 | 2014-09-24 16:18 |  | follow up required |  | 132 |  |  | 2014
173213 | HV Equipment | CB | No.3 Transformer 330/132/11kV | E | 2014Q3 | AR1 | TX | 2014-09-24 07:46 | 2014-09-24 11:18 | SF6 CB Pressure Lockout alarm received via SCADA. Note - alarms for this C.B. one of only, for both low pressure and lockout condition. Staff at site confirm Blue Phase low pressure only, with CB operable. No.3 Transformer removed from service for C.B. 5432 SF6 top up. | follow up required | SF6 Topup | 330 |  | Forced | 2014
173280 | Lightning/Storm | TL | 8M Dumaresq - Bulli Creek 330kV TL | Q | 2014Q3 | DMQ | TL | 2014-09-25 05:40 | 2014-09-25 05:40 | Single Pole AR at Dumaresq. 8M failed to close at Bulli Creek. Powerlink where unable to close manually at Bulli Creek. Line loaded by Powerlink at 05:54hrs | follow up required | Successful trip and reclose during storms. | 330 |  |  | 2014
173281 |  |  | No.4 Reactor |  | 2014Q3 | DMQ | RX | 2014-09-25 05:40 | 2014-09-25 05:40 |  |  |  | 330 |  |  | 2014
173303 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2014Q3 | MRE | TL | 2014-09-25 07:38 | 2014-09-25 07:38 |  | follow up required |  | 66 |  |  | 2014
173382 | Lightning/Storm | TL | 96R Glen Innes - Tenterfield 132kV TL | Q | 2014Q3 | GNS, TTF | TL | 2014-09-25 13:02 | 2014-09-25 13:13 | 96R & 96L T/Ls energised via 22kV side of No.1 and No.2 Transformers at Tenterfield at time of event. Site staff at Tenterfield confirm absence of protection operation for 96R T/L and no operation of C.B.s at site. Auto reclose at Glen Innes non auto at time of event. Protection design to follow up equipment configuration with suitability / adequacy of protection scheme to be advised. Note distance to fault advised as 4.5km from Glen Innes. | follow up required <Duplicate Record> 5/11/2014 11:31:00 AM ¦ follow up required ¦ Nil. ¦ Protection design to follow up the secondary systems equipment configuration with suitability / adequacy of protection scheme to be advised. Mains/Northern will carry out a close inspection of the line between Structures 10-20 of 96R TL during the next routine inspection. | 96R & 96L T/Ls energised via 22kV side of No.1 and No.2 Transformers at Tenterfield at time of event. Site staff at Tenterfield confirm absence of protection operation for 96R T/L and no operation of C.B.s at site. Auto reclose at Glen Innes non auto at time of event. Protection design to follow up equipment configuration with suitability / adequacy of protection scheme to be advised. Note distance to fault advised as 4.5km from Glen Innes. Secondary Systems staff confirmed the absence of protection operation for 96R TL at Tenterfield 132kV Substation during the trip. The fault event records indicated that the protection relays started and dropped out several times due to very low fault current (about 110A) at Tenterfield 132kV Substation. On Thursday 25/09/2014 13:13, the 132kV 96R TL was returned to service. | 132 | MJ to followup with Protection Design. Resolved. |  | 2014
173442 |  |  | No.6 330KV Generator Transformer Group |  | 2014Q3 | VP1 | TX | 2014-09-26 01:42 | 2014-09-26 16:59 |  | follow up required |  | 330 |  |  | 2014
173478 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2014Q3 | MRE | TL | 2014-09-26 11:21 | 2014-09-26 11:21 |  | follow up required |  | 66 |  |  | 2014
173508 |  |  | 99N Darlington Point - Hillston 132kV Line |  | 2014Q3 | DNT | TL | 2014-09-27 05:48 | 2014-09-27 05:48 |  | follow up required |  | 132 |  |  | 2014
173596 | Relay | Prot | No.1 Transformer 500/330/33kV | Z | 2014Q3 | BBY | TX | 2014-09-29 12:42 | 2014-09-30 19:23 |  | 19/03/2015 10:50:00 AM ¦ follow up required | At 12:41hrs No.1 Transformer Tripped. Staff called to site. Advised that R Strobel requested that would like protection to investigate the problem with the differential relay further. Isolation will be taken on the Transformer. | 500 | SSA - Likely failure of the analogue input module of an L90 relay. First time occurrence of this type of fault, where the current waveform was inverted by 180 degrees causing a trip. Faulted relay has been replaced and will be sent to the manufacturer for analysis & repair. Faulty unit replaced, issue closed. | Fault | 2014
173597 |  |  | No.1 Reactor |  | 2014Q3 | BBY | RX | 2014-09-29 12:42 | 2014-09-30 19:23 |  |  |  | 33 |  |  | 2014
173601 |  |  | M11 Murray - Murray 2 330kV TL | X | 2014Q4 | MUR | TL | 2014-10-15 07:17 | 2014-10-15 13:28 |  |  |  | 330 |  |  | 2014
173602 |  |  | L3 Lower Tumut - Tumut 3 330kV TL | X | 2014Q4 | LT1 | TL | 2014-10-14 08:22 | 2014-10-14 13:43 |  |  |  | 330 |  |  | 2014
173608 |  |  | 97L Guthega - Jindabyne Pumps 132kV TL | X | 2014Q4 | GTH | TL | 2014-10-13 07:32 | 2014-10-15 15:48 |  |  |  | 132 |  |  | 2014
173721 | Lightning/Storm | TL | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2014Q3 | GTH, MUR, GHI | TL | 2014-09-09 23:57 | 2014-09-10 14:07 |  |  | On Tuesday 09/09/2014 at 23:57hrs, the 132kV No.97G/3 transmission line from Guthega 132kV Substation to Geehi Dam Tee tripped at Guthega Substation. The line was returned to service the next day via SCADA at 14:07hrs. Protection at Guthega 132kV Substation indicated a three phase to earth fault. No distance to fault information was recorded. INDJI record a lightning strike at the time of the trip, 1.4km east of structure 50 and 8km north of Munyang 132kV Substation. An aerial inspection was conducted on Tuesday 23/09/2014 between structures 45 and 55 to assess any damage on the line. No evidence of damage was observed. | 132 |  | Fault | 2014
173752 |  |  | 99B Jindera - Albury 132kV TL | B | 2014Q3 | ALB, JDA | TL | 2014-09-30 15:33 | 2014-10-01 13:16 |  |  |  | 132 |  | Forced | 2014
173778 |  |  | 132kV B Bus 1-2 Section CB 4112 | Q | 2014Q4 | DPT | CB | 2014-10-01 06:37 | 2014-10-01 17:18 |  |  |  | 132 |  |  | 2014
173793 |  |  | 939 Sydney West - Mamre 132kV Line | X | 2014Q4 | SYW | TL | 2014-11-04 05:13 | 2014-11-04 14:15 |  |  |  | 132 |  |  | 2014
173797 | HV Equipment | CB | 132kV B Bus 1-2 Section CB 4112 | Q | 2014Q4 | DPT | CB | 2014-10-02 08:18 | 2014-10-02 14:13 |  |  | CB 4112 WON'T OPEN AFTER TRIP CHECKS BY PROT. TECH | 132 |  |  | 2014
173845 | Animal/Bird | TL | 5A3 Bayswater - Mt Piper 500kV TL | Q | 2014Q4 | BAY, MTP | TL | 2014-10-02 00:37 | 2014-10-02 00:37 |  | 17/11/2014 11:38:00 AM ¦ follow up required ¦ Nil. ¦ Nil. | On Friday 03/10/2014, a detailed aerial inspection of the line was carried out as part of routine aerial inspections. A bird nest was identified above the top phase of Structure 29 and was subsequently removed by line crew. No evidence of flashover was found. | 500 |  |  | 2014
173861 |  |  | No.1 Transformer 500/330/33kV | B | 2014Q4 | BBY | TX | 2014-10-02 08:44 | 2014-10-02 13:34 |  |  |  | 500 |  | Forced | 2014
173916 | LV/MECH Fail | Prot | 8L Dumaresq - Bulli Creek 330kV TL | Q | 2014Q4 | DMQ | TL | 2014-10-02 10:49 | 2014-10-02 11:25 | Prep work for 8L protection replacement loose red phase CT secondary wire found to be the cause found inadvertently. Dumaresq End single pole reclosed, Bulli Creek Coupler CB 6042 has no reclose selected manual close at Bulli Creek. | follow up required | Prep work for 8L protection replacement loose red phase CT secondary wire found to be the cause found inadvertently. Dumaresq End single pole reclosed, Bulli Creek Coupler CB 6042 has no reclose selected manual close at Bulli Creek. | 330 | SSA - FEOR due to existing defect on the protection panel - loose CT Wiring. Outage taken to make safe. No Further Follow Up. |  | 2014
173917 |  |  | No.3 Reactor |  | 2014Q4 | DMQ | RX | 2014-10-02 10:49 | 2014-10-02 11:25 |  |  |  | 330 |  |  | 2014
173932 |  |  | 868 Taree - Bohnock Tee Hallidays Point 66kV Line |  | 2014Q4 | TRE | TL | 2014-10-02 12:30 | 2014-10-02 12:30 |  | follow up required |  | 66 |  |  | 2014
174039 | HV Equipment | CB | 9J2 Sydney West - Blacktown 132kV Line | Q | 2014Q4 | SYW | TL | 2014-10-04 13:01 | 2014-10-04 15:13 | Low SF6 alarm received for 9J2 Blacktown C.B.. 9J22 & C.T.s. C.B. 9J22 opened via SCADA @ 1301 hours. C.B. isolated under HVPRI 54809. SF6 gas topped up and C.B. returned to service @ 1513 hours. | 7/11/2014 2:17:00 PM ¦ follow up required ¦ Nil ¦ Nil | Low SF6 alarm received for 9J2 Blacktown C.B.. 9J22 & C.T.s. C.B. 9J22 opened via SCADA @ 1301 hours. C.B. isolated under HVPRI 54809. SF6 gas topped up and C.B. returned to service @ 1513 hours. Follow isolation under HVPRI 54809, CB 9J22 was topped up with SF6 and returned to service at 1513 hours. Defect work order 00337110 raised against CB 9J22 to locate the SF6 leak. | 132 |  |  | 2014
174040 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2014Q4 | MRE | TL | 2014-10-04 14:04 | 2014-10-04 14:04 | Protection details to be advised. | follow up required |  | 66 |  |  | 2014
174098 | HV Equipment | TL | 6 Canberra - Capital Wind Farm 330kV TL | Z | 2014Q4 | CA1, CWF | TL | 2014-10-07 01:42 | 2014-10-07 15:41 | Broken Crossarm in Field. Crossarm fixed and T/L RTS Voltage depression of 87% for 2.5 cycles at Capital Wind Farm. Voltage depression of 46% for 2.5 cycles at Canberra. | 10/10/2014 4:41:00 PM ¦ follow up required ¦ Nil. ¦ An investigation into design options to prevent this defect occurring in the future is underway. | Broken Crossarm in Field. Crossarm fixed and T/L RTS Voltage depression of 87% for 2.5 cycles at Capital Wind Farm. Voltage depression of 46% for 2.5 cycles at Canberra. At approximately 08:00hrs the mains team commenced a patrol of the line at the suspected location and found that the red phase cross-arm on structure 129 had been disconnected on one side and had swung down together with the conductor and insulator strings. Structure 129 is a wood pole emergency structure. The king bolt used to attach the crossarm to the pole had sheared due to excessive wind loading. Remedial work was initiated and the king bolt was replaced. The king bolts on the other cross arms of the structure did not display evidence of damage. The work was completed at approximately 16:00hrs with the line being made available for service. | 330 |  | Fault | 2014
174149 |  |  | 99N Darlington Point - Hillston 132kV Line |  | 2014Q4 | DNT | TL | 2014-10-08 05:23 | 2014-10-08 05:23 | System Operator Essential Energy advises Nil loss of load. | follow up required |  | 132 |  |  | 2014
174192 |  |  | 9C8 Brandy Hill - Stroud 132kV TL | X | 2014Q4 | SRD, BRH | TL | 2014-10-10 06:05 | 2014-10-10 09:55 |  |  |  | 132 |  |  | 2014
174193 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2014Q4 | GRF | TL | 2014-10-08 07:44 | 2014-10-08 07:44 | DTF 9.9km Weather Fine/Clear | follow up required |  | 33 |  |  | 2014
174199 | Unknown | TL | 990 Yass - Wagga 132 132kV TL | Q | 2014Q4 | WG2, YSN | TL | 2014-10-09 05:25 | 2014-10-09 05:25 | Weather appears fine according to control room tools. Awaiting site report/prot flagging when next on site. | 14/11/2014 10:29:00 AM ¦ follow up required ¦ Nil. ¦ A close inspection of the line will be carried out in the next aerial inspection. | A close inspection of the line will be carried out in the next aerial inspection. | 132 |  |  | 2014
174232 | HV Equipment | CB | 78 Sydney South A CB 782A | Q | 2014Q4 | ING | CB | 2014-10-09 10:14 | 2014-10-09 11:39 |  |  | CB SF6 Topup | 330 |  |  | 2014
174270 |  |  | No.1 Transformer 330/132/11kV | X | 2014Q4 | HLD | TX | 2014-10-09 15:52 | 2014-10-10 15:54 |  |  |  | 330 |  |  | 2014
174275 |  |  | 5A2 Eraring - Kemps Creek 500kV TL | Q | 2014Q4 | ER0, KCR | TL | 2014-10-10 02:04 | 2014-10-10 02:04 | Due to outages of 5A1 and No2 Transformer at KCR No.3 Transformer was off loaded for reclose time. | 27/10/2014 2:57:00 PM ¦ follow up required ¦ Nil. ¦ Nil. |  | 500 |  |  | 2014
174348 | Animal/Bird | TL | 5A2 Eraring - Kemps Creek 500kV TL | Q | 2014Q4 | ER0, KCR | TL | 2014-10-10 23:13 | 2014-10-10 23:13 |  | 27/10/2014 2:59:00 PM ¦ follow up required ¦ Nil. ¦ Nil. | On Wednesday 15/10/2014, a ground patrol was carried out. A bird nest was identified on the top phase of Structure 108 and was removed on that day. It was clear from the burning sign in the corona ring that the bird nest was the cause of the flashovers. | 500 |  |  | 2014
174360 |  |  | 97R Cooma - Steeple Flat 132kV Line |  | 2014Q4 | CMA | TL | 2014-10-11 05:49 | 2014-10-11 05:49 |  | follow up required |  | 132 |  |  | 2014
174361 |  |  | 957 Vales Pt - Ourimbah tee Morisset 132kV Line |  | 2014Q4 | VP1 | TL | 2014-10-11 05:08 | 2014-10-11 18:13 |  | follow up required |  | 132 |  |  | 2014
174362 | Fire | TL | 28 Sydney North - Sydney East 330kV TL | Q | 2014Q4 | SE1, SYN | TL | 2014-10-11 11:56 | 2014-10-11 11:56 | Planned RFS burn off resulted in flare up in Berowra Valley (near intersection of Summerville Rd Hornsby and Crosslands Rd Galston) and subsequent TAR. | follow up required | Planned RFS burn off resulted in flare up in Berowra Valley (near intersection of Summerville Rd Hornsby and Crosslands Rd Galston) and subsequent TAR. | 330 |  |  | 2014
174363 | HV Equipment | CB | No.2 Transformer 132kV B CB 4422B | Q | 2014Q4 | SE1 | CB | 2014-10-11 15:42 | 2014-10-11 16:39 |  |  | CB SF6 Topup | 132 |  |  | 2014
174364 | Lightning/Storm | TL | 87 Armidale - Coffs Harbour 330kV TL | Q | 2014Q4 | AR1, COF | TL | 2014-10-11 14:30 | 2014-10-11 14:30 |  | follow up required |  | 330 |  |  | 2014
174365 |  |  | No.2 330kV Reactor |  | 2014Q4 | AR1 | RX | 2014-10-11 14:30 | 2014-10-11 14:30 |  |  |  | 330 |  |  | 2014
174369 | Unknown | TL | 99L Deniliquin - Coleambally 132kV TL | Q | 2014Q4 | CLY, DN2 | TL | 2014-10-12 05:19 | 2014-10-12 05:19 |  | 14/11/2014 10:31:00 AM ¦ follow up required ¦ Nil. ¦ A close inspection of the line will be carried out in the next aerial inspection | A close inspection of the line will be carried out in the next aerial inspection | 132 |  |  | 2014
174374 |  |  | 856 Wallerawang 132 - Oberon Tee Lillyvale 66kV Line |  | 2014Q4 | WWS | TL | 2014-10-12 13:27 | 2014-10-12 20:56 | EsE issue. | follow up required |  | 66 |  |  | 2014
174378 | Lightning/Storm | TL | X5/1 Darlington Point - Balranald 220kV TL | Q | 2014Q4 | BRD, DNT | TL | 2014-10-12 17:54 | 2014-10-12 17:54 |  | 30/10/2014 6:01:00 PM ¦ follow up required ¦ Nil. ¦ A close inspection of the line section will be carried out in the next aerial inspection. | On Sunday 12/10/2014 at 18:54hrs, the 220kV No.X5/1 transmission line from Darlington Point to Balranald tripped and reclosed at both ends of the line. No protection details or DTF information has been recorded. Indji record two lightning strikes at the time of the incident 3.2km apart and approximately 500m north of structures 214 and 223. There are no targeted areas in the vicinity of structures 214 and 223 and hence a close inspection of the line section will be carried out in the next aerial inspection. | 220 |  |  | 2014
174379 |  |  | X5/1 Balranald No.1 Reactor |  | 2014Q4 | DNT | RX | 2014-10-12 17:54 | 2014-10-12 17:54 |  |  |  | 220 |  |  | 2014
174380 |  |  | 895 Parkes 66kV CB 8952 |  | 2014Q4 | FB2 | CB | 2014-10-13 03:08 | 2014-10-13 03:08 |  | follow up required |  | 66 |  |  | 2014
174381 |  |  | 895 Forbes - Parkes (89H West Jemalong) 66kV Line |  | 2014Q4 | FB2 | TL | 2014-10-13 05:14 | 2014-10-13 05:14 |  | follow up required |  | 66 |  |  | 2014
174409 |  |  | 996 Wagga 330 - ANM tee Morven 132kV TL | X | 2014Q4 | ANM, WG1 | TL | 2014-10-28 14:26 | 2014-10-28 14:37 |  |  |  | 132 |  |  | 2014
174418 |  |  | 862/1 Taree - OCC Kew tee Johns River 66kV Line |  | 2014Q4 | TRE | TL | 2014-10-13 13:26 | 2014-10-13 13:26 | Trip and successful auto reclose during thunderstorm activity. | follow up required |  | 66 |  |  | 2014
174419 |  |  | 862/1 Taree - OCC Kew tee Johns River 66kV Line |  | 2014Q4 | TRE | TL | 2014-10-13 13:35 | 2014-10-13 13:35 | Trip and successful auto reclose during thunderstorm activity. Second auto reclose within short period of time. | follow up required |  | 66 |  |  | 2014
174420 |  |  | 818/1 Blayney CB 8182 |  | 2014Q4 | ORG | CB | 2014-10-13 14:11 | 2014-10-13 14:11 | Trip and successful auto reclose during thunderstorm activity | follow up required |  | 66 |  |  | 2014
174421 |  |  | 862/1 Taree - OCC Kew tee Johns River 66kV Line |  | 2014Q4 | TRE | TL | 2014-10-13 16:57 | 2014-10-13 16:57 |  | follow up required |  | 66 |  |  | 2014
174422 |  |  | 863 Ingleburn - Minto 66kV Line |  | 2014Q4 | ING | TL | 2014-10-13 17:07 | 2014-10-13 17:07 |  | follow up required |  | 66 |  |  | 2014
174423 |  |  | 662 Armidale - Walcha 66kV Line |  | 2014Q4 | AR1 | TL | 2014-10-14 00:47 | 2014-10-14 00:47 |  | follow up required |  | 66 |  |  | 2014
174465 |  |  | No.5 Taree - Council Kanangra Drive 33kV Line |  | 2014Q4 | TRE | TL | 2014-10-14 10:39 | 2014-10-14 10:39 |  | follow up required |  | 33 |  |  | 2014
174466 |  |  | 862/1 Taree - OCC Kew tee Johns River 66kV Line |  | 2014Q4 | TRE | TL | 2014-10-14 10:39 | 2014-10-14 10:39 |  | follow up required |  | 66 |  |  | 2014
174507 | HV Equipment | CB | No.5 Bay Coupler CB 5052 | Q | 2014Q4 | VP1 | CB | 2014-10-15 00:29 | 2014-10-15 09:21 |  |  | CB SF6 Topup | 330 |  |  | 2014
174508 |  |  | 875 Wallerawang 132 - Oakey Park 66kV Line |  | 2014Q4 | WWS | TL | 2014-10-14 20:47 | 2014-10-19 08:58 | SCADA only recorded a trip of the feeder and no reclose attempt. The site HMI indicates a TARTLO event. This needs to be confirmed by protection staff. | follow up required |  | 66 |  |  | 2014
174509 |  |  | 800 Wallerawang 132 - Railway 66kV Line |  | 2014Q4 | WWS | TL | 2014-10-14 21:38 | 2014-10-19 07:40 |  | follow up required |  | 66 |  |  | 2014
174510 |  |  | 941 Wallerawang 132 - Lawson tee North Katoomba 132kV Line |  | 2014Q4 | WWS | TL | 2014-10-14 22:14 | 2014-10-15 09:04 |  | follow up required |  | 132 |  |  | 2014
174511 |  |  | 940 Wallerawang 132 - Warimoo tee North Katoomba 132kV Line |  | 2014Q4 | WWS | TL | 2014-10-14 23:12 | 2014-10-15 09:04 |  | follow up required |  | 132 |  |  | 2014
174512 |  |  | 857 Wallerawang 132 - Lithgow 66kV Line |  | 2014Q4 | WWS | TL | 2014-10-14 23:17 | 2014-10-15 17:17 |  | follow up required |  | 66 |  |  | 2014
174513 |  |  | 85X Wallerawang 132 - Lithgow 66kV Line |  | 2014Q4 | WWS | TL | 2014-10-14 23:50 | 2014-10-15 07:35 |  | follow up required |  | 66 |  |  | 2014
174717 |  |  | 939 Sydney West - Mamre 132kV Line | X | 2014Q4 | SYW | TL | 2014-10-23 05:44 | 2014-10-23 15:06 |  |  |  | 132 |  |  | 2014
174797 | LV/MECH Fail | Prot | 19 Kangaroo Valley - Bendeela 330kV TL | Q | 2014Q4 | KVS | TL | 2014-10-16 12:22 | 2014-10-16 12:30 | Pole Discrepancy checks on CB 5432 caused Pole Discrepancy on 192. CB 192 closed via scada | 14/11/2014 10:07:00 AM ¦ follow up required ¦ Nil ¦ For future GL315 modifications under TWR107, simulation of the pole discrepancy will require all GL315 CBs in the switchyard not under test to have pole discrepancy timers increased to 10s during the test of the subject circuit breaker. | Pole Discrepancy checks on CB 5432 caused Pole Discrepancy on 192. CB 192 closed via scada At the time of the trip, 330kV Alstom GL315 CB 5432 was out of service and undergoing manufacturer warranty work to rectify a wiring defect under TWR 107. On completion of the work, the wiring modifications were tested by simulating a pole discrepency on CB 5432 for 2 seconds. This testing caused other GL315 CBs in the switchyard to incorrectly pick up on pole discrepancy causing a trip on CB 192 (also a GL315). The pole discrepancy simulation was removed from CB 5432 before any further trips of GL315 CBs occurred. The maloperation of other GL315 CBs in the yard was not anticipated during the testing and is understood to be a result of the incorrect wiring being corrected under TWR 107. CB 192 was restored by SCADA later the same day. | 330 | SSA - Due to internal Breaker Wiring Problem this is not a SSA Issue. Modified Asset Stream Responsible to Subs. |  | 2014
174927 | HV Equipment | CB | No.3 Transformer 330/220/33kV | B | 2014Q4 | DNT | TX | 2014-10-18 08:01 | 2014-10-18 10:07 |  |  | Top up SF6 in Blue Phase CB7432 Pole. | 330 |  | Forced | 2014
174935 |  |  | 850 Tumut - Talbingo tee Jounama Dam 66kV Line |  | 2014Q4 | TU2 | TL | 2014-10-17 17:22 | 2014-10-17 17:22 |  | follow up required |  | 66 |  |  | 2014
174941 |  |  | No.4 Transformer 330/132/11kV | B | 2014Q4 | SYW | TX | 2014-10-18 06:01 | 2014-10-18 11:01 |  |  |  | 330 |  | Forced | 2014
174944 |  |  | No.6 Capacitor | B | 2014Q4 | SYW | CAP | 2014-10-18 06:01 | 2014-10-18 11:01 |  |  |  | 330 |  | Forced | 2014
174945 |  |  | 20 Sydney West - Sydney North 330kV TL | B | 2014Q4 | SYN, SYW | TL | 2014-10-18 06:01 | 2014-10-18 11:01 |  |  |  | 330 |  | Forced | 2014
174954 | Animal/Bird | TL | 5A3 Bayswater - Mt Piper 500kV TL | Q | 2014Q4 | BAY, MTP | TL | 2014-10-20 04:06 | 2014-10-20 04:06 |  | 17/11/2014 11:59:00 AM ¦ follow up required ¦ Nil. ¦ Nil. | During an aerial inspection of the line as part of routine aerial inspections on Friday 03/10/2014, a bird nest was identified above the top phase of 5A3TL at Structure 129. The bird nest was removed by line crew during the week ending on 24 October 2014. No evidence of flashover was found. | 500 |  |  | 2014
174955 | Animal/Bird | TL | 998 Forbes - Cowra 132kV TL | Q | 2014Q4 | CW2, FB2 | TL | 2014-10-20 05:09 | 2014-10-20 05:09 |  | 3/11/2014 12:57:00 PM ¦ follow up required ¦ Nil ¦ Nil | An after fault patrol was conducted on T/L 998 at structure 287 and a few structures either side but this patrol found no definite evidence to the cause of the trip. The patrolman however found plenty of large bird feathers under structure 287 but no bird, a possibility is that a bird tripped the line and has been eaten or taken away over night. | 132 |  |  | 2014
174986 |  |  | 712 Port Macquarie - Rocks Ferry 33kV Line |  | 2014Q4 | PMQ | TL | 2014-10-20 11:37 | 2014-10-20 12:46 | Tree on line (EsE issue). | follow up required |  | 33 |  |  | 2014
174987 | Condition Monitor | TX | No.6 330/132/11kV Transformer | E | 2014Q4 | TOM | TX | 2014-10-19 05:29 | 2014-10-22 16:52 | Transformer taken out of service on receipt of Condition Monitoring Urgent Alarm. | 26/11/2014 9:28:00 AM ¦ follow up required ¦ As above. ¦ As above. | Transformer taken out of service on receipt of Condition Monitoring Urgent Alarm. | 330 |  | Forced | 2014
175124 |  |  | 862/1 Taree - OCC Kew tee Johns River 66kV Line |  | 2014Q4 | TRE | TL | 2014-10-22 16:02 | 2014-10-23 14:51 |  | follow up required |  | 66 |  |  | 2014
175203 | HV Equipment | CB | 132kV No.1 Bus Coupler CB 4012 | Q | 2014Q4 | RGV | CB | 2014-10-23 12:07 | 2014-10-23 12:43 |  |  | CB SF6 Topup | 132 |  |  | 2014
175210 | HV Equipment | CB | 6 Canberra A CB 62A | Q | 2014Q4 | CWF | CB | 2014-10-23 12:55 | 2014-10-23 15:58 |  |  | CB SF6 Topup | 330 |  |  | 2014
175243 |  |  | 97R Cooma - Steeple Flat 132kV Line |  | 2014Q4 | CMA | TL | 2014-10-23 15:06 | 2014-10-23 15:06 | Wind Farm generation has dropped. | follow up required |  | 132 |  |  | 2014
175244 | Lightning/Storm | TL | 966 Armidale - Koolkhan 132kV TL | Q | 2014Q4 | AR1, KLK | TL | 2014-10-23 14:28 | 2014-10-23 14:28 | Trip and successful auto reclose during thunderstorm activity. Protection details to be provided. | follow up required | Trip and successful auto reclose during thunderstorm activity. | 132 |  |  | 2014
175251 | Lightning/Storm | TL | 84 Liddell - Tamworth 330 330kV TL | Q | 2014Q4 | LD1, TA1 | TL | 2014-10-23 17:11 | 2014-10-23 17:11 | Successful auto reclose after trip. Concurrent trip of No.3 Generator and Bay at Bayswater 500/330kV Switchyard. Customer reports operation of interzone protection as reason for Generator trip from approximately 600MW. Staff travelling to site at time of report. Distance to fault reported as 122.8 km (No.1 Prot), 120.7 km (No.2 Prot), from Tamworth 33okV Switchyard. | follow up required | Successful auto reclose after trip. Concurrent trip of No.3 Generator and Bay at Bayswater 500/330kV Switchyard. Customer reports operation of interzone protection as reason for Generator trip from approximately 600MW. Staff travelling to site at time of report. Distance to fault reported as 122.8 km (No.1 Prot), 120.7 km (No.2 Prot), from Tamworth 33okV Switchyard. | 330 |  |  | 2014
175256 | Unknown | Prot | No.3 500kV Generator Transformer Group | Q | 2014Q4 | BAY | TX | 2014-10-23 17:11 | 2014-10-24 21:48 | 84 TL TAR at same time. Storms in the area. No.3 Gen TX bay energised on No.1 Prot only after testing. See IR 12893. | 26/11/2014 6:41:00 PM ¦ follow up required ¦ Nil. ¦ The trip incident of the 500kV No.3 Generator Transformer Group is currently being investigated by both TransGrid and AGL. | 84 TL TAR at same time. Storms in the area. No.3 Gen TX bay energised on No.1 Prot only after testing. Advised by shift manager at Bayswater that Interzone protection had operated. The on call fitter attended the site and found no visible sign of any issues. Secondary Systems/Technical Services staff completed testing on the No.1 Protection Differential relay on Thursday 23/10/2014 at 22:43hrs. The No.1 Protection Differential relay was found serviceable after testing. The No.2 Protection Differential relay was being tested at that time and remained isolated from the protection system. The 500kV No.3 Generator Transformer Group was energised on No.1 Protection only and returned to service on Friday 24/10/2014 at 00:49hrs | 500 | SSA - Potentially Spurious Event. The operation of the relay (and reproduction of the fault waveform) has not been able to be replicated. Internal Investigation suggests cabling between the switchyard and powerstation as the likely cause, however this cannot be determined definitively. TG working with Mac Gen to guard against future mal-operations. |  | 2014
175272 |  |  | 828 Mt Piper 132 - Portland tee BCSC 66kV Line |  | 2014Q4 | MPP | TL | 2014-10-24 06:25 | 2014-10-24 08:27 |  | follow up required |  | 66 |  |  | 2014
175303 |  |  | U1 Upper Tumut - Tumut 1 330kV TL | X | 2014Q4 | UT1 | TL | 2014-11-06 07:33 | 2014-11-11 12:14 |  |  |  | 330 |  |  | 2014
175324 |  |  | 712 Port Macquarie - Rocks Ferry 33kV Line |  | 2014Q4 | PMQ | TL | 2014-10-24 19:08 | 2014-10-24 19:08 |  | follow up required |  | 33 |  |  | 2014
175325 | Fire | TL | 967 Lismore 330 - Koolkhan 132kV TL | Q | 2014Q4 | KLK, LSM | TL | 2014-10-24 19:33 | 2014-10-24 19:33 |  | 25/11/2014 11:46:00 AM ¦ follow up required ¦ Nil. ¦ An aerial inspection of the 967TL will be carried out during the next routine Aerial patrols. | A ground inspection of the 967TL was carried out in late October 2014 and nothing particular was found during the inspection. However, it is suspected that a sugar cane fire under the 967TL flared up unexpectedly due to strong winds and caused a flashover. | 132 |  |  | 2014
175326 | HV Equipment | CB | O60 Wodonga A CB 0602A | Q | 2014Q4 | JDA | CB | 2014-10-24 22:00 | 2014-10-25 01:48 |  |  | CB failed to open | 330 |  |  | 2014
175353 |  |  | 330kV A Bus | Q | 2014Q4 | CWF | BB | 2014-10-26 04:21 | 2014-10-26 10:42 | Capital Wind Farm (Infigen) generating 49.9 MW at time of trip. | 6/12/2014 3:29:00 PM ¦ follow up required |  | 330 |  |  | 2014
175354 |  |  | 3W Kangaroo Valley A CB 3W2A |  | 2014Q4 | CWF | CB | 2014-10-26 04:21 | 2014-10-26 10:42 |  |  |  | 330 |  |  | 2014
175355 |  |  | 6 Canberra A CB 62A |  | 2014Q4 | CWF | CB | 2014-10-26 04:21 | 2014-10-26 10:42 |  |  |  | 330 |  |  | 2014
175356 |  |  | 330kV C Bus |  | 2014Q4 | CWF | BB | 2014-10-26 04:21 | 2014-10-26 10:42 |  |  |  | 330 |  |  | 2014
175357 |  |  | 330kV C Bus |  | 2014Q4 | CWF | BB | 2014-10-26 04:21 | 2014-10-26 10:42 |  |  |  | 330 |  |  | 2014
175359 |  |  | 6501 Koolkhan - Casino 66kV Line |  | 2014Q4 | KLK | TL | 2014-10-26 18:48 | 2014-10-26 18:48 | DTF P1 - 6.021km P2 - 10.81km | follow up required |  | 66 |  |  | 2014
175375 |  |  | U1 Upper Tumut - Tumut 1 330kV TL | X | 2014Q4 | UT1 | TL | 2014-11-26 07:56 | 2014-11-26 10:27 |  |  |  | 330 |  |  | 2014
175376 |  |  | U1 Upper Tumut - Tumut 1 330kV TL | X | 2014Q4 | UT1 | TL | 2014-11-27 07:01 | 2014-11-27 08:41 |  |  |  | 330 |  |  | 2014
175378 |  |  | U1 Upper Tumut - Tumut 1 330kV TL | X | 2014Q4 | UT1 | TL | 2014-11-26 11:09 | 2014-11-26 12:11 |  |  |  | 330 |  |  | 2014
175380 |  |  | U1 Upper Tumut - Tumut 1 330kV TL | X | 2014Q4 | UT1 | TL | 2014-11-27 08:47 | 2014-11-27 11:11 |  |  |  | 330 |  |  | 2014
175381 |  |  | U1 Upper Tumut - Tumut 1 330kV TL | X | 2014Q4 | UT1 | TL | 2014-11-26 12:13 | 2014-11-26 13:49 |  |  |  | 330 |  |  | 2014
175388 |  |  | 844 Deniliquin - Barham 66kV Line |  | 2014Q4 | DN2 | TL | 2014-10-27 07:05 | 2014-10-27 07:05 |  | follow up required |  | 66 |  |  | 2014
175389 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2014Q4 | CW2 | TL | 2014-10-27 13:30 | 2014-10-27 13:30 |  | follow up required |  | 66 |  |  | 2014
175402 |  |  | No.5 Wagga 132 - Macleay St 66kV Line |  | 2014Q4 | WG2 | TL | 2014-10-27 13:20 | 2014-10-27 13:20 |  | follow up required |  | 66 |  |  | 2014
175404 |  |  | No.5 Wagga 132 - Macleay St 66kV Line |  | 2014Q4 | WG2 | TL | 2014-10-27 14:25 | 2014-10-27 14:25 |  | follow up required |  | 66 |  |  | 2014
175460 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2014Q4 | MRE | TL | 2014-10-28 06:47 | 2014-10-28 06:47 |  | follow up required |  | 66 |  |  | 2014
175500 | HV Equipment | CB | No.2 Capacitor | B | 2014Q4 | RGV | CAP | 2014-10-28 14:38 | 2014-10-28 15:48 |  |  | SF6 Gas Top Up | 132 |  | Forced | 2014
175507 |  |  | No.3 330kV Generator Transformer Group |  | 2014Q4 | LD1 | TX | 2014-10-28 16:25 | 2014-11-06 12:48 |  |  |  | 330 |  |  | 2014
175514 |  |  | M13 Murray - Murray 2 330kV TL | X | 2014Q4 | MUR, MP2 | TL | 2014-11-17 07:31 | 2014-11-19 12:19 |  |  |  | 330 |  |  | 2014
175573 | Condition Monitor | TX | No.6 330/132/11kV Transformer | E | 2014Q4 | TOM | TX | 2014-10-30 04:03 | 2014-11-05 16:01 | No.6 Transformer de-energised after receiving condition monitoring urgent alarm. | 26/11/2014 09:27:00 ¦ Follow up ¦ As above. ¦ As above. | No.6 Transformer de-energised after receiving condition monitoring urgent alarm. | 330 |  | Forced | 2014
175632 |  |  | U7 Upper Tumut - Tumut 2 330kV TL | X | 2014Q4 | UT1 | TL | 2014-11-28 07:37 | 2014-11-29 12:13 |  |  |  | 330 |  |  | 2014
175671 | Unknown | TL | 86 Tamworth 330 - Armidale 330kV TL | Q | 2014Q4 | AR1, TA1 | TL | 2014-10-31 03:18 | 2014-10-31 03:18 |  | 2/12/2014 1:38:00 PM ¦ follow up required ¦ Nil. ¦ Nil. | A ground inspection of the 86TL was carried out on 31 October 2014 and evidence of a flashover such as burn marks on the cross arm and corona ring were identified over the Red phase long rod insulator at structure 305. The reason behind the flashover was not identified. The Red phase long rod insulator at structure 305 has been replaced. | 330 |  |  | 2014
175730 | Unknown | CB | No.2 Capacitor | B | 2014Q4 | CMA | CAP | 2014-12-03 08:58 | 2014-12-03 13:28 |  |  | Major Maint to CB3722 | 66 |  | Forced | 2014
175744 |  |  | 851 Mudgee Tee Gulgong 66kV CB 8512 |  | 2014Q4 | BER | CB | 2014-10-31 20:09 | 2014-11-01 03:03 |  |  |  | 66 |  |  | 2014
175765 |  |  | 915 Sydney South - Bankstown 132kV Line |  | 2014Q4 | SYS | TL | 2014-11-01 13:26 | 2014-11-02 15:28 | Both No1 & 2 Distance to fault indicate 1.5kms. | Follow up |  | 132 |  |  | 2014
175766 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2014Q4 | MRE | TL | 2014-11-01 15:21 | 2014-11-01 15:21 | Trip and auto reclose during storm activity. Protection details to be provided. | Follow up |  | 66 |  |  | 2014
175767 |  |  | 662 Armidale - Walcha 66kV Line |  | 2014Q4 | AR1 | TL | 2014-11-01 17:52 | 2014-11-01 17:52 |  |  |  | 66 |  |  | 2014
175768 |  |  | 662 Armidale - Walcha 66kV Line |  | 2014Q4 | AR1 | TL | 2014-11-01 17:52 | 2014-11-01 17:52 |  | Follow up |  | 66 |  |  | 2014
175769 |  |  | 662 Armidale - Walcha 66kV Line |  | 2014Q4 | AR1 | TL | 2014-11-01 18:09 | 2014-11-01 18:09 |  | Follow up |  | 66 |  |  | 2014
175802 | HV Equipment | CT | 99B Jindera - Albury 132kV TL | B | 2014Q4 | ALB, JDA | TL | 2014-11-26 08:45 | 2014-11-26 14:33 |  |  | Repair CT leaks | 132 |  | Forced | 2014
175836 | HV Equipment | CB | No.4 Generator Transformer Main Bus 500kV CB 6242M | Q | 2014Q4 | BAY | CB | 2014-11-03 16:56 | 2014-11-03 18:59 |  |  | Investigate spring discharge alarm | 500 |  |  | 2014
175943 | HV Equipment | CB | 32 Bayswater B CB 322B | Q | 2014Q4 | SYW | CB | 2014-11-04 17:24 | 2014-11-04 18:41 |  |  | CB SF6 Topup | 330 |  |  | 2014
175989 | LV/MECH Fail | CB | 132kV Bus No.1-2 Section CB 4102 | Q | 2014Q4 | MPP | CB | 2014-11-04 15:28 | 2014-11-04 18:16 |  |  | Burnt closing coil. | 132 |  |  | 2014
176058 | HV Equipment | CB | No.2 Transformer 132/66/11kV | E | 2014Q4 | KLK | TX | 2014-11-05 10:39 | 2014-11-05 14:27 |  |  | CB SF6 Topup | 132 |  | Forced | 2014
176103 | Lightning/Storm | TL | 5A2 Eraring - Kemps Creek 500kV TL | Q | 2014Q4 | ER0, KCR | TL | 2014-11-05 14:32 | 2014-11-05 14:32 |  | Follow up |  | 500 |  |  | 2014
176104 |  |  | 863 Ingleburn - Minto 66kV Line |  | 2014Q4 | ING | TL | 2014-11-05 14:35 | 2014-11-05 14:35 |  | Follow up |  | 66 |  |  | 2014
176111 | Lightning/Storm | TL | 5A2 Eraring - Kemps Creek 500kV TL | Q | 2014Q4 | ER0, KCR | TL | 2014-11-05 14:32 | 2014-11-05 14:32 | Successful trip and auto reclose during thunderstorm activity. | Follow up | Successful trip and auto reclose during thunderstorm activity. | 500 |  |  | 2014
176112 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2014Q4 | MRE | TL | 2014-11-05 16:20 | 2014-11-05 19:36 | Trip, auto reclose and lockout during storm activity. Customer reports 1100 customer interrupted (approx 2MW). | Follow up |  | 66 |  |  | 2014
176114 | Windblown/object | TL | 969 Tamworth 330 - Gunnedah 132kV TL | Z | 2014Q4 | GN2, TA1 | TL | 2014-11-05 16:51 | 2014-11-06 14:41 | distance to fault = 11.3km from Tamworth distance to fault = 48.3km from Gunnedah | 3/12/2014 10:11:00 ¦ Follow up ¦ Nil. ¦ Nil. | A line patrol was carried out on Wednesday 05/11/2014 and identified a broken OHEW at span 79-80 of the 969TL. It appeared that strong winds damaged surrounding tree tops/branches and carried them into 969TL, with the weight of the branches bringing the OHEW into contact with phase conductors. The resulting fault current damaged the OHEW and presumably caused damage to the phase conductors. On Thursday 6/11/2014, the OHEW was repaired and 969TL was returned to service at 15:41 on Thursday 06/11/2014. | 132 |  | Fault | 2014
176115 |  |  | 662 Armidale - Walcha 66kV Line |  | 2014Q4 | AR1 | TL | 2014-11-05 17:57 | 2014-11-05 17:57 |  | Follow up |  | 66 |  |  | 2014
176116 |  |  | 662 Armidale - Walcha 66kV Line |  | 2014Q4 | AR1 | TL | 2014-11-05 17:59 | 2014-11-05 17:59 |  | Follow up |  | 66 |  |  | 2014
176117 | Lightning/Storm | TL | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Q | 2014Q4 | AR1, COF | TL | 2014-11-05 19:14 | 2014-11-05 19:14 | Essential Energy report loss of load at Dorrigo. Distance to fault from Armidale - P1 124.81km P2 120.7km distance to fault from Coffs - P1 26.3km P2 27.3km | Follow up | Successful trip and reclose. Loss of load at Dorrigo due to faulty disconnector at Essential Energy's Dorrigo substation. | 132 |  |  | 2014
176118 |  |  | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Y | 2014Q4 | AR1, COF | TL | 2014-11-05 20:16 | 2014-11-05 23:31 | Essential Energy requested 96C de-energised due to significant arcing at Dorrigo on 96C. Arcing was 8 skirts down insulator stack. | Follow up |  | 132 |  |  | 2014
176119 |  |  | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL |  | 2014Q4 | AR1, COF | TL | 2014-11-05 19:14 | 2014-11-05 19:14 | Distance to fault from Armidale - P1 124.81km P2 120.7km distance to fault from Coffs - P1 26.3km P2 27.3km | Follow up |  | 132 |  |  | 2014
176320 |  |  | No.6 330/132/11kV Transformer | E | 2014Q4 | TOM | TX | 2014-11-06 12:28 | 2014-11-07 14:57 | Transformer off loaded and de-energised after receipt of "Condition Monitoring Urgent" alarm via SCADA. Asset owner notified. Transformer to remain de-energised, available for emergency use until investigations complete. | 26/11/2014 09:25:00 ¦ Follow up ¦ As above. ¦ As above. |  | 330 |  | Forced | 2014
176441 | HV Equipment | CB | No.3 Capacitor | E | 2014Q4 | WL1 | CAP | 2014-11-07 14:35 | 2014-11-07 18:01 |  | Follow up ¦ Nil ¦ Nil | A substation fitter attended site to top up SF6 on the same day and the CB was RTS. A defect has been raised against CB 4732 to repair the SF6 leak - RFA booked for 11-12 December 2014. | 132 |  | Forced | 2014
176459 | HV Equipment | CB | 78 Sydney South A CB 782A | Q | 2014Q4 | ING | CB | 2014-11-08 10:06 | 2014-11-08 12:48 |  |  | CB SF6 Topup | 330 |  |  | 2014
176461 | Condition Monitor | TX | No.6 330/132/11kV Transformer | E | 2014Q4 | TOM | TX | 2014-11-08 13:07 | 2014-11-25 15:32 | Transformer taken out of service on receipt of Condition Monitoring alarm. Investigations pending. | 26/11/2014 09:17:00 ¦ Follow up ¦ Nil. ¦ The original 132kV bushings will be sent to a HV testing lab for further examination. | Further inspection of the bushing monitor suggested that the monitor may be faulty, so the monitor was replaced. The new monitor subsequently initiated further alarms that did not appear to be genuine, so the remainder of the circuitry and components associated with the monitoring of the 132kV bushings was replaced. Routine maintenance tests were then carried out and did not reveal any issues. The bushing monitor then initiated another condition monitoring urgent alarm on Saturday 08/11/2014. It was confirmed that the alarm was again associated with the 132kV bushings. It was consequently decided that all three of the 132kV bushings should be replaced as a precaution. Replacement of the 132kV bushings commenced on Friday 21/11/2014. HV testing of the transformer, including the new 132kV bushinngs, is currently being carried out by Aurecon to ensure that the transformer can be returned to service. | 330 |  | Forced | 2014
176477 | Design Limitation | TL | 999 Yass - Cowra 132kV TL | E | 2014Q4 | CW2, YSN | TL | 2014-11-09 12:34 | 2015-01-24 04:07 |  |  | TL De-energised due to high ambient temperature. | 132 |  | Forced | 2014
176478 | HV Equipment | Cap | No.1 Capacitor | Z | 2014Q4 | TA1 | CAP | 2014-11-10 02:51 | 2014-11-11 08:41 |  | 10/12/2014 16:02:00 ¦ Follow up ¦ Nil. ¦ Due to higher spill currents measured on red phase on No.1 Capacitor, red phase capacitor cans are scheduled to be tested on Wednesday 17 December 2014. A 415V injection test will also be carried out prior to returning the No.1 Capacitor to service. | Advised HV access required to No.1 Capacitor for repairs after NUB trip on both protections. PRI preparation and checking to be progressed as work load allows. NCM advised. On Monday 10/11/2014, testing was carried out on the No.1 Capacitor and revealed a faulty capacitor can on blue phase. There were no other signs of damage observed in the switchbay. The faulty capacitor can on blue phase was replaced and the No.1 Capacitor was returned to service on Tuesday 11/11/2014. | 330 |  | Fault | 2014
176581 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2014Q4 | MRE | TL | 2014-11-10 19:06 | 2014-11-10 19:06 |  | Follow up |  | 66 |  |  | 2014
176582 |  |  | 870 Tamworth 132 - Kootingal 66kV Line |  | 2014Q4 | TMW | TL | 2014-11-10 19:23 | 2014-11-10 22:24 |  | Follow up |  | 66 |  |  | 2014
176625 |  |  | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | X | 2014Q4 | AR1, COF | TL | 2014-11-14 07:01 | 2014-11-14 15:29 |  |  |  | 132 |  |  | 2014
176667 |  |  | No.6 Council Feeder 22kV CB 62 |  | 2014Q4 | TTF | CB | 2014-11-11 16:20 | 2014-11-11 17:44 | Essential Energy staff report Trip, auto reclose and lockout. Line patrol in progress at time of report. Line sectionalised and closed by Essential Energy staff under direction of System Operator. TG staff to follow up when they arrive at site. | Follow up |  | 22 |  |  | 2014
176805 | HV Equipment | CB | No.1 Capacitor | E | 2014Q4 | DNT | CAP | 2014-11-12 19:45 | 2014-11-13 14:44 |  | 19/03/2015 11:05:00 ¦ Follow up | Advised on site at Darlington Point 330kV Substation and the No.1 Capacitor CB 4712 has Low SF6 Gas and the CB..4712 has locked out preventing it from opening 12/11/14 - C Hines, Callout to D/Point S/S, CB 4712 (abnormal alarm) found SF6 gas level to be .14mpa,operator requested to take busbar out (via log entry) & CB4712 taken out of service. 13/11/14 - B Mills, R Ubriehn confirmed gas level o.14 mpa. Found Wika density meter was loose in manifold. Note RH thread on density meter LH on union to manifold, O ring reset ok, Density meter re-tensioned.Refill CB 4712 with SF6 to 0.68 mpa, checked for leaks all ok, CB returned to service. (Note - CB had positive pressure, no moisture ingress) | 132 |  | Forced | 2014
176806 |  |  | 132kV Buses |  | 2014Q4 | DNT | BB | 2014-11-12 19:34 | 2014-11-12 19:47 | The No.1 Capacitor CB... 4712 has Low SF6 Gas and the CB..4712 has locked out preventing it from opening, 132kV A Bus and 132kV B Bus required de-energised to Open No.1 Capacitor bus Disconnector ..4713 So/Essential Rayn Young advised of the required outage at Darlington Point 330kV Substation and that 99R Hay and 99N Hilston lines would be de-energised ( Customer outage approx 16MW) | 19/03/2015 11:10:00 ¦ Follow up |  | 132 |  |  | 2014
176807 |  |  | 132kV A Bus |  | 2014Q4 | DNT | BB | 2014-11-12 19:34 | 2014-11-12 19:47 |  |  |  | 132 |  |  | 2014
176808 |  |  | 132kV B Bus |  | 2014Q4 | DNT | BB | 2014-11-12 19:34 | 2014-11-12 19:47 |  |  |  | 132 |  |  | 2014
176925 | HV Equipment | Cap | No.3 Capacitor | B | 2014Q4 | WL1 | CAP | 2014-11-14 10:52 | 2014-11-14 15:14 |  |  | Investigate NUB Alarm. Test Cap Bank, replace faulty cans and balance. | 132 |  | Forced | 2014
176966 | Unknown | TL | 940 Wallerawang 132 - Warimoo tee North Katoomba 132kV Line |  | 2014Q4 | WWS | TL | 2014-11-14 12:07 | 2014-11-14 12:07 | Trip and auto reclose. No storm activity at time. Customer advises line patrol to be undertaken. Staff called to site for protection details and bay inspection. | Follow up |  | 132 |  |  | 2014
176978 | HV Equipment | Cap | No.3 Capacitor | E | 2014Q4 | WL1 | CAP | 2014-11-17 06:56 | 2014-11-17 13:37 |  |  | Investigate NUB Alarm. Test Cap Bank, replace faulty cans and balance. | 132 |  | Forced | 2014
176979 | HV Equipment | CB | No.1 Capacitor | B | 2014Q4 | RGV | CAP | 2014-11-14 17:09 | 2014-11-14 17:38 |  |  | CB SF6 Topup | 132 |  | Forced | 2014
176980 | HV Equipment | CB | No.3 Transformer 330/132/11kV | B | 2014Q4 | MN1 | TX | 2014-11-14 17:22 | 2014-11-14 19:29 |  |  | CB SF6 Topup | 330 |  | Forced | 2014
176981 |  |  | 940 Wallerawang 132 - Warimoo tee North Katoomba 132kV Line |  | 2014Q4 | WWS | TL | 2014-11-14 12:51 | 2014-11-17 13:29 | Customer load transferred within their system by Auto changeover. Customer reports Bushfire directly under 940 TL. | Follow up |  | 132 |  |  | 2014
176988 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2014Q4 | GRF | TL | 2014-11-15 06:41 | 2014-11-15 06:41 |  | Follow up |  | 33 |  |  | 2014
176989 | Staff Error | Proc | Main Bus 330kV | Q | 2014Q4 | MN1 | BB | 2014-11-15 06:58 | 2014-11-15 07:13 | Inadvertent operation of bus protection during planned protection maintenance associated with 26 T/L. Staff at site report non genuine protection operation, with PMWI for planned work part completed at time of event. Bay inspection clear. Bus returned to service via SCADA. | 11/12/2014 09:18:00 ¦ Follow up ¦ Nil. ¦ Nil. | Inadvertent operation of bus protection during planned protection maintenance associated with 26 T/L. Staff at site report non genuine protection operation, with PMWI for planned work part completed at time of event. | 330 | SSA - Incorrected standard PMWI used for the work, resulting in FEOR. No further comment. |  | 2014
176990 |  |  | Station Transformer 2A (CB 5422) |  | 2014Q4 | MN1 | CB | 2014-11-15 06:58 | 2014-11-15 07:13 |  |  |  | 330 |  |  | 2014
176991 |  |  | 26 Sydney West CB 262 |  | 2014Q4 | MN1 | CB | 2014-11-15 06:58 | 2014-11-15 07:13 |  |  |  | 330 |  |  | 2014
176992 |  |  | No.3 Transformer 330kV CB 5432 |  | 2014Q4 | MN1 | CB | 2014-11-15 06:58 | 2014-11-15 07:13 |  |  |  | 330 |  |  | 2014
176993 |  |  | 2M Tuggerah Main Bus CB 2M2M |  | 2014Q4 | MN1 | CB | 2014-11-15 06:58 | 2014-11-15 07:13 |  |  |  | 330 |  |  | 2014
176994 |  |  | 23 Vales Point Main Bus CB 232M |  | 2014Q4 | MN1 | CB | 2014-11-15 06:58 | 2014-11-15 07:13 |  |  |  | 330 |  |  | 2014
176995 |  |  | C1 Colongra CB C12 |  | 2014Q4 | MN1 | CB | 2014-11-15 06:58 | 2014-11-15 07:13 |  |  |  | 330 |  |  | 2014
177004 |  |  | 8M2 Orange - Orange Industrial 66kV Line |  | 2014Q4 | ORG | TL | 2014-11-16 04:47 | 2014-11-16 12:21 | Essential Energy issue. | Follow up |  | 66 |  |  | 2014
177036 |  |  | L5 Lower Tumut - Tumut 3 330kV TL | X | 2014Q4 | LT1, TP3 | TL | 2014-12-03 07:02 | 2014-12-03 14:06 |  |  |  | 330 |  |  | 2014
177045 |  |  | 847 Murrumburrah - Boorowa 66kV Line | Q | 2014Q4 | MRU | TL | 2014-11-17 19:02 | 2014-11-18 15:02 |  |  |  | 66 |  |  | 2014
177047 |  |  | No.1 330kV Generator Transformer Group | Q | 2014Q4 | LD1 | TX | 2014-11-17 11:53 | 2015-07-28 14:38 |  | Follow up |  | 330 |  |  | 2014
177163 |  |  | 27 Sydney North - Sydney East 330kV TL | B | 2014Q4 | SE1, SYN | TL | 2014-11-20 11:41 | 2014-11-20 16:47 |  |  |  | 330 |  | Forced | 2014
177187 |  |  | M1 Murray - Murray 1 330kV TL | X | 2014Q4 | MUR, MP1 | TL | 2014-12-04 11:58 | 2014-12-10 12:21 |  |  |  | 330 |  |  | 2014
177261 | HV Equipment | CB | 132kV No.2 Bus Coupler CB 4022 | Q | 2014Q4 | SYS | CB | 2014-11-21 12:36 | 2014-11-21 13:29 |  |  | CB SF6 TOPUP | 132 |  |  | 2014
177274 | HV Equipment | CB | 926 Mason Park tee Carlingford CB 9262 | Q | 2014Q4 | SYN | CB | 2014-11-21 17:03 | 2014-11-23 07:40 |  |  | Replace failed white phase CT,including polarity and ratio checks and Balance White phase CT against Blue and Red phase CT's. | 132 |  |  | 2014
177283 | Relay | Prot | 98N Beresfield - Tomago 330 132kV Line | Q | 2014Q4 | TOM | TL | 2014-11-22 00:20 | 2014-11-27 15:58 | Faulty Protection relay has been replaced and tested including end to end tests with AusGrid Tech. All protections confirmed serviceable and line returned to service. | Follow up | Faulty Protection relay has been replaced and tested including end to end tests with AusGrid Tech. All protections confirmed serviceable and line returned to service. | 132 | SSA - Faulty OH1-311 Relay. No Further Comment |  | 2014
177285 |  |  | Broken Hill - West 22kV Line |  | 2014Q4 | BKH | TL | 2014-11-22 08:34 | 2014-11-22 10:11 |  | Follow up |  | 22 |  |  | 2014
177296 |  |  | 862/1 Taree - OCC Kew tee Johns River 66kV Line |  | 2014Q4 | TRE | TL | 2014-11-22 21:44 | 2014-11-25 16:40 | SO/Essential Chris confirmed loss of about 0.32MW customer load and that essential can back feed Johns River from KEW on 866. 23:05 So/Ess advised all customer load Approx 0.32MW for Johns river has been restored by Back feed in Essential network | Follow up |  | 66 |  |  | 2014
177302 |  |  | 662 Armidale - Walcha 66kV Line |  | 2014Q4 | AR1 | TL | 2014-11-23 15:09 | 2014-11-23 15:09 | Trip and successful auto reclose during storm activity | Follow up |  | 66 |  |  | 2014
177305 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2014Q4 | MRE | TL | 2014-11-23 21:14 | 2014-11-23 21:14 |  | Follow up |  | 66 |  |  | 2014
177307 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2014Q4 | MRE | TL | 2014-11-23 22:32 | 2014-11-23 22:32 |  | Follow up |  | 66 |  |  | 2014
177308 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2014Q4 | MRE | TL | 2014-11-23 23:00 | 2014-11-23 23:00 |  | Follow up |  | 66 |  |  | 2014
177309 |  |  | 723 Wenna Tee Wathagar 66kV CB 7232 |  | 2014Q4 | MRE | CB | 2014-11-24 00:04 | 2014-11-24 00:04 |  | Follow up |  | 66 |  |  | 2014
177310 |  |  | 882 Narrabri - Wee Waa 66kV Line |  | 2014Q4 | NB2 | TL | 2014-11-24 03:47 | 2014-11-24 03:47 | DTF P1 - 2.95km P2 - 88.04km | Follow up |  | 66 |  |  | 2014
177334 | Bushfire | TL | 81 Newcastle - Liddell 330kV TL | Z | 2014Q4 | LD1, NEW | TL | 2014-11-24 11:39 | 2014-11-24 14:21 | DTF 24.16km Reclose 23.76km from Newcastle Rural fire service advise there is bush fires on both sides of easement. SSE winds. | 11/12/2014 10:50:00 ¦ Follow up ¦ Nil. ¦ Nil. | Rural fire service advise there is bush fires on both sides of easement. SSE winds. A ground inspection was carried out on Monday 24/11/2014 and identified no evidence of damage to the 81TL. On Monday 24/11/2014 at 15:21, the 81TL was returned to service. | 330 |  | Fault | 2014
177351 |  |  | 879 Narrabri - Wee Waa 66kV Line |  | 2014Q4 | NB2 | TL | 2014-11-24 18:15 | 2014-11-24 18:15 |  | Follow up |  | 66 |  |  | 2014
177352 |  |  | No.3 Taree - Council Wingham 33kV Line |  | 2014Q4 | TRE | TL | 2014-11-24 19:00 | 2014-11-24 19:00 |  | Follow up |  | 33 |  |  | 2014
177353 |  |  | No.1 Taree - Council Bootawa 33kV Line |  | 2014Q4 | TRE | TL | 2014-11-24 19:11 | 2014-11-24 19:11 |  | Follow up |  | 33 |  |  | 2014
177354 |  |  | 879 Narrabri - Wee Waa 66kV Line |  | 2014Q4 | NB2 | TL | 2014-11-24 19:22 | 2014-11-24 19:22 |  | Follow up |  | 66 |  |  | 2014
177355 |  |  | No.10 Yanco - Kamarah (No.10 Council) |  | 2014Q4 | YA2 | TL | 2014-11-24 18:32 | 2014-11-25 03:45 | Fault sectionalised away and remainder of line returned to service at 20:04hrs | Follow up |  | 33 |  |  | 2014
177356 | Lightning/Storm | TL | 965 Armidale - Kempsey 132kV TL | Q | 2014Q4 | AR1, KS2 | TL | 2014-11-24 20:03 | 2014-11-24 20:03 | DTF - 65.13km | Follow up |  | 132 |  |  | 2014
177454 | Condition Monitor | Rx | No.4 Reactor | E | 2014Q4 | RWR | RX | 2014-11-26 01:57 | 2014-11-26 08:06 | Condition Monitor L1 Urgent alarm on No.4 Reactor. No.4 Reactor taken out of service. Staff on site advise No.4 Reactor Air Cell Rupture alarm. Advised known issue with minor leak in the Conservator valve. Clearance given to return No.4 Reactor to service. | Follow up | Condition Monitor L1 Urgent alarm on No.4 Reactor. No.4 Reactor taken out of service. Staff on site advise No.4 Reactor Air Cell Rupture alarm. Advised known issue with minor leak in the Conservator valve. Clearance given to return No.4 Reactor to service. | 330 |  | Forced | 2014
177490 |  |  | No.1 Transformer 330/132/11kV | X | 2014Q4 | VP1 | TX | 2014-11-26 08:50 | 2014-11-26 20:16 |  |  |  | 330 |  |  | 2014
177491 |  |  | 813 Tamworth 132 - Currabubula 66kV Line |  | 2014Q4 | TMW | TL | 2014-11-24 12:54 | 2014-11-24 12:54 | Distance to fault - 60.07km | Follow up |  | 66 |  |  | 2014
178795 |  |  | U1 Upper Tumut - Tumut 1 330kV TL | X | 2014Q4 | UT1 | TL | 2014-12-12 13:13 | 2014-12-15 09:31 |  |  |  | 330 |  |  | 2014
178796 |  |  | U3 Upper Tumut - Tumut 1 330kV TL | X | 2014Q4 | UT1 | TL | 2014-12-12 06:41 | 2014-12-16 15:47 |  |  |  | 330 |  |  | 2014
178806 |  |  | Broken Hill - West 22kV Line |  | 2014Q4 | BKH | TL | 2014-11-28 16:02 | 2014-11-28 16:02 |  | Follow up |  | 22 |  |  | 2014
178825 | Unknown | SVC | No.1 Static VAR Compensator | E | 2014Q4 | AR1 | SVC | 2014-11-29 11:32 | 2014-12-04 18:11 | SVC manually taken out of service via SCADA due to unwarranted high MVAR export. G.Francis OK'd RTS after investigations. | 12/12/2014 10:28:00 ¦ Follow up ¦ Nil. ¦ Nil. | At 11:26hrs #1 SVC at Armidale 330kV Substation had a malfunction and generated an excessive amount of MVAr's.(Approximately 160MVAr's) Volts at Armidale exceeded 362kV until SVC was able to be turned off at 11:31hrs. Staff arranged to investigate. AEMO notified and constraints invoked. Advised visual inspection not apparent of anything out of the normal. Unable to interrogate events as PC used to communicate with PLC is away being repaired. John happy to get SVC Isolated and he has organised for a control tech to investigate further some time over the next couple days. On Saturday 29/11/2014, the staff attended the site; however, was unable to investigate the fault as the computer required to interrogate the SVC control system was away being repaired. No evidence of damage was identified to any of the equipment during visual inspection of the No.1 SVC. On Thursday 04/12/2014, the staff completed the fault finding of the No.1 SVC control system but could not find the reason behind the malfunction of it. On Thursday 04/12/2014 at 19:11hrs, the No.1 SVC at Armidale 330kV Substation was returned to service. | 330 |  | Forced | 2014
178841 |  |  | 896 Forbes - West Jemalong 66kV Line |  | 2014Q4 | FB2 | TL | 2014-11-30 13:46 | 2014-11-30 13:46 |  | Follow up |  | 66 |  |  | 2014
178842 |  |  | 837 Murrumburrah - Jugiong 66kV Line |  | 2014Q4 | MRU | TL | 2014-11-30 14:49 | 2014-12-01 19:18 |  | Follow up |  | 66 |  |  | 2014
178843 |  |  | 863 Cowra - Canowindra 66kV Line |  | 2014Q4 | CW2 | TL | 2014-11-30 15:15 | 2014-11-30 15:15 |  | Follow up |  | 66 |  |  | 2014
178844 | Lightning/Storm | TL | 966 Armidale - Koolkhan 132kV TL | Q | 2014Q4 | AR1, KLK | TL | 2014-11-30 15:55 | 2014-11-30 15:55 | Distance to fault - Armidale No.1 127.83km No.2 93.15km | Follow up | Distance to fault - Armidale No.1 127.83km No.2 93.15km | 132 |  |  | 2014
178881 | HV Equipment | CB | 932 Sydney West - Mt Druitt 132kV Line | B | 2014Q4 | SYW | TL | 2014-12-01 14:00 | 2014-12-01 15:38 |  |  | CB SF6 Topup | 132 |  | Forced | 2014
178887 | Lightning/Storm | TL | 966 Armidale - Koolkhan 132kV TL | Q | 2014Q4 | AR1, KLK | TL | 2014-12-01 13:26 | 2014-12-01 13:26 | Successful auto reclose after trip during storm activity in area. Note similar occurrence 30/11/14. Distance to Fault Koolkhan - 100km Armidale - No.1 88.78km No.2 90.25km | Follow up | Successful auto reclose after trip during storm activity in area. Note similar occurrence 30/11/14. Distance to Fault Koolkhan - 100km Armidale - No.1 88.78km No.2 90.25km | 132 |  |  | 2014
178890 |  |  | 898 Parkes - Trundle 66kV Line |  | 2014Q4 | PKS | TL | 2014-12-01 21:23 | 2014-12-01 21:23 |  | Follow up |  | 66 |  |  | 2014
178891 |  |  | 895 Forbes - Parkes (89H West Jemalong) 66kV Line |  | 2014Q4 | FB2 | TL | 2014-12-01 22:01 | 2014-12-01 22:01 | DTF - 16.71km | Follow up |  | 66 |  |  | 2014
178892 |  |  | 893/1 Cowra - Grenfell 66kV Line |  | 2014Q4 | CW2 | TL | 2014-12-01 22:10 | 2014-12-01 22:10 | DTF - 23.81km | Follow up |  | 66 |  |  | 2014
178919 | LV/MECH Fail | SVC | No.2 Static VAr Compensator | E | 2014Q4 | BKH | SVC | 2014-12-02 07:38 | 2014-12-03 11:44 | No.2 SVC requested out of service by TL/Subs Byron Mills after cooling water system failure, advises conductivity level is now at 40.5uS/cm (Trip level supposably at 2uS/cm) Water gushing from cooling pipes and pickup filling with Town water and demineralsed water all but depleted. | 19/03/2015 11:26:00 ¦ Follow up | No.2 SVC requested out of service by TL/Subs Byron Mills after cooling water system failure, advises conductivity level is now at 40.5uS/cm (Trip level supposably at 2uS/cm) Water gushing from cooling pipes and pickup filling with Town water and demineralsed water all but depleted. | 22 |  | Forced | 2014
178945 |  |  | 661 Armidale - Oaky PS 66kV Line |  | 2014Q4 | AR1 | TL | 2014-12-02 16:53 | 2014-12-02 16:54 | Trip and auto reclose during storm activity | Follow up |  | 66 |  |  | 2014
179181 |  |  | 97L Guthega - Jindabyne Pumps 132kV TL | X | 2014Q4 | GTH, JDP | TL | 2014-12-09 10:15 | 2014-12-09 15:36 |  |  |  | 132 |  |  | 2014
179191 | Lightning/Storm | TL | 39 Sydney West - Bannaby 330kV TL | Q | 2014Q4 | SYW, BBY | TL | 2014-12-03 15:35 | 2014-12-03 15:35 |  | 11/03/2015 15:47:00 ¦ Follow up ¦ Nil ¦ Nil |  | 330 |  |  | 2014
179192 |  |  | 79L Griffith - Beelbangera 33kV Line |  | 2014Q4 | GRF | TL | 2014-12-03 23:19 | 2014-12-03 23:19 |  | Follow up |  | 33 |  |  | 2014
179271 |  |  | 963 Tomago330 - Taree T Hawksnest 132kV TL | X | 2015Q1 | TRE, TOM | TL | 2015-01-30 07:57 | 2015-01-30 15:32 |  |  |  | 132 |  |  | 2015
179304 | Lightning/Storm | TL | 9W2 Kempsey - Raleigh 132kV TL | Q | 2014Q4 | KS2, RAL | TL | 2014-12-04 12:30 | 2014-12-04 12:31 |  | Follow up |  | 132 |  |  | 2014
179315 |  |  | 662 Armidale - Walcha 66kV Line |  | 2014Q4 | AR1 | TL | 2014-12-04 13:05 | 2014-12-04 13:05 |  | Follow up |  | 66 |  |  | 2014
179334 |  |  | 850 Tumut - Talbingo tee Jounama Dam 66kV Line |  | 2014Q4 | TU2 | TL | 2014-12-04 13:59 | 2014-12-04 13:59 |  | Follow up |  | 66 |  |  | 2014
179339 |  |  | 896 Forbes - West Jemalong 66kV Line |  | 2014Q4 | FB2 | TL | 2014-12-04 16:29 | 2014-12-04 16:29 | Successful auto reclose after trip during storm activity. | Follow up |  | 66 |  |  | 2014
179340 |  |  | 817 Wallerawang 132 - Meadow Flat 66kV Line |  | 2014Q4 | WWS | TL | 2014-12-04 18:02 | 2014-12-04 18:02 |  | Follow up |  | 66 |  |  | 2014
179341 |  |  | 878 Narrabri - Boggabri 66kV Line |  | 2014Q4 | NB2 | TL | 2014-12-04 19:16 | 2014-12-04 19:16 | DTF - 43.89km | Follow up |  | 66 |  |  | 2014
179342 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2014Q4 | BER | TL | 2014-12-04 19:01 | 2014-12-04 19:01 |  | Follow up |  | 66 |  |  | 2014
179343 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2014Q4 | BER | TL | 2014-12-04 19:04 | 2014-12-04 19:04 |  | Follow up |  | 66 |  |  | 2014
179344 |  |  | No.6 Tenterfield - Council (Tenterfield Town) 22kV Line |  | 2014Q4 | TTF | TL | 2014-12-04 17:57 | 2014-12-04 19:04 | Essential Energy staff utilised in response. Feeder sectionalised and RTS. | Follow up |  | 22 |  |  | 2014
179345 | Lightning/Storm | TL | 36 Marulan - Bannaby 330kV TL | Q | 2014Q4 | MRN, BBY | TL | 2014-12-04 19:47 | 2014-12-04 19:47 | CB 5012 manually closed at Marulan. Protection details added for MRN. BBY protection details have not been received. see Note in outage for prot details. | 15/04/2015 14:21:00 ¦ Follow up ¦ No further action planned | CB 5012 manually closed at Marulan. | 330 |  |  | 2014
179346 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2014Q4 | MRE | TL | 2014-12-04 20:00 | 2014-12-04 20:00 |  | Follow up |  | 66 |  |  | 2014
179347 | Lightning/Storm | TL | 990 Yass - Wagga 132 132kV TL | Q | 2014Q4 | WG2, YSN | TL | 2014-12-04 20:44 | 2014-12-04 20:44 |  | 19/12/2014 14:37:00 ¦ Follow up ¦ Nil. ¦ A close inspection of the line section will be carried out in the next aerial inspection. | On Thursday 4/12/2014 at 21:44hrs, the 132kV No.990 transmission line from Wagga Wagga 132kV Substation to Yass 330kV Substation tripped and reclosed at both ends of the line. Protection at Yass indicated a three phase zone 1 fault. The distance to fault was recorded as being 33km from Yass 330kV Substation which corresponds to structure 422. There are no major road crossings or major waterways in the vicinity of this structure. Storms were reported in the area at the time of the event. However, Indji did not record any lightning strikes at the time of the incident. As there are no targeted areas in the vicinity of the calculated fault area, this section of line is noted for the next routine aerial inspection. | 132 |  |  | 2014
179348 | Lightning/Storm | TL | 9W6 Macksville - Nambucca 132kV TL | Q | 2014Q4 | NAM, MVL | TL | 2014-12-05 05:06 | 2014-12-05 05:06 |  | 18/12/2014 11:21:00 ¦ Follow up ¦ As above. ¦ As above. |  | 132 |  |  | 2014
179448 | Lightning/Storm | TL | 9W2 Kempsey - Raleigh 132kV TL | E | 2014Q4 | KS2, RAL | TL | 2014-12-05 10:09 | 2014-12-05 17:27 | Line de-energised due to report of OHEW down. Dual circuit with 9W6 | 18/12/2014 11:19:00 ¦ Follow up ¦ As above. ¦ As above. | Line de-energised due to report of OHEW down. Dual circuit with 9W6 | 132 |  | Forced | 2014
179449 | Lightning/Storm | TL | 9W6 Macksville - Nambucca 132kV TL | E | 2014Q4 | NAM, MVL | TL | 2014-12-05 09:30 | 2014-12-05 17:26 | Line de-energised due to report of OHEW down. Dual circuit with 9W2 | 18/12/2014 11:03:00 ¦ Follow up ¦ Nil. ¦ Nil. | On Friday 05/12/2014 at 10:30hrs, the 132kV 9W6TL from Macksville 132/11kV Substation to Nambucca 132kV Substation was manually taken out of service due to damaged OHEW caused by lightning strike. Due to this failure, the 132kV 9W2TL from Kempsey Substation to Raleigh 132/11kV Substation was also manually taken out of service (see FEOR 2014-E-0043) at 11:09hrs on Friday 05/12/2014. The damaged OHEW was repaired on Friday 05/12/2014 and 9W6TL was returned to service on Friday 05/12/2014 at 18:26hrs. The 9W2TL was also returned to service on Friday 05/12/2014 at 18:27hrs. | 132 |  | Forced | 2014
179485 | Lightning/Storm | TL | 966 Armidale - Koolkhan 132kV TL | Q | 2014Q4 | AR1, KLK | TL | 2014-12-05 15:37 | 2014-12-05 15:37 |  | Follow up |  | 132 |  |  | 2014
179486 |  |  | 868 Taree - Bohnock Tee Hallidays Point 66kV Line |  | 2014Q4 | TRE | TL | 2014-12-05 15:43 | 2014-12-05 15:43 |  | Follow up |  | 66 |  |  | 2014
179487 |  |  | 868 Taree - Bohnock Tee Hallidays Point 66kV Line |  | 2014Q4 | TRE | TL | 2014-12-05 16:06 | 2014-12-05 16:06 |  | Follow up |  | 66 |  |  | 2014
179488 |  |  | 879 Narrabri - Wee Waa 66kV Line |  | 2014Q4 | NB2 | TL | 2014-12-05 19:12 | 2014-12-05 19:12 |  | Follow up |  | 66 |  |  | 2014
179489 |  |  | 879 Narrabri - Wee Waa 66kV Line |  | 2014Q4 | NB2 | TL | 2014-12-05 19:26 | 2014-12-05 19:26 |  | Follow up |  | 66 |  |  | 2014
179491 |  |  | 662 Armidale - Walcha 66kV Line |  | 2014Q4 | AR1 | TL | 2014-12-05 21:48 | 2014-12-05 21:48 |  | Follow up |  | 66 |  |  | 2014
179492 |  |  | 662 Armidale - Walcha 66kV Line |  | 2014Q4 | AR1 | TL | 2014-12-05 22:10 | 2014-12-05 22:10 |  | Follow up |  | 66 |  |  | 2014
179493 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2014Q4 | MRE | TL | 2014-12-05 22:35 | 2014-12-05 22:35 |  | Follow up |  | 66 |  |  | 2014
179494 |  |  | 879 Narrabri - Wee Waa 66kV Line |  | 2014Q4 | NB2 | TL | 2014-12-05 22:41 | 2014-12-05 22:41 |  | Follow up |  | 66 |  |  | 2014
179495 |  |  | 96Z Newcastle - Maryland 132kV Line |  | 2014Q4 | NEW | TL | 2014-12-05 22:57 | 2014-12-06 13:56 |  | Follow up |  | 132 |  |  | 2014
179496 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2014Q4 | MRE | TL | 2014-12-05 23:13 | 2014-12-05 23:13 |  | Follow up |  | 66 |  |  | 2014
179509 |  |  | 895 Forbes - Parkes (89H West Jemalong) 66kV Line |  | 2014Q4 | FB2 | TL | 2014-12-06 08:38 | 2014-12-06 08:38 |  | Follow up |  | 66 |  |  | 2014
179569 |  |  | 893/5 Forbes - Payten's Bridge 66kV Line |  | 2014Q4 | FB2 | TL | 2014-12-06 11:12 | 2014-12-06 11:12 |  | Follow up |  | 66 |  |  | 2014
179570 |  |  | 851 Beryl - Mudgee tee Gulgong 66kV Line |  | 2014Q4 | BER | TL | 2014-12-06 11:20 | 2014-12-06 11:20 |  | Follow up |  | 66 |  |  | 2014
179583 |  |  | 898 Parkes - Trundle 66kV Line |  | 2014Q4 | PKS | TL | 2014-12-06 11:59 | 2014-12-06 11:59 |  | Follow up |  | 66 |  |  | 2014
179584 |  |  | 851 Beryl - Mudgee tee Gulgong 66kV Line |  | 2014Q4 | BER | TL | 2014-12-06 12:17 | 2014-12-06 12:17 |  | Follow up |  | 66 |  |  | 2014
179585 | Lightning/Storm | TL | 97K Cooma - Munyang tee Snowy Adit 132kV TL | Q | 2014Q4 | CMA, MNY | TL | 2014-12-06 09:56 | 2014-12-06 09:56 |  | 22/12/2014 08:53:00 ¦ Follow up ¦ Nil. ¦ A close inspection of the line section will be carried out in the next aerial inspection. | On Saturday 6/12/2014 at 10:56hrs, the 132kV No.97K transmission line from Cooma 132kV Substation to Munyang Substation (tee to Snowy Adit) tripped and reclosed at both ends of the line. Protection at Cooma Substation indicated a zone 2, red phase to earth fault. No distance to fault information has been recorded. Thunderstorms were present in the area at the time of the event. INDJI recorded two lightning strikes at the time of the trip, approximately 650m from structure 8 and 2km east of Munyang Substation. An inspection of the line section closest to the lightning strikes was conducted on 17 December 2014. No evidence of damage was observed. | 132 |  |  | 2014
179586 |  |  | 97K Cooma tee Snowy Adit 132kV CB 97K2 |  | 2014Q4 | MNY | CB | 2014-12-06 09:56 | 2014-12-06 09:56 |  |  |  | 132 |  |  | 2014
179587 |  |  | 97K Munyang tee Snowy Adit CB 97K2 |  | 2014Q4 | CMA | CB | 2014-12-06 09:56 | 2014-12-06 09:56 |  |  |  | 132 |  |  | 2014
179588 | Lightning/Storm | TX | 330kV C Bus | Q | 2014Q4 | CWF | BB | 2014-12-06 13:53 | 2014-12-06 17:01 | Woodlawn TX tripped on 3 ph transient fault, suspected lightning strike, arranged No.3 TX to be proven via CB 3W2A and then RTS 330kV C bus via 330kV A bus at Capital 330kV SS | 19/03/2015 11:35:00 ¦ Follow up | Woodlawn TX tripped on 3 ph transient fault, suspected lightning strike, arranged No.3 TX to be proven via CB 3W2A and then RTS 330kV C bus via 330kV A bus at Capital 330kV SS 330kV A Bus tripped due to I/T received from Capital Wind Farm resulting in the interruption of 68MW of generation. Storms in area. 330kV A Bus was returned to service at 17:05hrs Non Transgrid reason for trip | 330 |  |  | 2014
179589 |  |  | 81C Panorama - Blayney 66kV Line |  | 2014Q4 | PMA | TL | 2014-12-06 14:44 | 2014-12-06 14:44 |  | Follow up |  | 66 |  |  | 2014
179590 | Lightning/Storm | TL | 72 Mt Piper - Wellington 330kV TL | Q | 2014Q4 | MTP, WL1 | TL | 2014-12-06 15:57 | 2014-12-06 15:57 | CB 5022 Manually closed at Mount Piper via SCADA due to no auto reclose. | 16/02/2015 14:02:00 ¦ Follow up ¦ Nil ¦ Nil | CB 5022 Manually closed at Mount Piper via SCADA due to no auto reclose. | 330 |  |  | 2014
179591 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2014Q4 | BER | TL | 2014-12-06 16:02 | 2014-12-06 16:02 |  | Follow up |  | 66 |  |  | 2014
179592 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2014Q4 | MRE | TL | 2014-12-06 18:05 | 2014-12-06 18:05 |  | Follow up |  | 66 |  |  | 2014
179593 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2014Q4 | MRE | TL | 2014-12-06 18:09 | 2014-12-06 18:09 |  | Follow up |  | 66 |  |  | 2014
179594 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2014Q4 | MRE | TL | 2014-12-06 18:15 | 2014-12-06 18:15 |  | Follow up |  | 66 |  |  | 2014
179595 |  |  | 876 Moree - Moree Solar Farm 66kV Line |  | 2014Q4 | MRE | TL | 2014-12-06 18:20 | 2014-12-06 18:20 |  | Follow up |  | 66 |  |  | 2014
179607 |  |  | 851 Beryl - Mudgee tee Gulgong 66kV Line |  | 2014Q4 | BER | TL | 2014-12-07 11:55 | 2014-12-07 11:55 |  | Follow up |  | 66 |  |  | 2014
179608 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2014Q4 | MRE | TL | 2014-12-07 14:30 | 2014-12-07 14:30 |  | Follow up |  | 66 |  |  | 2014
179609 |  |  | 879 Narrabri - Wee Waa 66kV Line |  | 2014Q4 | NB2 | TL | 2014-12-07 14:31 | 2014-12-07 14:31 |  | Follow up |  | 66 |  |  | 2014
179610 |  |  | 879 Narrabri - Wee Waa 66kV Line |  | 2014Q4 | NB2 | TL | 2014-12-07 14:33 | 2014-12-07 14:33 |  | Follow up |  | 66 |  |  | 2014
179611 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2014Q4 | MRE | TL | 2014-12-07 15:13 | 2014-12-07 15:13 |  | Follow up |  | 66 |  |  | 2014
179612 |  |  | 876 Moree - Moree Solar Farm 66kV Line |  | 2014Q4 | MRE | TL | 2014-12-07 15:13 | 2014-12-07 15:13 |  | Follow up |  | 66 |  |  | 2014
179613 |  |  | Station Transformer 1A (CB 5412) |  | 2014Q4 | MN1 | CB | 2014-12-07 15:42 | 2014-12-08 11:50 |  | Follow up |  | 330 |  |  | 2014
179614 | Lightning/Storm | TL | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Q | 2014Q4 | AR1, COF | TL | 2014-12-07 16:42 | 2014-12-07 16:42 | Essential Energy report no loss of load at dorrigo | Follow up | Essential Energy report no loss of load at dorrigo | 132 |  |  | 2014
179615 | HV Equipment | CB | No.2 Transformer 132kV B CB 4422B | Q | 2014Q4 | SE1 | CB | 2014-12-07 18:56 | 2014-12-07 20:17 |  |  | SF6 Topup | 132 |  |  | 2014
179617 |  |  | 851 Mudgee Tee Gulgong 66kV CB 8512 |  | 2014Q4 | BER | CB | 2014-12-08 02:19 | 2014-12-08 02:19 |  | Follow up |  | 66 |  |  | 2014
179631 |  |  | 828 Mt Piper 132 - Portland tee BCSC 66kV Line |  | 2014Q4 | MPP | TL | 2014-12-08 05:50 | 2014-12-08 07:34 | Endeavour Energy unable to give a figure on load lost as there are no analogues at these load points Transgrid also has no analogues at the Mt Piper end. | Follow up |  | 66 |  |  | 2014
179645 |  |  | 662 Armidale - Walcha 66kV Line |  | 2014Q4 | AR1 | TL | 2014-12-08 09:34 | 2014-12-08 09:34 |  | Follow up |  | 66 |  |  | 2014
179649 |  |  | 85X Wallerawang 132 - Lithgow 66kV Line |  | 2014Q4 | WWS | TL | 2014-12-08 10:11 | 2014-12-08 10:12 |  | Follow up |  | 66 |  |  | 2014
179650 |  |  | 857 Wallerawang 132 - Lithgow 66kV Line |  | 2014Q4 | WWS | TL | 2014-12-08 10:18 | 2014-12-08 19:00 |  | Follow up |  | 66 |  |  | 2014
179651 |  |  | 817 Wallerawang 132 - Meadow Flat 66kV Line |  | 2014Q4 | WWS | TL | 2014-12-08 12:16 | 2014-12-08 12:16 |  | Follow up |  | 66 |  |  | 2014
179654 |  |  | 867 Taree - OCC Failford 66kV Line |  | 2014Q4 | TRE | TL | 2014-12-08 12:50 | 2014-12-08 12:50 |  | Follow up |  | 66 |  |  | 2014
179655 | Lightning/Storm | TL | 30 Sydney West - Liverpool 330kV TL | Z | 2014Q4 | LP1, SYW | TL | 2014-12-08 11:32 | 2014-12-08 18:44 | Heavy Storm in Vicinity at time of trip DTF indicated 12.6km From LP1 Darren Rickard advises found dislodged Birds nest on Str 20, wires and debris hanging from Tower, will need Field AA to remove nest/debris. Also found Flashed over insulator on Str 13, correlating with DTF calculation | 16/02/2015 10:56:00 ¦ Follow up ¦ Nil ¦ Nil | Heavy Storm in Vicinity at time of trip DTF indicated 12.6km From LP1 Darren Rickard advises found dislodged Birds nest on Str 20, wires and debris hanging from Tower, will need Field AA to remove nest/debris. Also found Flashed over insulator on Str 13, correlating with DTF calculation As a result of the flashed over insulators on structure 13 of TL 30, the left-most phase insulators were replaced with composite longrod insulators. TL 30 was returned back into service on the 08/12/14 at 18:44 hours (upon completion of repair works). | 330 |  | Fault | 2014
179665 | Lightning/Storm | TL | 96P Taree - Stroud 132kV TL | Q | 2014Q4 | TRE | TL | 2014-12-08 14:05 | 2014-12-08 14:05 |  | Follow up | Successful trip and reclose during storms. | 132 |  |  | 2014
179678 | Relay | Prot | 132kV A Bus Section No.2 | Q | 2014Q4 | SYW | BB | 2014-12-09 02:59 | 2014-12-09 09:10 | Trip appeared to have been initiated from 4X2 Spare No.2 Protection. 4X2 Spare protections isolated and confirmed BBP CTs shorted and open. Bus returned to service @ 0910 hours. | 10/02/2015 11:03:00 ¦ Follow up ¦ Nil ¦ Nil | Trip appeared to have been initiated from 4X2 Spare No.2 Protection. 4X2 Spare protections isolated and confirmed BBP CTs shorted and open. Bus returned to service @ 0910 hours. | 132 | SSA - This was a known issue at the site as the decommissioning of this bay (brought about by the energistaion of Holroyd Sub @ 330kV) had not been included in that project's scope of works. There is now a greater focus on identification of decommissioning activities in the scoping phase |  | 2014
179679 |  |  | 217 Sydney West - North Eastern Creek 132kV Line |  | 2014Q4 | SYW | TL | 2014-12-09 02:59 | 2014-12-09 09:10 |  |  |  | 132 |  |  | 2014
179680 |  |  | 4X2 Spare 132kV CB 4X22 | Q | 2014Q4 | SYW | CB | 2014-12-09 02:59 | 2014-12-09 09:10 |  |  |  | 132 |  |  | 2014
179681 |  |  | No.3 Transformer 132kV A CB 4432A |  | 2014Q4 | SYW | CB | 2014-12-09 02:59 | 2014-12-09 09:10 |  |  |  | 132 |  |  | 2014
179682 |  |  | No.4 Transformer 132kV A CB 4442A |  | 2014Q4 | SYW | CB | 2014-12-09 02:59 | 2014-12-09 09:10 |  |  |  | 132 |  |  | 2014
179683 |  |  | 132kV A Bus 1-2 Section CB 4102 |  | 2014Q4 | SYW | CB | 2014-12-09 02:59 | 2014-12-09 09:10 |  |  |  | 132 |  |  | 2014
179684 |  |  | No.5 Capacitor | Z | 2014Q4 | SYW | CAP | 2014-12-09 02:59 | 2014-12-09 09:10 |  |  |  | 132 |  | Fault | 2014
179685 |  |  | No.5 Transformer 132kV A CB 4452A |  | 2014Q4 | SYW | CB | 2014-12-09 02:59 | 2014-12-09 09:10 |  |  |  | 132 |  |  | 2014
179686 |  |  | 939 Sydney West - Mamre 132kV Line | Z | 2014Q4 | SYW | TL | 2014-12-09 02:59 | 2014-12-09 09:10 |  |  |  | 132 |  | Fault | 2014
179687 |  |  | 93Z Sydney West - Blacktown 132kV Line |  | 2014Q4 | SYW | TL | 2014-12-09 02:59 | 2014-12-09 09:10 |  |  |  | 132 |  |  | 2014
179688 |  |  | 237 Sydney West - OneSteel 132kV Line | S | 2014Q4 | SYW | TL | 2014-12-09 02:59 | 2014-12-09 09:10 |  |  |  | 132 |  |  | 2014
179730 | Condition Monitor | CT | 88 Muswellbrook - Tamworth 330 330kV TL | E | 2014Q4 | MRK, TA1 | TL | 2014-12-09 10:22 | 2014-12-10 18:00 | Line de-energised due to suspect oil sample readings. | 19/01/2015 14:07:00 ¦ Follow up ¦ Nil. ¦ Substations/Northern Region is carrying out an investigation into the faulty CT and will prepare a report to advise of the findings and any recommendations. | Line de-energised due to suspect oil sample readings. A follow up sample was taken which confirmed the elevated dissolved gas results, so the CT was subsequently replaced with an identical system spare. 88TL was then returned to service on Wednesday 10/12/2015 at 19:00hrs. | 330 |  | Forced | 2014
179736 | LV/MECH Fail | CB | 330kV B Bus No.2 Section | Q | 2014Q4 | SYS | BB | 2014-12-09 07:47 | 2014-12-09 08:26 |  | 13/02/2015 11:40:00 ¦ Follow up ¦ Nil ¦ Nil | Advises No.4 Transformer CB 5442 2 phases opened correctly, Blue phase did not open correctly, in indeterminate state. As a result of the Blue phase on CB5442 failing to operate correclty, 330kV Bus section 2 was de-energised to isolate CB 5445. The clutch of the spring on the blue phase of CB5442 was readjusted and the 330kV B Bus No.2 Section was returned to service at 826 hrs on the 9/12/14. | 330 | Clutch issue. Asset Manager advises closed. |  | 2014
179737 |  |  | No.4 Transformer 330/132/11kV | E | 2014Q4 | SYS | TX | 2014-12-09 07:47 | 2014-12-09 08:26 |  |  |  | 330 |  | Forced | 2014
179738 |  |  | No.6 Transformer 330/132/11kV | E | 2014Q4 | SYS | TX | 2014-12-09 07:47 | 2014-12-09 08:26 |  |  |  | 330 |  | Forced | 2014
179739 |  |  | 330kV B Bus 1-2 Section CB 5112 |  | 2014Q4 | SYS | CB | 2014-12-09 07:47 | 2014-12-09 08:26 |  |  |  | 330 |  |  | 2014
179740 |  |  | 12 Liverpool B CB 122B |  | 2014Q4 | SYS | CB | 2014-12-09 07:47 | 2014-12-09 08:26 |  |  |  | 330 |  |  | 2014
179741 |  |  | 42 Haymarket Series Reactor | E | 2014Q4 | SYS | RX | 2014-12-09 07:47 | 2014-12-09 08:26 |  |  |  | 330 |  | Forced | 2014
179742 |  |  | 78 Ingleburn - Sydney South 330kV TL | E | 2014Q4 | ING, SYS | TL | 2014-12-09 07:47 | 2014-12-09 08:26 |  |  |  | 330 |  | Forced | 2014
179766 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2014Q4 | MRE | TL | 2014-12-09 13:39 | 2014-12-09 13:39 |  | Follow up |  | 66 |  |  | 2014
179928 |  |  | 856 Wallerawang 132 - Oberon Tee Lillyvale 66kV Line |  | 2014Q4 | WWS | TL | 2014-12-10 13:09 | 2014-12-10 13:09 |  | Follow up |  | 66 |  |  | 2014
179938 |  |  | 890 Murrumburrah - Young 66kV Line |  | 2014Q4 | MRU | TL | 2014-12-10 13:09 | 2014-12-10 13:09 |  | Follow up |  | 66 |  |  | 2014
179948 |  |  | 851 Beryl - Mudgee tee Gulgong 66kV Line |  | 2014Q4 | BER | TL | 2014-12-10 16:52 | 2014-12-10 16:52 | 2 occasions of TAR 1st event - 16:52:01 2nd event - 16:52:14 | Follow up |  | 66 |  |  | 2014
179949 | Lightning/Storm | TL | 94B Beryl - Wellington 132kV TL | Z | 2014Q4 | BER, WL1 | TL | 2014-12-10 17:34 | 2014-12-11 14:34 | Transmission Line remained out of service overnight, but available for emergency service (reclose non auto). Scheduled outage for 11/12/2014 went ahead for line work, and full patrol carried out on line. No. defects found on line and returned to service on completion of field work. | Follow up ¦ Nil ¦ Nil | Transmission Line remained out of service overnight, but available for emergency service (reclose non auto). Scheduled outage for 11/12/2014 went ahead for line work, and full patrol carried out on line. No. defects found on line and returned to service on completion of field work. | 132 |  | Fault | 2014
179998 |  |  | 878 Narrabri - Boggabri 66kV Line |  | 2014Q4 | NB2 | TL | 2014-12-11 11:43 | 2014-12-11 11:43 |  | Follow up |  | 66 |  |  | 2014
180019 |  |  | 250 Sydney North - Berowra 132kV Line | X | 2014Q4 | SYN | TL | 2014-12-21 16:54 | 2014-12-23 15:09 |  |  |  | 132 |  |  | 2014
180026 | Lightning/Storm | TL | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Q | 2014Q4 | AR1, COF | TL | 2014-12-11 14:31 | 2014-12-11 14:31 | Trip and auto reclose during thunderstorm activity. | Follow up | Trip and auto reclose during thunderstorm activity. | 132 |  |  | 2014
180027 |  |  | No.3 Tenterfield - Council (Timbarra Mine) 22kV Line |  | 2014Q4 | TTF | TL | 2014-12-11 14:53 | 2014-12-11 19:01 | Essential Energy advise supply interruption to No.3 Fdr supply point. SCADA alarms from site indicate probable trip, auto reclose and lockout. Staff travelling to site for investigation at time of report. | Follow up |  | 22 |  |  | 2014
180028 |  |  | 0896 Koolkhan - Maclean 66kV Line |  | 2014Q4 | KLK | TL | 2014-12-11 15:32 | 2014-12-11 15:32 | Trip and auto reclose during storm activity. | Follow up |  | 66 |  |  | 2014
180078 |  |  | 705 Coffs Harbour - South Coffs Harbour 66kV Line |  | 2014Q4 | COF | TL | 2014-12-12 11:48 | 2014-12-12 11:48 | Trip and auto reclose during high wind in area. | Follow up |  | 66 |  |  | 2014
180114 | HV Equipment | CB | 330kV B Bus 1-2 Section CB 5112 | Q | 2014Q4 | SE1 | CB | 2014-12-14 20:33 | 2014-12-15 11:02 |  |  | CB SF6 Topup | 330 |  |  | 2014
180154 | HV Equipment | CB | No.1 Transformer 330/132/11kV | B | 2014Q4 | SYS | TX | 2014-12-16 06:30 | 2014-12-16 08:33 |  |  | CB SF6 Topup | 330 |  | Forced | 2014
180155 |  |  | 888/1 Cooma - Rhine Falls 66kV Line |  | 2014Q4 | CMA | TL | 2014-12-15 17:26 | 2014-12-16 11:25 |  | Follow up |  | 66 |  |  | 2014
180181 |  |  | 82K/1 Queanbeyan - Bungendore tee Sutton 66kV Line |  | 2014Q4 | QBY | TL | 2014-12-16 09:00 | 2014-12-16 09:00 | Advised by SO/Essential Energy of storms in area. Total Fire ban in customer area so customer A/R Non auto. | Follow up |  | 66 |  |  | 2014
180192 |  |  | 250 Sydney North - Berowra 132kV Line | X | 2014Q4 | SYN | TL | 2014-12-28 14:23 | 2014-12-31 15:04 |  |  |  | 132 |  |  | 2014
180193 |  |  | 250 Sydney North - Berowra 132kV Line | X | 2015Q1 | SYN | TL | 2015-01-04 13:53 | 2015-01-09 15:30 |  |  |  | 132 |  |  | 2015
180236 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2014Q4 | MRE | TL | 2014-12-16 16:29 | 2014-12-16 16:29 |  | Follow up |  | 66 |  |  | 2014
180276 |  |  | No.3 Transformer | N | 2014Q4 | TOM | TX | 2014-12-17 08:28 | 2014-12-17 09:55 | Potline 2 interrupted. TAC restoration from No.2 MRT soon after trip. Tomago Aluminium advised no fault found with No.3 TX. | Follow up |  | 330 |  |  | 2014
180301 |  |  | No.3 Transformer |  | 2014Q4 | TOM | TX | 2014-12-17 12:12 | 2014-12-17 13:04 | Trip from service whilst closed on CB 5432B only whilst customer in process of fault finding within it's system. Investigation ongoing at time of report. TG staff on site at time of event to assist in restoration as required. | Follow up |  | 330 |  |  | 2014
180306 | Animal/Bird | Cap | No.3 Capacitor | Z | 2014Q4 | SYN | CAP | 2014-12-17 11:51 | 2014-12-17 15:03 | Staff on site report dead crow inside No.3 Capacitor cage. Capacitor isolated and earthed for inspection. Clearance given to return No.3 Capacitor to service. | 6/02/2015 14:50:00 ¦ Follow up ¦ Nil ¦ Nil | Staff on site report dead crow inside No.3 Capacitor cage. Capacitor isolated and earthed for inspection. Clearance given to return No.3 Capacitor to service. | 132 |  | Fault | 2014
180410 |  |  | No.3 Transformer 330/132/11kV | B | 2014Q4 | MTP | TX | 2014-12-19 06:05 | 2014-12-19 08:01 |  |  |  | 330 |  | Forced | 2014
180416 |  |  | 32 Sydney West - Bayswater 330kV TL | X | 2015Q1 | BAY, SYW | TL | 2015-01-31 05:02 | 2015-01-31 15:52 |  |  |  | 330 |  |  | 2015
180417 |  |  | 32 Sydney West - Bayswater 330kV TL | X | 2015Q1 | BAY, SYW | TL | 2015-02-01 05:01 | 2015-02-01 12:49 |  |  |  | 330 |  |  | 2015
180427 |  |  | 664 Armidale - Armidale 66kV Line |  | 2014Q4 | AR1 | TL | 2014-12-18 13:54 | 2014-12-18 13:55 | Trip and auto reclose during storm activity. | Follow up |  | 66 |  |  | 2014
180431 | Lightning/Storm | TL | 9W3 Coffs Harbour - Raleigh 132kV TL | Z | 2014Q4 | COF, RAL | TL | 2014-12-18 16:37 | 2014-12-19 07:28 | Trip reclose and lockout. Customer reports notable surge at time of fault. Distance to fault appears 1.5 to 1.7 km from Coffs Harbour Substation. Line patrol in progress at time of report. Line returned to service after patrol by A. Wrona and advice from Bruce Fraser | 19/01/2015 11:03:00 ¦ Follow up ¦ Nil. ¦ Nil. | Trip reclose and lockout. Customer reports notable surge at time of fault. Distance to fault appears 1.5 to 1.7 km from Coffs Harbour Substation. Line patrol in progress at time of report. Line returned to service after patrol by A. Wrona and advice from Bruce Fraser A patrol was carried out on Thursday 18/12/2014 and identified no evidence of damage to the 9W3TL. On Friday 19/12/2014 at 08:28hrs, the 9W3TL was returned to service. | 132 |  | Fault | 2014
180434 |  |  | 94Y Mt Piper 330 - Mt Piper 132 132kV TL | B | 2014Q4 | MPP, MTP | TL | 2014-12-19 06:05 | 2014-12-19 08:01 |  |  |  | 132 |  | Forced | 2014
180453 |  |  | M5 Murray - Murray 1 330kV TL | X | 2015Q1 | MUR, MP1 | TL | 2015-01-08 07:54 | 2015-01-08 14:43 |  |  |  | 330 |  |  | 2015
180454 | Staff Error | TX | No.3 Transformer 330/132/11kV | Z | 2014Q4 | MTP | TX | 2014-12-19 08:01 | 2014-12-19 08:34 | During planned LV protection work on the No3 Transformer, the associated 330kV CBs were tripped. No operation of CBs listed on RFA. Bay had been closed after isolation steps completed. CBs closed during restoration switching. | Follow up | During planned LV protection work on the No3 Transformer, the associated 330kV CBs were tripped. No operation of CBs listed on RFA. Bay had been closed after isolation steps completed. CBs closed during restoration switching. | 330 | SSA - Faulted Equipment changed to Transformer (TX). FEOR came about due to an error in the PMWI used to perform the isolations. PWMI was checked independently, however the error was not identified. No Further comment. | Fault | 2014
180455 |  |  | 94Y Mt Piper 330 - Mt Piper 132 132kV TL | Z | 2014Q4 | MPP, MTP | TL | 2014-12-19 08:01 | 2014-12-19 08:34 |  |  |  | 132 |  | Fault | 2014
180513 | HV Equipment | CB | No.2 Capacitor | E | 2014Q4 | SYS | CAP | 2014-12-20 13:15 | 2014-12-20 14:24 |  |  | SF6 Topup | 132 |  | Forced | 2014
180514 | HV Equipment | CB | No.1 Transformer 330/132/11kV | E | 2014Q4 | SYS | TX | 2014-12-20 14:41 | 2014-12-20 16:23 | Low SF6 Red phase CB 5412, now topped up. | 6/02/2015 11:44:00 ¦ Follow up ¦ Nil ¦ Nil | Low SF6 Red phase CB 5412, now topped up. | 330 |  | Forced | 2014
180563 |  |  | U5 Upper Tumut - Tumut 2 330kV TL | X | 2015Q1 | UT1 | TL | 2015-01-06 10:44 | 2015-01-06 17:41 |  |  |  | 330 |  |  | 2015
180564 |  |  | U7 Upper Tumut - Tumut 2 330kV TL | X | 2015Q1 | UT1 | TL | 2015-01-06 10:48 | 2015-01-06 14:52 |  |  |  | 330 |  |  | 2015
180578 |  |  | 735 Inverell - Inverell 66kV Line |  | 2014Q4 | INV | TL | 2014-12-18 14:02 | 2014-12-18 14:02 | Trip and auto reclose during storm activity. Belated information provided by site staff when attending site on 22/12/14. No SCADA monitoring. Essential Energy advised of protection details. | Follow up |  | 66 |  |  | 2014
180579 |  |  | 83G Wagga North - Bomen 66kV Line |  | 2014Q4 | WGN | TL | 2014-12-22 21:00 | 2014-12-23 10:22 | Supply was restored by Essential Energy transfering lost load to No.4 Hammond Ave Wagga 132kV SS, Essential Energy advised crossarm down on conductors repairs required. | Follow up |  | 66 |  |  | 2014
180580 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2014Q4 | MRE | TL | 2014-12-23 00:59 | 2014-12-23 10:19 |  | Follow up |  | 66 |  |  | 2014
180581 |  |  | No.2 330kV Generator Transformer Group |  | 2014Q4 | ER0 | TX | 2014-12-23 01:25 | 2014-12-23 02:49 | PS carrying out prot'n work with TX group O/S and tripped No.2 bay, RTS Gen TX group when bay was closed | Follow up |  | 330 |  |  | 2014
180605 |  |  | 879 Narrabri - Wee Waa 66kV Line |  | 2014Q4 | NB2 | TL | 2014-12-23 07:25 | 2014-12-23 07:25 | Trip and successful auto reclose during storm activity in area. | Follow up |  | 66 |  |  | 2014
180606 |  |  | 879 Narrabri - Wee Waa 66kV Line |  | 2014Q4 | NB2 | TL | 2014-12-23 08:30 | 2014-12-24 20:06 | Trip auto reclose and lockout during storm activity in area. Previous trip and auto reclose approximately 1 hour prior. | Follow up |  | 66 |  |  | 2014
180610 |  |  | 895 Forbes - Parkes (89H West Jemalong) 66kV Line |  | 2014Q4 | FB2 | TL | 2014-12-23 09:15 | 2014-12-23 09:15 |  | Follow up |  | 66 |  |  | 2014
180611 |  |  | 896 Forbes - West Jemalong 66kV Line |  | 2014Q4 | FB2 | TL | 2014-12-23 09:22 | 2014-12-23 09:22 |  | Follow up |  | 66 |  |  | 2014
180614 |  |  | 896 Forbes - West Jemalong 66kV Line |  | 2014Q4 | FB2 | TL | 2014-12-23 09:37 | 2014-12-23 09:37 |  | Follow up |  | 66 |  |  | 2014
180616 |  |  | 895 Forbes - Parkes (89H West Jemalong) 66kV Line |  | 2014Q4 | FB2 | TL | 2014-12-23 09:46 | 2014-12-23 09:46 | Distance to fault - 3.51km | Follow up |  | 66 |  |  | 2014
180617 |  |  | 893/5 Forbes - Payten's Bridge 66kV Line |  | 2014Q4 | FB2 | TL | 2014-12-23 10:17 | 2014-12-23 10:18 |  | Follow up |  | 66 |  |  | 2014
180627 |  |  | 940 Wallerawang 132 - Warimoo tee North Katoomba 132kV Line |  | 2014Q4 | WWS | TL | 2014-12-23 12:47 | 2014-12-23 12:47 | Trip and successful auto reclose during thunderstorm activity. | Follow up |  | 132 |  |  | 2014
180640 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2014Q4 | CW2 | TL | 2014-12-23 17:44 | 2014-12-23 21:48 |  | Follow up |  | 66 |  |  | 2014
180641 |  |  | 893/1 Cowra - Grenfell 66kV Line |  | 2014Q4 | CW2 | TL | 2014-12-23 20:35 | 2014-12-23 20:35 |  | Follow up |  | 66 |  |  | 2014
180642 | Lightning/Storm | TL | 990 Yass - Wagga 132 132kV TL | Q | 2014Q4 | WG2, YSN | TL | 2014-12-23 22:14 | 2014-12-23 22:14 |  | 5/03/2015 12:44:00 ¦ Follow up ¦ Nil ¦ The line will be monitored through scheduled maintenance activities. |  | 132 |  |  | 2014
180683 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2014Q4 | MRE | TL | 2014-12-24 21:55 | 2014-12-24 21:55 |  | Follow up |  | 66 |  |  | 2014
180684 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2014Q4 | MRE | TL | 2014-12-24 22:22 | 2014-12-24 22:22 |  | Follow up |  | 66 |  |  | 2014
180693 |  |  | 836 Murrumburrah - Cootamundra 66kV Line |  | 2014Q4 | MRU | TL | 2014-12-25 10:25 | 2014-12-25 10:25 |  | Follow up |  | 66 |  |  | 2014
180694 |  |  | 82K/1 Bungendore tee Sutton CB 82K2 |  | 2014Q4 | QBY | CB | 2014-12-25 11:10 | 2014-12-25 11:10 |  | Follow up |  | 66 |  |  | 2014
180695 |  |  | 976/2 Yass - Spring Flat tee Murrumbateman 132kV TL | Q | 2014Q4 | YSN, SFF | TL | 2014-12-25 12:22 | 2014-12-25 12:22 |  | Follow up |  | 132 |  |  | 2014
180696 |  |  | 895 Parkes 66kV CB 8952 |  | 2014Q4 | FB2 | CB | 2014-12-25 13:34 | 2014-12-25 13:34 |  | Follow up |  | 66 |  |  | 2014
180697 |  |  | 895 Parkes 66kV CB 8952 |  | 2014Q4 | FB2 | CB | 2014-12-25 13:35 | 2014-12-25 13:35 |  | Follow up |  | 66 |  |  | 2014
180698 |  |  | 817 Wallerawang 132 - Meadow Flat 66kV Line |  | 2014Q4 | WWS | TL | 2014-12-25 13:51 | 2014-12-25 13:51 |  | Follow up |  | 66 |  |  | 2014
180699 |  |  | 875 Wallerawang 132 - Oakey Park 66kV Line |  | 2014Q4 | WWS | TL | 2014-12-25 14:10 | 2014-12-25 16:40 |  | Follow up |  | 66 |  |  | 2014
180700 |  |  | 856 Wallerawang 132 - Oberon Tee Lillyvale 66kV Line |  | 2014Q4 | WWS | TL | 2014-12-25 14:24 | 2014-12-25 14:24 |  | Follow up |  | 66 |  |  | 2014
180701 |  |  | 251 Sydney North - Pennant Hills 132kV Line |  | 2014Q4 | SYN | TL | 2014-12-25 15:04 | 2014-12-25 20:40 |  | Follow up |  | 132 |  |  | 2014
180702 | Lightning/Storm | TL | 85 Tamworth 330 - Armidale 330kV TL | Q | 2014Q4 | AR1, TA1 | TL | 2014-12-25 15:59 | 2014-12-25 15:59 |  | 23/01/2015 09:29:00 ¦ Follow up ¦ Nil. ¦ Nil. |  | 330 |  |  | 2014
180703 |  |  | 867 Taree - OCC Failford 66kV Line |  | 2014Q4 | TRE | TL | 2014-12-25 17:28 | 2014-12-25 17:28 | Also tripped No.4 TX | Follow up |  | 66 |  |  | 2014
180704 |  |  | 957 Vales Pt - Ourimbah tee Morisset 132kV Line |  | 2014Q4 | VP1 | TL | 2014-12-25 20:20 | 2014-12-26 11:30 |  | Follow up |  | 132 |  |  | 2014
180705 | Unknown | TX | No.4 Transformer 132/66/11kV | Z | 2014Q4 | TRE | TX | 2014-12-25 17:28 | 2014-12-25 20:17 | Advised John Mccall that a Visual check of transformer completed and there is no gas in the Bucholz and double check all protection flags prior to reseting all protections. then received permission to re-energise No.4 Transformer at Taree Substation | Follow up | Transformer tripped on Bucholz. Advised John Mccall that a Visual check of transformer completed and there is no gas in the Bucholz and double check all protection flags prior to reseting all protections. Then received permission to re-energise No.4 Transformer at Taree Substation. | 132 | SSA - No SSA Input Required - Subs Issue. | Fault | 2014
180740 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2014Q4 | GRF | TL | 2014-12-27 13:39 | 2014-12-27 13:39 | Protection details to be followed up. | Follow up |  | 33 |  |  | 2014
180741 | Unknown | TL | 97K Cooma - Munyang tee Snowy Adit 132kV TL | Q | 2014Q4 | CMA, MNY | TL | 2014-12-28 05:02 | 2014-12-28 05:02 | Please note, CB and R/C cyclos at Munyang are the same as when checked at last inspection, ie. no CB op at Munyang | 20/01/2015 09:26:00 ¦ Follow up ¦ Nil. ¦ Nil. | Successful trip and reclose, cause unknown. A ground patrol was conducted between structure 210 and 230 to identify any issues or cause of the trip. No evidence of damage was observed. | 132 |  |  | 2014
180742 |  |  | 97K Cooma tee Snowy Adit 132kV CB 97K2 |  | 2014Q4 | MNY | CB | 2014-12-28 05:02 | 2014-12-28 05:02 |  |  |  | 132 |  |  | 2014
180743 |  |  | 97K Munyang tee Snowy Adit CB 97K2 |  | 2014Q4 | CMA | CB | 2014-12-28 05:02 | 2014-12-28 05:02 |  |  |  | 132 |  |  | 2014
180748 |  |  | 850 Tumut - Talbingo tee Jounama Dam 66kV Line |  | 2014Q4 | TU2 | TL | 2014-12-29 00:07 | 2014-12-29 00:07 |  | Follow up |  | 66 |  |  | 2014
180815 |  |  | No.2 330kV Generator Transformer Group |  | 2014Q4 | ER0 | TX | 2014-12-30 21:07 | 2014-12-30 23:24 |  | Follow up |  | 330 |  |  | 2014
180828 | Relay | Prot | No.2 Transformer 500/330/33kV | Z | 2014Q4 | BBY | TX | 2014-12-31 08:32 | 2015-01-01 15:59 |  | 19/03/2015 11:55:00 ¦ Follow up | At 08:32hrs Banaby No.2 Transformer tripped. Protection operated alarms received, staff called out to investigate. No.1 protection relay found faulty. | 500 | SSA - Faulty T60 Relay. No Further Comment. | Fault | 2014
180829 |  |  | No.2 Reactor |  | 2014Q4 | BBY | RX | 2014-12-31 08:32 | 2015-01-01 15:59 |  |  |  | 33 |  |  | 2014
180833 | HV Equipment | CB | No.5 Transformer 330/132/11kV | E | 2014Q4 | SYN | TX | 2014-12-31 17:33 | 2015-01-13 13:28 |  |  | Replace SF6 gauge on CT. | 330 |  | Forced | 2014
180834 |  |  | 867 Taree - OCC Failford 66kV Line |  | 2015Q1 | TRE | TL | 2015-01-01 00:53 | 2015-01-01 00:53 |  | Follow up |  | 66 |  |  | 2015
180867 | HV Equipment | CB | No.2 Capacitor | B | 2015Q1 | SYS | CAP | 2015-01-01 11:13 | 2015-01-01 12:05 |  |  | CB SF6 Topup | 132 |  | Forced | 2015
180868 |  |  | Broken Hill - Railway Town 22kV Line |  | 2015Q1 | BKH | TL | 2015-01-01 11:28 | 2015-01-01 12:55 | Customer outage caused by birds on 22kV Gas Switch in the field ( Customer System) all load restored at 12:55 hrs via SCADA | Follow up |  | 22 |  |  | 2015
180870 | HV Equipment | VT | 29 Sydney West - Vineyard 330kV TL | E | 2015Q1 | SYW, VYD | TL | 2015-01-01 15:01 | 2015-01-02 15:01 | 29 Sydney West - Vineyard 330KV TL was I&E on HVPRI 56608 to replace faulty B phase CVT at Vineyard 330kV Substation | 4/03/2015 13:47:00 ¦ Follow up ¦ Nil ¦ Nil | 29 Sydney West - Vineyard 330KV TL was I&E on HVPRI 56608 to replace faulty B phase CVT at Vineyard 330kV Substation On the 2/2/15 the NSO/Central/Substations team replaced the faulty B phase CVT and returned the line back into service. | 330 |  | Forced | 2015
180871 | Lightning/Storm | TL | 9W8 Boambee South - Coffs Harbour 132kV TL | Q | 2015Q1 | COF, BOS | TL | 2015-01-01 20:16 | 2015-01-01 20:17 |  | Follow up | Successful trip and reclose. Thunderstorms in the area. | 132 |  |  | 2015
180872 | Lightning/Storm | TL | 9W3 Coffs Harbour - Raleigh 132kV TL | Q | 2015Q1 | COF, RAL | TL | 2015-01-01 20:16 | 2015-01-01 20:17 |  | Follow up | Successful trip and reclose. Thunderstorms in the area. | 132 |  |  | 2015
180873 |  |  | 878 Narrabri - Boggabri 66kV Line |  | 2015Q1 | NB2 | TL | 2015-01-01 23:41 | 2015-01-01 23:41 |  | Follow up |  | 66 |  |  | 2015
180874 | Lightning/Storm | TL | 968 Tamworth 330 - Narrabri 132kV TL | Q | 2015Q1 | NB2, TA1 | TL | 2015-01-02 03:04 | 2015-01-02 03:04 | CB 9682 manually closed via scada at Tamworth 330 | Follow up | At 03:04hrs 968 Tamworth330 to Narrabri132 132 kV T/L Tripped at Tamworth and Narabri, and reclosed only at Narrabri, C.B. at Tamworth closed via SCADA. Storms in the area. Site staff provided protection details and advised CB 9682 was selected for non auto reclose at Tamworth330. | 132 |  |  | 2015
180918 |  |  | 867 Taree - OCC Failford 66kV Line |  | 2015Q1 | TRE | TL | 2015-01-01 00:53 | 2015-01-01 00:53 | Apparent trip and successful auto reclose. | Follow up |  | 66 |  |  | 2015
180919 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2015Q1 | MRE | TL | 2015-01-02 06:20 | 2015-01-02 06:20 | Trip and successful auto reclose during storm activity in area. | Follow up |  | 66 |  |  | 2015
180920 |  |  | 723 Wenna Tee Wathagar 66kV CB 7232 |  | 2015Q1 | MRE | CB | 2015-01-02 06:35 | 2015-01-02 06:35 | Second trip and auto reclose within short time frame during storm activity in area. | Follow up |  | 66 |  |  | 2015
180921 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2015Q1 | MRE | TL | 2015-01-02 07:03 | 2015-01-02 07:03 | Trip and successful auto reclose during storm activity in area. | Follow up |  | 66 |  |  | 2015
180922 |  |  | 876 Moree - Moree Solar Farm 66kV Line |  | 2015Q1 | MRE | TL | 2015-01-02 08:33 | 2015-01-02 08:33 | Trip and successful auto reclose during storm activity in area. Attempts to notify Market participant unsuccessful at time of report with extended periods on hold experienced when using customer communication facilities. | Follow up |  | 66 |  |  | 2015
180923 |  |  | 870 Tamworth 132 - Kootingal 66kV Line |  | 2015Q1 | TMW | TL | 2015-01-02 07:40 | 2015-01-02 07:40 | Site staff report six C.B. operations (trip and auto reclose) at undisclosed times. FEOR created to capture identified protection details. | Follow up |  | 66 |  |  | 2015
180924 |  |  | 804 Tamworth 132 - Nundle 66kV Line |  | 2015Q1 | TMW | TL | 2015-01-02 08:00 | 2015-01-02 08:00 | Site staff report five C.B. operations at undisclosed times. FEOR created to capture identified protection details. | Follow up |  | 66 |  |  | 2015
180926 |  |  | 856 Wallerawang 132 - Oberon Tee Lillyvale 66kV Line |  | 2015Q1 | WWS | TL | 2015-01-02 13:57 | 2015-01-02 18:14 | Trip, auto reclose, trip and lock out during storm activity. Preceeded by two other trip and reclose in close succession. Customer supply restored from within customer system within short time frame. TG staff on-route to site for investigation at time of report generation. | Follow up |  | 66 |  |  | 2015
180974 | Pollution | TL | O7 Lower Tumut - Canberra 330kV TL | Q | 2015Q1 | CA1, LT1 | TL | 2015-01-03 16:01 | 2015-01-03 16:01 | Bush Fire reported directly under the line | 9/01/2015 12:27:00 ¦ Follow up ¦ As above. ¦ As above. | On Saturday 03/01/2015 at 17:01hrs, the 330kV No.O7 transmission line from Canberra 330kV Substation to Lower Tumut 330kV Substation tripped and reclosed at both ends of the line. A bushfire around the Lunds Plantation area north of Talbingo travelled under the line. A subsequent trip and reclose operation occurred 6 minutes later at 17:07 hours also due to the bushfire (see FEOR 2015-F-0016 and follow up report 2015-F-0016-945). No protection details were recorded. The weather was fine at the time of the event | 330 |  |  | 2015
180975 | Pollution | TL | O7 Lower Tumut - Canberra 330kV TL | Q | 2015Q1 | CA1, LT1 | TL | 2015-01-03 16:07 | 2015-01-03 16:07 | Bush fire reported directly under the line. | 9/01/2015 12:12:00 ¦ Follow up ¦ Nil. ¦ Nil. | On Saturday 03/01/2015 at 17:07hrs, the 330kV No.O7 transmission line from Canberra 330kV Substation to Lower Tumut 330kV Substation tripped and reclosed at both ends of the line. This was the second trip and reclose operation as a result of a bushfire which travelled underneath the line. The bushfire was present around the Lunds Plantation area north of Talbingo. Protection at Canberra 330kV Substation indicated a zone 1, 2 phase to earth fault. While protection at Lower Tumut 330kV Substation indicated a zone 1, phase to phase fault. The weather was fine at the time of the event An aerial inspection and a ground patrol were conducted on Saturday 03/01/2015 and Monday 05/01/2015 respectively. The patrols found that several earth wire vibration dampers were damaged on structure 19 as a result of the fire. These were replaced on Tuesday 06/01/2015. | 330 |  |  | 2015
180992 |  |  | 81C Panorama - Blayney 66kV Line |  | 2015Q1 | PMA | TL | 2015-01-04 12:28 | 2015-01-04 12:28 |  | Follow up |  | 66 |  |  | 2015
180993 |  |  | 847 Murrumburrah - Boorowa 66kV Line |  | 2015Q1 | MRU | TL | 2015-01-04 12:22 | 2015-01-04 12:22 | Storms crossing over the area. | Follow up |  | 66 |  |  | 2015
180994 |  |  | 875 Wallerawang 132 - Oakey Park 66kV Line |  | 2015Q1 | WWS | TL | 2015-01-04 16:23 | 2015-01-04 19:19 | Line returned to service after patrol by Sydney trains. | Follow up |  | 66 |  |  | 2015
180995 |  |  | 857 Wallerawang 132 - Lithgow 66kV Line |  | 2015Q1 | WWS | TL | 2015-01-04 17:12 | 2015-01-04 17:12 |  | Follow up |  | 66 |  |  | 2015
180996 |  |  | 82G Queanbeyan - Captains Flat 66kV Line |  | 2015Q1 | QBY | TL | 2015-01-04 17:34 | 2015-01-04 17:34 |  | Follow up |  | 66 |  |  | 2015
180997 |  |  | 940 Wallerawang 132 - Warimoo tee North Katoomba 132kV Line |  | 2015Q1 | WWS | TL | 2015-01-04 17:43 | 2015-01-04 17:43 |  | Follow up |  | 132 |  |  | 2015
180998 |  |  | 941 Wallerawang 132 - Lawson tee North Katoomba 132kV Line |  | 2015Q1 | WWS | TL | 2015-01-04 17:43 | 2015-01-04 17:43 |  | Follow up |  | 132 |  |  | 2015
181006 |  |  | 81F Panorama - Bathurst 66kV Line |  | 2015Q1 | PMA | TL | 2015-01-04 19:29 | 2015-01-04 19:29 |  | Follow up |  | 66 |  |  | 2015
181007 | Unknown/Storm | Other | 132kV B Bus No.2 Section | Q | 2015Q1 | SYS | BB | 2015-01-04 18:17 | 2015-01-05 12:16 | No.4 TX energised only prior trip. 910 TL I & E'd for AusGrid prior trip. Appears to have been a flashover on CB 4022 overhead conductors. CB 4022 subsequently isolated and bus made available in an emergency pending further investigations tomorrow. Amend 1: The above statement should read as follows: No.4 TX energised only prior trip. 914 TL I & E'd for AusGrid prior trip. Appears to have been a flashover on CB 4022 overhead conductors. CB 4022 subsequently isolated and bus made available in an emergency pending further investigations tomorrow. | 25/02/2015 16:46:00 ¦ Follow up ¦ Nil ¦ Nil | The above statement should read as follows: No.4 TX energised only prior trip. 914 TL I & E'd for AusGrid prior trip. Appears to have been a flashover on CB 4022 overhead conductors. CB 4022 subsequently isolated and bus made available in an emergency pending further investigations tomorrow. As the mechnical integrity of the insulator was deemed to be of sound condition, the bus coupler was returned to service on Monday (05/01/15) afternoon. A defect was recorded as the insulator string in question required replacement. Central Mains were able to replace the defective insulator string on the 24/01/2015 and has the bus sections returned to sevice on the same day. | 132 |  |  | 2015
181008 |  |  | 910 Chullora tee Canterbury CB 9102 |  | 2015Q1 | SYS | CB | 2015-01-04 18:17 | 2015-01-05 12:16 |  |  |  | 132 |  |  | 2015
181009 |  |  | No.4 Transformer 330/132/11kV | Z | 2015Q1 | SYS | TX | 2015-01-04 18:17 | 2015-01-05 12:16 |  |  |  | 330 |  | Fault | 2015
181010 |  |  | No.5 Transformer 330/132/11kV | Z | 2015Q1 | SYS | TX | 2015-01-04 18:17 | 2015-01-05 12:16 |  |  |  | 330 |  | Fault | 2015
181011 |  |  | No.2 Capacitor | Z | 2015Q1 | SYS | CAP | 2015-01-04 18:17 | 2015-01-05 12:16 |  |  |  | 132 |  | Fault | 2015
181012 |  |  | 283 Sydney South - Milperra tee Revesby 132kV Cable | S | 2015Q1 | SYS | UG | 2015-01-04 18:17 | 2015-01-05 12:16 |  |  |  | 132 |  |  | 2015
181013 |  |  | 914 Sydney South - Bankstown 132kV Line |  | 2015Q1 | SYS | TL | 2015-01-04 18:17 | 2015-01-05 12:16 |  |  |  | 132 |  |  | 2015
181014 |  |  | 828 Mt Piper 132 - Portland tee BCSC 66kV Line |  | 2015Q1 | MPP | TL | 2015-01-04 21:52 | 2015-01-04 21:52 |  | Follow up |  | 66 |  |  | 2015
181016 |  |  | M7 Murray - Murray 1 330kV TL | X | 2015Q1 | MUR, MP1 | TL | 2015-01-07 13:25 | 2015-01-20 15:01 |  |  |  | 330 |  |  | 2015
181038 |  |  | 996 Wagga 330 - ANM tee Morven 132kV TL | X | 2015Q1 | ANM, WG1 | TL | 2015-01-19 06:41 | 2015-01-19 06:55 |  |  |  | 132 |  |  | 2015
181039 |  |  | 996 Wagga 330 - ANM tee Morven 132kV TL | X | 2015Q1 | ANM, WG1 | TL | 2015-01-19 11:11 | 2015-01-19 11:28 |  |  |  | 132 |  |  | 2015
181046 | Relay | Prot | 850 Tumut - Talbingo tee Jounama Dam 66kV Line | Q | 2015Q1 | TU2 | TL | 2015-01-05 15:23 | 2015-01-05 16:47 | Trend suggest 1.7MW load lost. Feeder succesfully energised Storms in vicinity at time of trip | Follow up | 850 Tumut to Talbingo tee Jounama Dam 66kV Feeder tripped, failed to reclose. Storms in the area. | 66 | (WO 346864) Relay to be replaced 17 June Faulty Current input module |  | 2015
181047 |  |  | 82K/1 Queanbeyan - Bungendore tee Sutton 66kV Line |  | 2015Q1 | QBY | TL | 2015-01-05 17:53 | 2015-01-05 17:53 |  | Follow up |  | 66 |  |  | 2015
181119 | Secondary Equipment | Cont | 848 Tumut - Tumbarumba tee Batlow tee Adelong 66kV Line | Q | 2015Q1 | TU2 | TL | 2015-01-06 17:08 | 2015-01-06 19:23 | Note!!! CB 8482 failed to attempt a re-close SCADA log shows an alarm - 066 Tumbarumba 8482 CB A/R Operate FL ALARM. This is the second time in 2 days at Tumut 132 that a CB has not attempted a re-close after a line protection operation. | Follow up | CB 8482 failed to attempt a re-close SCADA log shows an alarm - 066 Tumbarumba 8482 CB A/R Operate FL ALARM. This is the second time in 2 days at Tumut 132 that a CB has not attempted a re-close after a line protection operation. Storms in the area. | 66 | Since this FEOR, there have been two occasions that the AR has worked correctly. This being on the 12th (FEOR 103 - TAR) and 13th (FEOR 113 - TARTLO) February. Therefore AR is operational. |  | 2015
181140 | HV Equipment | CB | No.2 Capacitor | B | 2015Q1 | SYS | CAP | 2015-01-07 09:22 | 2015-01-07 10:09 |  |  | CB SF6 TOPUP | 132 |  | Forced | 2015
181186 | Unknown | Cont | 9UR Marulan - Taralga Wind Farm 132kV Line | Q | 2015Q1 | MRN | TL | 2015-01-07 10:08 | 2015-01-07 14:49 |  | Follow up | Reclose not attempted when this line tripped. | 132 |  |  | 2015
181253 |  |  | M1 Murray - Murray 1 330kV TL | Y | 2015Q1 | MUR, MP1 | TL | 2015-01-08 12:29 | 2015-01-09 17:27 | SHL advised trip caused by an LV cabling fault in their system. HMI Alarms at Murray Units 1/2 CCP I/T Rec Units 1/2 Trip relay Operated Units 1/2 B I/T Rec or Faulty | Follow up |  | 330 |  |  | 2015
181260 |  |  | No.1 Balranald - Balranald 22kV Line |  | 2015Q1 | BRD | TL | 2015-01-08 14:30 | 2015-01-08 14:30 |  | Follow up |  | 22 |  |  | 2015
181261 |  |  | 84A Finley - Jerilderie 66kV Line |  | 2015Q1 | FNY | TL | 2015-01-08 17:02 | 2015-01-08 17:02 | Protection Reset Distance to Fault - 19.65km | Follow up |  | 66 |  |  | 2015
181281 | Unknown | VT | No.2 Transformer 500/330/33kV | E | 2015Q1 | BBY | TX | 2015-01-09 12:43 | 2015-01-13 13:18 | 13:34hrs Kitch Morris requested No.2 transformer at Bannaby be de-energised immediatey as a 330kV CVT is suspect. | Follow up | 13:34hrs Kitch Morris requested No.2 transformer at Bannaby be de-energised immediatey as a 330kV CVT is suspect. Unit found to have very black oil in the sight glass compared to other units which were clear. Equipment was taken out of service and oil sample taken from suspect CVT White Phase Trench- EGI TCHTEVP345-2 Results returned extremely high levels of Hydrogen, Methane, Carbon Monoxide, Ethylene, Ethane and Acetylene Unit replaced tested and commissioned There is ongoing investigation into these CVT's by Asset Performance | 500 |  | Forced | 2015
181282 |  |  | No.2 Reactor |  | 2015Q1 | BBY | RX | 2015-01-09 12:43 | 2015-01-13 13:18 |  |  |  | 33 |  |  | 2015
181283 |  |  | M5 Murray - Murray 1 330kV TL | X | 2015Q1 | MUR, MP1 | TL | 2015-01-15 09:20 | 2015-01-15 14:21 |  |  |  | 330 |  |  | 2015
181287 |  |  | 828 Mt Piper 132 - Portland tee BCSC 66kV Line |  | 2015Q1 | MPP | TL | 2015-01-09 14:43 | 2015-01-09 14:43 | Trip and successful auto reclose. | Follow up |  | 66 |  |  | 2015
181289 | LV/MECH Fail | CB | 828 Mt Piper 132 - Portland tee BCSC 66kV Line | S | 2015Q1 | MPP | TL | 2015-01-09 15:17 | 2015-01-09 21:46 | Customer indicates interruption of supply to 2 mines. Supply arranged via Endevour network via Kandos, CB had burnt out close coil, which eventuated into battery earth, probably caused by R/C after trip | Follow up | Customer indicates interruption of supply to 2 mines. Supply arranged via Endevour network via Kandos, CB had burnt out close coil, which eventuated into battery earth, probably caused by R/C after trip. Similar to the incident that occurred last year on 6th March 2014 on the same CB. | 66 | Extensive repair work carried out on CB clutch mechanism. |  | 2015
181295 | Relay | Prot | M13 Murray - Murray 2 330kV TL | Z | 2015Q1 | MUR, MP2 | TL | 2015-01-09 08:53 | 2015-01-11 17:36 | SHL Advised unit 13 was placed in-service and had synchronized on 330kV CB..M132A and loaded at 5 MW when the 330kV CB..M132B was closed and at the same time the Trip occurred. | Follow up | SHL Advised unit 13 was placed in-service and had synchronized on 330kV CB..M132A and loaded at 5 MW when the 330kV CB..M132B was closed and at the same time the Trip occurred. Only No.2 Protection operated. Further investigations found that the trip was caused by the No.2 Protection relay being faulty. | 330 |  | Fault | 2015
181296 |  |  | M13 Murray 2 A CB M132A |  | 2015Q1 | MUR | CB | 2015-01-09 08:53 | 2015-01-11 17:36 |  |  |  | 330 |  |  | 2015
181297 |  |  | M13 Murray 2 B CB M132B |  | 2015Q1 | MUR | CB | 2015-01-09 08:53 | 2015-01-11 17:36 |  |  |  | 330 |  |  | 2015
181299 |  |  | Station Transformer 1A (CB 5412) |  | 2015Q1 | MN1 | CB | 2015-01-09 22:46 | 2015-01-10 15:56 |  | Follow up |  | 330 |  |  | 2015
181300 | Lightning/Storm | TL | 99T Darlington Pt - Coleambally 132kV TL | Q | 2015Q1 | CLY, DNT | TL | 2015-01-10 05:06 | 2015-01-10 05:06 |  | 19/02/2015 13:13:00 ¦ Follow up ¦ Nil ¦ The line will be monitored through scheduled maintenance activities. | Successful trip and reclose. Storms in the area. A line inspection of towers 27-47 did not identify any defects. | 132 |  |  | 2015
181309 |  |  | 82K/1 Queanbeyan - Bungendore tee Sutton 66kV Line |  | 2015Q1 | QBY | TL | 2015-01-10 13:57 | 2015-01-10 13:57 |  | Follow up |  | 66 |  |  | 2015
181383 |  |  | 96Y Waratah West - Mayfield West 132kV Line | X | 2015Q1 | WRH | TL | 2015-02-02 09:24 | 2015-02-02 16:21 |  |  |  | 132 |  |  | 2015
181431 |  |  | L1 Lower Tumut - Tumut 3 330kV TL | X | 2015Q1 | LT1, TP3 | TL | 2015-01-18 06:30 | 2015-01-19 15:00 |  |  |  | 330 |  |  | 2015
181586 | Fire | Cap | No.2 Capacitor | E | 2015Q1 | KCR | CAP | 2015-01-14 10:15 | 2015-11-11 14:37 | Neutral Earthing reactor burned down. No2 Capaciotr will OOS for an extended period. | Follow up | At 10:02hrs No.2 Capacitor was reported by contractor there was a fire in the switchyard. After visual inspection via security camera, noted that No.2 capacitor reactor had caught on fire. No.2 Capacitor has been taken out of service at 10:08hrs. Fire Brigade and staff sent to site. Replacement reactor has been ordered and due to arrive in November 2015. Project not yet created for this replacement. | 330 | Work order No. 341314 was created on 24/02/2015 to investigate the condition of red and white phase reactors. Work order closed . | Forced | 2015
181754 |  |  | No.1 Capacitor | E | 2014Q2 | SYS | CAP | 2014-05-01 13:45 | 2015-07-07 14:23 |  |  |  | 132 |  | Forced | 2014
181755 |  |  | No.3 Transformer 330/132/11kV | E | 2014Q4 | BFD | TX | 2014-10-12 15:43 | 2014-12-14 16:08 |  |  |  | 330 |  | Forced | 2014
181772 | Unknown | TL | 99M Yass - Murrumburrah 132kV TL | Q | 2015Q1 | MRU, YSN | TL | 2015-01-19 05:06 | 2015-01-19 05:06 |  | 3/03/2015 14:08:00 ¦ Follow up ¦ Nil ¦ The line will be monitored through scheduled maintenance activities. | Successful trip and reclose. The fault is noted and will be investigated during the next scheduled aerial line inspection A line inspection from structure 229 - 263 did not identify any defects. | 132 |  |  | 2015
181819 | HV Equipment | Cap | No.6 Capacitor | B | 2015Q1 | SYW | CAP | 2015-02-11 14:49 | 2015-02-11 20:14 |  |  | Investigate and repair hot joints | 330 |  | Forced | 2015
181856 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q1 | CW2 | TL | 2015-01-19 17:04 | 2015-01-19 17:04 |  | Follow up |  | 66 |  |  | 2015
181857 | Lightning/Storm | TL | 9W7 Nambucca - Boambee South 132kV TL | Q | 2015Q1 | NAM, BOS | TL | 2015-01-19 17:59 | 2015-01-19 17:59 |  | Follow up | Successful trip and reclose. Storms in the area. | 132 |  |  | 2015
181858 | Lightning/Storm | TL | 9W3 Coffs Harbour - Raleigh 132kV TL | Q | 2015Q1 | COF, RAL | TL | 2015-01-19 17:59 | 2015-01-19 17:59 |  | Follow up | Successful trip and reclose. Storms in the area. | 132 |  |  | 2015
181859 |  |  | 893/1 Cowra - Grenfell 66kV Line |  | 2015Q1 | CW2 | TL | 2015-01-19 18:01 | 2015-01-19 18:01 |  | Follow up |  | 66 |  |  | 2015
181860 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q1 | CW2 | TL | 2015-01-19 22:13 | 2015-01-20 05:14 |  | Follow up |  | 66 |  |  | 2015
181861 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2015Q1 | BER | TL | 2015-01-19 22:14 | 2015-01-19 22:14 |  | Follow up |  | 66 |  |  | 2015
181862 | Lightning/Storm | TL | 9W2 Kempsey - Raleigh 132kV TL | Q | 2015Q1 | KS2, RAL | TL | 2015-01-20 00:29 | 2015-01-20 00:29 |  | Follow up | Successful trip and reclose. Storms in the area. | 132 |  |  | 2015
181874 |  |  | No.1 Transformer 132/33/11kV | X | 2015Q1 | MNY | TX | 2015-01-20 07:05 | 2015-01-20 14:58 |  |  |  | 132 |  |  | 2015
181886 | Lightning/Storm | TL | 964 Pt Macquarie - Taree Tee Herons Creek 132kV TL | C | 2015Q1 | PMQ, TRE | TL | 2015-01-20 09:10 | 2015-01-20 10:12 | Fault Thrower Closed at Herons Creek in EssE system after initial lightning strike which has caused the lockout to happen on reclose attempt | Follow up | Fault Thrower Closed at Herons Creek in EssE system after initial lightning strike which has caused the lockout to happen on reclose attempt. | 132 |  | Fault | 2015
181916 |  |  | 661 Armidale - Oaky PS 66kV Line |  | 2015Q1 | AR1 | TL | 2015-01-20 14:55 | 2015-01-20 14:55 | Trip and successful auto reclose | Follow up |  | 66 |  |  | 2015
181917 |  |  | 661 Armidale - Oaky PS 66kV Line |  | 2015Q1 | AR1 | TL | 2015-01-20 15:13 | 2015-01-20 22:36 |  | Follow up |  | 66 |  |  | 2015
181931 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2015Q1 | MRE | TL | 2015-01-20 17:10 | 2015-01-20 17:11 |  | Follow up |  | 66 |  |  | 2015
181932 |  |  | No.10 Yanco - Kamarah (No.10 Council) |  | 2015Q1 | YA2 | TL | 2015-01-20 21:02 | 2015-01-20 22:30 |  | Follow up |  | 33 |  |  | 2015
181933 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q1 | CW2 | TL | 2015-01-21 01:56 | 2015-01-21 01:56 | TAR on 891 Cowra to Young tee Wyangala tee Monteagle 66kV Feeder interrupted 8MW of generation, for time taken to synchronise and load generator. | Follow up |  | 66 |  |  | 2015
181975 | LV/MECH Fail | CB | No.1 Transformer 132/66kV | E | 2015Q1 | MPP | TX | 2015-01-21 13:36 | 2015-01-21 16:15 |  |  | Investigate #1 Tx CB4412 burnt out coil | 132 |  | Forced | 2015
181976 |  |  | No.2 Transformer 132/33/11kV | X | 2015Q1 | MNY | TX | 2015-01-21 08:02 | 2015-01-21 14:15 |  |  |  | 132 |  |  | 2015
181980 | Lightning/Storm | TL | 976/1 Canberra - Queanbeyan tee Spring Flat 132kV TL | Q | 2015Q1 | CA1, QBY, SFF | TL | 2015-01-21 18:40 | 2015-01-21 18:40 | SO/Essential Energy (Darren) advised that a Thunderstorm was rolling over the area at the time of trip. | 20/02/2015 07:51:00 ¦ Follow up ¦ Nil ¦ The line will be monitored through scheduled maintenance activities. | SO/Essential Energy (Darren) advised that a Thunderstorm was rolling over the area at the time of trip. A line inspection of structures 48-75 did not identify any defects. | 132 |  |  | 2015
182047 | Damaged Cable | Aux Tx | No.1 Transformer 132/33/11kV | B | 2015Q1 | YA2 | TX | 2015-01-22 12:42 | 2015-01-22 14:16 |  |  | Repair insulation on No.1 Auxiliary Transformer 11kV cable | 132 |  | Forced | 2015
182076 |  |  | 99F Uranqunity - Yanco 132kV TL | B | 2015Q1 | YA2, URQ | TL | 2015-01-23 06:28 | 2015-01-23 14:04 |  |  |  | 132 |  | Forced | 2015
182077 | Animal/Bird | CB | 722 Moree - Moree 66 66kV Line | Q | 2015Q1 | MRE | TL | 2015-01-22 19:02 | 2015-01-22 20:55 | SO/Essential Energy (Peter) advised that feeder remained closed at their end and confirmed it has an I/Trip installed on No.1 Protection. Confirmed No Load showing on this feeder and about 104 Amps on 721 Moree 66 Feeder. NCM advised. TG Staff on arrival found 2 frogs in the CB 7222 Control Cabinet which were removed and all switchgear otherwise looked OK. 722 Moree 66kV Feeder returned to service. | Follow up | TARTLO operation on the line. TG Staff on arrival found 2 frogs in the CB 7222 Control Cabinet which were removed and all switchgear otherwise looked OK. 722 Moree 66kV Feeder returned to service. | 66 |  |  | 2015
182158 |  |  | 80U Beryl - Ulan 66kV Line |  | 2015Q1 | BER | TL | 2015-01-23 16:48 | 2015-01-23 16:48 | Successful trip and auto reclose during storm activity. | Follow up |  | 66 |  |  | 2015
182159 |  |  | 662 Armidale - Walcha 66kV Line |  | 2015Q1 | AR1 | TL | 2015-01-23 20:14 | 2015-01-23 20:14 | No storms apparent on Indji. | Follow up |  | 66 |  |  | 2015
182166 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q1 | CW2 | TL | 2015-01-24 12:14 | 2015-01-24 12:14 | Trip and auto reclose during storm activity. | Follow up |  | 66 |  |  | 2015
182167 |  |  | 856 Wallerawang 132 - Oberon Tee Lillyvale 66kV Line |  | 2015Q1 | WWS | TL | 2015-01-24 13:54 | 2015-01-24 13:54 | Trip and auto reclose during storm activity. | Follow up |  | 66 |  |  | 2015
182168 | Lightning/Storm | TL | O1 Upper Tumut - Canberra 330kV TL | Q | 2015Q1 | CA1, UT1 | TL | 2015-01-24 14:46 | 2015-01-24 14:46 | Protection details required. CA1 CB O12B Closed by SCADA. | 30/03/2015 15:21:00 ¦ Follow up ¦ Nil ¦ The line will be monitored through scheduled maintenance activities. | Successful trip and reclose. Storms in the area. CA1 CB O12B Closed by SCADA. A line inspection of structures and spans from 1 to 56 did not identify any defects. | 330 |  |  | 2015
182169 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q1 | CW2 | TL | 2015-01-24 14:41 | 2015-01-24 14:41 | Trip and auto reclose during storm activity. Second TAR operation - previous 1214. | Follow up |  | 66 |  |  | 2015
182170 |  |  | 893/5 Forbes - Payten's Bridge 66kV Line |  | 2015Q1 | FB2 | TL | 2015-01-24 14:54 | 2015-01-24 14:54 | Trip and auto reclose during storm activity. | Follow up |  | 66 |  |  | 2015
182171 | Lightning/Storm | TL | O1 Upper Tumut - Canberra 330kV TL | Q | 2015Q1 | CA1, UT1 | TL | 2015-01-24 14:55 | 2015-01-24 14:55 | Protection details required. CA1 CB O12B Closed by SCADA. | 30/03/2015 15:21:00 ¦ Follow up ¦ Nil ¦ The line will be monitored through scheduled maintenance activities. | Successful trip and reclose. Storms in the area. CA1 CB O12B Closed by SCADA. A line inspection of structures and spans from 1 to 56 did not identify any defects. | 330 |  |  | 2015
182172 |  |  | 893/5 Forbes - Payten's Bridge 66kV Line |  | 2015Q1 | FB2 | TL | 2015-01-24 15:08 | 2015-01-24 15:08 | Trip and auto reclose during storm activity. Second TAR - Previous 1441. | Follow up |  | 66 |  |  | 2015
182173 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q1 | CW2 | TL | 2015-01-24 15:44 | 2015-01-24 15:44 | Trip and auto reclose during storm activity. Third TAR operation - previous 1441. | Follow up |  | 66 |  |  | 2015
182174 | Lightning/Storm | TL | 998 Forbes - Cowra 132kV TL | Z | 2015Q1 | CW2, FB2 | TL | 2015-01-24 17:02 | 2015-01-25 12:21 | Trip, auto reclose and lock out during storm activity. Staff on route to site. On Call Engineer advised and arranging line patrol. | 2/02/2015 09:05:00 ¦ Follow up ¦ Nil ¦ Nil | At 17:03hrs 998 Forbes to Cowra 132 kV T/L Tripped and Reclosed, Tripped and Locked out. 999 Yass to Cowra 132kV T/L placed in-service as a result. The distance to fault indicated approximately 67km from Forbes S/S and 30km from Cowra S/S. The failure of the insulator was discovered at 7am on 25/01/15. The cause of the failure was attributed to a direct lightning strike on the B phase insulator. All three insulators were replaced and line was returned to service at 13:00 on Sunday the 25/01/15. | 132 |  | Fault | 2015
182175 |  |  | 82G Queanbeyan - Captains Flat 66kV Line |  | 2015Q1 | QBY | TL | 2015-01-24 17:41 | 2015-01-24 17:41 |  | Follow up |  | 66 |  |  | 2015
182176 |  |  | 82K/1 Queanbeyan - Bungendore tee Sutton 66kV Line |  | 2015Q1 | QBY | TL | 2015-01-24 17:21 | 2015-01-24 18:20 | Essential Energy sectionalised, line energised OK. | Follow up |  | 66 |  |  | 2015
182177 | Lightning/Storm | TL | 32 Sydney West - Bayswater 330kV TL | Z | 2015Q1 | BAY, SYW | TL | 2015-01-24 20:45 | 2015-01-25 15:32 | Large storm cell observed on Indji at time of tripping. TL still out of service pending patrol. | 30/01/2015 11:43:00 ¦ Follow up ¦ Nil. ¦ Nil. | TARTLO operation during storms. On Sunday 25/01/2015, a patrol was carried out from Structures 20 to 48 on 32TL and identified failed insulator on structure 31 on 32TL. It appeared that the destructive energy of the lightning strike itself smashed the porcelain of the 18th disc, causing the insulator string to fail. The failed insulator was replaced and 32TL was returned to service at 16:32hrs on Sunday 25/01/2015. | 330 |  | Fault | 2015
182178 | Relay Setting | Prot | 31 Regentville - Bayswater 330kV TL | Q | 2015Q1 | BAY, RGV | TL | 2015-01-24 20:45 | 2015-01-24 20:45 | No CB operations at Bayswater. 32 TL TARTLO at same time. | Follow up | Maloperation of No.2 Protection directional earth fault trip functionality, caused a trip of Line 31 at the Regentville end only, followed by a successful reclose. This occurred simultaneously with a TARTLO operation on line 32. | 330 | Investigative testing of 31 Bayswater No2 Prot at Regentville indicated correct relay operation per standard DEFC test plan. Injections using test values derived from the initial fault records were performed however the through-fault operation could not be replicated. It was noted however that a DEF I/T receive signal from Bayswater would be echoed if no forward or reverse zone 3 was detected at Regentville. It is thought that this may be a form of internal weak-infeed logic. As tests were inconclusive Prot Design requested that the DEFC scheme on No2 Prot be made non-auto via isolation of the associated DEF I/T send & receive links. DEFC is available on the No1 Prot & is not required to be duplicated. |  | 2015
182179 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2015Q1 | MRE | TL | 2015-01-25 04:51 | 2015-01-25 04:51 |  | Follow up |  | 66 |  |  | 2015
182180 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2015Q1 | GRF | TL | 2015-01-25 04:55 | 2015-01-25 04:55 |  | Follow up |  | 33 |  |  | 2015
182181 | Unknown | TL | 999 Yass - Cowra 132kV TL | Q | 2015Q1 | CW2, YSN | TL | 2015-01-25 05:12 | 2015-01-25 05:12 |  | Follow up | Successful trip and reclose. | 132 |  |  | 2015
182196 |  |  | 862/1 Taree - OCC Kew tee Johns River 66kV Line |  | 2015Q1 | TRE | TL | 2015-01-26 08:25 | 2015-01-26 08:25 |  | Follow up |  | 66 |  |  | 2015
182201 | HV Equipment | TL | U7 Upper Tumut - Tumut 2 330kV TL | Z | 2015Q1 | UT1 | TL | 2015-01-26 06:57 | 2015-02-03 18:47 | U7 T/L has tripped whilst trying to run up # 8 unit, however CB U72 was open at UTSS. | 20/02/2015 07:55:00 ¦ Follow up ¦ Potential for additional dead ends in the Upper group lines to have similar failure mechanisms ¦ Review remaining dead ends on upper group lines for potential testing and/or replacement works. | U7 T/L has tripped whilst trying to run up # 8 unit. It appears the cause is due to a mid-span joint failure in the line. The failed dead end was replaced. 11 additional dead ends on the U7 line were tested with Dy-Check for external cracks. 6 of the tested dead ends had external cracks and were also replaced in this outage. The line was returned to service on 3 February 2015 at 19:47 | 330 |  | Fault | 2015
182202 |  |  | 877 Gunnedah - Keepit PS 66kV Line |  | 2015Q1 | GN2 | TL | 2015-01-26 15:26 | 2015-01-26 15:26 |  | Follow up |  | 66 |  |  | 2015
182205 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2015Q1 | MRE | TL | 2015-01-26 17:24 | 2015-01-26 17:24 |  | Follow up |  | 66 |  |  | 2015
182206 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q1 | CW2 | TL | 2015-01-26 19:37 | 2015-01-26 19:37 |  | Follow up |  | 66 |  |  | 2015
182212 | Lightning/Storm | TL | 944 Orange North - Wallerawang 132kV TL | Q | 2015Q1 | ONO, WWS | TL | 2015-01-27 08:00 | 2015-01-27 08:00 | Trip and Successfull reclose. | 26/02/2015 09:57:00 ¦ Follow up ¦ Nil ¦ Nil | Trip and Successful reclose. Storms in the area. An after fault patrol was undertaken by Mains Orange staff. The trip was 35.83km from Orange North Substaton therefore the patrol was completed on structures 261 to 271. The patrol found no defects causing the trip. | 132 |  |  | 2015
182214 |  |  | 851 Beryl - Mudgee tee Gulgong 66kV Line |  | 2015Q1 | BER | TL | 2015-01-27 10:28 | 2015-01-27 10:28 | Trip and successfull auto-reclose | Follow up |  | 66 |  |  | 2015
182229 |  |  | 97L Guthega - Jindabyne Pumps 132kV TL | X | 2015Q1 | GTH, JDP | TL | 2015-02-12 07:10 | 2015-02-12 16:33 |  |  |  | 132 |  |  | 2015
182232 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2015Q1 | MRE | TL | 2015-01-27 15:07 | 2015-01-27 15:07 | Trip and successfull auto reclose | Follow up |  | 66 |  |  | 2015
182233 | Unknown | Cont | 723 Moree - Wenna tee Wathagar 66kV Line | Q | 2015Q1 | MRE | TL | 2015-01-27 15:42 | 2015-01-27 16:43 |  | Follow up | Trip, with no indication of attempt for reclose at Moree. | 66 | 723 had a TARTLO later in the day at 18:24 as per FEOR 84. Therefore AR works correctly |  | 2015
182234 |  |  | 2 Upper Tumut - Yass 330kV TL | B | 2015Q1 | UT1, YSN | TL | 2015-01-28 08:05 | 2015-01-28 14:42 |  |  |  | 330 |  | Forced | 2015
182235 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2015Q1 | MRE | TL | 2015-01-27 17:24 | 2015-01-27 18:05 |  | Follow up |  | 66 |  |  | 2015
182236 |  |  | 9N9 Waratah West - Broadmeadow tee Waratah 132kV Line |  | 2015Q1 | WRH | TL | 2015-01-27 22:46 | 2015-01-28 09:05 | Ausgrid requested I & E due to low oil level alarms on cable, however when tech inspected cable alarms, they were found to be not genuine. | Follow up |  | 132 |  |  | 2015
182237 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q1 | CW2 | TL | 2015-01-28 03:06 | 2015-01-28 03:06 |  | Follow up |  | 66 |  |  | 2015
182247 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q1 | CW2 | TL | 2015-01-28 06:24 | 2015-01-28 06:24 |  | Follow up |  | 66 |  |  | 2015
182324 |  |  | 2 Upper Tumut - Yass 330kV TL | B | 2015Q1 | UT1, YSN | TL | 2015-01-29 09:18 | 2015-01-29 15:23 |  |  |  | 330 |  | Forced | 2015
182328 | HV Equipment | CT | No.1 Capacitor | B | 2015Q1 | NEW | CAP | 2015-01-30 06:34 | 2015-01-30 11:01 |  |  | Investigate CT Low SF6 Alarm and moisture ingress into Secondary Boxes. | 132 |  | Forced | 2015
182414 | Staff Error | Proc | 261 Beaconsfield West - Clovelly tee Zetland 132kV Cable | S | 2015Q1 | BFD | TL | 2015-01-30 07:38 | 2015-01-30 08:33 | 42 MW of customer load lost for trip of 261 Beaconsfield to Clovelly tee Zetland 132 kV U/C all load was restored in the Ausgrid network at 07:56 hrs as advised by Ausgrid. information from SCADA trends on the Inservice 260 Beaconsfield to Clovelly tee Zetland 132 kV U/C first load block restored approx 10 MW at 07:45hrs second load block restored approx 13 MW at 07:50hrs final load block restored at 07:56hrs no SCADA trends available for final load block. | Follow up | Line 261 tripped while staff were undertaking in service protection checks. 42 MW of customer load lost for trip of 261 Beaconsfield to Clovelly tee Zetland 132 kV U/C. All load was restored in the Ausgrid network at 07:56 hrs as advised by Ausgrid. | 132 | When restoring the CB Trip fuse for 261 on the BBP panel, vibration caused by pushing in the fuse operated the BBP Differential Relay. This in turn operated the two multi trip relays, causing CB 4012B and 2612 to trip (these where the only two services that had been restored . |  | 2015
182417 | HV Equipment | Cap | No.1 Capacitor | B | 2015Q1 | TA1 | CAP | 2015-01-30 12:05 | 2015-01-30 13:29 |  |  | NO 1 CAP REPAIR HOT JOINTS | 330 |  | Forced | 2015
182495 |  |  | U5 Upper Tumut - Tumut 2 330kV TL | B | 2015Q1 | UT1 | TL | 2015-02-01 14:07 | 2015-02-02 21:25 |  |  |  | 330 |  | Forced | 2015
182496 | HV Equipment | CB | 9J2 Sydney West - Blacktown 132kV Line | Q | 2015Q1 | SYW | TL | 2015-01-31 16:19 | 2015-01-31 16:55 |  |  | SF6 Topup | 132 |  |  | 2015
182540 |  |  | M1 Murray - Murray 1 330kV TL | X | 2015Q1 | MUR, MP1 | TL | 2015-02-01 10:09 | 2015-02-01 13:41 |  |  |  | 330 |  |  | 2015
182542 |  |  | 97L Guthega - Jindabyne Pumps 132kV TL | X | 2015Q1 | GTH, JDP | TL | 2015-02-01 09:33 | 2015-02-01 12:56 |  |  |  | 132 |  |  | 2015
182544 | HV Equipment | CB | 828 Mt Piper 132 - Portland tee BCSC 66kV Line | Q | 2015Q1 | MPP | TL | 2015-02-01 22:17 | 2015-02-01 23:18 | All load restored (2 MW) after 9 minutes within Endeavour Energy network. CB failed to reclose due to known fault. CB left open pending repairs (planned outage today), at Endeavour Energy request. | Follow up | CB failed to reclose due to known fault. CB left open pending repairs (planned outage today), at Endeavour Energy request. | 66 | Extensive repair work carried out on CB clutch mechanism. |  | 2015
182585 | Relay | Prot | No.2 Transformer 132/66/11kV | B | 2015Q1 | QBY | TX | 2015-02-03 07:25 | 2015-02-03 10:49 |  |  | Replace Tripping module of No1 Prot relay. | 132 |  | Forced | 2015
182592 |  |  | 862/1 Taree - OCC Kew tee Johns River 66kV Line |  | 2015Q1 | TRE | TL | 2015-02-03 03:56 | 2015-02-03 03:56 | No sign of storms on Indji. | Follow up |  | 66 |  |  | 2015
182606 |  |  | 945 Wellington - Molong tee Well'n Town 132kV TL | X | 2015Q1 | MOL, WL1 | TL | 2015-02-24 07:22 | 2015-02-24 15:14 |  |  |  | 132 |  |  | 2015
182850 | HV Equipment | CB | No.3 Capacitor | B | 2015Q1 | SYN | CAP | 2015-02-04 10:39 | 2015-02-04 11:22 |  |  | Top Up Low SF6 | 132 |  | Forced | 2015
183023 | Secondary Equipment | Cont | 87 Coffs Harbour B CB 872B | B | 2015Q1 | AR1 | CB | 2015-02-06 07:29 | 2015-02-06 15:25 |  |  | RTU Replacement. | 330 |  | Forced | 2015
183024 | Secondary Equipment | Cont | No.2 330kV Reactor | B | 2015Q1 | AR1 | RX | 2015-02-06 07:16 | 2015-02-06 15:39 |  |  | RTU Replacement. | 330 |  | Forced | 2015
183112 | LV/MECH Fail | CB | X2 Buronga No.2 Reactor | E | 2015Q1 | BKH | RX | 2015-02-28 11:29 | 2015-03-09 18:01 |  |  | Burnt trip coil discovered during planned ouatge. | 220 |  | Forced | 2015
183173 | HV Equipment | CB | 78 Sydney South A CB 782A | Q | 2015Q1 | ING | CB | 2015-02-08 10:24 | 2015-02-08 12:00 |  |  | SF6 topup. | 330 |  |  | 2015
183174 |  |  | 896 Forbes - West Jemalong 66kV Line |  | 2015Q1 | FB2 | TL | 2015-02-08 12:07 | 2015-02-08 14:09 |  | Follow up |  | 66 |  |  | 2015
183175 | Tree/Ground | TL | 6 Canberra - Capital Wind Farm 330kV TL | Q | 2015Q1 | CA1, CWF | TL | 2015-02-08 13:08 | 2015-02-08 13:08 | Advised Essential Energy field staff reported 6 Canberra to Capital Wind Farm 330 kV T/L has flashed over onto near by trees which had started a small grass fire which self extinguished | Follow up ¦ Nil ¦ The current vegetation management schedule for these trees will be reviewed. | Advised Essential Energy field staff reported 6 Canberra to Capital Wind Farm 330 kV T/L has flashed over onto near by trees which had started a small grass fire which self extinguished A line patrol identified trees underneath span 125-126 within the minimum clearance distance of the conductor with burn marks from the fire at the base of the tree. The identified trees have been trimmed back to around 2m tall. No conductor or asset damage was observed. | 330 | Update 30/09/2015: Trees trimmed 09/02/2015. |  | 2015
183176 |  |  | 82B Queanbeyan - High St 66kV Line |  | 2015Q1 | QBY | TL | 2015-02-09 00:25 | 2015-02-09 00:25 |  | Follow up |  | 66 |  |  | 2015
183220 | Secondary Equipment | Prot | No.2 Transformer 330/132/16kV | E | 2015Q1 | SE1 | TX | 2015-02-10 02:26 | 2015-02-10 13:50 |  |  | Replace C.T. Module in transformer protection relay | 330 | (WO 340813) 330kV Analogue/Digital Module alarm raised per Irregularity Report # 13638. Alarm code on relay display indicated: MOD FAILURE 03: CONTACT FACTORY (F8N). Note, this alarm had been raised previously during initial pre-commissioning checks 6/5/2014 (refer W/O 324029). Relay testing whilst in alarmed state indicated correct analogue values via the Ernavista metering page however diff prot remained completely non-auto. Application of a shunt trip (eg. main tank buchholz) resulted in relay operation AND CBF tripping of the LV B bus BBP. At this point the relay locked-up & could not be reset. Cycling the power supply resulted in resetting of the alarm. Subsequent testing indicated correct relay operation. As a precaution the original Analogue Module 8N (serial # A8NC12004257) was replaced with Analogue Module 8N from SYW No5 TX prot located in 132kV SSB (serial # A8NC13003015). Relay testing with replacement Analogue Module complete & correct. | Forced | 2015
183317 |  |  | 863 Cowra - Canowindra 66kV Line |  | 2015Q1 | CW2 | TL | 2015-02-10 17:50 | 2015-02-10 17:50 |  | Follow up |  | 66 |  |  | 2015
183396 | Lightning/Storm | TL | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2015Q1 | GTH, MUR, GHI | TL | 2015-02-11 20:09 | 2015-02-11 21:01 |  | Follow up ¦ Nil ¦ Replace insulator at structure 112 during next outage as per existing defect. | Thunderstorms in the area. | 132 |  | Fault | 2015
183397 |  |  | 97G/3 Geehi Tee CB 97G2 |  | 2015Q1 | GTH | CB | 2015-02-11 20:17 | 2015-02-11 21:01 |  |  |  | 132 |  |  | 2015
183398 |  |  | 97G/1 Geehi Tee CB 97G2 |  | 2015Q1 | MUR | CB | 2015-02-11 20:17 | 2015-02-11 21:01 |  |  |  | 132 |  |  | 2015
183399 | Lightning/Storm | TL | 99A Uranquinty - Finley 132kV TL | Q | 2015Q1 | FNY, URQ | TL | 2015-02-11 20:20 | 2015-02-11 20:20 |  | Follow up ¦ Nil ¦ Nil | Successful trip and reclose. Storms in the area. | 132 |  |  | 2015
183400 |  |  | 99N Hillston CB 99N2 |  | 2015Q1 | DNT | CB | 2015-02-11 17:56 | 2015-02-12 18:01 |  | Follow up |  | 132 |  |  | 2015
183401 |  |  | 83F Wagga North - Junee 66kV Line |  | 2015Q1 | WGN | TL | 2015-02-11 22:36 | 2015-02-11 22:36 |  | Follow up |  | 66 |  |  | 2015
183402 |  |  | 7R2 Kempsey - North St tee Smithtown 33kV Line |  | 2015Q1 | KS2 | TL | 2015-02-11 22:39 | 2015-02-11 22:39 |  | Follow up |  | 33 |  |  | 2015
183403 |  |  | 850 Tumut - Talbingo tee Jounama Dam 66kV Line |  | 2015Q1 | TU2 | TL | 2015-02-11 22:57 | 2015-02-11 22:57 |  | Follow up |  | 66 |  |  | 2015
183458 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q1 | CW2 | TL | 2015-02-12 11:56 | 2015-02-12 11:56 | Trip and successful auto reclose | Follow up |  | 66 |  |  | 2015
183459 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q1 | CW2 | TL | 2015-02-12 12:07 | 2015-02-12 12:07 | Trip and successful auto reclose | Follow up |  | 66 |  |  | 2015
183468 | HV Equipment | CB | 238 Regentville - Penrith 132kV Line | Q | 2015Q1 | RGV | TL | 2015-02-12 15:59 | 2015-02-12 16:57 |  |  | SF6 topup | 132 |  |  | 2015
183477 |  |  | 850 Tumut - Talbingo tee Jounama Dam 66kV Line |  | 2015Q1 | TU2 | TL | 2015-02-12 14:42 | 2015-02-12 14:42 |  | Follow up |  | 66 |  |  | 2015
183478 |  |  | 848 Tumut - Tumbarumba tee Batlow tee Adelong 66kV Line |  | 2015Q1 | TU2 | TL | 2015-02-12 15:04 | 2015-02-12 15:04 |  | Follow up |  | 66 |  |  | 2015
183479 |  |  | 898 Parkes - Trundle 66kV Line |  | 2015Q1 | PKS | TL | 2015-02-12 15:27 | 2015-02-12 15:27 | Trip and successful auto reclose | Follow up |  | 66 |  |  | 2015
183480 |  |  | 850 Tumut - Talbingo tee Jounama Dam 66kV Line |  | 2015Q1 | TU2 | TL | 2015-02-12 14:44 | 2015-02-12 14:44 |  | Follow up |  | 66 |  |  | 2015
183481 |  |  | 850 Tumut - Talbingo tee Jounama Dam 66kV Line |  | 2015Q1 | TU2 | TL | 2015-02-12 14:54 | 2015-02-12 14:54 |  | Follow up |  | 66 |  |  | 2015
183482 |  |  | 940 Wallerawang 132 - Warimoo tee North Katoomba 132kV Line |  | 2015Q1 | WWS | TL | 2015-02-12 19:12 | 2015-02-12 19:12 |  | Follow up |  | 132 |  |  | 2015
183483 |  |  | 941 Wallerawang 132 - Lawson tee North Katoomba 132kV Line |  | 2015Q1 | WWS | TL | 2015-02-12 12:12 | 2015-02-12 12:12 |  | Follow up |  | 132 |  |  | 2015
183484 |  |  | 890 Murrumburrah - Young 66kV Line |  | 2015Q1 | MRU | TL | 2015-02-12 20:40 | 2015-02-12 20:40 |  | Follow up |  | 66 |  |  | 2015
183548 |  |  | 940 Wallerawang 132 - Warimoo tee North Katoomba 132kV Line |  | 2015Q1 | WWS | TL | 2015-02-13 13:16 | 2015-02-13 13:16 |  | Follow up |  | 132 |  |  | 2015
183573 |  |  | 850 Tumut - Talbingo tee Jounama Dam 66kV Line |  | 2015Q1 | TU2 | TL | 2015-02-13 14:50 | 2015-02-13 14:50 |  | Follow up |  | 66 |  |  | 2015
183574 |  |  | 898 Parkes - Trundle 66kV Line |  | 2015Q1 | PKS | TL | 2015-02-13 14:59 | 2015-02-13 14:59 |  | Follow up |  | 66 |  |  | 2015
183575 |  |  | 848 Tumut - Tumbarumba tee Batlow tee Adelong 66kV Line |  | 2015Q1 | TU2 | TL | 2015-02-13 15:58 | 2015-02-13 18:07 |  | Follow up |  | 66 |  |  | 2015
183597 |  |  | 823 Wallerawang 132 - Portland 66kV Line |  | 2015Q1 | WWS | TL | 2015-02-14 07:38 | 2015-02-14 07:38 | Large bird found on line side of line disconnector. Burn marks found on arcing horn. DTF info 10.8m | Follow up |  | 66 |  |  | 2015
183598 | HV Equipment | TL | 99D Darlington Pt - Yanco 132kV TL | Z | 2015Q1 | DNT, YA2 | TL | 2015-02-14 15:13 | 2015-02-15 18:31 | Pole required replacing | Follow up ¦ Nil ¦ 1. Identify and reassess wood pole defects on H-Frame 132kV wood pole lines in termite prone areas of Southern Region. 2. Review 99D UGI periodic maintenance regime. 3. A request has been approved by the asset manager to push 336 grillage inspections into the15/16 FY allowing a focus on UGI of wood pole structures. | A fault patrol of structures 15-85 identified that both poles of structure 59 had snapped off at ground level and were lying on the ground. On 15 February structure 59 was replaced using steel poles and returned to service The poles appear to have failed due a combination of high wind and termite damage at the base of the poles. | 132 | Structure replaced 15/02/2015. | Fault | 2015
183602 | Unknown | TX | No.1 Transformer 132/11/11kV | Q | 2015Q1 | ANM | TX | 2015-02-14 14:46 | 2015-02-15 00:40 |  | 27/05/2015 11:54:00 ¦ Follow up | At 14:46hrs a CB Trip alarm was received from ANM. Staff were called out ot investigate and advised that No 1 Transformer had tripped. Investigations are continuing. Nil interruption. Upon investigation of trip conditions it was determined that the cause of the trip was the Tapchanger Bucholz relay not the overpressure relay which alarms only. The Tx was isolated and earthed and investigation of the Bucholz relay found that it was half full of water due to deteriorated gasket on the terminal cover and seals on the fastners perished. The terminal box was dried out gasket replaced, fibre washers placed under the fastners and function of wiring tested before returning to service. A weather cover has been produced to fit over the relay which is being fitted today 27/5/15 in conjunction with the following protection work: Verify the accuracy of the new Preliminary RTI for the No1 Transformer and operating the devices to verify the correct identification and functions as they apply to the protective devices and protection relay. Drawings and labeling will be updated to reflect the correct operation. | 132 | Work order No. 343119 was created on 16/03/2015 to fix this issue. A cover to prevent the driving rain from soaking into the terminal box on the Bulcholz was constructed on No 1 Tx. Work order closed. |  | 2015
183603 | Unknown | TL | 998 Forbes - Cowra 132kV TL | Q | 2015Q1 | CW2, FB2 | TL | 2015-02-15 01:07 | 2015-02-15 01:07 |  | 10/03/2015 11:36:00 ¦ Follow up ¦ Nil ¦ Nil | At 01:07hrs 998 Forbes to Cowra 132 kV T/L tripped and auto reclosed. Cause unknown, weather fine. A fault patrol was organised for the 20/2/2015 for 1.5km either side of the specified distance to fault. No defects were found. | 132 |  |  | 2015
183612 |  |  | M1 Murray - Murray 1 330kV TL | X | 2015Q1 | MUR, MP1 | TL | 2015-02-15 08:17 | 2015-02-15 12:25 |  |  |  | 330 |  |  | 2015
183614 |  |  | 97L Guthega - Jindabyne Pumps 132kV TL | X | 2015Q1 | GTH, JDP | TL | 2015-02-15 08:18 | 2015-02-15 11:58 |  |  |  | 132 |  |  | 2015
183615 |  |  | 857 Wallerawang 132 - Lithgow 66kV Line |  | 2015Q1 | WWS | TL | 2015-02-15 15:58 | 2015-02-16 09:35 |  | Follow up |  | 66 |  |  | 2015
183666 | Condition Monitor | TX | No.4 Transformer 330/132/16kV | E | 2015Q1 | SE1 | TX | 2015-02-16 17:29 | 2015-02-17 13:30 | Condition Monitor L1 alarm received. | 10/03/2015 08:47:00 ¦ Follow up ¦ Nil ¦ Nil | Condition Monitor L1 alarm received. The bushing monitors hardware configuration was rectified and No.4 Transformer was then returned to service shortly after. | 330 |  | Forced | 2015
183667 | LV/MECH Fail | CB | 79P Griffith - Goolgowi 33kV Line | Q | 2015Q1 | GRF | TL | 2015-02-16 18:22 | 2015-02-18 15:36 | Delay in returning 79P Goolgowi to service due to inability to close C.B. 79P2 at Griffith via SCADA or the site HMI. | Follow up | At 18:31hrs 79P Griffith to Goolgowi 33kV Feeder & 79M Griffith to Hanwood 33kV Feeder both Tripped, Reclosed, Tripped and Locked Out. Storms in the area. Essential Energy notified. Approximately 11MW lost on 79M & 5MW lost on 79P. Delay in returning 79P Goolgowi to service due to inability to close C.B. 79P2 at Griffith via SCADA or the site HMI. Received advice that CB 79P2 Mech not latching fully. Lubricated/ adjusted and CB 79P2 ok to be RTS. CB 79P2 Closed ok subsequently. | 33 |  |  | 2015
183668 |  |  | 79M Griffith - Hanwood 33kV Line |  | 2015Q1 | GRF | TL | 2015-02-16 18:22 | 2015-02-17 18:43 |  | Follow up |  | 33 |  |  | 2015
183757 |  |  | 890 Murrumburrah - Young 66kV Line |  | 2015Q1 | MRU | TL | 2015-02-17 14:21 | 2015-02-17 14:22 | Storms in area | Follow up |  | 66 |  |  | 2015
183760 |  |  | 836 Murrumburrah - Cootamundra 66kV Line |  | 2015Q1 | MRU | TL | 2015-02-17 15:26 | 2015-02-17 16:25 | Advised storms in area SCADA trend shows approx 8MW load interrupted. No Auto changeover scheme or SCADA at Cootamundra. | Follow up |  | 66 |  |  | 2015
183817 |  |  | 863 Ingleburn - Minto 66kV Line |  | 2015Q1 | ING | TL | 2015-02-18 12:18 | 2015-02-18 15:48 | Returned to service on advice from customer. Fault in their system. | Follow up |  | 66 |  |  | 2015
183821 |  |  | L5 Lower Tumut - Tumut 3 330kV TL | X | 2015Q1 | LT1, TP3 | TL | 2015-03-08 08:19 | 2015-03-08 14:40 |  |  |  | 330 |  |  | 2015
183822 |  |  | 64 Lower Tumut - Upper Tumut 330kV TL | X | 2015Q1 | LT1, UT1 | TL | 2015-03-08 08:19 | 2015-03-08 15:49 |  |  |  | 330 |  |  | 2015
183827 |  |  | U3 Upper Tumut - Tumut 1 330kV TL | X | 2015Q1 | UT1 | TL | 2015-03-08 07:57 | 2015-03-08 15:47 |  |  |  | 330 |  |  | 2015
183828 |  |  | U5 Upper Tumut - Tumut 2 330kV TL | X | 2015Q1 | UT1 | TL | 2015-03-08 07:57 | 2015-03-08 15:47 |  |  |  | 330 |  |  | 2015
183847 |  |  | U3 Upper Tumut - Tumut 1 330kV TL | X | 2015Q1 | UT1 | TL | 2015-03-21 07:42 | 2015-03-21 14:01 |  |  |  | 330 |  |  | 2015
183848 |  |  | L5 Lower Tumut - Tumut 3 330kV TL | X | 2015Q1 | LT1, TP3 | TL | 2015-03-21 07:47 | 2015-03-21 14:01 |  |  |  | 330 |  |  | 2015
183849 |  |  | 64 Lower Tumut - Upper Tumut 330kV TL | X | 2015Q1 | LT1, UT1 | TL | 2015-03-21 07:42 | 2015-03-21 14:01 |  |  |  | 330 |  |  | 2015
183851 |  |  | U5 Upper Tumut - Tumut 2 330kV TL | X | 2015Q1 | UT1 | TL | 2015-03-21 07:42 | 2015-03-21 14:01 |  |  |  | 330 |  |  | 2015
183853 | Relay | Prot | 850 Tumut - Talbingo tee Jounama Dam 66kV Line | Q | 2015Q1 | TU2 | TL | 2015-02-19 05:22 | 2015-02-19 17:16 | SCADA Alarms; 8502 CB Opened 8502 CB A/R Operate FL Alarm. 850 Prot2 Operated Confirmed with staff onsite Auto Reclose did not operate. | Follow up | 850 Tumut to Talbingo tee Jounama Dam 66kV Feeder Tripped, cause unknown & no storm activity. Auto reclose failed. | 66 | (WO 346864) Relay to be replaced 17 June Faulty Current input module |  | 2015
183916 |  |  | 850 Tumut - Talbingo tee Jounama Dam 66kV Line |  | 2015Q1 | TU2 | TL | 2015-02-20 05:24 | 2015-02-20 05:24 |  | Follow up |  | 66 |  |  | 2015
183944 |  |  | 67 Murray - Dederang 330kV Line | X | 2015Q1 | MUR | TL | 2015-03-31 06:22 | 2015-03-31 15:29 |  |  |  | 330 |  |  | 2015
183945 |  |  | 67 Murray - Dederang 330kV Line | X | 2015Q2 | MUR | TL | 2015-04-01 06:10 | 2015-04-01 14:31 |  |  |  | 330 |  |  | 2015
183982 |  |  | No.1 Taree - Council Bootawa 33kV Line |  | 2015Q1 | TRE | TL | 2015-02-21 15:24 | 2015-02-21 22:08 |  | Follow up |  | 33 |  |  | 2015
183992 |  |  | Broken Hill - South 22kV Line |  | 2015Q1 | BKH | TL | 2015-02-22 07:48 | 2015-02-22 09:22 | Customer advises trip caused by bird. | Follow up |  | 22 |  |  | 2015
184048 |  |  | 83C Wagga North - Oura 66kV Line |  | 2015Q1 | WGN | TL | 2015-02-23 19:29 | 2015-02-23 19:29 | Fault recorder details Fault duration 877.4ms Relay trip time 79.91ms IA 20.32Amps IB 1.678kA IC 30.1Amps VBN 26.48kV VCN 37.5kV VAN 38.28kV Fault Zone2 | Follow up |  | 66 |  |  | 2015
184049 |  |  | 79C Griffith - Darlington Point 33kV Line |  | 2015Q1 | GRF | TL | 2015-02-23 22:08 | 2015-02-23 22:08 |  | Follow up |  | 33 |  |  | 2015
184193 |  |  | 992 Burrinjuck - Tumut 132kV TL | B | 2015Q1 | BUK, TU2 | TL | 2015-02-26 06:02 | 2015-02-26 17:21 |  |  |  | 132 |  | Forced | 2015
184255 |  |  | 94C Wallerawang 132 - Oberon 132kV Line |  | 2015Q1 | WWS | TL | 2015-02-25 16:05 | 2015-02-25 16:05 |  | Follow up |  | 132 |  |  | 2015
184292 |  |  | 96Y Waratah West - Mayfield West 132kV Line | X | 2015Q1 | WRH | TL | 2015-03-16 06:34 | 2015-03-21 11:27 |  |  |  | 132 |  |  | 2015
184342 |  |  | 8F1 Orange - Orange South 66kV Line |  | 2015Q1 | ORG | TL | 2015-02-26 15:14 | 2015-02-26 15:14 | distance to fault - 0.26km | Follow up |  | 66 |  |  | 2015
184350 |  |  | 735 Inverell - Inverell 66kV Line |  | 2015Q1 | INV | TL | 2015-02-26 17:05 | 2015-02-26 17:05 |  | Follow up |  | 66 |  |  | 2015
184351 |  |  | 734 Inverell - Inverell 66kV Line |  | 2015Q1 | INV | TL | 2015-02-26 17:05 | 2015-02-26 17:05 |  | Follow up |  | 66 |  |  | 2015
184352 |  |  | 662 Armidale - Walcha 66kV Line |  | 2015Q1 | AR1 | TL | 2015-02-26 20:35 | 2015-02-26 20:35 |  | Follow up |  | 66 |  |  | 2015
184353 |  |  | 662 Armidale - Walcha 66kV Line |  | 2015Q1 | AR1 | TL | 2015-02-26 20:52 | 2015-02-26 20:52 |  | Follow up |  | 66 |  |  | 2015
184354 |  |  | 661 Armidale - Oaky PS 66kV Line |  | 2015Q1 | AR1 | TL | 2015-02-26 21:24 | 2015-02-26 21:24 |  | Follow up |  | 66 |  |  | 2015
184355 |  |  | 877 Gunnedah - Keepit PS 66kV Line |  | 2015Q1 | GN2 | TL | 2015-02-26 21:52 | 2015-02-26 21:52 |  | Follow up |  | 66 |  |  | 2015
184363 | Unknown | TL | 9U3 Boggabri East - Gunnedah 132kV TL | Q | 2015Q1 | GN2, BGE | TL | 2015-02-27 05:49 | 2015-02-27 05:49 |  | Follow up | Successful trip and reclose, cause unknown. | 132 |  |  | 2015
184370 | Tree/Ground | TL | 8 Marulan - Dapto 330kV TL | Q | 2015Q1 | DPT, MRN | TL | 2015-02-27 07:48 | 2015-02-27 07:48 | Fault recorder indicates Distance to Fault 21km from Dapto. Field staff report large limb from tree snapped and made contact with conductors as it fell to the ground. Tree located off easement. No apparent damage to conductors. | 5/03/2015 13:58:00 ¦ Follow up ¦ Nil ¦ Nil | Fault recorder indicates Distance to Fault 21km from Dapto. Field staff report large limb from tree snapped and made contact with conductors as it fell to the ground. Tree located off easement. No apparent damage to conductors. On arrival to site it was reported that a large limb from tree had snapped and made contact with conductors as it fell to the ground; causing the fault. The branch has since been placed of the easement. No apparent damage to conductors was reported. | 330 |  |  | 2015
184399 | Non Transgrid | UG | 43 Holroyd - Rookwood Rd 330kV Cable | Z | 2015Q1 | HLD, RWR | UG | 2015-02-27 10:39 | 2015-07-24 12:10 | Cable repairs completed RTS on HVPRI 57525 Field staff advise contractor operating boring machine to provide access for service under North Parade, Guildford near Joint Bay 16. Head of boring machine appears to have contacted and damaged White Phase of cable. | 12/03/2015 14:02:00 ¦ Follow up ¦ Nil ¦ Advice from Assets/Project Services and remediate the road to required conditions. | Field staff advise contractor operating boring machine to provide access for service under North Parade, Guildford near Joint Bay 16. Head of boring machine appears to have contacted and damaged White Phase of cable. The damaged cable section has been cut and capped. The damaged conduit section was also cut and a temporary section has been placed in in order to prevent dirt and residue ingress to the conduits/cable area. Fibre external 80mm conduit has also been cut, a temporary section installed and the fibre conduit bundle was sealed for protection against dirt/moisture ingress until final repairs are conducted. Water was noted in conduits and also there is seepage in the area. Furthermore, sand bags have also been placed on the abovementioned repairs. The temporary man hole in the ground has been shored and plated/bitumen sealed for now – as plans are finalised for repairs. | 330 | Richard Archer awaiting interim report. Update 30/09/2015: Cable repaired and returned to service 24/07/2015. | Fault | 2015
184413 | Lightning/Storm | TL | 85 Tamworth 330 - Armidale 330kV TL | Q | 2015Q1 | AR1, TA1 | TL | 2015-02-27 13:24 | 2015-02-27 13:24 | distance to fault - TA1 95.24km - AR1 9.74km | Follow up | Successful trip and reclose, storms in the area. | 330 |  |  | 2015
184414 |  |  | M1 Murray - Murray 1 330kV TL | X | 2015Q1 | MUR, MP1 | TL | 2015-03-10 06:36 | 2015-03-10 14:42 |  |  |  | 330 |  |  | 2015
184454 |  |  | No.6 Deniliquin - Moama 66kV Line |  | 2015Q1 | DN2 | TL | 2015-03-01 04:27 | 2015-03-01 04:27 |  | Follow up |  | 66 |  |  | 2015
184473 |  |  | 999 Yass - Cowra 132kV TL | E | 2015Q1 | CW2, YSN | TL | 2015-03-01 11:30 | 2015-03-01 16:38 |  |  |  | 132 |  | Forced | 2015
184480 |  |  | 863 Ingleburn - Minto 66kV Line |  | 2015Q1 | ING | TL | 2015-03-01 14:39 | 2015-03-01 23:29 | S.O./Endeavour Energy advises overhead earth wire fallen on conductors between poles 2 and 3. Feeder requested isolated and earthed at Ingleburn. Feeder returned to service under HVPRI 57553. | Follow up |  | 66 |  |  | 2015
184481 |  |  | 85Y Wallerawang 132 - Springvale Colliery T Blackmans Flat Tee Clarence Colliery 66kV Line |  | 2015Q1 | WWS | TL | 2015-03-01 15:23 | 2015-03-01 15:23 | Distance to fault - 3.465km | Follow up |  | 66 |  |  | 2015
184482 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2015Q1 | BER | TL | 2015-03-01 16:15 | 2015-03-01 16:15 | Distance to fault - 26.07km | Follow up |  | 66 |  |  | 2015
184484 | Secondary Equipment | Cont | 863 Taree - Whitbread St Zone SS 66kV Line | Q | 2015Q1 | TRE | TL | 2015-03-01 18:15 | 2015-03-01 19:13 |  | Follow up | Line trip due to thunderstorm, auto reclose failed. | 66 | AR is set to Non- Auto at the request of the Distributor |  | 2015
184485 | Secondary Equipment | Cont | 861 Taree - Whitbread St Zone SS 66kV Line | Q | 2015Q1 | TRE | TL | 2015-03-01 18:15 | 2015-03-01 19:14 |  | Follow up | Line trip due to thunderstorm, auto reclose failed. | 66 | AR is set to Non- Auto at the request of the Distributor |  | 2015
184521 |  |  | 96T Armidale - Glen Innes 132kV TL | B | 2015Q1 | AR1, GNS | TL | 2015-03-02 09:32 | 2015-03-02 14:44 |  |  |  | 132 |  | Forced | 2015
184546 | Condition Monitor | Cond | No.1 Reactor | E | 2015Q1 | DMQ | RX | 2015-03-02 08:35 | 2015-03-05 09:26 | High Gas Level Alarm. Reactor is unavailable for service. Further investigations for the presence of high gas levels. | 30/03/2015 16:05:00 ¦ Follow up ¦ Nil. ¦ Nil. | An oil sample was taken from the Reactor and sent to an oil testing lab to confirm the dissolved gas levels. No elevated gas levels were detected, so it was concluded that the Treetech condition monitoring device was faulty. The Treetech device was replaced with an identical unit and the reactor was returned to service on Thursday 5/03/2015 at 10:26hrs | 330 |  | Forced | 2015
184707 |  |  | 84Y Deniliquin - Moama 66kV Line |  | 2015Q1 | DN2 | TL | 2015-03-01 04:27 | 2015-03-01 04:27 |  | Follow up |  | 66 |  |  | 2015
184931 |  |  | M3 Murray - Murray 1 330kV TL | X | 2015Q1 | MUR, MP1 | TL | 2015-03-17 07:25 | 2015-03-17 14:48 |  |  |  | 330 |  |  | 2015
185003 |  |  | 893/1 Cowra - Grenfell 66kV Line |  | 2015Q1 | CW2 | TL | 2015-03-08 05:41 | 2015-03-08 05:41 |  | Follow up |  | 66 |  |  | 2015
185014 |  |  | No.4 330kV Generator Transformer Group |  | 2015Q1 | LD1 | TX | 2015-03-08 15:22 | 2015-03-14 00:03 |  | Follow up |  | 330 |  |  | 2015
185016 |  |  | 705 Coffs Harbour - South Coffs Harbour 66kV Line |  | 2015Q1 | COF | TL | 2015-03-08 16:20 | 2015-03-08 17:31 |  | Follow up |  | 66 |  |  | 2015
185027 |  |  | 705 Coffs Harbour - South Coffs Harbour 66kV Line |  | 2015Q1 | COF | TL | 2015-03-08 17:35 | 2015-03-09 14:02 | CB Requested open By Lloyd at Essential energy as they don't have indication of volts at their end. | Follow up |  | 66 |  |  | 2015
185103 |  |  | M3 Murray - Murray 1 330kV TL | X | 2015Q1 | MUR, MP1 | TL | 2015-03-23 07:33 | 2015-03-23 15:35 |  |  |  | 330 |  |  | 2015
185105 |  |  | M5 Murray - Murray 1 330kV TL | X | 2015Q1 | MUR, MP1 | TL | 2015-03-25 09:38 | 2015-03-25 10:43 |  |  |  | 330 |  |  | 2015
185137 |  |  | 800 Wallerawang 132 - Railway 66kV Line |  | 2015Q1 | WWS | TL | 2015-03-10 15:02 | 2015-03-10 17:26 | No.2 protection details updated. | Follow up |  | 66 |  |  | 2015
185138 |  |  | 851 Beryl - Mudgee tee Gulgong 66kV Line |  | 2015Q1 | BER | TL | 2015-03-10 16:18 | 2015-03-10 16:18 |  | Follow up |  | 66 |  |  | 2015
185140 |  |  | 723 Wenna Tee Wathagar 66kV CB 7232 |  | 2015Q1 | MRE | CB | 2015-03-10 19:09 | 2015-03-10 20:56 |  | Follow up |  | 66 |  |  | 2015
185179 |  |  | L5 Lower Tumut - Tumut 3 330kV TL | X | 2015Q1 | LT1, TP3 | TL | 2015-03-17 07:27 | 2015-03-17 09:15 |  |  |  | 330 |  |  | 2015
185180 |  |  | L5 Lower Tumut - Tumut 3 330kV TL | X | 2015Q1 | LT1, TP3 | TL | 2015-03-17 09:41 | 2015-03-17 11:13 |  |  |  | 330 |  |  | 2015
185182 |  |  | L5 Lower Tumut - Tumut 3 330kV TL | X | 2015Q1 | LT1, TP3 | TL | 2015-03-17 11:31 | 2015-03-17 13:59 |  |  |  | 330 |  |  | 2015
185184 |  |  | 996 Wagga 330 - ANM tee Morven 132kV TL | X | 2015Q2 | ANM, WG1 | TL | 2015-04-01 08:30 | 2015-04-01 09:00 |  |  |  | 132 |  |  | 2015
185191 |  |  | 996 Wagga 330 - ANM tee Morven 132kV TL | X | 2015Q2 | ANM, WG1 | TL | 2015-04-01 09:39 | 2015-04-01 09:52 |  |  |  | 132 |  |  | 2015
185192 |  |  | 996 Wagga 330 - ANM tee Morven 132kV TL | X | 2015Q2 | ANM, WG1 | TL | 2015-04-01 10:37 | 2015-04-01 11:01 |  |  |  | 132 |  |  | 2015
185217 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q1 | CW2 | TL | 2015-03-11 13:06 | 2015-03-11 13:06 | DTF - 4.475km | Follow up |  | 66 |  |  | 2015
185231 |  |  | No.4 500kV Generator Transformer Group |  | 2015Q1 | ER0 | TX | 2015-03-11 17:08 | 2015-03-13 19:00 |  | Follow up |  | 500 |  |  | 2015
185232 | External | Cond | No.2 Transformer 330/132/11kV | E | 2015Q1 | SYW | TX | 2015-03-11 18:23 | 2015-03-11 21:04 | No.2 TX de-energised due to L1 condition monitoring alarm. Condition monitoring marshalling kiosk door was ajar. Very heavy rain caused water ingress into condition monitoring marshalling kiosk. Water dried and alarms cleared. TX returned to service. | 17/03/2015 11:51:00 ¦ Follow up ¦ Nil ¦ Nil | The stand by fitter was called investigate the alarms associated with No.2 Transformer. While investigating, the condition monitoring marshalling door was found open with rain entering the kiosk. The internals were dried and all alarms cleared. No.2 Transformer was RTS at 22:04hrs on the same night. | 330 |  | Forced | 2015
185247 |  |  | 864 Ingleburn - Macquarie Fields 66kV Line |  | 2015Q1 | ING | TL | 2015-03-12 05:48 | 2015-03-12 11:25 |  | Follow up |  | 66 |  |  | 2015
185252 |  |  | M9 Murray - Murray 1 330kV TL | X | 2015Q1 | MUR, MP1 | TL | 2015-03-12 10:01 | 2015-03-13 14:31 |  |  |  | 330 |  |  | 2015
185317 |  |  | 88L Gunnedah - Gunnedah 66 66kV Line |  | 2015Q1 | GN2 | TL | 2015-03-12 14:11 | 2015-03-12 14:11 |  | Follow up |  | 66 |  |  | 2015
185321 |  |  | 88L Gunnedah - Gunnedah 66 66kV Line |  | 2015Q1 | GN2 | TL | 2015-03-12 14:12 | 2015-03-12 14:12 |  | Follow up |  | 66 |  |  | 2015
185332 |  |  | 879 Narrabri - Wee Waa 66kV Line |  | 2015Q1 | NB2 | TL | 2015-03-12 15:49 | 2015-03-12 15:49 |  | Follow up |  | 66 |  |  | 2015
185365 |  |  | 23 Munmorah - Vales Point 330kV TL | X | 2015Q2 | MN1, VP1 | TL | 2015-05-01 07:11 | 2015-05-01 17:12 |  |  |  | 330 |  |  | 2015
185396 | Wiring/Testing Error | CB | 99J Yanco - Griffith 132kV TL | Q | 2015Q1 | GRF, YA2 | TL | 2015-03-13 15:34 | 2015-03-13 19:05 | CB99J2 closed via scada after No.2 protection reset at Griffith. No.2 Prot was sending permanent trip to CB. Protection flagging updated. | 23/07/2015 13:13:00 ¦ Follow up | At 15:34hrs 99J Yanco to Griffith 132 kV T/L tripped and auto reclosed and then tripped at Griffith only. It was confirmed there is a known reclose issue at Griffith. Attempts to close via SCADA were unsuccessful and staff have been called out to assist. Subsequent investigation indcates No2 protection may have locked up resulting in a permanet trip pulse being sent to CB. Reset protection and returned feeder to service. | 132 | (WO 342862) There was a missing jumper in the CB. This jumper has been replaced. The relay was then showing correct indication. An out of service Auto Reclose test was carried out. |  | 2015
185400 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2015Q1 | MRE | TL | 2015-03-13 18:05 | 2015-03-13 18:05 |  | Follow up |  | 66 |  |  | 2015
185474 | HV Equipment | SVC | No.1 Static VAR Compensator | B | 2015Q1 | SYW | SVC | 2015-03-17 06:45 | 2015-03-17 14:38 |  |  | Investigate & Repair Faulty Thyristor Units | 330 |  | Forced | 2015
185512 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2015Q1 | MRE | TL | 2015-03-17 05:44 | 2015-03-17 05:44 |  | Follow up |  | 66 |  |  | 2015
185516 |  |  | 83C Wagga North - Oura 66kV Line |  | 2015Q1 | WGN | TL | 2015-03-17 05:53 | 2015-03-17 05:53 | Weather tools indicate rain in vicinity. DTF 7.839km's | Follow up |  | 66 |  |  | 2015
185541 |  |  | L3 Lower Tumut - Tumut 3 330kV TL | X | 2015Q2 | LT1, TP3 | TL | 2015-04-20 07:36 | 2015-04-22 15:19 |  |  |  | 330 |  |  | 2015
185568 | Lightning/Storm | TL | 4 Yass - Marulan 330kV TL | Q | 2015Q1 | MRN, YSN | TL | 2015-03-18 07:26 | 2015-03-18 07:27 | Storms in the Area at time of Trip | 5/05/2015 14:30:00 ¦ Follow up ¦ Potential for Insulator failure and increased probability of flashover. ¦ A defect has been raised to replace the broken insulator. | Successful trip and reclose. Storms in the area. A line inspection of the structures and spans from 180 to 214 identified a broken insulator on structure 196. | 330 |  |  | 2015
185753 | HV Equipment | CB | No.3 Transformer 330/132/11kV | B | 2015Q1 | SYS | TX | 2015-03-19 12:15 | 2015-03-19 13:08 |  |  | SF6 TOPUP | 330 |  | Forced | 2015
185801 | HV Equipment | CB | 949 Mt Piper 132 - Orange North 132kV TL | B | 2015Q1 | MPP, ONO | TL | 2015-03-20 13:01 | 2015-03-20 14:12 |  |  | Top up SF6 CB | 132 |  | Forced | 2015
185837 |  |  | No.4 500kV Generator Transformer Group |  | 2015Q1 | ER0 | TX | 2015-03-20 19:09 | 2015-03-22 09:44 | No.4 Genertaor transformer group trip caused by power station issue. | Follow up |  | 500 |  |  | 2015
185865 |  |  | 876 Moree - Moree Solar Farm 66kV Line |  | 2015Q1 | MRE | TL | 2015-03-21 15:33 | 2015-03-21 15:33 | Trip and successful auto reclose during storm activity in area. | Follow up |  | 66 |  |  | 2015
185866 |  |  | 9S6/1 Haymarket - Pyrmont tee Darling Harbour 132KV Cable |  | 2015Q1 | HYM | UG | 2015-03-21 14:07 | 2015-03-21 16:39 |  | Follow up |  | 132 |  |  | 2015
185867 |  |  | 862/1 Taree - OCC Kew tee Johns River 66kV Line |  | 2015Q1 | TRE | TL | 2015-03-22 03:17 | 2015-03-22 03:17 |  | Follow up |  | 66 |  |  | 2015
185868 |  |  | No.1 Reactor |  | 2015Q1 | DMQ | RX | 2015-03-22 03:58 | 2015-03-25 09:25 | No. 1 reactor de-energised following receipt of gas level high 2 urgent alarm. | 8/04/2015 11:34:00 ¦ Follow up ¦ Nil. ¦ The TreeTech gas monitors currently fitted to the 330kV No.1, No.3 and No.4 Reactors at Dumaresq Substation will all be replaced. The faulty monitors will then be returned to TreeTech for a firmware update. Replacement is currently scheduled for the week ending 17/04/2015. |  | 330 |  |  | 2015
185872 | Condition Monitor | Cond | No.1 Reactor | E | 2015Q1 | DMQ | RX | 2015-03-22 03:58 | 2015-03-25 09:25 |  | Follow up | Gas level high urgent alarm received. Advised that alarm on reactor due to faulty condition monitoring equipment. | 330 |  | Forced | 2015
185929 |  |  | 870 Tamworth 132 - Kootingal 66kV Line |  | 2015Q1 | TMW | TL | 2015-03-24 17:56 | 2015-03-24 22:49 |  | Follow up |  | 66 |  |  | 2015
186148 | HV Equipment | CB | 932 Sydney West - Mt Druitt 132kV Line | B | 2015Q1 | SYW | TL | 2015-03-26 18:38 | 2015-03-26 19:42 |  |  | CB 9322 Low Gas - Red Phase | 132 |  | Forced | 2015
186175 | HV Equipment | CB | 78 Ingleburn - Sydney South 330kV TL | B | 2015Q1 | ING, SYS | TL | 2015-03-27 07:09 | 2015-03-27 10:20 |  |  | SF6 Top up | 330 |  | Forced | 2015
186195 | HV Equipment | TX | No.1 Transformer 330/132/11KV | E | 2015Q1 | WL1 | TX | 2015-03-27 06:56 | 2015-03-27 16:09 |  |  | Run tapchanger thru range, divertor major maint, oil pipes and top of tx need re painting. Change Silica Gel. | 330 |  | Forced | 2015
186235 |  |  | 92Z Sydney North - Sydney East tee Mt Colah 132kV TL | X | 2015Q2 | SE1, SYN | TL | 2015-04-12 15:56 | 2015-04-16 18:23 |  |  |  | 132 |  |  | 2015
186260 | HV Equipment | CB | 7R3 Kempsey - Prince St 33kV Line | Q | 2015Q1 | KS2 | TL | 2015-03-28 00:31 | 2015-03-28 01:49 |  |  | CB SF6 Topup | 33 |  |  | 2015
186268 | Unknown | Prot | No.3 Transformer 330/132/11KV | Z | 2015Q1 | SYN | TX | 2015-03-28 07:32 | 2015-04-02 15:17 |  | 26/05/2015 09:24:00 ¦ Follow up | No2 Protection Aux Transformer Bucholz & Transformer Multitrip. Oil levels ok, no air in low level receiver, alarm & trip contacts open on Bucholz. Suspect problem in wiring from Bucholz to relay room. | 330 | Damaged secondary cable. | Fault | 2015
186278 | Condition Monitor | Cond | No.4 Transformer 330/132/11kV | E | 2015Q1 | COF | TX | 2015-03-28 19:44 | 2015-03-28 21:13 | No.4 Transformer was de-energised upon receiving Condition Monitoring L1 alarm. | 13/04/2015 13:47:00 ¦ Follow up ¦ Nil. ¦ A request will be sent to Control Systems to modify the alarm settings such that only L1 alarms go through to SCADA with the Hydran's device fail alarm routed as a Miscellaneous Substation Alarm. | No.4 Transformer was de-energised upon receiving Condition Monitoring L1 alarm. On arrival advises that the hydran CB has tripped on No.4 Transformer 330/132/11kV that caused Hydran Dissolve Gas Monitor Fail alarm . Advises that he has switched the Auxiliary supplies to alternative transformers and have reset the Hydran CB and all the alarms. Graham Francis advised. 21:06 28/03/2015, F, M/NO, Graham Francis Graham advises he has spoken to Ben Van Der Linden on site and the alarm has been isolated. Further investigations on the Hydran will be done on Monday and the No.4 Transformer 330/132/11kV may be returned to service now. NCM advised. Further investigation revealed that the alarm was due to loss of AC supply to the Hydran unit fitted to the No.4 Transformer. The Hydran's corresponding device fail alarm output is currently routed as a level 1 condition monitoring SCADA alarm. The alarm was subsequently isolated pending follow up and the No.4 Transformer was returned to service at 22:13hrs. | 330 |  | Forced | 2015
186336 | Lightning/Storm | TL | 96M Narrabri - Moree 132kV TL | Q | 2015Q1 | MRE, NB2 | TL | 2015-03-31 00:12 | 2015-03-31 00:12 |  | Follow up | Successful trip and reclose. Storms in the area. | 132 |  |  | 2015
186458 | Relay | Prot | No.1 Transformer 132/66/11kV | Z | 2015Q1 | NB2 | TX | 2015-03-31 23:35 | 2015-04-02 12:00 |  | 1/05/2015 14:06:00 ¦ Follow up ¦ Nil. ¦ Nil. | No.1 Tx tripped due to faulty No.1 Prot T60 relay. Relay subsequently replaced and restored to service. | 132 |  | Fault | 2015
186526 |  |  | 85L Macarthur - Nepean 66kV Line |  | 2015Q2 | MAC | TL | 2015-04-01 11:35 | 2015-04-01 12:06 |  | Follow up |  | 66 |  |  | 2015
186623 |  |  | 957 Vales Pt - Ourimbah tee Morisset 132kV Line |  | 2015Q2 | VP1 | TL | 2015-04-03 10:52 | 2015-04-03 19:25 |  | Follow up |  | 132 |  |  | 2015
186635 | Unknown | TL | 99J Yanco - Griffith 132kV TL | Q | 2015Q2 | GRF, YA2 | TL | 2015-04-04 09:58 | 2015-04-04 09:58 |  | 4/08/2015 09:11:00 ¦ Follow up ¦ Nil ¦ Nil | 99J Yanco - Griffith tripped and auto-reclosed. Light rain in the area. | 132 |  |  | 2015
186638 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2015Q2 | BER | TL | 2015-04-05 06:03 | 2015-04-05 06:03 |  | Follow up |  | 66 |  |  | 2015
186654 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2015Q2 | BER | TL | 2015-04-06 10:22 | 2015-04-06 10:22 |  | Follow up |  | 66 |  |  | 2015
186655 | HV Equipment | CB | No.2 Transformer 132kV B CB 4422B | Q | 2015Q2 | SE1 | CB | 2015-04-06 11:58 | 2015-04-06 15:05 |  | Follow up | SF6 Topup on CB4422B | 132 |  |  | 2015
186656 |  |  | 851 Beryl - Mudgee tee Gulgong 66kV Line |  | 2015Q2 | BER | TL | 2015-04-06 14:20 | 2015-04-06 14:20 |  | Follow up |  | 66 |  |  | 2015
186657 | Lightning/Storm | TL | 99K Darlington Pt - Griffith 132kV TL | Q | 2015Q2 | DNT, GRF | TL | 2015-04-06 16:23 | 2015-04-06 16:23 |  | 4/08/2015 09:13:00 ¦ Follow up ¦ Nil ¦ Nil | Successful trip and reclose. Storms in the area. | 132 |  |  | 2015
186658 |  |  | 877 Gunnedah - Keepit PS 66kV Line |  | 2015Q2 | GN2 | TL | 2015-04-06 16:26 | 2015-04-06 17:10 |  | Follow up |  | 66 |  |  | 2015
186659 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2015Q2 | MRE | TL | 2015-04-06 16:43 | 2015-04-06 16:43 |  | Follow up |  | 66 |  |  | 2015
186660 |  |  | 850 Tumut - Talbingo tee Jounama Dam 66kV Line |  | 2015Q2 | TU2 | TL | 2015-04-06 18:32 | 2015-04-06 18:32 |  | Follow up |  | 66 |  |  | 2015
186661 | Lightning/Storm | TL | O1 Upper Tumut - Canberra 330kV TL | Q | 2015Q2 | CA1, UT1 | TL | 2015-04-06 18:47 | 2015-04-06 18:47 |  | 27/04/2015 08:32:00 ¦ Follow up ¦ Nil ¦ Nil | Successful trip and reclose. Storms in the area. Using TAMIS and the distance to fault information provided in the FEOR the closest structure to the fault was structure 52. An after fault patrol was organised for this structure and a number of structures either side of the fault location (structures 45 - 59). The after fault patrol was completed by Mains Yass staff on 23 April 2015. No Defects were found. | 330 |  |  | 2015
186662 |  |  | 878 Narrabri - Boggabri 66kV Line |  | 2015Q2 | NB2 | TL | 2015-04-06 19:49 | 2015-04-06 19:49 |  | Follow up |  | 66 |  |  | 2015
186663 |  |  | 879 Narrabri - Wee Waa 66kV Line |  | 2015Q2 | NB2 | TL | 2015-04-06 19:59 | 2015-04-06 19:59 |  | Follow up |  | 66 |  |  | 2015
186664 |  |  | 662 Armidale - Walcha 66kV Line |  | 2015Q2 | AR1 | TL | 2015-04-06 23:36 | 2015-04-06 23:36 |  | Follow up |  | 66 |  |  | 2015
186665 |  |  | 661 Armidale - Oaky PS 66kV Line |  | 2015Q2 | AR1 | TL | 2015-04-07 00:22 | 2015-04-07 02:33 |  | Follow up |  | 66 |  |  | 2015
186878 | Wiring/Testing Error | Prot | 23 Munmorah - Vales Point 330kV TL | Q | 2015Q2 | MN1, VP1 | TL | 2015-04-10 09:12 | 2015-04-10 10:24 | Line remained energised from MPS, prot'n operations at VPPS where attributed to abnormal prot'n relay" B" ph volts, investigations found "B" ph cct wiring loose. | Follow up | Spurious protection operation on No.2 Protection only. Investigations found it was caused by loose blue phase VT supply wiring. | 330 | Losing wire confirmed by Northern TL |  | 2015
186890 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2015Q2 | BER | TL | 2015-04-12 04:58 | 2015-04-12 10:26 | Essential Energy sectionalised the line and line returned to service. | Follow up |  | 66 |  |  | 2015
186894 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2015Q2 | BER | TL | 2015-04-12 14:46 | 2015-04-12 16:06 | Previous TARLO 0459 12/04/15. Returned to service after Essential Energy line patrol completed with no visual defects reported. Customer advises aerial patrol to be initiated if possible as customer load interrupted exists. | Follow up |  | 66 |  |  | 2015
186945 | Relay | Prot | No.6 330/132/11kV Transformer | Z | 2015Q2 | TOM | TX | 2015-04-14 06:29 | 2015-04-14 18:19 | No.1 Protection relay replaced. No. 6 Transformer returned to service at 18:19hrs. | Follow up | No.1 Prot relay (T60) found faulty. Relay subsequently replaced and transformer returned to service. | 330 | (WO 345191) T60 Relay replaced | Fault | 2015
186946 |  |  | 99N Darlington Point - Hillston 132kV Line |  | 2015Q2 | DNT | TL | 2015-04-14 06:36 | 2015-04-14 06:36 | Storm Activity on Weather tools observed. | Follow up |  | 132 |  |  | 2015
186966 | Staff Error | Proc | 132kV B Bus No.2 Section | Q | 2015Q2 | SYN | BB | 2015-04-14 10:08 | 2015-04-14 11:23 | Concurrent work on No.3 Capacitor at Sydney North. | Follow up | Bus tripped initiated by staff working on No.3 Capacitor CT secondary circuits. Rod Begg advises trip due to meter placement when working on No.3 Capacitor triggering busbar protection. | 132 | The trip occurred when the terminal cover was being removed from the No3 Cap CT terminal box. 4 exposed terminal studs that sit out from the CT terminals came in contact with the earthed terminal cover. This earthing of the CT secondaries operated the protection relay |  | 2015
186967 |  |  | 92A Lane Cove tee Macquarie Park CB 92A2 |  | 2015Q2 | SYN | CB | 2015-04-14 10:08 | 2015-04-14 11:23 |  |  |  | 132 |  |  | 2015
186968 |  |  | No.3 Transformer 132kV B CB 4432B |  | 2015Q2 | SYN | CB | 2015-04-14 10:08 | 2015-04-14 11:23 |  |  |  | 132 |  |  | 2015
186969 |  |  | No.4 Transformer 132kV B CB 4442B |  | 2015Q2 | SYN | CB | 2015-04-14 10:08 | 2015-04-14 11:23 |  |  |  | 132 |  |  | 2015
186970 |  |  | 132kV B Bus 1-2 Section CB 4112 |  | 2015Q2 | SYN | CB | 2015-04-14 10:08 | 2015-04-14 11:23 |  |  |  | 132 |  |  | 2015
186971 |  |  | No.3 Capacitor |  | 2015Q2 | SYN | CAP | 2015-04-14 10:08 | 2015-04-14 11:23 |  |  |  | 132 |  |  | 2015
186972 |  |  | 959 Sydney North - Sydney East 132kV TL | Z | 2015Q2 | SE1, SYN | TL | 2015-04-14 10:08 | 2015-04-14 11:23 |  |  |  | 132 |  | Fault | 2015
186973 |  |  | 250 Sydney North - Berowra 132kV Line | Z | 2015Q2 | SYN | TL | 2015-04-14 10:08 | 2015-04-14 11:23 |  |  |  | 132 |  | Fault | 2015
187014 | Animal/Bird | SVC | No.2 Static VAr Compensator | Z | 2015Q2 | BKH | SVC | 2015-04-14 20:04 | 2015-04-15 10:04 |  | Follow up | Advises upon investigation they have found a large dead crow on the 11th Harmonics filter. Flash over marks found over B and C phases. | 22 |  | Fault | 2015
187033 | Secondary Equipment | Cont | No.1 Capacitor | B | 2015Q2 | CA1 | CAP | 2015-04-15 11:04 | 2015-04-17 15:34 |  |  | Brett advises No.1 Capacitor receives it's reference volts from 330kV A1 Busbar and is reading approx 300kV. Possible faulty transducer. | 132 |  | Forced | 2015
187046 | HV Equipment | CB | No.1 Transformer 220/22kV | B | 2015Q2 | BKH | TX | 2015-04-15 16:45 | 2015-04-15 19:45 |  |  | TOP UP SF6 GAS. | 220 |  | Forced | 2015
187088 |  |  | 81F Panorama - Bathurst 66kV Line |  | 2015Q2 | PMA | TL | 2015-04-15 18:46 | 2015-04-15 18:46 |  | Follow up |  | 66 |  |  | 2015
187089 | Unknown | Cont | 875 Wallerawang 132 - Oakey Park 66kV Line | Q | 2015Q2 | WWS | TL | 2015-04-15 19:04 | 2015-04-15 22:13 | HMI indicates that reclose was inhibited. | Follow up | No reclose attempt on tripped customer line. | 66 | These are new protections and a directional check had not yet been performed. Because of this the relays were on a "Temp Group" setting. This setting group did not have AR. Therefore all OK |  | 2015
187090 |  |  | 868 Taree - Bohnock Tee Hallidays Point 66kV Line |  | 2015Q2 | TRE | TL | 2015-04-16 06:16 | 2015-04-16 06:16 | Essential Energy advise zone 2 Earth fault | Follow up |  | 66 |  |  | 2015
187145 |  |  | 79C Griffith - Darlington Point 33kV Line |  | 2015Q2 | GRF | TL | 2015-04-16 09:58 | 2015-04-16 10:47 |  | Follow up |  | 33 |  |  | 2015
187166 |  |  | 9R4 Finley - Mulwala 132kV Line |  | 2015Q2 | FNY | TL | 2015-04-16 15:11 | 2015-04-16 15:11 |  | Follow up |  | 132 |  |  | 2015
187252 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2015Q2 | MRE | TL | 2015-04-18 12:48 | 2015-04-18 12:48 |  | Follow up |  | 66 |  |  | 2015
187253 |  |  | 703 Port Macquarie - Boronia St No.1 33kV Line |  | 2015Q2 | PMQ | TL | 2015-04-18 20:30 | 2015-04-18 20:30 |  | Follow up |  | 33 |  |  | 2015
187254 |  |  | 703 Port Macquarie - Boronia St No.1 33kV Line |  | 2015Q2 | PMQ | TL | 2015-04-18 20:56 | 2015-04-18 20:56 |  | Follow up |  | 33 |  |  | 2015
187256 |  |  | No.10 Yanco - Kamarah (No.10 Council) |  | 2015Q2 | YA2 | TL | 2015-04-19 10:53 | 2015-04-19 14:12 | Dave from Essential confirms approx 1MW loss of load. | Follow up |  | 33 |  |  | 2015
187273 |  |  | 94M Mt Piper 132 - Beryl tee Mudgee tee Ilford 132kV TL | X | 2015Q2 | BER, MPP | TL | 2015-04-30 07:45 | 2015-04-30 17:29 |  |  |  | 132 |  |  | 2015
187294 | HV Equipment | TX | No.1 Transformer 132/66/11kV | B | 2015Q2 | WWS | TX | 2015-04-21 11:07 | 2015-04-21 13:20 |  |  | Top up Oil in transformer. | 132 |  | Forced | 2015
187295 | Damaged Cable | Prot | No.3 Transformer 330/132/11KV | Z | 2015Q2 | SYN | TX | 2015-04-20 21:21 | 2015-04-21 16:01 | Protection tech advises trip caused by defective cable between No.3 Aux Tx and Bay Marshalling Kiosk triggering buchholz trip. cable has been replaced | Follow up | Transformer tripped 2 minutes after receiving a fleeting Buchholz alarm. Buchholz alarm from No.3 Aux Tx | 330 | Cable fault found. Investigation closed. | Fault | 2015
187296 |  |  | 957 Vales Pt - Ourimbah tee Morisset 132kV Line |  | 2015Q2 | VP1 | TL | 2015-04-20 22:01 | 2015-04-22 04:16 | SO/Ausgrid Mark advised no customer load lost. | Follow up |  | 132 |  |  | 2015
187297 |  | CB | No.6 Bay Coupler CB 5062 | Q | 2015Q2 | VP1 | CB | 2015-04-21 05:03 | 2015-04-21 06:30 | No.6 Bay Coupler CB 5062 Low SF6 - Isolated SF6 topped up and CB5062 RTS | Follow up | CB SF6 Topup. | 330 |  |  | 2015
187298 | Lightning/Storm | TL | 95 Newcastle - Tomago 330kV TL | Q | 2015Q2 | NEW, TOM | TL | 2015-04-21 04:28 | 2015-04-21 04:28 |  | Follow up | Successful trip and reclose. Storms in the area. | 330 |  |  | 2015
187299 |  |  | 96U Newcastle - Kurri 132kV/11kV Line |  | 2015Q2 | NEW | TL | 2015-04-21 05:25 | 2015-04-23 13:21 |  | Follow up |  | 132 |  |  | 2015
187300 |  |  | 96W Newcastle - Capral 132kV Line |  | 2015Q2 | NEW | TL | 2015-04-21 05:29 | 2016-03-10 09:48 |  | Follow up |  | 132 |  |  | 2015
187301 |  |  | 95M Muswellbrook 330 - Mitchell Line 132kV Line |  | 2015Q2 | MRK | TL | 2015-04-21 05:49 | 2015-04-21 05:54 | Line remained energised from AusGrids Mitchell Line 132kV SS. Only opened at Muswellbrook 330kV SS on CB..95M2 - Placed on load via SCADA at Ausgrid's request | Follow up |  | 132 |  |  | 2015
187302 | HV Equipment | Aux Tx | No.2 Transformer 330/66/11kV | Z | 2015Q2 | ING | TX | 2015-04-21 04:44 | 2015-04-21 15:18 | subs staff advises Conservator Low oil on Aux Tx cause of trip - Oil was topped up and TX was RTS | Follow up | Advises Conservator Low oil on Aux Tx cause of trip. PRI prepared to facilitate top up. | 330 |  | Fault | 2015
187315 |  |  | 950 Newcastle - Jesmond 132kV Line |  | 2015Q2 | NEW | TL | 2015-04-21 06:27 | 2015-04-22 18:46 |  | Follow up |  | 132 |  |  | 2015
187341 | HV Equipment | CB | No.6 Bay Coupler CB 5062 | Q | 2015Q2 | VP1 | CB | 2015-04-21 10:08 | 2015-04-21 13:34 | 5062 opened after HV CB abnormal alarm. On-site staff advised sf6 low alarm. CB opened as soon as possible as a precaution. SF6 levels checked OK and were at the same level following top up during earlier outage. 5062 returned to service. | 20/05/2015 09:35:00 ¦ Follow up ¦ Nil. ¦ This circuit breaker will be monitored for any similar recurrence in the future. | 5062 opened after HV CB abnormal alarm. On-site staff advised sf6 low alarm. CB opened as soon as possible as a precaution. SF6 levels checked OK and were at the same level following top up during earlier outage. 5062 returned to service. Requested 5062 closed, SF6 gas pressure was OK, likely cause was water. Staff responding to the alarm confirmed that SF6 pressures were normal in the breaker. The SF6 alarm circuits were investigated but no issues could be found to explain the alarm initiation. It was noted that it was rainy and windy around the time of the alarm; and although there were no obvious signs of moisture affecting any of the circuits; it is possible that the weather conditions contributed to the alarm initiation. The circuit breaker was subsequently returned to service on 21/04/2015 at 13:34hrs | 330 |  |  | 2015
187354 |  |  | 96Z Newcastle - Maryland 132kV Line |  | 2015Q2 | NEW | TL | 2015-04-21 13:24 | 2015-04-23 18:43 |  | Follow up |  | 132 |  |  | 2015
187355 |  |  | 828 Mt Piper 132 - Portland tee BCSC 66kV Line |  | 2015Q2 | MPP | TL | 2015-04-21 11:31 | 2015-04-21 13:18 | Endeavour Energy sectionalised faulted part of line. 828 returned to service. | Follow up |  | 66 |  |  | 2015
187362 |  |  | Station Transformer 1A (CB 5412) |  | 2015Q2 | MN1 | CB | 2015-04-21 17:34 | 2015-04-27 20:09 |  | Follow up |  | 330 |  |  | 2015
187363 |  |  | No.2 Transformer 330/66/11kV |  | 2015Q2 | ING | TX | 2015-04-21 04:44 | 2015-04-21 15:18 | Tripped on Buchholz caused by Aux Tx Low oil level. Heavy Rain and Winds at time of trip. | Follow up |  | 330 |  |  | 2015
187375 | HV Equipment | CB | No.5 330kV Generator Transformer CB 5252 | Q | 2015Q2 | VP1 | CB | 2015-04-22 08:58 | 2015-04-22 10:13 |  |  | CB SF6 Topup | 330 |  |  | 2015
187416 |  |  | 950 Newcastle - Jesmond 132kV Line |  | 2015Q2 | NEW | TL | 2015-04-22 18:51 | 2015-04-23 18:24 | 950 was returned to service at 18:46hrs on 22/04/15 and placed on load, but tripped 5 minutes later at 18:51. Ausgrid quickly identified the cause. | Follow up |  | 132 |  |  | 2015
187467 |  |  | No.1 Transformer 330/132/11kV | B | 2015Q2 | MAC | TX | 2015-04-24 07:13 | 2015-04-24 15:38 |  |  |  | 330 |  | Forced | 2015
187482 | HV Equipment | TL | 965 Armidale - Kempsey 132kV TL | Q | 2015Q2 | AR1, KS2 | TL | 2015-04-23 10:51 | 2015-04-23 10:51 | Arimadle DTF No1 104.9km, No2 104.9km Kempsey DTF No1 47.06km, No2 49.69km | 30/04/2015 14:02:00 ¦ Follow up ¦ N/A ¦ Final repairs to the overhead earth wire are planned for Friday 1/05/2015. | Successful trip and reclose due to fallen earth wire. A patrol was carried out on Saturday 25/04/2015 and a damaged overhead earth wire was found between poles 297A and 298. Temporary repairs to the earth wire were completed on Sunday 26/04/2015. | 132 |  |  | 2015
187489 | HV Equipment | VT | No.5 Transformer 330/132/11kV | B | 2015Q2 | SYN | TX | 2015-04-24 07:07 | 2015-05-22 15:09 |  |  | Resample CVTs - high methane levels | 330 |  | Forced | 2015
187511 |  |  | 96U Newcastle - Kurri 132kV/11kV Line |  | 2015Q2 | NEW | TL | 2015-04-23 13:27 | 2015-04-24 18:24 | DTF 5.264km | Follow up |  | 132 |  |  | 2015
187592 |  |  | 850 Tumut - Talbingo tee Jounama Dam 66kV Line |  | 2015Q2 | TU2 | TL | 2015-04-24 16:17 | 2015-04-24 16:17 |  | Follow up |  | 66 |  |  | 2015
187594 | Lightning/Storm | TL | 99A Uranquinty - Finley 132kV TL | Q | 2015Q2 | FNY, URQ | TL | 2015-04-25 04:48 | 2015-04-25 04:48 |  | 8/05/2015 14:45:00 ¦ Follow up ¦ Nil ¦ Nil | Successful trip and reclose. Storms in the area. Using Indji it was identified that there was lightning activity at the time of the fault around structure 495. An after fault patrol was organised for this structure and a number of structures either side of the fault location (structures 490 - 500). The after fault patrol was completed by Mains Wagga staff on 8 May 2015. No Defects were found. | 132 |  |  | 2015
187595 | HV Equipment | TL | 965 Armidale - Kempsey 132kV TL | E | 2015Q2 | AR1, KS2 | TL | 2015-04-25 11:52 | 2015-04-26 11:14 |  | Follow up | Essential Energy Staff advised earth wire associated with 965 Armidale to Kempsey 132kV T/L has come down in paddock near Bellbrook. Request de-energise 965 T/L. Repairs to take place first thing tomorrow. | 132 | Update 30/09/2015: Repairs carried out 01/05/2015. | Forced | 2015
187596 | Lightning/Storm | TL | 990 Yass - Wagga 132 132kV TL | Q | 2015Q2 | WG2, YSN | TL | 2015-04-25 11:27 | 2015-04-25 11:27 | Protection details shown cover multiple TAR events. Refer to FEORs 2015-F-0222 and 2015-F-0223. | 6/05/2015 14:46:00 ¦ Follow up ¦ Nil ¦ Nil | Successful trip and reclose. Storms in the area. Using Indji it was identified that there was lightning activity at the time of the fault around structure 303. An after fault patrol was organised for this structure and a number of structures either side of the fault location (structures 295 - 312). The after fault patrol was completed by Mains Yass staff on 6 May 2015. No Defects were found. | 132 |  |  | 2015
187597 | Lightning/Storm | TL | 990 Yass - Wagga 132 132kV TL | Q | 2015Q2 | WG2, YSN | TL | 2015-04-25 11:44 | 2015-04-25 11:44 | Protection details shown cover multiple TAR events. Refer to FEORs 2015-F-0221 and 2015-F-0223. | 5/05/2015 10:32:00 ¦ Follow up ¦ Nil ¦ Nil | Successful trip and reclose. Storms in the area. Using Indji it was identified that there were substantial lightning activity at the time of both faults between structures 474 - 494. An after fault patrol was organised for structures 474 - 494. The after fault patrol was completed by Mains Yass staff on 29 April 2015. No Defects were found. | 132 |  |  | 2015
187598 | Lightning/Storm | TL | 990 Yass - Wagga 132 132kV TL | Q | 2015Q2 | WG2, YSN | TL | 2015-04-25 11:45 | 2015-04-25 11:45 | Protection details shown cover multiple TAR events. Refer to FEORs 2015-F-0221 and 2015-F-0222. | 5/05/2015 10:32:00 ¦ Follow up ¦ Nil ¦ Nil | Successful trip and reclose. Storms in the area. Using Indji it was identified that there were substantial lightning activity at the time of both faults between structures 474 - 494. An after fault patrol was organised for structures 474 - 494. The after fault patrol was completed by Mains Yass staff on 29 April 2015. No Defects were found. | 132 |  |  | 2015
187599 |  |  | 836 Murrumburrah - Cootamundra 66kV Line |  | 2015Q2 | MRU | TL | 2015-04-25 11:55 | 2015-04-25 14:19 |  | Follow up |  | 66 |  |  | 2015
187600 |  |  | 893/5 Forbes - Payten's Bridge 66kV Line |  | 2015Q2 | FB2 | TL | 2015-04-25 17:41 | 2015-04-25 17:41 |  | Follow up |  | 66 |  |  | 2015
187618 |  |  | 863 Cowra - Canowindra 66kV Line |  | 2015Q2 | CW2 | TL | 2015-04-26 10:33 | 2015-04-26 10:33 | Trip & Auto Reclose. | Follow up |  | 66 |  |  | 2015
187637 |  |  | 96M Narrabri - Moree 132kV TL | B | 2015Q2 | MRE, NB2 | TL | 2015-04-27 12:54 | 2015-04-27 15:27 |  |  |  | 132 |  | Forced | 2015
187693 |  |  | M9 Murray - Murray 1 330kV TL | X | 2015Q2 | MUR, MP1 | TL | 2015-05-14 12:33 | 2015-05-21 13:23 |  |  |  | 330 |  |  | 2015
187695 |  |  | 14 Sydney North - Kemps Creek 330kV TL | Y | 2015Q2 | KCR, SYN | TL | 2015-04-27 14:33 | 2015-04-27 14:58 |  |  |  | 330 |  |  | 2015
187713 |  |  | Broken Hill - Railway Town 22kV Line |  | 2015Q2 | BKH | TL | 2015-04-27 20:42 | 2015-04-27 20:42 |  | Follow up |  | 22 |  |  | 2015
187718 | HV Equipment | CB | No.3 Bay Coupler CB 6032 | Q | 2015Q2 | ER0 | CB | 2015-04-28 10:39 | 2015-04-28 14:49 |  |  | Defective white phase hydaulic pump contactor replaced. | 500 |  |  | 2015
187812 |  |  | 97L Guthega - Jindabyne Pumps 132kV TL | X | 2015Q2 | GTH, JDP | TL | 2015-05-04 11:47 | 2015-05-04 15:28 |  |  |  | 132 |  |  | 2015
187824 | Protection | Prot | No.3 Transformer 330/132/11kV | Z | 2015Q2 | MN1 | TX | 2015-04-29 17:24 | 2015-04-30 14:54 |  | 27/05/2015 08:54:00 ¦ Follow up ¦ Nil. ¦ Nil. | At 17:24hrs No.3 Transformer CB 5042 tripped on energising after outage. Peter McLeod believes trip may have been inrush issue only. He will followup with Protection Staff Thursday 30th April to confirm. CB 5042 tripped on 3 Phase Bias Differential relay (No.2 Protection) and High Speed Trip Relay 86. A visual inspection of the transformer was carried out and no issues were observed. Protection Design Group confirmed that no evidence of a genuine fault could be found in the fault records retrieved from site, so it was concluded that the trip was due to inrush currents associated with energisation of the transformer at a particular point on the 50Hz cycle. There is a history of similar trips associated with RADSB relays. The transformer was subsequently returned to service on Thursday 30/04/2015 at 14:54hrs | 330 | (WO 345849) Found that relay tested ok, tested No 1 protection KBCH all ok. These realys are prone to inrush. Investiagtions by Protection Design confirmed ther was no fault on the system at the time of the trip. Therefore relay tripped on inrush | Fault | 2015
187825 |  |  | 97E Munmorah - Charmhaven Tee Lake Munmorah 132kV Line | Q | 2015Q2 | MN1 | TL | 2015-04-29 17:24 | 2015-04-30 14:54 |  |  |  | 132 |  |  | 2015
187826 |  |  | No.3 Transformer 330/132/11kV |  | 2015Q2 | MN1 | TX | 2015-04-29 17:24 | 2015-04-30 14:54 |  | Follow up |  | 330 |  |  | 2015
187827 |  |  | 97E Munmorah - Charmhaven Tee Lake Munmorah 132kV Line |  | 2015Q2 | MN1 | TL | 2015-04-29 17:24 | 2015-04-30 14:54 |  |  |  | 132 |  |  | 2015
187828 |  |  | No.3 Transformer 330/132/11kV |  | 2015Q2 | MN1 | TX | 2015-04-29 17:24 | 2015-04-30 14:54 |  | Follow up |  | 330 |  |  | 2015
187829 |  |  | 97E Munmorah - Charmhaven Tee Lake Munmorah 132kV Line |  | 2015Q2 | MN1 | TL | 2015-04-29 17:24 | 2015-04-30 14:54 |  |  |  | 132 |  |  | 2015
187830 |  |  | No.3 Transformer 330/132/11kV |  | 2015Q2 | MN1 | TX | 2015-04-29 17:24 | 2015-04-30 14:54 |  | Follow up |  | 330 |  |  | 2015
187831 |  |  | 97E Munmorah - Charmhaven Tee Lake Munmorah 132kV Line |  | 2015Q2 | MN1 | TL | 2015-04-29 17:24 | 2015-04-30 14:54 |  |  |  | 132 |  |  | 2015
187832 |  |  | No.3 Transformer 330/132/11kV |  | 2015Q2 | MN1 | TX | 2015-04-29 17:24 | 2015-04-30 14:54 |  | Follow up |  | 330 |  |  | 2015
187833 |  |  | 97E Munmorah - Charmhaven Tee Lake Munmorah 132kV Line |  | 2015Q2 | MN1 | TL | 2015-04-29 17:24 | 2015-04-30 14:54 |  |  |  | 132 |  |  | 2015
187834 |  |  | No.3 Transformer 330/132/11kV |  | 2015Q2 | MN1 | TX | 2015-04-29 17:24 | 2015-04-30 14:54 |  | Follow up |  | 330 |  |  | 2015
187835 |  |  | 97E Munmorah - Charmhaven Tee Lake Munmorah 132kV Line |  | 2015Q2 | MN1 | TL | 2015-04-29 17:24 | 2015-04-30 14:54 |  |  |  | 132 |  |  | 2015
187836 |  |  | No.3 Transformer 330/132/11kV |  | 2015Q2 | MN1 | TX | 2015-04-29 17:24 | 2015-04-30 14:54 |  | Follow up |  | 330 |  |  | 2015
187837 |  |  | 97E Munmorah - Charmhaven Tee Lake Munmorah 132kV Line |  | 2015Q2 | MN1 | TL | 2015-04-29 17:24 | 2015-04-30 14:54 |  |  |  | 132 |  |  | 2015
187838 | HV Equipment | Disc | 6 Capital Wind Farm A CB 62A | Q | 2015Q2 | CA1 | CB | 2015-04-29 17:45 | 2016-02-10 12:25 |  |  | During restoration of 6 Canberra to Capital Wind Farm 330 kV T/L, 65 A Bus Selector failed to close. Requested Brett lock open. 6 Canberra to Capital Wind Farm 330 kV T/L returned to service on BCB 62B only at Canberra. | 330 | Work order No. 346136 was created on 6/05/2015 to find and fix this problem. Hydraulic gear box was replaced. Work order closed. |  | 2015
187848 |  |  | No.1 Transformer 132/33/11kV |  | 2015Q2 | CLY | TX | 2015-04-30 08:37 | 2015-04-30 08:59 |  | Follow up |  | 132 |  |  | 2015
187874 | Unknown | Other | No.1 Transformer 330/132/11kV | Z | 2015Q2 | RWR | TX | 2015-04-30 14:23 | 2015-09-04 12:32 |  | 25/05/2015 16:06:00 ¦ Follow up | Ben advised fault traces passed on to Protection and Metering Design Manager, Gurinder Saluja. Gurinder advised suspected geniune TX fault. Protection relay data for the fault indicated a 3kA fault on Blue (C) phase between the air core reactor and the outdoor post CT. Visual inspection of the AIS equipment did not identify any cause of the fault, nor did insulation resistance measurements. SF6 gas analysis identified decomposition byproducts in the blue phase GIS chamber G10. Alstom has been contacted to assist with inspection of the GIS chamber. No.1 Transformer remains out of service. | 330 | Work order No. 346081 was created on 5/05/2015 to investigate this issue. Work order No. 346081 is closed now. Alstom has been asked to fix this issue as RWR substation is still under warranty. GIS chamber replacement, regasing and testing has been completed. Ready to be in service now. Tx in service now. | Fault | 2015
187995 | External | Other | 19 Kangaroo Valley - Bendeela 330kV Line | Q | 2015Q2 | KVS | TL | 2015-05-01 13:43 | 2015-05-02 14:23 |  | 25/05/2015 11:50:00 ¦ Follow up | During investigation of trip on 19 Bendeela C.B.. 192 yesterday, No.2 DC control cabling IR measured at 2.8 MΩ. The cabling had recently measured 15 MΩ during protection maintenance work. The cabling to 19 Bendeela Bay Marshalling Kiosk was submerged under approximately 50mm of water in the cable trench adjacent to the BMK. The cabling was elevated above the water level and subsequent testing of the control cabling IR showed an improved measurement of 5.6 MΩ. On 02/05/2015, Field Services technicians investigated the trip. No protection event was recorded and the control circuit was inspected. There was no indication of a cable fault however the were found sitting in ~50mm of water which had pooled the in the cable trench. Secondary cable insulation resistance was measured at 2.8MOhms and The cables were treated with spray on fire retardent which was moisture laden. The cables were lifted and supoprted above the water and allowed to dry with cable insulation resistance improving to 5.6MOhm in 3 hours. The cables remain supported above the pool of water in the cable trench. | 330 | No further comments |  | 2015
188016 |  |  | No.2 Transformer 330/132/11kV | X | 2015Q2 | VP1 | TX | 2015-05-01 08:54 | 2015-05-01 17:12 |  |  |  | 330 |  |  | 2015
188020 |  |  | No.2 Capacitor | X | 2015Q2 | VP1 | CAP | 2015-05-01 08:54 | 2015-05-01 17:12 |  |  |  | 330 |  |  | 2015
188134 | Damaged Cable | Cont | No.1 Transformer 330/132/11kV | E | 2015Q2 | SYW | TX | 2015-05-02 14:57 | 2015-05-08 15:47 | No.1 Transformer 330kV C.B.. 5412 C.T. SF6 Depleted and SF6 Low alarms received via SCADA. Heavy rain at time. Transformer taken out of service as a precaution. No loading issues at time. | Follow up | Tx de-energised immediately due to SF6 depleted alarm associated with CB5412 CTs. At 15:26hrs on 02/05/2015, No.1 Transformer 330kV CB 5412 at Sydney West Substation alarmed on low and depleted SF6. No.1 Transformer at Sydney West Substations was manually switched out of service No.1 Transformer 330kV C.B.. 5412 C.T. SF6 Depleted and SF6 Low alarms received via SCADA. Heavy rain at time. Transformer taken out of service as a precaution. No loading issues at time. The issue was traced to a defective alarms cable, causing the SF6 alarms to be spuriously raised during heavy rain. A temporary repair was made to this alarms cable by taping around the affected section. Field Services to check with Project Services if the cable is to be replaced as part of the SYW secondary systems replacement project, and if not will organise replacement of the affected cable. | 330 | SSAM - Not investigated by Secondary Systems, Substations issue. Work oder No. 345941 was created to identify and fix the problem. Bite marks were found on either white phase or red phase cable from CT to BMK. The cable was taped with red insulation tape. Work order closed. Steve Cunningham has advised cable will be replaced if not already in the scope of the SYS project. | Forced | 2015
188199 |  |  | 77 Wallerawang - Ingleburn 330kV TL | Y | 2015Q2 | ING, WW1 | TL | 2015-05-04 09:29 | 2015-05-04 15:34 | RTS at Wallerawang on CB 772 only. Protection integrity of Bay E to be followed up. | Follow up |  | 330 |  |  | 2015
188325 |  |  | No.1 Reactor |  | 2015Q2 | LSM | RX | 2015-05-05 12:31 | 2015-05-05 12:41 |  | Follow up |  | 330 |  |  | 2015
188326 | Staff Error | Proc | No.1 Reactor | Z | 2015Q2 | LSM | RX | 2015-05-05 12:31 | 2015-05-05 12:41 | Staff fault finding No.1 RX hot oil alarm have inadvertently operated a micro switch on the side of the temperature indicator operating the No2 Protection. | Follow up | Staff fault finding No.1 RX hot oil alarm have inadvertently operated a micro switch on the side of the temperature indicator operating the No2 Protection. | 330 | Work order No. 347209 was created on 22/05/2015 to investigate and fix hot oil alarms issue. Rx oil temp was found ok and the problem is with alarm cabling. The hot oil alarms are changed to spare cores. Work order closed. | Fault | 2015
188345 |  |  | 9C8 Brandy Hill - Stroud 132kV TL | X | 2015Q2 | SRD, BRH | TL | 2015-05-25 06:51 | 2015-05-25 16:38 |  |  |  | 132 |  |  | 2015
188498 |  |  | 14 Sydney North - Kemps Creek 330kV TL | X | 2015Q2 | KCR, SYN | TL | 2015-05-28 06:02 | 2015-05-28 17:11 |  |  |  | 330 |  |  | 2015
188633 |  |  | 92Z Sydney North - Sydney East tee Mt Colah 132kV TL | X | 2015Q2 | SE1, SYN | TL | 2015-05-13 19:13 | 2015-05-14 19:42 |  |  |  | 132 |  |  | 2015
188727 |  |  | 65 Upper Tumut A CB 652A |  | 2015Q2 | MUR | CB | 2015-04-01 09:23 |  |  |  |  | 330 |  |  | 2015
188728 |  |  | 65 Upper Tumut B CB 652B |  | 2015Q2 | MUR | CB | 2015-04-01 09:23 |  |  |  |  | 330 |  |  | 2015
188838 | Wiring/Testing Error | Cont | No.4 Capacitor | B | 2015Q2 | SYN | CAP | 2015-05-09 14:50 | 2015-05-09 16:02 |  |  | Whilst working on No5 Capacitor CB 5752 under RFA 2015-3781, techs found a problem with Blue Phase SF6 alarm wiring. Incorrect wiring would have prevented Blue Phase SF6 alarm being generated. Suspect same wiring issue with No4 Capacitor CB 5742. | 330 |  | Forced | 2015
188840 | HV Equipment | TX | No.3 Transformer 330/132/11kV | E | 2015Q2 | BFD | TX | 2015-05-08 18:16 | 2015-05-08 21:02 | Info update At 18:01hrs No.3 Transformer initiated the first of several L1 Condition Monitoring Alarms. Temperatures appeared okay on HMI. At 18:16hrs No.3 Transformer was de-energised. (Tx normally off loaded) Richard Manderson contacted. Advised that the No.3 Transformer condition monitoring relay has interrogated in Consultation with Graeme Mackey and no data found to indicate that there is anything wrong with No.3 Transformer and the alarm has been reset. Richard advised its ok to RTS No.3 Transformer | Follow up | Transformer de-energised subsequent to Condition Monitoring L1 alarm being received. Advised that the No.3 Transformer condition monitoring relay has interrogated in Consultation with Graeme Mackey and no data found to indicate that there is anything wrong with No.3 Transformer and the alarm has been reset. | 330 |  | Forced | 2015
188855 |  |  | No.6 Tenterfield - Council (Tenterfield Town) 22kV Line |  | 2015Q2 | TTF | TL | 2015-05-10 09:16 | 2015-05-10 11:40 | Duplaciate FEOR to 2015-F-0248/1 due to TheOS error - sent to allow completion | Follow up |  | 22 |  |  | 2015
188856 |  |  | No.6 Tenterfield - Council (Tenterfield Town) 22kV Line |  | 2015Q2 | TTF | TL | 2015-05-10 09:16 | 2015-05-10 11:40 | Less than 0.5MVA interrupted | Follow up |  | 22 |  |  | 2015
188857 |  |  | 96M Narrabri - Moree 132kV TL |  | 2015Q2 | MRE, NB2 | TL | 2015-05-11 04:59 | 2015-05-11 04:59 |  | Follow up |  | 132 |  |  | 2015
188858 | Unknown | TL | 96M Narrabri - Moree 132kV TL | Q | 2015Q2 | MRE, NB2 | TL | 2015-05-11 04:59 | 2015-05-11 04:59 |  |  | Successful trip and reclose. Cause unknown. | 132 |  |  | 2015
188987 |  |  | 96P Taree - Stroud 132kV TL | X | 2015Q2 | TRE | TL | 2015-05-15 08:20 | 2015-05-15 12:43 |  |  |  | 132 |  |  | 2015
189028 | HV Equipment | CB | 26 Munmorah B CB 262B | Q | 2015Q2 | SYW | CB | 2015-05-14 04:01 | 2015-05-14 10:00 |  |  | CB SF6 Topup. | 330 |  |  | 2015
189287 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2015Q2 | GRF | TL | 2015-05-15 10:49 | 2015-05-15 10:49 |  | Follow up |  | 33 |  |  | 2015
189294 |  |  | 79M Griffith - Hanwood 33kV Line |  | 2015Q2 | GRF | TL | 2015-05-15 11:28 | 2015-05-15 11:28 |  | Follow up |  | 33 |  |  | 2015
189306 | Staff Error | Proc | 22kV Bus | Q | 2015Q2 | BRD | BB | 2015-05-15 11:05 | 2015-05-15 11:18 | Protection Staff inadvertently caused trip during Functional tests on No.2 Moulamein T/L Project work (PRI 58867). | 26/05/2015 09:45:00 ¦ Follow up | Protection Staff inadvertently caused trip during Functional tests on No.2 Moulamein T/L Project work (PRI 58867). During the replacement of the No2 Moulamein Feeder, whilst completing CBF trip checks the No1 Balranald CB12 & No1 Transformer CB2412 were tripped. This was because of a non-standard orphan design installed by Alstom. This scheme uses a BBP MTR and a BBP Trip Bus | 22 | In the process of replacing No2 Prot on Molamein fdr, the existing panel was isolated using a PMWI. As per TranGrid procedure CBF trip checks were carried out on the new panel to an open link on the feeder protection panrl. Further testing by the contractor was to be carried out. The TransGrid Technician mistakingly thought the existing isolations on the BBP panel were adequate. The isolations were not adequate because the scheme at BRD uses a BBP trip bus from the feeder protection panels which is not the norm at TransGrid Substations and requires additional isolations. |  | 2015
189307 |  |  | No.1 Transformer 220/22kV | Z | 2015Q2 | BRD | TX | 2015-05-15 11:05 | 2015-05-15 11:18 |  |  |  | 220 |  | Fault | 2015
189308 |  |  | No.3 SPARE 22kV CB 32 |  | 2015Q2 | BRD | CB | 2015-05-15 11:05 | 2015-05-15 11:18 |  |  |  | 22 |  |  | 2015
189309 |  |  | No.1 Balranald - Balranald 22kV Line | S | 2015Q2 | BRD | TL | 2015-05-15 11:05 | 2015-05-15 11:18 |  |  |  | 22 |  |  | 2015
189310 |  |  | No.2 Balranald - Moulamein 22kV Line |  | 2015Q2 | BRD | TL | 2015-05-15 11:05 | 2015-05-15 11:18 |  |  |  | 22 |  |  | 2015
189364 | HV Equipment | CB | No.1 Transformer 330/132/11kV | E | 2015Q2 | DPT | TX | 2015-05-17 09:10 | 2015-05-17 14:36 | CB 5412 SF6 top-up. | Follow up | SF6 Topup. | 330 |  | Forced | 2015
189369 | Unknown | TL | 96R Glen Innes - Tenterfield 132kV TL | Q | 2015Q2 | GNS, TTF | TL | 2015-05-18 05:56 | 2015-05-18 05:56 | Distance to fault from TTF - 16.4km | Follow up | Successful trip and reclose, cause unknown. | 132 |  |  | 2015
189370 |  |  | 96R Glen Innes - Tenterfield 132kV TL |  | 2015Q2 | GNS, TTF | TL | 2015-05-18 05:56 | 2015-05-18 05:56 |  |  |  | 132 |  |  | 2015
189371 |  |  | 96R Glen Innes - Tenterfield 132kV TL |  | 2015Q2 | GNS, TTF | TL | 2015-05-18 05:56 | 2015-05-18 05:56 |  |  |  | 132 |  |  | 2015
189405 |  |  | 79C Griffith - Darlington Point 33kV Line |  | 2015Q2 | GRF | TL | 2015-05-18 14:20 | 2015-05-18 14:20 |  | Follow up |  | 33 |  |  | 2015
189435 | Unknown | Prot | No.1 Transformer 220/22kV | C | 2015Q2 | BRD | TX | 2015-05-19 10:09 | 2015-06-24 09:11 |  | 10/07/2015 13:20:00 ¦ Follow up ¦ Further followup 10/7/15 Nil – the scheme involved in the fault has been removed. The new BBP scheme has been separately tested and commissioned. | No1 Balranald Feeder had been opened off. All the load was on the Moulamein Feeder. It appears a fault occurred on the Moulamein Feeder, not enough to trip the Feeder. The REF scheme operated for the 22kV Bus, tripping the Transformer. No investigation was conducted. New CT's had just been installed on the Moulamein Fdr | 220 | It appears that the REF protection on the BBP maloperated. Prior to the fault, the CTs associated with the Moulamein Fdr had been replaced by contractors. This maloperation is linked to the protection changes that were occuring at the time of the upgrade. Because Balranald is currently undergoing an upgrade and the REF in the BBP scheme no longer exists, no further investigation is possible or required. | Fault | 2015
189436 | LV/MECH Fail | T/C | No.3 Transformer 330/132/11kV | E | 2015Q2 | DPT | TX | 2015-05-19 14:31 | 2015-05-19 17:55 |  |  | Graeme has repaired No3 Transformer Tapchanger MCB/Contactor. AA cancelled serviceable, however not confident it will not trip overnight. Left Transformer on standby untill tommorrow when we can place in F/P Auto and keep an eye on it. | 330 |  | Forced | 2015
189445 |  |  | 79L Griffith - Beelbangera 33kV Line |  | 2015Q2 | GRF | TL | 2015-05-19 14:49 | 2015-05-19 14:49 |  | Follow up |  | 33 |  |  | 2015
189458 |  |  | 878 Narrabri - Boggabri 66kV Line |  | 2015Q2 | NB2 | TL | 2015-05-19 19:15 | 2015-05-19 19:15 |  | Follow up |  | 66 |  |  | 2015
189459 |  |  | 893/5 Forbes - Payten's Bridge 66kV Line |  | 2015Q2 | FB2 | TL | 2015-05-20 00:37 | 2015-05-20 00:37 |  | Follow up |  | 66 |  |  | 2015
189460 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2015Q2 | BER | TL | 2015-05-20 05:15 | 2015-05-20 05:15 |  | Follow up |  | 66 |  |  | 2015
189461 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2015Q2 | BER | TL | 2015-05-20 05:15 | 2015-05-20 05:15 |  | Follow up |  | 66 |  |  | 2015
189462 |  |  | 851 Beryl - Mudgee tee Gulgong 66kV Line |  | 2015Q2 | BER | TL | 2015-05-20 05:20 | 2015-05-20 05:20 | TAR time amended | Follow up |  | 66 |  |  | 2015
189572 | HV Equipment | CB | 132kV No.1 Bus Coupler CB 4012 | Q | 2015Q2 | RGV | CB | 2015-05-20 15:25 | 2015-05-20 16:56 |  |  | SF6 Topup | 132 |  |  | 2015
189921 |  |  | No.3 Transformer 330/132/11kV | B | 2015Q2 | AR1 | TX | 2015-05-22 11:07 | 2015-05-22 15:43 |  |  |  | 330 |  | Forced | 2015
189922 |  |  | 86 Tamworth 330 - Armidale 330kV TL | B | 2015Q2 | AR1, TA1 | TL | 2015-05-22 11:07 | 2015-05-22 15:43 |  |  |  | 330 |  | Forced | 2015
189923 |  |  | 8C Armidale - Dumaresq 330kV TL | B | 2015Q2 | AR1, DMQ | TL | 2015-05-22 11:07 | 2015-05-22 15:43 |  |  |  | 330 |  | Forced | 2015
189989 |  |  | 865 Cowra - Cowra Town 66kV Line |  | 2015Q2 | CW2 | TL | 2015-05-24 07:22 | 2015-05-24 07:22 | Line to open point within customer system. Weather fine (fog) at time of event. Protection details to be provided. | Follow up |  | 66 |  |  | 2015
189993 | LV/MECH Fail | CB | 873 Tamworth132 - East Tamworth 66kV Line | Q | 2015Q2 | TMW | TL | 2015-05-25 04:58 | 2015-05-25 05:23 | 8732 TARTLO at TransGrid end. 873 energised from Essential Energy end. Feeder placed on load at 0523hrs | 21/07/2015 11:18:00 ¦ Follow up ¦ Nil | A fault occurred on 873 feeder which resulted in the line remaining energised from the Essential Energy end only. Staff were called out to Tamworth 132kV SS to investigate. A review of protection flagging and CB operations counters indicated CB8732 should have tripped and reclosed. Operations staff closed CB873 manually to place the feeder on load at 0523hrs. CB873 is a 66kV Delle HPGE 9/12 CB. These CBs have a history of maloperation due to mechanism problems. The Delle CBs at Tamworth 132kV SS are being lubricated on a 12 month basis to reduce the risk of maloperation until they are replaced. Tamworth 132kV SS is currently being re-built and the Delle CBs should be decommissioned within 12 months. | 66 |  |  | 2015
190069 |  |  | Broken Hill - South 22kV Line |  | 2015Q2 | BKH | TL | 2015-05-25 17:26 | 2015-05-25 18:37 |  | Follow up |  | 22 |  |  | 2015
190072 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2015Q2 | MRE | TL | 2015-05-26 06:28 | 2015-05-26 06:33 | No attempt at auto reclose due to current planned outage to disable reclose for Essential Energy. Line energised via SCADA at request of Essential Energy after verifying no Access Authorities are issued within their system. | Follow up |  | 66 |  |  | 2015
190156 |  |  | 828 Mt Piper 132 - Portland tee BCSC 66kV Line |  | 2015Q2 | MPP | TL | 2015-05-27 06:17 | 2015-05-27 06:17 |  | Follow up |  | 66 |  |  | 2015
190194 |  |  | 330kV A Bus |  | 2015Q2 | CWF | BB | 2015-05-27 11:34 | 2015-05-27 14:33 | Capital wind Farm staff advised they failed to open trip links while carrying out protection maintenance on their transformers. | Follow up |  | 330 |  |  | 2015
190195 |  |  | 3W Kangaroo Valley A CB 3W2A |  | 2015Q2 | CWF | CB | 2015-05-27 11:34 | 2015-05-27 14:33 |  |  |  | 330 |  |  | 2015
190196 |  |  | 6 Canberra A CB 62A |  | 2015Q2 | CWF | CB | 2015-05-27 11:34 | 2015-05-27 14:33 |  |  |  | 330 |  |  | 2015
190197 |  |  | 330kV C Bus |  | 2015Q2 | CWF | BB | 2015-05-27 11:34 | 2015-05-27 14:33 |  |  |  | 330 |  |  | 2015
190208 |  |  | 96F Stroud - Tomago 330 132kV TL | X | 2015Q2 | TOM | TL | 2015-06-10 10:25 | 2015-06-10 15:50 |  |  |  | 132 |  |  | 2015
190215 |  |  | 9C8 Brandy Hill - Stroud 132kV TL | X | 2015Q2 | SRD, BRH | TL | 2015-06-18 08:12 | 2015-06-18 16:06 |  |  |  | 132 |  |  | 2015
190309 |  |  | 957 Vales Pt - Ourimbah tee Morisset 132kV Line |  | 2015Q2 | VP1 | TL | 2015-05-28 14:23 | 2015-05-29 21:51 |  | Follow up |  | 132 |  |  | 2015
190372 |  |  | L1 Lower Tumut - Tumut 3 330kV TL | Y | 2015Q2 | LT1, TP3 | TL | 2015-05-29 12:32 | 2015-05-30 16:24 |  |  |  | 330 |  |  | 2015
190376 | HV Equipment | SVC | No.1 Static VAR Compensator | B | 2015Q2 | LSM | SVC | 2015-05-29 10:35 | 2015-05-29 13:14 |  |  | INVESTIGATE NON CRITICAL THYRISTOR ALARM. | 132 |  | Forced | 2015
190481 |  |  | 95A Newcastle - Awaba 132kV Line |  | 2015Q2 | NEW | TL | 2015-05-29 12:58 | 2015-05-29 12:58 |  | Follow up |  | 132 |  |  | 2015
190601 |  |  | 97L Guthega - Jindabyne Pumps 132kV TL | X | 2015Q2 | GTH, JDP | TL | 2015-06-19 10:18 | 2015-06-19 13:41 |  |  |  | 132 |  |  | 2015
190603 |  |  | O97B Tumut - Blowering 132kV TL | X | 2015Q2 | TU2 | TL | 2015-06-29 07:53 | 2015-07-09 15:51 |  |  |  | 132 |  |  | 2015
190622 | HV Equipment | Aux Tx | No.1 Transformer 330/132/16kV | E | 2015Q2 | SE1 | TX | 2015-06-02 02:08 | 2015-06-02 14:34 |  |  | Tx de-energised immediately after buchholz alarm received. Alarm caused by low oil in No.1 Aux Transformer. | 330 |  | Forced | 2015
191061 |  |  | 9C8 Brandy Hill - Stroud 132kV TL | B | 2015Q2 | SRD, BRH | TL | 2015-06-04 06:34 | 2015-06-04 18:11 |  |  |  | 132 |  | Forced | 2015
191290 | Relay | Prot | 132kV B Bus Section 2 | Q | 2015Q2 | NEW | BB | 2015-06-03 13:04 | 2015-06-03 14:54 |  | Follow up | Advised that No4 TX No1 Prot is faulty and continues to output trips and is the cause of bus trip. Requested to reset BBP. Advised No4 TX No1 prot trip alarm and all LEDs are flashing looks like relay fault. | 132 | No4 Tx at NEW had been removed and the No4 Tx Protetion was only protecting the 132kV Bus Coupler. The faulty T60 relay on the No4 Tx No1 protection is the cause of the busbar trip. The relay was replaced 05/06/2015. Awaiting Relay to return from manufacturer with associated fault report. |  | 2015
191291 |  |  | No.3 Transformer 132kV B Bus CB 4432B |  | 2015Q2 | NEW | CB | 2015-06-03 13:04 | 2015-06-03 14:54 |  |  |  | 132 |  |  | 2015
191292 |  |  | No.4 Transformer 132kV B Bus CB 4442B |  | 2015Q2 | NEW | CB | 2015-06-03 13:04 | 2015-06-03 14:54 |  |  |  | 132 |  |  | 2015
191293 |  |  | No.4 Capacitor | Z | 2015Q2 | NEW | CAP | 2015-06-03 13:04 | 2015-06-03 14:54 |  |  |  | 132 |  | Fault | 2015
191294 |  |  | 132KV B Bus 1-2 Section CB 4122 |  | 2015Q2 | NEW | CB | 2015-06-03 13:04 | 2015-06-03 14:54 |  |  |  | 132 |  |  | 2015
191295 |  |  | 96B Newcastle - Capral 132kV Line |  | 2015Q2 | NEW | TL | 2015-06-03 13:04 | 2015-06-03 14:54 |  |  |  | 132 |  |  | 2015
191296 |  |  | 961 Newcastle - Merewether Tee Argenton 132kV Line |  | 2015Q2 | NEW | TL | 2015-06-03 13:04 | 2015-06-03 14:54 |  |  |  | 132 |  |  | 2015
191298 |  |  | No.4 Transformer 132kV A Bus CB 4442A | Q | 2015Q2 | NEW | CB | 2015-06-03 12:57 | 2015-06-05 15:12 |  | Follow up |  | 132 |  |  | 2015
191309 |  |  | No.9 Yanco - Leeton (No.9 Council) 33kV Line |  | 2015Q2 | YA2 | TL | 2015-06-03 21:01 | 2015-06-03 21:01 |  | Follow up |  | 33 |  |  | 2015
191956 | HV Equipment | TL | 9W3 Coffs Harbour - Raleigh 132kV TL | B | 2015Q2 | COF, RAL | TL | 2015-06-05 08:02 | 2015-06-05 10:08 |  |  | OHEW repair Coffs to str 178. | 132 |  | Forced | 2015
192279 |  |  | 735 Inverell - Inverell 66kV Line |  | 2015Q2 | INV | TL | 2015-06-04 13:24 | 2015-06-04 13:24 | Customer advised Trip and successful auto reclose with associated voltage depression within it's system. No SCADA monitoring or alarms received, supporting customer advice of trip and reclose. | Follow up |  | 66 |  |  | 2015
192822 |  |  | 93B Liverpool - West Liverpool 132kV Line |  | 2015Q2 | LP1 | TL | 2015-06-07 06:36 | 2015-06-07 12:22 | Line de-energisesd at request of customer. | Follow up |  | 132 |  |  | 2015
192828 | HV Equipment | CB | No.2 Transformer 132kV B CB 4422B | Q | 2015Q2 | SE1 | CB | 2015-06-07 13:51 | 2015-06-07 15:40 |  |  | CB SF6 Topup | 132 |  |  | 2015
192832 |  |  | 98W Dapto - Mt Terry 132kV Line |  | 2015Q2 | DPT | TL | 2015-06-08 10:22 | 2015-06-08 16:38 | Trip, auto reclose, trip and lockout. Customer advises windy conditions locally. Staff proceeding to site at time of report preparation. | Follow up |  | 132 |  |  | 2015
192918 | Consequential | TX | No.1 Transformer 330/132/11KV | B | 2015Q2 | CA1 | TX | 2015-06-10 08:32 | 2015-06-10 11:09 |  |  | Outage for safety clearance for the removal of No.1 TX 330kV surge arrestor footings. | 330 |  | Forced | 2015
193280 |  |  | 875 Wallerawang 132 - Oakey Park 66kV Line |  | 2015Q2 | WWS | TL | 2015-06-10 19:35 | 2015-06-10 19:35 |  | Follow up |  | 66 |  |  | 2015
193448 |  |  | 866 Ingleburn - Bow Bowing 66kV Line |  | 2015Q2 | ING | TL | 2015-06-12 03:36 | 2015-06-12 03:36 | SO/Endeavour advised CB did not close at Bow Bowing and was closed via SCADA, confirmed no customer load lost. | Follow up |  | 66 |  |  | 2015
193894 | Unknown | TL | 944 Orange North - Wallerawang 132kV TL | Q | 2015Q2 | ONO, WWS | TL | 2015-06-15 20:56 | 2015-06-15 20:56 | Transmission line later requested out of service by Manager/Network Operations. Refer to Emergency Outage Report 2015-E-0027. | 23/07/2015 13:57:00 ¦ Follow up ¦ Nil ¦ Nil | Orange Mains staff conducted an after fault patrol of structures 120 - 140 as well as road crossings from of structures 100 - 170 on 16 June 2015. From this patrol no defects were identified. | 132 |  |  | 2015
193895 | Unknown | TL | 944 Orange North - Wallerawang 132kV TL | E | 2015Q2 | ONO, WWS | TL | 2015-06-15 23:47 | 2015-06-16 13:35 | Outage requested by Manager/Network Operations following TAR event (refer to FEOR 2015-F-0277). 944 was patrolled and RTS after no conclusive evidence of trip. | Follow up | 944 Wallerawang132 New to Orange North 132 kV T/L taken out of service following discussion with Andrew Kingsmill. Concerns raised as to condition of wood poles. AEMO advised. No system issues at this time. Protection details from Orange North indicate Blue phase to earth fault, 67km from Orange. Mains staff to be advised and requested to patrol in the morning. Advised patrol completed from ST 100 - 170 and all okay no damage found and clearance given to RTS 944, advised NCM, clearance given to RTS | 132 |  | Forced | 2015
193958 | Unknown | TL | 99K Darlington Pt - Griffith 132kV TL | Q | 2015Q2 | DNT, GRF | TL | 2015-06-16 11:28 | 2015-06-16 11:28 |  | 4/08/2015 09:00:00 ¦ Follow up ¦ Nil ¦ Nil | Successful trip and reclose. Cause unknown. | 132 |  |  | 2015
193981 |  |  | 18 Dapto - Kangaroo Valley 330kV TL | X | 2015Q2 | DPT, KVS | TL | 2015-06-29 07:31 | 2015-06-29 16:40 |  |  |  | 330 |  |  | 2015
193996 |  |  | 82B Queanbeyan - High St 66kV Line |  | 2015Q2 | QBY | TL | 2015-06-16 16:54 | 2015-06-16 16:54 |  | Follow up |  | 66 |  |  | 2015
194032 |  |  | 96B Newcastle - Capral 132kV Line |  | 2015Q2 | NEW | TL | 2015-06-17 10:03 | 2015-06-17 10:03 | Distance to fault - 12.5km | Follow up |  | 132 |  |  | 2015
194152 |  |  | 925 Sydney East - Willoughby T Castle Cove & Mosman 132kV Line |  | 2015Q2 | SE1 | TL | 2015-06-17 20:03 | 2015-06-20 16:50 |  | Follow up |  | 132 |  |  | 2015
194311 | LV/MECH Fail | SVC | No.1 Static VAR Compensator | E | 2015Q2 | SYW | SVC | 2015-06-19 14:29 | 2015-06-19 17:44 |  |  | Requested to take O/O/S #1 SVC at Sydney West. Control system inverter replaced. | 330 | SSAM - The control system inverter supplying the SVC HMI failed. The faulty unit was replaced with a new unit. | Forced | 2015
194319 | Unknown | Cap | No.2 Capacitor | Z | 2015Q2 | SYN | CAP | 2015-06-19 14:02 | 2015-11-26 15:10 |  | Follow up | At 14:02hrs #2 Cap at Sydney North 330kV Substation tripped on 'B' Phase Neutral Unbalance. Cause unknown. Staff to investigate. | 132 | SSAM - Both Protections operated indicating that there was a genuine fault therefore no secondary systems investigation. Substations checked for can failures. 351245 was created on 27/06/2015 to investigate the cause of this trip. The work order is still open. The work order extended text mentions that follow up is required to test cans and protection. The required by date in Ellipse is 25/09/2015. [Update 16/12/2015] Caps to be removed, needs statement created. | Fault | 2015
194334 |  |  | 837 Murrumburrah - Jugiong 66kV Line |  | 2015Q2 | MRU | TL | 2015-06-20 13:28 | 2015-06-21 15:07 |  | Follow up |  | 66 |  |  | 2015
194335 | Unknown | TL | 968 Tamworth 330 - Narrabri 132kV TL | Q | 2015Q2 | NB2, TA1 | TL | 2015-06-21 06:53 | 2015-06-21 06:53 |  | Follow up | At 06:53hrs 968 Tamworth330 to Narrabri132 132 kV T/L tripped and reclosed. Cause unknown | 132 |  |  | 2015
194336 | HV Equipment | CB | 238 Regentville - Penrith 132kV Line | Q | 2015Q2 | RGV | TL | 2015-06-21 12:14 | 2015-06-21 12:47 |  |  | CB SF6 Topup | 132 | Work order No. 355583 was created on 30/06/2015 and SF6 was topped up. Work order closed. |  | 2015
194361 | Unknown | TL | 963 Tomago330 - Taree T Hawksnest 132kV TL | Q | 2015Q2 | TRE, TOM | TL | 2015-06-22 08:37 | 2015-06-22 08:37 | Protection details for Taree added. Interruption to Hawks Nest (Essential Energy) for reclose time only. Ausgrid advised. (shared line ownership to str. 184 from Tomago 330kV Switchyard) DTF from Tomago 330 139.7km. | Follow up | Successful trip and reclose, cause unknown. | 132 |  |  | 2015
194484 | Condition Monitor | TX | No.3 Transformer 330/132/11kV | E | 2015Q2 | WRH | TX | 2015-06-23 05:01 | 2015-06-23 07:54 | Condition Monitoring L1 alarm received on scada. No.3 transformer de-nergised. | Follow up | Condition Monitoring L1 alarm received on scada. No.3 transformer de-energised. Alarm condition possibly caused by Coronal Mass Ejection. Ken & Tony Gray have given formal clearance to RTS NO.3 Tx at Waratah West follow the L1 alarm. | 330 |  | Forced | 2015
194521 |  |  | No.3 Capacitor | B | 2015Q2 | CA1 | CAP | 2015-06-23 11:53 | 2015-06-23 14:04 |  |  |  | 132 |  | Forced | 2015
194667 |  |  | 873 Tamworth132 - East Tamworth 66kV Line |  | 2015Q2 | TMW | TL | 2015-06-25 05:01 | 2015-06-25 05:01 | Advised by Essential Energy. 25/6/15 at 1100hrs - APIC confirmed no protection or CB operated at Tamworth 132. 25/6/15 at 0800 - Prot'n details faxed to control room, however no phone conversation to indicate details sent and relays reset. DTF 3.76km, EE advised. | Follow up |  | 66 |  |  | 2015
194830 | Relay | Prot | No.4 Capacitor | E | 2015Q2 | CA1 | CAP | 2015-06-29 21:10 | 2015-07-03 11:37 | Cap was out of service when protection alarmed Tech/P advised No.4 Capacitor No.1 protection relay is faulty and needs to be replaced. | Follow up | Cap was out of service when protection alarmed Tech/P advised No.4 Capacitor No.1 protection relay is faulty and needs to be replaced. | 132 | C70 relay on No1 Protection was found to be faulty. The analogue card F8N CT/VT has been replaced. | Forced | 2015
195110 | HV Equipment | CB | 932 Sydney West - Mt Druitt 132kV Line | E | 2015Q2 | SYW | TL | 2015-06-30 14:17 | 2015-06-30 15:19 |  |  | CB SF6 Topup | 132 | Couldn't find work order number for this work. Raised this issue with Tim Blair and waiting for his response. | Forced | 2015
195135 | Damaged Cable | Other | 330kV A Bus 1-2 Section CB 5102 | Q | 2015Q3 | SYW | CB | 2015-07-01 04:01 | 2015-07-01 11:38 | de-energised after receivingd HV abnorma. Further investigation required. Investigation revealed alarms caused by redundant cabling laying in water. cabling identified and removed | Follow up | De-energised after receivingd HV abnormal. Further investigation required. Investigation revealed alarms caused by redundant cabling laying in water. Cabling identified and removed. | 330 | Work order No. 355717 was created on 01/07/2015 to disconnect redundant cabling. Work order closed now. |  | 2015
195175 | HV Equipment | CB | 238 Regentville - Penrith 132kV Line | Q | 2015Q3 | RGV | TL | 2015-08-28 10:51 | 2015-08-28 12:41 |  |  | CB2832 SF6 Topup. | 132 | No work order is created in Ellipse yet. To be checked with Tim Blair. This CB has very high frequency of SF6 top ups. Update 17/09/2015: CB topped up under workorder No. 355837. Workorder is closed now. |  | 2015
195207 | Relay | Prot | 36 Marulan - Bannaby 330kV TL | Z | 2015Q3 | MRN, BBY | TL | 2015-07-02 07:42 | 2015-07-02 19:06 | Weather tools indicate no storm activitiy. Switchgear condition good. Beleived to be faulty No.1 Protection Relay at Bannaby. Confirmed faulty No.1 Protection relay and relay replaced. Line RTS @ 1906 hours via SCADA. | Follow up | Weather tools indicate no storm activitiy. Switchgear condition good. Beleived to be faulty No.1 Protection Relay at Bannaby. Confirmed faulty No.1 Protection relay and relay replaced. Line RTS @ 1906 hours via SCADA. | 330 | The analogue card in the D60/2 was found to be faulty. With no source connected, the relay was reading current. The relay was replaced with a D60/3. | Fault | 2015
195208 | Relay | Prot | 330kV B Bus | Q | 2015Q3 | BBY | BB | 2015-07-02 07:50 | 2015-07-02 10:29 | Weather tools indicate no storms at time of trip. Manager Network Operations - Andrew Kingsmill Advised Trip believed to be caused by 36 T/L No.1 Protection Protections reset, Switchgear condition OK. | Follow up | Weather tools indicate no storms at time of trip. Manager Network Operations - Andrew Kingsmill Advised Trip believed to be caused by 36 T/L No.1 Protection Protections reset, Switchgear condition OK. | 330 | This FEOR is associated with FEOR 2015-F-0287. |  | 2015
195209 |  |  | 36 Marulan CB 362 |  | 2015Q3 | BBY | CB | 2015-07-02 07:50 | 2015-07-02 10:29 |  |  |  | 330 |  |  | 2015
195210 |  |  | 61 Yass CB 612 |  | 2015Q3 | BBY | CB | 2015-07-02 07:50 | 2015-07-02 10:29 |  |  |  | 330 |  |  | 2015
195211 |  |  | 35 Marulan B CB 352B |  | 2015Q3 | BBY | CB | 2015-07-02 07:50 | 2015-07-02 10:29 |  |  |  | 330 |  |  | 2015
195212 |  |  | 39 Sydney West B CB 392B |  | 2015Q3 | BBY | CB | 2015-07-02 07:50 | 2015-07-02 10:29 |  |  |  | 330 |  |  | 2015
195497 | HV Equipment | CB | 5A1 Eraring B CB 5A12B | Q | 2015Q3 | KCR | CB | 2015-07-04 14:09 | 2015-07-04 16:58 |  |  | CB SF6 Topup. | 500 | Work order No. 357662 was created on 14/07/2015. CB topped up and work order closed now. |  | 2015
195498 | LV/MECH Fail | CB | No.1 330kV Generator CB 5212 | Q | 2015Q3 | MTP | CB | 2015-07-05 08:25 | 2015-07-05 10:10 |  |  | Short notice outage to investigate suspect hydraulic pump over-run. | 330 | Work order No. 357478 was created on 10/07/2015. CB was reset and work order closed now. |  | 2015
195611 |  |  | 848 Tumut - Tumbarumba tee Batlow tee Adelong 66kV Line |  | 2015Q3 | TU2 | TL | 2015-07-06 20:49 | 2015-07-06 23:46 | Note: approx 7MW of customer load lost for duration of the outage 20:49 hrs to 23:45hrs Customer advises two phase supply only after previous TAR event. CB 8482 opened at request of customer via SCADA. Request for I&E of line received. | Follow up |  | 66 |  |  | 2015
195612 |  |  | 848 Tumut - Tumbarumba tee Batlow tee Adelong 66kV Line |  | 2015Q3 | TU2 | TL | 2015-07-06 20:43 | 2015-07-06 20:43 | Concurrent substation alarms initiated. Customer request to de-energise received approximately 5 minutes after event. See corresponding Emergency Outage Report. | Follow up |  | 66 |  |  | 2015
196252 | HV Equipment | CB | No.1 Transformer 132/33/11kV | E | 2015Q3 | TRE | TX | 2015-07-09 09:04 | 2015-07-09 11:36 |  |  | CB 2412 SF6 Topup | 132 |  | Forced | 2015
196257 | LV/MECH Fail | CB | No.3 Transformer 330/220/33kV | B | 2015Q3 | DNT | TX | 2015-07-09 12:31 | 2015-07-09 14:59 |  |  | Outage to investigate CB7432 motor spring charging. | 330 | Work order No. 357465 was created on 10/07/2015 to investigate this issue. A small screw from terminal block had fallen into gear mechanism. The screw is removed now and CB tested and works OK. Work order closed now. | Forced | 2015
196509 | Animal/Bird | Insulator | No.2 Transformer 132/66/11kV | Z | 2015Q3 | TU2 | TX | 2015-07-10 07:21 | 2015-07-10 14:36 | Dislodged birds nest above 66kv underslung insulators above 66 kv CT’s RED and WHITE Phase’s. Raining and pollution helped cause trip. Advised by Will Kroker. | 29/07/2015 09:35:00 ¦ Follow up ¦ At this time of year nest building is an ongoing hazard. ¦ Continued monitoring of sites for birds nests. | Dislodged birds nest above 66kv underslung insulators above 66 kv CT’s RED and WHITE Phase’s. Raining and pollution helped cause trip. Advised by Will Kroker. | 132 | Work order No. 357472 was created on 10/07/2015 to investigiate this issue. Options for stopping this happening again are being considered. Work order still open. | Fault | 2015
196541 |  |  | 847 Murrumburrah - Boorowa 66kV Line |  | 2015Q3 | MRU | TL | 2015-07-11 07:14 | 2015-07-11 12:15 | Essential advised found a broken Crossarm | Follow up |  | 66 |  |  | 2015
196543 |  |  | 828 Tumut - Gundagai 66kV Line |  | 2015Q3 | TU2 | TL | 2015-07-11 13:38 | 2015-07-11 13:38 |  | Follow up |  | 66 |  |  | 2015
196557 | Lightning/Storm | TL | 64 Lower Tumut - Upper Tumut 330kV TL | Q | 2015Q3 | LT1, UT1 | TL | 2015-07-11 17:19 | 2015-07-11 17:19 | CB..642A closed via SCADA | 10/08/2015 08:25:00 ¦ Follow up ¦ Nil ¦ Nil | Successful trip and reclose. Storms in the area. | 330 |  |  | 2015
196558 |  |  | 64 UPPER TUMUT 330KV A BUS CB BAY |  | 2015Q3 | LT1 | CB | 2015-07-11 17:19 | 2015-07-11 17:19 |  |  |  | 330 |  |  | 2015
196559 |  |  | 64 UPPER TUMUT 330KV B BUS CB BAY |  | 2015Q3 | LT1 | CB | 2015-07-11 17:19 | 2015-07-11 17:19 |  |  |  | 330 |  |  | 2015
196560 | Unknown | CB | O7 Lower Tumut - Canberra 330kV TL | Z | 2015Q3 | CA1, LT1 | TL | 2015-07-11 17:19 | 2015-07-11 17:23 | 1. O7 Lower Tumut - Canberra 330kV TL Opend at Canberra end only at the same time that 64 Lower Tumut - Upper Tumut 330kV TL tripped and reclosed 2. O7 Lower Tumut - Canberra 330kV TL A and B CB's Closed via SCADA at Canberra 3. John Hicks advised trip of O7 Lower Tumut - Canberra 330kV TL at Canberra 330 was caused due to Memory timer had not been energised and this made zone 3 instant and O7 Lower Tumut - Canberra 330kV TL tripped at Canberra 330 on a Zone 3. further investigation indicates that the memory timer in now energised, believes it was a pallet switch issue and the CB operation at canberra reset the pallets | Follow up | 1. O7 Lower Tumut - Canberra 330kV TL Opend at Canberra end only at the same time that 64 Lower Tumut - Upper Tumut 330kV TL tripped and reclosed 2. O7 Lower Tumut - Canberra 330kV TL A and B CB's Closed via SCADA at Canberra 3. John Hicks advised trip of O7 Lower Tumut - Canberra 330kV TL at Canberra 330 was caused due to Memory timer had not been energised and this made zone 3 instant and O7 Lower Tumut - Canberra 330kV TL tripped at Canberra 330 on a Zone 3. Further investigation indicates that the memory timer in now energised, believes it was a pallet switch issue and the CB operation at canberra reset the pallets. | 330 | Memory timer to be removed with the upcoming replacement of the protection panels. | Fault | 2015
196561 | Lightning/Storm | TL | O51 Lower Tumut - Wagga 330kV TL | Q | 2015Q3 | LT1, WG1 | TL | 2015-07-11 19:09 | 2015-07-11 19:09 | Lower Tumut CB O512A closed manually via SCADA. | 10/08/2015 08:23:00 ¦ Follow up ¦ Nil ¦ Nil | Successful trip and reclose. Storms in the area. | 330 |  |  | 2015
196562 |  |  | O51 Lower Tumut 330kV CB 0512 |  | 2015Q3 | WG1 | CB | 2015-07-11 19:09 | 2015-07-11 19:09 |  |  |  | 330 |  |  | 2015
196563 |  |  | 051 WAGGA 330KV A BUS CB BAY |  | 2015Q3 |  | CB | 2015-07-11 19:09 | 2015-07-11 19:09 |  |  |  | 330 |  |  | 2015
196564 |  |  | 051 WAGGA 330KV B BUS CB BAY |  | 2015Q3 |  | CB | 2015-07-11 19:09 | 2015-07-11 19:09 |  |  |  | 330 |  |  | 2015
196565 |  |  | 94F Wellington - Dubbo 132kV Line |  | 2015Q3 | WL1 | TL | 2015-07-11 19:48 | 2015-07-11 19:48 |  | Follow up |  | 132 |  |  | 2015
196566 |  |  | 82K/1 Queanbeyan - Bungendore tee Sutton 66kV Line |  | 2015Q3 | QBY | TL | 2015-07-11 20:17 | 2015-07-11 20:17 |  | Follow up |  | 66 |  |  | 2015
196567 |  |  | 82K/1 Queanbeyan - Bungendore tee Sutton 66kV Line |  | 2015Q3 | QBY | TL | 2015-07-11 20:25 | 2015-07-11 20:25 |  | Follow up |  | 66 |  |  | 2015
196568 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2015Q3 | BER | TL | 2015-07-11 20:46 | 2015-07-11 20:46 |  | Follow up |  | 66 |  |  | 2015
196569 | Lightning/Storm | TL | 94M Mt Piper 132 - Beryl tee Mudgee tee Ilford 132kV TL | Q | 2015Q3 | BER, MPP | TL | 2015-07-11 21:19 | 2015-07-11 21:19 | DTF from Bery,l No.1 Prot'n - 67.15 kms, No2 Prot'n - 65.87 kms | 4/08/2015 08:50:00 ¦ Follow up ¦ A defect has been created for the replacements of the structures insulator strings. | Successful trip and reclose. Storms in the area. | 132 |  |  | 2015
196570 |  |  | 823 Wallerawang 132 - Portland 66kV Line |  | 2015Q3 | WWS | TL | 2015-07-11 21:44 | 2015-07-11 21:44 |  | Follow up |  | 66 |  |  | 2015
196571 |  |  | 665 Armidale - Armidale 66kV Line |  | 2015Q3 | AR1 | TL | 2015-07-12 03:44 | 2015-07-12 05:37 | 665 T/L returned to service at Essential Energy's request upon completion of ine patrol | Follow up |  | 66 |  |  | 2015
196572 |  |  | 665 Armidale - Armidale 66kV Line |  | 2015Q3 | AR1 | TL | 2015-07-12 06:21 | 2015-07-12 15:21 |  | Follow up |  | 66 |  |  | 2015
196575 |  |  | 7L3 Yanco - Kamarah 33kV Line |  | 2015Q3 | YA2 | TL | 2015-07-12 10:11 | 2015-07-12 10:11 |  | Follow up |  | 33 |  |  | 2015
196576 | Tree/Ground | TL | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2015Q3 | GTH, MUR, GHI | TL | 2015-07-12 23:04 | 2015-07-18 13:21 | Heavy snow and storms in area at time of event. Guthega restored via Munyang. 97G 132kV T/L to remain out of service pending site inspection and line patrol during daylight hours. | 10/08/2015 08:29:00 ¦ Follow up ¦ D2015/09113 ¦ Nil ¦ Site rehabilitation post winter 2015. | Heavy snow and storms in area at time of event. Guthega restored via Munyang. 97G 132kV T/L to remain out of service pending site inspection and line patrol during daylight hours. Helicopter Patrol on Tuesday 14 July 2015 identified a tree had fallen and broken the left hand conductor on span 100 around midspan and structure 101 was leaning in the 97G/3 section of line. On Thursday 16 July 2015, Transmission Lines maintenance staff accessed the site and inspected. Confirmed the structure was suitable to stabilise/straighten and conductor could be repaired. On Friday 17 July 2015, the conductor was repaired and structure 101 was straightened. The line was restored to service on Saturday 18 July 2015. | 132 | Off easement tree. Conductor and structure repaired. Site remediation not possible at time of repair due to snow. Remediation planned for completion by end of December. No further action by TL&C Asset Mgr. | Fault | 2015
196577 |  |  | 97G/3 Geehi Tee CB 97G2 |  | 2015Q3 | GTH | CB | 2015-07-12 23:04 | 2015-07-18 13:21 |  |  |  | 132 |  |  | 2015
196578 |  |  | 97G/1 Geehi Tee CB 97G2 |  | 2015Q3 | MUR | CB | 2015-07-12 23:04 | 2015-07-18 13:21 |  |  |  | 132 |  |  | 2015
196592 |  |  | Station Transformer 1A |  | 2015Q3 | LD1 | TX | 2015-07-13 09:02 | 2015-07-14 09:29 | Fire in CB 0412 caused the ST TX 1A to trip | Follow up |  | 330 |  |  | 2015
196593 | HV Equipment | ESW | 1F Holroyd - Sydney West 330kV TL | B | 2015Q3 | SYW, HLD | TL | 2015-07-13 13:59 | 2015-07-13 17:12 |  |  | Advised while switching on HVPRI 59982 to Isolate and Earth 1F Holroyd B CB..1FB2 the 1F Holroyd B CB Earthing switch ..1F0/B2 - failed to close on all 3 phases and can not be opened. | 330 | Work order No. 357633 was created on 14/07/2015 to investigate this issue. Earth switch operational and ancillary maintenance was completed. Work order closed now. | Forced | 2015
196616 |  |  | 840 Wagga 132 - Lockhart 66kV Line |  | 2015Q3 | WG2 | TL | 2015-07-13 13:48 | 2015-07-13 17:19 | Essential advised possable wires down Customer load restored in essential energy system at 15:48hrs | Follow up |  | 66 |  |  | 2015
196617 |  |  | No.2 330kV Generator Transformer Group |  | 2015Q3 | LD1 | TX | 2015-07-13 08:54 | 2015-07-15 12:27 | Generator trip - unit parked | Follow up |  | 330 |  |  | 2015
196969 |  |  | No.3 Tenterfield - Council (Timbarra Mine) 22kV Line |  | 2015Q3 | TTF | TL | 2015-07-17 08:02 | 2015-07-17 10:47 | EE report 11kV fault on a shared structure within EE system Snow & Wind | Follow up |  | 22 |  |  | 2015
197092 | Unknown | CB | 889 Spare CB 8892 | Q | 2015Q3 | WG2 | CB | 2015-07-19 13:39 | 2015-07-23 15:31 | No SCADA visibility of site. Field staff advise CB 8892 open with No.1 protection operation only. Essential Energy report multiple alarms from within it's system. Uranquinty fault recorder operated indicates voltage depression of 30% blue phase. Field staff investigating at time of report. | Follow up | Advised C.B. 8892 found in tripped condition. Protection operation No.1 scheme only (phase to phase) fault. HVOD status confirmed visulally at site. Uranquinty fault recorder operated indicates voltage depression of 30% blue phase. Reports loud explosive type sound emanating from site at time of alarm receipt. Staff called out confirmed CB has opened and leaking oil. All oil has been contained and CB isolated and earthed pending further investigation. | 66 | Work order No. 358036 was created on 20/07/2015 to investigate this issue. The probable cause of the trip is magpie nest building. Work order closed now |  | 2015
197158 | Unknown | TL | 963 Tomago330 - Taree T Hawksnest 132kV TL | Q | 2015Q3 | TRE, TOM | TL | 2015-07-20 15:17 | 2015-07-20 15:17 | Essential Energy advised DTF information 200km from Hawkes Nest | Follow up | Successful trip and reclose during rainy weather. | 132 |  |  | 2015
197166 | Animal/Bird | Other | No.2 Transformer 132/66/11kV | B | 2015Q3 | TU2 | TX | 2015-07-21 13:36 | 2015-07-21 15:36 |  |  | Bird nest removed from 66kV gantry and bird deterrent installed. | 132 | Work order No. 357472 was created on 10/07/2015 to investigiate this issue. Checked No.2 TX , magpie had made a nest on 66kv side above the CTs. raining , cleaned up , bird still making nest after removing, follow up required. Work order closed now. | Forced | 2015
197196 |  |  | 6501 Koolkhan - Casino 66kV Line |  | 2015Q3 | KLK | TL | 2015-07-21 10:07 | 2015-07-21 15:06 | No customer load lost as Casino is currently being supplied from 96L TL. Essential Energy line patrol found broken cross-arm 37 km out from Koolkhan. | Follow up |  | 66 |  |  | 2015
197357 |  |  | 82G Queanbeyan - Captains Flat 66kV Line |  | 2015Q3 | QBY | TL | 2015-07-22 13:08 | 2015-07-22 15:54 | 13:09 SO/Ess Paul advised -confirmed 1.91 MW 13:36 SO/Ess approx 1MW customer load restored via customer system | Follow up |  | 66 |  |  | 2015
197694 |  |  | 735 Inverell - Inverell 66kV Line |  | 2015Q3 | INV | TL | 2015-07-12 20:40 | 2015-07-12 20:40 | No SCADA monitoring or alarms received, supporting customer advice of trip and reclose. | Follow up |  | 66 |  |  | 2015
197696 | Lightning/Storm | TL | 97K Cooma - Munyang tee Snowy Adit 132kV TL | Q | 2015Q3 | CMA, MNY | TL | 2015-07-26 10:44 | 2015-07-26 10:44 |  | Follow up | Successful trip and reclose. Storms reported in area. | 132 |  |  | 2015
197697 |  |  | 97K Cooma tee Snowy Adit 132kV CB 97K2 |  | 2015Q3 | MNY | CB | 2015-07-26 10:44 | 2015-07-26 10:44 |  |  |  | 132 |  |  | 2015
197698 |  |  | 97K Munyang tee Snowy Adit CB 97K2 |  | 2015Q3 | CMA | CB | 2015-07-26 10:44 | 2015-07-26 10:44 |  |  |  | 132 |  |  | 2015
197699 | Lightning/Storm | TL | 97K Cooma - Munyang tee Snowy Adit 132kV TL | Q | 2015Q3 | CMA, MNY | TL | 2015-07-26 10:57 | 2015-07-26 10:57 |  | Follow up | Successful trip and reclose. Storms reported in area. | 132 |  |  | 2015
197700 |  |  | 97K Cooma tee Snowy Adit 132kV CB 97K2 |  | 2015Q3 | MNY | CB | 2015-07-26 10:57 | 2015-07-26 10:57 |  |  |  | 132 |  |  | 2015
197701 |  |  | 97K Munyang tee Snowy Adit CB 97K2 |  | 2015Q3 | CMA | CB | 2015-07-26 10:57 | 2015-07-26 10:57 |  |  |  | 132 |  |  | 2015
197702 | Unknown | TL | 97K Cooma - Munyang tee Snowy Adit 132kV TL | Z | 2015Q3 | CMA, MNY | TL | 2015-07-26 11:03 | 2015-07-26 21:16 | Confirmed that Essental customer load restored via Auto Change over scheme at Munyang and advised that Munyang is supplied from Murray via 97G Note: 97L Guthega - Jindabyne Pumps 132kV TL tripped at the same time | Follow up | Trip, auto-reclose, tripped and locked out. Storms in the area. 97L tripped at the same time. | 132 | 97K tripped four times within 19 minutes. Each time three of the four protections on 97K operated. The fourth protection, i.e. No2 Prot THR at MNY, did not operate. Checks on this protection by field Services, found no irregularity. It was noted by field staff that the power supply was an old style unit and was therefore changed. Protection Design have recommended a review of the THR No2 Prot settings at MNY as well as the THS No2 Protection settings at CMA. Update 30/09/2015: No line follow up report received as yet. Action on TL&C Maint Mgr. 25/11/15: Fault was failed substation dropper at CMA. No further action on TL&C Asset mgr | Fault | 2015
197703 |  |  | 97K Cooma tee Snowy Adit 132kV CB 97K2 |  | 2015Q3 | MNY | CB | 2015-07-26 11:03 | 2015-07-26 21:16 |  |  |  | 132 |  |  | 2015
197704 |  |  | 97K Munyang tee Snowy Adit CB 97K2 |  | 2015Q3 | CMA | CB | 2015-07-26 11:03 | 2015-07-26 21:16 |  |  |  | 132 |  |  | 2015
197705 |  |  | 97K Cooma - Munyang tee Snowy Adit 132kV TL |  | 2015Q3 | CMA, MNY | TL | 2015-07-26 11:03 | 2015-07-26 21:16 | Confirmed that Essental customer load restored via Auto Change over scheme at Munyang and advised that Munyang is supplied from Murray via 97G Note: 97L Guthega - Jindabyne Pumps 132kV TL tripped at the same time this FEOR is a double UP refer to FEOR 2015-F-0317 | Follow up |  | 132 |  |  | 2015
197706 |  |  | 97K Cooma tee Snowy Adit 132kV CB 97K2 |  | 2015Q3 | MNY | CB | 2015-07-26 11:03 | 2015-07-26 21:14 |  |  |  | 132 |  |  | 2015
197707 |  |  | 97K Munyang tee Snowy Adit CB 97K2 |  | 2015Q3 | CMA | CB | 2015-07-26 11:03 | 2015-07-26 21:14 |  |  |  | 132 |  |  | 2015
197708 | Lightning/Storm | TL | 97L Guthega - Jindabyne Pumps 132kV TL | Z | 2015Q3 | GTH, JDP | TL | 2015-07-26 11:03 | 2015-07-27 15:27 | SHL confirmed the Loss 35MW of pumping load. Note: 97K Cooma - Munyang tee Snowy Adit 132kV TL tripped to lockout at the same time. 11/08/2015 - Further information. “We now have confirmation from SHL that the No.1 transformer tripped on 87TB differential and this protection initiated an I/T to Guthega. SHL are investigating operation of their protection. Moreover, the LED6 at Guthega (which indicates Zone 3) is actually initiated by IT receive from the Jindabyne end of 97L. “ | Follow up | Tripped, no reclose attempted. Storms in the area. 97K tripped at the same time. | 132 | Protection Design have received confirmation that the Snowy transformer protection mal operated at JPS. The Snowy transformer protection sent an intertrip to 97L No2 protection at GTH. This intertrip is not checked at GTH and the P442 initiates a "Internal General Trip" which sends a direct trip to the CB. Therefore there is no issue with TG equipment. | Fault | 2015
197710 |  |  | 853 Macarthur - Ambarvale 66kV Line |  | 2015Q3 | MAC | TL | 2015-07-26 15:17 | 2015-07-26 15:17 | Endeavour advised Closed CB via SCADA in there System | Follow up |  | 66 |  |  | 2015
197732 |  |  | No.1 Wagga 132 - Culcairn 66kV Line |  | 2015Q3 | WG2 | TL | 2015-07-27 15:27 | 2015-07-27 15:27 |  | Follow up |  | 66 |  |  | 2015
197745 | HV Equipment | CB | No.3 Transformer 132/66/11kV | E | 2015Q3 | NB2 | TX | 2015-07-28 05:50 | 2015-07-28 10:38 |  |  | CB 3432 SF6 Topup | 132 | Work order No. 359266 was created on 30/07/2015 to top up this CBR. Work order closed now. | Forced | 2015
197885 |  |  | 876 Moree - Moree Solar Farm 66kV Line |  | 2015Q3 | MRE | TL | 2015-07-30 01:51 | 2015-07-30 01:51 | DTF - 31.28km | Follow up |  | 66 |  |  | 2015
197899 |  |  | 7L5 Yanco - Murrami 33kV Line |  | 2015Q3 | YA2 | TL | 2015-07-30 09:24 | 2015-09-02 13:19 | Approx 1.4MW load lost. EE restored load. Fault appears to be located in 33kV Cable approx 200m from Yanco substation. | Follow up |  | 33 |  |  | 2015
198055 |  |  | No.1 & No.2 Gas Turbines 22kV CB 2212 |  | 2015Q3 | BKH | G | 2015-07-31 13:43 | 2015-07-31 17:32 | Chad Ryan (EsE) advises of Faulty Winding Temp micro switch on Essential Energy Gas Turbine No.1 Transformer caused trip. Alarm contacts wired to initiate Trip now. EsE will follow up replacement. Gas Turbines not operating at time of trip. Note: Equipment is No.1 & No.2 Gas Turbines 22kV CB 2212. When PDF created, unfortunately Broken Hill - Cockburn - 22kV line is displayed. | Follow up |  | 11 |  |  | 2015
198068 |  |  | 7L6 Yanco - Whitton 33kV Line |  | 2015Q3 | YA2 | TL | 2015-08-01 22:02 | 2015-08-02 05:26 | Essential Energy advised that they found a conductor down on the ground during Patrol of the line. Repairs completed and feeder returned to service. | Follow up |  | 33 |  |  | 2015
198096 | Unknown | TL | 963 Tomago330 - Taree T Hawksnest 132kV TL | Q | 2015Q3 | TRE, TOM | TL | 2015-08-02 08:10 | 2015-08-02 08:10 |  | Follow up | Successful trip and reclose during rainy weather. | 132 |  |  | 2015
198237 | HV Equipment | CB | 132kV Bus No.1-2 Section CB 4102 | Q | 2015Q3 | LSM | CB | 2015-08-04 14:20 | 2015-08-04 14:50 |  |  | CB4102 SF6 Topup | 132 | Work order No. 359584 was created on 04/08/2015 to top up blue phase CBR. |  | 2015
198286 | HV Equipment | TX | No.1 Transformer 330/132/11kV | E | 2015Q3 | BFD | TX | 2015-08-05 04:31 | 2015-08-05 16:39 | No.1 Transformer buchholz alarm received at 04:30. No1 Transformer topped up with oil ok. Flags reset and transformer placed back into service all ok. | Follow up | No.1 Transformer buchholz alarm received at 04:30. No1 Transformer topped up with oil ok. Flags reset and transformer placed back into service all ok. | 330 | Oil topped up and transformer due to be replaced. | Forced | 2015
198287 | Relay | Prot | No.2 Transformer 330/132/11kV | Z | 2015Q3 | BFD | TX | 2015-08-05 06:21 | 2015-08-06 12:33 | No1 Protection Relay GE Type has failed. Known fault with this type of relay. | Follow up | No1 Protection Relay GE Type has failed. Known fault with this type of relay. | 330 | It has been identified that there is a possible issue with GE T60 relays bought on TG Order N81747 of which this relay is one. Discussions are under way with the manufacturer to determine the cause of the problem. This relay has been replaced and planning is under way to replace all the relays in the affected batch. | Fault | 2015
198674 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2015Q3 | MRE | TL | 2015-08-08 20:23 | 2015-08-08 20:23 | Trip and successful auto reclose. Prot details updated. | Follow up |  | 66 |  |  | 2015
198682 | HV Equipment | CB | 132kV Bus No.1-2 Section CB 4102 | Q | 2015Q3 | LSM | CB | 2015-08-09 15:17 | 2015-08-09 17:36 |  |  | CB 4102 SF6 Topup | 132 | Work order No. 360130 was created on 11/08/2015 to again top up this CBR. This CBR is being refurbished on 25/08/2015 as it is leaking very badly. There was one more top up on 17/08/2015. |  | 2015
198732 | Unknown | TL | 990 Yass - Wagga 132 132kV TL | Q | 2015Q3 | WG2, YSN | TL | 2015-08-11 05:20 | 2015-08-11 05:20 | No SCADA available at Wagga 132 end | Follow up | Successful trip and reclose. Cause unknown. | 132 |  |  | 2015
198827 | HV Equipment | CB | 132kV Bus No.1-2 Section CB 4102 | Q | 2015Q3 | LSM | CB | 2015-08-11 13:30 | 2015-08-11 13:51 |  |  | CB4102 SF6 Topup | 132 |  |  | 2015
199631 |  |  | 282 Sydney South - Milperra tee Revesby 132kV Line |  | 2015Q3 | SYS | TL | 2015-08-13 12:21 | 2015-08-14 18:35 | SCADA trend indicates 14MW load lost. Ausgrid Load restored via 11kV Network. | Follow up |  | 132 |  |  | 2015
199644 | HV Equipment | Aux Tx | No.1 Transformer 330/132/11KV | E | 2015Q3 | CA1 | TX | 2015-08-14 10:07 | 2015-08-14 13:39 |  |  | Short notice outage to repair sight glass on conservator and top up oil level on No.1 Aux Tx | 330 | Work order No. 00360549 was created on 13/08/2015 to Clean sight glass and top up No.1 AUX TX. Work order closed now. The comments from Ellipse are as follows. Sight glass removed and cleaned. Additional 40L of oil added to conservator. Conservator will need to be drained and cleaned in future as holes feeding the sight glass were filled/bocked with sludge. PCB 16ppm. J Forbutt 14/8/15 | Forced | 2015
199651 | HV Equipment | CB | No.2 Transformer 132/33/11kV | E | 2015Q3 | KS2 | TX | 2015-08-14 07:20 | 2015-08-14 08:12 |  |  | CB2422 SF6 Topup. | 132 | Work order No. 360666 was created on 17/08/2015 to top up SF6. This work order is still open. Leak inspection is required. | Forced | 2015
199667 | HV Equipment | CB | 238 Regentville - Penrith 132kV Line | Q | 2015Q3 | RGV | TL | 2015-08-14 10:26 | 2015-08-14 12:30 |  | Follow up | CB2382 SF6 Topup | 132 | Work order No. 00360587 was created on 14/08/2015 to top up this CBR. Work order closed now. |  | 2015
199678 |  |  | 916 Sydney South - Kurnell tee Cronulla 132kV Line |  | 2015Q3 | SYS | TL | 2015-08-14 10:11 | 2015-08-14 15:51 | SCADA trend indicates 49MW load lost DTF 17.1km Ausgrid advised failure of Overhead Earthwire on structure near Kurnell. | Follow up |  | 132 |  |  | 2015
199679 |  |  | 916 Sydney South tee Cronulla CB 9162 |  | 2015Q3 | KNL | CB | 2015-08-14 11:15 | 2015-08-14 15:51 |  |  |  | 132 |  |  | 2015
199680 |  |  | 916 Sydney South tee Kurnell CB 9162 |  | 2015Q3 | CRN | CB | 2015-08-14 11:15 | 2015-08-14 15:51 |  |  |  | 132 |  |  | 2015
199681 |  |  | 916 Kurnell tee Cronulla CB 9162 |  | 2015Q3 | SYS | CB | 2015-08-14 11:15 | 2015-08-14 15:51 |  |  |  | 132 |  |  | 2015
199718 | HV Equipment | CB | No.2 Transformer 132kV B CB 4422B | Q | 2015Q3 | SE1 | CB | 2015-08-15 15:31 | 2015-08-15 16:38 |  |  | CB4422B SF6 Topup | 132 |  |  | 2015
199721 |  |  | No.7 Transformer 132/33/11kV |  | 2015Q3 | SE1 | TX | 2015-08-16 04:17 | 2015-08-16 06:55 | Ausgrid advised that they found a possom across the section of the 33kV Busbar that caused the trip. Possom has been cleared and all alarms reset. Requested to energise No.7 transformer at SE1. 06:55 No.7 Tx Energised. NCM advised. | Follow up |  | 132 |  |  | 2015
199735 |  |  | 98Y Dapto - Springhill 132kV Line |  | 2015Q3 | DPT | TL | 2015-08-16 14:17 | 2015-08-16 14:17 |  |  |  | 132 |  |  | 2015
199736 | Fire | TL | 11 Dapto - Sydney South 330kV TL | Q | 2015Q3 | DPT, SYS | TL | 2015-08-16 14:17 | 2015-08-16 14:17 | A Controlled hazard reduction carried out by NSW Rural Fire service at the time of the trip between structures 128 and 134. Mains staff were present on site and monitoring | 20/08/2015 09:49:00 ¦ Follow up | At ignition 1214 hrs on Sunday 16 August 2015, system Operations where contacted, the System Operator was informed that the HR commenced. At approximately 1345 hrs the weather conditions changed (no wind and plumes of smoke where stagnant building up around the conductors), the Easement Officer asked the Incident Controller whether staff or volenteers were on site as conditions changed. The Incident Controller confirmed all where well clear from the easement. At 1417 hrs the Easement Officer heard a loud bang which was confirmed by NPWS staff on the fire ground (well away from the easement), the Easement Officer contacted the System Operator who confirmed that the line had trip and returned to service. At 1625 hrs the HR was no longer impaction on the easement. The Easement Officer contacted the System Operator and informed him that he was leaving site and would do a fault patrol in the morning as the area was still an active fire ground. After fault patrol was conducted by the Easement Officer on Monday 17 August 2015 of TL 11 spans 129-134 with no damage or defects being identified. | 330 |  |  | 2015
199752 | HV Equipment | CB | 132kV Bus No.1-2 Section CB 4102 | Q | 2015Q3 | LSM | CB | 2015-08-17 09:30 | 2015-08-17 09:51 |  |  | CB4102 Topup | 132 | CB topped up under work order No. 359584. CB poles are now replaced as a part of work order No. 360130. |  | 2015
199848 |  |  | 84A Finley - Jerilderie 66kV Line |  | 2015Q3 | FNY | TL | 2015-08-18 06:39 | 2015-08-18 06:39 | Distance to Fault indicates 13.99km from FNY | Follow up |  | 66 |  |  | 2015
199869 |  |  | No.4 330kV Generator Transformer Group |  | 2015Q3 | LD1 | TX | 2015-08-18 09:12 | 2015-08-27 12:58 |  |  |  | 330 |  |  | 2015
199943 | HV Equipment | CB | 79J Griffith - Griffith Zone Standby 33kV Line | Q | 2015Q3 | GRF | TL | 2015-08-19 05:16 | 2015-08-19 15:09 | 79J Griffith Zone Standby CB 79J2 removed from service due to Low SF6 alarm received via SCADA. Feeder normally off-loaded. | Follow up | CB SF6 Topup | 33 | Work order No. 361045 was created on 19/08/2015 to investigate thjis issue. CB topped up and work order closed now.(CB 79J2, low SF6 white phase alarm. Leak detected on lower rear side of interupter, leaking through a previous repair job. leak temporarily patched with silicon. white phase pole pressure tested to be 120kpa well below the desired 160kpa. alarm contacts in pressure switch tested all ok. alarming at 106 kpa. white phase topped up to 175 kpa. very slow leak but will need more attention in future.) |  | 2015
199958 | HV Equipment | CB | No.2 Transformer 132/66/11kV | E | 2015Q3 | KLK | TX | 2015-08-19 12:02 | 2015-08-19 14:33 |  |  | CB SF6 Topup | 132 | Work order No. 361060 was created on 19/08/2015 to investigate this issue. SF6 topped up and work order closed now. No leaks were found but this CB has high frequency of SF6 top ups. (Last top up in November 2014) | Forced | 2015
199997 |  |  | 971 Yass - Goulburn tee Cullerin Range tee Gunning 132kV Line |  | 2015Q3 | YSN | TL | 2015-08-20 06:37 | 2015-08-20 13:02 | 8.7MW of generation lost. No Essential Energy load lost. Generation only from wind farms. | Follow up |  | 132 |  |  | 2015
200017 | HV Equipment | CT | No.1 Transformer 132/66/11kV | E | 2015Q3 | NB2 | TX | 2015-08-20 10:54 | 2015-08-20 12:31 |  |  | Inspect and topup leaking CTs. | 132 | Work order No. 361120 was created on 20/08/2015 to investigate this issue. Red phase CT was topped up. Update 29/09/2015: Work order is still open in Ellipse but work is completed? To be checked. | Forced | 2015
200027 | Staff Error | Proc | 90T Beaconsfield South - Haymarket tee Green Square 132kV Cable | Q | 2015Q3 | BFD, HYM | UG | 2015-08-20 09:10 | 2015-08-20 12:38 | Prot Techs at Haymarket inadvertently sent intertrip while working on BBP | Follow up | Prot Techs at Haymarket inadvertently sent intertrip while working on BBP Protection technicians were working on cutting over the new busbar protection at Haymarket with Beaconsfield and Green Square still in service. The protection technician was correcting wiring and as he was stripping the cable, an earth was unintentionally placed on the Green Square intertrip. There was an inquiry in to the incident and no major issues were found. The feeder was returned to service the same day. | 132 |  |  | 2015
200028 |  |  | 90T Beaconsfield South tee Haymarket CB 90T2 |  | 2015Q3 | GSQ | CB | 2015-08-20 09:10 | 2015-08-20 12:38 |  |  |  | 132 |  |  | 2015
200029 |  |  | 90T Beaconsfield South tee Green Square CB 90T2 |  | 2015Q3 | HYM | CB | 2015-08-20 09:10 | 2015-08-20 12:38 |  |  |  | 132 |  |  | 2015
200030 |  |  | 90T Haymarket tee Green Square CB 90T2 |  | 2015Q3 | BFD | CB | 2015-08-20 09:10 | 2015-08-20 12:38 |  |  |  | 132 |  |  | 2015
200071 | Communications | Com | 63 Wagga - Darlington Point 330kV TL | Q | 2015Q3 | DNT, WG1 | TL | 2015-08-21 10:01 | 2015-08-21 13:46 |  |  | Fleeting alarms at Square Head microwave are causing disruptions. Short notice outage required to investigate alarms and replace indoor unit or upgrade firmware. This work will cause interruption to services carried on this system. Services to be affected are: Darlington Point SCADA, TL63 Darlington Point-Wagga 330 Protection No 2 VF Intertrip. Also Griffith, Coleambally, Buronga, Deniliquin and Balranald Smart (Back up) Alarms. | 330 |  |  | 2015
200097 | HV Equipment | Cap | No.5 Capacitor | E | 2015Q3 | TRE | CAP | 2015-08-21 12:19 | 2015-08-21 13:48 |  |  | Urgent Hot Joint Repair on Blue Phase southern side bottom row. | 66 | Work order No. 362594 was created on 28/08/2015 to fix this issue. Joint cleaned, copper anti-sieze applied and tightened. Work order closed now. Update 29/08/2015: Completion Date 28/08/2015. | Forced | 2015
200101 | HV Equipment | CB | 132kV Bus No.1-2 Section CB 4102 | Q | 2015Q3 | LSM | CB | 2015-08-21 11:06 | 2015-08-21 11:40 |  |  | CB4102 SF6 Topup | 132 | CB poles replaced as a part of work order No. 360130. Work order closed now. |  | 2015
200222 |  |  | 851 Mudgee Tee Gulgong 66kV CB 8512 |  | 2015Q3 | BER | CB | 2015-08-23 04:54 | 2015-08-23 04:54 |  | Follow up |  | 66 |  |  | 2015
200223 | Secondary Equipment | Cont | 896 Forbes - West Jemalong 66kV Line | Q | 2015Q3 | FB2 | TL | 2015-08-24 04:12 | 2015-08-24 06:32 |  | Follow up | Customer line tripped, auto reclose did not occur. | 66 |  |  | 2015
200233 |  |  | 893/5 Forbes - Payten's Bridge 66kV Line |  | 2015Q3 | FB2 | TL | 2015-08-24 07:37 | 2015-08-24 07:37 | DTF - 58.01 kms | Follow up |  | 66 |  |  | 2015
200234 |  |  | 896 Forbes - West Jemalong 66kV Line |  | 2015Q3 | FB2 | TL | 2015-08-24 05:54 | 2015-08-24 05:54 | No A/R at Forbes due to A/R made N/A at Forbes, reason being prot'n design problem, (switch tagged at site), DTF 58.47 kms | Follow up |  | 66 |  |  | 2015
200235 |  |  | 0896 Koolkhan - Maclean 66kV Line |  | 2015Q3 | KLK | TL | 2015-08-24 06:44 | 2015-08-24 06:44 |  | Follow up |  | 66 |  |  | 2015
200255 | Lightning/Storm | TL | 96R Glen Innes - Tenterfield 132kV TL | Q | 2015Q3 | GNS, TTF | TL | 2015-08-24 06:28 | 2015-08-24 06:28 | DTF - 24.5kms | Follow up | Successful trip and reclose during storms. | 132 |  |  | 2015
200258 |  |  | 836 Murrumburrah - Cootamundra 66kV Line |  | 2015Q3 | MRU | TL | 2015-08-24 14:29 | 2015-08-24 14:29 |  | Follow up |  | 66 |  |  | 2015
200259 | Lightning/Storm | TL | 82 Liddell - Tomago 330kV TL | Q | 2015Q3 | LD1, TOM | TL | 2015-08-24 14:49 | 2015-08-24 14:49 |  | Follow up | Successful trip and reclose during storms. | 330 |  |  | 2015
200261 | Lightning/Storm | TL | 28 Sydney North - Sydney East 330kV TL | Q | 2015Q3 | SE1, SYN | TL | 2015-08-24 19:54 | 2015-08-24 19:54 | CB..282A closed via SCADA | Follow up ¦ Defect work order has been opened to replaced flashed pilot insulator. | Successful trip and reclose during storms. | 330 |  |  | 2015
200262 | Lightning/Storm | TL | 94X Wallerawang 132 - Panorama 132kV TL | Q | 2015Q3 | PMA, WWS | TL | 2015-08-24 21:39 | 2015-08-24 21:39 |  | 11/09/2015 09:39:00 ¦ Follow up ¦ Nil ¦ Nil | Successful trip and reclose during storms. | 132 |  |  | 2015
200268 | Unknown | CB | 41 Beaconsfield West Series Reactor Bypass B CB 412B | Q | 2015Q3 | SYS | CB | 2015-08-24 23:55 | 2015-08-25 21:48 | 23:55 41 Cable Series Rx Bypass CB... 412B - Closed via SCADA - CB status changed to closed and straight back to the Open state. No alarms received or protection operations indicated. | Follow up | 23:55 41 Cable Series Rx Bypass CB... 412B - Closed via SCADA - CB status changed to closed and straight back to the Open state. No alarms received or protection operations indicated. Mark advises that problem looks to be some type of tab preventing red phase from closing. | 330 | Work order No. 362260 was created on 26/08/2015 to investigate this issue. Work order is still open. (FOUND RED PHASE CLOSING PAW JAMBED BY TAB WASHER. WHITE PHASE TAB WASHERS ALSO DISLODGED.) |  | 2015
200269 |  |  | 5A2 Eraring - Kemps Creek 500kV TL |  | 2015Q3 | ER0, KCR | TL | 2015-08-25 03:08 | 2015-08-25 03:08 | selected wrong service data disregard this FEOR 2015-F0350 | Follow up |  | 500 |  |  | 2015
200270 | HV Equipment | Rx | No.3 Reactor | Q | 2015Q3 | KCR | RX | 2015-08-25 03:08 |  | Advised by Paul Hazeltine cracked paint surrounding Reactor. Unavailable for service. | Follow up | Advised by Paul Hazeltine cracked paint surrounding Reactor. Unavailable for service. | 33 | A replacement reactor would be sourced from Eraring. |  | 2015
200318 | Unknown | TL | 97K Cooma (New) - Munyang tee Snowy Adit 132kV TL | Q | 2015Q3 | MNY, COA | TL | 2015-08-25 08:34 | 2015-08-25 08:34 |  | 4/09/2015 13:57:00 ¦ Follow up ¦ Potential additional trees along the edge of the easement that could cause future trips. ¦ Recommend a review of the vegetation practices on the 97K to ensure that current practice meets Transgrids requirements as per the previous 97G recommendation regarding tall trees at the edge of the easement. | Successful trip and reclose during rainy and windy weather. Cause unknown. | 132 |  |  | 2015
200325 | HV Equipment | Disc | 132kV Bus No.1 Section | Q | 2015Q3 | CW2 | BB | 2015-08-25 11:22 | 2015-08-25 16:07 |  |  | Outage to repair hot joint on isolator 9993 | 132 | Work order No. 362838 was created on 25/08/2015 to investigate this issue. Repair has been completed. Update 29/09/2015: [Outage arranged and repaired when found. Found 2 bolts that bolted the copper plate to the insulator had been extremely og and welded themselves in place. removed the plates replace the bolts and cleaned the surfaces applying new alminox to the connections needed. Also found that a spring in the top fixed contact had seized from being hot. replaced with a cut down valve spring and put back into service. thermovisioned after 45mins of being on load and no heating of the joint had occured] Work order now closed. |  | 2015
200361 | Unknown | TL | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2015Q3 | GTH, MUR, GHI | TL | 2015-08-25 11:25 | 2015-08-26 11:02 |  | 4/09/2015 12:42:00 ¦ Follow up ¦ Nil identified in relation to the transmission line. The previously observed risk of tall trees in the tree line that appear capable of taking out all three phases and whole structures on the transmission line. ¦ It may be possible to implement a reclose scheme on this line to safely isolate the generator and perform a dead check prior to a reclose attempt. Such a scheme may reduce customer outage times, pressure on operations staff for manual reclose and field staff for patrols during lockout. The previous recommendation to review the vegetation management on 97G is further supported by this outage. | Advised line patrol of 97G Murray to Guthega tee Geehi 132 kV T/L from Murray to structure 48 complete. No signs of damage to line. Section of line patrolled is in dense bush area where previous trip occured and is past the DTF distance of 17km obtained from protection relay at Guthega. | 132 | Update 30/09/2015: Aerial patrol 02/09/2015 found no damage. | Fault | 2015
200362 |  |  | 97G/3 Geehi Tee CB 97G2 |  | 2015Q3 | GTH | CB | 2015-08-25 11:25 | 2015-08-26 11:02 |  |  |  | 132 |  |  | 2015
200363 |  |  | 97G/1 Geehi Tee CB 97G2 |  | 2015Q3 | MUR | CB | 2015-08-25 11:25 | 2015-08-26 11:02 |  |  |  | 132 |  |  | 2015
200412 |  |  | No.1 Transformer 132/66/11kV | E | 2015Q3 | CW2 | TX | 2015-08-25 11:22 | 2015-08-25 16:07 |  |  |  | 132 |  | Forced | 2015
200413 |  |  | 999 Yass - Cowra 132kV TL | E | 2015Q3 | CW2, YSN | TL | 2015-08-25 11:22 | 2015-08-25 16:07 |  |  |  | 132 |  | Forced | 2015
200424 | Unknown | TL | 96M Narrabri - Moree 132kV TL | Q | 2015Q3 | MRE, NB2 | TL | 2015-08-26 04:54 | 2015-08-26 04:54 |  | Follow up | Successful trip and reclose, cause unknown. | 132 |  |  | 2015
200537 |  |  | 97R Cooma - Bega tee Steeple Flat 132kV Line |  | 2015Q3 | CMA | TL | 2015-08-26 13:29 | 2015-08-26 13:30 |  | Follow up |  | 132 |  |  | 2015
200545 | HV Equipment | Rx | No.1 Reactor | E | 2015Q3 | BFD | RX | 2015-08-26 16:17 | 2016-05-14 11:08 | Requested out of service by Tim Blair Support Engineer Field Services due to poor oil sample result. New sample to be tested. | Follow up | Requested out of service by Tim Blair Support Engineer Field Services due to poor oil sample result. New sample to be tested. | 132 | This reactor would be replaced. Update 29/09/2015: Reactor replacement project. | Forced | 2015
200615 | HV Equipment | CB | No.3 Transformer 330/132/11kV | E | 2015Q3 | BFD | TX | 2015-08-27 11:27 | 2015-08-27 16:17 |  |  | CB5432 SF6 Topup | 330 | No work order is created in Ellipse yet. To be checked with Tim Blair. Update 17/09/2015: Waiting for response from Tim Blair. | Forced | 2015
200828 | HV Equipment | CT | 939 Sydney West - Mamre 132kV Line | E | 2015Q3 | SYW | TL | 2015-08-28 14:20 | 2015-08-31 10:50 | Requested out of service by Tim Blair Support Engineer Field Services due to poor oil sample result. New sample to be tested. Tim Barnes Asset Monitoring Centre Manger advised resample tested OK and feeder can be placed in-service. | Follow up | Requested out of service by Tim Blair Support Engineer Field Services due to poor CT oil sample result. New sample to be tested. Tim Barnes Asset Monitoring Centre Manger advised resample tested OK and feeder can be placed in-service. | 132 | No work order is created in Ellipse yet. To be checked with Tim Blair. Update 17/09/2015: Workorder No. 362989 was created on 28/08/2015 to resample this CT. Update 29/09/2015: Work order is still open in Ellipse but work is completed? To be checked. | Forced | 2015
200843 | HV Equipment | Rx | No.4 Transformer Reactor | Q | 2015Q3 | DNT | RX | 2015-08-29 13:23 |  | Brad Ashton (EsE) advises of visible black marking on topr of reactor. Byron Mills advised. Info update RX still out of service. | Follow up | Brad Ashton (EsE) advises of visible black marking on topr of reactor. Byron Mills advised. | 33 | Workorder No.363629 was created on 01/09/2015 to investigate this issue. No 4 Trans Blue Phase Reactor core failed on 30/08/15. There are no spare units. A new unit would be procured from Trench. Update 29/09/2015: Reactor replacement project. |  | 2015
200956 | HV Equipment | TX | No.1 Transformer 132/66/11kV | Z | 2015Q3 | CMA | TX | 2015-08-31 20:08 | 2015-09-01 15:24 | Transformer isolated pending further investigations. Possible low oil in regulator. | Follow up | Transformer isolated pending further investigations. Possible low oil in regulator.Transformer isolated pending further investigations. Possible low oil in regulator. | 132 | Update 17/09/2015: Workorder No. 363531 was created on 01/09/2015 to investigate this issue. [1.9.15 main conservator topped uo to 2/3 full .there is still old leaks present tm] Work order is closed now. | Fault | 2015
201121 | HV Equipment | CB | No.1 Transformer 132/33/11kV | E | 2015Q3 | TRE | TX | 2015-09-02 06:18 | 2015-09-02 08:22 |  |  | CB2412 SF6 Topup | 132 | Update 17/09/2015: Workorder No. 363681 was created on 02/09/2015 to investigate this issue. CB was topped up. [CB defective alarm recieved. Pole B low gas alarm ( blue phase ) CB 2412 Sf6 top up completed. Unable to detect leak with gas detector, will need camera to invetigate further. S.Johnston 2/9/15] | Forced | 2015
201178 | Animal/Bird | Other | No.3 Transformer 132/66kV | E | 2015Q3 | ORG | TX | 2015-09-02 13:23 | 2015-09-02 16:16 |  |  | Remove birds nest from Gantry above transformer | 132 | Update 17/09/2015: Workorder No. 363772 was created on 02/09/2015 to investigate this issue. [Magpie's nest was located above No. 3 TX and associated 66kV circuit breaker red phase supporting insulator on the gantry, using the bird spikes in that location as a stable base for the nest. There was a dangling bit that reached down to within 200mm of the conductor. TX was isolated and the gantry climbed by a linesman as an EWP couldn't be placed close enough due to limited space and the construction site. The dangling bit was a length of wire. Most of the nest turned out to be metal, so the metal was all removed and the center of the nest, which had four eggs and was made of wood, was moved to one of the uprights of the gantry, away from conductors. A supporting mesh was cable-tied to the structure to provide a stable base for the nest, and encourage the bird not to rebuild back over the TX. The bird returned and is nesting in the new location.] Work order now closed. | Forced | 2015
201221 | Secondary Equipment | SVC | No.1 Static VAr Compensator | Z | 2015Q3 | BKH | SVC | 2015-09-02 18:04 | 2015-09-02 19:40 | No.1 and No.2 SVCs tripped at exactly the same time No.1 Transformer was energised following an outage. Investigations indicated that Loss of 415V Auxiliary supply during Auto changeover is believed to be the cause of trip. Further investigations to be carried during day time hours on Thursday 03/09/15 | Follow up | No.1 and No.2 SVCs tripped at exactly the same time No.1 Transformer was energised following an outage. Investigations indicated that Loss of 415V Auxiliary supply during Auto changeover is believed to be the cause of trip. Further investigations to be carried during day time hours on Thursday 03/09/15. | 22 | Update 17/09/2015: Workorder No. 365595 was created on 11/09/2015 to investigate this issue. Workorder is still open. Update 29/09/2015: Work order is still open in Ellipse but work is completed? To be checked. This SVC is still under warranty. ABB has shipped breaker which is due to arrive in mid october. Repair would be completed once parts are available onsite. | Fault | 2015
201222 | Secondary Equipment | SVC | No.2 Static VAr Compensator | N | 2015Q3 | BKH | SVC | 2015-09-02 18:04 | 2015-09-02 19:40 | No.1 and No.2 SVCs tripped at exactly the same time No.1 Transformer was energised following an outage. Investigations indicated that Loss of 415V Auxiliary supply during Auto change over is believed to be the cause of trip. Further investigations to be carried during day time hours on Thursday 03/09/15 Both SVCs have been returned to service (at 19:40) | Follow up | No.1 and No.2 SVCs tripped at exactly the same time No.1 Transformer was energised following an outage. Investigations indicated that Loss of 415V Auxiliary supply during Auto change over is believed to be the cause of trip. Further investigations to be carried during day time hours on Thursday 03/09/15 | 22 | Update 17/09/2015: Workorder No. 365595 was created on 11/09/2015 to investigate this issue. Workorder is still open. Update 29/09/2015: Work order is still open in Ellipse but work is completed? To be checked. This SVC is still under warranty. ABB has shipped breaker which is due to arrive in mid october. Repair would be completed once parts are available onsite. |  | 2015
201223 | Lightning/Storm | TL | 994 Wagga 330 - Yanco 132kV TL | Q | 2015Q3 | WG1, YA2 | TL | 2015-09-02 22:27 | 2015-09-02 22:27 | Heavy rains in the area | Follow up | Successful trip and reclose during storms. | 132 |  |  | 2015
201224 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q3 | CW2 | TL | 2015-09-03 00:39 | 2015-09-03 00:39 |  | Follow up |  | 66 |  |  | 2015
201225 | Lightning/Storm | TL | 86 Tamworth 330 - Armidale 330kV TL | Q | 2015Q3 | AR1, TA1 | TL | 2015-09-03 03:41 | 2015-09-03 03:41 |  | Follow up | Successful trip and reclose during storms. | 330 |  |  | 2015
201226 | Lightning/Storm | TL | 968 Tamworth 330 - Narrabri 132kV TL | Q | 2015Q3 | NB2, TA1 | TL | 2015-09-03 03:41 | 2015-09-03 03:41 |  | Follow up | Successful trip and reclose during storms. | 132 |  |  | 2015
201227 |  |  | No.3 Transformer 132/66/11kV |  | 2015Q3 | TA1, TMW | TX | 2015-09-03 03:41 | 2015-10-08 05:20 | FEOR Information update 23/10/15. No.3 transformer at Tamworth (New) 132kV Substation tripped at the same time as 86 Tamworth to Armidale 330kV T/L and 968 Tamworth 330 to Narrabri 132 kV T/L. Staff dispatched to investigate advised no apparant damage to No.3 Transformer after visual inspection. Transformer left out of service for further investigation. A lightening storm was passing over the area at the time of the trip. | Follow up |  | 132 |  |  | 2015
201228 |  |  | 804 Tamworth 132 - Nundle 66kV Line |  | 2015Q3 | TMW | TL | 2015-09-03 02:52 | 2015-09-03 02:52 |  | Follow up |  | 66 |  |  | 2015
201295 | Relay Faulty | Cont | No.1 Capacitor | E | 2015Q3 | YSN | CAP | 2015-09-03 12:22 | 2015-10-22 11:09 |  |  | Faulty POW relay replaced. | 132 |  | Forced | 2015
201323 |  |  | 90W/1 Haymarket - City Central tee City South 132KV Cable |  | 2015Q3 | HYM | UG | 2015-09-04 07:01 | 2015-09-04 10:40 | Ausgrid advise of Transformer trip at City South. No loss off load reported. Faulty Transformer will be isolated. | Follow up |  | 132 |  |  | 2015
201361 |  |  | 705 Coffs Harbour - South Coffs Harbour 66kV Line |  | 2015Q3 | COF | TL | 2015-09-04 11:10 | 2015-09-04 15:51 | EE advise of broken suspension insulator | Follow up |  | 66 |  |  | 2015
201425 | Animal/Bird | VT | No.1 Transformer 132/66/11kV | Z | 2015Q3 | KLK | TX | 2015-09-05 10:13 | 2015-09-11 15:15 | Trip from service condition. No remote indication of visual equipment damage or other anomalies. Staff on route to site | Follow up | Trip from service condition. No remote indication of visual equipment damage or other anomalies. Protection details provided and recorded within FEOR. Instantenous diff protection indicated on both schemes. No Earth Fault protection operated. No operation of external tripping devices. Advised birds nest (timber sticks) observed above red phase 66kV VTs. Inadvertently dislodged in process of investigation by proving dead equipment. Further advised no other visible damage or irregularities observed after thorough inspection of transformer and bay equipment. | 132 | Update 17/09/2015: Workorder No. 364361 was created on 06/09/2015 to investigate this issue. [5/9/15 Tx triopped out on Inst over current red phase due to stick from birds nest coming into contact with 66kV dropper below gantry structure that the nest was being built on. Testing required to determine if tx sustained any damage to the insulation.] Update 29/09/2015: 7/9/15 to 11/9/15 Test conducted: Megger and DLa windings, 415 excitation, Oil sample for DGA. All tests results OK Birds nest preventing cones put in place. 11/9/15 Tony Gray gave OK to put Tx back in service. Tx back in service 11/9/15 @ 15.00. G . Robinson] Work order is now closed. Completion date = 15/09/2015 | Fault | 2015
201431 | Unknown | TL | 96M Narrabri - Moree 132kV TL | Q | 2015Q3 | MRE, NB2 | TL | 2015-09-06 01:09 | 2015-09-06 01:09 |  | Follow up | Successful trip and reclose, cause unknown. | 132 |  |  | 2015
201730 | HV Equipment | TX | No.2 Transformer 330/132/11kV | Z | 2015Q3 | RWR | TX | 2015-09-10 08:12 | 2015-09-23 11:48 | 23/09/2015 - Advised ok to return to service Visible Blow Out Mark on 132kV Red Phase Wall Bushing | Follow up | Visible Blow Out Mark on 132kV Red Phase Wall Bushing | 330 | Workorder No. 365571 was created on 11/09/2015 to investigate this issue. The transformer is back in service now. The cause of this incident is being investigated. | Fault | 2015
201776 | Staff Error | Proc | 969 Tamworth 330 - Gunnedah 132kV TL | Z | 2015Q3 | GN2, TA1 | TL | 2015-09-10 10:47 | 2015-09-10 11:19 | Protection staff wiring in back of 132kV Bus Section 3 No1 Protection panel at the time of the trip | Follow up | Protection staff wiring in back of 132kV Bus Section 3 No1 Protection panel at the time of the trip | 132 |  | Fault | 2015
201784 | HV Equipment | Cap | No.2 Capacitor | E | 2015Q3 | NEW | CAP | 2015-09-11 07:01 | 2015-09-11 10:17 |  |  | Repair Hot Joints on No2 Capacitor | 132 | Update 29/09/2015: Work order No. 365570 was created on 11/09/2015 to repair multiple hot joints on the capacitor bank. Work order closed now. | Forced | 2015
201907 | HV Equipment | CB | No.2 Transformer 330kV A CB 5422A | Q | 2015Q3 | TOM | CB | 2015-09-13 07:34 | 2015-09-13 10:11 |  |  | Low SF6. Top-up required. | 330 | Workorder No. 366001 was created on 14/09/2015 to investigate this issue. [Stage 1 alarm initiated at approx. 530kPa @ 13 DegC. Topped up to 660kPa @ 20 DegC. Alarm cleared. CB checked with SF6 camera and found to be leaking from the main pole seal at the bottom of the Blue phase pole.] |  | 2015
201908 |  |  | 850 Tumut - Talbingo tee Jounama Dam 66kV Line |  | 2015Q3 | TU2 | TL | 2015-09-13 17:24 | 2015-09-14 01:13 | HV equipment checked ok. Essential Energy repairs completed and line returned to service. | Follow up |  | 66 |  |  | 2015
201909 | Unknown | Prot | No.3 Bay Coupler CB 5032 | Q | 2015Q3 | LD1 | CB | 2015-09-13 20:19 | 2015-09-14 15:31 | Generator bay opened while unit 3 was isolated for AGL Macquarie at the time. | Follow up | Generator bay opened while unit 3 was isolated for AGL Macquarie at the time. Being investigated. | 330 | AGL Generator issue |  | 2015
202001 | HV Equipment | Disc | 91J Sydney South - Peakhurst 132kV Line | Q | 2015Q3 | SYS | TL | 2015-09-14 21:03 | 2015-09-14 21:03 |  |  | Outage attributed to repairs required on disconnector 91J1. | 132 | Workorder No. 366138 was created on 15/09/2015 to investigate this issue. [LINE DISC 91J1 NOT CLOSING FULLY. HAND OPERATED FINGER TYPE DISCONNECTOR NEEDS ADJUSTMENT ON WHITE PHASE TO CLOSE ONTO FIXED CONTACTS]. Workorder is still open. |  | 2015
202008 | Unknown | TL | 66 Murray - Lower Tumut 330kV TL | Q | 2015Q3 | LT1, MUR | TL | 2015-09-14 17:06 | 2015-09-14 17:06 | Trip and Auto reclose from in service condition. A C.B.s reclosed at both locations via SCADA. | 29/09/2015 09:00:00 ¦ Follow up ¦ An after fault patrol was completed by Mains Wagga on 28th September 2015 of structure 92 and a number of structures either side with no defects being found. | Trip and Auto reclose from in service condition. A C.B.s reclosed at both locations via SCADA. | 330 |  |  | 2015
202009 |  |  | 66 Murray A CB 662A | Q | 2015Q3 | LT1 | CB | 2015-09-14 17:06 | 2015-09-14 17:06 |  |  |  | 330 |  |  | 2015
202010 |  |  | 66 Murray B Bus CB 662B | Q | 2015Q3 | LT1 | CB | 2015-09-14 17:06 | 2015-09-14 17:06 |  |  |  | 330 |  |  | 2015
202011 |  |  | 66 Lower Tumut A CB 662A | Q | 2015Q3 | MUR | CB | 2015-09-14 17:06 | 2015-09-14 17:06 |  |  |  | 330 |  |  | 2015
202012 |  |  | 66 Lower Tumut B CB 662B | Q | 2015Q3 | MUR | CB | 2015-09-14 17:06 | 2015-09-14 17:06 |  |  |  | 330 |  |  | 2015
202013 | Staff Error | SVC | No.2 Static VAr Compensator | Z | 2015Q3 | BKH | SVC | 2015-09-14 15:53 | 2015-09-14 18:03 | Trip from service in process of investigating 415V auxiliary supply issues. Successful return to service after plant inspection completed. | Follow up | No.1 & No.2 SVC trip from service whilst in service preperation work being undertaken regarding 415V auxiliary supply arrangements. | 22 | This SVC is still under warranty. ABB has shipped breaker which is due to arrive in mid october. Repair would be completed once parts are available onsite. | Fault | 2015
202014 | Staff Error | SVC | No.1 Static VAr Compensator | N | 2015Q3 | BKH | SVC | 2015-09-14 15:53 | 2015-09-15 16:39 | Trip from service during fault finding work on 415V ac auxiliary supply. | Follow up | No.1 & No.2 SVC trip from service whilst in service preperation work being undertaken regarding 415V auxiliary supply arrangements. | 22 | This SVC is still under warranty. ABB has shipped breaker which is due to arrive in mid october. Repair would be completed once parts are available onsite. |  | 2015
202128 | HV Equipment | CB | 132kV No.1 Bus Coupler CB 4012 | Q | 2015Q3 | RGV | CB | 2015-09-15 12:24 | 2015-09-15 13:15 |  |  | SF6 top-up. | 132 | Workorder No. 366133 was created on 15/09/2015. CB was topped up and workorder is closed now. Completion date = 15/09/2015 |  | 2015
202295 |  |  | 6501 Koolkhan - Casino 66kV Line |  | 2015Q3 | KLK | TL | 2015-09-16 14:11 | 2015-09-16 17:51 | Request from Essential Energy to de energise due to cross arm issue on T/L. | Follow up |  | 66 |  |  | 2015
202296 | LV/MECH Fail | VT | 9W6 Macksville - Nambucca 132kV TL | E | 2015Q3 | NAM, MVL | TL | 2015-09-16 14:10 | 2015-09-16 14:19 | CVT unbalance alarm after returning T/L to service, field staff request de energise T/L to tighten loose wire on W ph in CVT sec cct. | Follow up | CVT unbalance alarm after returning T/L to service, field staff request de energise T/L to tighten loose wire on W ph in CVT sec cct. | 132 | No work order in Ellipse. | Forced | 2015
202338 |  |  | 7L3 Yanco - Kamarah 33kV Line |  | 2015Q3 | YA2 | TL | 2015-09-16 17:43 | 2015-09-16 17:43 |  | Follow up |  | 33 |  |  | 2015
202361 | HV Equipment | Rx | X2 Reactor | E | 2015Q3 | BRG | RX | 2015-09-17 12:29 | 2015-09-17 15:36 |  |  | Investigate oil level abnormal alarm. | 220 | Workorder No. 366328 was created on 17/09/2015 to investigate this issue. This reactor is still under warranty and warrantly repair has been requested from ABB. | Forced | 2015
202362 | HV Equipment | CB | 969 Tamworth 330 - Gunnedah 132kV TL | E | 2015Q3 | GN2, TA1 | TL | 2015-09-17 08:23 | 2015-09-17 10:22 |  |  | CB SF6 Topup | 132 | No work order in Ellipse. | Forced | 2015
202476 |  |  | 7R5 Kempsey - North St 33kV Line |  | 2015Q3 | KS2 | TL | 2015-09-17 13:39 | 2015-09-17 13:39 |  | Follow up |  | 33 |  |  | 2015
202561 | Unknown | Other | 132kV Bus | Q | 2015Q3 | HYM | BB | 2015-09-18 16:01 | 2015-09-18 17:55 |  |  | Could not electrically operate disconnector 4436. Outage to transfer all HYM equipment from 132kV B2 Bus to A2 Bus. Flagging due to notice time being < 24 hours. Notice time: 1hr37min as per TheOS confirmed time. Following up with Operations Planning. | 132 |  |  | 2015
202585 | Relay | Cont | 330kV Bus No.3 Section | Q | 2015Q3 | KVS | BB | 2015-09-18 23:39 | 2015-09-19 14:14 |  |  | 18 September 2015: Advised of alarm. Alarm initiated from 330kV Section 3 Bus CVT. Note: Bus was out of service this week for work. Alarm initiated on return to service. Maintenance Team Leader advised and requested bus be taken out of service and alarm followed up tomorrow. AEMO advised and Bus taken out of service (source: OPSLog). 19 September 2015: Phil Baigent - Advises C.V.T. Unbalance relay on 3W Capital Wind Farm may need replacing. Have been able to adjust to clear C.V.T Unbalance alarm. Checked all C.V.T secondary voltages and no signifant errors (source: OPSLog). | 330 |  |  | 2015
202586 |  |  | 19 Kangaroo Valley - Bendeela 330kV Line | Q | 2015Q3 | KVS | TL | 2015-09-18 23:39 | 2015-09-19 14:14 |  |  |  | 330 |  |  | 2015
202588 |  |  | 3W Capital Wind Farm - Kangaroo Valley 330kV TL | E | 2015Q3 | KVS, CWF | TL | 2015-09-18 23:39 | 2015-09-19 14:14 |  |  |  | 330 |  | Forced | 2015
202589 | Unknown/Other | TL | 96M Narrabri - Moree 132kV TL | Q | 2015Q3 | MRE, NB2 | TL | 2015-09-19 01:16 | 2015-09-19 01:16 |  | Follow up | Successful trip and reclose. Cause unknown. Weather fine. | 132 |  |  | 2015
202593 |  |  | 5A1 Eraring - Kemps Creek 500kV TL | E | 2015Q3 | ER0, KCR | TL | 2015-09-20 02:30 | 2015-09-20 07:49 |  |  |  | 500 |  | Forced | 2015
202644 | Lightning/Storm | TL | 999 Yass - Cowra 132kV TL | Q | 2015Q3 | CW2, YSN | TL | 2015-09-21 15:31 | 2015-09-21 15:31 | Weather tools indicate Storms in the Yass/Canberra area at time of TAR. | Follow up | Successful trip and reclose during storms. | 132 |  |  | 2015
202666 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2015Q3 | GRF | TL | 2015-09-22 07:55 | 2015-09-22 07:56 |  | Follow up |  | 33 |  |  | 2015
202695 |  |  | 703 Port Macquarie - Boronia St No.1 33kV Line |  | 2015Q3 | PMQ | TL | 2015-09-22 15:01 | 2015-09-22 15:01 | Distance to fault 4.87 km from Port Macquarie 132kV Substation. | Follow up |  | 33 |  |  | 2015
202742 | Animal/Bird | Disc | 330kV Bus Section 1 | Q | 2015Q3 | AR1 | BB | 2015-09-23 16:14 | 2015-09-23 19:18 |  |  | Bird nest 330KV red phase on ISOL 864. | 330 | Workorder No. 366840 was createrd on 23/09/2015 to investigate this issue. [bird nest on the insulator suppot and has a piece of wire hanging down the insulator on R PH]. Workorder is still open. |  | 2015
203821 |  |  | No.3 Transformer 330/132/11kV | E | 2015Q3 | AR1 | TX | 2015-09-23 16:14 | 2015-09-23 19:18 |  |  |  | 330 |  | Forced | 2015
203822 |  |  | 86 Tamworth 330 - Armidale 330kV TL | E | 2015Q3 | AR1, TA1 | TL | 2015-09-23 16:14 | 2015-09-23 19:18 |  |  |  | 330 |  | Forced | 2015
203823 |  |  | 8C Armidale - Dumaresq 330kV TL | E | 2015Q3 | AR1, DMQ | TL | 2015-09-23 16:14 | 2015-09-23 19:18 |  |  |  | 330 |  | Forced | 2015
204398 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2015Q3 | MRE | TL | 2015-09-26 00:44 | 2015-09-26 02:50 | Essential advised found a 66kV Pole down in a sectionalised part of the line | Follow up |  | 66 |  |  | 2015
204399 | Unknown | TL | 96M Narrabri - Moree 132kV TL | Q | 2015Q3 | MRE, NB2 | TL | 2015-09-26 04:38 | 2015-09-26 04:38 | DTF 57.05 | Follow up | Successful trip and reclose. Cause unknown. Weather fine. | 132 |  |  | 2015
204400 | Lightning/Storm | TL | 5A4 Bayswater - Wollar 500kV TL | Q | 2015Q3 | BAY, WOL | TL | 2015-09-26 05:33 | 2015-09-26 05:33 |  | Follow up | Successful trip and reclose. Cause unknown. Weather unknown. | 500 |  |  | 2015
204403 |  |  | 862 Ingleburn - Minto 66kV Line | N | 2015Q3 | ING | TL | 2015-09-26 20:38 | 2015-09-26 20:38 |  | Follow up |  | 66 |  |  | 2015
204529 | HV Equipment | CB | No.1 Transformer 330/132/16kV | E | 2015Q3 | SE1 | TX | 2015-09-29 20:03 | 2015-09-29 23:27 | CB5412 White phase topped up with SF6. No.1 Transformer returned to service. | Follow up | CB5412 White phase topped up with SF6. No.1 Transformer returned to service. | 330 | SF6 top up completed. | Forced | 2015
204530 |  |  | No.1 Auxiliary Transformer 16kV/415V |  | 2015Q3 | SE1 | TX | 2015-09-29 20:03 | 2015-09-29 23:27 |  |  |  | 16 |  |  | 2015
204559 | Unknown | TL | 99J Yanco - Griffith 132kV TL | Q | 2015Q3 | GRF, YA2 | TL | 2015-09-30 05:41 | 2015-09-30 05:41 |  | Follow up | Successful trip and reclose. Cause unknown. Weather fine. | 132 |  |  | 2015
204589 | Protection | Prot | No.1 Transformer 330/132/11kV | Z | 2015Q3 | MRK | TX | 2015-09-30 15:23 | 2015-09-30 16:47 | Transformer was out of service for a planned outage, trip occured on energising the transformer. | Follow up | Transformer was out of service for a planned outage, trip occured on energising the transformer. No.2 Protection White Phase operated. Asset monitoring gave clearance to RTS. | 330 |  | Fault | 2015
204590 | Contractor Error | Proc | No.3 Tie | E | 2015Q3 | BFD | UG | 2015-09-30 15:28 | 2015-10-09 15:58 |  | Follow up | BFS NO3TIE BT3 GIL SF6 DEPLETED and BFS NO3TIE BT3 GIL SF6 LOW alarms. Advised ABB staff knocked a density meter on the No3 Tie and this meter started leaking so the AA staff removed the meter and stopped the leak. The ABB staff were packing their equipment up after they had completed their work. Advised spare bay density meters are different and parts will need to be booked out of store and replaced (source: OPSLog). | 132 |  | Forced | 2015
206318 | Staff Error | Proc | No.3 Transformer 132/33/11kV | Z | 2015Q4 | WG2 | TX | 2015-10-01 13:39 | 2015-10-01 14:29 | Fitter advised accidentally tripped transformer while carrying out transformer temperature checks. | Follow up | Fitter advised accidentally tripped transformer while carrying out transformer temperature checks. | 132 |  | Fault | 2015
206319 |  |  | No.3 Depot Tranformer 11kV/415V | N | 2015Q4 | WG2 | G | 2015-10-01 13:39 | 2015-10-01 14:29 |  |  |  | 11 |  |  | 2015
206464 |  |  | 9MC Orange North - Cadia 132kV Line |  | 2015Q4 | ONO | TL | 2015-10-02 20:39 | 2015-10-03 19:09 | Essential Energy advised that the Cadia 100MVA Transformer is on fire and emergency services are on site. | Follow up |  | 132 |  |  | 2015
206466 | Unknown | TL | 5A3 Bayswater - Mt Piper 500kV TL | Q | 2015Q4 | BAY, MTP | TL | 2015-10-03 05:40 | 2015-10-03 05:40 | Wheather report show that the weather should be fine however the weather radar indicates patchy rain in the area. | Follow up | Successful trip and reclose. Weather reports show that the weather should be fine however the weather radar indicates patchy rain in the area. | 500 |  |  | 2015
206510 | HV Equipment | TX | No.5 Transformer 330/132/11kV | E | 2015Q4 | SYN | TX | 2015-10-03 09:36 | 2015-10-08 17:30 | Pressure relief alarms received on Scada. No.5 Transformer normally off-loaded. Isolated for investigation. | Follow up | Pressure relief alarms received on Scada. No.5 Transformer normally off-loaded. Isolated for investigation. | 330 |  | Forced | 2015
206522 |  |  | 705 Coffs Harbour - South Coffs Harbour 66kV Line |  | 2015Q4 | COF | TL | 2015-10-05 10:29 | 2015-10-05 10:55 | Outage reqd by EE to trim tree branches touching conductors. | Follow up |  | 66 |  |  | 2015
206523 | Unknown | TL | 77 Wallerawang - Ingleburn 330kV TL | Z | 2015Q4 | ING, WW1 | TL | 2015-10-05 11:04 | 2015-10-05 18:47 | Property owner has advised that a load explosion occurred and a fire ball was seen travel between two towers and started a bush fire. | Follow up | Property owner has advised that a load explosion occurred and a fire ball was seen travel between two towers and started a bush fire. The 77 line arc'ed on to a fence which caused spot fires along the fence line. | 330 | Committee of Enquiry formed, investigations of the event and its cause, responses by stakeholders, review of AM strategies, maintenance policies and practices, review of public safety with conclusions and recommendations. Final report submitted 6/11/15 to general council. | Fault | 2015
206524 | HV Equipment | CB | No.1 Capacitor | E | 2015Q4 | SYW | CAP | 2015-10-05 14:20 | 2015-10-05 15:41 |  |  | CB SF6 Topup | 132 | Work order No. 367823 was created on 6/10/2015 to top up this CB. Work order closed now. | Forced | 2015
206525 | HV Equipment | CB | 132kV B Bus 1-2 Section CB 4112 | Q | 2015Q4 | SYW | CB | 2015-10-05 13:58 | 2015-10-06 07:21 |  | Follow up | CB SF6 TOPUP | 132 | Work order No. 367824 was created on 6/10/2015 to top up this CB. Work order closed now. |  | 2015
206529 |  |  | No.3 Transformer 330kV A CB 5432A | Q | 2015Q4 | TOM | CB | 2015-10-05 22:10 | 2015-10-06 15:30 |  |  |  | 330 |  |  | 2015
206530 | HV Equipment | CB | 330kV A Bus | Q | 2015Q4 | TOM | BB | 2015-10-05 22:10 | 2015-10-05 22:41 |  |  | For the Outage of Tomago 330kV A Bus, due to CB 5432A CB Abnormal ( no oil Pressure) TAC had transferred No.3 Transformer load to No.2 Transformer After clearance from TAC for the de-energising of the 330kV A Bus. TAC had ramped down approx 330MW and offloaded No1 & 1A Transformer and OPENED C.B 5412 and this impediatley tripped No.2 Transformer LV CB Q0.06 at TAC. Operator had advised that trip caused by UFLS. Frequency at the time was >50hz Load previous was 647MW and load shed was 307MW ( No.2 Transformer load) for a total load at Tomago of 340MW. During this time the 330kV A Bus 330Kv was taken out of service at 2210 and returned to service at 2242hrs. A Bus total outage time was 33mins | 330 | Work order No. 367820 was created on 5/10/2015 to investigate this issue. Work order is still open. [Investigate and replace blown Uzit on CB hydraulic system. Replace hydraulic oil and carry out timing tests on CB.] Andrew Kingsmill to advise when this investigation can be considered complete. [20/07/2016] Andrew Kingsmill advised report complete and signed off, may be closed. |  | 2015
206531 |  |  | No.8 Transformer | E | 2015Q4 | TOM | TX | 2015-10-05 22:10 | 2015-10-05 22:41 |  |  |  | 330 |  | Forced | 2015
206536 |  |  | 95 Newcastle - Tomago 330kV TL | E | 2015Q4 | NEW, TOM | TL | 2015-10-05 22:10 | 2015-10-05 22:41 |  |  |  | 330 |  | Forced | 2015
206537 |  |  | No.1 Transformer | E | 2015Q4 | TOM | TX | 2015-10-05 22:10 | 2015-10-05 22:41 |  |  |  | 330 |  | Forced | 2015
206596 |  |  | 950 Newcastle - Jesmond 132kV Line |  | 2015Q4 | NEW | TL | 2015-10-07 00:43 | 2015-10-07 15:01 |  | Follow up |  | 132 |  |  | 2015
206618 |  |  | Misc LV (Haymarket 330kV Substation) | N | 2015Q4 | HYM | LV | 2015-10-08 06:36 | 2015-10-31 12:06 |  |  |  | 0 |  |  | 2015
206690 |  |  | 822 Deniliquin tee Moulamein CB 8222 | N | 2015Q4 | DN2 | CB | 2015-10-07 02:03 | 2015-10-07 02:03 |  | Follow up |  | 66 |  |  | 2015
206698 | Relay | Prot | No.4 Transformer 330/132/11kV | E | 2015Q4 | COF | TX | 2015-10-08 18:00 | 2015-10-10 11:33 |  |  | Advised No1 protection relay self diagnostic indicating relay faulty. Relay will be replaced tomorrow. Decision to take Transformer out of service in consultation with Protection Design, Field Services, Asset Management and NCM. Relay is a known type fault. REF is not duplicated on No2 Prot. No4 TX will remain on open CB available for emergency use due to No1 Protection Relay Fault. No1 Protection Diff and REF have been made non-auto on No1 Prot. Buchholz and O/Pressure remain auto on No1 Protection. If used in Emergency Diff and REF will not be functional on No1 Prot. | 330 |  | Forced | 2015
206761 | LV/MECH Fail | SVC | No.2 Static VAr Compensator | Z | 2015Q4 | BKH | SVC | 2015-10-09 18:47 | 2015-10-09 20:50 | Byron Mills advises review of No.2 SVC event log suggests similar issue occurring with the SVC Current Pulse Supervision circuit when de-energising the X2 Buronga Line Reactors as occurred when energising No.1 and No.2 Transformers. No.2 SVC remained well within operating limits and advises available to be returned to service. | Follow up | Byron Mills advises review of No.2 SVC event log suggests similar issue occurring with the SVC Current Pulse Supervision circuit when de-energising the X2 Buronga Line Reactors as occurred when energising No.1 and No.2 Transformers. No.2 SVC remained well within operating limits and advises available to be returned to service. | 22 |  | Fault | 2015
206762 |  |  | 82K/1 Queanbeyan - Bungendore tee Sutton 66kV Line |  | 2015Q4 | QBY | TL | 2015-10-09 19:10 | 2015-10-09 23:19 | Patrol completed on 82K/1 Queanbeyan to Bungendore tee Sutton 66kV Feeder by Essential Energy staff and no issues found. | Follow up |  | 66 |  |  | 2015
206763 |  |  | 824 Yass - Yass Town 66kV Line |  | 2015Q4 | YSN | TL | 2015-10-09 22:13 | 2015-10-09 22:14 |  | Follow up |  | 66 |  |  | 2015
206764 |  |  | No.3 Transformer 132/66/11kV | N | 2015Q4 | YSN | TX | 2015-10-09 22:13 | 2015-10-09 22:14 |  |  |  | 132 |  |  | 2015
206765 |  |  | 836 Murrumburrah - Cootamundra 66kV Line |  | 2015Q4 | MRU | TL | 2015-10-09 22:58 | 2015-10-09 22:58 | No.2 Protection details are for multiple operations (refer to FEOR 2015-F-400). | Follow up |  | 66 |  |  | 2015
206766 |  |  | 836 Murrumburrah - Cootamundra 66kV Line |  | 2015Q4 | MRU | TL | 2015-10-10 02:10 | 2015-10-10 08:10 | No.2 Protection details are for multiple operations (refer to FEOR 2015-F-400). Patrol of line by Essential Energy found conductor on ground. Line Isolated and Earthed under HVPRI 61728 for repairs. | Follow up |  | 66 |  |  | 2015
206767 |  |  | 828 Mt Piper 132 - Portland tee BCSC 66kV Line |  | 2015Q4 | MPP | TL | 2015-10-10 03:08 | 2015-10-10 03:08 |  | Follow up |  | 66 |  |  | 2015
206768 | HV Equipment | TX | No.5 Transformer 330/132/11kV | E | 2015Q4 | SYN | TX | 2015-10-10 06:20 | 2015-11-11 09:49 | Fleeting pressure relief alarms. Transformer de-energised as a precaution. Follow up required | Follow up | Fleeting pressure relief alarms. Transformer de-energised as a precaution. Follow up required | 330 | Work order No. 367822 was created on 06/10/2015 to investigate this issue. Work order is still open. [Called out and Found moisture and corrosion in micro switch and the junction box it was enclosed in. L.O 7/10/15 Called out again for same alarm but this time it was fleeting. new micro switch ordered and waiting for replacemet. L.O 10/10/15] | Forced | 2015
206770 | Bushfire | TL | 21 Sydney North - Tuggerah 330kV TL | Q | 2015Q4 | SYN, TGH | TL | 2015-10-10 12:16 | 2015-10-10 12:16 | No lightning in area. RFS web site indicated that there was hazard reduction burn in the area of Mt White between structures 114 & 109 RFS staff on site reported a flashover ( similar to lightning strike) due to dense smoke. All staff are OK. No reclose of CB 212B by design. | 14/10/2015 12:16:00 ¦ Follow up ¦ N/A ¦ Noted for next aerial inspection. | No lightning in area. RFS web site indicated that there was hazard reduction burn in the area of Mt White between structures 114 & 109 RFS staff on site reported a flashover ( similar to lightning strike) due to dense smoke. All staff are OK. No reclose of CB 212B by design. | 330 |  |  | 2015
206771 |  |  | 21 Sydney North - Tuggerah 330kV TL |  | 2015Q4 | SYN, TGH | TL | 2015-10-10 12:16 | 2015-10-10 12:16 |  |  |  | 330 |  |  | 2015
206772 | HV Equipment | CB | No.2 Transformer 132kV B CB 4422B | Q | 2015Q4 | SE1 | CB | 2015-10-10 12:58 | 2015-10-10 15:54 | Received LV CB abnormal on Scada. HMI indicates low SF6 alarm. Opened CB 4422B and arranged for staff to attend site. | Follow up | CB SF6 Topup | 132 | Work order No. 368869 was created on 12/10/2015 to top up this CB. Work order closed now. [FOUND LOW GAS CB4422B. ISOLATED, TOPPED UP, RESTORED.] |  | 2015
206773 |  |  | Broken Hill - South 22kV Line |  | 2015Q4 | BKH | TL | 2015-10-10 17:07 | 2015-10-10 17:07 |  | Follow up |  | 22 |  |  | 2015
206774 | HV Equipment | CB | 932 Sydney West - Mt Druitt 132kV Line | E | 2015Q4 | SYW | TL | 2015-10-10 18:13 | 2015-10-10 19:05 |  |  | CB 9322 SF6 Topup | 132 | No work order in Ellipse. | Forced | 2015
206776 |  |  | 661 Armidale - Oaky PS 66kV Line |  | 2015Q4 | AR1 | TL | 2015-10-11 18:20 | 2015-10-11 18:20 |  | Follow up |  | 66 |  |  | 2015
206844 | Relay Setting | SVC | No.2 Static VAr Compensator | Z | 2015Q4 | BKH | SVC | 2015-10-12 10:45 | 2015-10-12 11:21 | No.2 SVC tripped while AGL were carrying out MVar import/Export testing on No.2 Solar plant. Wagga Maintenance staff advised that the Pulse supervision relay is quite sensetive and can pick up small sudden variations in system parameters which apparntly could have lead to thr tripping. Further investigations will be carried out | Follow up | No.2 SVC tripped while AGL were carrying out MVar import/Export testing on No.2 Solar plant. Wagga Maintenance staff advised that the Pulse supervision relay is quite sensetive and can pick up small sudden variations in system parameters which apparntly could have lead to thr tripping. Further investigations will be carried out | 22 | Awaiting input from Power Systems Analysis, Tony Gray to follow up. | Fault | 2015
206854 |  |  | 0896 Koolkhan - Maclean 66kV Line |  | 2015Q4 | KLK | TL | 2015-10-12 18:11 | 2015-10-12 18:11 |  | Follow up |  | 66 |  |  | 2015
206855 | Lightning/Storm | TL | 96M Narrabri - Moree 132kV TL | Q | 2015Q4 | MRE, NB2 | TL | 2015-10-13 01:28 | 2015-10-13 01:28 |  | 14/10/2015 12:16:00 ¦ Follow up ¦ N/A ¦ Noted for next aerial inspection. | Successful trip and reclose. Storms in the area. | 132 |  |  | 2015
206856 | Unknown | TL | 99L Deniliquin - Coleambally 132kV TL | Q | 2015Q4 | CLY, DN2 | TL | 2015-10-13 05:23 | 2015-10-13 05:23 |  | Follow up | Succesful trip and reclose, cause unknown. | 132 |  |  | 2015
206869 | HV Equipment | CB | 35 Bannaby CB 352 | Q | 2015Q4 | MRN | CB | 2015-10-13 07:42 | 2015-10-13 13:10 |  |  | SF6 Inspection on CB 352. | 330 | No work order in Ellipse. |  | 2015
206871 | HV Equipment | CB | No.1 Transformer 132/66/11kV | E | 2015Q4 | KLK | TX | 2015-10-13 07:55 | 2015-10-13 12:24 |  |  | SF6 Topup on CB 4412 | 132 | Work order No. 369301 was created on 16/10/2015 to investigate this issue. Work order is still open. [13.10.15 SF6 Low alarm up. Ops had taken CB and Tx OUT OF Service. Topped up gas G.Robinson Replace cb pole 22-10-15] | Forced | 2015
206872 | Contractor Error | Proc | 945 Wellington - Molong tee Well'n Town 132kV TL | Q | 2015Q4 | MOL, WL1 | TL | 2015-10-13 08:21 | 2015-10-13 08:21 | Project staff at Molong report that a contractor operating a skid steer excavator (Bobcat) has reversed onto the structure stay of 945 and when the machine was driven off the stay the line bounced and caused white phase to flash over. | 15/10/2015 10:53:00 ¦ Follow up | Project staff at Molong report that a contractor operating a skid steer excavator (Bobcat) has reversed onto the structure stay of 945 and when the machine was driven off the stay the line bounced and caused white phase to flash over. Protection distance to fault data showed fault occurred 6.6km from Molong Substation making the closest structure 22. An after fault patrol was organised. The patrol was of structure 22 and a few structures either side. No defects were found. | 132 |  |  | 2015
206886 |  |  | 84A Finley - Jerilderie 66kV Line |  | 2015Q4 | FNY | TL | 2015-10-13 08:31 | 2015-10-13 10:34 | Essential Energy advise of bird strike on their 22kV Bus in Zone sub. This initiated fault thrower operatiion. | Follow up |  | 66 |  |  | 2015
206906 | HV Equipment | VT | No.4 Transformer 330/132/11kV | E | 2015Q4 | SYW | TX | 2015-10-14 04:39 | 2015-10-14 08:07 |  |  | Replacement of Faulty MVT. | 330 | Work order No. 368881 was created on 13/10/2015 to replaced blue phase MVT as it was leaking. Work order closed now. Requires accuracy testing. | Forced | 2015
206957 | HV Equipment | Reg | No.1 Transformer 132/66/11kV | Z | 2015Q4 | CMA | TX | 2015-10-14 06:20 | 2015-10-16 06:53 | No.1 Transformer - No visible signs of fault No.1 Regulator - No visible signs of fault | Follow up | No.1 Transformer at Cooma 132kV Substation tripped. Staff on site report cause is a White Phase 11kV Regulator fault. | 132 | Work order No. 369004 was created on 14/10/2015 to investigate this issue. Work order is still open. [No1 Regulator/TX tripped on differential protection white phase,no obvious reasons eg birds etc. Needs investigating] | Fault | 2015
207103 | HV Equipment | CB | No.1 Transformer 132/66/11kV | E | 2015Q4 | KLK | TX | 2015-10-15 19:05 | 2015-10-27 14:54 |  |  | Repair SF6 leak on CB 4412 | 132 | Same as above. | Forced | 2015
207161 | Tree/Ground | TL | 5A4 Bayswater - Wollar 500kV TL | E | 2015Q4 | BAY, WOL | TL | 2015-10-16 11:38 | 2015-10-16 18:20 | Line taken out of service due to trees encroaching the line | 26/11/2015 15:51:00 ¦ Follow up ¦ Nil ¦ Nil | Line taken out of service due to trees encroaching the line. | 500 |  | Forced | 2015
207213 |  |  | 813 Tamworth 132 - Currabubula 66kV Line |  | 2015Q4 | TMW | TL | 2015-10-17 07:56 | 2015-10-17 10:01 | No indication as to any attempt at auto reclose. HMI events say Auto reclose inhibit. | Follow up |  | 66 |  |  | 2015
207216 |  |  | 971 Yass - Goulburn tee Cullerin Range tee Gunning 132kV Line |  | 2015Q4 | YSN | TL | 2015-10-19 05:21 | 2015-10-19 05:21 |  | Follow up |  | 132 |  |  | 2015
207298 |  |  | 817 Wallerawang 132 - Meadow Flat 66kV Line |  | 2015Q4 | WWS | TL | 2015-10-19 14:48 | 2015-10-19 14:48 |  | Follow up |  | 66 |  |  | 2015
207301 |  |  | 800 Wallerawang 132 - Railway 66kV Line |  | 2015Q4 | WWS | TL | 2015-10-19 15:05 | 2015-10-19 15:05 |  | Follow up |  | 66 |  |  | 2015
207305 |  |  | 97L Guthega - Jindabyne Pumps 132kV TL | Y | 2015Q4 | GTH, JDP | TL | 2015-10-19 15:10 | 2015-10-19 15:28 | Trip Caused by SHL Staff working at Jindabyne Pumps | Follow up |  | 132 |  |  | 2015
207334 | Staff Error | Proc | 702 Coffs Harbour - Nana Glen 66kV Line | Q | 2015Q4 | COF | TL | 2015-10-20 08:06 | 2015-10-20 13:03 | No load lost, load transferred to I/S fdr, CB 7022 also reqd a LV/Mech outage to investigate mechanism closing problem. | Follow up | Protection staff where carrying out in service protection maintenance and inadvertently caused the trip. No load lost as a result if this incident. | 66 |  |  | 2015
207341 | Staff Error | Proc | No.1 Reactor | Z | 2015Q4 | DMQ | RX | 2015-10-20 09:13 | 2015-10-20 09:55 | Control system work caused trip of No.1 reactor. | Follow up | Control system work caused trip of No.1 reactor. | 330 |  | Fault | 2015
207405 | LV/MECH Fail | Other | No.3 Transformer 132kV B CB 4432B | Q | 2015Q4 | HYM | CB | 2015-10-20 16:25 | 2015-10-20 18:01 |  |  | Stephen Barton advises that whilst following up on a No.3 Transformer 132kV B CB 4432B alarm, it would seem that only 1 Trip coil is operational. | 132 | AMC to follow up. [8/6/2016] Trip coil replaced on 2nd March 2016. Can be closed. |  | 2015
207482 | Animal/Bird | CB | No.4 Capacitor | E | 2015Q4 | CMA | CAP | 2015-10-21 11:35 | 2015-10-21 12:31 |  |  | Remove Birds nest from CB Mech box. | 66 |  | Forced | 2015
207636 |  |  | Broken Hill - Solar Plant 2 22kV Line |  | 2015Q4 | BKH | TL | 2015-10-21 14:43 | 2015-10-21 16:46 |  | Follow up |  | 22 |  |  | 2015
207637 |  |  | No.1 Taree - Council Bootawa 33kV Line |  | 2015Q4 | TRE | TL | 2015-10-21 18:15 | 2015-10-21 18:15 |  | Follow up |  | 33 |  |  | 2015
207639 |  |  | 879 Narrabri - Wee Waa 66kV Line |  | 2015Q4 | NB2 | TL | 2015-10-22 02:21 | 2015-10-22 02:21 |  | Follow up |  | 66 |  |  | 2015
207774 |  |  | Broken Hill - Solar Plant 1 22kV Line |  | 2015Q4 | BKH | TL | 2015-10-22 14:04 | 2015-10-22 14:57 |  | Follow up |  | 22 |  |  | 2015
207951 | Secondary Equipment | Cont | 702 Coffs Harbour - Nana Glen 66kV Line | Q | 2015Q4 | COF | TL | 2015-10-23 08:07 | 2015-10-23 16:48 | Suspect earth fault within control system. | Follow up | CB unsolicited trip. Suspect earth fault within control system. | 66 |  |  | 2015
207957 | Unknown | Cont | 993 Wagga 330 - Gadara 132kV TL | Z | 2015Q4 | GAD, WG1 | TL | 2015-10-24 06:22 | 2015-10-24 08:44 | NOTE: Published FEOR shows times in DST. 970 Out of service for pole replacement work. 993 TAR at Wagga 330 - 993 Trip at Gadara. Approximately 25MW load lost at Visy. Blowering generator maintained approximately 35MW (Tumut 132 & Visy load) for 9 mins and then we lost supply to Tumut 132 substation on UFLS. Blowering generator shut down on request of SHL. RTU failure received from Gadara and loss of comms with site. Delays in restoration due to staff attending site (approx 1 hr away) and loss of comms to site. Restoration of 993 T/L achieved via a dead line close of both 9932CB & 99P2 CB at Gadara and then energised from Wagga 330. | Follow up | 970 Out of service for pole replacement work. 993 TAR at Wagga 330 - 993 Trip at Gadara. Approximately 25MW load lost at Visy. Blowering generator maintained approximately 35MW (Tumut 132 & Visy load) for 9 mins and then we lost supply to Tumut 132 substation on UFLS. Blowering generator shut down on request of SHL. RTU failure received from Gadara and loss of comms with site. Delays in restoration due to staff attending site (approx 1 hr away) and loss of comms to site. Restoration of 993 T/L achieved via a dead line close of both 9932CB & 99P2 CB at Gadara and then energised from Wagga 330. | 132 | Protection maloperation caused of loss loss of supply. Investigation report noting several recommendations drafted. Line patrolled, no fault found. No further action from TL&C Asset Mgr. Andrew Kingsmill to advise when this investigation can be considered complete. [20/07/2016] Tim Barnes advised report complete and signed off, may be closed. | Fault | 2015
207979 |  |  | 957 Vales Pt - Ourimbah tee Morisset 132kV Line |  | 2015Q4 | VP1 | TL | 2015-10-25 08:33 | 2015-10-25 17:57 | 957 Transmission line energised at Ausgrid's request. | Follow up |  | 132 |  |  | 2015
208067 |  |  | 868 Taree - Bohnock Tee Hallidays Point 66kV Line |  | 2015Q4 | TRE | TL | 2015-10-26 15:49 | 2015-10-26 15:49 |  | Follow up |  | 66 |  |  | 2015
208068 | Relay | Prot | 863 Taree - Whitbread St Zone SS 66kV Line | Q | 2015Q4 | TRE | TL | 2015-10-26 15:46 | 2015-10-26 23:13 | Split Bus at Essential Energy's Whitbread Zone. 6MW tripped off and Essential Energy manually restored load onto 861 FDR. 863 Feeder returned to service at 23:13hrs following No.1 protection relay replacement. | Follow up | Replacement of defective power pack on No.1 relay. | 66 |  |  | 2015
208069 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2015Q4 | MRE | TL | 2015-10-26 17:11 | 2015-10-26 17:11 |  | Follow up |  | 66 |  |  | 2015
208070 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2015Q4 | MRE | TL | 2015-10-26 17:12 | 2015-10-26 17:12 |  | Follow up |  | 66 |  |  | 2015
208072 | Staff Error | CT | No.4 Transformer 330/132/11KV | E | 2015Q4 | SYN | TX | 2015-10-27 01:10 | 2015-10-28 14:08 |  | Follow up | Advises No.4 Transformer 330kV C.T. SF6 gas pressure OK on Red and Blue phases. White phase has an incorrect SF6 pressure gauge fitted and this gauge is indicating off scale at the high pressure end of the scale. Gas pressure can be checked using the SF6 gas filling equipment pressure gauge. | 330 | Work order 371960 created. New SF6 gauge required. | Forced | 2015
208102 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q4 | CW2 | TL | 2015-10-27 03:42 | 2015-10-27 08:27 | Essential Energy advise that a "pole is down" in their system. | Follow up |  | 66 |  |  | 2015
208104 |  |  | 836 Murrumburrah - Cootamundra 66kV Line |  | 2015Q4 | MRU | TL | 2015-10-27 07:02 | 2015-10-27 11:13 | SCADA trend indicates 6.3MW lost load. | Follow up |  | 66 |  |  | 2015
208132 |  |  | Station Transformer 1A |  | 2015Q4 | LD1 | TX | 2015-10-27 10:45 | 2015-10-27 11:14 | PowerStation advised that staff working on 3.3kV boards caused trip. | Follow up |  | 330 |  |  | 2015
208137 |  |  | 96F Stroud - Tomago 330 132kV TL | X | 2015Q4 | TOM | TL | 2015-10-27 16:08 | 2015-10-27 16:58 |  |  |  | 132 |  |  | 2015
208359 | Lightning/Storm | TL | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Q | 2015Q4 | AR1, COF | TL | 2015-10-28 00:29 | 2015-10-28 00:29 |  | 13/11/2015 15:25:00 ¦ Follow up ¦ Noted for next routine aerial patrol in September/October 2016. | Successful trip and reclose during storms. | 132 |  |  | 2015
208421 | HV Equipment | VT | No.4 Transformer 330/132/11kV | E | 2015Q4 | SYW | TX | 2015-10-28 17:10 | 2015-10-28 18:15 |  |  | Advised No.4 transformer 132kV red phase C.V.T. is leaking. | 330 |  | Forced | 2015
208588 | LV/MECH Fail | SVC | No.1 Static VAR Compensator | E | 2015Q4 | LSM | SVC | 2015-10-29 10:00 | 2015-10-29 10:09 |  |  | Filed staff advise cooling water leak on No1 SVC. Request outage as a bleed screw is leaking and will reqiure changing a washer. | 132 |  | Forced | 2015
208850 |  |  | 84A Finley - Jerilderie 66kV Line |  | 2015Q4 | FNY | TL | 2015-10-31 07:00 | 2015-10-31 07:00 |  | Follow up |  | 66 |  |  | 2015
208851 | Unknown | TL | 94P Molong - Manildra 132kV TL | Q | 2015Q4 | MOL, MNL | TL | 2015-10-31 06:50 | 2015-10-31 06:50 |  | 10/11/2015 11:32:00 ¦ Follow up ¦ This area is noted for the next routine aerial patrol scheduled for September/October 2016 | Successful trip and reclose, cause unknown. | 132 |  |  | 2015
208855 |  |  | 824 Yass - Yass Town 66kV Line |  | 2015Q4 | YSN | TL | 2015-10-31 14:28 | 2015-10-31 15:42 |  | Follow up |  | 66 |  |  | 2015
208856 |  |  | No.3 Transformer 132/66/11kV |  | 2015Q4 | YSN | TX | 2015-10-31 14:28 | 2015-10-31 15:42 |  |  |  | 132 |  |  | 2015
208857 |  |  | Broken Hill - West 22kV Line |  | 2015Q4 | BKH | TL | 2015-10-31 17:29 | 2015-10-31 17:29 |  | Follow up |  | 22 |  |  | 2015
208865 |  |  | 84A Finley - Jerilderie 66kV Line |  | 2015Q4 | FNY | TL | 2015-11-01 14:08 | 2015-11-01 14:08 |  | Follow up |  | 66 |  |  | 2015
208866 |  |  | 84A Finley - Jerilderie 66kV Line |  | 2015Q4 | FNY | TL | 2015-11-01 14:16 | 2015-11-01 14:16 |  | Follow up |  | 66 |  |  | 2015
208867 |  |  | 84A Finley - Jerilderie 66kV Line |  | 2015Q4 | FNY | TL | 2015-11-01 14:20 | 2015-11-01 14:20 |  | Follow up |  | 66 |  |  | 2015
208868 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2015Q4 | GRF | TL | 2015-11-01 15:42 | 2015-11-01 15:42 | Storms in vicinity | Follow up |  | 33 |  |  | 2015
208869 |  |  | 7L5 Yanco - Murrami 33kV Line |  | 2015Q4 | YA2 | TL | 2015-11-01 15:48 | 2015-11-01 15:48 | Storms in area. Yanco Distance to Fault = 9.94km | Follow up |  | 33 |  |  | 2015
208870 |  |  | No.5 Wagga 132 - Macleay St 66kV Line |  | 2015Q4 | WG2 | TL | 2015-11-01 16:46 | 2015-11-01 18:15 | SO/Essential Energy advised that the they lost about 3MW load with this trip but the load was transferred to No.3 Coleman Street 66kV Feeder with in 10 minutes and restored back to normal at 18:17 when No.5 Mcleay St 66kV Feeder was energised. | Follow up |  | 66 |  |  | 2015
208871 |  |  | 83F Wagga North - Junee 66kV Line |  | 2015Q4 | WGN | TL | 2015-11-01 16:51 | 2015-11-01 16:51 | Fault at 17:04hrs Fault duration 18.3ms | Follow up |  | 66 |  |  | 2015
208872 | Lightning/Storm | TL | 21 Sydney North - Tuggerah 330kV TL | Q | 2015Q4 | SYN, TGH | TL | 2015-11-01 19:06 | 2015-11-01 19:06 | Time of fault | Follow up | Successful trip and reclose during storms. | 330 |  |  | 2015
208873 | Lightning/Storm | TL | 92Z Sydney North - Sydney East tee Mt Colah 132kV TL | Q | 2015Q4 | SE1, SYN | TL | 2015-11-01 19:14 | 2015-11-01 19:14 | 92Z T/L Auto reclosed at Sydney East end successfully. SO Ausgrid advised. Ausgrid advised that they lost 7.6 MW at Somersby as their end did not Auto reclose. Load restored manually by Ausgrid from Gosford vis 95E T/L. NCM advised. | 25/11/2015 07:37:00 ¦ Follow up ¦ Nil | Trip and reclose during storms. Reclose was successful at Sydney East, however was unsuccessful at Ausgrid's Mt Colah substation. This resulted in approximately 8MW of lost load for 6 minutes. | 132 | Failure of Ausgrid CB to reclose resulted in loss of supply. A check of the Indji system did not identify any lightning on the TransGrid section of the line. There is no recording of lightning away from the TransGrid infrastructure. It is expected that the line tripped due to a lighting strike in the Ausgrid section of line. No further works by asset manager. |  | 2015
208874 |  |  | 92Z Sydney North tee Mt Colah 132kV CB 92Z2 | N | 2015Q4 | SE1 | CB | 2015-11-01 19:14 | 2015-11-01 19:14 |  |  |  | 132 |  |  | 2015
208875 |  |  | 92Z Sydney East tee Mt Colah CB 92Z2 | N | 2015Q4 | SYN | CB | 2015-11-01 19:14 | 2015-11-01 19:14 |  |  |  | 132 |  |  | 2015
208876 |  |  | 940 Wallerawang 132 - Warimoo tee North Katoomba 132kV Line |  | 2015Q4 | WWS | TL | 2015-11-01 18:29 | 2015-11-01 18:29 |  | Follow up |  | 132 |  |  | 2015
208877 |  |  | 941 Wallerawang 132 - Lawson tee North Katoomba 132kV Line |  | 2015Q4 | WWS | TL | 2015-11-01 18:29 | 2015-11-01 18:29 | Tripped at the same time as 940 Wallerawang to Warrimoo Tee North Katoomba 132kV T/L trip and Reclose | Follow up |  | 132 |  |  | 2015
208909 | HV Equipment | Disc | No.3 Capacitor | E | 2015Q4 | SYW | CAP | 2015-11-02 14:00 | 2016-02-02 17:00 |  |  | Advised the #3 Cap at Sydney West Substation has a defective Disconnector 4733 on white phase. It will not close fully under manual operation. | 132 |  | Forced | 2015
209036 |  |  | 6501 Koolkhan - Casino 66kV Line |  | 2015Q4 | KLK | TL | 2015-11-03 16:14 | 2015-11-03 16:14 |  | Follow up |  | 66 |  |  | 2015
209037 | Relay | Prot | No.2 Capacitor | Q | 2015Q4 | YA2 | CAP | 2015-11-03 15:33 | 2015-12-03 16:54 |  |  | Requested to investigate Prot2 Fault alarm received at 08:37 on No.2 Capacitor at Yanco 132kV Substation. | 33 | Relay replaced. |  | 2015
209132 | Staff Error | Proc | Unit 11 Uranquinty PS CB 42A2 | Q | 2015Q4 | URQ | CB | 2015-11-04 09:51 | 2015-11-04 10:50 | Due to initiation of runback stage 2 @ WG1 | Follow up | At 09:51hrs Units 1-4 tripped at Uranquinty. 300MWs of generation interrupted. Staff LV link switching error found to be the cause. | 132 |  |  | 2015
209133 |  |  | Unit 12 Uranquinty PS CB 42B2 | Q | 2015Q4 | URQ | CB | 2015-11-04 09:51 | 2015-11-04 10:51 |  |  |  | 132 |  |  | 2015
209134 |  |  | Unit 13 Uranquinty PS CB 42C2 | Q | 2015Q4 | URQ | CB | 2015-11-04 09:51 | 2015-11-04 10:52 |  |  |  | 132 |  |  | 2015
209135 |  |  | Unit 14 Uranquinty PS CB 42D2 | Q | 2015Q4 | URQ | CB | 2015-11-04 09:51 |  |  |  |  | 132 |  |  | 2015
209155 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2015Q4 | MRE | TL | 2015-11-05 04:44 | 2015-11-05 04:44 |  | Follow up |  | 66 |  |  | 2015
209156 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2015Q4 | MRE | TL | 2015-11-05 04:53 | 2015-11-05 04:53 |  | Follow up |  | 66 |  |  | 2015
209308 |  |  | No.6 Deniliquin - Moama 66kV Line |  | 2015Q4 | DN2 | TL | 2015-11-04 23:51 | 2015-11-05 12:45 | No.6 Moama 66kV Feeder energised only into Moama as Moama load supplied from 84Y feeder. Essential Energy advise length of bark found across conductors on No.6 Moama 66kV Feeder. | Follow up |  | 66 |  |  | 2015
209330 | Lightning/Storm | TL | 86 Tamworth 330 - Armidale 330kV TL | Q | 2015Q4 | AR1, TA1 | TL | 2015-11-06 01:39 | 2015-11-06 01:39 |  | 10/11/2015 16:37:00 ¦ Follow up ¦ Noted for the next aerial patrol in 2016. | Successful trip and reclose during storms. | 330 |  |  | 2015
209427 | LV/MECH Fail | CB | No.2 Transformer 330/66/11kV | E | 2015Q4 | ING | TX | 2015-11-06 15:37 | 2015-11-06 18:04 |  |  | At the completion of Ingleburn 66kV B Bus Prot Maint, CB 3422 failed to close. Paul Hazeltine advises that CB is not serviceable (requires major work approx 8hrs) | 330 | Work order 371678 created on 06/11/2015, now closed. Roller latch in mechanism was found to be worn, pin replaced in the latch. | Forced | 2015
209461 |  |  | Broken Hill - South 22kV Line |  | 2015Q4 | BKH | TL | 2015-11-06 16:57 | 2015-11-06 18:00 | Failed Gas switch in field. | Follow up |  | 22 |  |  | 2015
209462 | HV Equipment | CB | No.1 Transformer 132/66/11kV | E | 2015Q4 | NB2 | TX | 2015-11-06 17:52 | 2015-11-06 19:08 |  |  | CB 4412 SF6 Topup | 132 |  | Forced | 2015
209463 | LV/MECH Fail | CB | No.2 Transformer 330/66/11kV | E | 2015Q4 | ING | TX | 2015-11-07 05:55 | 2015-11-07 13:15 |  |  | At the completion of Ingleburn 66kV B Bus Prot Maint, CB 3422 failed to close. Paul Hazeltine advises that CB is not serviceable (requires major work approx 8hrs) | 330 | Work order 371678 created on 06/11/2015, now closed. Roller latch in mechanism was found to be worn, pin replaced in the latch. | Forced | 2015
209636 | Unknown | TL | 5A4 Bayswater - Wollar 500kV TL | Q | 2015Q4 | BAY, WOL | TL | 2015-11-10 04:44 | 2015-11-10 04:44 | Protection indication from fault recorder - W-E | 13/11/2015 14:58:00 ¦ Follow up ¦ There is a likelihood of further trips during nesting season. ¦ Noted for nest removal during non-nesting season. | Successful trip and reclose, cause unknown. | 500 |  |  | 2015
209713 | LV/MECH Fail | CB | No.1 Capacitor | E | 2015Q4 | KCR | CAP | 2015-11-10 11:51 | 2015-11-12 13:31 |  |  | Outage to repair defective CB 5712 | 330 | Work order 371586 was created on 11/11/2015. Motor limit switch found faulty red phase. Parts sourced. | Forced | 2015
209721 | Unknown | TL | 97K Cooma - Munyang tee Snowy Adit 132kV TL | Q | 2015Q4 | CMA, MNY | TL | 2015-11-10 08:01 | 2015-11-10 08:01 | No trip at Munyang as C.B. 9792 was open at Guthega and no infeed to fault from Munyang. Essential Energy advise TAR of C.B. occurred at Snowy Adit. | 13/11/2015 11:03:00 ¦ Follow up ¦ This area is noted for the next routine aerial patrol scheduled for September/October 2016. | Successful trip and reclose of line 97K at Cooma. No trip at Munyang as C.B. 9792 was open at Guthega and no infeed to fault from Munyang. Essential Energy advise TAR of C.B. occurred at Snowy Adit. Advises following protection details for TAR of 97K Cooma to Munyang tee Snowy Adit 132 kV T/L at Cooma :- No.1 Protection (Optimho Distance Scheme) - Trip, Alarm LEDs. Zone 1, A-N Fault. Multitrip (CA01). Distance to Fault 1.014 km No.2 Protection (THS Distance Scheme) - R-E (Q12), Multitrip (CA02). Switchbay inspected and all equipment OK. Protections reset OK. Carried out check of line in near vicinity of substation and no sign of possible cause of trip. Cause of trip unknown. | 132 |  |  | 2015
209722 |  |  | 97K Cooma tee Snowy Adit 132kV CB 97K2 |  | 2015Q4 | MNY | CB | 2015-11-10 08:01 | 2015-11-10 08:01 |  |  |  | 132 |  |  | 2015
209723 |  |  | 97K Munyang tee Snowy Adit CB 97K2 |  | 2015Q4 | CMA | CB | 2015-11-10 08:01 | 2015-11-10 08:01 |  |  |  | 132 |  |  | 2015
209764 |  |  | 258 Sydney North - Galston 132kV Cable |  | 2015Q4 | SYN | UG | 2015-11-10 18:18 | 2015-12-15 17:36 | 258 Galston 132kV Feeder about 30 seconds after it was energised for customer following a planned outage. Customer investigating the fault. | Follow up |  | 132 |  |  | 2015
209896 |  |  | 7L6 Yanco - Whitton 33kV Line |  | 2015Q4 | YA2 | TL | 2015-11-12 05:58 | 2015-11-12 05:58 | Lightning in area at time | Follow up |  | 33 |  |  | 2015
209911 |  |  | 7L3 Yanco - Kamarah 33kV Line |  | 2015Q4 | YA2 | TL | 2015-11-12 06:12 | 2015-11-12 06:12 | Storms in area | Follow up |  | 33 |  |  | 2015
209927 |  |  | 836 Murrumburrah - Cootamundra 66kV Line |  | 2015Q4 | MRU | TL | 2015-11-12 06:41 | 2015-11-12 06:41 | Storms in area | Follow up |  | 66 |  |  | 2015
209978 |  |  | 850 Tumut - Talbingo tee Jounama Dam 66kV Line |  | 2015Q4 | TU2 | TL | 2015-11-12 08:59 | 2015-11-12 08:59 | Storms in area | Follow up |  | 66 |  |  | 2015
209983 | HV Equipment | TL | 9R5 Wagga 330 - Wagga North 132kV TL | E | 2015Q4 | WG1, WGN | TL | 2015-11-12 12:11 | 2015-11-12 15:10 |  |  | Short notice outage to replace insulator on structure 611. | 132 |  | Forced | 2015
210111 |  |  | 836 Murrumburrah - Cootamundra 66kV Line |  | 2015Q4 | MRU | TL | 2015-11-12 15:34 | 2015-11-12 15:34 |  | Follow up |  | 66 |  |  | 2015
210112 |  |  | 836 Murrumburrah - Cootamundra 66kV Line |  | 2015Q4 | MRU | TL | 2015-11-12 15:36 | 2015-11-12 15:36 |  | Follow up |  | 66 |  |  | 2015
210113 |  |  | 898 Parkes - Trundle 66kV Line |  | 2015Q4 | PKS | TL | 2015-11-12 16:32 | 2015-11-12 16:32 |  | Follow up |  | 66 |  |  | 2015
210117 |  |  | Broken Hill - Railway Town 22kV Line |  | 2015Q4 | BKH | TL | 2015-11-12 17:20 | 2015-11-12 17:20 |  | Follow up |  | 22 |  |  | 2015
210118 |  |  | 847 Murrumburrah - Boorowa 66kV Line |  | 2015Q4 | MRU | TL | 2015-11-12 18:48 | 2015-11-12 18:48 |  | Follow up |  | 66 |  |  | 2015
210119 | Lightning/Storm | TL | O1 Upper Tumut - Canberra 330kV TL | Q | 2015Q4 | CA1, UT1 | TL | 2015-11-13 02:20 | 2015-11-13 02:20 | O1 Upper Tumut Tumut B C.B.. O12B closed via SCADA at Canberra. | 16/11/2015 14:37:00 ¦ Follow up ¦ The location has been noted for the next routine aerial inspection. | Successful trip and reclose during storms. | 330 |  |  | 2015
210120 |  |  | No.6 Tenterfield - Council (Tenterfield Town) 22kV Line |  | 2015Q4 | TTF | TL | 2015-11-13 00:40 | 2015-11-13 04:00 | Essential Energy patrol found conductors on ground. Section of faulted line isolated and earthed within customer system and feeder returned to service at Tenterfield Substation. | Follow up |  | 22 |  |  | 2015
210164 | Lightning/Storm | TL | 99M Yass - Murrumburrah 132kV TL | Q | 2015Q4 | MRU, YSN | TL | 2015-11-13 09:48 | 2015-11-13 09:48 |  | 8/02/2016 12:55:00 ¦ Follow up ¦ Nil | Successful trip and reclose during storms. | 132 |  |  | 2015
210165 | Lightning/Storm | TL | 99M Yass - Murrumburrah 132kV TL | Q | 2015Q4 | MRU, YSN | TL | 2015-11-13 09:51 | 2015-11-13 09:51 |  | 8/02/2016 12:55:00 ¦ Follow up ¦ Nil | Successful trip and reclose during storms. | 132 |  |  | 2015
210191 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q4 | CW2 | TL | 2015-11-13 13:22 | 2015-11-13 13:22 | Trend indicates Wyangala was generating approx 9MW at time of trip | Follow up |  | 66 |  |  | 2015
210199 |  |  | 896 Forbes - West Jemalong 66kV Line |  | 2015Q4 | FB2 | TL | 2015-11-13 14:09 | 2015-11-13 14:09 |  | Follow up |  | 66 |  |  | 2015
210208 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q4 | CW2 | TL | 2015-11-13 14:43 | 2015-11-13 14:43 |  | Follow up |  | 66 |  |  | 2015
210211 |  |  | 856 Wallerawang 132 - Oberon Tee Lillyvale 66kV Line |  | 2015Q4 | WWS | TL | 2015-11-13 15:35 | 2015-11-13 15:35 |  | Follow up |  | 66 |  |  | 2015
210220 | Lightning/Storm | TL | 82 Liddell - Tomago 330kV TL | Z | 2015Q4 | LD1, TOM | TL | 2015-11-13 16:00 | 2015-11-14 14:57 | Line isolated and earth to facilitate repairs at Str 94 | 5/02/2016 16:09:00 ¦ Follow up ¦ The driveway was a private access road, and the property owner was consulted. Public safety was maintained. ¦ Nil | Fallen conductors during thunderstorm. | 330 | Very high intensity lightning strike punchured disc insulator causing conductor to drop over private access road. No damage to conductor. Composite longrods replaced on all phases. Targeted insulator replacements to be considered in the next Renewal and Miantenance Plan. | Fault | 2015
210221 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q4 | CW2 | TL | 2015-11-13 16:05 | 2015-11-13 16:05 |  | Follow up |  | 66 |  |  | 2015
210222 |  |  | 7R2 Kempsey - North St tee Smithtown 33kV Line |  | 2015Q4 | KS2 | TL | 2015-11-13 22:48 | 2015-11-13 22:48 |  | Follow up |  | 33 |  |  | 2015
210223 |  |  | 877 Gunnedah - Keepit PS 66kV Line |  | 2015Q4 | GN2 | TL | 2015-11-14 00:21 | 2015-11-14 00:21 |  | Follow up |  | 66 |  |  | 2015
210226 |  |  | No1 Transformer Tie |  | 2015Q4 | BGE | TL | 2015-11-14 04:02 | 2015-11-14 08:33 | Both Tie transformers tripped resulting in 2MW of load tripped | Follow up |  | 132 |  |  | 2015
210227 |  |  | No2 Transformer Tie |  | 2015Q4 | BGE | TL | 2015-11-14 04:02 | 2015-11-14 08:33 | Both Tie Transformer tripped resulting in 2MW of load tripped | Follow up |  | 132 |  |  | 2015
210228 |  |  | 893/1 Cowra - Grenfell 66kV Line |  | 2015Q4 | CW2 | TL | 2015-11-14 11:11 | 2015-11-14 11:11 |  | Follow up |  | 66 |  |  | 2015
210229 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2015Q4 | MRE | TL | 2015-11-14 13:22 | 2015-11-14 13:22 |  | Follow up |  | 66 |  |  | 2015
210230 |  |  | 804 Tamworth 132 - Nundle 66kV Line |  | 2015Q4 | TMW | TL | 2015-11-14 14:34 | 2015-11-14 14:34 |  | Follow up |  | 66 |  |  | 2015
210252 | Protection | Prot | 703 Port Macquarie - Boronia St No.1 33kV Line | Q | 2015Q4 | PMQ | TL | 2015-11-15 17:41 | 2015-11-16 21:56 | Essential Energy advised no loss of load and 703 Boronia St remained energised from Essential energy system. Faulty No.1 protection relay GE D60 | Follow up | Faulty No.1 protection relay (D60). | 33 |  |  | 2015
210297 |  |  | 13 Sydney South - Kemps Creek 330kV TL | E | 2015Q4 | KCR, SYS | TL | 2015-11-17 05:06 | 2015-11-28 14:07 |  |  |  | 330 |  | Forced | 2015
210320 | HV Equipment | CB | 330kV B Bus 1-2 Section CB 5112 | Q | 2015Q4 | SE1 | CB | 2015-11-16 18:38 | 2015-11-16 19:40 |  |  | CB 5112 SF6 Topup | 330 |  |  | 2015
210406 | HV Equipment | CB | No.2 Transformer 132kV B CB 4422B | Q | 2015Q4 | SE1 | CB | 2015-11-18 06:23 | 2015-11-18 07:54 |  |  | CB 4422B SF6 Topup | 132 |  |  | 2015
210412 | HV Equipment | CB | No.2 Capacitor | Q | 2015Q4 | SE1 | CAP | 2015-11-18 08:46 | 2015-11-18 11:06 |  |  | CB 4722 SF6 Topup | 132 |  |  | 2015
210436 | Unknown | TL | 96F Stroud - Tomago 330 132kV TL | Q | 2015Q4 | TOM | TL | 2015-11-17 14:01 | 2015-11-17 14:01 | Protection flagging added. | 8/12/2015 15:53:00 ¦ Follow up ¦ Nil ¦ Nil | Successful trip and reclose, cause unknown. | 132 |  |  | 2015
210443 |  |  | 97R Cooma - Bega tee Steeple Flat 132kV Line |  | 2015Q4 | CMA | TL | 2015-11-17 15:00 | 2015-11-17 15:00 |  | Follow up |  | 132 |  |  | 2015
210501 | LV/MECH Fail | SVC | No.1 Static VAr Compensator | Z | 2015Q4 | BKH | SVC | 2015-11-18 06:25 | 2015-11-18 06:37 | During switching on No1 Transformer prior to de-energising, the following switch was selected to OFF - No1 SVC No1 Aux Supply Isolator. Supplies looked to have failed to changeover and No1 SVC tripped. | Follow up | At 06:25hrs Broken Hill No.1 SVC tripped when staff on site were reselecting ac supply for a planned outage of BKH No.1 Transformer. Checks found AC Supply within limits, however termination of cabling to the Voltage Monitoring relay was found to be loose. Terminations on both No.1 SVC and No.2 SVC Voltage Monitoring relays checked and tightened where required. Alarm reset OK. | 22 |  | Fault | 2015
211421 | Design Limitation | TL | 991 Wagga North - Murrumburrah 132kV TL | E | 2015Q4 | MRU, WGN | TL | 2015-11-19 15:40 |  |  |  | Line 99X approaching rating, short notice outage required to open line 991 to prevent overload. | 132 |  | Forced | 2015
211459 | Animal/Bird | Cap | No.1 Capacitor | Z | 2015Q4 | WG1 | CAP | 2015-11-20 06:16 | 2015-11-20 08:12 | Visual inspection indicates likely to be a bird strike. RTS OK | Follow up | Visual inspection indicates likely to be a bird strike. | 132 |  | Fault | 2015
211479 | Design Limitation | TL | 999 Yass - Cowra 132kV TL | E | 2015Q4 | CW2, YSN | TL | 2015-11-20 09:47 | 2015-11-20 23:24 |  |  | Yass ambient temperature has exceeded 35 degrees. Clearance received from NCM to de-energise 999 in accordance with OM605. | 132 |  | Forced | 2015
212018 |  |  | 77 Wallerawang B CB 772B |  | 2015Q4 | ING | CB | 2015-11-20 12:46 | 2015-12-05 16:03 | Failure of the white phase CT associated with 772B CB | Follow up |  | 330 |  |  | 2015
212020 | HV Equipment | CT | 77 Wallerawang - Ingleburn 330kV TL | Z | 2015Q4 | ING, WW1 | TL | 2015-11-20 12:46 | 2015-11-22 00:01 |  |  | Failed CT (CB772B, white phase) at Ingleburn caught on fire, causing a trip of line 77. The plume of smoke caused a trip of all 330kV mesh CBs at Ingleburn, resulting in a loss of 115MW of load. | 330 | Andrew Kingsmill to advise when this investigation can be considered complete. [20/07/2016] Tim Barnes advised report complete and signed off, may be closed. | Fault | 2015
212070 | HV Equipment | VT | 37 Macarthur - Kemps Ck 330kV TL | E | 2015Q4 | KCR, MAC | TL | 2015-11-21 00:20 | 2015-11-21 23:22 |  |  | Line 37 red phase CVT at Kemps Creek replaced following a confirmed voltage imbalance: R Ph - 92V W Ph - 63.5V B Ph - 63.0V | 330 | Work order 372342 was created on 23/11/2015. CVT replaced. | Forced | 2015
212079 |  |  | Misc LV (Sydney West 330kV Substation) |  | 2015Q4 | SYW | LV | 2015-11-21 10:00 | 2015-11-21 11:53 |  |  |  | 0 |  |  | 2015
212083 |  |  | Broken Hill - Cockburn 22kV Line |  | 2015Q4 | BKH | TL | 2015-11-21 17:47 | 2015-11-21 23:16 | Advised by Essential Energy trip caused by failure of equipment in customer system. | Follow up |  | 22 |  |  | 2015
212197 |  |  | 8L Dumaresq - Bulli Creek 330kV TL |  | 2015Q4 | DMQ | TL | 2015-11-22 16:34 | 2015-11-22 16:34 | Advised by Powerlink of Trip and reclose of 8L at Bulli Creek. No indication of CB operation at Dumaresq although prot alarms received via SCADA. Info Update Operation of Single Pole Auto Reclose (White Phase). | 8/12/2015 16:12:00 ¦ Follow up ¦ Nil. |  | 330 |  |  | 2015
212198 |  |  | No.3 Reactor |  | 2015Q4 | DMQ | RX | 2015-11-22 16:34 | 2015-11-22 16:34 |  |  |  | 330 |  |  | 2015
212222 | HV Equipment | CT | 78 Ingleburn - Sydney South 330kV TL | E | 2015Q4 | ING, SYS | TL | 2015-11-25 07:16 | 2015-11-25 14:03 |  |  | Short notice outage for oil sampling CB782B CTs at Ingleburn. | 330 | Work order 372310 was created on 23/11/2015 | Forced | 2015
212239 | HV Equipment | CT | 88 Muswellbrook - Tamworth 330 330kV TL | E | 2015Q4 | MRK, TA1 | TL | 2015-11-23 12:33 | 2015-11-23 13:56 |  |  | Short notice outage for oil sampling on the CTs for this line at Tamworth 330. | 330 | Work order 372276 was created on 20/11/2015. Oil resample required of all 3 phases due to gases in caution range and water in danger range. | Forced | 2015
212281 | HV Equipment | TX | No.2 Transformer 132/66/11kV | Z | 2015Q4 | WG2 | TX | 2015-11-23 15:09 | 2015-11-23 18:27 | Buchholz bled, no gas. | Follow up | No.2 Transformer tripped while being energised. Bucholz relay subsequently bled and transformer returned to service. | 132 | Work order 373812 created on 1/12/2015, now closed. | Fault | 2015
212282 | Staff Error | Proc | 330kV A Bus | Q | 2015Q4 | CWF | BB | 2015-11-23 18:32 | 2015-11-23 22:22 |  |  | Unusual readings received on return (following routine maintenance) of the 330kV A Bus at Capital Wind Farm 330kV Substation and generation from the wind farm. Advises Revenue metering CT found open circuited. | 330 |  |  | 2015
212305 |  |  | 99N Darlington Point - Hillston 132kV Line |  | 2015Q4 | DNT | TL | 2015-11-24 05:13 | 2015-11-24 05:13 |  | Follow up |  | 132 |  |  | 2015
212326 |  |  | 99F Uranqunity - Yanco 132kV TL |  | 2015Q4 | YA2, URQ | TL | 2015-11-24 08:05 | 2015-11-24 08:05 | Harvesting in progress in area | 5/04/2016 10:08:00 ¦ Follow up ¦ Structures 210-250 have been noted for the next routine aerial patrol. |  | 132 |  |  | 2015
212374 | Secondary Equipment | Cont | No.2 Static Var Compensator | E | 2015Q4 | KCR | SVC | 2015-11-25 07:56 | 2015-11-25 12:13 |  |  | Short notice outage to test CVT unbalance relay. | 330 | Work order 372379 was created on 23/11/2015. False alarm of CVT unbalance, CVT unbalance relay may be faulty or require calibration. Update 10/02/2016: Relay fixed | Forced | 2015
212722 | HV Equipment | SVC | No.1 Static VAR Compensator | Z | 2015Q4 | AR1 | SVC | 2015-11-28 08:50 | 2015-11-28 14:34 | Capacitor can found failed in TSCB cap bank. | Follow up | Capacitor can found failed in TSCB cap bank. | 330 | Work order 373732 createdon 30/11/2015. Capacitor can replaced and SVC returned to service. | Fault | 2015
212723 | HV Equipment | CB | No.2 Static Var Compensator | E | 2015Q4 | KCR | SVC | 2015-11-28 11:20 | 2015-11-28 14:15 |  |  | CB 5V22 SF6 Topup | 330 |  | Forced | 2015
212728 | Relay | Prot | No.1 Transformer 330/132/11kV | Z | 2015Q4 | VP1 | TX | 2015-11-28 18:34 | 2015-11-29 15:44 | No fault recorder operations. Lake Munmorah 132kV load interrupted. Lake Munmorah restored via 97E at 18:38hrs. Station Transformer 3 restored at 21:16hrs. No.1 Transformer isolated pending further protection relay investigation and/or replacement. | Follow up | Advised No.1 transformer protection No.1 Prot in a faulted state which caused the Trip on No.1 Transformer 330/132/11kV at Vales point. | 330 | Mark Jones to follow up. [9/5/2016] Mark Jones: report complete. Close. | Fault | 2015
212740 | Lightning/Storm | TL | 9W1 Lismore 330 - Lismore 132 132kV Line | Q | 2015Q4 | LSM | TL | 2015-11-29 14:58 | 2015-11-29 14:58 |  | Follow up | Successful trip and reclose during storms. | 132 |  |  | 2015
212741 |  |  | Broken Hill - Railway Town 22kV Line |  | 2015Q4 | BKH | TL | 2015-11-29 19:08 | 2015-11-29 20:14 | Essential Energy staff advise trip caused by birds on or near a recloser on the Railway Town 22kV feeder. | Follow up |  | 22 |  |  | 2015
212747 | Animal/Bird | Other | No.2 Transformer 132/66/11kV | E | 2015Q4 | TA2 | TX | 2015-11-30 07:56 | 2015-11-30 14:42 |  |  | Short notice outage to remove birds nest from gantry. | 132 | Nest removed | Forced | 2015
212773 |  |  | 898 Parkes - Trundle 66kV Line |  | 2015Q4 | PKS | TL | 2015-11-30 09:47 | 2015-11-30 11:57 |  | Follow up |  | 66 |  |  | 2015
212790 | Lightning/Storm | TL | 967 Lismore 330 - Koolkhan 132kV TL | Q | 2015Q4 | KLK, LSM | TL | 2015-11-30 16:04 | 2015-11-30 16:04 |  | 5/02/2016 11:43:00 ¦ Follow up ¦ Nil | Successful trip and reclose during storms. | 132 |  |  | 2015
212859 | HV Equipment | CB | 96A Newcastle - Kurri 132kV Line | Q | 2015Q4 | NEW | TL | 2015-12-01 10:20 | 2015-12-01 11:30 |  |  | CB96A2 SF6 Topup | 132 |  |  | 2015
212876 | Staff Error | Proc | 9W1 Lismore 330 - Lismore 132 132kV Line | Q | 2015Q4 | LSM | TL | 2015-12-01 13:02 | 2015-12-01 13:24 | 9W1, 9U9 & 9U8 all tripped concurrently during planned work on the Directlink ECS. Refer to separate FEORs. | Follow up | Inadvertent activation of Directlink Emergency Control Scheme at Lismore by communications technician, during planned maintenance. | 132 |  |  | 2015
212881 |  |  | 9U9 Lismore 330 - Lismore 132 132kV Line | Q | 2015Q4 | LSM | TL | 2015-12-01 13:02 | 2015-12-01 13:26 | 9W1, 9U9 & 9U8 all tripped concurrently during planned work on the Directlink ECS. Refer to separate FEORs. | Follow up |  | 132 |  |  | 2015
212882 |  |  | 9U8 Lismore 330 - Lismore 132 132kV Line | Q | 2015Q4 | LSM | TL | 2015-12-01 13:02 | 2015-12-01 13:26 | 9W1, 9U9 & 9U8 all tripped concurrently during planned work on the Directlink ECS. Refer to separate FEORs. | Follow up |  | 132 |  |  | 2015
212888 | Design Limitation | TL | 999 Yass - Cowra 132kV TL | E | 2015Q4 | CW2, YSN | TL | 2015-12-01 14:28 | 2015-12-01 17:58 |  |  | Line 999 required out of service due to risk of overload in the event of a contingent trip of line 973. | 132 |  | Forced | 2015
212890 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2015Q4 | MRE | TL | 2015-12-02 00:02 | 2015-12-02 00:02 |  | Follow up |  | 66 |  |  | 2015
212933 |  |  | 19 Kangaroo Valley - Bendeela 330kV Line |  | 2015Q4 | KVS | TL | 2015-12-02 08:04 | 2015-12-02 14:21 | Received advice from KVPS that work being carried out on Unit 2 at KVPS. Problem with Main Gate Valve) | Follow up |  | 330 |  |  | 2015
212949 |  |  | 78 Ingleburn - Sydney South 330kV TL | Z | 2015Q4 | ING, SYS | TL | 2015-11-20 12:46 | 2015-11-20 14:10 |  |  |  | 330 |  | Fault | 2015
212950 |  |  | No.1 Transformer 330/66/11kV | Z | 2015Q4 | ING | TX | 2015-11-20 12:46 | 2015-11-20 14:11 |  |  |  | 330 |  | Fault | 2015
212951 |  |  | No.2 Transformer 330/66/11kV | Z | 2015Q4 | ING | TX | 2015-11-20 12:46 | 2015-11-20 18:32 |  |  |  | 330 |  | Fault | 2015
212994 | LV/MECH Fail | Rx | No.1 Reactor | E | 2015Q4 | WL1 | RX | 2015-12-03 07:23 | 2015-12-03 08:55 |  |  | No.1 Rx Cooling fault alarm received advise NCM of above alarm and request the requirement of the reactor to stay in service called out kev Middleton to site to investigate John advised No.1 Rx can be removed from service 07:23 removed No.1 Rx from service Kev advised that faulty fan has been disconnected and remaining fans now set to manual and the Rx can be RTS 08:55 Advise NCM and requested to place No.1 Rx at WL1 Placed No.1 Rx in service | 330 | Fan fixed. | Forced | 2015
213138 | LV/MECH Fail | T/C | No.1 Transformer 330/132/11kV | E | 2015Q4 | TA1 | TX | 2015-12-04 09:33 | 2015-12-04 13:51 |  |  | Short notice outage to investigate tapchanger fault. | 330 | Fixed. | Forced | 2015
213208 | Unknown | Prot | No.3 Transformer 330/132/11kV | Z | 2015Q4 | SYS | TX | 2015-12-04 15:21 | 2016-02-11 15:20 | Tripped on Initial energisation from C.B. 4432 (Back energised for Auxillary supplies) zero sequence from phase currents is in opposition to neutral CT current indicating no fault in transformer. Relay has tripped due to intermittent rest of 2nd harmonic block. Clearance given for another attempt at initial energisation. Succesfully close C.B. 4432 at 1704hrs. | Follow up | Tripped on Initial energisation from C.B. 4432 (Back energised for Auxillary supplies) Appears No.3 Transformer tripped on No.1 Protection Diff Relay only. Diff Relay is a GE T60 relay that have known issues. After consultation with Gordon Keen it was decided to leave the No.3 Transformer O/O/S based on the fact it has been O/O/S since 16/11/15 and staff can be arranged to investigate further Monday 7/12/15. | 330 | TWR created to fix protection settings. | Fault | 2015
213255 | HV Equipment | CB | 9J1 Sydney West - Blacktown 132kV Line | Q | 2015Q4 | SYW | TL | 2015-12-05 14:01 | 2015-12-05 16:20 |  |  | CB9J12 SF6 Topup | 132 |  |  | 2015
213262 | HV Equipment | CB | 330kV B Bus 1-2 Section CB 5112 | Q | 2015Q4 | SE1 | CB | 2015-12-05 18:34 | 2015-12-05 19:34 |  |  | CB 5112 SF6 Topup | 330 |  |  | 2015
213275 | HV Equipment | CB | No.2 Static Var Compensator | E | 2015Q4 | KCR | SVC | 2015-12-06 20:03 | 2015-12-06 22:30 | CB5V22 blue phase topped up with SF6 and returned to service. | Follow up | CB5V22 blue phase topped up with SF6 and returned to service. | 330 |  | Forced | 2015
213276 |  |  | 712 Port Macquarie - Rocks Ferry 33kV Line |  | 2015Q4 | PMQ | TL | 2015-12-06 21:17 | 2015-12-07 00:42 | No fault found. 712 Rocks Ferry feeder returned to service at Essential Energy's request. | Follow up |  | 33 |  |  | 2015
213277 |  |  | Unit 3 Transformer |  | 2015Q4 | KVS | TX | 2015-12-07 01:18 |  |  | Follow up |  | 330 |  |  | 2015
213301 | HV Equipment | CB | No.2 Static Var Compensator | E | 2015Q4 | KCR | SVC | 2015-12-08 09:05 | 2015-12-08 09:51 |  |  | Investigate CB Low Gas Alarm on Blue Phase. | 330 | Incorrect SF6 gauge used, issue addressed. | Forced | 2015
213792 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2015Q4 | GRF | TL | 2015-12-08 15:57 | 2015-12-08 15:57 |  | Follow up |  | 33 |  |  | 2015
213794 |  |  | 79F Griffith - Yenda 33kV Line |  | 2015Q4 | GRF | TL | 2015-12-08 16:05 | 2015-12-08 16:05 |  | Follow up |  | 33 |  |  | 2015
213795 |  |  | 97C Tamworth 330- Tamworth 132 132kV TL |  | 2015Q4 | TA1, TMW | TL | 2015-12-08 17:11 | 2015-12-08 18:15 | Protection staff on site advise that temporary overcurrent settings for No.1 Transformer at Tamworth 132 (New) are less than the load current on the transformer. The temporary protection initiated the CBF I/Ts on 97C Tamworth 330 to Tamworth 132 Feeder Protections. | 15/12/2015 16:04:00 ¦ Follow up ¦ A review of process prior to commissioning to check that any temporary protection settings are suitable for the load on the day of commissioning. |  | 132 |  |  | 2015
213796 |  |  | 79F Griffith - Yenda 33kV Line |  | 2015Q4 | GRF | TL | 2015-12-08 18:22 | 2015-12-08 18:22 |  | Follow up |  | 33 |  |  | 2015
213797 |  |  | 97C Tamworth 330- Tamworth 132 132kV TL |  | 2015Q4 | TA1, TMW | TL | 2015-12-08 18:15 | 2015-12-08 19:41 |  | 5/02/2016 13:32:00 ¦ Follow up ¦ Nil |  | 132 |  |  | 2015
213984 |  |  | 7R2 Kempsey - North St tee Smithtown 33kV Line |  | 2015Q4 | KS2 | TL | 2015-12-09 15:06 | 2015-12-09 18:08 | So/Essential Chris advised all customer load restored via customer System at 17:53hrs Essential energy found a recloser was damaged by lighting | Follow up |  | 33 |  |  | 2015
214083 |  |  | 813 Tamworth 132 - Currabubula 66kV Line |  | 2015Q4 | TMW | TL | 2015-12-10 08:03 | 2015-12-10 08:03 | Distance to fault 20.1km | Follow up |  | 66 |  |  | 2015
214095 | Lightning/Storm | TL | 878 Narrabri - Boggabri 66kV Line | Q | 2015Q4 | NB2 | TL | 2015-12-10 09:06 | 2015-12-10 09:06 |  | Follow up | Successful trip and reclose during storms. | 66 |  |  | 2015
214096 | Lightning/Storm | TL | 878 Narrabri - Boggabri 66kV Line | Q | 2015Q4 | NB2 | TL | 2015-12-10 09:22 | 2015-12-10 09:22 |  | Follow up | Successful trip and reclose during storms. | 66 |  |  | 2015
214220 |  |  | No.3 Tenterfield - Council (Timbarra Mine) 22kV Line |  | 2015Q4 | TTF | TL | 2015-12-10 16:03 | 2015-12-10 16:50 |  | Follow up |  | 22 |  |  | 2015
214388 | HV Equipment | VT | No.1 Transformer 330/132/11kV | E | 2015Q4 | LSM | TX | 2015-12-11 14:47 | 2015-12-12 17:00 |  |  | CVT unbalance alarm. Faulty CVT replaced. | 330 |  | Forced | 2015
214393 |  |  | Broken Hill - Solar Plant 2 22kV Line |  | 2015Q4 | BKH | TL | 2015-12-11 12:47 | 2015-12-11 15:47 | AGL found a dead bird under the Line Disc at their end. Line was patroled by AGL and Energised at AGL request at Broken Hill. | Follow up |  | 22 |  |  | 2015
214406 |  |  | 999 Yass - Cowra 132kV TL | E | 2015Q4 | CW2, YSN | TL | 2015-12-11 13:01 | 2015-12-11 22:14 |  |  |  | 132 |  | Forced | 2015
214407 |  |  | 97A Tamworth 330 - Tamworth 132 132kV TL | E | 2015Q4 | TA2, TA1, TMW | TL | 2015-12-11 16:23 | 2015-12-11 17:21 |  |  |  | 132 |  | Forced | 2015
214449 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2015Q4 | GRF | TL | 2015-12-12 14:12 | 2015-12-12 14:12 |  | Follow up |  | 33 |  |  | 2015
214462 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2015Q4 | GRF | TL | 2015-12-13 15:11 | 2015-12-13 15:11 |  | Follow up |  | 33 |  |  | 2015
214464 | Bushfire | TL | 11 Dapto - Sydney South 330kV TL | Q | 2015Q4 | DPT, SYS | TL | 2015-12-14 04:39 | 2015-12-14 04:39 | A bushfire was identified in the vacinity of 11 Dapto - Sydney South 330kV TL at Madens Plain on Indji. Rural Fire Service were contacted (NCM) who advised that the fire is still on the Eastern side of Pacific Highway and has not travelled west (towards 11 T/L). Mains Staff advised | 8/02/2016 16:16:00 ¦ Follow up ¦ An Asset Management response is underway to identify similar damage to other polymer longrod insulators of the same type and vintage. | 11 Dapto to Sydney South 330 kV T/L Tripped and reclosed. Cause Unknown at this stage. There is reported fire at Maddens Plains ( near Darks Forest) which has been burning for a while. RFS reported that the fire has not travelled west of the Princess highway. Investigation will be required. | 330 |  |  | 2015
214534 | Bushfire | TL | 11 Dapto - Sydney South 330kV TL | Q | 2015Q4 | DPT, SYS | TL | 2015-12-15 05:21 | 2015-12-15 05:21 |  | 8/02/2016 16:24:00 ¦ Follow up ¦ An Asset Management response is underway to identify similar damage to other polymer longrod insulators of the same type and vintage. | 11 Dapto to Sydney South 330 kV T/L Tripped and reclosed. Cause Unknown at this stage. There is reported fire at Maddens Plains ( near Darks Forest) which has been burning for a while. RFS reported that the fire has not travelled west of the Princess highway. Investigation will be required. | 330 |  |  | 2015
214535 | HV Equipment | TL | 11 Dapto - Sydney South 330kV TL | Z | 2015Q4 | DPT, SYS | TL | 2015-12-15 05:36 | 2015-12-15 13:56 | Distance to Fault of 34.54km from Dapto Very similar DTF to yesterdays (14/12/15) TAR SCADA event list suggest AR attempt at SYS but not DPT. Mains staff advise dirty insulator on Str 82, to be replaced. | 8/02/2016 16:28:00 ¦ Follow up ¦ An Asset Management response is underway to identify similar damage to other polymer longrod insulators of the same type and vintage. | Distance to Fault of 34.54km from Dapto Very similar DTF to yesterdays (14/12/15) TAR SCADA event list suggest AR attempt at SYS but not DPT. Mains staff advise dirty insulator on Str 82, to be replaced. | 330 | All phases on Str 82 replaced. Insulators showed signs of deterioration, significant cracking/splits on the spine/seam and fading of the sheds. 26 other structures were inspected by climbing, 2 had same type of insulator, 9 structures has similar poor condition has been replaced. Review for revenue reset having a replacemenrt program for this batch / brand of insulator will be undertaken. | Fault | 2015
214720 |  |  | No.4 500kV Generator Transformer Group |  | 2015Q4 | ER0 | TX | 2015-12-15 23:15 | 2015-12-16 23:09 |  | Follow up |  | 500 |  |  | 2015
214882 |  |  | 916 Sydney South - Kurnell tee Cronulla 132kV Line |  | 2015Q4 | SYS | TL | 2015-12-16 09:30 | 2015-12-17 19:10 |  | Follow up |  | 132 |  |  | 2015
214883 |  |  | 916 Sydney South tee Cronulla CB 9162 |  | 2015Q4 | KNL | CB | 2015-12-16 09:30 | 2015-12-17 19:10 |  |  |  | 132 |  |  | 2015
214884 |  |  | 916 Sydney South tee Kurnell CB 9162 |  | 2015Q4 | CRN | CB | 2015-12-16 09:30 | 2015-12-17 19:10 |  |  |  | 132 |  |  | 2015
214885 |  |  | 916 Kurnell tee Cronulla CB 9162 |  | 2015Q4 | SYS | CB | 2015-12-16 09:30 | 2015-12-17 19:10 |  |  |  | 132 |  |  | 2015
214894 | External | Cap | No.1 Capacitor | E | 2015Q4 | WL1 | CAP | 2015-12-17 10:18 | 2015-12-17 11:09 |  |  | Short notice outage to remove Weeds from No.1 Capacitor Bank Cage | 132 |  | Forced | 2015
214908 |  |  | 867 Taree - OCC Failford 66kV Line |  | 2015Q4 | TRE | TL | 2015-12-16 12:30 | 2015-12-16 12:30 |  | Follow up |  | 66 |  |  | 2015
214918 | Lightning/Storm | TL | 5A3 Bayswater - Mt Piper 500kV TL | Q | 2015Q4 | BAY, MTP | TL | 2015-12-16 14:09 | 2015-12-16 14:09 |  | Follow up | Successful trip and reclose during storms. | 500 |  |  | 2015
214919 |  |  | Broken Hill - Cockburn 22kV Line |  | 2015Q4 | BKH | TL | 2015-12-16 14:41 | 2015-12-16 15:29 | So/Essential Energy advised bird strike caused a Gas switch G-14835 to Fail, | Follow up |  | 22 |  |  | 2015
214920 | Lightning/Storm | TL | 9W2 Kempsey - Raleigh 132kV TL | Z | 2015Q4 | KS2, RAL | TL | 2015-12-16 17:28 | 2015-12-17 10:29 | Distance to fault @ Kempsey 37.39km @ Raleigh 43.21km | 22/02/2016 09:17:00 ¦ Follow up ¦ Nil ¦ Nil | At 17:28hrs 9W2 Kempsey to Raleigh 132 kV T/L tripped, reclosed, tripped and locked out. Staff called out. Storms in the area. Distance to fault: @ Kempsey 37.39km @ Raleigh 43.21km | 132 |  | Fault | 2015
214921 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2015Q4 | MRE | TL | 2015-12-16 17:58 | 2015-12-16 17:58 |  | Follow up |  | 66 |  |  | 2015
214922 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2015Q4 | MRE | TL | 2015-12-16 18:00 | 2015-12-16 18:00 |  | Follow up |  | 66 |  |  | 2015
214923 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2015Q4 | MRE | TL | 2015-12-16 18:01 | 2015-12-16 23:50 |  | Follow up |  | 66 |  |  | 2015
215010 | Relay | Prot | 99P Tumut - Gadara 132kV TL | E | 2015Q4 | GAD, TU2 | TL | 2015-12-18 11:25 | 2015-12-18 17:19 |  |  | Short notice outage to replace the No.1 Prot relay at Gadara. | 132 | Relay replaced. | Forced | 2015
215029 | HV Equipment | CB | No.2 Static Var Compensator | E | 2015Q4 | KCR | SVC | 2015-12-18 13:48 | 2015-12-18 14:27 |  |  | CB 5V22 SF6 Topup | 330 |  | Forced | 2015
215035 | HV Equipment | CB | No.4 Transformer 330/132/11kV | E | 2015Q4 | CA1 | TX | 2015-12-18 17:56 | 2015-12-18 20:34 | Low SF6 on No.4 Transformer 132kV B CB..4442B CT's required Transformer de-energised until 132kV B CB..4442B CT's were Isolated, TX remained de-energised until No.4 Transformer 132kV B CB..4442B CT's SF6 was topped up. | Follow up | Low SF6 on No.4 Transformer 132kV B CB..4442B CT's required Transformer de-energised until 132kV B CB..4442B CT's were Isolated, TX remained de-energised until No.4 Transformer 132kV B CB..4442B CT's SF6 was topped up. | 330 |  | Forced | 2015
215037 | Unknown | TL | 92Z Sydney North - Sydney East tee Mt Colah 132kV TL | Q | 2015Q4 | SE1, SYN | TL | 2015-12-18 23:19 | 2015-12-18 23:19 | SO/Ausgrid Daryl advised 95Z opend at Somersby at the same time. | Follow up | Successful trip and reclose, cause unknown. | 132 |  |  | 2015
215043 | Communications | Com | 4 Yass - Marulan 330kV TL | E | 2015Q4 | MRN, YSN | TL | 2015-12-19 14:07 | 2015-12-20 00:26 |  |  | Short notice outage to repair defective fibre optic cable between structures 76 & 77. | 330 |  | Forced | 2015
215049 |  |  | 84A Finley - Jerilderie 66kV Line |  | 2015Q4 | FNY | TL | 2015-12-20 13:58 | 2015-12-20 21:02 |  | Follow up |  | 66 |  |  | 2015
215050 |  |  | Broken Hill - West 22kV Line |  | 2015Q4 | BKH | TL | 2015-12-20 16:35 | 2015-12-20 16:35 | An Electrical storm was passing over tha area at the time of trip. Protection flags updated. | Follow up |  | 22 |  |  | 2015
215062 | Communications | Com | 4 Yass - Marulan 330kV TL | E | 2015Q4 | MRN, YSN | TL | 2015-12-22 06:33 | 2015-12-22 15:09 |  |  | Short notice outage to repair broken OPGW | 330 |  | Forced | 2015
215089 | Unknown | CB | No.1 Transformer 220/22kV | E | 2015Q4 | BKH | TX | 2015-12-22 10:01 | 2015-12-22 13:33 |  |  | Short notice outage to investigate CB2412 abnormal alarm. | 220 | Spring defect fixed | Forced | 2015
215137 |  |  | 862/1 Taree - OCC Kew tee Johns River 66kV Line |  | 2015Q4 | TRE | TL | 2015-12-22 04:33 | 2015-12-22 04:33 | 862 was off-load at the time of the trip. | Follow up |  | 66 |  |  | 2015
215323 |  |  | 662 Armidale - Walcha 66kV Line |  | 2015Q4 | AR1 | TL | 2015-12-22 14:25 | 2015-12-22 14:25 |  | Follow up |  | 66 |  |  | 2015
215326 | HV Equipment | TX | No.3 Transformer 330/132/11kV | E | 2015Q4 | WRH | TX | 2015-12-22 16:13 | 2015-12-24 15:11 |  |  | Short notice outage to repair transformer bushing defect. | 330 | Characteristic of monitoring equipment, no issue with bushings. | Forced | 2015
215556 | HV Equipment | TL | 4 Yass - Marulan 330kV TL | E | 2015Q4 | MRN, YSN | TL | 2015-12-23 12:01 | 2015-12-23 16:16 |  |  | Repair Broken Conductor between structure 75 and 76. | 330 | Bullet Damage. OPGW was repaired firstly (new span). During repairs damage to conductor was observed which was repaired with mid-span joint. | Forced | 2015
215588 | HV Equipment | CB | No.2 Static Var Compensator | E | 2015Q4 | KCR | SVC | 2015-12-23 14:00 | 2015-12-23 15:18 |  |  | CB 5V22 SF6 Topup | 330 |  | Forced | 2015
215613 |  |  | 841 Yanco - Narrandera 66kV Line |  | 2014Q2 | YA2 | TL | 2014-04-29 06:31 | 2014-04-29 06:31 |  | follow up required |  | 66 |  |  | 2014
215614 |  |  | No.4 Transformer 66/33/11kV |  | 2014Q2 | YA2 | TX | 2014-04-29 06:31 | 2014-04-29 06:31 |  |  |  | 66 |  |  | 2014
215615 |  |  | 822 Deniliquin - Moulamein tee Deniliquin 66kV SS 66kV Line |  | 2015Q4 | DN2 | TL | 2015-11-04 19:52 | 2015-11-04 19:52 |  | Follow up |  | 66 |  |  | 2015
215616 |  |  | 844 Deniliquin - Barham 66kV Line |  | 2015Q4 | DN2 | TL | 2015-10-31 05:54 | 2015-10-31 05:54 |  | Follow up |  | 66 |  |  | 2015
215617 |  |  | 822 Deniliquin - Moulamein tee Deniliquin 66kV SS 66kV Line |  | 2015Q4 | DN2 | TL | 2015-10-31 21:45 | 2015-10-31 21:45 |  | Follow up |  | 66 |  |  | 2015
215653 | HV Equipment | CB | 932 Sydney West - Mt Druitt 132kV Line | E | 2015Q4 | SYW | TL | 2015-12-24 13:32 | 2015-12-24 15:45 |  |  | CB 9322 SF6 Topup | 132 |  | Forced | 2015
215654 | HV Equipment | CB | 330kV B Bus 1-2 Section CB 5112 | Q | 2015Q4 | SE1 | CB | 2015-12-24 17:45 | 2015-12-24 19:06 |  |  | CB5112 SF6 Topup | 330 |  |  | 2015
215655 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2015Q4 | MRE | TL | 2015-12-24 19:55 | 2015-12-24 19:55 |  | Follow up |  | 66 |  |  | 2015
215661 |  |  | 79M Griffith - Hanwood 33kV Line |  | 2015Q4 | GRF | TL | 2015-12-26 04:59 | 2015-12-26 04:59 |  | Follow up |  | 33 |  |  | 2015
215662 | HV Equipment | CB | 61 Bannaby B CB 612B | Q | 2015Q4 | GUR | CB | 2015-12-26 06:01 | 2015-12-26 08:53 |  | Follow up | CB612B SF6 Topup | 330 |  |  | 2015
215680 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q4 | CW2 | TL | 2015-12-26 15:32 | 2015-12-26 17:01 |  | Follow up |  | 66 |  |  | 2015
215682 |  |  | 999 Yass - Cowra 132kV TL | E | 2015Q4 | CW2, YSN | TL | 2015-12-26 14:39 | 2015-12-27 01:42 |  |  |  | 132 |  | Forced | 2015
215683 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q4 | CW2 | TL | 2015-12-26 17:17 | 2015-12-26 19:30 |  | Follow up |  | 66 |  |  | 2015
215684 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2015Q4 | CW2 | TL | 2015-12-26 19:43 | 2015-12-26 19:53 |  | Follow up |  | 66 |  |  | 2015
215686 | HV Equipment | CB | No.2 Static Var Compensator | E | 2015Q4 | KCR | SVC | 2015-12-27 23:38 | 2015-12-28 02:56 |  |  | CB 5V22 SF6 Topup | 330 |  | Forced | 2015
215782 |  |  | 708 Port Macquarie - Owen St tee Boronia St 33kV Line |  | 2016Q1 | PMQ | TL | 2016-01-01 23:01 | 2016-01-01 23:01 |  | Follow up |  | 33 |  |  | 2016
215815 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2016Q1 | GRF | TL | 2016-01-02 08:37 | 2016-01-02 08:38 | Weather tools indicate adverse weather | Follow up |  | 33 |  |  | 2016
215816 | HV Equipment | CB | 61 Bannaby B CB 612B | Q | 2016Q1 | GUR | CB | 2016-01-03 21:42 | 2016-01-04 12:40 |  |  | CB 612B SF6 Topup | 330 |  |  | 2016
215852 | HV Equipment | CB | 61 Bannaby B CB 612B | Q | 2016Q1 | GUR | CB | 2016-01-04 10:03 | 2016-01-04 12:40 |  |  | CB 612B SF6 Topup | 330 |  |  | 2016
215938 |  |  | 723 Wenna Tee Wathagar 66kV CB 7232 |  | 2016Q1 | MRE | CB | 2016-01-05 13:25 | 2016-01-05 13:25 |  | Follow up |  | 66 |  |  | 2016
215949 | HV Equipment | CB | No.2 Static Var Compensator | E | 2016Q1 | KCR | SVC | 2016-01-05 16:13 | 2016-01-05 17:30 |  |  | CB 5V22 SF6 Topup | 330 |  | Forced | 2016
215952 |  |  | 221 Sydney North - Kenthurst 132kV Line |  | 2016Q1 | SYN | TL | 2016-01-05 18:22 | 2016-01-05 18:22 |  | Follow up |  | 132 |  |  | 2016
216033 |  |  | Broken Hill - West 22kV Line |  | 2016Q1 | BKH | TL | 2016-01-06 16:55 | 2016-01-06 16:55 |  | Follow up |  | 22 |  |  | 2016
216034 |  |  | 862/1 Taree - OCC Kew tee Johns River 66kV Line |  | 2016Q1 | TRE | TL | 2016-01-06 19:00 | 2016-01-06 21:20 | 862 Kew Tee Johns River 66kV Feeder was closed at Essential Energy's request at 21:20. | Follow up |  | 66 |  |  | 2016
216100 | HV Equipment | CB | No.2 Transformer 132kV B CB 4422B | Q | 2016Q1 | SE1 | CB | 2016-01-08 11:17 | 2016-01-08 15:24 |  | Follow up | CB 4422B SF6 Topup | 132 |  |  | 2016
216131 | HV Equipment | CB | 61 Bannaby B CB 612B | Q | 2016Q1 | GUR | CB | 2016-01-10 06:40 | 2016-02-17 09:34 |  |  | CB 612B SF6 Topup | 330 |  |  | 2016
216135 | HV Equipment | Other | No.2 Tie | Q | 2016Q1 | BFD | UG | 2016-01-10 08:37 | 2016-01-10 11:17 |  |  | Short notice outage to investigate SF6 alarm for the No.2 Beaconsfield North - Beaconsfield South Tie. | 132 |  |  | 2016
216136 | Relay | Prot | 96A Newcastle - Kurri 132kV Line | Q | 2016Q1 | NEW | TL | 2016-01-10 19:15 | 2016-01-10 22:13 |  |  | Replacement of the No.2 Protection relay (Micom P442/2) which had raised a protection faulty alarm. | 132 | Relay replaced. |  | 2016
216137 |  |  | SPARE CB 95W2C | Q | 2016Q1 | NEW | CB | 2016-01-10 19:13 | 2016-01-10 22:12 |  |  |  | 132 |  |  | 2016
216173 |  |  | 879 Narrabri - Wee Waa 66kV Line |  | 2016Q1 | NB2 | TL | 2016-01-11 13:57 | 2016-01-12 15:14 |  | Follow up |  | 66 |  |  | 2016
216174 |  |  | 879 Narrabri - Wee Waa 66kV Line |  | 2016Q1 | NB2 | TL | 2016-01-11 13:57 |  |  |  |  | 66 |  |  | 2016
216183 | Lightning/Storm | TL | 2M Tuggerah - Munmorah 330kV TL | Q | 2016Q1 | MN1, TGH | TL | 2016-01-11 18:39 | 2016-01-11 18:39 | Fault Recorder at Munmorah indicated a distance to fault of 18.2 km. | Follow up | Successful trip and reclose during storms. | 330 |  |  | 2016
216203 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2016Q1 | GRF | TL | 2016-01-12 05:59 | 2016-01-12 05:59 |  | Follow up |  | 33 |  |  | 2016
216254 | Lightning/Storm | TL | 96P Taree - Stroud 132kV TL | Q | 2016Q1 | TRE | TL | 2016-01-12 15:32 | 2016-01-12 15:32 |  | Follow up | Successful trip and reclose during storms. | 132 |  |  | 2016
216255 | HV Equipment | CB | No.2 Static Var Compensator | E | 2016Q1 | KCR | SVC | 2016-01-12 23:50 | 2016-01-13 01:10 |  |  | CB 5V22 SF6 Topup | 330 |  | Forced | 2016
216257 | Animal/Bird | SD | No.2 Transformer 132/66/11kV | Z | 2016Q1 | PMA | TX | 2016-01-13 05:44 | 2016-01-13 13:58 | Called out Joel Scully to investigate | Follow up | A bird contacted the No.2 Transformer 11kV conductors at the 11kV surge diverter. The transformer will be isolated and earthed to replace the 11kV surge diverters. Protection flags indicate the fault was on the 11kV. | 132 |  | Fault | 2016
216327 | HV Equipment | CT | No.1 Generator 330kV CB 5212 | Q | 2016Q1 | ER0 | CB | 2016-01-13 15:21 | 2016-01-13 17:18 |  |  | SF6 topup for CT associated with CB 5212 | 330 |  |  | 2016
216393 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2016Q1 | GRF | TL | 2016-01-13 14:36 | 2016-01-13 19:32 | SO/Essential Energy advises that they have found a damaged pole on 79P Griffith - Goolgowi 33kV Line closer to Griffith 132kV Substation. They will be isolating in their network and carry out the repairs. Also advises that they have lost about 7MW load and will be transferring it to 79C Darlington Point 33kV Feeder at Griffith 132kV Substation. | Follow up |  | 33 |  |  | 2016
216489 | Unknown/Other | CB | 240 Potts Hill tee Chullora CB 2402 | Q | 2016Q1 | RWR | CB | 2016-01-15 06:45 | 2016-01-15 12:18 |  |  | Short notice outage for CB timing, SF6, and operational checks. | 132 |  |  | 2016
216496 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2016Q1 | BER | TL | 2016-01-14 15:34 | 2016-01-14 15:34 |  | Follow up |  | 66 |  |  | 2016
216497 | Lightning/Storm | TL | 948 Orange North - Panorama 132kV TL | Q | 2016Q1 | PMA, ONO | TL | 2016-01-14 16:13 | 2016-01-14 16:13 |  | Follow up | Successful trip and reclose during storms. | 132 |  |  | 2016
216598 | Tree/Ground | TL | 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL | Z | 2016Q1 | AR1, COF | TL | 2016-01-15 16:23 | 2016-01-16 10:57 | Essential Energy lost approx 3MW load at Dorrigo which was later back fed by Essential via their network. Mains staff were requested to patrol the 96C TL they advised that due to poor Visibility Mains staff were able to patrol road crossings only and could not go into the bush and they will be resuming patrol with the first day light tomorrow morning. After discussions with NCM 96C Armidale - Coffs Harbour Tee Dorrigo 132kV TL was left de-energised only overnight and only to be Isolated and Earthed if required the next morning. | Follow up | Armidale – Coffs Harbour tee Dorrigo 132kV Line 96C tripped, reclosed, tripped and locked out at Coffs Harbour, and tripped at Armidale. This resulted in an immediate loss of supply to Essential Energy’s Dorrigo substation and all load emanating from there. A subsequent patrol of the line found bark on the earth wire and braches on the ground around the area believed to be faulted. | 132 | Line 96C has a narrow easement (30m) and goes through areas of very tall (over 30m) trees, this does not provide much protection even on a well maintained easement. | Fault | 2016
216606 | HV Equipment | CB | 330kV B Bus 1-2 Section CB 5112 | Q | 2016Q1 | SE1 | CB | 2016-01-16 16:46 | 2016-01-16 19:09 |  |  | CB 5112 SF6 Topup | 330 |  |  | 2016
216629 |  |  | 867 Taree - OCC Failford 66kV Line |  | 2016Q1 | TRE | TL | 2016-01-17 19:18 | 2016-01-17 19:18 |  | Follow up |  | 66 |  |  | 2016
216630 |  |  | 867 Taree - OCC Failford 66kV Line |  | 2016Q1 | TRE | TL | 2016-01-17 19:36 | 2016-01-19 16:56 | Pole top fire. TL I & E'd pending repairs on 18/1/16. | Follow up |  | 66 |  |  | 2016
216634 | HV Equipment | TX | No.1 Transformer 330/132/11kV | E | 2016Q1 | BFD | TX | 2016-01-18 12:02 | 2016-01-18 13:37 |  |  | Short notice outage to topup No.1 Tx conservator low oil. | 330 |  | Forced | 2016
216775 |  |  | Broken Hill - South 22kV Line |  | 2016Q1 | BKH | TL | 2016-01-20 05:55 | 2016-01-20 07:21 | EsE (Murray) advises of bird strike on pole top transformer. | Follow up |  | 22 |  |  | 2016
216842 | LV/MECH Fail | CB | 35 Marulan CB 352 | Q | 2016Q1 | MTP | CB | 2016-01-20 19:19 |  |  |  | Reported C.B 352 has Hydralic oil leak and has locked out. Unable to open via SCADA. | 330 | Leak fixed. |  | 2016
216843 |  |  | 35 Marulan CB 352 |  | 2016Q1 | MTP | CB | 2016-01-20 19:19 | 2016-01-21 13:33 |  | Follow up |  | 330 |  |  | 2016
216861 |  |  | Broken Hill - Cockburn 22kV Line |  | 2016Q1 | BKH | TL | 2016-01-21 09:43 | 2016-01-21 10:48 | Essential Energy patrolled line and requested reclose made non auto and line energised @ 1048 hours. | Follow up |  | 22 |  |  | 2016
216862 |  |  | Broken Hill - Railway Town 22kV Line |  | 2016Q1 | BKH | TL | 2016-01-21 09:47 | 2016-01-21 09:47 |  | Follow up |  | 22 |  |  | 2016
216870 |  |  | Broken Hill - Talc St 2 22kV line |  | 2016Q1 | BKH | TL | 2016-01-21 09:47 | 2016-01-21 09:47 |  | Follow up |  | 22 |  |  | 2016
216900 |  |  | 898 Parkes - Trundle 66kV Line |  | 2016Q1 | PKS | TL | 2016-01-21 15:11 | 2016-01-21 15:11 |  | Follow up |  | 66 |  |  | 2016
216901 |  |  | Broken Hill - Cockburn 22kV Line |  | 2016Q1 | BKH | TL | 2016-01-21 10:49 | 2016-01-21 14:38 | Clearance given by Essential Energy to energising the Cockburn 22kV feeder at 1048 hours. The feeder tripped at 1049 hours (reclose non auto). Staff on site reported a flash and smoke coming from the top of a pole near Broken Hill 220kV Substation. Essential Energy reported a failed insulator on the pole. Line isolated and earthed under HVPRI 63560 to allow Essential Energy to carry out repairs. | Follow up |  | 22 |  |  | 2016
216902 | Unknown/Other | TL | 969 Tamworth 330 - Gunnedah 132kV TL | Q | 2016Q1 | GN2, TA1 | TL | 2016-01-22 05:04 | 2016-01-22 05:04 |  | Follow up | Successful trip and reclose, cause unknown. | 132 |  |  | 2016
216933 |  |  | 822 Deniliquin tee Moulamein CB 8222 |  | 2016Q1 | DN2 | CB | 2016-01-22 06:59 | 2016-01-22 06:59 |  | Follow up |  | 66 |  |  | 2016
216953 |  |  | 851 Beryl - Mudgee tee Gulgong 66kV Line |  | 2016Q1 | BER | TL | 2016-01-22 12:54 | 2016-01-22 12:54 |  | Follow up |  | 66 |  |  | 2016
216956 |  |  | 9MC Orange North - Cadia 132kV Line |  | 2016Q1 | ONO | TL | 2016-01-22 13:00 | 2016-01-22 13:47 | DTF 26.9km (No 1 Prot) | Follow up |  | 132 |  |  | 2016
216981 |  |  | 95U Muswellbrook 330 - Singleton 132kV Line |  | 2016Q1 | MRK | TL | 2016-01-22 15:16 | 2016-01-25 11:57 | Patrol of transmission line carried out by Ausgrid and no fault found. Line successfully energised at 1157 hours. | Follow up |  | 132 |  |  | 2016
216982 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2016Q1 | BER | TL | 2016-01-22 15:54 | 2016-01-22 15:54 |  | Follow up |  | 66 |  |  | 2016
216983 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2016Q1 | BER | TL | 2016-01-22 15:55 | 2016-01-22 15:55 |  | Follow up |  | 66 |  |  | 2016
216984 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2016Q1 | BER | TL | 2016-01-22 15:58 | 2016-01-22 15:58 |  | Follow up |  | 66 |  |  | 2016
216985 |  |  | 852 Beryl - Dunedoo 66kV Line |  | 2016Q1 | BER | TL | 2016-01-22 16:06 | 2016-01-22 16:06 |  | Follow up |  | 66 |  |  | 2016
216986 |  |  | 80U Beryl - Ulan 66kV Line |  | 2016Q1 | BER | TL | 2016-01-22 16:23 | 2016-01-22 16:23 |  | Follow up |  | 66 |  |  | 2016
216987 |  |  | 80U Beryl - Ulan 66kV Line |  | 2016Q1 | BER | TL | 2016-01-22 16:28 | 2016-01-22 16:28 |  | Follow up |  | 66 |  |  | 2016
216993 |  |  | 7R2 Kempsey - North St tee Smithtown 33kV Line |  | 2016Q1 | KS2 | TL | 2016-01-23 05:42 | 2016-01-23 05:42 |  | Follow up |  | 33 |  |  | 2016
217005 |  |  | 99N Hillston CB 99N2 |  | 2016Q1 | DNT | CB | 2016-01-23 22:52 | 2016-01-24 11:37 | Car collided with structure. | Follow up |  | 132 |  |  | 2016
217008 | HV Equipment | CB | 99N Hillston CB 99N2 | Q | 2016Q1 | DNT | CB | 2016-01-24 15:56 | 2016-01-24 17:35 |  |  | CB 99N2 SF6 Topup | 132 |  |  | 2016
217009 |  |  | 82K/1 Queanbeyan - Bungendore tee Sutton 66kV Line |  | 2016Q1 | QBY | TL | 2016-01-24 18:44 | 2016-01-24 18:44 |  | Follow up |  | 66 |  |  | 2016
217030 |  |  | 88L Gunnedah - Gunnedah 66 66kV Line |  | 2016Q1 | GN2 | TL | 2016-01-25 15:56 | 2016-01-25 15:56 |  | Follow up |  | 66 |  |  | 2016
217031 | Lightning/Storm | TL | 949 Mt Piper 132 - Orange North 132kV TL | Q | 2016Q1 | MPP, ONO | TL | 2016-01-25 16:14 | 2016-01-25 16:14 |  | 26/02/2016 10:18:00 ¦ Follow up ¦ These defects do not pose an immediate threat to the line's serviceability. ¦ Work Orders 376080 and 376104 have been raised with 12 month priorities to replace the insulators and repair the jumper. | Successful trip and reclose during storms. | 132 |  |  | 2016
217032 |  |  | 80U Beryl - Ulan 66kV Line |  | 2016Q1 | BER | TL | 2016-01-25 18:01 | 2016-01-25 18:01 |  | Follow up |  | 66 |  |  | 2016
217033 |  |  | 836 Murrumburrah - Cootamundra 66kV Line |  | 2016Q1 | MRU | TL | 2016-01-25 21:54 | 2016-01-25 21:54 |  | Follow up |  | 66 |  |  | 2016
217034 |  |  | 890 Murrumburrah - Young 66kV Line |  | 2016Q1 | MRU | TL | 2016-01-25 22:55 | 2016-01-25 22:55 |  | Follow up |  | 66 |  |  | 2016
217035 |  |  | 893/1 Cowra - Grenfell 66kV Line |  | 2016Q1 | CW2 | TL | 2016-01-25 23:05 | 2016-01-25 23:05 |  | Follow up |  | 66 |  |  | 2016
217043 | Lightning/Storm | TL | 99A Uranquinty - Finley 132kV TL | Q | 2016Q1 | FNY, URQ | TL | 2016-01-27 00:39 | 2016-01-27 00:39 | Severe lightning activity near Uranquinty at time of TAR. | 31/03/2016 14:28:00 ¦ Follow up ¦ Structures 72-80 have been noted for the next routine aerial patrol.. | Successful trip and reclose during storms. | 132 |  |  | 2016
217109 |  |  | 82G Queanbeyan - Captains Flat 66kV Line |  | 2016Q1 | QBY | TL | 2016-01-27 11:12 | 2016-01-27 15:53 | Advised wires down on 82G outside zone sub. I&E being created | Follow up |  | 66 |  |  | 2016
217141 | Staff Error | Proc | 330kV C Bus | Q | 2016Q1 | GUR | BB | 2016-01-27 14:00 | 2016-01-27 14:25 | 20MW of Load restored by 14:25 Restoration by GoldWind staff. | Follow up | At 14:00hrs 330kV C Bus @ Gullen Range Wind Farm tripped. Transgrid and UGL ( Contractors) carrying out Interzone protection tests caused trip of 330kV C Bus. Windfarm generating approx 20MW at the time of trip. Load restored at 14:25hrs. | 330 |  |  | 2016
217280 |  |  | 890 Murrumburrah - Young 66kV Line |  | 2016Q1 | MRU | TL | 2016-01-29 06:39 | 2016-01-29 06:39 | Advised by SO/Essential Energy storms in area | Follow up |  | 66 |  |  | 2016
217295 |  |  | 828 Tumut - Gundagai 66kV Line |  | 2016Q1 | TU2 | TL | 2016-01-29 07:54 | 2016-01-29 07:54 |  | Follow up |  | 66 |  |  | 2016
217365 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2016Q1 | MRE | TL | 2016-01-29 10:07 | 2016-01-29 10:07 |  | Follow up |  | 66 |  |  | 2016
217370 | Lightning/Storm | TL | 99M Yass - Murrumburrah 132kV TL | Q | 2016Q1 | MRU, YSN | TL | 2016-01-29 08:24 | 2016-01-29 08:24 |  | 5/02/2016 13:22:00 ¦ Follow up ¦ The fault is to be noted for the next routine inspection. | Successful trip and reclose during storms | 132 |  |  | 2016
217371 |  |  | 64 Lower Tumut - Upper Tumut 330kV TL |  | 2016Q1 | LT1, UT1 | TL | 2016-01-29 08:59 | 2016-01-29 08:59 | CB 642A closed via SCADA at LTSS at 0900 | 2/03/2016 16:16:00 ¦ Follow up ¦ The area is to be noted for the next routine inspection. Protection flagging notes a red phase trip. |  | 330 |  |  | 2016
217372 |  |  | 64 UPPER TUMUT 330KV A BUS CB BAY |  | 2016Q1 | LT1 | CB | 2016-01-29 08:59 | 2016-01-29 08:59 |  |  |  | 330 |  |  | 2016
217373 |  |  | 64 UPPER TUMUT 330KV B BUS CB BAY |  | 2016Q1 | LT1 | CB | 2016-01-29 08:59 | 2016-01-29 08:59 |  |  |  | 330 |  |  | 2016
217382 | Lightning/Storm | TL | 97G Murray - Guthega tee Geehi 132kV TL | Q | 2016Q1 | GTH, MUR, GHI | TL | 2016-01-29 09:14 | 2016-01-29 09:14 | Confirmed with SHL that Geehi Dam is OOS. Clearance to attempt to close 97G 0924 - Clearance from NCM to RTS 97G. RTS ok | 3/03/2016 16:13:00 ¦ Follow up ¦ This fault has been requested to be checked on the next routine inspection of this section of line. | Successful trip and reclose during storms. | 132 |  |  | 2016
217383 |  |  | 97G/3 Geehi Tee CB 97G2 |  | 2016Q1 | GTH | CB | 2016-01-29 09:14 | 2016-01-29 09:14 |  |  |  | 132 |  |  | 2016
217384 |  |  | 97G/1 Geehi Tee CB 97G2 |  | 2016Q1 | MUR | CB | 2016-01-29 09:14 | 2016-01-29 09:14 |  |  |  | 132 |  |  | 2016
217385 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line |  | 2016Q1 | MRE | TL | 2016-01-29 11:01 | 2016-01-29 11:03 |  | Follow up |  | 66 |  |  | 2016
217386 |  |  | 847 Murrumburrah - Boorowa 66kV Line |  | 2016Q1 | MRU | TL | 2016-01-29 10:39 | 2016-01-29 10:39 |  | Follow up |  | 66 |  |  | 2016
217387 |  |  | 879 Narrabri - Wee Waa 66kV Line |  | 2016Q1 | NB2 | TL | 2016-01-29 11:09 | 2016-01-29 11:09 |  | Follow up |  | 66 |  |  | 2016
217388 |  |  | 85X Wallerawang 132 - Lithgow 66kV Line |  | 2016Q1 | WWS | TL | 2016-01-29 11:15 | 2016-01-29 11:15 |  | Follow up |  | 66 |  |  | 2016
217389 | Lightning/Storm | TL | 16 Marulan - Avon 330kV TL | Q | 2016Q1 | AVS, MRN | TL | 2016-01-29 10:46 | 2016-01-29 10:46 |  | 3/03/2016 16:33:00 ¦ Follow up ¦ This fault has been requested to be checked on the next routine inspection of this section of line. | Successful trip and reclose during storms. | 330 |  |  | 2016
217390 | Lightning/Storm | TL | O1 Upper Tumut - Canberra 330kV TL | Q | 2016Q1 | CA1, UT1 | TL | 2016-01-29 11:17 | 2016-01-29 11:17 | 11:17 - 01 T/L RTS 11:18 - CB 012B Closed via SCADA | 3/03/2016 16:37:00 ¦ Follow up ¦ This fault has been requested to be checked on the next routine inspection of this section of line. |  | 330 |  |  | 2016
217395 |  |  | 92Z Sydney North - Sydney East tee Mt Colah 132kV TL |  | 2016Q1 | SE1, SYN | TL | 2016-01-29 11:57 | 2016-01-29 11:57 | Storms in area Protection Details updated - AMC - Richard Archer 4/3/2016 | Follow up |  | 132 |  |  | 2016
217396 |  |  | 92Z Sydney North tee Mt Colah 132kV CB 92Z2 |  | 2016Q1 | SE1 | CB | 2016-01-29 11:57 | 2016-01-29 11:57 |  |  |  | 132 |  |  | 2016
217397 |  |  | 92Z Sydney East tee Mt Colah CB 92Z2 |  | 2016Q1 | SYN | CB | 2016-01-29 11:57 | 2016-01-29 11:57 |  |  |  | 132 |  |  | 2016
217404 |  |  | 250 Sydney North - Berowra 132kV Line | Y | 2016Q1 | SYN | TL | 2016-01-29 12:09 | 2016-01-29 16:12 | Storms in area Ausgrid to perform line patrol | Follow up |  | 132 |  |  | 2016
217416 | Lightning/Storm | TL | 27 Sydney North - Sydney East 330kV TL | Q | 2016Q1 | SE1, SYN | TL | 2016-01-29 12:15 | 2016-01-29 12:15 | CB 272B Manually closed at SE1 via SCADA DTF 11.89km | Follow up | Successful trip and reclose during storms | 330 |  |  | 2016
217447 | Unknown/Other | Cont | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2016Q1 | GTH, MUR, GHI | TL | 2016-01-29 12:23 | 2016-01-29 20:32 | SHL Generating 31MW from Unit 1 at Guthega at time of trip Storms in area. 1223hrs - F, SO - attempted to Close CB..97G2 received command failure and C.B. did not close. LV CB Abnormal alarm at time of closing most likely culprit. 18:30 SMF advised SF6 Lockout follower relay had failed and was preventing the CB..97G2 from closing | 3/03/2016 16:23:00 ¦ Follow up ¦ This fault has been requested to be checked on the next routine inspection of this section of line. | SHL Generating 31MW from Unit 1 at Guthega at time of trip Storms in area. 1223hrs - F, SO - attempted to Close CB..97G2 received command failure and C.B. did not close. LV CB Abnormal alarm at time of closing most likely culprit. 18:30 SMF advised SF6 Lockout follower relay had failed and was preventing the CB..97G2 from closing | 132 |  | Fault | 2016
217448 |  |  | 97G/3 Geehi Tee CB 97G2 |  | 2016Q1 | GTH | CB | 2016-01-29 12:23 | 2016-01-29 20:32 |  |  |  | 132 |  |  | 2016
217449 |  |  | 97G/1 Geehi Tee CB 97G2 |  | 2016Q1 | MUR | CB | 2016-01-29 12:23 | 2016-01-29 20:32 |  |  |  | 132 |  |  | 2016
217450 |  |  | 881 Moree - Garah tee Ashley 66kV Line |  | 2016Q1 | MRE | TL | 2016-01-29 13:48 | 2016-01-29 13:48 |  | Follow up |  | 66 |  |  | 2016
217507 | Relay Faulty | Prot | No.2 Static Var Compensator | Z | 2016Q1 | KCR | SVC | 2016-01-29 21:06 | 2016-01-30 10:14 | After investigation by On Call Fitter, protection indicated a CBF Trip input LED initiated No.1 Prot only. The SVC Reactor has been isolated off the system until further investigation by Protection Staff. note received a sub Miscellaneous Equipment Fail alarm 4 minutes prior to the No.2 SVC (Reactor) trip and reset just after the No.2 SVC (Reactor) tripped. | Follow up | After investigation by On Call Fitter, protection indicated a CBF Trip input LED initiated No.1 Prot only. The SVC Reactor has been isolated off the system until further investigation by Protection Staff. note received a sub Miscellaneous Equipment Fail alarm 4 minutes prior to the No.2 SVC (Reactor) trip and reset just after the No.2 SVC (Reactor) tripped. | 330 |  | Fault | 2016
217508 | Lightning/Storm | TL | 11 Dapto - Sydney South 330kV TL | Q | 2016Q1 | DPT, SYS | TL | 2016-01-29 21:12 | 2016-01-29 21:12 |  | Follow up | Successful trip and reclose during storms. | 330 |  |  | 2016
217542 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line |  | 2016Q1 | CW2 | TL | 2016-01-30 13:00 | 2016-01-30 16:15 |  | Follow up |  | 66 |  |  | 2016
217543 |  |  | 93X Sydney West - Nepean tee Bringelly 132kV Line |  | 2016Q1 | SYW | TL | 2016-01-30 14:46 | 2016-01-30 14:47 |  | Follow up |  | 132 |  |  | 2016
217544 |  |  | 79P Griffith - Goolgowi 33kV Line |  | 2016Q1 | GRF | TL | 2016-01-30 14:52 | 2016-01-30 14:52 |  | Follow up |  | 33 |  |  | 2016
217545 |  |  | 912 Sydney South - Port Hacking 132kV Line |  | 2016Q1 | SYS | TL | 2016-01-30 15:58 | 2016-01-30 19:54 | SO/Ausgrid advised 912 Sydney South - Port Hacking 132kV Line has been patrolled and requested energised from Sydney south, no information received about Trip. Approx 70MW customer load lost, load was restored via customer network in blocks unsure of timing. | Follow up |  | 132 |  |  | 2016
217546 |  |  | 282 Sydney South - Milperra tee Revesby 132kV Line |  | 2016Q1 | SYS | TL | 2016-01-30 16:02 | 2016-01-30 20:29 | SO/Ausgrid advised 282 Sydney South to Revesby 132 kV Line has been patrolled and requested energised from Sydney south, no information received about Trip. No customer load lost as 282 Revesby in parallel with 283 Revesby | Follow up |  | 132 |  |  | 2016
217547 | Lightning/Storm | TL | 944 Orange North - Wallerawang 132kV TL | Q | 2016Q1 | ONO, WWS | TL | 2016-01-30 17:33 | 2016-01-30 17:33 |  | Follow up | Successful trip and reclose during storms. | 132 |  |  | 2016
217561 |  |  | No.4 Council Feeder 22kV CB 42 | N | 2016Q1 | TTF | CB | 2016-01-31 14:52 | 2016-01-31 18:31 | Transformer ended feeder. Nil auto reclose, Essential Energy staff confirmed No.3 TX supplied Via No.4 fdr has had the explosion vent operate giving evidence to No.3 TX fault. Essential energy staff isolated No.3 TX and No.4 fdr was the closed to energise No.4 TX and load restored. (Note - 2MW off for 4hr 20mins). | Follow up |  | 22 |  |  | 2016
217702 | Relay Faulty | Prot | No.2 Transformer 330/132/11KV | Z | 2016Q1 | SYN | TX | 2016-02-01 11:01 | 2016-02-03 15:36 | Advised by Protection staff that the Transformer No.1 Protection T60 Relay is faulty and operated incorrectly. Relay to be replaced on Tuesday 02/02/2016. | Follow up | Advised by Protection staff that the Transformer No.1 Protection T60 Relay is faulty and operated incorrectly. Relay to be replaced on Tuesday 02/02/2016. | 330 | Relay replaced. | Fault | 2016
217703 |  |  | Station Transformer 1A | N | 2016Q1 | LD1 | TX | 2016-02-01 11:05 | 2016-02-05 12:47 |  | Follow up |  | 330 |  |  | 2016
217721 | HV Equipment | Rx | No.2 Reactor | E | 2016Q1 | BFD | RX | 2016-02-01 14:49 | 2016-02-03 17:44 | Asset Monitoring Centre requested No.2 Reactor taken out of service due to high water content in oil. No.2 Reactor not available for service. | Follow up | Asset Monitoring Centre requested No.2 Reactor taken out of service due to high water content in oil. No.2 Reactor not available for service. | 132 | Sampling issue - no problem with reactor. | Forced | 2016
217783 | HV Equipment | CB | No.3 Transformer 330/132/11kV | N | 2016Q1 | BFD | TX | 2016-02-02 12:35 | 2016-02-02 14:24 |  |  | CB 5432 SF6 Topup | 330 |  |  | 2016
217791 | Unknown/Other | TL | 96F Stroud - Tomago 330 132kV TL | E | 2016Q1 | TOM | TL | 2016-02-03 07:23 | 2016-02-03 15:47 |  |  | Less than 24Hr notice outage for pole replacement | 132 |  | Forced | 2016
217942 |  |  | 881 Moree - Garah tee Ashley 66kV Line | N | 2016Q1 | MRE | TL | 2016-02-03 14:20 | 2016-02-03 14:20 |  | Follow up |  | 66 |  |  | 2016
217943 | LV/MECH Fail | Cont | 9U2 Inverell - Moree 132kV TL | Z | 2016Q1 | INV, MRE | TL | 2016-02-03 15:00 | 2016-02-03 15:17 | CB 9U22 at Inverell failed to close due to check relay failure. Closing check relay power cycled by Field staff to reset relay and clear closing check relay faulty alarm. A/R initiate relay also locked up which was also reset by power cycling. CB 9U22 at Inverell eventually closed via SCADA. | Follow up | CB 9U22 at Inverell failed to close due to check relay failure. Closing check relay power cycled by Field staff to reset relay and clear closing check relay faulty alarm. A/R initiate relay also locked up which was also reset by power cycling. CB 9U22 at Inverell eventually closed via SCADA. | 132 | No further action required. | Fault | 2016
217944 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line | N | 2016Q1 | MRE | TL | 2016-02-03 17:26 | 2016-02-03 17:26 |  | Follow up |  | 66 |  |  | 2016
218010 | LV/MECH Fail | CB | No.3 330kV Reactor | Z | 2016Q1 | AR1 | RX | 2016-02-04 13:32 | 2016-02-04 14:20 |  |  | No.3 reactor 330kV C.B 5932 tripped when operations attempted to close it on red phase pole discrepancy. a LV/Mechanical permit was taken out and red phase failed to close. Internal auxillary contacts were cleaned and inspected. A furter five operations of the C.B were successful and the C.B was returned to service. This problem has occurred in the past and white phase auxillary contact block was replaced. | 330 | No further action required. | Fault | 2016
218181 |  |  | Broken Hill - Solar Plant 1 22kV Line | N | 2016Q1 | BKH | TL | 2016-02-06 13:03 | 2016-02-06 17:06 | AGL contractor conducted line patrol advised found dead bird at base of pole | Follow up |  | 22 |  |  | 2016
218225 | LV/MECH Fail | Prot | 708 Port Macquarie - Owen St tee Boronia St 33kV Line | N | 2016Q1 | PMQ | TL | 2016-02-09 00:28 | 2016-02-09 18:46 | 708 Owen St tee Boronia St CB..7082 was taken out of service after several trip and reclose operations at Port Macquarie Substation were Essential Energy was able to confirm there was no fault. Faulty No1 protection relay was replaced and feeder returned to service. | Follow up | 708 Owen St tee Boronia St CB..7082 was taken out of service after several trip and reclose operations at Port Macquarie Substation were Essential Energy was able to confirm there was no fault. Faulty No1 protection relay was replaced and feeder returned to service. | 33 | Known issue |  | 2016
218359 |  |  | 79C Griffith - Darlington Point 33kV Line | N | 2016Q1 | GRF | TL | 2016-02-09 14:43 | 2016-02-09 16:11 | EsE advises that a faulty recloser was cause of fault. Further work to repair will be carried out by EsE. | Follow up |  | 33 |  |  | 2016
218407 | Unknown/Other | SVC | No.1 Static VAr Compensator | Z | 2016Q1 | BKH | SVC | 2016-02-10 10:49 | 2016-02-10 15:49 | No1 SVC tripped during Aux Supply changeover | Follow up | No1 SVC tripped during Aux Supply changeover | 22 | Mark Jones to follow up on switching practice and arrangements for 415V at Broken Hill. | Fault | 2016
218449 | HV Equipment | CB | 330kV B Bus 1-2 Section CB 5112 | N | 2016Q1 | SE1 | CB | 2016-02-10 18:29 | 2016-02-10 19:47 |  |  | low gas on cb 5112 blue phase topped up | 330 |  |  | 2016
218491 |  |  | 990 Yass - Wagga 132 132kV TL | N | 2016Q1 | WG2, YSN | TL | 2016-01-30 20:50 | 2016-01-30 20:50 |  | Follow up |  | 132 |  |  | 2016
218527 |  |  | 800 Wallerawang 132 - Railway 66kV Line | N | 2016Q1 | WWS | TL | 2016-02-11 15:04 | 2016-02-11 19:48 |  | Follow up |  | 66 |  |  | 2016
218528 |  |  | 828 Mt Piper 132 - Portland tee BCSC 66kV Line | N | 2016Q1 | MPP | TL | 2016-02-11 15:40 | 2016-02-11 15:40 |  | Follow up |  | 66 |  |  | 2016
218529 |  |  | 82G Queanbeyan - Captains Flat 66kV Line | N | 2016Q1 | QBY | TL | 2016-02-11 16:05 | 2016-02-11 16:05 |  | Follow up |  | 66 |  |  | 2016
219836 |  |  | 800 Wallerawang 132 - Railway 66kV Line | N | 2016Q1 | WWS | TL | 2016-02-11 21:21 | 2016-02-11 21:31 |  | Follow up |  | 66 |  |  | 2016
219837 |  |  | 81F Panorama - Bathurst 66kV Line | N | 2016Q1 | PMA | TL | 2016-02-12 05:13 | 2016-02-12 05:13 |  | Follow up |  | 66 |  |  | 2016
219845 | Unknown/Other | TL | 976/1 Canberra - Queanbeyan tee Spring Flat 132kV TL | N | 2016Q1 | CA1, QBY, SFF | TL | 2016-02-12 06:09 | 2016-02-12 06:09 | DTF 53.68km from CA1 | Follow up | TAR | 132 |  |  | 2016
220159 |  |  | 828 Mt Piper 132 - Portland tee BCSC 66kV Line | N | 2016Q1 | MPP | TL | 2016-02-12 14:53 | 2016-02-13 10:28 |  | Follow up |  | 66 |  |  | 2016
220177 |  |  | No.3 Transformer 330/132/11kV | N | 2016Q1 | VYD | TX | 2016-02-14 05:22 | 2016-02-14 14:50 |  |  |  | 330 |  |  | 2016
220178 | HV Equipment | CB | No.1 Transformer 330/132/16kV | E | 2016Q1 | SE1 | TX | 2016-02-13 22:45 | 2016-02-13 23:48 |  |  | Top up SF6 Gas C.B.. 5412 | 330 |  | Forced | 2016
220179 |  |  | No.1 Auxiliary Transformer 16kV/415V | N | 2016Q1 | SE1 | TX | 2016-02-13 22:45 | 2016-02-13 23:48 |  |  |  | 16 |  |  | 2016
220180 |  |  | 712 Port Macquarie - Rocks Ferry 33kV Line | N | 2016Q1 | PMQ | TL | 2016-02-14 03:47 | 2016-02-14 03:47 | Fault location 4.269km | Follow up |  | 33 |  |  | 2016
220188 | HV Equipment | CB | 232 Regentville - Glenmore Park 132kV Line | N | 2016Q1 | RGV | TL | 2016-02-14 10:59 | 2016-02-14 10:59 |  |  | SF6 topup of CB 2322 | 132 |  |  | 2016
220189 | HV Equipment | CB | 132kV No.1 Bus Coupler CB 4012 | N | 2016Q1 | RGV | CB | 2016-02-14 10:59 | 2016-02-14 12:30 | Low SF6 on Bus coupler CB..4012 at Regentville 330kV Substation | Follow up | Low SF6 on Bus coupler CB..4012 at Regentville 330kV Substation | 132 |  |  | 2016
220193 | HV Equipment | CB | 875 (NOT CONNECTED) CB 8752 | N | 2016Q1 | GN2 | CB | 2016-02-15 07:41 | 2016-02-15 11:03 |  |  | Remove pallet switch from CB 8752 | 66 |  |  | 2016
220199 |  |  | 877 Gunnedah - Keepit PS 66kV Line | N | 2016Q1 | GN2 | TL | 2016-02-15 07:42 | 2016-02-15 07:42 |  | Follow up |  | 66 |  |  | 2016
220230 | Unknown/Other | TL | 96L Lismore 330 - Tenterfield tee Casino 132kV TL | N | 2016Q1 | LSM, TTF | TL | 2016-02-15 13:10 | 2016-02-15 13:10 |  | Follow up | TAR | 132 |  |  | 2016
220294 |  |  | No.1 Taree - Council Bootawa 33kV Line | N | 2016Q1 | TRE | TL | 2016-02-15 21:23 | 2016-02-15 22:38 |  | Follow up |  | 33 |  |  | 2016
220337 |  |  | L5 Lower Tumut - Tumut 3 330kV TL | X | 2016Q1 | LT1, TP3 | TL | 2016-02-16 13:35 | 2016-02-16 17:21 |  |  |  | 330 |  |  | 2016
220366 |  |  | 712 Port Macquarie - Rocks Ferry 33kV Line | N | 2016Q1 | PMQ | TL | 2016-02-17 05:06 | 2016-02-17 13:43 |  |  |  | 33 |  |  | 2016
220367 |  |  | No.2 330kV Generator Transformer Group | N | 2016Q1 | LD1 | TX | 2016-02-16 20:14 | 2016-02-23 02:21 |  |  |  | 330 |  |  | 2016
220370 |  |  | 662 Armidale - Walcha 66kV Line | N | 2016Q1 | AR1 | TL | 2016-02-16 19:41 | 2016-02-16 19:41 |  | Follow up |  | 66 |  |  | 2016
220562 | LV/MECH Fail | Cont | 9R2 Wagga 330 - Uranquinty 132kV TL | E | 2016Q1 | WG1, URQ | TL | 2016-02-18 14:45 | 2016-02-19 12:00 | CVT Phase imballance alarm received. Requested out of service by B Mills. | Follow up | CVT Phase imballance alarm received. Requested out of service by B Mills. Investigations determined that the cause was a failed power meter. | 132 | No further action required. | Forced | 2016
220576 |  |  | 712 Port Macquarie - Rocks Ferry 33kV Line | N | 2016Q1 | PMQ | TL | 2016-02-19 03:39 | 2016-02-19 03:39 |  | Follow up |  | 33 |  |  | 2016
220677 |  |  | No.2 Balranald - Moulamein 22kV Line | N | 2016Q1 | BRD | TL | 2016-02-20 02:19 | 2016-02-20 02:19 |  | Follow up |  | 22 |  |  | 2016
220685 |  |  | No.1 Taree - Council Bootawa 33kV Line | N | 2016Q1 | TRE | TL | 2016-02-20 13:52 | 2016-02-20 13:52 |  | Follow up |  | 33 |  |  | 2016
220686 |  |  | 867 Taree - OCC Failford 66kV Line | N | 2016Q1 | TRE | TL | 2016-02-20 15:02 | 2016-02-20 15:02 |  | Follow up |  | 66 |  |  | 2016
220689 | HV Equipment | CB | No.2 Capacitor | N | 2016Q1 | TRE | CAP | 2016-02-20 17:47 | 2016-02-20 18:42 |  |  | SF6 topup of CB 2722 | 33 |  |  | 2016
220690 |  |  | 712 Port Macquarie - Rocks Ferry 33kV Line | N | 2016Q1 | PMQ | TL | 2016-02-21 00:46 | 2016-02-21 00:46 |  | Follow up |  | 33 |  |  | 2016
220700 | HV Equipment | CB | 932 Sydney West - Mt Druitt 132kV Line | E | 2016Q1 | SYW | TL | 2016-02-21 14:37 | 2016-02-21 15:27 |  |  | SF6 topup of CB 9322 | 132 |  | Forced | 2016
220701 | HV Equipment | CB | No.2 Static Var Compensator | E | 2016Q1 | KCR | SVC | 2016-02-21 19:28 | 2016-02-21 21:52 | Site HMI indicates Low SF6 Gas Pressure alarm for No.2 SVC C.B.. 5V22 or associated C.T. SF6 gas topped up on blue phase of No.2 SVC C.B.. 5V22 under HVPRI 64147. | Follow up | Site HMI indicates Low SF6 Gas Pressure alarm for No.2 SVC C.B.. 5V22 or associated C.T. SF6 gas topped up on blue phase of No.2 SVC C.B.. 5V22 under HVPRI 64147. | 330 |  | Forced | 2016
220898 |  |  | 854 Macarthur - Campbelltown 66kV Line | N | 2016Q1 | MAC | TL | 2016-02-23 14:48 | 2016-02-23 14:48 | Did not auto-reclose at remote end. Manually restored by SO/Endeavour Energy 14:53. Approx 22MW load lost. | Follow up |  | 66 |  |  | 2016
220899 |  |  | 257 Sydney North - Galston 132kV Cable | N | 2016Q1 | SYN | UG | 2016-02-23 15:53 | 2016-07-20 19:31 | CB 2572 at Sydney North closed on request from Ausgrid under HVPRI 63887. CB tripped 22 seconds later. No customer load lost as still isolated at remote end. | Follow up |  | 132 |  |  | 2016
220926 | Condition Monitor | Cond | 99N Hillston CB 99N2 | N | 2016Q1 | DNT | CB | 2016-02-24 09:03 | 2016-02-24 14:14 |  |  | REPLACE DENSITY MONITOR | 132 | AMC to follow up. [9/5/2016] Complete. |  | 2016
220971 | HV Equipment | CT | 35 Marulan CB 352 | N | 2016Q1 | MTP | CB | 2016-02-24 10:21 |  | Received advice from Ken Wyper CB..352 CT's are faulty and are to be take out of service. | Follow up | CTs have damaged Bellows | 330 | Currently under review by Tony Gray. [8/4/2016] Needs statement being put together by Evan Lamplough for the decommissioning of this bay. [9/5/2016] Tim Barnes: Agreed with Tony Gray and Operations - can leave out of service and it will be decommissioned. |  | 2016
220980 | Wiring/Testing Error | Proc | No.1 Reactor | E | 2016Q1 | SE1 | RX | 2016-02-24 13:23 | 2016-02-24 16:06 |  |  | Reccuring CB abnormal Alarm on operation | 132 | AMC to follow up. [8/4/2016] W/O 379272 closed. Issue resolved. | Forced | 2016
221035 | LV/MECH Fail | Cond | 42 Sydney South - Haymarket 330kV Cable | Z | 2016Q1 | HYM, SYS | UG | 2016-02-24 15:40 | 2016-02-24 18:41 | Trip Caused by 42 CMS temperature monitoring system failure which operated cable Protections at both ends of cable 42. 42 CMS Temperature sensor system has been Isolated and the CMS Low Oil Trip remains in-service, Permission from OCM Sam Cavaleri to return to Service Cable 42 . Cable 42 RTS on load at 18:41hrs | Follow up | Failed temp sensor | 330 |  | Fault | 2016
221062 | LV/MECH Fail | Cont | No.4 Capacitor | E | 2016Q1 | TRE | CAP | 2016-02-25 10:20 | 2016-02-25 12:03 |  |  | Faulty control system (relay based) | 66 | AMC to provide more details. [8/4/2016] Issue resolved. | Forced | 2016
221156 |  |  | L1 Lower Tumut - Tumut 3 330kV TL | Y | 2016Q1 | LT1, TP3 | TL | 2016-02-25 14:38 | 2016-02-26 16:59 | L1 Tumut 3 330kV T/L tripped. SHL investigating.Lost about 500MW of Generation. | Follow up |  | 330 |  |  | 2016
221159 | HV Equipment | CT | 217 Sydney West - North Eastern Creek 132kV Line | N | 2016Q1 | SYW | TL | 2016-02-25 16:44 | 2016-02-25 18:07 |  |  | Topup SF6 in all three phases of the CT | 132 |  |  | 2016
221165 |  |  | 9E3 Sydney East - Willoughby 132kV Line | N | 2016Q1 | SE1 | TL | 2016-02-25 19:07 | 2016-02-25 19:18 |  |  |  | 132 |  |  | 2016
221258 | Relay Faulty | Prot | No.1 Transformer 330/132/11KV | Z | 2016Q1 | WL1 | TX | 2016-02-26 15:43 | 2016-02-27 13:59 | Maloperation of buchholz relay. Buchholz checked and TX returned to service. | Follow up | Maloperation of buchholz relay. Buchholz checked and TX returned to service. | 330 |  | Fault | 2016
221259 | LV/MECH Fail | TX | No.5 Transformer 330/132/11kV | E | 2016Q1 | SYN | TX | 2016-02-26 16:55 | 2016-02-26 19:07 | Received No.5 Transformer Pressure Relief - Urgent Transformer Returned to Service with clearance from On Call Engineer and NCM as the alarm was caused by suspected moisture in the Junction Box of one of the two Pressure Relief valves. Alarm from that particular Pressure Relief valve isolated and the one from second valve still operational. Transformer data was checked by On Call Engineer and found to be satisfactory. | Follow up ¦ Work Order #379569 created to identify cause of erroneous alarm associated with the QUALITROL type pressure relief device. Work committed for March 16, 2016. Alarm isolated until issue can be corrected. | Received No.5 Transformer Pressure Relief - Urgent Transformer Returned to Service with clearance from On Call Engineer and NCM as the alarm was caused by suspected moisture in the Junction Box of one of the two Pressure Relief valves. Alarm from that particular Pressure Relief valve isolated and the one from second valve still operational. Transformer data was checked by On Call Engineer and found to be satisfactory. | 330 | Known issue - being resolved with workorder. | Forced | 2016
221261 |  |  | 868 Taree - Bohnock Tee Hallidays Point 66kV Line | N | 2016Q1 | TRE | TL | 2016-02-26 19:42 | 2016-02-26 19:42 |  | Follow up |  | 66 |  |  | 2016
221327 | HV Equipment | CB | No.2 Transformer 132kV B CB 4422B | N | 2016Q1 | SE1 | CB | 2016-02-28 11:19 | 2016-02-28 14:21 | Low SF6 Gas Pressure alarm indicated on Site HMI. SF6 gas topped up under HVPRI 64278 and C.B.. 4422B returned to service at 1421 hours. | Follow up | Low SF6 Gas Pressure alarm indicated on Site HMI. SF6 gas topped up under HVPRI 64278 and C.B.. 4422B returned to service at 1421 hours. | 132 |  |  | 2016
221899 | LV/MECH Fail | Cond | No.3 Transformer 330/132/11kV | E | 2016Q1 | WDL | TX | 2016-02-29 15:29 | 2016-03-01 12:45 |  |  | Concerns with connections to Condition Monitoring equipment on No.3 Transformer bushings at Williamsdale 330kV Substation. | 330 |  | Forced | 2016
221900 |  |  | 974 Cooma - Bega 132kV Line |  | 2016Q1 | CMA | TL | 2016-01-30 13:00 | 2016-01-30 13:00 | NOTE - Time of TAR unknown. Essential Energy only able to advise date of incident. | Follow up |  | 132 |  |  | 2016
221958 | HV Equipment | CB | 330kV B Bus 1-2 Section CB 5112 | N | 2016Q1 | SE1 | CB | 2016-03-01 18:06 | 2016-03-01 19:25 |  |  | Low SF6 gas pressure on 330kV B Bus 1-2 Section C.B.. 5112. C.B. taken out of service under HVPRI 64323 and SF6 gas topped up @ 1908 hours and 330kV B Bus 1-2 Section C.B.. 5112 returned to service @ 1925 hours. | 330 |  |  | 2016
222016 | LV/MECH Fail | TL | 949 Mt Piper 132 - Orange North 132kV TL | E | 2016Q1 | MPP, ONO | TL | 2016-03-02 10:33 | 2016-03-02 16:18 |  |  | Straighten Pole and Instal Guy - STR 169 | 132 | Issue resolved. | Forced | 2016
222042 | Relay Faulty | Prot | No.8 330/132/11kV Transformer | Z | 2016Q1 | TOM | TX | 2016-03-02 15:58 | 2016-03-04 19:58 |  | Follow up | Replace No.1 protection relay and test | 330 | Suspect T60 [9/5/2016] Mark Jones: Close. | Fault | 2016
222144 | Unknown/Other | TL | 999 Yass - Cowra 132kV TL | E | 2016Q1 | CW2, YSN | TL | 2016-03-03 13:01 | 2016-03-07 21:44 |  |  | Advised ambient temp above 35 deg | 132 |  | Forced | 2016
222405 |  |  | Broken Hill - Solar Plant 1 22kV Line | N | 2016Q1 | BKH | TL | 2016-03-04 13:11 | 2016-03-04 13:42 | AGL Found a couple of dead birds underneath the line outside the Solar Plant Substation. Advised that the fault has cleared and requested to energise the No.1 Solar 22kV T/L from Broken Hill 220kV Substation. | Follow up |  | 22 |  |  | 2016
222452 |  |  | Broken Hill - Solar Plant 1 22kV Line | N | 2016Q1 | BKH | TL | 2016-03-05 15:29 | 2016-03-06 07:22 |  | Follow up |  | 22 |  |  | 2016
222511 |  |  | Broken Hill - Solar Plant 2 22kV Line | N | 2016Q1 | BKH | TL | 2016-03-07 12:08 | 2016-03-07 13:40 |  | Follow up |  | 22 |  |  | 2016
222993 | Tree/Ground | Other | No.2 Static Var Compensator | E | 2016Q1 | KCR | SVC | 2016-03-09 07:39 | 2016-03-09 14:15 |  |  | Requires Urgent Weeding In Cage | 330 | Issue resolved. | Forced | 2016
223871 | HV Equipment | CB | 7R4 Kempsey - Munga 33kV Line | N | 2016Q1 | KS2 | TL | 2016-03-10 07:46 | 2016-03-10 09:52 |  |  | SF6 Top up | 33 |  |  | 2016
223945 |  |  | 875 Wallerawang 132 - Oakey Park 66kV Line | N | 2016Q1 | WWS | TL | 2016-03-10 13:09 | 2016-03-10 13:09 | Distance to fault - 11km | Follow up |  | 66 |  |  | 2016
223948 |  |  | 800 Wallerawang 132 - Railway 66kV Line | N | 2016Q1 | WWS | TL | 2016-03-10 09:13 | 2016-03-10 14:25 | Line returned to service at request of SRA | Follow up |  | 66 |  |  | 2016
223951 |  |  | 85X Wallerawang 132 - Lithgow 66kV Line | N | 2016Q1 | WWS | TL | 2016-03-10 13:17 | 2016-03-10 13:17 | Distance to fault - 8.154km | Follow up |  | 66 |  |  | 2016
223962 | HV Equipment | CB | 5A2 Eraring B CB 5A22B | N | 2016Q1 | KCR | CB | 2016-03-10 18:21 | 2016-03-10 19:01 |  |  | SF6 TOPUP | 500 |  |  | 2016
223966 |  |  | 848 Tumut - Tumbarumba tee Batlow tee Adelong 66kV Line | N | 2016Q1 | TU2 | TL | 2016-03-10 23:32 | 2016-03-11 10:55 |  | Follow up |  | 66 |  |  | 2016
224286 |  |  | 712 Port Macquarie - Rocks Ferry 33kV Line | N | 2016Q1 | PMQ | TL | 2016-03-11 20:49 | 2016-03-11 20:49 |  | Follow up |  | 33 |  |  | 2016
224294 |  |  | 99R Darlington Point - Hay 132kV Line | N | 2016Q1 | DNT | TL | 2016-03-12 14:42 | 2016-03-12 20:28 | 17:45 SO/Essential confirmed approx 60% of customer load has been restored Essential 33kV system. | Follow up |  | 132 |  |  | 2016
224295 |  |  | 94B Beryl - Wellington 132kV TL | N | 2016Q1 | BER, WL1 | TL | 2016-03-13 05:50 | 2016-03-13 05:50 | Beryl Protection Details updated - AMC - RA | 15/03/2016 14:53:00 ¦ Follow up ¦ Noted for the next routine inspection. |  | 132 |  |  | 2016
224300 |  |  | 893/5 Forbes - Payten's Bridge 66kV Line | N | 2016Q1 | FB2 | TL | 2016-03-13 17:29 | 2016-03-13 17:29 |  | Follow up |  | 66 |  |  | 2016
224301 |  |  | 893/5 Forbes - Payten's Bridge 66kV Line | N | 2016Q1 | FB2 | TL | 2016-03-13 17:52 | 2016-03-13 17:52 |  | Follow up |  | 66 |  |  | 2016
224302 |  |  | 893/5 Forbes - Payten's Bridge 66kV Line | N | 2016Q1 | FB2 | TL | 2016-03-13 18:28 | 2016-03-13 18:30 |  | Follow up |  | 66 |  |  | 2016
224303 |  |  | 893/5 Forbes - Payten's Bridge 66kV Line | N | 2016Q1 | FB2 | TL | 2016-03-13 18:40 | 2016-03-13 18:40 |  | Follow up |  | 66 |  |  | 2016
224304 |  |  | 866 Cowra - Cowra Town 66kV Line | N | 2016Q1 | CW2 | TL | 2016-03-13 18:55 | 2016-03-13 18:55 | Distance to fault - 3.476km | Follow up |  | 66 |  |  | 2016
224305 |  |  | 866 Cowra - Cowra Town 66kV Line | N | 2016Q1 | CW2 | TL | 2016-03-13 18:55 | 2016-03-13 18:55 | Distance to fault - 3.476km | Follow up |  | 66 |  |  | 2016
224306 |  |  | 865 Cowra - Cowra Town 66kV Line | N | 2016Q1 | CW2 | TL | 2016-03-13 19:03 | 2016-03-13 19:03 |  | Follow up |  | 66 |  |  | 2016
224307 |  |  | 973 Yass - Cowra 132kV TL | N | 2016Q1 | CW2, YSN | TL | 2016-03-13 19:30 | 2016-03-13 19:30 | Protection Details added - AMC - SC & RA | 22/03/2016 10:26:00 ¦ Follow up ¦ Structures 470 - 485 have been noted for the next routine aerial patrol. |  | 132 |  |  | 2016
224308 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line | N | 2016Q1 | CW2 | TL | 2016-03-13 19:36 | 2016-03-13 19:36 | Distance to fault - 10.21km | Follow up |  | 66 |  |  | 2016
224309 |  |  | 7R2 Kempsey - North St tee Smithtown 33kV Line | N | 2016Q1 | KS2 | TL | 2016-03-13 20:33 | 2016-03-13 21:54 | Suspect bats to be cause of trip, EE reuest close CB after patrol | Follow up |  | 33 |  |  | 2016
225877 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line | N | 2016Q1 | MRE | TL | 2016-03-13 20:04 | 2016-03-15 15:40 |  | Follow up |  | 66 |  |  | 2016
225878 |  |  | 867 Taree - OCC Failford 66kV Line | N | 2016Q1 | TRE | TL | 2016-03-15 03:24 | 2016-03-15 03:24 |  | Follow up |  | 66 |  |  | 2016
225993 | Unknown/Other | Other | 895 Forbes - Parkes (89H West Jemalong) 66kV Line | N | 2016Q1 | FB2 | TL | 2016-03-15 17:07 | 2016-03-15 18:30 |  |  | CT ratio change Less than 24 hours notice | 66 | AMC to followup to find out why a <24 hr notice outage was necessary for a CT ratio change. [9/5/2016]. Problem with design. Raise with Design in another forum. Close. |  | 2016
226074 |  |  | No.2 Transformer 500/330/33KV | E | 2016Q1 | KCR | TX | 2016-03-16 17:38 | 2016-03-16 19:09 |  |  |  | 500 |  | Forced | 2016
226128 | Relay Setting | Prot | No.1 Transformer 500/330/33kV | Z | 2016Q1 | BBY | TX | 2016-03-17 07:43 | 2016-03-17 22:40 | No adverse weather at time of trip, Fault recorder indicates operation of No.1 Prot, no obvious fault observed. RTI indicates T60 relay. | Follow up | L90 relay bad firmware/settings | 500 | L90 firmware being upgrded across the network [9/5/2016] Mark Jones: Close. | Fault | 2016
226129 |  |  | No.1 Reactor | N | 2016Q1 | BBY | RX | 2016-03-17 07:43 | 2016-03-17 22:40 |  |  |  | 33 |  |  | 2016
226169 | HV Equipment | CB | No.2 Transformer 132kV B CB 4422B | N | 2016Q1 | SE1 | CB | 2016-03-17 12:52 | 2016-03-17 15:09 |  |  | SF6 top-up | 132 |  |  | 2016
226212 | HV Equipment | CB | No.2 Static Var Compensator | E | 2016Q1 | KCR | SVC | 2016-03-17 20:53 | 2016-03-17 22:47 | Low SF6 Gas alarm received onSCADA for No.2 SVC C.B.. 5V22. C.B. isolated and SF6 gas topped up. No.2 SVC Reactor available for service at 2247. AEMO requested No.2 SVC Reactor in service @ 2250. | Follow up | SF6 top-up | 330 |  | Forced | 2016
226248 |  |  | 79L Griffith - Beelbangera 33kV Line | N | 2016Q1 | GRF | TL | 2016-03-18 08:56 | 2016-03-18 16:56 |  | Follow up |  | 33 |  |  | 2016
226249 |  |  | 83G Wagga North - Bomen 66kV Line | N | 2016Q1 | WGN | TL | 2016-03-18 09:55 | 2016-03-18 09:55 |  | Follow up |  | 66 |  |  | 2016
226339 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line | N | 2016Q1 | MRE | TL | 2016-03-18 14:14 | 2016-03-18 14:14 |  | Follow up |  | 66 |  |  | 2016
226345 | Lightning/Storm | TL | 88 Muswellbrook - Tamworth 330 330kV TL | N | 2016Q1 | MRK, TA1 | TL | 2016-03-18 17:36 | 2016-03-18 17:36 | TA1 Prot details added | 22/03/2016 11:12:00 ¦ Follow up ¦ Structures 140 - 160A, 'A' phase, noted for the next routine inspection. | Successful trip and reclose during storms | 330 |  |  | 2016
226346 |  |  | 878 Narrabri - Boggabri 66kV Line | N | 2016Q1 | NB2 | TL | 2016-03-18 17:51 | 2016-03-18 17:51 |  | Follow up |  | 66 |  |  | 2016
226347 |  |  | 870 Tamworth 132 - Kootingal 66kV Line | N | 2016Q1 | TMW | TL | 2016-03-18 18:41 | 2016-03-18 18:41 |  | Follow up |  | 66 |  |  | 2016
226348 |  |  | 870 Tamworth 132 - Kootingal 66kV Line | N | 2016Q1 | TMW | TL | 2016-03-18 18:49 | 2016-03-18 18:49 |  | Follow up |  | 66 |  |  | 2016
226349 |  |  | 870 Tamworth 132 - Kootingal 66kV Line | N | 2016Q1 | TMW | TL | 2016-03-18 19:09 | 2016-03-18 19:09 |  | Follow up |  | 66 |  |  | 2016
226375 | LV/MECH Fail | CB | No.3 330kV Reactor | E | 2016Q1 | AR1 | RX | 2016-03-21 13:20 | 2016-03-23 14:20 |  |  | Less than 24 Hrs notice C.B 5932 investigate Pole Discrepancy operation. | 330 | Tim Barnes to follow up. [9/5/2016] Work Order (WO) 376879 complete. WO 382201 complete. | Forced | 2016
226399 | LV/MECH Fail | CB | L3 Tumut 3 A CB L32A | N | 2016Q1 | LT1 | CB | 2016-03-22 07:14 | 2016-03-22 10:08 |  |  | Less than 24 Hrs notice INVESTIGATE WHITE AND BLUE PHASES CLOSING SPRINGS NOT CHARGING. | 330 | Tim Barnes to follow up. [9/5/2016] Work Order 382226 complete. |  | 2016
226400 |  |  | 879 Narrabri - Wee Waa 66kV Line | N | 2016Q1 | NB2 | TL | 2016-03-21 16:34 | 2016-03-21 16:34 |  | Follow up |  | 66 |  |  | 2016
226402 |  |  | 850 Tumut - Talbingo tee Jounama Dam 66kV Line | N | 2016Q1 | TU2 | TL | 2016-03-21 18:20 |  | Advised that at 18:20hrs 850 Tumut to Talbingo tee Jounama Dam 66kV Essential Energy feeder tripped, auto reclosed, tripped and locked out. 10MW generation into Tumut132 SS interrupted and 2MW load at Talbingo interrupted. 21:55 hrs All Essential Customer load at Talbingo restored via SHL Reactor supply from T3PS, with 850 Talbingo tee Jounama Dam line out of service. | Follow up |  | 66 |  |  | 2016
226434 | LV/MECH Fail | CB | No.2 Reactor | E | 2016Q1 | WL1 | RX | 2016-03-23 07:43 | 2016-03-23 10:18 |  |  | Less than 24hrs notice Investigate Spring charge failure in Mech Box. | 330 | Tim Barnes to follow up. [9/5/2016] Work Order 382243. Still open. [8/6/2016] Power switch replaced. | Forced | 2016
226618 | HV Equipment | CB | 330kV B Bus 1-2 Section CB 5112 | N | 2016Q1 | SE1 | CB | 2016-03-23 16:07 | 2016-03-23 18:29 |  |  | SF6 Top-up. | 330 |  |  | 2016
226619 |  |  | 863 Canowindra 66kV CB 8632 | N | 2016Q1 | CW2 | CB | 2016-03-23 18:01 | 2016-03-23 18:01 |  | Follow up |  | 66 |  |  | 2016
226708 |  |  | 841 Yanco - Narrandera 66kV Line | N | 2016Q1 | YA2 | TL | 2016-03-25 17:31 | 2016-03-25 23:11 | Combined protection schemes for No.4 Transformer and 841 Narrandera 66kV feeder. | Follow up |  | 66 |  |  | 2016
226709 |  |  | No.4 Transformer 66/33/11kV | N | 2016Q1 | YA2 | TX | 2016-03-25 17:31 | 2016-03-25 23:11 |  |  |  | 66 |  |  | 2016
226933 | HV Equipment | TX | No.1 Transformer 330/132/11kV | E | 2016Q1 | SYN | TX | 2016-03-30 18:20 | 2016-03-31 16:09 |  |  | Tx needs to be taken OOS due to loud Corona like sounds coming from 330kV bushings. Tx was only energised today after long outage to carry out refurbishment of Tx | 330 | Substations Asset Manager to followup. This was due to arcing horn on bushing. Not required. Removed and problem resolved. | Forced | 2016
226936 | Unknown/Other | Other | 96M Narrabri - Moree 132kV TL | N | 2016Q1 | MRE, NB2 | TL | 2016-03-31 05:48 | 2016-03-31 05:48 | No storms in the area on Indji. | 13/04/2016 09:35:00 ¦ Follow up ¦ Structures 230-280 have been noted for the next routine aerial patrol. | Successful TAR | 132 |  |  | 2016
226985 | HV Equipment | CB | No.2 Transformer 132kV B CB 4422B | N | 2016Q1 | SE1 | CB | 2016-03-31 14:44 | 2016-03-31 16:11 |  |  | SF6 top up | 132 |  |  | 2016
227139 | HV Equipment | CB | No.2 Static Var Compensator | E | 2016Q2 | KCR | SVC | 2016-04-03 04:23 | 2016-04-03 06:03 |  | Follow up | SF6 top up | 330 |  | Forced | 2016
227150 | Animal/Bird | Other | 33kV Bus No.2 Section | N | 2016Q2 | YA2 | BB | 2016-04-03 18:15 | 2016-04-03 21:33 | SCADA trend shows 1.4MW load loss on 7L5 Murrami 33kV Feeder and 2.4 MW load loss on 7L6 Whitton 33kV Feeder. Full load restored by Essential Energy via 7L3 Kamarah and 7L4 Leeton 33kV Feeders at 2023 hours | Follow up | Dead bird found next to bus section VT disconn | 33 | [9/5/2016] Tony Gray: being followed up. W/O to be established. [20/06/2016] Robert Li advised can be closed. |  | 2016
227151 |  |  | No.2 Transformer 132/33/11kV | Z | 2016Q2 | YA2 | TX | 2016-04-03 18:15 | 2016-04-03 21:33 |  |  |  | 132 |  | Fault | 2016
227152 |  |  | 33kV Bus Section 1-2 CB 2102 | N | 2016Q2 | YA2 | CB | 2016-04-03 18:15 | 2016-04-03 21:33 |  |  |  | 33 |  |  | 2016
227153 |  |  | No.2 Capacitor | N | 2016Q2 | YA2 | CAP | 2016-04-03 18:15 | 2016-04-03 21:33 |  |  |  | 33 |  |  | 2016
227154 |  |  | No.5 Yanco - Whitton (No.5 Council) 33kV Line | N | 2016Q2 | YA2 | TL | 2016-04-03 18:15 | 2016-04-03 21:33 |  |  |  | 33 |  |  | 2016
227155 |  |  | No.7 Yanco - Murrami (No.7 Council) 33kV Line | N | 2016Q2 | YA2 | TL | 2016-04-03 18:15 | 2016-04-03 21:33 |  |  |  | 33 |  |  | 2016
227451 | HV Equipment | Cap | No.2 Capacitor | Z | 2016Q2 | PKS | CAP | 2016-04-06 20:03 | 2016-04-07 15:12 |  | Follow up | Tripped on Neutral unbalance | 66 |  | Fault | 2016
227846 | HV Equipment | CB | No.2 Transformer 132kV B CB 4422B | N | 2016Q2 | SE1 | CB | 2016-04-08 13:43 | 2016-04-08 16:03 |  |  | Received CB abnormal alarm at Sydney East 330kV Substation. Advised low gas on No.2 Transformer 132kV B CB 4422B. | 132 |  |  | 2016
227871 | Lightning/Storm | TL | 8C Armidale - Dumaresq 330kV TL | N | 2016Q2 | AR1, DMQ | TL | 2016-04-10 13:24 | 2016-04-10 13:24 | Single Pole (White Phase) trip and auto reclose. CB Operations confirmed from Site HMIs DTF from AR1 Fault Recorder 72.1km | Follow up | Single Pole (White Phase) trip and auto reclose | 330 |  |  | 2016
227872 |  |  | No.4 330kV Reactor | N | 2016Q2 | AR1 | RX | 2016-04-10 13:24 | 2016-04-10 13:24 |  |  |  | 330 |  |  | 2016
227873 |  |  | No.2 Reactor | N | 2016Q2 | DMQ | RX | 2016-04-10 13:24 | 2016-04-10 13:24 |  |  |  | 330 |  |  | 2016
227874 | Lightning/Storm | TL | 7R5 Kempsey - North St 33kV Line | N | 2016Q2 | KS2 | TL | 2016-04-10 15:29 | 2016-04-10 15:29 |  | Follow up | TAR | 33 |  |  | 2016
227875 | Lightning/Storm | TL | 7R2 Kempsey - North St tee Smithtown 33kV Line | N | 2016Q2 | KS2 | TL | 2016-04-10 15:44 | 2016-04-10 15:44 |  | Follow up | TAR | 33 |  |  | 2016
227876 | Lightning/Storm | TL | 879 Narrabri - Wee Waa 66kV Line | N | 2016Q2 | NB2 | TL | 2016-04-10 16:02 | 2016-04-10 16:02 |  | Follow up |  | 66 |  |  | 2016
227877 | Lightning/Storm | TL | 879 Narrabri - Wee Waa 66kV Line | N | 2016Q2 | NB2 | TL | 2016-04-10 16:05 | 2016-04-10 16:05 |  | Follow up | TAR | 66 |  |  | 2016
227878 | Lightning/Storm | TL | 88K Gunnedah - Gunnedah 66 66kV Line | N | 2016Q2 | GN2 | TL | 2016-04-10 18:07 | 2016-04-10 18:07 |  | Follow up | TAR | 66 |  |  | 2016
227879 | Lightning/Storm | TL | 870 Tamworth 132 - Kootingal 66kV Line | N | 2016Q2 | TMW | TL | 2016-04-10 19:07 | 2016-04-10 19:07 |  | Follow up | TAR | 66 |  |  | 2016
228617 | Unknown/Other | TL | 94X Wallerawang 132 - Panorama 132kV TL | N | 2016Q2 | PMA, WWS | TL | 2016-04-15 03:50 | 2016-04-15 03:50 |  | Follow up | TAR | 132 |  |  | 2016
228678 | Animal/Bird | Bus | 33kV Bus No.3 Section | N | 2016Q2 | GRF | BB | 2016-04-15 14:45 | 2016-04-15 15:03 | Confirmed caused by Bird Strike. White Phase fault on both protections Latching M/T both protections | Follow up | Confirmed caused by Bird Strike. White Phase fault on both protections Latching M/T both protections | 33 | [9/5/2016] Tony Gray: being followed up. Can be closed. Wos established to confirm no rod gaps/remove. |  | 2016
228679 |  |  | No.3 Bus VT | N | 2016Q2 | GRF | VT | 2016-04-15 14:45 | 2016-04-15 15:03 |  |  |  | 33 |  |  | 2016
228680 |  |  | 2X1 Spare CB 2X12 | N | 2016Q2 | GRF | CB | 2016-04-15 14:45 | 2016-04-15 15:03 |  |  |  | 33 |  |  | 2016
228681 |  |  | 2X0 Spare CB 2X02 | N | 2016Q2 | GRF | CB | 2016-04-15 14:45 | 2016-04-15 15:03 |  |  |  | 33 |  |  | 2016
228682 |  |  | No.3 Transformer 132/33/11kV | Z | 2016Q2 | GRF | TX | 2016-04-15 14:45 | 2016-04-15 15:03 |  |  |  | 132 |  | Fault | 2016
228683 |  |  | 33kV Bus Section 2-3 CB 2112 | N | 2016Q2 | GRF | CB | 2016-04-15 14:45 | 2016-04-15 15:03 |  |  |  | 33 |  |  | 2016
228684 |  |  | 79U Griffith - Griffith Zone Duty 33kV Line | N | 2016Q2 | GRF | TL | 2016-04-15 14:45 | 2016-04-15 15:03 |  |  |  | 33 |  |  | 2016
228789 |  |  | 81L Panorama - Raglan 66kV Line | N | 2016Q2 | PMA | TL | 2016-04-16 11:27 | 2016-04-16 16:53 | Essential Energy Operator request 81L Raglan de-energised for urgent repairs | Follow up |  | 66 |  |  | 2016
228799 |  |  | 79P Griffith - Goolgowi 33kV Line | N | 2016Q2 | GRF | TL | 2016-04-17 15:48 | 2016-04-17 15:48 | No Known storms in area | Follow up |  | 33 |  |  | 2016
228993 | Staff Error | CT | 85 Tamworth 330 - Armidale 330kV TL | E | 2016Q2 | AR1, TA1 | TL | 2016-04-19 13:45 | 2016-04-19 19:57 |  |  | 330kV CT has had a Capacitance change of >8%. Retesting did not confirm this > 8% change. | 330 | [9 May 2016] Tony Gray following up with Field Services. | Forced | 2016
229010 |  |  | 96Z Newcastle - Maryland 132kV Line | N | 2016Q2 | NEW | TL | 2016-04-19 12:38 | 2016-04-19 15:13 | SO/Ausgrid request deenengise 96Z T/L, undercrossed 11kV line (O/S), has sustained some damage whilst trying to stand a new pole, work crew able to remove pole without further outage of 96Z. | Follow up |  | 132 |  |  | 2016
229438 | HV Equipment | CB | No.2 Transformer 132kV B CB 4422B | N | 2016Q2 | SE1 | CB | 2016-04-20 11:42 | 2016-04-20 15:15 |  |  | HMI indicates low SF6 on CB4422B. SF6 topped up | 132 |  |  | 2016
229475 | Unknown/Other | TL | 97K Cooma (New) - Munyang tee Snowy Adit 132kV TL | N | 2016Q2 | MNY, COA | TL | 2016-04-20 15:39 | 2016-04-20 15:39 |  | Follow up | TAR | 132 |  |  | 2016
229537 |  |  | Broken Hill - Talc St 2 22kV line | N | 2016Q2 | BKH | TL | 2016-04-21 12:35 | 2016-04-21 12:35 |  | Follow up |  | 22 |  |  | 2016
229842 |  |  | 661 Armidale - Oaky PS 66kV Line | N | 2016Q2 | AR1 | TL | 2016-04-22 23:22 | 2016-04-22 23:22 |  | Follow up | TAR Customer Line | 66 |  |  | 2016
230148 |  |  | 79F Griffith - Yenda 33kV Line | N | 2016Q2 | GRF | TL | 2016-04-25 16:02 | 2016-04-25 16:02 |  | Follow up | TAR Customer Line | 33 |  |  | 2016
230408 | Secondary Equipment | SVC | No.1 Static VAR Compensator | E | 2016Q2 | AR1 | SVC | 2016-04-27 17:00 | 2016-04-27 20:06 | When No.1 svc was returned to service it's MVAr output went to 330MVAr export and Arimdale bus voltage went to 363kV for reasons unknown (V setpoint was 346kV) SVC stopped immediately. Following investigations by TransGrid and ABB staff, the SVC Control System and SCADA Gateway Server were rebooted and the SVC was returned to service at 2006 hours. | Follow up | When No.1 svc was returned to service it's MVAr output went to 330MVAr export and Arimdale bus voltage went to 363kV for reasons unknown (V setpoint was 346kV) SVC stopped immediately. Following investigations by TransGrid and ABB staff, the SVC Control System and SCADA Gateway Server were rebooted and the SVC was returned to service at 2006 hours. | 330 | [9/5/2016] Close. | Forced | 2016
230446 | Switching error | Proc | 28 Sydney North A CB 282A | N | 2016Q2 | SE1 | CB | 2016-04-28 11:13 | 2016-04-28 11:16 |  |  | Operating Error | 330 |  |  | 2016
230918 |  |  | 841 Yanco - Narrandera 66kV Line | N | 2016Q2 | YA2 | TL | 2016-04-29 06:27 | 2016-04-29 11:15 | Patrol carried out by Essential Energy Staff. No issues found | Follow up | Patrol carried out by Essential Energy Staff. No issues found | 66 |  |  | 2016
230919 |  |  | No.4 Transformer 66/33/11kV | N | 2016Q2 | YA2 | TX | 2016-04-29 06:27 | 2016-04-29 11:15 |  |  | Brad Ashton (EsE) advises of visible black marking on top of reactor. Byron Mills advised. Info update RX still out of service. | 66 |  |  | 2016
231096 |  |  | 261 Beaconsfield West - Clovelly tee Zetland 132kV Cable | N | 2016Q2 | BFD | TL | 2016-04-30 13:25 | 2016-05-05 23:30 | cable failed when energised on RTS switching on HVPRI 65302 there was no load affected as cable was still ISOLATED in the customer system. | Follow up | cable failed when energised on RTS switching on HVPRI 65302 there was no load affected as cable was still ISOLATED in the customer system. | 132 |  |  | 2016
231097 | Lightning/Storm | TL | 63 Wagga - Darlington Point 330kV TL | N | 2016Q2 | DNT, WG1 | TL | 2016-05-01 01:42 | 2016-05-01 01:42 | At 01:42hrs 63 Wagga to Darlington Point 330 kV T/L tripped and reclosed operating the X5 tripping scheme. CBs 7442, 7432 and X52 opened. No.4 and No.3 Transformer RTS at 01:46hrs. X5 closed at 01:46hrs. No load lost. Update - WG1 Prot details added - AMC - Richard Archer | 2/05/2016 13:42:00 ¦ Follow up ¦ The area around structure 322 has been noted for the next routine inspection. | 63 Wagga to Darlington Point 330 kV T/L tripped and reclosed operating the X5 tripping scheme. CBs 7442, 7432 and X52 opened. No.4 and No.3 Transformer RTS at 01:46hrs. X5 closed at 01:46hrs. A lightning strike was identified at the time of the trip near structure 322. | 330 |  |  | 2016
231245 | HV Equipment | Rx | No.2 Reactor | E | 2016Q2 | DMQ | RX | 2016-05-03 10:31 | 2016-05-03 15:19 |  |  | Oil level Alarm Type fault investigate and repair, less than 24 hours notice. | 330 | Alarm not useful, disabled. | Forced | 2016
231270 | Switching error | Proc | Unit 12 Uranquinty PS CB 42B2 | N | 2016Q2 | URQ | CB | 2016-05-03 08:50 |  | Runback stage 2 operated when 9R22 at WG1 was opened under HVPRI after opening the runback bypass links. | Follow up | Runback stage 2 operated when 9R22 at WG1 was opened under HVPRI after opening the runback bypass links. Loss of 150MW of generation. | 132 | OM instruction or design issue. Tim Barnes advised can be closed. |  | 2016
231369 | HV Equipment | CB | 330kV B Bus 1-2 Section CB 5112 | N | 2016Q2 | SE1 | CB | 2016-05-03 16:44 | 2016-05-03 18:37 |  |  | SF6 top-up | 330 |  |  | 2016
231491 | HV Equipment | Rx | No.3 Reactor | E | 2016Q2 | DMQ | RX | 2016-05-05 10:18 | 2016-05-05 14:30 |  |  | Oil level Alarm Type fault investigate and repair, less than 24 hours notice. | 330 | Alarm not useful, disabled. | Forced | 2016
231707 | HV Equipment | CB | No.2 Transformer 132kV B CB 4422B | N | 2016Q2 | SE1 | CB | 2016-05-05 13:26 | 2016-05-05 15:50 |  |  | SF6 top-up | 132 |  |  | 2016
231722 |  |  | No.3 330kV Generator Transformer Group | N | 2016Q2 | LD1 | TX | 2016-05-06 00:27 | 2016-05-23 16:04 | AGL advised No.3 Unit tripped when Transformer differential protection had operated. It was reported that No.3 Generator transformer had asurge in oil level. | Follow up |  | 330 |  |  | 2016
231758 |  |  | No.1 Transformer 132/11kV | N | 2016Q2 | GTH | TX | 2016-05-06 09:09 | 2016-05-06 20:06 |  |  |  | 132 |  |  | 2016
232942 | HV Equipment | CB | 11 Dapto - Sydney South 330kV TL | E | 2016Q2 | DPT, SYS | TL | 2016-05-07 12:30 | 2016-05-07 13:39 |  |  | SF6 Top-up | 330 |  | Forced | 2016
232962 |  |  | No.3 330kV Generator Transformer Group | N | 2016Q2 | LD1 | TX | 2016-05-08 13:05 | 2016-05-08 17:57 |  |  |  | 330 |  |  | 2016
232963 |  |  | 79L Griffith - Beelbangera 33kV Line | N | 2016Q2 | GRF | TL | 2016-05-08 12:17 | 2016-05-08 12:17 |  | Follow up |  | 33 |  |  | 2016
233069 | Unknown/Other | TL | 96M Narrabri - Moree 132kV TL | N | 2016Q2 | MRE, NB2 | TL | 2016-05-09 21:47 | 2016-05-09 21:47 | Indji weather monitor didn't indicate any adverse weather conditions at the time. | Follow up | Successful TAR | 132 |  |  | 2016
233097 |  |  | No.2 Wagga 132 - Forest Hill 66kV Line | N | 2016Q2 | WG2 | TL | 2016-05-10 11:30 | 2016-05-10 13:08 |  |  |  | 66 |  |  | 2016
233267 |  |  | No.6 Orange - Orange North 66kV Line | N | 2016Q2 | ORG | TL | 2016-05-11 05:06 | 2016-05-13 09:30 | Low oil level on Essential Energy No.6 TX Cold temperatures overnight. | Follow up |  | 66 |  |  | 2016
233513 | HV Equipment | CB | No.2 Transformer 132/66/11kV | E | 2016Q2 | KLK | TX | 2016-05-12 06:03 | 2016-05-12 07:55 |  |  | SF6 Top-up | 132 |  | Forced | 2016
233577 |  |  | 381 Essential Energy FREQ INJ 66kV Line | N | 2016Q2 | BER | TL | 2016-05-12 12:52 | 2016-05-13 16:56 | White phase VT has failed. White phase VT replaced and placed back into service | Follow up |  | 66 |  |  | 2016
252485 | HV Equipment | CB | No.1 Transformer 132/66/11kV | E | 2016Q2 | NB2 | TX | 2016-05-13 08:46 | 2016-05-13 09:43 |  |  | Top up SF6 Circuit Breaker 4412 | 132 |  | Forced | 2016
253146 | HV Equipment | CB | No.3 Transformer 132/66/11kV | E | 2016Q2 | NB2 | TX | 2016-05-13 09:56 | 2016-05-13 10:34 |  |  | Top up SF6 Circuit Breaker 3432 | 132 |  | Forced | 2016
254365 | HV Equipment | CB | No.2 Static Var Compensator | E | 2016Q2 | KCR | SVC | 2016-05-13 19:46 | 2016-05-13 20:59 |  |  | Top-up SF6 CB5V22 | 330 |  | Forced | 2016
254382 |  |  | 93X Sydney West - Nepean tee Bringelly 132kV Line | N | 2016Q2 | SYW | TL | 2016-05-14 16:03 | 2016-05-14 16:03 |  | Follow up |  | 132 |  |  | 2016
254526 |  |  | 712 Port Macquarie - Rocks Ferry 33kV Line | N | 2016Q2 | PMQ | TL | 2016-05-16 22:34 | 2016-05-17 03:06 | Requested by Essential Energy to de-energise the feeder due to reports of a pole top fire. | Follow up |  | 33 |  |  | 2016
254527 | HV Equipment | CB | No.1 Transformer 220/22kV | Z | 2016Q2 | BKH | TX | 2016-05-16 18:35 | 2016-05-27 13:12 | Trip initiated from 220kV BBP as a consequence of a failure of No.1 Transformer 220kV C.B.. 7412. Refer to FEOR 2016-F-0173 for the 220kV BBP trip. No.1 Transformer isolated off system to allow 220kV Bus to be returned to service. No.1 Transformer 220kV C.B. 7412 open at time of trip. | Follow up | Trip initiated from 220kV BBP as a consequence of a failure of No.1 Transformer 220kV C.B.. 7412. Refer to FEOR 2016-F-0173 for the 220kV BBP trip. No.1 Transformer isolated off system to allow 220kV Bus to be returned to service. No.1 Transformer 220kV C.B. 7412 open at time of trip. | 220 | Report pending from Tim Barnes | Fault | 2016
254528 | HV Equipment | SD | 220kV Bus | N | 2016Q2 | BKH | BB | 2016-05-16 18:35 |  | Trip occurred due suspected failure of No.1 Transformer 220kV C.B.. 7412. Refer to FEOR 2016-F-0172 (No.1 Transformer). Broken Hill 22kV load being supplied from No.1 and No.2 Gas Turbines at time of trip. | Follow up | Trip occurred due suspected failure of No.1 Transformer 220kV C.B.. 7412. Refer to FEOR 2016-F-0172 (No.1 Transformer). Broken Hill 22kV load being supplied from No.1 and No.2 Gas Turbines at time of trip. 1835:32 - Abnormal SCADA voltage indications continue with excursions up to 270kV. X292 opened at Buronga by Operator to de-energise X2 Reactor, which may have contributed to significant switching overvoltage, leading to failure of both the Rphase pole of 7412 and the Bphase surge arrestor on the #1 Reactor. Abnormal status indications received from 7412 due to failure, as BKH 220kV Busbar protection operates. Both transformers tripped via 2412 and 2422 (no Aux supply to Sub, town load still on GT’s). Bphase surge arrestor failure not yet detected onsite | 220 | Report pending from Tim Barnes |  | 2016
254529 | HV Equipment | CB | No.1 Transformer 220/22kV | N | 2016Q2 | BKH | TX | 2016-05-16 18:35 |  |  |  | Trip initiated from 220kV BBP as a consequence of a failure of No.1 Transformer 220kV C.B.. 7412. Refer to FEOR 2016-F-0173 for the 220kV BBP trip. No.1 Transformer isolated off system to allow 220kV Bus to be returned to service. No.1 Transformer 220kV C.B. 7412 open at time of trip. | 220 | Report pending from Tim Barnes |  | 2016
254530 | HV Equipment | CB | No.2 Transformer 220/22kV | Z | 2016Q2 | BKH | TX | 2016-05-16 18:35 |  |  |  | Trip initiated from 220kV BBP as a consequence of a failure of No.1 Transformer 220kV C.B.. 7412. Refer to FEOR 2016-F-0173 for the 220kV BBP trip. No.1 Transformer isolated off system to allow 220kV Bus to be returned to service. No.1 Transformer 220kV C.B. 7412 open at time of trip. | 220 | Report pending from Tim Barnes | Fault | 2016
254531 | HV Equipment | CB | X2 Buronga - Broken Hill 220kV TL | Z | 2016Q2 | BKH, BRG | TL | 2016-05-16 18:35 |  |  |  | Attempted to return to service X2 Buronga to Broken Hill T/L at Buronga following earlier trip (refer to FEOR 2016-F-0174). No.1 Transfomer isolated off system at Broken Hill. Line tripped on closing with Temporary Protections indicating a Blue Phase Fault. Inspection at Broken Hill found failure of No.1 Reactor Blue Phase Surge Arrestor. No.1 Reactor isolated off system at Broken Hill and X2 Buronga to Broken Hill T/L returned to service at 2230 hours. Temporary Protections installed at Buronga following replacement of Line C.V.T. and were in service to allow Directional Checks to be carried out. | 220 | Report pending from Tim Barnes | Fault | 2016
254532 | HV Equipment | SD | X4 Broken Hill - Broken Hill Mine 220kV Line | N | 2016Q2 | BKH | TL | 2016-05-16 18:35 |  |  |  | Attempted to return to service X2 Buronga to Broken Hill T/L at Buronga following earlier trip (refer to FEOR 2016-F-0174). No.1 Transfomer isolated off system at Broken Hill. Line tripped on closing with Temporary Protections indicating a Blue Phase Fault. Inspection at Broken Hill found failure of No.1 Reactor Blue Phase Surge Arrestor. No.1 Reactor isolated off system at Broken Hill and X2 Buronga to Broken Hill T/L returned to service at 2230 hours. Temporary Protections installed at Buronga following replacement of Line C.V.T. and were in service to allow Directional Checks to be carried out. | 220 | Report pending from Tim Barnes |  | 2016
254533 | HV Equipment | CB | X2 Buronga - Broken Hill 220kV TL | Z | 2016Q2 | BKH, BRG | TL | 2016-05-16 17:59 |  | X2 Energised at Buronga @ 1744 hours and 220kV Bus energised at Broken Hill. X4 Broken Hill Mines C.B. X42 closed at Broken Hill @ 1756 hours. C.B.. X22 tripped at Buronga @ 1759 hours. At time of trip, X2 Buronga to Broken Hill T/L was being returned to service following field work and the replacement of the C.V.T. at Buronga. Failure of No.1 Transformer 220kV C.B.. 7412 suspected cause of trip. Temporary Protections installed at Buronga following replacement of Line C.V.T. and were in service to allow Directional Checks to be carried out. Refer to FEOR 2016-F-0172 (No.1 Transformer) and FEOR 2016-F-0173 (BKH 220kV Bus). | Follow up | X2 Energised at Buronga @ 1744 hours and 220kV Bus energised at Broken Hill. X4 Broken Hill Mines C.B. X42 closed at Broken Hill @ 1756 hours. C.B.. X22 tripped at Buronga @ 1759 hours. At time of trip, X2 Buronga to Broken Hill T/L was being returned to service following field work and the replacement of the C.V.T. at Buronga. Failure of No.1 Transformer 220kV C.B.. 7412 suspected cause of trip. Temporary Protections installed at Buronga following replacement of Line C.V.T. and were in service to allow Directional Checks to be carried out. Refer to FEOR 2016-F-0172 (No.1 Transformer) and FEOR 2016-F-0173 (BKH 220kV Bus). X2 trips at Buronga via CBX22. CBX42 at BKH still closed and 220kV Bus at Broken Hill shows volts fluctuating between 115 to 172kV. With no other source of 220kV supply, it is possible that a single phase of 7412 or 7422 did not open and has been feeding single phase volts (not synchronised to the system) via the TX onto the BKH Bus. Varying voltage levels appear on SCADA via the 220kV Bus VT associated with the X4 circuit. #1 Reactor is also partially energised with this single phase supply, with varying level of volts appearing on the other two phases through mutual induction/transformer action of the Reactor. The circuit remains energised with an increasing voltage difference between the GT supplied single phase voltage and the 220kV system supply (due to non-synchronicity). | 220 | Report pending from Tim Barnes | Fault | 2016
254534 | HV Equipment | CB | X2 Buronga No.1 Reactor | N | 2016Q2 | BKH | RX | 2016-05-16 17:59 |  |  |  | 17:59hrs – X2 trips at Buronga via CBX22. CBX42 still closed and 220kV Bus at Broken Hill shows volts fluctuating between 115 to 172kV. With no other source of 220kV supply, it is possible that a single phase of 7412 or 7422 did not open and has been feeding single phase volts (not synchronised to the system) via the TX onto the BKH Bus. Varying voltage levels appear on SCADA via the 220kV Bus VT associated with the X4 circuit. #1 Reactor is also partially energised with this single phase supply, with varying level of volts appearing on the other two phases through mutual induction/transformer action of the Reactor. The circuit remains energised with an increasing voltage difference between the GT supplied single phase voltage and the 220kV system supply (due to non-synchronicity). | 220 | Report pending from Tim Barnes |  | 2016
254535 | HV Equipment | CB | X2 Buronga No.2 Reactor | N | 2016Q2 | BKH | RX | 2016-05-16 17:59 |  |  |  | 17:59hrs – X2 trips at Buronga via CBX22. CBX42 still closed and 220kV Bus at Broken Hill shows volts fluctuating between 115 to 172kV. With no other source of 220kV supply, it is possible that a single phase of 7412 or 7422 did not open and has been feeding single phase volts (not synchronised to the system) via the TX onto the BKH Bus. Varying voltage levels appear on SCADA via the 220kV Bus VT associated with the X4 circuit. #1 Reactor is also partially energised with this single phase supply, with varying level of volts appearing on the other two phases through mutual induction/transformer action of the Reactor. The circuit remains energised with an increasing voltage difference between the GT supplied single phase voltage and the 220kV system supply (due to non-synchronicity). | 220 | Report pending from Tim Barnes |  | 2016
254536 | HV Equipment | CB | X2 Reactor | N | 2016Q2 | BRG | RX | 2016-05-16 17:59 |  |  |  | 17:59hrs – X2 trips at Buronga via CBX22. CBX42 still closed and 220kV Bus at Broken Hill shows volts fluctuating between 115 to 172kV. With no other source of 220kV supply, it is possible that a single phase of 7412 or 7422 did not open and has been feeding single phase volts (not synchronised to the system) via the TX onto the BKH Bus. Varying voltage levels appear on SCADA via the 220kV Bus VT associated with the X4 circuit. #1 Reactor is also partially energised with this single phase supply, with varying level of volts appearing on the other two phases through mutual induction/transformer action of the Reactor. The circuit remains energised with an increasing voltage difference between the GT supplied single phase voltage and the 220kV system supply (due to non-synchronicity). | 220 | Report pending from Tim Barnes |  | 2016
254537 | HV Equipment | SD | X2 Buronga - Broken Hill 220kV TL | Z | 2016Q2 | BKH, BRG | TL | 2016-05-16 19:47 |  | Attempted to return to service X2 Buronga to Broken Hill T/L at Buronga following earlier trip (refer to FEOR 2016-F-0174). No.1 Transfomer isolated off system at Broken Hill. Line tripped on closing with Temporary Protections indicating a Blue Phase Fault. Inspection at Broken Hill found failure of No.1 Reactor Blue Phase Surge Arrestor. No.1 Reactor isolated off system at Broken Hill and X2 Buronga to Broken Hill T/L returned to service at 2230 hours. Temporary Protections installed at Buronga following replacement of Line C.V.T. and were in service to allow Directional Checks to be carried out. | Follow up | Attempted to return to service X2 Buronga to Broken Hill T/L at Buronga following earlier trip (refer to FEOR 2016-F-0174). No.1 Transfomer isolated off system at Broken Hill. Line tripped on closing with Temporary Protections indicating a Blue Phase Fault. Inspection at Broken Hill found failure of No.1 Reactor Blue Phase Surge Arrestor. No.1 Reactor isolated off system at Broken Hill and X2 Buronga to Broken Hill T/L returned to service at 2230 hours. Temporary Protections installed at Buronga following replacement of Line C.V.T. and were in service to allow Directional Checks to be carried out. | 220 | Report pending from Tim Barnes | Fault | 2016
254538 | HV Equipment | SD | X2 Buronga No.1 Reactor | Z | 2016Q2 | BKH | RX | 2016-05-16 19:47 |  |  |  | Attempted to return to service X2 Buronga to Broken Hill T/L at Buronga following earlier trip (refer to FEOR 2016-F-0174). No.1 Transfomer isolated off system at Broken Hill. Line tripped on closing with Temporary Protections indicating a Blue Phase Fault. Inspection at Broken Hill found failure of No.1 Reactor Blue Phase Surge Arrestor. No.1 Reactor isolated off system at Broken Hill and X2 Buronga to Broken Hill T/L returned to service at 2230 hours. Temporary Protections installed at Buronga following replacement of Line C.V.T. and were in service to allow Directional Checks to be carried out. | 220 | Report pending from Tim Barnes | Fault | 2016
254539 | HV Equipment | SD | X2 Buronga No.2 Reactor | N | 2016Q2 | BKH | RX | 2016-05-16 19:47 |  |  |  | Attempted to return to service X2 Buronga to Broken Hill T/L at Buronga following earlier trip (refer to FEOR 2016-F-0174). No.1 Transfomer isolated off system at Broken Hill. Line tripped on closing with Temporary Protections indicating a Blue Phase Fault. Inspection at Broken Hill found failure of No.1 Reactor Blue Phase Surge Arrestor. No.1 Reactor isolated off system at Broken Hill and X2 Buronga to Broken Hill T/L returned to service at 2230 hours. Temporary Protections installed at Buronga following replacement of Line C.V.T. and were in service to allow Directional Checks to be carried out. | 220 | Report pending from Tim Barnes |  | 2016
254540 | HV Equipment | SD | X2 Reactor | N | 2016Q2 | BRG | RX | 2016-05-16 19:47 |  |  |  | Attempted to return to service X2 Buronga to Broken Hill T/L at Buronga following earlier trip (refer to FEOR 2016-F-0174). No.1 Transfomer isolated off system at Broken Hill. Line tripped on closing with Temporary Protections indicating a Blue Phase Fault. Inspection at Broken Hill found failure of No.1 Reactor Blue Phase Surge Arrestor. No.1 Reactor isolated off system at Broken Hill and X2 Buronga to Broken Hill T/L returned to service at 2230 hours. Temporary Protections installed at Buronga following replacement of Line C.V.T. and were in service to allow Directional Checks to be carried out. | 220 | Report pending from Tim Barnes |  | 2016
254541 | HV Equipment | SD | X2 Buronga No.1 Reactor | N | 2016Q2 | BKH | RX | 2016-05-16 19:47 |  | Attempted to return to service X2 Buronga to Broken Hill T/L at Buronga following earlier trip (refer to FEOR 2016-F-0174). No.1 Transfomer isolated off system at Broken Hill. Line tripped on closing with Temporary Protections indicating a Blue Phase Fault. Inspection at Broken Hill found failure of No.1 Reactor Blue Phase Surge Arrestor. No.1 Reactor isolated off system at Broken Hill and X2 Buronga to Broken Hill T/L returned to service at 2230 hours. Temporary Protections installed at Buronga following replacement of Line C.V.T. and were in service to allow Directional Checks to be carried out. Refer to FEOR 2016-F-0175 (X2 Buronga to Broken Hill T/L) | Follow up | Attempted to return to service X2 Buronga to Broken Hill T/L at Buronga following earlier trip (refer to FEOR 2016-F-0174). No.1 Transfomer isolated off system at Broken Hill. Line tripped on closing with Temporary Protections indicating a Blue Phase Fault. Inspection at Broken Hill found failure of No.1 Reactor Blue Phase Surge Arrestor. No.1 Reactor isolated off system at Broken Hill and X2 Buronga to Broken Hill T/L returned to service at 2230 hours. Temporary Protections installed at Buronga following replacement of Line C.V.T. and were in service to allow Directional Checks to be carried out. Refer to FEOR 2016-F-0175 (X2 Buronga to Broken Hill T/L) | 220 | Report pending from Tim Barnes |  | 2016
254550 |  |  | 94C Wallerawang 132 - Oberon 132kV Line | N | 2016Q2 | WWS | TL | 2016-05-17 07:53 | 2016-05-17 07:53 | Distance to fault - 57.23km | Follow up |  | 132 |  |  | 2016
254766 | HV Equipment | Disc | 22 Sydney North 330kV Main Bus CB 222M | N | 2016Q2 | VP1 | CB | 2016-05-18 17:12 | 2016-07-30 14:43 |  |  | Isolator 225 defective. Turntable on centre pole has corroded and forced the contacts out of alignment. The isolator could not be closed and CB isolated to allow repairs | 330 | Tim Barnes investigating [20/07/2016] Tim Barnes advised can be closed |  | 2016
254773 |  |  | 711 Port Macquarie - Clearwater Crescent 33kV Line | N | 2016Q2 | PMQ | TL | 2016-05-18 22:13 | 2016-05-18 22:13 | Distance to fault 5.5km | Follow up |  | 33 |  |  | 2016
254894 |  |  | No.1 330kV Generator Transformer Group | N | 2016Q2 | LD1 | TX | 2016-05-20 21:50 | 2016-05-31 07:21 | Unit 1 tripped at Liddell Power Station and CBs 5212, 5012 and Line Disconnector opened. Power Station staff investigating the cause. | Follow up |  | 330 |  |  | 2016
254998 | Damaged Cable | Other | No.2 Transformer 132/66/11kV | E | 2016Q2 | FNY | TX | 2016-05-23 15:14 | 2016-05-23 17:13 |  |  | Numerous fleeting No2 Tx 66kV Limit High alarms. Nil Tap Change operations. When inspectiog No2 Tx VT secondary box noticed loose wiring. | 132 |  | Forced | 2016
255057 | Relay Faulty | Prot | No.1 Transformer 330/132/11kV | Z | 2016Q2 | TGH | TX | 2016-05-24 09:50 | 2016-05-24 18:27 | The transformer 132kV CB did not trip, no protection operated alarms. T60 relay replaced. | Follow up | Faulty T60 Tx Diff. relay. Relay replaced. | 330 |  | Fault | 2016
255066 |  |  | 853 Macarthur - Ambarvale 66kV Line | N | 2016Q2 | MAC | TL | 2016-05-24 11:25 | 2016-05-24 20:53 |  |  |  | 66 |  |  | 2016
255215 | HV Equipment | Disc | 66kV Bus Section 5 | N | 2016Q2 | NB2 | BB | 2016-05-26 13:58 | 2016-05-26 16:28 |  |  | Hot joint on Disconnector 3118 | 66 |  |  | 2016
255222 | HV Equipment | Rx | X2 Reactor | E | 2016Q2 | BRG | RX | 2016-05-27 09:35 | 2016-05-27 13:01 |  |  | Investigate Rx pressure relief alarm | 220 | Caused by moisture ingress | Forced | 2016
255228 |  |  | 852 Macarthur - Douglas Park 66kV Line | N | 2016Q2 | MAC | TL | 2016-05-26 15:08 | 2016-05-26 18:01 |  |  |  | 66 |  |  | 2016
255238 |  |  | No.3 Transformer 132/66/11kV | E | 2016Q2 | NB2 | TX | 2016-05-26 13:58 | 2016-05-26 16:28 |  |  |  | 132 |  | Forced | 2016
255239 |  |  | 861 Narrabri - Walgett 66kV Line | N | 2016Q2 | NB2 | TL | 2016-05-26 13:58 | 2016-05-26 16:28 |  |  |  | 66 |  |  | 2016
255307 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line | N | 2016Q2 | CW2 | TL | 2016-05-26 16:46 | 2016-05-26 20:43 | Essential Energy advised there are reports of a pole fire | Follow up |  | 66 |  |  | 2016
255428 | HV Equipment | CT | No.2 Static Var Compensator | E | 2016Q2 | KCR | SVC | 2016-05-28 10:03 | 2016-05-28 11:42 |  |  | Low SF6 on No2 SVC 330kV CB 5V22 CTs. | 330 |  | Forced | 2016
255430 | HV Equipment | CB | 79G Griffith - Griffith West 33kV Line | N | 2016Q2 | GRF | TL | 2016-06-01 11:20 | 2016-06-01 12:18 |  |  | Low SF6 alarm | 33 |  |  | 2016
255442 | HV Equipment | CB | 330kV B Bus 1-2 Section CB 5112 | N | 2016Q2 | SE1 | CB | 2016-05-29 14:45 | 2016-05-29 15:55 |  |  | Low SF6 330kV B Bus 1-2 Section CB 5112 | 330 |  |  | 2016
255493 |  |  | 97R Cooma (New) - Bega tee Steeple Flat 132kV TL | N | 2016Q2 | CMA, COA | TL | 2016-05-31 06:47 | 2016-05-31 13:23 |  | Follow up |  | 132 |  |  | 2016
255494 |  |  | 97R Bega tee Steeple Flat CB 97R2 | N | 2016Q2 | COA | CB | 2016-05-31 06:47 | 2016-05-31 13:23 |  |  |  | 132 |  |  | 2016
255675 | HV Equipment | CB | 79M Griffith - Hanwood 33kV Line | N | 2016Q2 | GRF | TL | 2016-06-01 05:25 | 2016-06-01 11:31 |  |  | Low SF6 alarm | 33 |  |  | 2016
255704 | RTU/MITS/PLC | Rx | No.1 Reactor | E | 2016Q2 | HYM | RX | 2016-06-02 07:37 | 2016-06-02 16:29 |  |  | Less than 24 hours notice. Test new data base, alarms, controls and indications through to SCADA | 132 |  | Forced | 2016
257269 |  |  | 870 Tamworth 132 - Kootingal 66kV Line | N | 2016Q2 | TMW | TL | 2016-06-01 12:59 | 2016-06-01 12:59 |  | Follow up |  | 66 |  |  | 2016
257332 | HV Equipment | Cap | No.2 Capacitor | Z | 2016Q2 | GN2 | CAP | 2016-06-01 22:18 |  | This Should be No.2 Capacitor. TheOS error wouldn't allow the creation of outage to the correct service. FEOR resent with correct details | Follow up | Tripped on NUB | 66 |  | Fault | 2016
257657 | HV Equipment | CB | No.2 Transformer 132/33/11kV | E | 2016Q2 | GRF | TX | 2016-06-02 21:58 | 2016-06-03 00:27 | Emergency outage on No.2 Transformer as 132kV CB 4422 had leaking SF6 gas at a considerable rate and could have lead to CB Lockout. Staff was on site and advised that Current pressure was 420 KPI and CB would have locked out at 400 KPI. NCM advised. Leak rectified, SF6 gas topped up and No.2 transformer returned to service. | Follow up | Emergency outage on No.2 Transformer as 132kV CB 4422 had leaking SF6 gas at a considerable rate and could have lead to CB Lockout. Staff was on site and advised that Current pressure was 420 KPI and CB would have locked out at 400 KPI. NCM advised. Leak rectified, SF6 gas topped up and No.2 transformer returned to service. | 132 |  | Forced | 2016
257800 | HV Equipment | CB | No.2 Transformer 330/132/11kV | E | 2016Q2 | LSM | TX | 2016-06-03 13:02 | 2016-06-03 13:34 |  |  | SF6 top-up | 330 |  | Forced | 2016
257990 | Pollution | TX | No.2 Transformer 330/132/11kV | E | 2016Q2 | LP1 | TX | 2016-06-05 21:56 | 2016-06-06 10:18 | Condition L1 alarm. AMC unable to login and requested TX de-energised. Clearance from AMC (Sam) to place back in service | Follow up | Condition L1 alarm. AMC unable to login and requested TX de-energised. Clearance from AMC (Sam) to place back in service Alarm caused by pollution on bushings. Work order 00396102 | 330 |  | Forced | 2016
257991 |  |  | 93N Liverpool - West Liverpool 132kV Line | N | 2016Q2 | LP1 | TL | 2016-06-05 21:56 | 2016-06-06 10:18 |  |  |  | 132 |  |  | 2016
257992 |  |  | No.3 Murray - Khancoban Town 11kV Supply 11kV Line | N | 2016Q2 | MUR | TL | 2016-06-05 21:03 | 2016-06-06 08:52 |  | Follow up |  | 11 |  |  | 2016
257993 | Unknown/Other | TL | 96M Narrabri - Moree 132kV TL | N | 2016Q2 | MRE, NB2 | TL | 2016-06-06 04:41 | 2016-06-06 04:41 |  | Follow up | Successful TAR | 132 |  |  | 2016
258135 |  |  | 893/5 Forbes - Payten's Bridge 66kV Line | N | 2016Q2 | FB2 | TL | 2016-06-07 17:03 | 2016-06-07 17:17 |  |  |  | 66 |  |  | 2016
258303 | Wiring/Testing Error | Proc | 132kV Bus Sections 1, 1-2 & 2 | N | 2016Q2 | ALB | BB | 2016-06-08 16:19 | 2016-06-08 18:44 | *Amendment* Load was restored in 2 blocks by Essential Energy. Figures for total MWH re-calculated. 35MW load lost between 1619hrs and 1634hrs, all load restored by 1634hrs. 1631hrs Alubury Load Restored - 19MW for 12 minutes = 3.8MWH 1634 Mulwala/Corowa Load Restored - 16MW for 15 minutes = 4MWH Total = 7.8MWH The wiring error that caused the trip was carried out by the contractors who are installing the SSB. | Follow up | Advised by protection staff on site that the 132kV Bypass protection circuitry was crossed causing mal operation of Bus Bar Protection. | 132 |  |  | 2016
258304 |  |  | 132kV Bus Section 1-2 | N | 2016Q2 | ALB | BB | 2016-06-08 16:19 | 2016-06-08 18:44 |  |  |  | 132 |  |  | 2016
258305 |  |  | 132kV Bus Section 1 | N | 2016Q2 | ALB | BB | 2016-06-08 16:19 | 2016-06-08 18:44 |  |  |  | 132 |  |  | 2016
258306 |  |  | 132kV Bus Section 2 | N | 2016Q2 | ALB | BB | 2016-06-08 16:19 | 2016-06-08 18:44 |  |  |  | 132 |  |  | 2016
258411 |  |  | No.3 Transformer 330/220/33kV | Z | 2016Q2 | DNT | TX | 2016-05-01 01:42 | 2016-05-01 01:42 |  |  |  | 330 |  | Fault | 2016
258412 |  |  | No.4 Transformer 330/220/33kV | Z | 2016Q2 | DNT | TX | 2016-05-01 01:42 | 2016-05-01 01:42 |  |  |  | 330 |  | Fault | 2016
258413 |  |  | X5/1 Darlington Point - Balranald 220kV TL | Z | 2016Q2 | BRD, DNT | TL | 2016-05-01 01:42 | 2016-05-01 01:42 |  |  |  | 220 |  | Fault | 2016
258437 |  |  | 99E Albury - Jelbart 132kV Line | N | 2016Q2 | ALB | TL | 2016-06-08 16:19 | 2016-06-08 18:44 |  |  |  | 132 |  |  | 2016
258438 |  |  | 99B Jindera - Albury 132kV TL | Z | 2016Q2 | ALB, JDA | TL | 2016-06-08 16:19 | 2016-06-08 18:44 |  |  |  | 132 |  | Fault | 2016
258439 |  |  | 997/1 Albury - Corowa 132kV Line | N | 2016Q2 | ALB | TL | 2016-06-08 16:19 | 2016-06-08 18:44 |  |  |  | 132 |  |  | 2016
258440 |  |  | No.1 Transformer 132/22/6.6kV | N | 2016Q2 | ALB | TX | 2016-06-08 16:19 | 2016-06-08 18:44 |  |  |  | 132 |  |  | 2016
258461 | HV Equipment | CB | No.2 Capacitor | N | 2016Q2 | TRE | CAP | 2016-06-11 07:17 | 2016-06-11 08:58 |  |  | Top up SF6 on CB 2722 | 33 |  |  | 2016
258466 |  |  | 132kV B Bus | N | 2016Q2 | WG1 | BB | 2016-06-11 09:50 | 2016-06-11 14:31 | 132kV B Bus trip In conjunction with trips on No.2 and No.3 Transformers Wagga 330kV Substation No load lost as is been supported by the Yass and darlington Pt 132kV transmission system | Follow up |  | 132 |  |  | 2016
258467 |  |  | No.2 Transformer 132kV B CB 4422B | N | 2016Q2 | WG1 | CB | 2016-06-11 09:50 | 2016-06-11 14:31 |  |  |  | 132 |  |  | 2016
258468 |  |  | No.1 Capacitor | Z | 2016Q2 | WG1 | CAP | 2016-06-11 09:50 | 2016-06-11 14:31 |  |  |  | 132 |  | Fault | 2016
258469 |  |  | No.2 132kV Bus Coupler CB 4022 | N | 2016Q2 | WG1 | CB | 2016-06-11 09:50 | 2016-06-11 14:31 |  |  |  | 132 |  |  | 2016
258470 |  |  | 993 Wagga 330 - Gadara 132kV TL | Z | 2016Q2 | GAD, WG1 | TL | 2016-06-11 09:50 | 2016-06-11 14:31 |  |  |  | 132 |  | Fault | 2016
258471 |  |  | 99X Wagga 330 - Wagga 132 132kV TL | Z | 2016Q2 | WG2, WG1 | TL | 2016-06-11 09:50 | 2016-06-11 14:31 |  |  |  | 132 |  | Fault | 2016
258472 |  |  | 994 Wagga 330 - Yanco 132kV TL | Z | 2016Q2 | WG1, YA2 | TL | 2016-06-11 09:50 | 2016-06-11 14:31 |  |  |  | 132 |  | Fault | 2016
258473 |  |  | 9R2 Wagga 330 - Uranquinty 132kV TL | Z | 2016Q2 | WG1, URQ | TL | 2016-06-11 09:50 | 2016-06-11 14:31 |  |  |  | 132 |  | Fault | 2016
258474 |  |  | No.3 Transformer 330/132/11kV | N | 2016Q2 | WG1 | TX | 2016-06-11 09:50 | 2016-06-11 14:31 |  |  |  | 330 |  |  | 2016
258475 |  |  | No.3 Transformer 330/132/11kV | Z | 2016Q2 | WG1 | TX | 2016-06-11 09:50 | 2016-06-11 14:31 | 132kV B Bus trip In conjunction with trips on No.2 and No.3 Transformers Wagga 330kV Substation No load lost as is been supported by the Yass and darlington Pt 132kV transmission system | Follow up |  | 330 |  | Fault | 2016
258476 | HV Equipment | CB | No.2 Transformer 330/132/11kV | Z | 2016Q2 | WG1 | TX | 2016-06-11 09:50 | 2016-06-14 10:55 | 132kV B Bus trip In conjunction with trips on No.2 and No.3 Transformers Wagga 330kV Substation No load lost as is been supported by the Yass and darlington Pt 132kV transmission system | Follow up | HV fault internal to CB 4422B | 330 | Robert Li investigating. | Fault | 2016
258477 | HV Equipment | CB | No.2 Transformer 132kV B CB 4422B | N | 2016Q2 | WG1 | CB | 2016-06-12 08:13 | 2016-07-21 16:07 |  |  | Fault invetsigation CB442B and No.2 TX | 132 |  |  | 2016
258479 | HV Equipment | CB | No.1 Transformer 330/132/16kV | E | 2016Q2 | SE1 | TX | 2016-06-11 21:30 | 2016-06-11 23:38 |  |  | Top up SF6 on CB 5412 White Phase . | 330 |  | Forced | 2016
258493 |  |  | 824 Yass - Yass Town 66kV Line | N | 2016Q2 | YSN | TL | 2016-06-13 04:25 | 2016-06-13 06:22 |  | Follow up |  | 66 |  |  | 2016
258494 |  |  | No.3 Transformer 132/66/11kV | N | 2016Q2 | YSN | TX | 2016-06-13 04:25 | 2016-06-13 06:22 |  |  |  | 132 |  |  | 2016
258496 | HV Equipment | Rx | No.2 Reactor | N | 2016Q2 | KCR | RX | 2016-06-14 03:56 | 2016-07-06 19:29 |  | Follow up | HV Fault on reactor work order 00397365 No.2 Reactor repaired by using No.3 Reactor for spare parts | 33 |  |  | 2016
258518 |  |  | 219 Mamre - Mt Druitt 132kV Line | E | 2016Q2 | MAM, MDT | TL | 2016-06-14 17:24 | 2016-06-15 18:08 |  |  |  | 132 |  | Forced | 2016
258547 |  |  | 850 Tumut - Talbingo tee Jounama Dam 66kV Line | N | 2016Q2 | TU2 | TL | 2016-06-15 07:20 | 2016-06-15 07:20 |  | Follow up |  | 66 |  |  | 2016
258593 |  |  | 98R Beresfield - Tomago 330 132kV Line | N | 2016Q2 | TOM | TL | 2016-06-15 15:37 |  |  |  |  | 132 |  |  | 2016
258923 |  |  | 703 Port Macquarie - Boronia St No.1 33kV Line | N | 2016Q2 | PMQ | TL | 2016-06-19 18:02 | 2016-06-19 18:02 |  | Follow up |  | 33 |  |  | 2016
259040 | Secondary Equipment | Prot | 875 Wallerawang 132 - Oakey Park 66kV Line | N | 2016Q2 | WWS | TL | 2016-06-20 13:35 | 2016-06-20 15:32 | Reclose attempt failed due to a reclose inhibit received , Sydney trains restored supply via lithgow manually. line patrol all clear | Follow up | Events on local HMI show a reclose start and inhibit which lengthened the outage time. | 66 |  |  | 2016
259140 | HV Equipment | CB | 330kV B Bus 1-2 Section CB 5112 | N | 2016Q2 | SE1 | CB | 2016-06-21 16:17 | 2016-06-21 17:43 |  |  | Topup SF6 on CB5112 | 330 |  |  | 2016
259184 |  |  | 875 Wallerawang 132 - Oakey Park 66kV Line | N | 2016Q2 | WWS | TL | 2016-06-22 08:58 | 2016-06-22 12:05 | Line patrolled by Sydney Trains. No faults found. Line energised at 12:05 at Sydney Trains request. | Follow up |  | 66 |  |  | 2016
259222 |  |  | No1 Transformer Tie | N | 2016Q2 | BGE | TL | 2016-06-22 07:58 |  | No.1 tripped due to a protection wiring issue within the customer system. Customer identfied issue and requested No.1 transformer be energised at 16:44hrs. | Follow up |  | 132 |  |  | 2016
259426 |  |  | 7R5 Kempsey - North St 33kV Line | N | 2016Q2 | KS2 | TL | 2016-06-24 14:10 | 2016-06-24 21:08 | Feeder isolated and earthed for customer to allow repairs to be carried out. | Follow up |  | 33 |  |  | 2016
259429 |  |  | 852 Beryl - Dunedoo 66kV Line | N | 2016Q2 | BER | TL | 2016-06-24 14:47 | 2016-06-27 14:44 | No loss of load in customer system | Follow up |  | 66 |  |  | 2016
259430 |  |  | 703 Coffs Harbour - Nana Glen 66kV Line | N | 2016Q2 | COF | TL | 2016-06-24 11:25 | 2016-06-24 11:25 | Group 2 settings applied to No.1 and No.2 protections at time of TAR | Follow up |  | 66 |  |  | 2016
259431 |  |  | 703 Coffs Harbour - Nana Glen 66kV Line | N | 2016Q2 | COF | TL | 2016-06-24 11:32 | 2016-06-24 11:51 | Group 2 settings applied to No.1 and No.2 protections at time of TARTLO. Essential Energy opened bypass which extended 703 Nana Glen through to Nymboida and returned feeder to service into Nana Glen only. Group 1 protection settings restored after return to service.. | Follow up |  | 66 |  |  | 2016
259432 | LV/MECH Fail | Other | No.1 Transformer 330/132/11kV | E | 2016Q2 | NEW | TX | 2016-06-24 10:32 | 2016-06-24 12:29 | Saddles securing conduit on overhead gantry above No.1 Transformer at Newcastle 330kV Substation broke and unsupported length of conduit being blown towards HV conductors. No.1 Transformer de-energised. Conduit originally installed for floodlight supplies which are now redundant. Conduit safely cut and removed and No.1 Transformer returned to service. | Follow up | Saddles securing conduit on overhead gantry above No.1 Transformer at Newcastle 330kV Substation broke and unsupported length of conduit being blown towards HV conductors. No.1 Transformer de-energised. Conduit originally installed for floodlight supplies which are now redundant. Conduit safely cut and removed and No.1 Transformer returned to service. | 330 |  | Forced | 2016
259439 | HV Equipment | CB | No.2 Capacitor | N | 2016Q2 | TRE | CAP | 2016-06-25 08:56 | 2016-06-25 10:28 |  |  | SF6 top up | 33 |  |  | 2016
259442 | Tree/Ground | TL | 9W3 Coffs Harbour - Raleigh 132kV TL | N | 2016Q2 | COF, RAL | TL | 2016-06-24 15:00 | 2016-06-24 15:00 | No.1 Protection Ohmega OH1-311 relay at Raleigh displayed a distance to fault of -78.20 km and not recorded in protection details. | 30/06/2016 09:24:00 ¦ Follow up ¦ Structures 96-126 have been noted for the next routine aerial patrol. | Successful auto reclose, caused by falling tree brushing the HV conductors. Small grass fire started, extinguished by an easment officer conducting the patrol. Work order 00398286 | 132 | Off easement tree, strong wind and wood rot led to this tree falling. |  | 2016
259443 | HV Equipment | TX | No.3 Transformer 132/66/11kV | E | 2016Q2 | KLK | TX | 2016-06-25 10:38 | 2016-06-27 11:45 | AUX Transformer Oil level low. | Follow up | Oil top up | 132 |  | Forced | 2016
259445 | HV Equipment | CB | 7R4 Kempsey - Munga 33kV Line | N | 2016Q2 | KS2 | TL | 2016-06-25 22:42 | 2016-06-26 00:04 |  |  | SF6 top up | 33 |  |  | 2016
259446 | LV/MECH Fail | SVC | No.1 Static VAR Compensator | Z | 2016Q2 | LSM | SVC | 2016-06-25 23:21 | 2016-06-26 01:54 | TCR gate control panel failure. | Follow up | Faulty power supply Work order 00398271 | 132 |  | Fault | 2016
259447 | Unknown/Other | TL | 96M Narrabri - Moree 132kV TL | N | 2016Q2 | MRE, NB2 | TL | 2016-06-26 02:34 | 2016-06-26 02:34 |  | Follow up | Successful auto reclose | 132 |  |  | 2016
259800 | Unknown/Other | Proc | No.3 Transformer 500/330/33kV | E | 2016Q2 | KCR | TX | 2016-06-28 07:15 | 2016-06-28 07:16 |  |  | less than 24 hours notice. Completion of protection routine maintenance(relays), meggering and trip checks. | 500 |  | Forced | 2016
259823 | HV Equipment | Rx | No.3 330kV Reactor | E | 2016Q2 | AR1 | RX | 2016-06-29 08:16 | 2016-06-29 13:07 |  |  | Oil top up | 330 |  | Forced | 2016
259927 |  |  | No.3 Aux Transformer 33kV/415V | N | 2016Q2 | KCR | TX | 2016-06-28 07:15 | 2016-06-28 07:16 |  |  |  | 33 |  |  | 2016
259928 |  |  | No.3 Reactor | N | 2016Q2 | KCR | RX | 2016-06-28 07:15 | 2016-06-28 07:16 |  |  |  | 33 |  |  | 2016
259993 | Unknown/Other | Prot | 92P Beaconsfield South - Belmore Park 132kV Cable | N | 2016Q2 | BFD | UG | 2016-06-29 08:06 | 2016-07-01 17:39 | "BFIELD STH 132 BELMORE PK 92P PROT1 FAULT" & "BFIELD STH 132 BELMORE PK 92P PROT1 OPERATED" alarms received at time of trip. | Follow up | "BFIELD STH 132 BELMORE PK 92P PROT1 FAULT" & "BFIELD STH 132 BELMORE PK 92P PROT1 OPERATED" alarms received at time of trip of the switchbay for 92P. Work order 00398402 | 132 |  |  | 2016
260032 | LV/MECH Fail | TL | 11 Dapto - Sydney South 330kV TL | E | 2016Q2 | DPT, SYS | TL | 2016-06-29 13:28 | 2016-06-29 17:55 |  |  | Earthwire clevis bolt loose on TL 11 , Str 11. outage required to repair. Work orders 00398328,00398404,00398406 | 330 | Line due for climbing inspection this regulatory period. | Forced | 2016
260047 | HV Equipment | CB | 132kV No.1 Bus Coupler CB 4012 | N | 2016Q2 | RGV | CB | 2016-06-29 11:43 | 2016-06-29 12:41 |  |  | SF6 top up | 132 |  |  | 2016
260148 |  |  | No.2 330kV Generator Transformer Group | N | 2016Q2 | LD1 | TX | 2016-06-30 09:21 | 2016-07-08 02:32 |  |  |  | 330 |  |  | 2016
260489 | Staff Error | Proc | No.2 Transformer 330/132/11kV | Z | 2016Q3 | WG1 | TX | 2016-07-01 13:53 | 2016-07-01 14:08 |  | Follow up | Protection staff were carrying out BBP balance for new CB 4422B using ground bus to 99X T/L at the time. | 330 |  | Fault | 2016
260604 | Relay Faulty | SVC | No.1 Static VAR Compensator | Z | 2016Q3 | LSM | SVC | 2016-07-03 22:47 | 2016-07-04 01:33 | 24V auxiliary relay in power circuit in AVR 2 replaced and now functioning. Further investigation by field staff on Tuesday. | Follow up | 24V auxiliary relay in power circuit in AVR 2 replaced and now functioning. Further investigation by field staff on Tuesday. Work order 00400126 | 132 |  | Fault | 2016
260734 |  |  | 822 Deniliquin - Moulamein tee Deniliquin 66kV SS 66kV Line | N | 2016Q3 | DN2 | TL | 2016-07-05 07:14 | 2016-07-05 07:14 | 19.62km Distance to Fault. HV Switchgear inspected and all OK. | Follow up |  | 66 |  |  | 2016
260884 | Unknown/Other | Proc | No.2 Capacitor | E | 2016Q3 | DN2 | CAP | 2016-07-06 13:21 | 2016-07-06 14:26 |  |  | <24hrs notice. #2 Cap required Out Of Service for transport clearance. Work order 393365. | 66 |  | Forced | 2016
260993 | Unknown/Other | CT | 4 Marulan CB 42 | N | 2016Q3 | YSN | CB | 2016-07-08 07:58 | 2016-07-08 11:08 |  |  | 4 Marulan CB42 CT ratio changes, Insulation, winding resistance, Ratio & Polarity checks Testing voltage <3kv | 330 |  |  | 2016
261176 |  |  | 881 Moree - Garah tee Ashley 66kV Line | N | 2016Q3 | MRE | TL | 2016-07-07 17:12 | 2016-07-07 17:12 |  | Follow up |  | 66 |  |  | 2016
261228 | Secondary Equipment | Prot | No.5 Transformer 330/132/11kV | Z | 2016Q3 | SYW | TX | 2016-07-08 08:14 | 2016-07-08 10:11 | Tripped on energising after SSB cutover. No.1 Prot and temporarys didn't operate. Protection design and AMC OK'd second attempt which was successful. | Follow up | Tripped on energising after SSB cutover. No.1 Prot and temporarys didn't operate. Protection design and AMC OK'd second attempt which was successful. Tripped on inrush. | 330 |  | Fault | 2016
261296 |  |  | 971 Yass - Goulburn tee Cullerin Range tee Gunning 132kV Line | N | 2016Q2 | YSN | TL | 2016-06-30 02:54 | 2016-06-30 05:46 | 5MW Gunning Wind Farm 16MW Culerin Range | Follow up |  | 132 |  |  | 2016
261429 |  |  | No.3 500kV Generator Transformer Group | N | 2016Q3 | ER0 | TX | 2016-07-11 13:46 | 2016-07-11 22:03 |  | Follow up |  | 500 |  |  | 2016
261495 |  |  | 79P Griffith - Goolgowi 33kV Line | N | 2016Q3 | GRF | TL | 2016-07-12 14:45 | 2016-07-12 20:26 | EssE informed TRTLO cause by switching within their network. Repairs carried out and feeder energised at Essential Energy request. | Follow up |  | 33 |  |  | 2016
261508 | Unknown/Other | TL | 66 Murray - Lower Tumut 330kV TL | N | 2016Q3 | LT1, MUR | TL | 2016-07-12 21:36 | 2016-07-12 21:36 | Transmission Line reclosed boths ends on the 'B' CB. Normal arrangement is for single CB reclose each end. 'A' CB's closed manually via Scada both ends. | Follow up | Transmission Line reclosed boths ends on the 'B' CB. Normal arrangement is for single CB reclose each end. 'A' CB's closed manually via Scada both ends. | 330 |  |  | 2016
261509 | Unknown/Other |  | 66 Murray A CB 662A | N | 2016Q3 | LT1 | CB | 2016-07-12 21:36 | 2016-07-12 21:36 |  |  |  | 330 |  |  | 2016
261510 |  |  | 66 Murray B Bus CB 662B | N | 2016Q3 | LT1 | CB | 2016-07-12 21:36 | 2016-07-12 21:36 |  |  |  | 330 |  |  | 2016
261511 |  |  | 66 Lower Tumut A CB 662A | N | 2016Q3 | MUR | CB | 2016-07-12 21:36 | 2016-07-12 21:36 |  |  |  | 330 |  |  | 2016
261512 |  |  | 66 Lower Tumut B CB 662B | N | 2016Q3 | MUR | CB | 2016-07-12 21:36 | 2016-07-12 21:36 |  |  |  | 330 |  |  | 2016
261544 | Lightning/Storm | CB | U7 Tumut 2 CB U72 | N | 2016Q3 | UT1 | CB | 2016-07-13 16:00 | 2016-07-14 15:20 |  |  | Investigate CB U72 pole discrepency and repair CB U72 Mech box lid has come off and Mech box is full of snow | 330 |  |  | 2016
261621 | Lightning/Storm | CB | U7 Upper Tumut - Tumut 2 330kV TL | Z | 2016Q3 | UT1 | TL | 2016-07-12 21:59 |  |  | Follow up | CB U72 unable to be closed.and fleeting discrepency alarm CB U72 Mech box lid has come off and Mech box is full of snow | 330 |  | Fault | 2016
261760 | HV Equipment | CB | 330kV B Bus 1-2 Section CB 5112 | N | 2016Q3 | SE1 | CB | 2016-07-14 18:05 | 2016-07-14 19:42 |  |  | Topup SF6 in CB 5112 | 330 |  |  | 2016
261947 | Relay Faulty | Prot | 9R1 Wagga 330 - Uranquinty 132kV TL | Z | 2016Q3 | WG1, URQ | TL | 2016-07-14 19:11 | 2016-07-14 20:08 | Uranquinty PS total generation at time of trip was 655MW. Generation reduced to 500MW via runback scheme after trip. CB 9R12 closed after consultation with AMC. | Follow up | URQ No2 Prot Relay suspected maloperation | 132 |  | Fault | 2016
262185 | Unknown/Other | TL | 948 Orange North - Panorama 132kV TL | N | 2016Q3 | PMA, ONO | TL | 2016-07-16 06:53 | 2016-07-16 06:53 |  | Follow up | Successful TAR | 132 |  |  | 2016
262201 | HV Equipment | CB | 932 Sydney West - Mt Druitt 132kV Line | N | 2016Q3 | SYW | TL | 2016-07-17 13:50 | 2016-07-17 14:57 |  |  | Top up of CB9322 RTS ok | 132 |  |  | 2016
262252 | HV Equipment | CB | No.1 Capacitor | E | 2016Q3 | LSM | CAP | 2016-07-18 11:06 |  |  |  | Broken pull rod yoke between the operating mechanism and pole A. | 132 | Parts ordered from ABB. Failure likely due to fatigue from 6000 operations. May require a replacement strategy. | Forced | 2016
262272 | HV Equipment | CB | 9W3 Coffs Harbour - Raleigh 132kV TL | N | 2016Q3 | COF, RAL | TL | 2016-07-18 14:32 | 2016-07-18 15:21 |  |  | Top up SF6 CB 9W32 | 132 |  |  | 2016
262310 |  |  | Spare Tie Transformer | N | 2016Q3 | ER0 | TX | 2016-07-19 07:16 | 2016-07-19 13:51 |  |  |  | 500 |  |  | 2016
262543 | Relay Faulty | TX | No.2 Transformer 330/132/11kV | Z | 2016Q3 | JDA | TX | 2016-07-20 11:51 | 2016-07-20 18:19 | Field satff advise Buchholz Relay operation caused by water ingress into Buchholz Relay. | Follow up | No2 Tx T/C Buchholz tripped due to water ingress in Buccholz | 330 |  | Fault | 2016
262544 |  |  | O60 Wodonga A CB 0602A | N | 2016Q3 | JDA | CB | 2016-07-20 11:51 | 2016-07-20 18:19 |  |  |  | 330 |  |  | 2016
262545 |  |  | 62 Wagga B CB 622B | N | 2016Q3 | JDA | CB | 2016-07-20 11:51 | 2016-07-20 18:19 |  |  |  | 330 |  |  | 2016
262603 |  |  | 92P Beaconsfield South - Belmore Park 132kV Cable | N | 2016Q3 | BFD | UG | 2016-07-20 15:33 |  | Suspect Communications problem with No1 Protection. Ausgrid have requested line de-energised only while Techs investigate. | Follow up |  | 132 |  |  | 2016
262761 |  |  | 8M1 Orange - Orange Industrial 66kV Line | N | 2016Q3 | ORG | TL | 2016-07-22 09:09 | 2016-07-22 09:09 |  | Follow up |  | 66 |  |  | 2016
262842 | Tree/Ground | TL | 97G Murray - Guthega tee Geehi 132kV TL | Z | 2016Q3 | GTH, MUR, GHI | TL | 2016-07-22 14:19 | 2016-07-26 17:11 | TG Protection staff in Murray advise heavy winds and rain | 28/07/2016 11:48:00 ¦ Follow up ¦ Heavy snow and steep terrain. ¦ Structures 96-101 have been noted for the next routine aerial patrol. | Fallen Trees | 132 |  | Fault | 2016
262843 |  |  | 97G/3 Geehi Tee CB 97G2 | N | 2016Q3 | GTH | CB | 2016-07-22 14:19 | 2016-07-26 17:11 |  |  |  | 132 |  |  | 2016
262844 |  |  | 97G/1 Geehi Tee CB 97G2 | N | 2016Q3 | MUR | CB | 2016-07-22 14:19 | 2016-07-26 17:11 |  |  |  | 132 |  |  | 2016
262913 |  |  | 847 Murrumburrah - Boorowa 66kV Line | N | 2016Q3 | MRU | TL | 2016-07-22 15:31 | 2016-07-22 16:51 | Advised Essential Energy Staff patrolling line. Essential Energy Staff on site at Murrumburrah - Protection Flags reset ok. | Follow up |  | 66 |  |  | 2016
262918 |  |  | 891 Cowra - Young tee Wyangala tee Monteagle 66kV Line | N | 2016Q3 | CW2 | TL | 2016-07-22 17:42 | 2016-07-22 19:55 | Storms in the area. Fault isolated within Essential Energy system and CB 8912 closed at Cowra. | Follow up |  | 66 |  |  | 2016
262919 | HV Equipment | CB | No.3 Transformer 330/132/11kV | E | 2016Q3 | BFD | TX | 2016-07-22 19:13 | 2016-07-22 23:27 |  |  | CB 5432 Blue phase Low SF6 | 330 |  | Forced | 2016
262920 |  |  | 847 Murrumburrah - Boorowa 66kV Line | N | 2016Q3 | MRU | TL | 2016-07-22 17:00 | 2016-07-22 17:00 |  | Follow up |  | 66 |  |  | 2016
262921 |  |  | 847 Murrumburrah - Boorowa 66kV Line | N | 2016Q3 | MRU | TL | 2016-07-22 17:10 | 2016-07-22 17:10 |  | Follow up |  | 66 |  |  | 2016
262945 |  |  | No.4 Transformer | N | 2016Q3 | TOM | TX | 2016-07-24 06:39 | 2016-07-27 16:14 |  | Follow up |  | 330 |  |  | 2016
262946 |  |  | 97G/3 Geehi Tee CB 97G2 | N | 2016Q3 | GTH | CB | 2016-07-25 11:45 | 2016-07-26 17:11 |  |  |  | 132 |  |  | 2016
262947 |  |  | No.2 Balranald - Moulamein 22kV Line | N | 2016Q3 | BRD | TL | 2016-07-24 09:39 | 2016-07-24 10:59 | Protection flags may include those for TARTLO detailed in FEOR 2016-F-228. | Follow up |  | 22 |  |  | 2016
262948 |  |  | No.2 Balranald - Moulamein 22kV Line | N | 2016Q3 | BRD | TL | 2016-07-24 14:37 | 2016-07-24 17:29 | Protection flags may include those for TARTLO detailed in FEOR 2016-F-227. | Follow up |  | 22 |  |  | 2016
262981 |  |  | 887 Glen Innes - Glen Innes 66kV Line | N | 2016Q3 | GNS | TL | 2016-07-25 18:38 | 2016-07-25 18:38 |  | Follow up |  | 66 |  |  | 2016
263005 | HV Equipment | CB | No.3 Transformer 132/66/11kV | E | 2016Q3 | NB2 | TX | 2016-07-26 11:35 | 2016-07-26 12:27 |  |  | CB 3432 Low SF6 | 132 |  | Forced | 2016
263048 | Relay Faulty | Prot | No.4 Transformer 132/66/11kV | Z | 2016Q3 | TRE | TX | 2016-07-27 04:44 | 2016-07-27 17:19 |  | Follow up | Faulty T60 relay on No1 Protection | 132 | Replacement program in progress. | Fault | 2016
263049 | Relay Faulty | Prot | 914 Sydney South - Bankstown 132kV Line | N | 2016Q3 | SYS | TL | 2016-07-27 11:14 | 2016-07-27 11:42 |  |  | No2 Prot L90 requires battery replacement | 132 | In service outage |  | 2016
263115 |  |  | 7R2 Kempsey - North St tee Smithtown 33kV Line | N | 2016Q3 | KS2 | TL | 2016-07-28 06:53 | 2016-07-28 06:53 |  | Follow up |  | 33 |  |  | 2016
263140 | HV Equipment | CB | No.1 Transformer 132KV B CB 4412B | N | 2016Q3 | DPT | CB | 2016-07-22 15:01 |  |  |  | Close coil appears to be burnt out | 132 |  |  | 2016
263287 |  |  | No.2 Transformer 132/66/11kV | N | 2016Q3 | MRE | TX | 2016-07-29 13:10 | 2016-07-29 14:26 |  |  |  | 132 |  |  | 2016
263333 | HV Equipment | Aux Tx | No.2 Transformer 132/66/11kV | E | 2016Q3 | MRE | TX | 2016-07-29 13:10 | 2016-07-29 14:26 | Outage taken to top-up No2 Aux Transformer oil. | Follow up | Topup of low oil in No2 Aux Tx | 132 |  | Forced | 2016
263338 |  |  | 898 Parkes - Trundle 66kV Line | N | 2016Q3 | PKS | TL | 2016-07-29 23:13 | 2016-07-29 23:13 |  | Follow up |  | 66 |  |  | 2016
263344 | Animal/Bird | Other | No.2 Transformer 330/132/11kV | Z | 2016Q3 | WL1 | TX | 2016-07-30 12:22 | 2016-08-02 14:41 | Obvious flash marks found on white phase insulator between 330kV TX bushings and CT's. Still bits of wire attached to conductor. See IR 16179. | Follow up | Obvious flash marks found on white phase insulator between 330kV TX bushings and CT's. Still bits of wire attached to conductor. See IR 16179. | 330 |  | Fault | 2016
263353 |  |  | 971 Yass - Goulburn tee Cullerin Range tee Gunning 132kV Line | N | 2016Q3 | YSN | TL | 2016-07-30 21:28 | 2016-07-30 22:31 | Advised SO/Essential Energy of prot'n details and DTF, SO requested attempt close CB 9712, done and CB remained closed | Follow up |  | 132 |  |  | 2016
263452 |  |  | 850 Tumut - Talbingo tee Jounama Dam 66kV Line | N | 2016Q3 | TU2 | TL | 2016-08-01 09:21 | 2016-08-01 09:21 | SHL Jounama was generating at time of trip approx. 8MW generation lost. |  |  | 66 |  |  | 2016
263577 |  |  | No.5 Wagga 132 - Macleay St 66kV Line | N | 2016Q3 | WG2 | TL | 2016-08-02 08:05 | 2016-08-02 08:05 |  |  |  | 66 |  |  | 2016
263664 |  |  | 723 Moree - Wenna tee Wathagar 66kV Line | N | 2016Q3 | MRE | TL | 2016-08-02 16:27 | 2016-08-02 16:27 | Storms in the area. |  |  | 66 |  |  | 2016
263669 | Lightning/Storm | TL | 9U2 Inverell - Moree 132kV TL | N | 2016Q3 | INV, MRE | TL | 2016-08-02 18:28 | 2016-08-02 18:28 |  |  | Successful TAR | 132 |  |  | 2016
263672 |  |  | 887 Glen Innes - Glen Innes 66kV Line | N | 2016Q3 | GNS | TL | 2016-08-02 21:26 | 2016-08-02 21:26 |  |  |  | 66 |  |  | 2016
263673 | Secondary Equipment | TX | No.1 Transformer 132/66/11KV | Z | 2016Q3 | MOL | TX | 2016-08-03 02:05 | 2016-08-03 13:52 | approx 3.2MW of customer load lost, Essential requested to restore from there system. 04:15 hrs customer load restored through essential energy network. No.1 Transformer returned to service at 13:52 via scada. |  | Faulty sensors in Thermal units | 132 |  | Fault | 2016
263746 |  |  | 862/1 Taree - OCC Kew tee Johns River 66kV Line | N | 2016Q3 | TRE | TL | 2016-08-03 11:19 | 2016-08-03 12:38 |  |  |  | 66 |  |  | 2016
263790 | Secondary Equipment | TX | No.3 Transformer 132/66/11kV | Z | 2016Q3 | KLK | TX | 2016-08-03 23:00 |  |  |  | Suspected faulty Over Pressure Device on Tap Changer | 132 |  | Fault | 2016

## Stats
Cal Yr: | TL/UG Fault Outages: | TL/UG Forced Outages: | TX Fault Outages: | TX Forced Outages: | CAP/RX/SVC Fault Outages: | CAP/RX/SVC Forced Outages: | TL/UG Count: | TX Count: | CAP/RX/SVC Count: | TL/UG Fault Outage Rate: | TL/UG Forced Outage Rate: | TX Fault Outage Rate: | TX Forced Outage Rate: | CAP/RX/SVC Fault Outage Rate: | CAP/RX/SVC Forced Outage Rate:
2014 | 21 | 35 | 20 | 72 | 21 | 30 | 205.333 | 184.5 | 134.167 | 10.23% | 17.05% | 10.84% | 39.02% | 15.65% | 22.36%
2015 | 24 | 48 | 24 | 57 | 13 | 37 | 210.333 | 183.75 | 137.25 | 11.41% | 22.82% | 13.06% | 31.02% | 9.472% | 26.96%