## Notes
Notes
1. LV capacitors not included ie 11,22 and 33 kV
2. SCADA minutes lost data from Terry Day at AEMO as TNSD NOCS people don't have the history
3. Circuit numbers for calcs are the annual average
4. transient outages not included
5. for average outage duration calcs, use time off in monthly calcs files
6. with LOS gradual restoration over time, take the outage to the last restore (ask question though eg should we split events?)
7. TQS numbers, eg TQS0101, refer to parameter labels in the Economic Benchmarking RIN

## TQS0101-0115 outage rate ptable
AER STPIS | - multiple -
Request Type | - multiple -
Duration (Min) | - multiple -
Count of Duration (Min) | Element Type
Actual Start Time | Capacitor | Transformer | Transmission | Total Result
2006
2007 | 2 | 14 | 20 | 36
2008 | 1 | 4 | 6 | 11
2009 | 1 | 3 | 6 | 10
2010 | 1 | 3 | 7 | 11
2011 |  | 4 | 7 | 11
2012 | 4 | 1 | 19 | 24
2013 | 2 | 4 | 14 | 20
2014
<01/02/2006
>01/02/2014
Total Result | 11 | 33 | 79 | 123
[8 empty] | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013
[5 empty] | TQS0101 | Lines outage rate - fault | per cent | 40.2% | 55.34% | 25.24% | 34.95% | 12.75% | 24.53% | 51.85% | 31.78%
[5 empty] | TQS0102 | Number of Lines fault outages | number | 41 | 57 | 26 | 36 | 13 | 26 | 56 | 34
[5 empty] | TQS0103 | Number of defined Lines | number | 102 | 103 | 103 | 103 | 102 | 106 | 108 | 107
[5 empty] | TQS0104 | Transformers outage rate - fault | per cent | 15.84% | 25% | 6.863% | 13.46% | 9.615% | 7.477% | 10.91% | 16.51%
[5 empty] | TQS0105 | Number of Transformer fault outages | number | 16 | 25 | 7 | 14 | 10 | 8 | 12 | 18
[5 empty] | TQS0106 | Number of defined Transformers | number | 101 | 100 | 102 | 104 | 104 | 107 | 110 | 109
[5 empty] | TQS0107 | Reactive plant outage rate - fault | per cent | 22.22% | 0% | 10% | 0% | 0% | 0% | 16.67% | 0%
[5 empty] | TQS0108 | Number of Reactive plant fault outages | number | 2006: 2; 2008: 1; 2012: 2
[5 empty] | TQS0109 | Number of defined Reactive plant | number | 9 | 10 | 10 | 10 | 10 | 12 | 12 | 12
[5 empty] | TQS0110 | Lines outage rate – forced outage | per cent | 0% | 19.42% | 5.825% | 5.825% | 6.863% | 6.604% | 17.59% | 13.08%
[5 empty] | TQS0111 | Number of Lines forced outages | number | 0 | 20 | 6 | 6 | 7 | 7 | 19 | 14
[5 empty] | TQS0112 | Transformer outage rate – forced outage | per cent | 0% | 14% | 3.922% | 2.885% | 2.885% | 3.738% | 0.9091% | 3.67%
[5 empty] | TQS0113 | Number of Transformers forced outages | number | 0 | 14 | 4 | 3 | 3 | 4 | 1 | 4
[5 empty] | TQS0114 | Reactive plant outage rate – forced outage | per cent | 0% | 20% | 10% | 10% | 10% | 0% | 33.33% | 16.67%
[5 empty] | TQS0115 | Number of Reactive plant forced outages | number | 0 | 2 | 1 | 1 | 1 | 0 | 4 | 2

## TQS0101-0115 Outage Query
Outage Query
Outage ID | WASP Outage Key | Source ID | Planned Start Time | Planned End Time | Actual Start Time | Actual End Time | Duration (Min) | Element ID | Element Name | Element Type | Request Type | Request Reason | Request Instigator | Status | Out of Service | Unserved MW Min | Included | Reason | Comment | CAPEX | AER STPIS
98772 | 4103 | 1115 |  |  | 2006-01-05 03:11 | 2006-01-05 03:18 | 7 | E0270 | PM-HA 3 110 kV Transmission Circuit | Transmission | Fault | Wildlife | Transend | Completed | TRUE | 0 | TRUE |  | IR207 - PM-HA 3 interrupted due to bird streamer causing flashover at T18 (top phase). | FALSE | Critical
98773 | 4104 | 1117 |  |  | 2006-01-09 06:57 | 2006-01-09 07:08 | 11 | E0772 | PL-ST 110 kV Transmission Circuit | Transmission | Fault | Internal Fault | Transend | Completed | TRUE | 194 | TRUE |  | IR208 - PL-ST 110 kV and PL T2 interrupted due to faulty directional overcurrent relay element at PL. | FALSE | Non-Critical
98774 | 4104 | 1117 |  |  | 2006-01-09 06:57 | 2006-01-09 10:28 | 211 | E0777 | PL 110/22 kV T2 Transformer Circuit | Transformer | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR208 - PL-ST 110 kV and PL T2 interrupted due to faulty directional overcurrent relay element at PL. | FALSE | Non-Critical
98775 | 4105 | 6077 |  |  | 2006-01-16 07:52 | 2006-01-16 07:52 | 0 | E0902 | TR 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98776 | 4106 | 6095 |  |  | 2006-01-23 09:57 | 2006-01-23 09:58 | 1 | E0597 | DP 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98777 | 4107 | 6094 |  |  | 2006-01-23 07:42 | 2006-01-23 07:42 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98778 | 4108 | 6093 |  |  | 2006-01-23 03:43 | 2006-01-23 03:43 | 0 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98779 | 4109 | 6091 |  |  | 2006-01-20 22:18 | 2006-01-20 22:53 | 35 | E0489 | GT 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98780 | 4110 | 6090 |  |  | 2006-01-20 20:04 | 2006-01-20 20:04 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98781 | 4111 | 6089 |  |  | 2006-01-20 08:32 | 2006-01-20 08:32 | 0 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98782 | 4112 | 6088 |  |  | 2006-01-20 08:03 | 2006-01-20 08:32 | 29 | E0022 | BW 11 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98783 | 4113 | 6087 |  |  | 2006-01-20 08:02 | 2006-01-20 08:02 | 0 | E0022 | BW 11 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98784 | 4114 | 6086 |  |  | 2006-01-20 07:41 | 2006-01-20 08:01 | 20 | E0605 | DP 22 kV XG2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98785 | 4115 | 6085 |  |  | 2006-01-20 05:37 | 2006-01-20 05:38 | 1 | E0022 | BW 11 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98786 | 4116 | 6084 |  |  | 2006-01-20 05:31 | 2006-01-20 05:31 | 0 | E0014 | BW 11 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98787 | 4117 | 6082 |  |  | 2006-01-20 05:15 | 2006-01-20 05:16 | 1 | E0022 | BW 11 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98788 | 4119 | 6080 |  |  | 2006-01-19 15:12 | 2006-01-19 15:12 | 0 | E0639 | ST 22 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98789 | 4120 | 6079 |  |  | 2006-01-18 23:39 | 2006-01-18 23:39 | 0 | E0902 | TR 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98790 | 4121 | 6078 |  |  | 2006-01-17 09:54 | 2006-01-17 10:18 | 24 | E0014 | BW 11 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98792 | 4123 | 6076 |  |  | 2006-01-16 05:40 | 2006-01-16 05:40 | 0 | E0158 | MB 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98793 | 4124 | 6074 |  |  | 2006-01-11 21:57 | 2006-01-12 00:49 | 172 | E0083 | CR 33 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98794 | 4125 | 6075 |  |  | 2006-01-11 21:57 | 2006-01-12 00:49 | 172 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98795 | 4126 | 6073 |  |  | 2006-01-11 12:30 | 2006-01-11 12:49 | 19 | E0885 | SR 22 kV D2 Feeder Circuit (Future) | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98796 | 4127 | 6072 |  |  | 2006-01-09 14:04 | 2006-01-09 14:04 | 0 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98797 | 4128 | 6070 |  |  | 2006-01-09 09:39 | 2006-01-09 09:39 | 0 | E0150 | NN 22 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98798 | 4129 | 6068 |  |  | 2006-01-08 10:11 | 2006-01-08 10:11 | 0 | E0150 | NN 22 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98799 | 4130 | 6067 |  |  | 2006-01-08 06:53 | 2006-01-08 07:40 | 47 | E0344 | LF E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98800 | 4131 | 6052 |  |  | 2006-01-02 08:28 | 2006-01-02 08:28 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98801 | 4132 | 6053 |  |  | 2006-01-03 08:31 | 2006-01-03 08:31 | 0 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98802 | 4133 | 6054 |  |  | 2006-01-03 10:09 | 2006-01-03 10:31 | 22 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98803 | 4134 | 6055 |  |  | 2006-01-03 11:36 | 2006-01-03 11:36 | 0 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98804 | 4135 | 6059 |  |  | 2006-01-03 13:42 | 2006-01-03 13:42 | 0 | E0300 | AV 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98805 | 4136 | 6060 |  |  | 2006-01-03 13:45 | 2006-01-03 13:45 | 0 | E0300 | AV 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98806 | 4137 | 6062 |  |  | 2006-01-03 14:24 | 2006-01-03 14:24 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98807 | 4138 | 6061 |  |  | 2006-01-03 13:48 | 2006-01-03 18:39 | 291 | E0300 | AV 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98808 | 4139 | 6063 |  |  | 2006-01-04 17:08 | 2006-01-04 17:08 | 0 | E0273 | PM 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98809 | 4140 | 6066 |  |  | 2006-01-05 05:22 | 2006-01-05 05:22 | 0 | E0902 | TR 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98810 | 4141 | 6058 |  |  | 2006-01-03 12:38 | 2006-01-03 12:38 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98811 | 4142 | 6057 |  |  | 2006-01-03 12:34 | 2006-01-03 12:34 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98812 | 4143 | 1118 |  |  | 2006-01-17 13:39 | 2006-01-17 22:38 | 539 | E0401 | BU-PL 110 kV Transmission Circuit | Transmission | Fault | Overheating | Transend | Completed | TRUE | 5815 | TRUE |  | IR209 - BU-PL 110 kV interrupted due to broken conductor loop. | FALSE | Non-Critical
98813 | 4144 | 1119 |  |  | 2006-01-19 09:18 | 2006-01-19 11:08 | 110 | E0421 | BB-GT 2 110 kV Transmission Circuit | Transmission | Fault | Customer | Generator Request | Completed | TRUE | 0 | TRUE |  | IR213 - BB-GT 2 220 kV interrupted due to incorrect CT configuration in switchyard at Bell Bay during machine synchronisation. | FALSE | Undefined
98814 | 4145 | 1120 |  |  | 2006-01-20 04:45 | 2006-01-20 06:55 | 130 | E0453 | KE 110/11 kV T2 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 636 | TRUE |  | IR223 - Kermandie Substation transformer T2 interrupted due to incorrect CT secondary connections (during commissioning). This resulted in feeder faults causing TF REF protection operation. | FALSE | Non-Critical
98815 | 4145 | 1120 |  |  | 2006-01-20 07:11 | 2006-01-20 07:36 | 25 | E0453 | KE 110/11 kV T2 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR223 - Kermandie Substation transformer T2 interrupted due to incorrect CT secondary connections (during commissioning). This resulted in feeder faults causing TF REF protection operation. | FALSE | Non-Critical
98816 | 4145 | 1120 |  |  | 2006-01-20 07:43 | 2006-01-20 08:12 | 29 | E0453 | KE 110/11 kV T2 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR223 - Kermandie Substation transformer T2 interrupted due to incorrect CT secondary connections (during commissioning). This resulted in feeder faults causing TF REF protection operation. | FALSE | Non-Critical
98817 | 4146 | 1123 |  |  | 2006-01-20 05:17 | 2006-01-20 05:17 | 0 | E1073 | BW-LF 110 kV Transmission Circuit | Transmission | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR219 - BW-LF 110 kV momentarily interrupted due to lightning strike on WA-LF 110 kV transmission circuit and incorrect relay setting. | FALSE | Non-Critical
98818 | 4147 | 1125 |  |  | 2006-01-20 05:18 | 2006-01-20 19:05 | 827 | E0001 | WA-BW 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 3359 | TRUE |  | IR219 - WA-BW 110 kV interrupted due to lightning strike causing two conductors to break. | FALSE | Non-Critical
98819 | 4149 | 1127 |  |  | 2006-01-20 05:39 | 2006-01-20 09:17 | 218 | E0190 | LF-RK 2-SO 110 kV Transmission Circuit | Transmission | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 29 | TRUE |  | IR233 - LF-RK 2-SO interrupted during severe lightning storms. Lindisfarne circuit breaker F152 failed to reclose due to incorrect auto reclose settings. | FALSE | Non-Critical
98820 | 4150 | 1132 |  |  | 2006-01-20 07:10 | 2006-01-20 07:11 | 1 | E0027 | LI-CL-RE-CS 1 220 kV Transmission Circuit (Changed to E1958) | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR233 - LI-CL-RE-CS No 1 220 kV interrupted during severe lightning storms due. Autoreclose of the circuit breaker did not occur due to a relay failure. A single phase fault was detected by the protection at Liapootah but failed to auto reclose successfully resulting in an extended outage of the circuit. | FALSE | Critical
98821 | 4151 | 1130 |  |  | 2006-01-20 07:11 | 2006-01-20 07:12 | 1 | E0138 | TA-NN 1 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR233 - TA-NN 1 110 kV interrupted during severe lightning storms. | FALSE | Critical
98822 | 4152 | 1134 |  |  | 2006-01-20 07:40 | 2006-01-20 07:40 | 0 | E0554 | SH-WV 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 162 | TRUE |  | IR233 - SH-WV and DP-WV 110 kV interrupted during severe lightning storms. | FALSE | Non-Critical
98823 | 4152 | 1134 |  |  | 2006-01-20 07:40 | 2006-01-20 07:46 | 6 | E0608 | DP-WV 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR233 - SH-WV and DP-WV 110 kV interrupted during severe lightning storms. | FALSE | Non-Critical
98824 | 4155 | 1139 |  |  | 2006-01-24 04:45 | 2006-01-24 06:55 | 130 | E0453 | KE 110/11 kV T2 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 68 | TRUE |  | IR223 - Kermandie Substation transformer T2 interrupted due to incorrect CT secondary connections (during commissioning). This resulted in feeder faults causing TF REF protection operation. | FALSE | Non-Critical
98825 | 4156 | 1143 |  |  | 2006-01-25 14:14 | 2006-01-25 21:02 | 408 | E0538 | SH-FA 1 220 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR225 - SH-FA 1 220 kV interrupted due to incorrect OPGW pulling process utilised by Contractor resulting in OPGW falling and contacting the 220 KV circuit below. | FALSE | Critical
98827 | 4161 | 6097 |  |  | 2006-01-23 22:18 | 2006-01-23 22:18 | 0 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98828 | 4162 | 6098 |  |  | 2006-01-23 14:36 | 2006-01-23 23:26 | 530 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault | Fire (Bush) | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98829 | 4163 | 6099 |  |  | 2006-01-25 05:10 | 2006-01-25 05:11 | 1 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98830 | 4164 | 6101 |  |  | 2006-01-26 13:16 | 2006-01-26 13:16 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98831 | 4165 | 6102 |  |  | 2006-01-27 02:00 | 2006-01-27 02:00 | 0 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98832 | 4166 | 6103 |  |  | 2006-01-27 03:13 | 2006-01-27 04:36 | 83 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98833 | 4167 | 6105 |  |  | 2006-01-27 10:36 | 2006-01-27 10:58 | 22 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98835 | 4169 | 6107 |  |  | 2006-01-27 12:41 | 2006-01-27 12:42 | 1 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98836 | 4170 | 6108 |  |  | 2006-01-27 13:14 | 2006-01-27 13:19 | 5 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98837 | 4171 | 6109 |  |  | 2006-01-27 14:20 | 2006-01-27 14:21 | 1 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98838 | 4172 | 6110 |  |  | 2006-01-27 17:51 | 2006-01-27 17:52 | 1 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98839 | 4173 | 6111 |  |  | 2006-01-28 04:35 | 2006-01-28 04:54 | 19 | E0489 | GT 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139202 | 4174 | 6112 |  |  | 2006-01-28 13:54 | 2006-01-28 13:55 | 1 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98841 | 4175 | 6113 |  |  | 2006-01-29 04:45 | 2006-01-29 04:45 | 0 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98842 | 4176 | 6114 |  |  | 2006-01-29 17:01 | 2006-01-29 17:01 | 0 | E0158 | MB 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98843 | 4177 | 6115 |  |  | 2006-01-29 18:35 | 2006-01-29 18:35 | 0 | E0639 | ST 22 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98844 | 4178 | 6116 |  |  | 2006-01-29 21:09 | 2006-01-29 21:09 | 0 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98845 | 4180 | 6118 |  |  | 2006-01-30 03:34 | 2006-01-30 03:34 | 0 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98846 | 4181 | 6119 |  |  | 2006-01-30 06:21 | 2006-01-30 06:21 | 0 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98848 | 4184 | 6123 |  |  | 2006-02-02 21:55 | 2006-02-02 21:55 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98849 | 4186 | 6125 |  |  | 2006-02-03 00:05 | 2006-02-03 00:05 | 0 | E0460 | KR 11 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98850 | 4189 | 6127 |  |  | 2006-02-04 03:43 | 2006-02-04 03:43 | 0 | E0273 | PM 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98851 | 4191 | 6129 |  |  | 2006-02-06 12:12 | 2006-02-06 12:12 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98852 | 4193 | 6131 |  |  | 2006-02-09 05:34 | 2006-02-09 05:34 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98853 | 4195 | 6133 |  |  | 2006-02-09 06:59 | 2006-02-09 06:59 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98854 | 4196 | 6134 |  |  | 2006-02-09 07:22 | 2006-02-09 07:22 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98855 | 4198 | 6135 |  |  | 2006-02-10 04:33 | 2006-02-10 04:33 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98856 | 4199 | 6136 |  |  | 2006-02-10 07:50 | 2006-02-10 07:50 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98857 | 4200 | 6137 |  |  | 2006-02-11 15:13 | 2006-02-11 15:13 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98858 | 4201 | 6138 |  |  | 2006-02-12 10:13 | 2006-02-12 10:13 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98859 | 4202 | 6139 |  |  | 2006-02-12 16:19 | 2006-02-12 16:19 | 0 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98860 | 4204 | 6141 |  |  | 2006-02-13 16:53 | 2006-02-13 16:53 | 0 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98861 | 4205 | 6122 |  |  | 2006-02-01 07:57 | 2006-02-01 15:15 | 438 | E0219 | RI 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98862 | 4206 | 6150 |  |  | 2006-02-19 17:00 | 2006-02-19 17:00 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98863 | 4207 | 6153 |  |  | 2006-02-21 06:33 | 2006-02-21 06:33 | 0 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98864 | 4209 | 1145 |  |  | 2006-02-07 14:14 | 2006-02-07 21:16 | 422 | E0538 | SH-FA 1 220 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR243 - SH-FA 1 and 2 220 kV interrupted due to poor risk assessment by Contractor. A swivel was passed through the bull wheel while erecting OPGW resulting in OPGW breaking and falling to ground. | FALSE | Critical
98865 | 4209 | 1145 |  |  | 2006-02-07 14:14 | 2006-02-07 21:20 | 426 | E0539 | SH-FA 2 220 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR243 - SH-FA 1 and 2 220 kV interrupted due to poor risk assessment by Contractor. A swivel was passed through the bull wheel while erecting OPGW resulting in OPGW breaking and falling to ground. | FALSE | Critical
98866 | 4211 | 1148 |  |  | 2006-02-20 11:45 | 2006-02-20 11:48 | 3 | E0240 | RI 11 kV T3 Feeder Circuit | Feeder | Fault | Switching Error | Transend | Completed | TRUE | 25 | TRUE |  | IR236 - Three 11 kV feeders (FZ9, FZ10, FZ11) tripped due to incorrect switching during planned work at the Risdon Substation. | FALSE | Undefined
98867 | 4211 | 1148 |  |  | 2006-02-20 11:45 | 2006-02-20 11:48 | 3 | E0241 | RI 11 kV U3 Feeder Circuit | Feeder | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR236 - Three 11 kV feeders (FZ9, FZ10, FZ11) tripped due to incorrect switching during planned work at the Risdon Substation. | FALSE | Undefined
98868 | 4211 | 1148 |  |  | 2006-02-20 11:45 | 2006-02-20 11:48 | 3 | E0242 | RI 11 kV V3 Feeder Circuit | Feeder | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR236 - Three 11 kV feeders (FZ9, FZ10, FZ11) tripped due to incorrect switching during planned work at the Risdon Substation. | FALSE | Undefined
98869 | 4212 | 1149 |  |  | 2006-02-27 18:03 | 2006-02-27 19:16 | 73 | E0776 | PL 110/22 kV T1 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 958 | TRUE |  | IR237 - Port Latta T1 transformer isolated due to protection operations resulting from incorrect protection settings applied prior to commissioning of new plant. | FALSE | Non-Critical
98870 | 4213 | 1147 |  |  | 2006-02-14 00:42 | 2006-02-15 12:08 | 2126 | E0794 | QT 110/22 kV T2 Transformer Circuit | Transformer | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR235 - Queenstown T2 transformer interrupted due to gas pressure trip. Root cause unknown. | FALSE | Non-Critical
98871 | 4214 | 1141 |  |  | 2006-01-27 10:43 | 2006-01-27 11:20 | 37 | E0228 | RI 11 kV A Bus | Bus | Fault | Switching Error | Transend | Completed | TRUE | 918 | TRUE |  | IR230 - Load shedding occurred at Risdon Substation due to incorrectly applied ScriptCalc during planned work. | FALSE | Undefined
98872 | 4214 | 1141 |  |  | 2006-01-27 10:43 | 2006-01-27 11:20 | 37 | E0229 | RI 11 kV B Bus | Bus | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR230 - Load shedding occurred at Risdon Substation due to incorrectly applied ScriptCalc during planned work. | FALSE | Undefined
98873 | 4214 | 1141 |  |  | 2006-01-27 10:43 | 2006-01-27 11:20 | 37 | E0230 | RI 11 kV C Bus | Bus | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR230 - Load shedding occurred at Risdon Substation due to incorrectly applied ScriptCalc during planned work. | FALSE | Undefined
98874 | 4214 | 1141 |  |  | 2006-01-27 10:43 | 2006-01-27 11:20 | 37 | E0231 | RI 11 kV D Bus | Bus | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR230 - Load shedding occurred at Risdon Substation due to incorrectly applied ScriptCalc during planned work. | FALSE | Undefined
98875 | 4215 | 6152 |  |  | 2006-02-21 05:18 | 2006-02-21 05:18 | 0 | E0910 | TR 22 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98876 | 4216 | 6151 |  |  | 2006-02-20 14:42 | 2006-02-20 14:59 | 17 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98878 | 4218 | 6142 |  |  | 2006-02-15 08:48 | 2006-02-15 08:49 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98879 | 4219 | 6143 |  |  | 2006-02-15 19:03 | 2006-02-15 19:20 | 17 | E0186 | TU 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98880 | 4220 | 6146 |  |  | 2006-02-17 08:07 | 2006-02-17 08:20 | 13 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98881 | 4221 | 6147 |  |  | 2006-02-17 11:09 | 2006-02-17 11:27 | 18 | E0356 | KI 11 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98882 | 4222 | 6148 |  |  | 2006-02-18 07:31 | 2006-02-18 07:31 | 0 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98883 | 4223 | 6149 |  |  | 2006-02-18 07:55 | 2006-02-18 07:55 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98885 | 4225 | 6154 |  |  | 2006-02-21 16:13 | 2006-02-21 16:13 | 0 | E0943 | UL 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98886 | 4226 | 6155 |  |  | 2006-02-22 23:58 | 2006-02-22 23:59 | 1 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98887 | 4227 | 6156 |  |  | 2006-02-23 05:42 | 2006-02-23 05:42 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98888 | 4228 | 6157 |  |  | 2006-02-23 21:47 | 2006-02-23 21:47 | 0 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98889 | 4229 | 6158 |  |  | 2006-02-25 07:36 | 2006-02-25 07:36 | 0 | E0970 | SO 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98890 | 4230 | 6159 |  |  | 2006-02-26 16:51 | 2006-02-26 16:51 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98891 | 4231 | 6160 |  |  | 2006-02-26 10:00 | 2006-02-26 10:00 | 0 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98892 | 4232 | 6161 |  |  | 2006-02-26 22:57 | 2006-02-26 22:57 | 0 | E0495 | GT 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98893 | 4233 | 6162 |  |  | 2006-02-27 01:22 | 2006-02-27 01:22 | 0 | E0601 | DP 22 kV XC2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98894 | 4234 | 6163 |  |  | 2006-02-27 06:04 | 2006-02-27 06:04 | 0 | E0766 | NW 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98895 | 4236 | 6165 |  |  | 2006-02-28 01:15 | 2006-02-28 01:15 | 0 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98896 | 4237 | 6166 |  |  | 2006-02-28 07:06 | 2006-02-28 07:06 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98897 | 4238 | 6167 |  |  | 2006-02-28 07:06 | 2006-02-28 07:06 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98898 | 4239 | 6168 |  |  | 2006-03-04 15:09 | 2006-03-04 15:09 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
187047 | 4240 | 6169 |  |  | 2006-03-06 06:01 | 2006-03-06 06:03 | 2 | E0158 | MB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98899 | 4241 | 6170 |  |  | 2006-03-06 11:23 | 2006-03-06 12:16 | 53 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98900 | 4242 | 6171 |  |  | 2006-02-06 13:04 | 2006-02-06 13:20 | 16 | E0844 | RK 11 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98901 | 4247 | 6176 |  |  | 2006-03-08 02:14 | 2006-03-08 02:14 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139203 | 4249 | 6178 |  |  | 2006-03-09 08:12 | 2006-03-09 08:12 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98905 | 4250 | 6180 |  |  | 2006-03-10 19:06 | 2006-03-10 19:06 | 0 | E0760 | NW 22 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98906 | 4251 | 6181 |  |  | 2006-03-11 03:16 | 2006-03-11 03:16 | 0 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98907 | 4252 | 6182 |  |  | 2006-03-11 11:28 | 2006-03-11 11:45 | 17 | E0450 | KE 11 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98908 | 4253 | 6183 |  |  | 2006-03-12 02:31 | 2006-03-12 02:31 | 0 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98909 | 4254 | 6184 |  |  | 2006-03-12 05:09 | 2006-03-12 05:09 | 0 | E0606 | DP 22 kV XH2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98910 | 4255 | 6185 |  |  | 2006-03-13 02:24 | 2006-03-13 02:24 | 0 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98911 | 4256 | 6186 |  |  | 2006-03-14 01:30 | 2006-03-14 01:31 | 1 | E0300 | AV 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139204 | 4257 | 6187 |  |  | 2006-03-14 08:32 | 2006-03-14 08:32 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98913 | 4258 | 6189 |  |  | 2006-03-15 12:08 | 2006-03-15 12:26 | 18 | E0883 | X-SR 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98914 | 4259 | 6190 |  |  | 2006-03-15 20:42 | 2006-03-15 20:42 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98915 | 4260 | 6191 |  |  | 2006-03-16 02:01 | 2006-03-16 02:01 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98916 | 4261 | 6192 |  |  | 2006-03-16 06:36 | 2006-03-16 06:43 | 7 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98917 | 4263 | 6193 |  |  | 2006-03-16 08:47 | 2006-03-16 10:00 | 73 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98918 | 4264 | 6194 |  |  | 2006-03-16 13:02 | 2006-03-16 13:24 | 22 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98919 | 4265 | 6195 |  |  | 2006-03-16 11:35 | 2006-03-16 12:23 | 48 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98920 | 4266 | 6196 |  |  | 2006-03-16 13:36 | 2006-03-16 13:37 | 1 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139205 | 4268 | 6197 |  |  | 2006-03-16 13:37 | 2006-03-16 13:37 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98922 | 4269 | 6198 |  |  | 2006-03-16 14:32 | 2006-03-16 14:32 | 0 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98923 | 4270 | 6199 |  |  | 2006-03-16 14:35 | 2006-03-16 14:35 | 0 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98924 | 4271 | 6200 |  |  | 2006-03-16 13:49 | 2006-03-16 15:27 | 98 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98925 | 4272 | 6201 |  |  | 2006-03-16 16:11 | 2006-03-16 16:11 | 0 | E0197 | SO 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98926 | 4273 | 6202 |  |  | 2006-03-16 23:45 | 2006-03-16 23:45 | 0 | E0912 | TR 22 kV T2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98928 | 4274 | 1152 |  |  | 2006-03-16 16:11 | 2006-03-16 17:34 | 83 | E0193 | SO 110/22 kV T2 Transformer Circuit | Transformer | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR256 - LF-SO-TB 110 kV tripped and reclosed during lightning storm. Sorell T2 experienced sustained interruption due to operation of undervoltage protection and operation of auto-close scheme on 22 kV 'B' bus. There was no loss of supply. | FALSE | Non-Critical
98927 | 4274 | 1152 |  |  | 2006-03-16 16:11 | 2006-03-16 16:11 | 0 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR256 - LF-SO-TB 110 kV tripped and reclosed during lightning storm. Sorell T2 experienced sustained interruption due to operation of undervoltage protection and operation of auto-close scheme on 22 kV 'B' bus. There was no loss of supply. | FALSE | Non-Critical
98929 | 4275 | 6203 |  |  | 2006-03-18 23:36 | 2006-03-18 23:36 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98930 | 4276 | 6204 |  |  | 2006-03-20 06:47 | 2006-03-20 06:47 | 0 | E0820 | RA 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98931 | 4277 | 6205 |  |  | 2006-03-20 22:46 | 2006-03-20 23:15 | 29 | E0600 | DP 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98933 | 4280 | 1153 |  |  | 2006-03-17 12:08 | 2006-03-17 12:15 | 7 | E0228 | RI 11 kV A Bus | Bus | Fault | Switching Error | Transend | Completed | TRUE | 285 | TRUE |  | IR263 - Load shed within Zinifex installation due to ScriptCalc switching error in control room. | FALSE | Undefined
98934 | 4280 | 1153 |  |  | 2006-03-17 12:08 | 2006-03-17 12:15 | 7 | E0229 | RI 11 kV B Bus | Bus | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR263 - Load shed within Zinifex installation due to ScriptCalc switching error in control room. | FALSE | Undefined
98935 | 4280 | 1153 |  |  | 2006-03-17 12:08 | 2006-03-17 12:15 | 7 | E0230 | RI 11 kV C Bus | Bus | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR263 - Load shed within Zinifex installation due to ScriptCalc switching error in control room. | FALSE | Undefined
98936 | 4280 | 1153 |  |  | 2006-03-17 12:08 | 2006-03-17 12:15 | 7 | E0231 | RI 11 kV D Bus | Bus | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR263 - Load shed within Zinifex installation due to ScriptCalc switching error in control room. | FALSE | Undefined
98937 | 4281 | 1154 |  |  | 2006-03-17 14:55 | 2006-03-17 14:56 | 1 | E0401 | BU-PL 110 kV Transmission Circuit | Transmission | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR264 - BU-PL 110 kV interrupted due to incorrect circuit breaker autoreclose point mapping. | FALSE | Non-Critical
98938 | 4282 | 1150 |  |  | 2006-03-01 08:15 | 2006-03-01 08:23 | 8 | E0376 | BU 110 kV B Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 153 | TRUE |  | IR238 - Burnie Substation 110 kV 'B' bus and Smithton Substation interrupted during planned work due to protection scheme design error. | FALSE | Undefined
98944 | 4987 | 6206 |  |  | 2006-03-22 20:23 | 2006-03-22 20:23 | 0 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98945 | 4988 | 6207 |  |  | 2006-03-23 03:48 | 2006-03-23 03:48 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98946 | 4989 | 6209 |  |  | 2006-03-23 23:43 | 2006-03-23 23:43 | 0 | E0888 | DE 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98947 | 4990 | 6210 |  |  | 2006-03-25 08:39 | 2006-03-25 08:39 | 0 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98948 | 4991 | 6211 |  |  | 2006-03-25 20:22 | 2006-03-25 20:22 | 0 | E0389 | BU 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98949 | 4991 | 6211 |  |  | 2006-03-25 20:22 | 2006-03-25 20:22 | 0 | E1000 | BU 22 kV K2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98950 | 4992 | 6212 |  |  | 2006-03-27 03:46 | 2006-03-27 04:38 | 52 | E0744 | NH 11 kV P2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98951 | 4994 | 6213 |  |  | 2006-03-28 02:08 | 2006-03-28 02:08 | 0 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98952 | 4995 | 6214 |  |  | 2006-03-28 13:07 | 2006-03-28 14:18 | 71 | E0413 | EL 11 kV XC2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98953 | 4996 | 6215 |  |  | 2006-03-28 13:07 | 2006-03-28 14:30 | 83 | E0412 | EL 11 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98954 | 4997 | 6216 |  |  | 2006-03-28 16:19 | 2006-03-28 16:37 | 18 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98955 | 4998 | 6217 |  |  | 2006-03-28 16:34 | 2006-03-28 16:34 | 0 | E0760 | NW 22 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98956 | 4999 | 6218 |  |  | 2006-03-28 22:50 | 2006-03-28 22:50 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98957 | 5000 | 6219 |  |  | 2006-03-29 06:22 | 2006-03-29 06:23 | 1 | E0273 | PM 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98958 | 5001 | 6208 |  |  | 2006-03-23 11:11 | 2006-03-23 11:11 | 0 | E0604 | DP 22 kV XF2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98959 | 5002 | 6223 |  |  | 2006-03-30 20:05 | 2006-03-30 20:05 | 0 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98960 | 5003 | 6222 |  |  | 2006-03-30 15:31 | 2006-03-30 15:31 | 0 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139206 | 5004 | 6221 |  |  | 2006-03-29 22:48 | 2006-03-29 22:48 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98962 | 5005 | 6220 |  |  | 2006-03-29 09:02 | 2006-03-29 09:02 | 0 | E0917 | TR 22 kV X2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98963 | 5006 | 1155 |  |  | 2006-04-02 01:21 | 2006-04-02 14:54 | 813 | E0001 | WA-BW 110 kV Transmission Circuit | Transmission | Fault | Fatigue | Transend | Completed | TRUE | 0 | TRUE |  | IR267 - WA-BW 110 kV interrupted due to broken clevis thimble causing conductor to fall to ground. | FALSE | Non-Critical
98964 | 5063 | 6224 |  |  | 2006-04-01 06:32 | 2006-04-01 06:52 | 20 | E0496 | GT 22 kV N2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98965 | 5064 | 6225 |  |  | 2006-04-01 23:46 | 2006-04-01 23:46 | 0 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98966 | 5065 | 6226 |  |  | 2006-04-02 18:55 | 2006-04-02 18:56 | 1 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98967 | 5066 | 6227 |  |  | 2006-04-02 19:38 | 2006-04-02 19:39 | 1 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98968 | 5067 | 6228 |  |  | 2006-04-03 11:17 | 2006-04-03 12:13 | 56 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98969 | 5068 | 6229 |  |  | 2006-04-04 06:38 | 2006-04-04 06:38 | 0 | E0605 | DP 22 kV XG2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98970 | 5069 | 6230 |  |  | 2006-04-04 09:25 | 2006-04-04 10:31 | 66 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98971 | 5070 | 6232 |  |  | 2006-04-04 14:11 | 2006-04-04 14:19 | 8 | E0287 | PM 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98972 | 5071 | 6233 |  |  | 2006-04-04 19:40 | 2006-04-04 19:40 | 0 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98973 | 5072 | 6234 |  |  | 2006-04-04 20:37 | 2006-04-04 20:37 | 0 | E0300 | AV 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98974 | 5073 | 6235 |  |  | 2006-04-05 04:48 | 2006-04-05 04:48 | 0 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98975 | 5074 | 6236 |  |  | 2006-04-05 05:04 | 2006-04-05 05:04 | 0 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98976 | 5086 | 6240 |  |  | 2006-04-06 10:12 | 2006-04-06 12:53 | 161 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98977 | 5087 | 6241 |  |  | 2006-04-06 10:56 | 2006-04-06 11:33 | 37 | E0640 | ST 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98978 | 5088 | 6239 |  |  | 2006-04-06 08:42 | 2006-04-06 08:43 | 1 | E0273 | PM 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98979 | 5089 | 6238 |  |  | 2006-04-05 19:38 | 2006-04-05 19:38 | 0 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98980 | 5090 | 6237 |  |  | 2006-04-05 19:38 | 2006-04-05 19:38 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
119429 | 5091 | 1158 |  |  | 2006-04-05 10:55 | 2006-04-05 11:02 | 7 | E0515 | SH-GT 1 220 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR269 - SH-GT 1 220 kV interrupted due to human error during protection testing at George Town Substation. | FALSE | Critical
98981 | 5092 | 1159 |  |  | 2006-04-08 12:44 | 2006-04-08 13:48 | 64 | E0485 | GT 22 kV A Bus | Bus | Fault | Unknown | Transend | Completed | TRUE | 498 | TRUE |  | IR270 - George Town Substation 22 kV 'A' Bus interrupted. 22 kV circuit breaker (E252) failure. Under investigation by manufacturer. | FALSE | Undefined
98982 | 5093 | 6255 |  |  | 2006-04-13 09:46 | 2006-04-13 10:38 | 52 | E0085 | CR 33 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98983 | 5094 | 6254 |  |  | 2006-04-12 15:49 | 2006-04-12 15:53 | 4 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98984 | 5095 | 6251 |  |  | 2006-04-09 22:45 | 2006-04-09 23:32 | 47 | E0768 | NW 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98985 | 5096 | 6253 |  |  | 2006-04-09 23:16 | 2006-04-09 23:16 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98986 | 5097 | 6252 |  |  | 2006-04-09 23:13 | 2006-04-09 23:13 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139207 | 5098 | 6250 |  |  | 2006-04-09 22:21 | 2006-04-09 22:37 | 16 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98988 | 5099 | 6249 |  |  | 2006-04-11 12:02 | 2006-04-11 16:39 | 277 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98989 | 5101 | 6247 |  |  | 2006-04-09 13:46 | 2006-04-09 14:34 | 48 | E0744 | NH 11 kV P2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98990 | 5102 | 6246 |  |  | 2006-04-08 13:59 | 2006-04-08 14:23 | 24 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98991 | 5103 | 6245 |  |  | 2006-04-08 13:58 | 2006-04-08 13:58 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98996 | 5104 | 6244 |  |  | 2006-04-08 12:44 | 2006-04-08 13:57 | 73 | E0492 | GT 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98993 | 5104 | 6244 |  |  | 2006-04-08 12:44 | 2006-04-08 13:57 | 73 | E0489 | GT 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98994 | 5104 | 6244 |  |  | 2006-04-08 12:44 | 2006-04-08 13:57 | 73 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98995 | 5104 | 6244 |  |  | 2006-04-08 12:44 | 2006-04-08 13:57 | 73 | E0491 | GT 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98992 | 5104 | 6244 |  |  | 2006-04-08 12:44 | 2006-04-08 13:57 | 73 | E0488 | GT 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98997 | 5105 | 6243 |  |  | 2006-04-07 17:42 | 2006-04-07 17:42 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98998 | 5106 | 6242 |  |  | 2006-04-07 08:24 | 2006-04-07 08:24 | 0 | E0970 | SO 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
98999 | 5107 | 1160 |  |  | 2006-04-23 12:37 | 2006-04-23 12:55 | 18 | E0406 | FA-QU-SR-HM 110 kV Transmission Circuit | Transmission | Fault | Internal Fault | Transend | Completed | TRUE | 495 | TRUE |  | IR276 - FA-QU-SR-HM 110 kV interrupted. LV feeder fault (tree across feeder) at Que Substation caused transmission line protection to operate. Cause of maloperation unknown. | FALSE | Non-Critical
99000 | 5108 | 6256 |  |  | 2006-04-14 20:42 | 2006-04-14 20:42 | 0 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99001 | 5109 | 6257 |  |  | 2006-04-14 23:10 | 2006-04-14 23:10 | 0 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99002 | 5110 | 6258 |  |  | 2006-04-14 22:36 | 2006-04-14 22:36 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99004 | 5112 | 6259 |  |  | 2006-04-15 01:36 | 2006-04-15 01:36 | 0 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99005 | 5113 | 6260 |  |  | 2006-04-16 02:37 | 2006-04-16 02:37 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139208 | 5114 | 6261 |  |  | 2006-04-16 16:46 | 2006-04-16 16:46 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99007 | 5115 | 6262 |  |  | 2006-04-17 01:21 | 2006-04-17 01:21 | 0 | E0865 | RB 44 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99008 | 5116 | 6263 |  |  | 2006-04-18 02:08 | 2006-04-18 03:30 | 82 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99009 | 5117 | 6264 |  |  | 2006-04-18 03:07 | 2006-04-18 03:07 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99010 | 5118 | 6265 |  |  | 2006-04-18 03:13 | 2006-04-18 05:30 | 137 | E0820 | RA 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99011 | 5120 | 6267 |  |  | 2006-04-18 04:17 | 2006-04-18 05:55 | 98 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99012 | 5121 | 6268 |  |  | 2006-04-18 04:59 | 2006-04-18 07:35 | 156 | E0219 | RI 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
118384 | 5122 | 6269 |  |  | 2006-04-18 04:59 | 2006-04-18 07:09 | 130 | E0221 | RI 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99014 | 5123 | 6270 |  |  | 2006-04-18 04:59 | 2006-04-18 07:36 | 157 | E0224 | RI 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99015 | 5124 | 6271 |  |  | 2006-04-18 04:59 | 2006-04-18 10:33 | 334 | E0225 | RI 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99016 | 5125 | 6272 |  |  | 2006-04-19 05:49 | 2006-04-19 05:49 | 0 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99017 | 5126 | 6273 |  |  | 2006-04-19 07:15 | 2006-04-19 07:15 | 0 | E0464 | KR 11 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99018 | 5127 | 6274 |  |  | 2006-04-19 19:14 | 2006-04-19 19:43 | 29 | E0760 | NW 22 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99019 | 5128 | 6276 |  |  | 2006-04-20 00:06 | 2006-04-20 00:23 | 17 | E0910 | TR 22 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99020 | 5129 | 6277 |  |  | 2006-04-20 11:30 | 2006-04-20 11:30 | 0 | E0869 | RB 44 kV E4 Circuit Breaker | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99021 | 5130 | 6278 |  |  | 2006-04-20 18:22 | 2006-04-20 18:22 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99022 | 5131 | 6279 |  |  | 2006-04-21 09:08 | 2006-04-21 09:25 | 17 | E0342 | LF 33 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99023 | 5132 | 6280 |  |  | 2006-04-22 12:20 | 2006-04-22 12:20 | 0 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99024 | 5133 | 6281 |  |  | 2006-04-22 15:29 | 2006-04-22 15:46 | 17 | E0122 | CS 11 kV X2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99025 | 5134 | 6282 |  |  | 2006-04-22 17:35 | 2006-04-22 17:53 | 18 | E0122 | CS 11 kV X2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99026 | 5135 | 6283 |  |  | 2006-04-23 21:43 | 2006-04-23 22:02 | 19 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99027 | 5137 | 6285 |  |  | 2006-04-24 13:58 | 2006-04-24 14:21 | 23 | E0109 | CS 11 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99028 | 5138 | 6286 |  |  | 2006-04-24 17:49 | 2006-04-24 19:00 | 71 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99029 | 5139 | 6287 |  |  | 2006-04-25 03:55 | 2006-04-25 05:40 | 105 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99030 | 5140 | 6288 |  |  | 2006-04-25 09:18 | 2006-04-25 10:12 | 54 | E0943 | UL 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99031 | 5141 | 6289 |  |  | 2006-04-25 10:41 | 2006-04-25 11:24 | 43 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99032 | 5142 | 6290 |  |  | 2006-04-25 21:56 | 2006-04-25 21:57 | 1 | E0638 | ST 22 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99033 | 5143 | 6291 |  |  | 2006-04-25 21:56 | 2006-04-25 21:57 | 1 | E0644 | ST 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99034 | 5145 | 6293 |  |  | 2006-04-27 13:39 | 2006-04-27 15:10 | 91 | E0902 | TR 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99045 | 5203 | 6295 |  |  | 2006-04-29 21:44 | 2006-04-29 21:44 | 0 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99046 | 5204 | 6297 |  |  | 2006-05-01 21:12 | 2006-05-01 21:38 | 26 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99047 | 5205 | 6231 |  |  | 2006-04-04 09:07 | 2006-04-04 15:36 | 389 | E0912 | TR 22 kV T2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99048 | 5206 | 6294 |  |  | 2006-04-27 18:20 | 2006-04-28 08:55 | 875 | E0219 | RI 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99049 | 5208 | 6301 |  |  | 2006-05-03 15:20 | 2006-05-03 15:56 | 36 | E0604 | DP 22 kV XF2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99050 | 5209 | 6298 |  |  | 2006-05-02 18:32 | 2006-05-02 19:24 | 52 | E0225 | RI 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99051 | 5210 | 6299 |  |  | 2006-05-03 00:40 | 2006-05-03 00:40 | 0 | E0869 | RB 44 kV E4 Circuit Breaker | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99052 | 5211 | 6307 |  |  | 2006-05-09 09:12 | 2006-05-09 10:32 | 80 | E0415 | EL 11 kV XE2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99053 | 5212 | 6302 |  |  | 2006-05-06 23:18 | 2006-05-06 23:18 | 0 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99054 | 5214 | 6306 |  |  | 2006-05-07 04:54 | 2006-05-07 06:39 | 105 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99055 | 5215 | 6305 |  |  | 2006-05-07 04:23 | 2006-05-07 08:58 | 275 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99056 | 5216 | 6304 |  |  | 2006-05-07 03:25 | 2006-05-07 03:25 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99058 | 5310 | 6308 |  |  | 2006-05-15 01:11 | 2006-05-15 01:12 | 1 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99059 | 5311 | 6309 |  |  | 2006-05-15 10:43 | 2006-05-15 10:44 | 1 | E0638 | ST 22 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99060 | 5312 | 6310 |  |  | 2006-05-15 12:30 | 2006-05-15 13:11 | 41 | E0863 | RB 44 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99071 | 5337 | 6312 |  |  | 2006-05-17 13:11 | 2006-05-17 14:10 | 59 | E0489 | GT 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99072 | 5338 | 6313 |  |  | 2006-05-18 12:43 | 2006-05-18 12:43 | 0 | E0104 | CS 11 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99073 | 5339 | 6314 |  |  | 2006-05-19 10:45 | 2006-05-19 17:44 | 419 | E0023 | BW 11 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99074 | 5340 | 6315 |  |  | 2006-05-21 22:15 | 2006-05-21 22:15 | 0 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99075 | 5341 | 6316 |  |  | 2006-05-21 22:15 | 2006-05-21 22:35 | 20 | E1001 | BU 22 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99076 | 5342 | 6317 |  |  | 2006-05-22 01:23 | 2006-05-22 01:23 | 0 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99077 | 5344 | 6319 |  |  | 2006-05-22 16:26 | 2006-05-22 16:26 | 0 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99078 | 5345 | 6266 |  |  | 2006-04-18 03:49 | 2006-04-18 07:36 | 227 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99079 | 5347 | 1163 |  |  | 2006-05-25 13:43 | 2006-05-25 14:59 | 76 | E0261 | PO-PM 3 220 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR301 - Poatina-Palmerston No 3 220 kV transmission circuit interrupted due to loose relay wiring associated with the 220 kV 'A' bus VT A797 at the Palmerston Substation. | FALSE | Non-Critical
99080 | 5348 | 6303 |  |  | 2006-05-07 03:07 | 2006-05-07 06:24 | 197 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99081 | 5349 | 6300 |  |  | 2006-05-03 13:54 | 2006-05-03 14:27 | 33 | E0839 | RK 11 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99091 | 5482 | 1164 |  |  | 2006-05-29 17:19 | 2006-05-29 17:29 | 10 | E0352 | LF 110 kV C1 Capacitor Circuit | Capacitor | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR302: Lindisfarne Substation - Capacitor C1 isolated due to control cable fault while removing redundant equipment. | FALSE | Non-Critical
99092 | 5493 | 6324 |  |  | 2006-06-01 09:29 | 2006-06-01 09:29 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99093 | 5494 | 6322 |  |  | 2006-05-31 21:21 | 2006-05-31 21:21 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99102 | 5495 | 1162 |  |  | 2006-05-23 07:59 | 2006-05-23 08:35 | 36 | E1007 | BY 110 kV A Bus | Bus | Fault | NEMMCO | NEMMCO | Completed | TRUE | 0 | TRUE |  | IR300 - UFLS initiated at Comalco, Zinifex, Temco and Boyer due to drop in system frequency resulting from Generator and NEMMCO activities. | FALSE | Undefined
99103 | 5495 | 1162 |  |  | 2006-05-23 07:59 | 2006-05-23 08:35 | 36 | E1008 | BY 110 kV B Bus | Bus | Fault | NEMMCO | NEMMCO | Completed | TRUE | 0 | TRUE |  | IR300 - UFLS initiated at Comalco, Zinifex, Temco and Boyer due to drop in system frequency resulting from Generator and NEMMCO activities. | FALSE | Undefined
99095 | 5495 | 1162 |  |  | 2006-05-23 07:59 | 2006-05-23 08:31 | 32 | E0229 | RI 11 kV B Bus | Bus | Fault | NEMMCO | NEMMCO | Completed | TRUE | 0 | TRUE |  | IR300 - UFLS initiated at Comalco, Zinifex, Temco and Boyer due to drop in system frequency resulting from Generator and NEMMCO activities. | FALSE | Undefined
99096 | 5495 | 1162 |  |  | 2006-05-23 07:59 | 2006-05-23 08:31 | 32 | E0230 | RI 11 kV C Bus | Bus | Fault | NEMMCO | NEMMCO | Completed | TRUE | 0 | TRUE |  | IR300 - UFLS initiated at Comalco, Zinifex, Temco and Boyer due to drop in system frequency resulting from Generator and NEMMCO activities. | FALSE | Undefined
99097 | 5495 | 1162 |  |  | 2006-05-23 07:59 | 2006-05-23 08:31 | 32 | E0231 | RI 11 kV D Bus | Bus | Fault | NEMMCO | NEMMCO | Completed | TRUE | 0 | TRUE |  | IR300 - UFLS initiated at Comalco, Zinifex, Temco and Boyer due to drop in system frequency resulting from Generator and NEMMCO activities. | FALSE | Undefined
99094 | 5495 | 1162 |  |  | 2006-05-23 07:59 | 2006-05-23 08:31 | 32 | E0228 | RI 11 kV A Bus | Bus | Fault | NEMMCO | NEMMCO | Completed | TRUE | 0 | TRUE |  | IR300 - UFLS initiated at Comalco, Zinifex, Temco and Boyer due to drop in system frequency resulting from Generator and NEMMCO activities. | FALSE | Undefined
99101 | 5495 | 1162 |  |  | 2006-05-23 07:59 | 2006-05-23 08:24 | 25 | E0514 | GT-TE 2 110 kV Transmission Circuit | Transmission | Fault | NEMMCO | NEMMCO | Completed | TRUE | 0 | TRUE |  | IR300 - UFLS initiated at Comalco, Zinifex, Temco and Boyer due to drop in system frequency resulting from Generator and NEMMCO activities. | FALSE | Non-Critical
99098 | 5495 | 1162 |  |  | 2006-05-23 07:59 | 2006-05-23 08:17 | 18 | E0510 | GT-CO 4 220 kV Transmission Circuit | Transmission | Fault | NEMMCO | NEMMCO | Completed | TRUE | 6312 | TRUE |  | IR300 - UFLS initiated at Comalco, Zinifex, Temco and Boyer due to drop in system frequency resulting from Generator and NEMMCO activities. | FALSE | Non-Critical
99099 | 5495 | 1162 |  |  | 2006-05-23 07:59 | 2006-05-23 08:17 | 18 | E0511 | GT-CO 5 220 kV Transmission Circuit | Transmission | Fault | NEMMCO | NEMMCO | Completed | TRUE | 0 | TRUE |  | IR300 - UFLS initiated at Comalco, Zinifex, Temco and Boyer due to drop in system frequency resulting from Generator and NEMMCO activities. | FALSE | Non-Critical
99100 | 5495 | 1162 |  |  | 2006-05-23 07:59 | 2006-05-23 08:24 | 25 | E0513 | GT-TE 1 110 kV Transmission Circuit | Transmission | Fault | NEMMCO | NEMMCO | Completed | TRUE | 0 | TRUE |  | IR300 - UFLS initiated at Comalco, Zinifex, Temco and Boyer due to drop in system frequency resulting from Generator and NEMMCO activities. | FALSE | Non-Critical
99104 | 5496 | 6333 |  |  | 2006-06-05 18:53 | 2006-06-05 18:53 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99105 | 5497 | 6334 |  |  | 2006-06-06 07:21 | 2006-06-06 07:38 | 17 | E0111 | CS 11 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99106 | 5498 | 6327 |  |  | 2006-06-02 22:01 | 2006-06-02 22:59 | 58 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99107 | 5499 | 6326 |  |  | 2006-06-02 22:01 | 2006-06-02 22:52 | 51 | E0906 | TR 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99108 | 5500 | 6328 |  |  | 2006-06-02 22:01 | 2006-06-02 23:01 | 60 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99109 | 5501 | 6329 |  |  | 2006-06-02 22:01 | 2006-06-02 23:02 | 61 | E0910 | TR 22 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99110 | 5502 | 6330 |  |  | 2006-06-03 19:47 | 2006-06-03 19:47 | 0 | E0156 | MB 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99111 | 5503 | 6331 |  |  | 2006-06-04 01:02 | 2006-06-04 01:06 | 4 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99114 | 5557 | 1165 |  |  | 2006-06-02 22:01 | 2006-06-02 22:46 | 45 | E0696 | TR 22 kV B Bus | Bus | Fault | DNSP | Transend | Completed | TRUE | 783 | TRUE |  | IR313 - Trevallyn 22 kV 'B' Bus isolated due to failure by DNSP Operators to follow agreed feeder earthing practices during planned work. | FALSE | Undefined
99117 | 5558 | 1167 |  |  | 2006-06-08 11:47 | 2006-06-08 12:00 | 13 | E0779 | PL 22 kV B2 Feeder Circuit | Feeder | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR315 - Burnie-Port Latta 110 kV, Port Latta transformer T2 and two 22 kV feeders interrupted due to a commissioning error resulting from incorrect optical fibre labelling. | FALSE | Undefined
99115 | 5558 | 1167 |  |  | 2006-06-08 11:47 | 2006-06-08 11:52 | 5 | E0401 | BU-PL 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 79 | TRUE |  | IR315 - Burnie-Port Latta 110 kV, Port Latta transformer T2 and two 22 kV feeders interrupted due to a commissioning error resulting from incorrect optical fibre labelling. | FALSE | Non-Critical
99116 | 5558 | 1167 |  |  | 2006-06-08 11:47 | 2006-06-08 11:56 | 9 | E0777 | PL 110/22 kV T2 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR315 - Burnie-Port Latta 110 kV, Port Latta transformer T2 and two 22 kV feeders interrupted due to a commissioning error resulting from incorrect optical fibre labelling. | FALSE | Non-Critical
99118 | 5569 | 6337 |  |  | 2006-06-12 09:34 | 2006-06-12 11:44 | 130 | E0273 | PM 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99119 | 5570 | 6336 |  |  | 2006-06-11 13:56 | 2006-06-11 13:56 | 0 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99120 | 5571 | 6335 |  |  | 2006-06-06 20:05 | 2006-06-06 20:05 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99121 | 5572 | 6338 |  |  | 2006-06-13 10:41 | 2006-06-13 18:06 | 445 | E0083 | CR 33 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99122 | 5573 | 6344 |  |  | 2006-06-15 19:38 | 2006-06-15 19:38 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99123 | 5575 | 6340 |  |  | 2006-06-14 13:22 | 2006-06-14 13:22 | 0 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99124 | 5576 | 6339 |  |  | 2006-06-14 09:33 | 2006-06-14 09:33 | 0 | E0902 | TR 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99125 | 5577 | 6346 |  |  | 2006-06-18 09:10 | 2006-06-18 09:10 | 0 | E0273 | PM 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99126 | 5578 | 6345 |  |  | 2006-06-18 08:11 | 2006-06-18 08:11 | 0 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99132 | 5643 | 1169 |  |  | 2006-06-28 07:15 | 2006-06-28 11:00 | 225 | E0400 | BU-HM 110 kV Transmission Circuit | Transmission | Fault | Wildlife | Transend | Completed | TRUE | 40 | TRUE |  | IR325 - BU-HM 110 kV interrupted due to bird streamer causing insulator flashover at tower 78. | FALSE | Non-Critical
99133 | 5645 | 1170 |  |  | 2006-06-28 12:40 | 2006-06-28 13:41 | 61 | E0284 | PM 22 kV B Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 369 | TRUE |  | IR326 - Supply interrupted to Palmerston Substation 22 kV 'B' bus due to incorrect SCADA configuration applied by Contractor during pre-commissioning. | FALSE | Undefined
99134 | 5646 | 1168 |  |  | 2006-06-22 16:35 | 2006-06-22 21:42 | 307 | E0717 | FA-RC 2 220 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR324 - FA-RC No 2 220 kV interrupted due to intertrip received from Reece Power Station due to Hydro equipment failure. | FALSE | Non-Critical
99135 | 5647 | 6343 |  |  | 2006-06-15 14:34 | 2006-06-15 14:57 | 23 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 13 | TRUE |  | IR322 - 22 kV Feeder No. 2 at Meadowbank Substation interrupted due to Contractor striking underground cable during post hole excavations. | FALSE | Undefined
99136 | 5648 | 1171 |  |  | 2006-07-05 19:29 | 2006-07-05 19:51 | 22 | E0290 | PO-PM 2 110 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR327 - Supply interruption to PO-PM No 2 110 kV due to intertrip signal received from Poatina Power Station during load rejection tests being performed by Generator. | FALSE | Non-Critical
99139 | 5680 | 1172 |  |  | 2006-07-09 14:33 | 2006-07-09 14:46 | 13 | E1427 | HA 22 kV B Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 140 | TRUE |  | IR328 - Hadspen Substation 22 kV 'B' Bus interrupted due to poor secondary isolation processes utilised by Contractor while downloading feeder protection configuration. | FALSE | Undefined
99140 | 5682 | 6348 |  |  | 2006-06-21 14:28 | 2006-06-21 15:14 | 46 | E0273 | PM 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99141 | 5683 | 6349 |  |  | 2006-06-21 20:47 | 2006-06-22 18:53 | 1326 | E1052 | SR 22 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99142 | 5684 | 6350 |  |  | 2006-06-21 20:55 | 2006-06-22 18:52 | 1317 | E1029 | SR 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99143 | 5685 | 6351 |  |  | 2006-06-22 18:17 | 2006-06-22 19:06 | 49 | E0746 | NH 11 kV R2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99144 | 5686 | 6352 |  |  | 2006-06-25 15:56 | 2006-06-25 15:57 | 1 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99145 | 5687 | 6353 |  |  | 2006-06-28 12:39 | 2006-06-28 14:23 | 104 | E0278 | PM 22 kV A8 Bus Coupler Circuit | Bus Coupler | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR326 - 22 kV bus coupler circuit breaker A852 tripped at Palmerston Substation during commissioning due to an incorrect SCADA address in the local HMI. | FALSE | Undefined
99146 | 5688 | 6354 |  |  | 2006-07-01 01:31 | 2006-07-01 01:49 | 18 | E0738 | NH 11 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99147 | 5689 | 6355 |  |  | 2006-07-01 02:31 | 2006-07-01 02:52 | 21 | E1041 | SD 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99148 | 5690 | 6356 |  |  | 2006-07-01 07:27 | 2006-07-01 07:28 | 1 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99149 | 5691 | 6357 |  |  | 2006-07-02 01:49 | 2006-07-02 01:49 | 0 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99150 | 5692 | 6358 |  |  | 2006-07-02 18:09 | 2006-07-02 18:09 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99151 | 5693 | 6365 |  |  | 2006-07-11 03:22 | 2006-07-11 03:22 | 0 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99152 | 5694 | 6359 |  |  | 2006-07-05 16:20 | 2006-07-05 16:20 | 0 | E0273 | PM 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99153 | 5695 | 6360 |  |  | 2006-07-05 16:55 | 2006-07-05 18:15 | 80 | E0602 | DP 22 kV XD2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99154 | 5696 | 6361 |  |  | 2006-07-05 18:15 | 2006-07-05 19:36 | 81 | E0602 | DP 22 kV XD2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99155 | 5697 | 6363 |  |  | 2006-07-06 10:18 | 2006-07-06 10:53 | 35 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99156 | 5698 | 6364 |  |  | 2006-07-09 13:22 | 2006-07-09 13:35 | 13 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 48 | TRUE |  | IR328 - Hadspen Substation 22 kV feeder M252 interrupted due to poor secondary isolation processes by Contractor while downloading feeder protection configuration. | FALSE | Undefined
99157 | 5699 | 1173 |  |  | 2006-07-11 21:23 | 2006-07-11 21:27 | 4 | E0027 | LI-CL-RE-CS 1 220 kV Transmission Circuit (Changed to E1958) | Transmission | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR329 - LI-CL-RE-CS 1 220 kV interrupted due to faulty relay board. | FALSE | Critical
99161 | 5717 | 6366 |  |  | 2006-07-11 10:06 | 2006-07-11 10:59 | 53 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99162 | 5718 | 6367 |  |  | 2006-07-12 21:57 | 2006-07-12 21:57 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99163 | 5719 | 6368 |  |  | 2006-07-14 23:34 | 2006-07-14 23:34 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99164 | 5720 | 1174 |  |  | 2006-07-19 13:52 | 2006-07-19 14:19 | 27 | E0475 | GT 110 kV C1 Capacitor Circuit | Capacitor | Fault | Poor Design | Transend | Completed | TRUE | 0 | TRUE |  | IR331 - George Town Substation capacitor C1 interrupted during scheduled control wiring modifications due to utilisation of incorrect VT selection relay within wiring design. | FALSE | Non-Critical
99165 | 5721 | 6374 |  |  | 2006-07-21 10:11 | 2006-07-21 10:31 | 20 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139210 | 5722 | 6372 |  |  | 2006-07-18 16:45 | 2006-07-18 20:27 | 222 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99167 | 5723 | 6373 |  |  | 2006-07-19 17:28 | 2006-07-19 20:18 | 170 | E0119 | CS 11 kV U2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99168 | 5724 | 6371 |  |  | 2006-07-18 13:13 | 2006-07-18 22:13 | 540 | E0356 | KI 11 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139211 | 5835 | 6375 |  |  | 2006-07-26 15:24 | 2006-07-26 15:24 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99179 | 5836 | 6376 |  |  | 2006-07-27 09:14 | 2006-07-27 09:38 | 24 | E0602 | DP 22 kV XD2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99180 | 5837 | 6377 |  |  | 2006-07-29 07:26 | 2006-07-29 08:12 | 46 | E0606 | DP 22 kV XH2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99181 | 5838 | 6378 |  |  | 2006-07-30 13:03 | 2006-07-30 13:03 | 0 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99182 | 5839 | 6379 |  |  | 2006-07-31 00:39 | 2006-07-31 01:44 | 65 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99185 | 5862 | 1177 |  |  | 2006-08-01 12:32 | 2006-08-01 13:52 | 80 | E1426 | HA 22 kV A Bus | Bus | Fault | Internal Fault | Transend | Completed | TRUE | 1209 | TRUE |  | IR337 - Supply interrupted to transformer T4 and 22 kV 'A' and 'B' buses at Hadspen Substation due to transformer fault. | FALSE | Undefined
99186 | 5862 | 1177 |  |  | 2006-08-01 12:32 | 2006-08-01 13:52 | 80 | E1427 | HA 22 kV B Bus | Bus | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR337 - Supply interrupted to transformer T4 and 22 kV 'A' and 'B' buses at Hadspen Substation due to transformer fault. | FALSE | Undefined
99184 | 5862 | 1177 |  |  | 2006-08-01 12:59 | 2006-08-01 13:52 | 53 | E1424 | HA 110/22 kV T4 Transformer Circuit | Transformer | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR337 - Supply interrupted to transformer T4 and 22 kV 'A' and 'B' buses at Hadspen Substation due to transformer fault. | FALSE | Non-Critical
99187 | 5863 | 1178 |  |  | 2006-08-09 22:08 | 2006-08-09 23:26 | 78 | E0440 | HA-NW 2 110 kV Transmission Circuit | Transmission | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR338 - Hadspen-Norwood 110 kV transmission circuit interrupted due to protection maloperation in response to 22 kV feeder fault. | FALSE | Non-Critical
99188 | 5864 | 6388 |  |  | 2006-08-10 10:05 | 2006-08-10 10:55 | 50 | E1052 | SR 22 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99189 | 5865 | 6389 |  |  | 2006-08-11 08:27 | 2006-08-11 09:08 | 41 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99190 | 5866 | 6390 |  |  | 2006-08-13 08:05 | 2006-08-13 08:05 | 0 | E0273 | PM 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99191 | 5867 | 6391 |  |  | 2006-08-13 14:14 | 2006-08-13 14:15 | 1 | E0273 | PM 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99192 | 5868 | 6383 |  |  | 2006-08-09 11:45 | 2006-08-09 11:45 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99193 | 5869 | 6384 |  |  | 2006-08-09 11:45 | 2006-08-09 11:45 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99194 | 5870 | 6385 |  |  | 2006-08-09 15:31 | 2006-08-09 15:53 | 22 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99195 | 5871 | 6386 |  |  | 2006-08-09 15:44 | 2006-08-09 15:44 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99196 | 5872 | 6387 |  |  | 2006-08-09 22:09 | 2006-08-09 23:22 | 73 | E0762 | NW 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99197 | 5873 | 6382 |  |  | 2006-08-06 21:51 | 2006-08-06 21:52 | 1 | E0158 | MB 22 kV C2 Feeder Circuit | Feeder | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99198 | 5874 | 6380 |  |  | 2006-08-01 00:29 | 2006-08-01 01:49 | 80 | E1041 | SD 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99199 | 5875 | 6381 |  |  | 2006-08-01 12:32 | 2006-08-01 13:52 | 80 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99200 | 7376 | 6399 |  |  | 2006-08-20 03:56 | 2006-08-20 03:56 | 0 | E0902 | TR 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99201 | 7377 | 6397 |  |  | 2006-08-19 00:03 | 2006-08-19 12:03 | 720 | E0902 | TR 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99202 | 7378 | 6393 |  |  | 2006-08-19 16:02 | 2006-08-19 16:02 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99203 | 7379 | 6396 |  |  | 2006-08-17 00:22 | 2006-08-17 12:45 | 743 | E0358 | KI 11 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99204 | 7380 | 6395 |  |  | 2006-08-16 23:02 | 2006-08-17 12:45 | 823 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99205 | 7382 | 1180 |  |  | 2006-08-18 11:56 | 2006-08-18 11:56 | 0 | E0228 | RI 11 kV A Bus | Bus | Fault | Basslink | Basslink | Completed | TRUE | 0 | TRUE |  | Basslink tripped at Loy Yang when importing 299MW initiating FCSPS action at Comalco, Zinifex and Temco. | FALSE | Undefined
99206 | 7382 | 1180 |  |  | 2006-08-18 11:56 | 2006-08-18 11:56 | 0 | E0510 | GT-CO 4 220 kV Transmission Circuit | Transmission | Fault | Basslink | Basslink | Completed | TRUE | 5206 | TRUE |  | Basslink tripped at Loy Yang when importing 299MW initiating FCSPS action at Comalco, Zinifex and Temco. | FALSE | Non-Critical
99207 | 7382 | 1180 |  |  | 2006-08-18 11:56 | 2006-08-18 11:56 | 0 | E0513 | GT-TE 1 110 kV Transmission Circuit | Transmission | Fault | Basslink | Basslink | Completed | TRUE | 0 | TRUE |  | Basslink tripped at Loy Yang when importing 299MW initiating FCSPS action at Comalco, Zinifex and Temco. | FALSE | Non-Critical
99208 | 7383 | 1175 |  |  | 2006-07-22 11:51 | 2006-07-22 13:22 | 91 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Failure at Remote Station | Basslink | Completed | TRUE | 451 | TRUE |  | IR344 - Basslink circuit interrupted resulting in FCSPS operation. Transend did not cause or contribute to the outage. | FALSE | Undefined
99209 | 7384 | 1176 |  |  | 2006-07-22 14:52 | 2006-07-23 01:12 | 620 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Failure at Remote Station | Basslink | Completed | TRUE | 3805 | TRUE |  | IR344 - Basslink circuit interrupted resulting in FCSPS operation. Transend did not cause or contribute to the outage. | FALSE | Undefined
99210 | 7385 | 6400 |  |  | 2006-08-20 10:25 | 2006-08-20 10:25 | 0 | E0760 | NW 22 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99211 | 7386 | 6403 |  |  | 2006-08-22 00:44 | 2006-08-22 02:11 | 87 | E0820 | RA 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99212 | 7387 | 6404 |  |  | 2006-08-23 23:12 | 2006-08-23 23:12 | 0 | E0287 | PM 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99213 | 7388 | 1179 |  |  | 2006-08-17 14:29 | 2006-08-17 19:36 | 307 | E0550 | SH-PA Tee 110 kV Transmission Circuit Section | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR341 - SH-PA 110 kV interrupted due to Contractor error while installing OPGW. Existing earthwire fell onto 110 kV circuit causing a protection operation and isolation of the circuit. | FALSE | Non-Critical
99214 | 7389 | 6407 |  |  | 2006-08-28 15:18 | 2006-08-28 15:18 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99215 | 7390 | 6406 |  |  | 2006-08-25 10:24 | 2006-08-27 16:10 | 3226 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99216 | 7391 | 6405 |  |  | 2006-08-24 22:41 | 2006-08-24 23:19 | 38 | E0747 | NH 11 kV S2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99217 | 7392 | 6392 |  |  | 2006-08-14 03:34 | 2006-08-14 07:12 | 218 | E0489 | GT 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99218 | 7393 | 6342 |  |  | 2006-06-15 07:36 | 2006-06-15 08:42 | 66 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99219 | 7394 | 6284 |  |  | 2006-04-23 22:51 | 2006-04-23 22:51 | 0 | E0925 | TB 110/22 kV T1 Transformer Circuit | Transformer | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | Feeder fault | FALSE | Non-Critical
99220 | 7395 | 6248 |  |  | 2006-04-09 18:39 | 2006-04-09 18:39 | 0 | E1042 | SD 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99228 | 7546 | 1181 |  |  | 2006-09-01 09:19 | 2006-09-01 09:19 | 0 | E0298 | AV-SM 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR345 - Avoca-St Marys 110 kV transmission circuit tripped and reclosed successfully. Suspect windborne debris during strong winds. | FALSE | Non-Critical
139212 | 7547 | 6423 |  |  | 2006-09-09 07:39 | 2006-09-09 07:39 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99230 | 7548 | 6417 |  |  | 2006-09-04 10:12 | 2006-09-04 10:30 | 18 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99231 | 7549 | 6418 |  |  | 2006-09-04 21:22 | 2006-09-04 21:22 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99232 | 7550 | 6419 |  |  | 2006-09-05 10:51 | 2006-09-05 11:22 | 31 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99233 | 7551 | 6421 |  |  | 2006-09-05 21:10 | 2006-09-05 21:10 | 0 | E0768 | NW 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99234 | 7552 | 6422 |  |  | 2006-09-06 06:46 | 2006-09-06 06:47 | 1 | E0826 | RA 22 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99236 | 7554 | 6408 |  |  | 2006-08-29 10:18 | 2006-08-29 10:41 | 23 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99237 | 7554 | 6408 |  |  | 2006-08-29 10:18 | 2006-08-29 10:41 | 23 | E1001 | BU 22 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99235 | 7554 | 6408 |  |  | 2006-08-29 10:18 | 2006-08-29 10:41 | 23 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99239 | 7556 | 6410 |  |  | 2006-08-31 01:14 | 2006-08-31 12:23 | 669 | E0122 | CS 11 kV X2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99240 | 7557 | 6413 |  |  | 2006-09-01 05:58 | 2006-09-01 07:48 | 110 | E0464 | KR 11 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99241 | 7559 | 6430 |  |  | 2006-09-16 05:32 | 2006-09-16 06:32 | 60 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99242 | 7560 | 6323 |  |  | 2006-06-01 09:05 | 2006-06-02 17:52 | 1967 | E0110 | CS 11 kV K2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99243 | 7561 | 6320 |  |  | 2006-05-24 21:09 | 2006-06-05 17:40 | 17071 | E0109 | CS 11 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99244 | 7562 | 6321 |  |  | 2006-05-31 11:32 | 2006-05-31 12:00 | 28 | E1475 | RI 33 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99245 | 7563 | 6426 |  |  | 2006-09-14 11:16 | 2006-09-14 11:56 | 40 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99246 | 7564 | 6429 |  |  | 2006-09-14 18:42 | 2006-09-14 18:43 | 1 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99247 | 7565 | 6428 |  |  | 2006-09-14 19:22 | 2006-09-14 19:22 | 0 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99248 | 7566 | 6427 |  |  | 2006-09-14 17:46 | 2006-09-14 18:19 | 33 | E0764 | NW 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99249 | 7567 | 6425 |  |  | 2006-09-11 01:31 | 2006-09-11 01:31 | 0 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99251 | 7569 | 6398 |  |  | 2006-08-19 03:55 | 2006-08-19 09:30 | 335 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99252 | 7570 | 6370 |  |  | 2006-07-17 14:33 | 2006-07-17 17:07 | 154 | E0446 | KE 11 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99253 | 7571 | 6369 |  |  | 2006-07-17 13:10 | 2006-07-17 15:26 | 136 | E0303 | AV 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99256 | 7573 | 1182 |  |  | 2006-09-14 10:33 | 2006-09-14 23:09 | 756 | E0510 | GT-CO 4 220 kV Transmission Circuit | Transmission | Fault | Failure at Remote Station | Basslink | Completed | TRUE | 6038 | TRUE |  | IR347 - Basslink trip due to loss of supply to valve house cooling fans at Loy Yang converter station. FCSPS initiated resulting in load shedding at Comalco, Temco and Zinifex as designed. | FALSE | Non-Critical
99257 | 7573 | 1182 |  |  | 2006-09-14 10:33 | 2006-09-14 11:18 | 45 | E0513 | GT-TE 1 110 kV Transmission Circuit | Transmission | Fault | Failure at Remote Station | Basslink | Completed | TRUE | 0 | TRUE |  | IR347 - Basslink trip due to loss of supply to valve house cooling fans at Loy Yang converter station. FCSPS initiated resulting in load shedding at Comalco, Temco and Zinifex as designed. | FALSE | Non-Critical
99255 | 7573 | 1182 |  |  | 2006-09-14 10:33 | 2006-09-14 11:13 | 40 | E0228 | RI 11 kV A Bus | Bus | Fault | Failure at Remote Station | Basslink | Completed | TRUE | 0 | TRUE |  | IR347 - Basslink trip due to loss of supply to valve house cooling fans at Loy Yang converter station. FCSPS initiated resulting in load shedding at Comalco, Temco and Zinifex as designed. | FALSE | Undefined
99258 | 7574 | 1183 |  |  | 2006-09-21 03:53 | 2006-09-21 05:54 | 121 | E0718 | FA-MA 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR350 - Farrell-Mackintosh 110 kV interrupted. Lightning was reported in the area however no evidence of lightning strike or other cause was identified during an inspection of the circuit. | FALSE | Non-Critical
99259 | 7575 | 6431 |  |  | 2006-09-17 15:51 | 2006-09-17 15:51 | 0 | E0869 | RB 44 kV E4 Circuit Breaker | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99260 | 7576 | 6432 |  |  | 2006-09-19 05:46 | 2006-09-19 05:46 | 0 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99261 | 7577 | 6433 |  |  | 2006-09-21 01:44 | 2006-09-21 05:13 | 209 | E0489 | GT 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99262 | 7578 | 6434 |  |  | 2006-09-21 06:03 | 2006-09-21 07:37 | 94 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99263 | 7579 | 6435 |  |  | 2006-09-21 07:33 | 2006-09-21 07:33 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99264 | 7580 | 6436 |  |  | 2006-09-21 14:38 | 2006-09-21 14:45 | 7 | E0012 | BW 11 kV A2 Feeder Circuit | Feeder | Fault | Fire (Bush) | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99265 | 7581 | 6437 |  |  | 2006-09-21 20:57 | 2006-09-21 20:57 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99266 | 7583 | 1186 |  |  | 2006-09-23 23:31 | 2006-09-24 02:02 | 151 | E0005 | BW 110 kV A Bus | Bus | Fault | Communication Failure | Transend | Completed | TRUE | 0 | TRUE |  | IR351 - Bridgewater Substation T1 and 110 kV 'A' Bus and BW-LF 110 kV transmission circuit interrupted due to faulty data converter between RTU and bay controller. | FALSE | Undefined
99267 | 7583 | 1186 |  |  | 2006-09-23 23:31 | 2006-09-24 02:05 | 154 | E0006 | BW 110/11 kV T1 Transformer Circuit | Transformer | Fault | Communication Failure | Transend | Completed | TRUE | 0 | TRUE |  | IR351 - Bridgewater Substation T1 and 110 kV 'A' Bus and BW-LF 110 kV transmission circuit interrupted due to faulty data converter between RTU and bay controller. | FALSE | Non-Critical
99268 | 7583 | 1186 |  |  | 2006-09-23 11:31 | 2006-09-24 01:20 | 829 | E1073 | BW-LF 110 kV Transmission Circuit | Transmission | Fault | Communication Failure | Transend | Completed | TRUE | 0 | TRUE |  | IR351 - Bridgewater Substation T1 and 110 kV 'A' Bus and BW-LF 110 kV transmission circuit interrupted due to faulty data converter between RTU and bay controller. | FALSE | Non-Critical
99269 | 7584 | 6438 |  |  | 2006-09-22 05:35 | 2006-09-22 05:35 | 0 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99270 | 7585 | 6439 |  |  | 2006-09-22 06:02 | 2006-09-22 06:02 | 0 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99271 | 7586 | 6440 |  |  | 2006-09-22 06:04 | 2006-09-22 07:34 | 90 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99272 | 7587 | 6441 |  |  | 2006-09-22 06:45 | 2006-09-22 06:45 | 0 | E1538 | MY 22 kV P2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99273 | 7588 | 6442 |  |  | 2006-09-22 07:21 | 2006-09-22 08:03 | 42 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99274 | 7589 | 6443 |  |  | 2006-09-22 07:24 | 2006-09-22 12:32 | 308 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99275 | 7590 | 6444 |  |  | 2006-09-22 07:54 | 2006-09-22 07:54 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99276 | 7591 | 6445 |  |  | 2006-09-22 08:07 | 2006-09-22 08:07 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99277 | 7592 | 6446 |  |  | 2006-09-22 08:11 | 2006-09-22 08:11 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99278 | 7593 | 6447 |  |  | 2006-09-22 08:23 | 2006-09-22 08:23 | 0 | E0366 | KI 11 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99279 | 7594 | 6448 |  |  | 2006-09-22 08:21 | 2006-09-22 09:29 | 68 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99280 | 7595 | 6449 |  |  | 2006-09-24 11:29 | 2006-09-24 13:10 | 101 | E1482 | RI 33 kV K2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99281 | 7596 | 6451 |  |  | 2006-09-25 05:46 | 2006-09-25 06:34 | 48 | E0084 | CR 33 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99282 | 7597 | 6452 |  |  | 2006-09-25 05:46 | 2006-09-25 06:38 | 52 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99283 | 7599 | 1184 |  |  | 2006-09-22 12:36 | 2006-09-22 13:42 | 66 | E0290 | PO-PM 2 110 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR352 - Poatina-Palmerston No. 2 110 kV interrupted due to fault within Generator installation at Poatina Power Station. | FALSE | Non-Critical
99292 | 7730 | 6347 |  |  | 2006-06-18 19:33 | 2006-06-18 19:33 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99293 | 7731 | 6456 |  |  | 2006-09-28 09:39 | 2006-09-28 10:06 | 27 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99294 | 7732 | 6455 |  |  | 2006-09-27 13:35 | 2006-09-27 14:05 | 30 | E0842 | RK 11 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99295 | 7733 | 6453 |  |  | 2006-09-27 10:58 | 2006-09-27 14:00 | 182 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99296 | 7734 | 6454 |  |  | 2006-09-27 11:53 | 2006-09-27 12:29 | 36 | E0842 | RK 11 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139213 | 7735 | 6457 |  |  | 2006-09-28 17:54 | 2006-09-28 17:54 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99298 | 7742 | 1187 |  |  | 2006-10-03 09:16 | 2006-10-03 13:21 | 245 | E0261 | PO-PM 3 220 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR353 - Poatina-Palmerston No. 3 220 kV interrupted due to intertrip received from Poatina Power Station during Machine No. 3 startup. | FALSE | Non-Critical
99299 | 7744 | 1188 |  |  | 2006-10-04 14:38 | 2006-10-04 15:52 | 74 | E0280 | PM 110/22 kV T4 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 443 | TRUE |  | IR355 - Palmerston Substation transformer T4 interrupted. Contractor left TF neutral CT links open resulting in transformer trip in response to a feeder fault. ITOMS: Not included as the CT in question is integral to protection systems that are protecting against LV faults only. | FALSE | Non-Critical
99300 | 7745 | 1190 |  |  | 2006-10-05 10:55 | 2006-10-05 13:28 | 153 | E0419 | KR-EL 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR356 - Knights Road-Electrona 110 kV interrupted during heavy rains. Cause unknown. | FALSE | Non-Critical
99301 | 7746 | 1191 |  |  | 2006-10-05 15:51 | 2006-10-05 19:15 | 204 | E0560 | NW-SD-DE 88 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 2939 | TRUE |  | IR357 - Norwood-Scottsdale-Derby 88 kV interrupted. No cause identified. | FALSE | Undefined
99302 | 7747 | 6469 |  |  | 2006-10-08 08:13 | 2006-10-08 08:14 | 1 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99303 | 7748 | 6470 |  |  | 2006-10-08 08:57 | 2006-10-08 08:57 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139214 | 7749 | 6471 |  |  | 2006-10-08 09:03 | 2006-10-08 09:03 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99305 | 7750 | 6472 |  |  | 2006-10-08 19:03 | 2006-10-08 19:03 | 0 | E0366 | KI 11 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99306 | 7751 | 6466 |  |  | 2006-10-04 15:20 | 2006-10-04 15:20 | 0 | E0639 | ST 22 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99307 | 7752 | 6468 |  |  | 2006-10-05 16:49 | 2006-10-05 16:49 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139215 | 7753 | 6467 |  |  | 2006-10-05 12:03 | 2006-10-05 12:33 | 30 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99309 | 7754 | 6463 |  |  | 2006-10-04 14:38 | 2006-10-04 15:53 | 75 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99310 | 7755 | 6460 |  |  | 2006-10-03 10:31 | 2006-10-03 11:01 | 30 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99311 | 7756 | 6461 |  |  | 2006-10-03 11:09 | 2006-10-03 11:19 | 10 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99312 | 7757 | 6459 |  |  | 2006-10-02 18:14 | 2006-10-02 18:14 | 0 | E0970 | SO 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99313 | 7758 | 6458 |  |  | 2006-09-30 04:26 | 2006-09-30 04:27 | 1 | E0303 | AV 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99314 | 7759 | 1192 |  |  | 2006-10-11 19:58 | 2006-10-11 21:50 | 112 | E0193 | SO 110/22 kV T2 Transformer Circuit | Transformer | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR358 - Sorell Substation transformer T2 interrupted due to gas/temperature trip. Root cause unknown. | FALSE | Non-Critical
99315 | 7760 | 6499 |  |  | 2006-10-18 15:20 | 2006-10-18 15:39 | 19 | E0837 | RK 11 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99316 | 7761 | 1193 |  |  | 2006-10-12 15:31 | 2006-10-12 16:40 | 69 | E0348 | LF-RK 1 110 kV Transmission Circuit | Transmission | Fault | Fire (Bush) | Transend | Completed | TRUE | 0 | TRUE |  | IR359 - Lindisfarne-Rokeby No 1 110 kV transmission circuit interrupted due to bushfire. Lindisfarne-Rokeby No 2-Sorell 110 kV transmission circuit interrupted due to incorrect substation configuration. | FALSE | Non-Critical
99326 | 7855 | 1195 |  |  | 2006-10-13 12:36 | 2006-10-13 12:52 | 16 | E1546 | DP 22 kV C Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 177 | TRUE |  | IR361 - Devonport 22 kV 'C' Bus interrupted due to Contractor isolations error during commissioning tests for 110 kV bus zone protection. | FALSE | Undefined
99325 | 7855 | 1195 |  |  | 2006-10-13 12:36 | 2006-10-13 12:52 | 16 | E0595 | DP 110/22 kV T3 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR361 - Devonport 22 kV 'C' Bus interrupted due to Contractor isolations error during commissioning tests for 110 kV bus zone protection. | FALSE | Non-Critical
99327 | 7856 | 6473 |  |  | 2006-10-10 12:47 | 2006-10-10 12:47 | 0 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99328 | 7857 | 6475 |  |  | 2006-10-12 05:19 | 2006-10-12 07:06 | 107 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99329 | 7858 | 6476 |  |  | 2006-10-12 11:51 | 2006-10-12 14:27 | 156 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99330 | 7859 | 6477 |  |  | 2006-10-12 12:20 | 2006-10-12 17:43 | 323 | E0343 | LF 33 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99331 | 7860 | 6478 |  |  | 2006-10-12 12:20 | 2006-10-12 17:28 | 308 | E0353 | LF 33 kV K2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99332 | 7861 | 6479 |  |  | 2006-10-12 12:51 | 2006-10-12 15:11 | 140 | E0366 | KI 11 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99333 | 7862 | 6480 |  |  | 2006-10-12 14:54 | 2006-10-12 15:00 | 6 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99334 | 7863 | 6481 |  |  | 2006-10-12 14:55 | 2006-10-12 18:48 | 233 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99335 | 7864 | 6482 |  |  | 2006-10-12 23:20 | 2006-10-13 14:24 | 904 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99336 | 7865 | 6483 |  |  | 2006-10-13 14:53 | 2006-10-13 15:47 | 54 | E0835 | RK 11 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99337 | 7866 | 6484 |  |  | 2006-10-14 09:59 | 2006-10-14 09:59 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99338 | 7867 | 6486 |  |  | 2006-10-15 10:54 | 2006-10-15 10:54 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99339 | 7868 | 6487 |  |  | 2006-10-16 21:51 | 2006-10-16 21:52 | 1 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99340 | 7869 | 6488 |  |  | 2006-10-17 00:32 | 2006-10-17 01:32 | 60 | E0085 | CR 33 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99341 | 7870 | 6489 |  |  | 2006-10-17 06:52 | 2006-10-17 07:09 | 17 | E1045 | TU 22 kV S2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99342 | 7871 | 6490 |  |  | 2006-10-18 00:44 | 2006-10-18 00:44 | 0 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99343 | 7872 | 6491 |  |  | 2006-10-18 01:22 | 2006-10-18 01:22 | 0 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99344 | 7873 | 6492 |  |  | 2006-10-18 02:07 | 2006-10-18 02:07 | 0 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99345 | 7874 | 6493 |  |  | 2006-10-18 02:44 | 2006-10-18 02:44 | 0 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99346 | 7875 | 6494 |  |  | 2006-10-18 11:15 | 2006-10-18 11:15 | 0 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99347 | 7876 | 6495 |  |  | 2006-10-18 12:52 | 2006-10-18 16:14 | 202 | E0186 | TU 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99348 | 7877 | 6496 |  |  | 2006-10-18 13:23 | 2006-10-18 13:23 | 0 | E0014 | BW 11 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99349 | 7878 | 6497 |  |  | 2006-10-18 13:55 | 2006-10-18 13:55 | 0 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99350 | 7879 | 6498 |  |  | 2006-10-18 13:50 | 2006-10-18 21:04 | 434 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99352 | 7880 | 6414 |  |  | 2006-09-03 06:17 | 2006-09-03 06:17 | 0 | E1451 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99351 | 7880 | 6414 |  |  | 2006-09-03 06:17 | 2006-09-03 06:17 | 0 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99353 | 7881 | 6501 |  |  | 2006-10-18 18:42 | 2006-10-18 19:19 | 37 | E0835 | RK 11 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99354 | 7882 | 6502 |  |  | 2006-10-18 19:10 | 2006-10-18 20:07 | 57 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99355 | 7884 | 6505 |  |  | 2006-10-22 18:39 | 2006-10-22 19:20 | 41 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99356 | 7885 | 6506 |  |  | 2006-10-28 00:08 | 2006-10-28 12:08 | 720 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99357 | 7886 | 6507 |  |  | 2006-10-28 00:49 | 2006-10-28 01:56 | 67 | E0465 | KR 11 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
105695 | 7887 | 6508 |  |  | 2006-10-28 05:10 | 2006-10-28 06:30 | 80 | E0366 | KI 11 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99359 | 7888 | 6509 |  |  | 2006-10-28 09:36 | 2006-10-28 09:36 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99360 | 7889 | 6510 |  |  | 2006-10-28 17:45 | 2006-10-28 18:19 | 34 | E0199 | SO 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99362 | 7890 | 1197 |  |  | 2006-11-09 19:45 | 2006-11-09 20:17 | 32 | E1540 | MY 22 kV B Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 234 | TRUE |  | IR366 - Mowbray Substation 22 kV B Bus and transformer T2 were interrupted in response to a 22 kV feeder fault due to incorrect protection wiring design. | FALSE | Undefined
99363 | 7891 | 6529 |  |  | 2006-11-13 07:38 | 2006-11-13 08:48 | 70 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99364 | 7893 | 6520 |  |  | 2006-11-06 22:24 | 2006-11-06 22:26 | 2 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99365 | 7894 | 6519 |  |  | 2006-11-06 22:21 | 2006-11-06 22:22 | 1 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
119516 | 7895 | 6518 |  |  | 2006-11-06 08:00 | 2006-11-06 12:00 | 240 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99366 | 7896 | 1198 |  |  | 2006-11-12 10:49 | 2006-11-12 11:11 | 22 | E0404 | SH-BU 2 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR367 - Sheffield-Burnie No 2 and Paloona-Ulverstone 110 kV transmission circuits interrupted due to lightning. | FALSE | Non-Critical
99367 | 7896 | 1198 |  |  | 2006-11-12 10:49 | 2006-11-12 11:13 | 24 | E0550 | SH-PA Tee 110 kV Transmission Circuit Section | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR367 - Sheffield-Burnie No 2 and Paloona-Ulverstone 110 kV transmission circuits interrupted due to lightning. | FALSE | Non-Critical
99368 | 7897 | 1200 |  |  | 2006-11-14 15:57 | 2006-11-14 15:57 | 0 | E0274 | PM-AV 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR368 - Palmerston-Avoca 110 kV transmission circuit interrupted due to lightning. | FALSE | Non-Critical
99369 | 7898 | 6518 |  |  | 2006-11-06 20:54 | 2006-11-06 21:00 | 6 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99370 | 7899 | 6517 |  |  | 2006-11-06 20:50 | 2006-11-06 20:50 | 0 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99371 | 7900 | 6532 |  |  | 2006-11-15 13:28 | 2006-11-15 13:28 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99372 | 7901 | 6533 |  |  | 2006-11-15 13:49 | 2006-11-15 13:49 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99373 | 7902 | 6534 |  |  | 2006-11-15 15:05 | 2006-11-15 15:39 | 34 | E0764 | NW 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99374 | 7903 | 6535 |  |  | 2006-11-16 02:06 | 2006-11-16 02:06 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99375 | 7904 | 6531 |  |  | 2006-11-14 16:38 | 2006-11-14 17:10 | 32 | E1045 | TU 22 kV S2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99376 | 7905 | 6530 |  |  | 2006-11-13 13:08 | 2006-11-13 13:24 | 16 | E0943 | UL 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99377 | 7906 | 6513 |  |  | 2006-11-01 01:24 | 2006-11-01 01:24 | 0 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99378 | 7907 | 6512 |  |  | 2006-11-01 01:24 | 2006-11-01 01:24 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99379 | 7908 | 6511 |  |  | 2006-10-30 13:15 | 2006-10-30 13:26 | 11 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99380 | 7910 | 6526 |  |  | 2006-11-11 05:47 | 2006-11-11 06:03 | 16 | E1045 | TU 22 kV S2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99381 | 7911 | 6527 |  |  | 2006-11-12 05:41 | 2006-11-12 05:41 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99382 | 7912 | 6516 |  |  | 2006-11-06 19:33 | 2006-11-06 19:33 | 0 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99383 | 7913 | 6515 |  |  | 2006-11-05 05:48 | 2006-11-05 06:09 | 21 | E1045 | TU 22 kV S2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99384 | 7914 | 6528 |  |  | 2006-11-07 19:31 | 2006-11-07 19:31 | 0 | E0762 | NW 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99385 | 7915 | 6537 |  |  | 2006-11-17 10:27 | 2006-11-17 10:55 | 28 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99386 | 7916 | 6538 |  |  | 2006-11-20 08:41 | 2006-11-20 09:24 | 43 | E0643 | ST 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99387 | 7917 | 6540 |  |  | 2006-11-20 23:11 | 2006-11-20 23:11 | 0 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99388 | 7918 | 6539 |  |  | 2006-11-20 12:18 | 2006-11-20 13:23 | 65 | E0643 | ST 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99389 | 7919 | 6541 |  |  | 2006-11-23 11:57 | 2006-11-23 11:57 | 0 | E0014 | BW 11 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99395 | 8042 | 6500 |  |  | 2006-11-13 05:36 | 2006-11-19 14:38 | 9182 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99396 | 8043 | 6498 |  |  | 2006-11-18 13:50 | 2006-11-18 21:04 | 434 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99397 | 8044 | 6542 |  |  | 2006-11-24 21:59 | 2006-11-24 22:43 | 44 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99398 | 8045 | 6543 |  |  | 2006-11-24 22:44 | 2006-11-24 22:54 | 10 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99399 | 8046 | 6544 |  |  | 2006-11-26 08:38 | 2006-11-26 08:38 | 0 | E0640 | ST 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99400 | 8048 | 6545 |  |  | 2006-11-29 05:00 | 2006-11-29 05:00 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99401 | 8049 | 1201 |  |  | 2006-11-29 12:27 | 2006-11-29 13:17 | 50 | E0795 | QT 110/11 kV T3 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR369 - Queenstown Substation transformer T3 interrupted due to trip of 11 kV circuit breaker C552 due to a partially decommissioned control cable causing inadvertent trip signals. | FALSE | Non-Critical
99405 | 8074 | 6549 |  |  | 2006-12-01 00:13 | 2006-12-01 00:16 | 3 | E0767 | NW 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99406 | 8075 | 6548 |  |  | 2006-11-30 23:09 | 2006-11-30 23:26 | 17 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99407 | 8076 | 6547 |  |  | 2006-11-30 15:07 | 2006-11-30 15:31 | 24 | E0111 | CS 11 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99409 | 8078 | 6551 |  |  | 2006-12-03 12:45 | 2006-12-03 12:45 | 0 | E1552 | DP 22 kV L2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99410 | 8079 | 6550 |  |  | 2006-12-01 19:59 | 2006-12-01 20:18 | 19 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99411 | 8080 | 6554 |  |  | 2006-12-05 12:39 | 2006-12-05 12:56 | 17 | E1029 | SR 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99412 | 8082 | 6555 |  |  | 2006-12-07 16:05 | 2006-12-07 16:05 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99413 | 8084 | 6566 |  |  | 2006-12-12 07:02 | 2006-12-12 07:02 | 0 | E0902 | TR 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99414 | 8085 | 6557 |  |  | 2006-12-09 13:53 | 2006-12-09 14:52 | 59 | E0118 | CS 11 kV T2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99415 | 8086 | 6558 |  |  | 2006-12-09 15:29 | 2006-12-09 15:51 | 22 | E1557 | CR 33 kV Z2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99416 | 8087 | 6559 |  |  | 2006-12-10 04:20 | 2006-12-10 04:56 | 36 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99417 | 8088 | 6560 |  |  | 2006-12-10 22:17 | 2006-12-10 22:17 | 0 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99418 | 8089 | 6561 |  |  | 2006-12-11 05:02 | 2006-12-11 05:25 | 23 | E0075 | CR 33 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99419 | 8090 | 6562 |  |  | 2006-12-11 14:32 | 2006-12-11 14:53 | 21 | E0835 | RK 11 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99420 | 8091 | 6563 |  |  | 2006-12-11 14:29 | 2006-12-11 15:00 | 31 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99421 | 8092 | 6564 |  |  | 2006-12-11 15:33 | 2006-12-11 16:30 | 57 | E0835 | RK 11 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99422 | 8093 | 6565 |  |  | 2006-12-11 16:14 | 2006-12-11 16:56 | 42 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99423 | 8095 | 6568 |  |  | 2006-12-12 08:34 | 2006-12-12 08:35 | 1 | E0768 | NW 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99424 | 8097 | 1202 |  |  | 2006-11-30 13:28 | 2006-11-30 13:33 | 5 | E0438 | HA-GT 2 220 kV Transmission Circuit | Transmission | Fault | Fire Fighting | Transend | Completed | TRUE | 0 | TRUE |  | IR374 - HA-GT 2 interrupted due to insulator flashover caused by helicopter dropping water onto transmission tower during fire fighting activities. BB-BE-GT 2 tripped due to a customer earth fault that occurred at the same time. | FALSE | Critical
99425 | 8097 | 1202 |  |  | 2006-11-30 13:28 | 2006-11-30 14:12 | 44 | E1443 | BB-BE-GT 2 110 kV Transmission Circuit | Transmission | Fault | Fire Fighting | Transend | Completed | TRUE | 0 | TRUE |  | IR374 - HA-GT 2 interrupted due to insulator flashover caused by helicopter dropping water onto transmission tower during fire fighting activities. BB-BE-GT 2 tripped due to a customer earth fault that occurred at the same time. | FALSE | Non-Critical
99426 | 8098 | 1204 |  |  | 2006-12-10 12:32 | 2006-12-10 12:42 | 10 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Failure at Remote Station | Basslink | Completed | TRUE | 2465 | TRUE |  | IR375 - Basslink loss of link signal received due to extreme temperatures in Victoria, resulting in SPS load shedding at Comalco and TEMCO. | FALSE | Undefined
99427 | 8099 | 6577 |  |  | 2006-12-21 04:25 | 2006-12-21 07:17 | 172 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99428 | 8100 | 6583 |  |  | 2006-12-21 19:36 | 2006-12-21 19:38 | 2 | E0655 | SM 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99429 | 8101 | 6580 |  |  | 2006-12-21 15:44 | 2006-12-21 19:02 | 198 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99430 | 8102 | 6582 |  |  | 2006-12-21 18:38 | 2006-12-21 19:00 | 22 | E0655 | SM 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99431 | 8103 | 6581 |  |  | 2006-12-21 16:17 | 2006-12-21 17:53 | 96 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99432 | 8104 | 6579 |  |  | 2006-12-21 15:34 | 2006-12-21 16:24 | 50 | E0639 | ST 22 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99433 | 8105 | 6578 |  |  | 2006-12-21 12:24 | 2006-12-21 12:47 | 23 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93283 | 8107 | 6603 |  |  | 2007-01-01 19:38 | 2007-01-01 20:10 | 32 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93284 | 8108 | 6602 |  |  | 2007-01-01 19:34 | 2007-01-01 19:35 | 1 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139217 | 8109 | 6601 |  |  | 2007-01-01 16:30 | 2007-01-01 16:30 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99434 | 8110 | 6600 |  |  | 2006-12-29 23:17 | 2006-12-29 23:17 | 0 | E0199 | SO 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99435 | 8111 | 6599 |  |  | 2006-12-28 06:34 | 2006-12-28 07:20 | 46 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99436 | 8112 | 6598 |  |  | 2006-12-28 04:00 | 2006-12-28 04:00 | 0 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99437 | 8113 | 6597 |  |  | 2006-12-27 22:26 | 2006-12-27 22:26 | 0 | E0766 | NW 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99438 | 8114 | 6596 |  |  | 2006-12-27 21:45 | 2006-12-27 21:45 | 0 | E0944 | UL 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99439 | 8115 | 6595 |  |  | 2006-12-26 12:23 | 2006-12-26 12:23 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99440 | 8116 | 6594 |  |  | 2006-12-25 19:35 | 2006-12-25 20:29 | 54 | E0085 | CR 33 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99441 | 8117 | 6593 |  |  | 2006-12-25 19:35 | 2006-12-25 20:38 | 63 | E0084 | CR 33 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99442 | 8118 | 6592 |  |  | 2006-12-25 19:35 | 2006-12-25 20:37 | 62 | E0102 | CS 11 kV C2 Feeder Circuit (Spare) | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139218 | 8119 | 6591 |  |  | 2006-12-24 17:57 | 2006-12-24 17:57 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99444 | 8120 | 6590 |  |  | 2006-12-24 06:08 | 2006-12-24 06:08 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99445 | 8121 | 6589 |  |  | 2006-12-24 04:53 | 2006-12-24 04:53 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99446 | 8122 | 6588 |  |  | 2006-12-23 22:55 | 2006-12-23 22:55 | 0 | E0944 | UL 22 kV B2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99447 | 8123 | 6587 |  |  | 2006-12-23 05:07 | 2006-12-23 05:07 | 0 | E0764 | NW 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99448 | 8124 | 6586 |  |  | 2006-12-22 19:44 | 2006-12-22 21:11 | 87 | E0906 | TR 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99449 | 8125 | 6585 |  |  | 2006-12-22 18:17 | 2006-12-22 20:54 | 157 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99450 | 8126 | 6584 |  |  | 2006-12-22 17:38 | 2006-12-22 17:58 | 20 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93286 | 8128 | 6606 |  |  | 2007-01-03 11:40 | 2007-01-03 11:40 | 0 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93287 | 8129 | 6604 |  |  | 2007-01-02 16:18 | 2007-01-02 16:41 | 23 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99458 | 8314 | 1207 |  |  | 2006-12-20 12:39 | 2006-12-20 12:41 | 2 | E0401 | BU-PL 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 49 | TRUE |  | IR377 - Burnie-Port Latta 110 kV transmission circuit interrupted due to human error during protection testing. | FALSE | Non-Critical
93349 | 8315 | 1208 |  |  | 2007-01-02 07:00 | 2007-01-02 17:28 | 628 | E0794 | QT 110/22 kV T2 Transformer Circuit | Transformer | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR378 - Queenstown Substation transformer T2 interrupted due to gas pressure alarm. Information on NOCS indicates that at 17:28 on the 2nd of January we were informed that T2 was available in an emergency and this information was attached to a tag on B452 at Queenstown at that time. I have yet to confirm the time of the availability but 17:28 was the time we placed the tag.RegardsJan | FALSE | Non-Critical
93350 | 8316 | 6608 |  |  | 2007-01-04 18:10 | 2007-01-04 18:10 | 0 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93351 | 8317 | 6609 |  |  | 2007-01-05 00:23 | 2007-01-05 00:23 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93352 | 8318 | 6610 |  |  | 2007-01-05 01:29 | 2007-01-05 01:29 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93353 | 8319 | 6611 |  |  | 2007-01-05 01:38 | 2007-01-05 01:38 | 0 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93354 | 8320 | 6612 |  |  | 2007-01-05 06:40 | 2007-01-05 10:27 | 227 | E0085 | CR 33 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93355 | 8321 | 6613 |  |  | 2007-01-06 14:40 | 2007-01-06 15:19 | 39 | E0083 | CR 33 kV F2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93356 | 8322 | 6614 |  |  | 2007-01-06 17:39 | 2007-01-06 17:39 | 0 | E0764 | NW 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93357 | 8323 | 6615 |  |  | 2007-01-06 20:00 | 2007-01-07 03:10 | 430 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93358 | 8324 | 6616 |  |  | 2007-01-06 20:15 | 2007-01-06 20:15 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93360 | 8326 | 6619 |  |  | 2007-01-07 16:46 | 2007-01-07 17:45 | 59 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93361 | 8327 | 6620 |  |  | 2007-01-07 17:32 | 2007-01-07 17:32 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93362 | 8328 | 6621 |  |  | 2007-01-07 17:37 | 2007-01-07 19:30 | 113 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93363 | 8329 | 6622 |  |  | 2007-01-07 19:41 | 2007-01-07 19:41 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93364 | 8330 | 6623 |  |  | 2007-01-07 22:18 | 2007-01-07 23:28 | 70 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93365 | 8332 | 1209 |  |  | 2007-01-09 18:27 | 2007-01-09 18:44 | 17 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 343 | TRUE |  | IR379 - Queenstown Substation interrupted due to inadvertent protection operation. Source of protection operation unknown. | FALSE | Non-Critical
93366 | 8333 | 6624 |  |  | 2007-01-10 20:55 | 2007-01-10 20:55 | 0 | E0358 | KI 11 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93368 | 8335 | 6637 |  |  | 2007-01-14 17:27 | 2007-01-14 17:27 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93369 | 8337 | 1210 |  |  | 2007-01-12 22:17 | 2007-01-13 | 103 | E1468 | RI 110/33 kV T6 Transformer Circuit | Transformer | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR380 - Risdon Substation transformer T5 and T6 interrupted due to faulty relay causing inadvertent circuit breaker fail (CBF) operation. | FALSE | Non-Critical
93370 | 8337 | 1210 |  |  | 2007-01-12 22:17 | 2007-01-12 23:53 | 96 | E1489 | RI 110/33 kV T5 Transformer Circuit | Transformer | Fault | Internal Fault | Transend | Completed | TRUE | 1609 | TRUE |  | IR380 - Risdon Substation transformer T5 and T6 interrupted due to faulty relay causing inadvertent circuit breaker fail (CBF) operation. | FALSE | Non-Critical
93371 | 8344 | 6635 |  |  | 2007-01-13 03:51 | 2007-01-13 03:51 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93372 | 8345 | 6636 |  |  | 2007-01-13 06:37 | 2007-01-13 06:37 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195501 | 8346 | 1211 |  |  | 2007-01-16 23:44 | 2007-01-17 00:55 | 71 | E0796 | QT 110/11 kV T4 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR382 - Queenstown Substation transformers T3 and T4 interrupted due to a partially decommissioned control cable causing inadvertent trip signals. | FALSE | Non-Critical
93373 | 8346 | 1211 |  |  | 2007-01-16 09:56 | 2007-01-16 10:15 | 19 | E0795 | QT 110/11 kV T3 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 210 | TRUE |  | IR382 - Queenstown Substation transformers T3 and T4 interrupted due to a partially decommissioned control cable causing inadvertent trip signals. | FALSE | Non-Critical
93376 | 8347 | 6641 |  |  | 2007-01-16 22:32 | 2007-01-16 22:57 | 25 | E0869 | RB 44 kV E4 Circuit Breaker | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93377 | 8348 | 6639 |  |  | 2007-01-16 16:28 | 2007-01-16 17:55 | 87 | E0496 | GT 22 kV N2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93378 | 8349 | 6638 |  |  | 2007-01-16 12:16 | 2007-01-16 12:16 | 0 | E0639 | ST 22 kV H2 Feeder Circuit | Feeder | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
175130 | 8350 | 1212 |  |  | 2007-01-19 13:27 | 2007-01-19 14:30 | 63 | E0179 | TU 110/22 kV T9X Transformer Circuit | Transformer | Fault | Internal Fault | Transend | Completed | TRUE | 47 | TRUE |  | IR383 - Tungatinah Substation transformer T9 interrupted due to suspected lightning. | FALSE | Undefined
93380 | 8351 | 1213 |  |  | 2007-01-21 00:15 | 2007-01-21 13:20 | 785 | E0192 | SO 110/22 kV T1 Transformer Circuit | Transformer | Fault | Poor Design | Transend | Completed | TRUE | 793 | TRUE |  | IR384 - Sorell Substation interrupted due to poor circuit breaker design resulting in a cracked bus coupler circuit breaker shutter. Resultant partial discharge and ozone corrosion caused flashover of CT in D252 switchgear cubicle. ITOMS: Not included as CB is low voltage. | FALSE | Non-Critical
93381 | 8352 | 1214 |  |  | 2007-01-21 05:11 | 2007-01-21 06:06 | 55 | E1488 | RI 110/33 kV T4 Transformer Circuit | Transformer | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR385 - Risdon Substation transformer T4 and 33 kV 'G' Bus interrupted due to faulty circuit breaker fail input into relay G599. | FALSE | Non-Critical
93382 | 8353 | 6646 |  |  | 2007-01-21 13:49 | 2007-01-21 14:15 | 26 | E0085 | CR 33 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93383 | 8356 | 6354 |  |  | 2007-01-21 00:29 | 2007-01-21 00:30 | 1 | E0944 | UL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93384 | 8357 | 6646 |  |  | 2007-01-18 03:17 | 2007-01-18 03:39 | 22 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93385 | 8358 | 6647 |  |  | 2007-01-18 06:57 | 2007-01-18 06:57 | 0 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93386 | 8359 | 6648 |  |  | 2007-01-18 10:31 | 2007-01-18 11:15 | 44 | E0906 | TR 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93387 | 8360 | 6649 |  |  | 2007-01-18 22:02 | 2007-01-18 22:02 | 0 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93388 | 8361 | 6681 |  |  | 2007-01-28 23:52 | 2007-01-28 23:52 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93389 | 8362 | 6680 |  |  | 2007-01-28 22:14 | 2007-01-28 22:43 | 29 | E0019 | BW 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93390 | 8363 | 6678 |  |  | 2007-01-28 14:54 | 2007-01-28 16:30 | 96 | E0826 | RA 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93391 | 8364 | 6679 |  |  | 2007-01-28 15:14 | 2007-01-28 15:14 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93392 | 8365 | 6677 |  |  | 2007-01-28 14:53 | 2007-01-28 14:53 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93393 | 8366 | 6676 |  |  | 2007-01-28 09:29 | 2007-01-28 09:29 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93394 | 8367 | 6675 |  |  | 2007-01-28 09:24 | 2007-01-28 09:24 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93395 | 8368 | 6674 |  |  | 2007-01-27 15:33 | 2007-01-27 15:33 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93396 | 8369 | 6673 |  |  | 2007-01-27 11:04 | 2007-01-27 11:23 | 19 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93397 | 8370 | 6672 |  |  | 2007-01-27 02:24 | 2007-01-27 02:24 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139224 | 8371 | 6670 |  |  | 2007-01-26 23:01 | 2007-01-26 23:52 | 51 | E0185 | TU 22 kV X D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93399 | 8372 | 6669 |  |  | 2007-01-26 20:47 | 2007-01-26 20:47 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93400 | 8373 | 6668 |  |  | 2007-01-26 20:15 | 2007-01-26 20:15 | 0 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139225 | 8374 | 6667 |  |  | 2007-01-24 01:46 | 2007-01-24 06:51 | 305 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139226 | 8375 | 6666 |  |  | 2007-01-23 22:06 | 2007-01-24 01:30 | 204 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139227 | 8376 | 6665 |  |  | 2007-01-23 21:45 | 2007-01-23 22:02 | 17 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93482 | 8590 | 6682 |  |  | 2007-01-30 15:02 | 2007-01-30 15:02 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93483 | 8591 | 6683 |  |  | 2007-01-31 22:54 | 2007-01-31 23:12 | 18 | E0489 | GT 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93484 | 8592 | 6684 |  |  | 2007-01-31 21:57 | 2007-02-01 00:25 | 148 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93485 | 8593 | 6685 |  |  | 2007-02-01 00:38 | 2007-02-01 00:38 | 0 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93486 | 8595 | 6686 |  |  | 2007-02-01 22:09 | 2007-02-01 22:09 | 0 | E0022 | BW 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93487 | 8596 | 6689 |  |  | 2007-02-05 02:46 | 2007-02-05 02:46 | 0 | E0643 | ST 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93488 | 8597 | 6690 |  |  | 2007-02-05 03:20 | 2007-02-05 03:20 | 0 | E0643 | ST 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93489 | 8598 | 6691 |  |  | 2007-02-05 11:03 | 2007-02-05 11:03 | 0 | E0643 | ST 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93490 | 8599 | 1215 |  |  | 2007-02-05 18:36 | 2007-02-06 14:14 | 1178 | E0290 | PO-PM 2 110 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR386 - Poatina-Palmerston No. 2 110 kV transmission circuit interrupted due to intertrip signal while Machine No. 2 was shutting down at Poatina Station. | FALSE | Non-Critical
93491 | 8600 | 6693 |  |  | 2007-02-08 03:37 | 2007-02-08 03:37 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93492 | 8601 | 6692 |  |  | 2007-02-07 16:59 | 2007-02-07 16:59 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139230 | 8602 | 6701 |  |  | 2007-02-11 03:51 | 2007-02-11 04:07 | 16 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139231 | 8603 | 6700 |  |  | 2007-02-11 03:48 | 2007-02-11 03:49 | 1 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139232 | 8604 | 6699 |  |  | 2007-02-11 03:09 | 2007-02-11 03:10 | 1 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93496 | 8605 | 6698 |  |  | 2007-02-10 23:52 | 2007-02-10 23:53 | 1 | E0389 | BU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93497 | 8606 | 6697 |  |  | 2007-02-10 03:56 | 2007-02-10 03:56 | 0 | E1550 | DP 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93498 | 8607 | 6695 |  |  | 2007-02-09 06:04 | 2007-02-09 06:04 | 0 | E1004 | BU 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93499 | 8608 | 6694 |  |  | 2007-02-08 17:42 | 2007-02-08 17:42 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93500 | 8609 | 6703 |  |  | 2007-02-12 15:12 | 2007-02-12 15:13 | 1 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93501 | 8610 | 6704 |  |  | 2007-02-13 21:00 | 2007-02-13 21:00 | 0 | E0354 | KI 11 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93502 | 8611 | 6705 |  |  | 2007-02-14 04:04 | 2007-02-14 04:04 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93503 | 8612 | 6702 |  |  | 2007-02-12 10:32 | 2007-02-12 10:32 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
99459 | 8613 | 1193 |  |  | 2006-10-12 15:31 | 2006-10-12 16:45 | 74 | E0190 | LF-RK 2-SO 110 kV Transmission Circuit | Transmission | Fault | Poor Design | Transend | Completed | TRUE | 0 | TRUE |  | IR359 - Lindisfarne-Rokeby No 1 110 kV transmission circuit interrupted due to bushfire. Lindisfarne-Rokeby No 2-Sorell 110 kV transmission circuit interrupted due to incorrect substation configuration. ITOMS: Not included as bus coupler CB is on 22 kV. | FALSE | Non-Critical
99461 | 8613 | 1193 |  |  | 2006-10-12 15:31 | 2006-10-12 16:44 | 73 | E0832 | RK 11 kV A Bus | Bus | Fault | Poor Design | Transend | Completed | TRUE | 982 | TRUE |  | IR359 - Lindisfarne-Rokeby No 1 110 kV transmission circuit interrupted due to bushfire. Lindisfarne-Rokeby No 2-Sorell 110 kV transmission circuit interrupted due to incorrect substation configuration. ITOMS: Not included as bus coupler CB is on 22 kV. | FALSE | Undefined
99462 | 8613 | 1193 |  |  | 2006-10-12 15:31 | 2006-10-12 16:46 | 75 | E0833 | RK 11 kV B Bus | Bus | Fault | Poor Design | Transend | Completed | TRUE | 0 | TRUE |  | IR359 - Lindisfarne-Rokeby No 1 110 kV transmission circuit interrupted due to bushfire. Lindisfarne-Rokeby No 2-Sorell 110 kV transmission circuit interrupted due to incorrect substation configuration. ITOMS: Not included as bus coupler CB is on 22 kV. | FALSE | Undefined
99460 | 8613 | 1193 |  |  | 2006-10-12 15:31 | 2006-10-12 19:48 | 257 | E0192 | SO 110/22 kV T1 Transformer Circuit | Transformer | Fault | Poor Design | Transend | Completed | TRUE | 0 | TRUE |  | IR359 - Lindisfarne-Rokeby No 1 110 kV transmission circuit interrupted due to bushfire. Lindisfarne-Rokeby No 2-Sorell 110 kV transmission circuit interrupted due to incorrect substation configuration. ITOMS: Not included as bus coupler CB is on 22 kV. | FALSE | Non-Critical
93504 | 8614 | 6729 |  |  | 2007-02-18 22:03 | 2007-02-18 23:53 | 110 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93505 | 8615 | 6728 |  |  | 2007-02-18 21:58 | 2007-02-18 23:41 | 103 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93506 | 8616 | 6272 |  |  | 2007-02-18 21:55 | 2007-02-18 21:56 | 1 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93507 | 8617 | 6726 |  |  | 2007-02-18 21:43 | 2007-02-18 21:43 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93508 | 8618 | 6725 |  |  | 2007-02-18 21:41 | 2007-02-18 21:41 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93509 | 8621 | 6721 |  |  | 2007-02-17 07:04 | 2007-02-17 07:04 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93510 | 8622 | 6709 |  |  | 2007-02-16 18:18 | 2007-02-17 00:26 | 368 | E0158 | MB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93511 | 8623 | 6720 |  |  | 2007-02-16 23:20 | 2007-02-16 23:20 | 0 | E0837 | RK 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93512 | 8624 | 6719 |  |  | 2007-02-16 20:55 | 2007-02-16 20:55 | 0 | E0149 | NN 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93513 | 8625 | 6718 |  |  | 2007-02-16 20:48 | 2007-02-16 20:48 | 0 | E0149 | NN 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93514 | 8626 | 6717 |  |  | 2007-02-16 20:30 | 2007-02-16 20:30 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93515 | 8627 | 6716 |  |  | 2007-02-16 19:00 | 2007-02-16 19:00 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93516 | 8628 | 6715 |  |  | 2007-02-16 18:50 | 2007-02-16 18:50 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93517 | 8629 | 6714 |  |  | 2007-02-16 18:40 | 2007-02-16 18:40 | 0 | E0461 | KR 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93518 | 8630 | 6713 |  |  | 2007-02-16 18:28 | 2007-02-16 18:28 | 0 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93519 | 8631 | 6712 |  |  | 2007-02-16 18:26 | 2007-02-16 18:26 | 0 | E0156 | MB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93520 | 8632 | 6711 |  |  | 2007-02-16 18:24 | 2007-02-16 18:24 | 0 | E0156 | MB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93521 | 8633 | 6710 |  |  | 2007-02-16 18:24 | 2007-02-16 18:24 | 0 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93522 | 8634 | 6708 |  |  | 2007-02-16 17:34 | 2007-02-16 17:34 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93523 | 8635 | 6724 |  |  | 2007-02-18 15:43 | 2007-02-18 15:43 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93524 | 8636 | 6707 |  |  | 2007-02-15 07:32 | 2007-02-15 07:32 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93525 | 8637 | 6706 |  |  | 2007-02-14 08:44 | 2007-02-14 08:44 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93526 | 8638 | 6730 |  |  | 2007-02-20 12:39 | 2007-02-20 12:39 | 0 | E0156 | MB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93527 | 8639 | 6742 |  |  | 2007-02-25 23:59 | 2007-02-25 23:59 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93528 | 8640 | 6741 |  |  | 2007-02-25 21:42 | 2007-02-25 21:42 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93529 | 8641 | 6740 |  |  | 2007-02-24 15:50 | 2007-02-24 15:50 | 0 | E0149 | NN 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93530 | 8642 | 6739 |  |  | 2007-02-23 21:34 | 2007-02-23 21:34 | 0 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93532 | 8643 | 1229 |  |  | 2007-02-18 05:53 | 2007-02-18 07:29 | 96 | E1474 | RI 33 kV B2 Feeder Circuit | Feeder | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR387 - Risdon Substation transformer T4 and 33 kV 'G' Bus interrupted due to faulty circuit breaker fail input into relay G599. | FALSE | Undefined
93533 | 8643 | 1229 |  |  | 2007-02-18 05:53 | 2007-02-18 07:27 | 94 | E1475 | RI 33 kV C2 Feeder Circuit | Feeder | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR387 - Risdon Substation transformer T4 and 33 kV 'G' Bus interrupted due to faulty circuit breaker fail input into relay G599. | FALSE | Undefined
93531 | 8643 | 1229 |  |  | 2007-02-18 05:53 | 2007-02-18 07:14 | 81 | E1472 | RI 33 kV G8 Bus Coupler Circuit | Circuit Breaker | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR387 - Risdon Substation transformer T4 and 33 kV 'G' Bus interrupted due to faulty circuit breaker fail input into relay G599. | FALSE | Undefined
93535 | 8643 | 1229 |  |  | 2007-02-18 05:53 | 2007-02-18 08:15 | 142 | E1488 | RI 110/33 kV T4 Transformer Circuit | Transformer | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR387 - Risdon Substation transformer T4 and 33 kV 'G' Bus interrupted due to faulty circuit breaker fail input into relay G599. | FALSE | Non-Critical
93534 | 8643 | 1229 |  |  | 2007-02-18 05:53 | 2007-02-18 07:30 | 97 | E1483 | RI 33 kV ST1 Station Service Transformer Circuit | Station Service Transformer | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR387 - Risdon Substation transformer T4 and 33 kV 'G' Bus interrupted due to faulty circuit breaker fail input into relay G599. | FALSE | Undefined
93537 | 8644 | 1233 |  |  | 2007-02-22 18:54 | 2007-02-22 19:50 | 56 | E0854 | RB 44 kV B Bus | Bus | Fault | Vibration | Transend | Completed | TRUE | 0 | TRUE |  | IR388 - Rosebery Substation 44/22 kV T4 and T5 transformer circuits interrupted during severe lightning storms. | FALSE | Undefined
93538 | 8644 | 1233 |  |  | 2007-02-22 18:54 | 2007-02-22 19:50 | 56 | E0858 | RB 44/22 kV T4 Transformer Circuit | Transformer | Fault | Vibration | Transend | Completed | TRUE | 219 | TRUE |  | IR388 - Rosebery Substation 44/22 kV T4 and T5 transformer circuits interrupted during severe lightning storms. | FALSE | Non-Critical
93539 | 8644 | 1233 |  |  | 2007-02-22 18:54 | 2007-02-22 19:55 | 61 | E0859 | RB 44/22 kV T5 Transformer Circuit | Transformer | Fault | Vibration | Transend | Completed | TRUE | 0 | TRUE |  | IR388 - Rosebery Substation 44/22 kV T4 and T5 transformer circuits interrupted during severe lightning storms. | FALSE | Non-Critical
93536 | 8644 | 1233 |  |  | 2007-02-22 18:54 | 2007-02-22 19:50 | 56 | E0853 | RB 44 kV A Bus | Bus | Fault | Vibration | Transend | Completed | TRUE | 0 | TRUE |  | IR388 - Rosebery Substation 44/22 kV T4 and T5 transformer circuits interrupted during severe lightning storms. | FALSE | Undefined
93540 | 8645 | 6738 |  |  | 2007-02-23 21:24 | 2007-02-23 21:24 | 0 | E0149 | NN 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93541 | 8646 | 6737 |  |  | 2007-02-23 21:04 | 2007-02-23 21:05 | 1 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93542 | 8647 | 6736 |  |  | 2007-02-23 19:38 | 2007-02-23 19:38 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93544 | 8649 | 6735 |  |  | 2007-02-23 16:25 | 2007-02-23 16:26 | 1 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93545 | 8650 | 6733 |  |  | 2007-02-23 02:33 | 2007-02-23 02:34 | 1 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93546 | 8651 | 6732 |  |  | 2007-02-22 06:55 | 2007-02-22 06:55 | 0 | E0640 | ST 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93547 | 8652 | 6731 |  |  | 2007-02-21 14:31 | 2007-02-21 14:31 | 0 | E0156 | MB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93548 | 8654 | 1216 |  |  | 2007-02-16 15:10 | 2007-02-16 16:34 | 84 | E0250 | LI-WY 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 74 | TRUE |  | IR389 - Liapootah-Wayatinah 220 kV transmission circuit interrupted due to lightning. The failure of the single protection and telecommunications scheme between Wayatinah and Catagunya caused the circuit breaker A152 to remain closed extending the outage time of the circuit. | FALSE | Non-Critical
93549 | 8655 | 1217 |  |  | 2007-02-16 17:21 | 2007-02-16 17:26 | 5 | E0138 | TA-NN 1 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR389 - Tarraleah-New Norfolk No 1 110 kV transmission circuit interrupted due to lightning. | FALSE | Critical
93550 | 8656 | 1218 |  |  | 2007-02-16 17:40 | 2007-02-18 17:13 | 2853 | E0139 | TA-NN 2 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR389 - Tarraleah-New Norfolk No 2 110 kV transmission circuit interrupted due to lightning strike causing conductor failure. | FALSE | Critical
93551 | 8657 | 1221 |  |  | 2007-02-16 18:17 | 2007-02-16 18:51 | 34 | E0161 | TA-MB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR389 - Tarraleah-Meadowbank 110 kV transmission circuit interrupted due to lightning. | FALSE | Non-Critical
93552 | 8658 | 1222 |  |  | 2007-02-16 18:20 | 2007-02-16 19:08 | 48 | E0138 | TA-NN 1 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR389 - Tarraleah-New Norfolk No 1 110 kV transmission circuit interrupted due to lightning. | FALSE | Critical
93553 | 8659 | 1223 |  |  | 2007-02-16 18:30 | 2007-02-16 18:30 | 0 | E0027 | LI-CL-RE-CS 1 220 kV Transmission Circuit (Changed to E1958) | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR389 - Liapootah-Cluny-Repulse-Chapel Street No 1 220 kV transmission circuit interrupted due to lightning. | FALSE | Critical
93554 | 8661 | 1225 |  |  | 2007-02-16 20:08 | 2007-02-16 20:09 | 1 | E0125 | MB-NN 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR389 - Tarraleah-New Norfolk No 1 110 kV and Meadowbank-New Norfolk 110 kV transmission circuit interrupted due to lightning. | FALSE | Non-Critical
93555 | 8661 | 1225 |  |  | 2007-02-16 20:08 | 2007-02-16 20:11 | 3 | E0138 | TA-NN 1 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR389 - Tarraleah-New Norfolk No 1 110 kV and Meadowbank-New Norfolk 110 kV transmission circuit interrupted due to lightning. | FALSE | Critical
93556 | 8662 | 1220 |  |  | 2007-02-16 20:28 | 2007-02-16 20:29 | 1 | E0027 | LI-CL-RE-CS 1 220 kV Transmission Circuit (Changed to E1958) | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR389 - Liapootah-Cluny-Repulse-Chapel Street No 1 220 kV transmission circuit interrupted due to lightning. Faulted assets have been registered against WASP outage 8659. | FALSE | Critical
93557 | 8663 | 1226 |  |  | 2007-02-16 20:41 | 2007-02-16 20:42 | 1 | E0026 | LI-CS 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR389 - Liapootah-Chapel Street No 2 220 kV transmission circuit interrupted due to lightning. Incorrect configuration installed within the protection relays resulted in the inadvertent trip of breaker S752 at Chapel Street. | FALSE | Critical
93558 | 8665 | 1230 |  |  | 2007-02-22 13:14 | 2007-02-22 13:14 | 0 | E0275 | WA-PM 2 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR390 - Waddamana-Palmerston No 2 110 kV transmission circuit momentarily interrupted due to suspected lightning strike. | FALSE | Critical
93559 | 8667 | 1232 |  |  | 2007-02-22 15:22 | 2007-02-22 17:50 | 148 | E0275 | WA-PM 2 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR390 - Waddamana-Palmerston No 2 110 kV and Waddamana-Lindisfarne No 2 110 kV transmission circuits interrupted due to lightning strike. Logic within the bay controller failed to allow the remote close of breaker E752 at Waddamana. This resulted in an extended outage of the Waddamana-Palmerston circuit. Tripping of the WA-LF circuit was not a protection problem but rather that the D152 breaker at Waddamana had to trip to clear the fault on the Waddamana-Palmerston circuit. | FALSE | Critical
93560 | 8667 | 1232 |  |  | 2007-02-22 15:22 | 2007-02-22 15:35 | 13 | E0351 | WA-LF 2 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR390 - Waddamana-Palmerston No 2 110 kV and Waddamana-Lindisfarne No 2 110 kV transmission circuits interrupted due to lightning strike. Logic within the bay controller failed to allow the remote close of breaker E752 at Waddamana. This resulted in an extended outage of the Waddamana-Palmerston circuit. Tripping of the WA-LF circuit was not a protection problem but rather that the D152 breaker at Waddamana had to trip to clear the fault on the Waddamana-Palmerston circuit. | FALSE | Undefined
93561 | 8670 | 1238 |  |  | 2007-02-23 19:43 | 2007-02-23 19:43 | 0 | E0026 | LI-CS 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR392 - LI-CS 2 220 kV, MB-NN 1 110 kV and TA-NN 2 110 kV transmission circuits and bus coupler circuit breaker S752 at Chapel Street Substation interrupted due to lightning. | FALSE | Critical
93563 | 8670 | 1238 |  |  | 2007-02-23 19:43 | 2007-02-23 19:48 | 5 | E0125 | MB-NN 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR392 - LI-CS 2 220 kV, MB-NN 1 110 kV and TA-NN 2 110 kV transmission circuits and bus coupler circuit breaker S752 at Chapel Street Substation interrupted due to lightning. | FALSE | Non-Critical
93564 | 8670 | 1238 |  |  | 2007-02-23 19:43 | 2007-02-23 19:48 | 5 | E0139 | TA-NN 2 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR392 - LI-CS 2 220 kV, MB-NN 1 110 kV and TA-NN 2 110 kV transmission circuits and bus coupler circuit breaker S752 at Chapel Street Substation interrupted due to lightning. | FALSE | Critical
93562 | 8670 | 1238 |  |  | 2007-02-23 19:43 | 2007-02-23 20:54 | 71 | E0038 | CS 220 kV By-Pass Bus | Bus | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR392 - LI-CS 2 220 kV, MB-NN 1 110 kV and TA-NN 2 110 kV transmission circuits and bus coupler circuit breaker S752 at Chapel Street Substation interrupted due to lightning. | FALSE | Undefined
93565 | 8671 | 1240 |  |  | 2007-02-23 21:42 | 2007-02-23 21:43 | 1 | E0972 | CS-KI-EL 110 kV Transmission Circuit (Changed to E1956) | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR392 - Chapel Street-Kingston-Electrona 110 kV transmission circuit interrupted due to lightning. | FALSE | Non-Critical
93566 | 8672 | 1241 |  |  | 2007-02-23 22:11 | 2007-02-23 22:13 | 2 | E0030 | CS-KI-KR 110 kV Transmission Circuit (changed to E1955) | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR392 - Chapel Street-Kingston-Knights Road 110 kV transmission circuit interrupted due to lightning. | FALSE | Non-Critical
93610 | 8795 | 1234 |  |  | 2007-02-22 17:02 | 2007-02-22 17:15 | 13 | E0538 | SH-FA 1 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 1847 | TRUE |  | IR391 - SH-FA 1 and SH-FA 2 220 kV transmission circuits interrupted due to lightning strike. Supply to west coast interrupted. | FALSE | Critical
93611 | 8795 | 1234 |  |  | 2007-02-22 17:02 | 2007-02-22 17:16 | 14 | E0539 | SH-FA 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 0 | TRUE |  | IR391 - SH-FA 1 and SH-FA 2 220 kV transmission circuits interrupted due to lightning strike. Supply to west coast interrupted. | FALSE | Critical
93612 | 8795 | 1234 |  |  | 2007-02-22 17:02 | 2007-02-22 17:33 | 31 | E0714 | FA-TI 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 0 | TRUE |  | IR391 - SH-FA 1 and SH-FA 2 220 kV transmission circuits interrupted due to lightning strike. Supply to west coast interrupted. | FALSE | Non-Critical
93613 | 8795 | 1234 |  |  | 2007-02-22 17:02 | 2007-02-22 17:34 | 32 | E0715 | FA-JB 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 0 | TRUE |  | IR391 - SH-FA 1 and SH-FA 2 220 kV transmission circuits interrupted due to lightning strike. Supply to west coast interrupted. | FALSE | Non-Critical
93614 | 8795 | 1234 |  |  | 2007-02-22 17:02 | 2007-02-22 17:34 | 32 | E0716 | FA-RC 1 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 0 | TRUE |  | IR391 - SH-FA 1 and SH-FA 2 220 kV transmission circuits interrupted due to lightning strike. Supply to west coast interrupted. | FALSE | Non-Critical
93615 | 8795 | 1234 |  |  | 2007-02-22 17:02 | 2007-02-22 17:35 | 33 | E0717 | FA-RC 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 0 | TRUE |  | IR391 - SH-FA 1 and SH-FA 2 220 kV transmission circuits interrupted due to lightning strike. Supply to west coast interrupted. | FALSE | Non-Critical
93616 | 8795 | 1234 |  |  | 2007-02-22 17:02 | 2007-02-22 17:35 | 33 | E1391 | FA-BA 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 0 | TRUE |  | IR391 - SH-FA 1 and SH-FA 2 220 kV transmission circuits interrupted due to lightning strike. Supply to west coast interrupted. | FALSE | Undefined
93617 | 8796 | 1242 |  |  | 2007-02-26 12:47 | 2007-02-26 12:52 | 5 | E0206 | RI 110 kV G7 Circuit Breaker | Circuit Breaker | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR393 - Bus coupler circuit breaker G752 at Risdon Substation tripped due to Contractor error while performing routine protection tests. | FALSE | Undefined
93618 | 8797 | 1243 |  |  | 2007-02-26 13:53 | 2007-03-07 16:13 | 13100 | E0034 | CS 220/110 kV T4 Transformer Circuit | Transformer | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR395 - Chapel Street transformer T4 interrupted due to OLTC pressure alarm caused by poor OLTC design. Was originally classified as 'Third Party' outage (and hence was not included in ITOMS), however discussion at the QPR forum (Q1 2007-08) resulted in this being classified as an 'Equipment Failure'. | FALSE | Non-Critical
118387 | 8798 | 1244 |  |  | 2007-02-27 06:20 | 2007-02-27 06:20 | 0 | E1621 | RI 110 kV Bus SPS | Bus | Fault | Incorrect Drawings | Transend | Completed | TRUE | 722 | TRUE |  | IR394 - Load shedding intitiated at Risdon Substation due to incorrect drawings utilised during transformer maintenance and metering testing. | FALSE | Undefined
93620 | 8800 | 6761 |  |  | 2007-03-08 00:39 | 2007-03-08 00:39 | 0 | E1531 | MY 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93621 | 8803 | 6760 |  |  | 2007-03-07 22:56 | 2007-03-07 23:30 | 34 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93622 | 8804 | 6759 |  |  | 2007-03-07 09:48 | 2007-03-07 09:48 | 0 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93623 | 8805 | 6757 |  |  | 2007-02-05 21:28 | 2007-02-05 21:29 | 1 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93624 | 8806 | 6753 |  |  | 2007-03-03 03:03 | 2007-03-03 03:03 | 0 | E1000 | BU 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93625 | 8807 | 6752 |  |  | 2007-03-02 22:27 | 2007-03-02 22:28 | 1 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93626 | 8809 | 6754 |  |  | 2007-03-03 13:04 | 2007-03-03 13:58 | 54 | E1004 | BU 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93627 | 8810 | 6756 |  |  | 2007-03-04 23:23 | 2007-03-04 23:23 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93628 | 8811 | 6755 |  |  | 2007-03-04 07:24 | 2007-03-04 07:57 | 33 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93629 | 8812 | 6751 |  |  | 2007-03-02 02:41 | 2007-03-02 02:41 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139233 | 8813 | 6750 |  |  | 2007-03-02 02:22 | 2007-03-02 02:22 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93631 | 8814 | 6749 |  |  | 2007-03-01 03:45 | 2007-03-01 03:45 | 0 | E0158 | MB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93632 | 8815 | 6748 |  |  | 2007-03-01 03:31 | 2007-03-01 03:31 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93633 | 8816 | 6747 |  |  | 2007-02-28 16:41 | 2007-02-28 16:41 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93634 | 8817 | 6746 |  |  | 2007-02-28 09:46 | 2007-02-28 09:46 | 0 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93635 | 8818 | 6745 |  |  | 2007-02-27 22:10 | 2007-02-27 22:10 | 0 | E0898 | SD 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93636 | 8819 | 6743 |  |  | 2007-02-27 05:22 | 2007-02-27 05:22 | 0 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93637 | 8820 | 6765 |  |  | 2007-03-11 21:11 | 2007-03-11 21:11 | 0 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93638 | 8821 | 6764 |  |  | 2007-03-11 13:49 | 2007-03-11 14:29 | 40 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93639 | 8822 | 6763 |  |  | 2007-03-10 19:09 | 2007-03-10 19:09 | 0 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93640 | 8823 | 6762 |  |  | 2007-03-08 13:04 | 2007-03-08 13:04 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93641 | 8824 | 1245 |  |  | 2007-03-13 21:02 | 2007-03-13 22:00 | 58 | E0594 | DP 110/22 kV T2 Transformer Circuit | Transformer | Fault | Incorrect Drawings | Transend | Completed | TRUE | 0 | TRUE |  | IR396 - Devonport Substation transformer T2 interrupted during injection tests due to incorrect drawing. | FALSE | Non-Critical
93642 | 8826 | 6774 |  |  | 2007-03-18 06:05 | 2007-03-18 06:05 | 0 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93643 | 8827 | 6773 |  |  | 2007-03-18 02:18 | 2007-03-18 02:18 | 0 | E0760 | NW 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93644 | 8828 | 6776 |  |  | 2007-03-20 02:17 | 2007-03-20 02:17 | 0 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93645 | 8829 | 6775 |  |  | 2007-03-19 06:37 | 2007-03-19 06:38 | 1 | E1004 | BU 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93646 | 8830 | 6766 |  |  | 2007-03-14 19:29 | 2007-03-14 20:33 | 64 | E0826 | RA 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93647 | 8831 | 6767 |  |  | 2007-03-14 22:38 | 2007-03-14 22:38 | 0 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93648 | 8832 | 6768 |  |  | 2007-03-15 14:29 | 2007-03-15 14:29 | 0 | E1529 | MY 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93649 | 8833 | 6769 |  |  | 2007-03-16 14:43 | 2007-03-16 15:21 | 38 | E1474 | RI 33 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93650 | 8834 | 6770 |  |  | 2007-03-16 20:18 | 2007-03-16 20:18 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93651 | 8835 | 6771 |  |  | 2007-03-16 22:03 | 2007-03-16 22:03 | 0 | E0762 | NW 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93652 | 8836 | 6772 |  |  | 2007-03-17 08:57 | 2007-03-17 08:57 | 0 | E0946 | UL 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93653 | 8837 | 6777 |  |  | 2007-03-22 22:37 | 2007-03-22 22:54 | 17 | E0826 | RA 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93654 | 8839 | 6778 |  |  | 2007-03-23 07:30 | 2007-03-23 08:07 | 37 | E0826 | RA 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93655 | 8840 | 6779 |  |  | 2007-03-23 13:34 | 2007-03-23 13:34 | 0 | E0762 | NW 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93656 | 8841 | 6780 |  |  | 2007-03-23 15:19 | 2007-03-23 15:38 | 19 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93657 | 8842 | 6781 |  |  | 2007-03-23 16:03 | 2007-03-23 16:57 | 54 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93660 | 8845 | 6784 |  |  | 2007-03-23 23:25 | 2007-03-24 02:55 | 210 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93661 | 8846 | 6785 |  |  | 2007-03-25 01:36 | 2007-03-25 01:37 | 1 | E0902 | TR 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93662 | 8847 | 6786 |  |  | 2007-03-25 08:54 | 2007-03-25 08:54 | 0 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93700 | 8942 | 6790 |  |  | 2007-03-28 09:02 | 2007-03-28 09:02 | 0 | E0356 | KI 11 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139234 | 8944 | 6788 |  |  | 2007-03-27 06:58 | 2007-03-27 06:58 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93702 | 8945 | 6787 |  |  | 2007-03-26 23:52 | 2007-03-26 23:52 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93703 | 8946 | 6801 |  |  | 2007-04-02 06:42 | 2007-04-02 08:09 | 87 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93704 | 8947 | 6800 |  |  | 2007-04-02 02:31 | 2007-04-02 02:31 | 0 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93705 | 8948 | 6799 |  |  | 2007-04-01 17:33 | 2007-04-01 17:33 | 0 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93706 | 8949 | 6793 |  |  | 2007-03-30 10:31 | 2007-03-30 11:27 | 56 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93707 | 8950 | 6794 |  |  | 2007-03-30 13:49 | 2007-03-30 15:06 | 77 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault | Unknown | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93708 | 8951 | 6795 |  |  | 2007-03-30 14:15 | 2007-03-30 15:14 | 59 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93709 | 8952 | 6798 |  |  | 2007-04-01 08:16 | 2007-04-01 08:17 | 1 | E0197 | SO 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93710 | 8953 | 6797 |  |  | 2007-04-01 00:33 | 2007-04-01 00:34 | 1 | E0389 | BU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93711 | 8954 | 6796 |  |  | 2007-03-31 20:53 | 2007-03-31 20:53 | 0 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93712 | 8955 | 6792 |  |  | 2007-03-29 19:23 | 2007-03-29 19:23 | 0 | E0764 | NW 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93713 | 8956 | 6791 |  |  | 2007-03-29 08:33 | 2007-03-29 09:24 | 51 | E0462 | KR 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93719 | 8964 | 6802 |  |  | 2007-04-04 18:05 | 2007-04-04 21:26 | 201 | E0358 | KI 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139235 | 8965 | 6803 |  |  | 2007-04-05 16:19 | 2007-04-05 16:19 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93721 | 8966 | 6804 |  |  | 2007-04-06 02:20 | 2007-04-06 02:20 | 0 | E1000 | BU 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93722 | 8967 | 6805 |  |  | 2007-04-06 02:20 | 2007-04-06 02:20 | 0 | E0389 | BU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93723 | 8968 | 6806 |  |  | 2007-04-06 06:10 | 2007-04-06 07:38 | 88 | E0186 | TU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93724 | 8969 | 6807 |  |  | 2007-04-06 09:25 | 2007-04-06 09:25 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93725 | 8970 | 6808 |  |  | 2007-04-08 02:15 | 2007-04-08 02:31 | 16 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139236 | 8971 | 6809 |  |  | 2007-04-09 07:30 | 2007-04-09 07:30 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139237 | 8973 | 6810 |  |  | 2007-04-11 02:57 | 2007-04-11 03:31 | 34 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93728 | 8974 | 6811 |  |  | 2007-04-11 17:13 | 2007-04-11 17:13 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93729 | 8975 | 6812 |  |  | 2007-04-12 14:07 | 2007-04-12 14:45 | 38 | E0906 | TR 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93730 | 8976 | 6813 |  |  | 2007-04-13 10:40 | 2007-04-13 10:40 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139238 | 8977 | 6814 |  |  | 2007-04-14 06:30 | 2007-04-14 06:30 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93732 | 8978 | 6815 |  |  | 2007-04-14 17:06 | 2007-04-14 17:06 | 0 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93769 | 9037 | 1248 |  |  | 2007-04-02 09:02 | 2007-04-02 11:02 | 120 | E0250 | LI-WY 220 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR404 - Liapootah-Wayatinah 220 kV transmission circuit interrupted due to intertrip generated by Hydro asset failure. | FALSE | Non-Critical
93770 | 9038 | 1250 |  |  | 2007-04-14 04:52 | 2007-04-14 08:36 | 224 | E1540 | MY 22 kV B Bus | Bus | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR405 - Mowbray Substation 22 kV 'A' and 'B' buses interrupted due to faulty current transformer. Cause of CT failure unknown. | FALSE | Undefined
93771 | 9038 | 1250 |  |  | 2007-04-14 04:52 | 2007-04-14 08:36 | 224 | E1542 | MY 22 kV A Bus | Bus | Fault | Internal Fault | Transend | Completed | TRUE | 1399 | TRUE |  | IR405 - Mowbray Substation 22 kV 'A' and 'B' buses interrupted due to faulty current transformer. Cause of CT failure unknown. | FALSE | Undefined
93772 | 9039 | 1251 |  |  | 2007-04-15 17:28 | 2007-04-15 18:55 | 87 | E0274 | PM-AV 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 743 | TRUE |  | IR406 - Palmerston-Avoca 110 kV transmission circuit interrupted due to lightning. | FALSE | Non-Critical
93773 | 9040 | 1252 |  |  | 2007-04-18 07:08 | 2007-04-18 07:17 | 9 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 157 | TRUE |  | IR407 - Farrell-Rosebery-Queenstown 110 kV transmission circuit interrupted due to lightning. | FALSE | Non-Critical
93774 | 9041 | 6825 |  |  | 2007-04-22 13:07 | 2007-04-22 15:09 | 122 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93775 | 9042 | 6826 |  |  | 2007-04-22 13:07 | 2007-04-22 13:07 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93776 | 9043 | 6824 |  |  | 2007-04-22 13:06 | 2007-04-22 13:06 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93777 | 9044 | 6823 |  |  | 2007-04-22 13:05 | 2007-04-22 13:05 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93778 | 9045 | 6822 |  |  | 2007-04-22 09:49 | 2007-04-22 09:50 | 1 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93779 | 9046 | 6821 |  |  | 2007-05-18 21:54 | 2007-05-18 22:16 | 22 | E0496 | GT 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93780 | 9047 | 6820 |  |  | 2007-04-18 15:31 | 2007-04-18 16:15 | 44 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93781 | 9048 | 6819 |  |  | 2007-04-18 10:21 | 2007-04-18 10:21 | 0 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93782 | 9049 | 6816 |  |  | 2007-04-16 12:44 | 2007-04-16 12:45 | 1 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93783 | 9050 | 6817 |  |  | 2007-04-16 20:19 | 2007-04-16 20:19 | 0 | E1041 | SD 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93784 | 9051 | 6818 |  |  | 2007-04-18 08:32 | 2007-04-18 08:32 | 0 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93785 | 9052 | 1253 |  |  | 2007-04-19 08:44 | 2007-04-19 19:24 | 640 | E0785 | QU 110/22 kV T1 Transformer Circuit | Transformer | Fault | Internal Fault | Transend | Completed | TRUE | 64 | TRUE |  | IR411 - Transformer T1 at Que Substation interrupted due to suspected relay failure. | FALSE | Non-Critical
93835 | 9109 | 6827 |  |  | 2007-04-24 01:17 | 2007-04-24 01:17 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139241 | 9110 | 6828 |  |  | 2007-04-24 01:17 | 2007-04-24 07:14 | 357 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93837 | 9111 | 6829 |  |  | 2007-04-24 09:56 | 2007-04-24 10:23 | 27 | E0767 | NW 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93838 | 9112 | 6830 |  |  | 2007-04-24 15:02 | 2007-04-24 15:07 | 5 | E0764 | NW 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93839 | 9113 | 6831 |  |  | 2007-04-26 09:41 | 2007-04-26 10:28 | 47 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93840 | 9114 | 6833 |  |  | 2007-04-26 22:35 | 2007-04-26 22:35 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93841 | 9115 | 6834 |  |  | 2007-04-27 14:48 | 2007-04-27 15:20 | 32 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93842 | 9116 | 6835 |  |  | 2007-04-28 12:17 | 2007-04-28 12:17 | 0 | E0762 | NW 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93843 | 9117 | 6836 |  |  | 2007-04-28 16:51 | 2007-04-28 16:51 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93844 | 9118 | 6837 |  |  | 2007-04-29 07:23 | 2007-04-29 07:23 | 0 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93845 | 9119 | 6838 |  |  | 2007-04-29 12:20 | 2007-04-29 12:21 | 1 | E0820 | RA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93846 | 9120 | 6839 |  |  | 2007-04-30 08:15 | 2007-04-30 09:04 | 49 | E0078 | CR 33 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93847 | 9122 | 6840 |  |  | 2007-05-01 14:55 | 2007-05-01 19:05 | 250 | E0075 | CR 33 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93848 | 9123 | 6841 |  |  | 2007-05-02 03:03 | 2007-05-02 04:16 | 73 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93849 | 9124 | 6842 |  |  | 2007-05-02 06:41 | 2007-05-02 06:41 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93850 | 9125 | 6843 |  |  | 2007-05-02 08:29 | 2007-05-02 09:50 | 81 | E0760 | NW 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93851 | 9126 | 6844 |  |  | 2007-05-03 08:58 | 2007-05-03 08:58 | 0 | E1001 | BU 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93852 | 9127 | 6845 |  |  | 2007-05-03 10:05 | 2007-05-03 10:05 | 0 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93853 | 9128 | 6846 |  |  | 2007-05-03 10:11 | 2007-05-03 10:11 | 0 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93854 | 9129 | 6847 |  |  | 2007-05-03 10:37 | 2007-05-03 10:38 | 1 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93855 | 9130 | 6848 |  |  | 2007-05-03 10:23 | 2007-05-03 10:52 | 29 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93856 | 9131 | 6849 |  |  | 2007-05-03 11:07 | 2007-05-03 11:07 | 0 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93857 | 9132 | 6850 |  |  | 2007-05-03 09:47 | 2007-05-03 11:09 | 82 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93858 | 9133 | 6851 |  |  | 2007-05-03 10:23 | 2007-05-03 11:26 | 63 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93859 | 9134 | 6852 |  |  | 2007-05-03 09:53 | 2007-05-03 12:42 | 169 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93861 | 9136 | 6854 |  |  | 2007-05-03 15:04 | 2007-05-03 15:04 | 0 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93862 | 9137 | 6855 |  |  | 2007-05-03 01:12 | 2007-05-03 15:12 | 840 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93863 | 9138 | 6856 |  |  | 2007-05-03 15:16 | 2007-05-03 15:16 | 0 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93864 | 9139 | 6857 |  |  | 2007-05-03 15:40 | 2007-05-03 15:41 | 1 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93865 | 9140 | 6858 |  |  | 2007-05-04 05:35 | 2007-05-04 07:11 | 96 | E1592 | CS 11 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93866 | 9141 | 6859 |  |  | 2007-05-04 16:44 | 2007-05-04 17:01 | 17 | E0489 | GT 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93867 | 9142 | 6860 |  |  | 2007-05-04 19:57 | 2007-05-04 19:57 | 0 | E1051 | SR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93868 | 9143 | 6861 |  |  | 2007-05-04 20:34 | 2007-05-04 20:56 | 22 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93869 | 9144 | 6862 |  |  | 2007-05-04 02:54 | 2007-05-04 21:54 | 1140 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93870 | 9145 | 6863 |  |  | 2007-05-04 22:55 | 2007-05-04 22:55 | 0 | E1530 | MY 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93871 | 9147 | 6865 |  |  | 2007-05-04 23:27 | 2007-05-04 23:27 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93873 | 9149 | 6867 |  |  | 2007-05-05 00:13 | 2007-05-05 00:13 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93874 | 9150 | 6868 |  |  | 2007-05-05 00:26 | 2007-05-05 00:48 | 22 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93875 | 9151 | 6869 |  |  | 2007-05-05 00:48 | 2007-05-05 01:07 | 19 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93877 | 9153 | 6873 |  |  | 2007-05-05 01:46 | 2007-05-05 01:47 | 1 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93879 | 9155 | 6875 |  |  | 2007-05-05 02:56 | 2007-05-05 05:08 | 132 | E0888 | DE 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93880 | 9156 | 6876 |  |  | 2007-05-07 07:30 | 2007-05-07 07:50 | 20 | E0199 | SO 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93881 | 9157 | 6877 |  |  | 2007-05-08 00:25 | 2007-05-08 00:48 | 23 | E0819 | RA 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93882 | 9158 | 6878 |  |  | 2007-05-08 00:48 | 2007-05-08 00:48 | 0 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93883 | 9159 | 6879 |  |  | 2007-05-08 01:18 | 2007-05-08 01:18 | 0 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93884 | 9160 | 6880 |  |  | 2007-05-08 01:48 | 2007-05-08 01:48 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93885 | 9161 | 6881 |  |  | 2007-05-08 01:55 | 2007-05-08 01:55 | 0 | E0495 | GT 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93886 | 9162 | 6882 |  |  | 2007-05-08 04:54 | 2007-05-08 04:54 | 0 | E1393 | SD 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93887 | 9163 | 6883 |  |  | 2007-05-08 19:09 | 2007-05-08 19:09 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93888 | 9164 | 6884 |  |  | 2007-05-08 19:13 | 2007-05-08 22:14 | 181 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93889 | 9165 | 6885 |  |  | 2007-05-10 13:11 | 2007-05-10 13:11 | 0 | E1531 | MY 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93890 | 9166 | 6886 |  |  | 2007-05-10 14:14 | 2007-05-10 14:35 | 21 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93892 | 9171 | 1254 |  |  | 2007-05-04 09:06 | 2007-05-04 09:22 | 16 | E1487 | RI 33 kV J Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR412 - Risdon Substation 33 kV 'J' Bus and transformer T6 interrupted due to contractor error. no load lost as as both feeders are duplicate supplies to Derwent Park and East Hobart.ITOMS: Not included due to out of scope 33 kV. | FALSE | Undefined
93891 | 9171 | 1254 |  |  | 2007-05-04 09:06 | 2007-05-04 09:22 | 16 | E1468 | RI 110/33 kV T6 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR412 - Risdon Substation 33 kV 'J' Bus and transformer T6 interrupted due to contractor error. no load lost as as both feeders are duplicate supplies to Derwent Park and East Hobart.ITOMS: Not included due to out of scope 33 kV. | FALSE | Non-Critical
146150 | 9173 | 1256 |  |  | 2007-05-04 23:46 | 2007-05-05 01:06 | 80 | E0169 | TU-BG-DB 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 7 | TRUE |  | IR416 - Tungatinah-Butlers Gorge-Derwent Bridge 110 kV transmission circuit interrupted. | FALSE | Non-Critical
93894 | 9174 | 1257 |  |  | 2007-05-13 00:01 | 2007-05-13 01:00 | 59 | E0268 | PO-PM 6 220 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR420 - Poatina-Palmerston No 6 220 kV transmission circuit interrupted due to fault in Generator installation. | FALSE | Non-Critical
93895 | 9175 | 1258 |  |  | 2007-05-17 16:32 | 2007-05-17 17:51 | 79 | E0154 | MB 110/22 kV T4 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 152 | TRUE |  | IR421 - Meadowbank Substation transformer T4 interrupted due to incorrect protection settings. ITOMS: Not included as the protection settings that had been applied incorrectly were for low voltage assets only (ie. outside ITOMS scope). | FALSE | Non-Critical
195504 | 9176 | 1259 |  |  | 2007-05-18 08:59 | 2007-05-18 08:59 | 0 | E0298 | AV-SM 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 1 | TRUE |  | IR422 - Avoca-St Marys 110 kV transmission circuit momentarily interrupted due to lightning strike. | FALSE | Non-Critical
93897 | 9177 | 1260 |  |  | 2007-05-26 17:22 | 2007-05-28 17:03 | 2861 | E0028 | GO-CS 1 220 kV Transmission Circuit | Transmission | Fault | Fatigue | Transend | Completed | TRUE | 0 | TRUE |  | IR430 - Gordon-Chapel Street No 1 220 kV transmission circuit interrupted due to broken dropper conductor. ITOMS: Classified under 'Other cct end equip due to the fact that it was the termination palm that failed (inside the substation) rather than the conductor itself. | FALSE | Critical
93898 | 10863 | 6916 |  |  | 2007-05-31 04:34 | 2007-05-31 04:34 | 0 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94073 | 10985 | 6902 |  |  | 2007-05-21 16:47 | 2007-05-21 16:47 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94074 | 10986 | 6901 |  |  | 2007-05-21 11:37 | 2007-05-21 11:37 | 0 | E1042 | SD 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94076 | 10988 | 6899 |  |  | 2007-05-20 14:49 | 2007-05-20 14:49 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94077 | 10990 | 6918 |  |  | 2007-06-05 12:04 | 2007-06-05 12:04 | 0 | E1538 | MY 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94078 | 10991 | 6898 |  |  | 2007-05-20 06:48 | 2007-05-20 06:48 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
105717 | 10992 | 6897 |  |  | 2007-05-19 06:48 | 2007-05-19 19:30 | 762 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94080 | 10993 | 6896 |  |  | 2007-05-19 18:36 | 2007-05-19 18:36 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94081 | 10994 | 6895 |  |  | 2007-05-19 07:12 | 2007-05-19 07:12 | 0 | E0412 | EL 11 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94082 | 10995 | 6893 |  |  | 2007-05-18 18:11 | 2007-05-18 18:11 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94083 | 10996 | 6889 |  |  | 2007-05-18 06:29 | 2007-05-18 06:47 | 18 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94085 | 10998 | 6892 |  |  | 2007-05-18 12:33 | 2007-05-18 12:53 | 20 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94086 | 10999 | 6891 |  |  | 2007-05-18 10:44 | 2007-05-18 11:57 | 73 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94087 | 11000 | 1261 |  |  | 2007-06-05 09:05 | 2007-06-05 09:15 | 10 | E0714 | FA-TI 220 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR431 - Farrell-tribute 220 kV transmission circuit interrupted due to intertrip caused by Hydro. | FALSE | Non-Critical
94088 | 11001 | 1262 |  |  | 2007-06-05 22:05 | 2007-06-07 14:04 | 2399 | E0878 | SR 110/22 kV T3 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR440 - Savage River transformer T3 interrupted due to poor contractor workmanship resulting in cable failure. ITOMS: Not included as cable is 22 kV. | FALSE | Non-Critical
94089 | 11002 | 6890 |  |  | 2007-05-18 10:31 | 2007-05-18 10:49 | 18 | E0489 | GT 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94090 | 11004 | 6915 |  |  | 2007-05-31 03:49 | 2007-05-31 04:05 | 16 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94091 | 11005 | 6914 |  |  | 2007-05-30 03:21 | 2007-05-30 04:51 | 90 | E0415 | EL 11 kV XE2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94092 | 11006 | 6913 |  |  | 2007-05-30 01:33 | 2007-05-30 02:30 | 57 | E0354 | KI 11 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94093 | 11007 | 6912 |  |  | 2007-05-30 00:19 | 2007-05-30 00:21 | 2 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94094 | 11008 | 6919 |  |  | 2007-06-07 08:48 | 2007-06-07 08:48 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94095 | 11009 | 6734 |  |  | 2007-02-23 14:24 | 2007-02-23 14:24 | 0 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139288 | 11010 | 6577 |  |  | 2006-12-21 04:25 | 2006-12-21 07:17 | 172 | E0644 | ST 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94096 | 11014 | 6921 |  |  | 2007-06-21 01:56 | 2007-06-21 01:56 | 0 | E1550 | DP 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94097 | 11015 | 6922 |  |  | 2007-06-21 09:37 | 2007-06-21 09:38 | 1 | E0970 | SO 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94098 | 11016 | 6923 |  |  | 2007-06-21 16:20 | 2007-06-21 16:21 | 1 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94099 | 11017 | 6924 |  |  | 2007-06-24 22:09 | 2007-06-24 22:09 | 0 | E0156 | MB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139289 | 11018 | 6925 |  |  | 2007-06-25 07:32 | 2007-06-25 07:32 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94165 | 11102 | 1263 |  |  | 2007-06-19 00:39 | 2007-06-19 00:39 | 0 | E1497 | NW-SD 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR435 - Norwood-Scottsdale-Derby 110 kV transmission circuit momentarily interrupted five times due to OPGW clashing with phase conductor in wind. Total outage duration approximately 2 minutes. | FALSE | Non-Critical
94166 | 11102 | 1263 |  |  | 2007-06-19 00:41 | 2007-06-19 00:41 | 0 | E1497 | NW-SD 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR435 - Norwood-Scottsdale-Derby 110 kV transmission circuit momentarily interrupted five times due to OPGW clashing with phase conductor in wind. Total outage duration approximately 2 minutes. | FALSE | Non-Critical
94167 | 11102 | 1263 |  |  | 2007-06-19 00:43 | 2007-06-19 00:43 | 0 | E1497 | NW-SD 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR435 - Norwood-Scottsdale-Derby 110 kV transmission circuit momentarily interrupted five times due to OPGW clashing with phase conductor in wind. Total outage duration approximately 2 minutes. | FALSE | Non-Critical
94163 | 11102 | 1263 |  |  | 2007-06-18 22:48 | 2007-06-18 22:48 | 0 | E1497 | NW-SD 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR435 - Norwood-Scottsdale-Derby 110 kV transmission circuit momentarily interrupted five times due to OPGW clashing with phase conductor in wind. Total outage duration approximately 2 minutes. | FALSE | Non-Critical
94164 | 11102 | 1263 |  |  | 2007-06-19 00:28 | 2007-06-19 00:28 | 0 | E1497 | NW-SD 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR435 - Norwood-Scottsdale-Derby 110 kV transmission circuit momentarily interrupted five times due to OPGW clashing with phase conductor in wind. Total outage duration approximately 2 minutes. | FALSE | Non-Critical
94168 | 11103 | 1266 |  |  | 2007-06-28 11:46 | 2007-07-08 16:01 | 14655 | E0777 | PL 110/22 kV T2 Transformer Circuit | Transformer | Fault | Moisture Ingress | Transend | Completed | TRUE | 0 | TRUE |  | IR436 - Port Latta transformer T2 interrupted due to cable box failure caused by moisture ingress. | FALSE | Non-Critical
94179 | 11131 | 6932 |  |  | 2007-07-08 11:12 | 2007-07-08 12:23 | 71 | E0415 | EL 11 kV XE2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94180 | 11132 | 6933 |  |  | 2007-07-11 00:55 | 2007-07-11 00:55 | 0 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94181 | 11134 | 6934 |  |  | 2007-07-12 06:59 | 2007-07-12 07:21 | 22 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94182 | 11135 | 6935 |  |  | 2007-07-12 10:18 | 2007-07-12 12:25 | 127 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94183 | 11136 | 6936 |  |  | 2007-07-13 18:57 | 2007-07-13 18:57 | 0 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94184 | 11138 | 3937 |  |  | 2007-07-16 07:44 | 2007-07-16 07:45 | 1 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94185 | 11139 | 6941 |  |  | 2007-07-17 06:00 | 2007-07-17 06:17 | 17 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94186 | 11140 | 6940 |  |  | 2007-07-17 05:58 | 2007-07-17 05:58 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94187 | 11141 | 6939 |  |  | 2007-07-17 05:21 | 2007-07-17 05:21 | 0 | E1393 | SD 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94188 | 11142 | 6942 |  |  | 2007-07-17 10:15 | 2007-07-17 10:15 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94189 | 11143 | 6943 |  |  | 2007-07-18 04:42 | 2007-07-18 08:17 | 215 | E1051 | SR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
105527 | 11144 | 6945 |  |  | 2007-07-18 18:56 | 2007-07-18 18:56 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94190 | 11145 | 6944 |  |  | 2007-07-18 09:49 | 2007-07-18 14:48 | 299 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94191 | 11146 | 6930 |  |  | 2007-07-03 03:25 | 2007-07-03 03:26 | 1 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94192 | 11147 | 6946 |  |  | 2007-07-21 07:18 | 2007-07-21 07:18 | 0 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139292 | 11148 | 6947 |  |  | 2007-07-23 09:24 | 2007-07-23 09:24 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94194 | 11149 | 6948 |  |  | 2007-07-24 08:52 | 2007-07-24 08:52 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139293 | 11150 | 6949 |  |  | 2007-07-26 12:45 | 2007-07-26 12:45 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94318 | 11326 | 1267 |  |  | 2007-07-24 08:52 | 2007-07-24 10:04 | 72 | E0647 | ST 110/22 kV T1 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR438 - Smithton Substation transformer T1 interrupted due to incorrect earthing process and incorrect protection settings. | FALSE | Non-Critical
94319 | 11326 | 1267 |  |  | 2007-07-24 08:52 | 2007-07-24 10:12 | 80 | E1565 | BP-SB-ST 110 kV Transmission Circuit | Transmission | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR438 - Smithton Substation transformer T1 interrupted due to incorrect earthing process and incorrect protection settings. | FALSE | Undefined
94317 | 11326 | 1267 |  |  | 2007-07-24 08:52 | 2007-07-24 10:00 | 68 | E0631 | ST 110 kV A Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR438 - Smithton Substation transformer T1 interrupted due to incorrect earthing process and incorrect protection settings. | FALSE | Undefined
94320 | 11327 | 6950 |  |  | 2007-08-01 06:24 | 2007-08-01 06:24 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94321 | 11328 | 6951 |  |  | 2007-08-02 00:28 | 2007-08-02 00:48 | 20 | E0492 | GT 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94322 | 11329 | 6952 |  |  | 2007-08-02 00:28 | 2007-08-02 00:49 | 21 | E0493 | GT 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94323 | 11330 | 6953 |  |  | 2007-08-02 11:16 | 2007-08-02 11:16 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195547 | 11331 | 1268 |  |  | 2007-08-06 07:05 | 2007-08-06 07:05 | 0 | E0972 | CS-KI-EL 110 kV Transmission Circuit (Changed to E1956) | Transmission | Fault | Unknown | Transend | Completed | TRUE | 1 | TRUE |  | IR439 - Chapel Street-Kingston-Electrona 110 kV transmission circuit momentarily interrupted during strong winds. | FALSE | Non-Critical
94325 | 11332 | 1269 |  |  | 2007-08-09 21:51 | 2007-08-09 22:00 | 9 | E1635 | NW-SD-DE 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 39 | TRUE |  | IR453 - Norwood-Scottsdale-Derby 110 kV transmission circuit interrupted during severe weather. Total outage duration 17 minutes. | FALSE | Non-Critical
94326 | 11332 | 1269 |  |  | 2007-08-09 23:53 | 2007-08-09 23:57 | 4 | E1635 | NW-SD-DE 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR453 - Norwood-Scottsdale-Derby 110 kV transmission circuit interrupted during severe weather. Total outage duration 17 minutes. | FALSE | Non-Critical
94327 | 11332 | 1269 |  |  | 2007-08-10 08:57 | 2007-08-10 09:01 | 4 | E1635 | NW-SD-DE 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR453 - Norwood-Scottsdale-Derby 110 kV transmission circuit interrupted during severe weather. Total outage duration 17 minutes. | FALSE | Non-Critical
94328 | 11333 | 1273 |  |  | 2007-08-10 13:34 | 2007-08-11 08:57 | 1163 | E0282 | PM 220/110 kV T1 Transformer Circuit | Transformer | Fault | Fatigue | Transend | Completed | TRUE | 0 | TRUE |  | IR454 - Hadspen Substation transformer T1 interrupted due to dropper failure at surge diverter. At the same time PM-HA 4 110 kV transmission circuit also tripped open. | FALSE | Non-Critical
94329 | 11334 | 1274 |  |  | 2007-08-10 16:49 | 2007-08-11 12:17 | 1168 | E0028 | GO-CS 1 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR456 - Gordon-Chapel Street No 1 and 2 220 kV transmission circuits interrupted twice due to ice and snow loading. Total outage duration 20 hours 15 minutes. | FALSE | Critical
94330 | 11334 | 1274 |  |  | 2007-08-10 15:26 | 2007-08-10 16:13 | 47 | E0243 | GO-CS 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR456 - Gordon-Chapel Street No 1 and 2 220 kV transmission circuits interrupted twice due to ice and snow loading. Total outage duration 20 hours 15 minutes. | FALSE | Critical
94331 | 11335 | 1276 |  |  | 2007-08-15 08:50 | 2007-08-15 08:59 | 9 | E0027 | LI-CL-RE-CS 1 220 kV Transmission Circuit (Changed to E1958) | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR457 - LI-CL-RE-CS 220 kV transmission circuit interrupted due to error during planned work. | FALSE | Critical
94332 | 11336 | 1278 |  |  | 2007-08-18 10:13 | 2007-08-18 10:30 | 17 | E1497 | NW-SD 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR458 - Scottsdale Substation transformer T2 interrupted twice due to inadvertent circuit breaker trip during planned maintenance. Total outage duration 24 minutes. | FALSE | Non-Critical
94333 | 11336 | 1278 |  |  | 2007-08-18 12:32 | 2007-08-18 12:39 | 7 | E1497 | NW-SD 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR458 - Scottsdale Substation transformer T2 interrupted twice due to inadvertent circuit breaker trip during planned maintenance. Total outage duration 24 minutes. | FALSE | Non-Critical
94334 | 11336 | 1278 |  |  | 2007-08-18 10:13 | 2007-08-18 10:30 | 17 | E1626 | SD 110 kV B Bus Circuit | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR458 - Scottsdale Substation transformer T2 interrupted twice due to inadvertent circuit breaker trip during planned maintenance. Total outage duration 24 minutes. | FALSE | Undefined
94335 | 11336 | 1278 |  |  | 2007-08-18 12:32 | 2007-08-18 12:39 | 7 | E1626 | SD 110 kV B Bus Circuit | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR458 - Scottsdale Substation transformer T2 interrupted twice due to inadvertent circuit breaker trip during planned maintenance. Total outage duration 24 minutes. | FALSE | Undefined
94336 | 11337 | 1280 |  |  | 2007-08-21 09:01 | 2007-08-21 10:42 | 101 | E0435 | HA 220/110 kV T1 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR459 - Hadspen Substation transformer T1 interrupted due to slow blocking of protection during VT changeover. | FALSE | Non-Critical
94337 | 11338 | 6954 |  |  | 2007-08-06 05:41 | 2007-08-06 06:50 | 69 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94338 | 11341 | 6996 |  |  | 2007-08-29 22:32 | 2007-08-29 22:35 | 3 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94339 | 11342 | 6995 |  |  | 2007-08-29 19:24 | 2007-08-29 19:24 | 0 | E0760 | NW 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94340 | 11343 | 6956 |  |  | 2007-08-07 07:26 | 2007-08-07 07:27 | 1 | E1533 | MY 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94341 | 11344 | 6957 |  |  | 2007-08-08 11:32 | 2007-08-08 11:32 | 0 | E0727 | QT 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94342 | 11345 | 6958 |  |  | 2007-08-08 21:55 | 2007-08-09 01:56 | 241 | E0655 | SM 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94343 | 11346 | 6959 |  |  | 2007-08-09 04:03 | 2007-08-09 04:22 | 19 | E0492 | GT 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94344 | 11347 | 6960 |  |  | 2007-08-09 04:03 | 2007-08-09 04:22 | 19 | E0493 | GT 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94345 | 11348 | 6961 |  |  | 2007-08-09 09:23 | 2007-08-09 10:23 | 60 | E0766 | NW 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
105528 | 11349 | 6962 |  |  | 2007-08-09 11:04 | 2007-08-09 13:21 | 137 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94346 | 11350 | 6963 |  |  | 2007-08-09 12:36 | 2007-08-09 12:37 | 1 | E0639 | ST 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94347 | 11351 | 6964 |  |  | 2007-08-09 13:57 | 2007-08-09 13:57 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94348 | 11352 | 6965 |  |  | 2007-08-09 13:55 | 2007-08-09 13:56 | 1 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94350 | 11354 | 6967 |  |  | 2007-08-09 18:58 | 2007-08-09 21:43 | 165 | E0300 | AV 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94351 | 11355 | 6968 |  |  | 2007-08-09 20:54 | 2007-08-09 20:54 | 0 | E1454 | HA 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94352 | 11356 | 6969 |  |  | 2007-08-10 00:33 | 2007-08-10 03:03 | 150 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94353 | 11357 | 6970 |  |  | 2007-08-10 01:59 | 2007-08-10 01:59 | 0 | E0944 | UL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94354 | 11358 | 6971 |  |  | 2007-08-10 00:19 | 2007-08-10 12:35 | 736 | E1065 | QU 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94355 | 11359 | 6972 |  |  | 2007-08-10 07:29 | 2007-08-10 10:42 | 193 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94356 | 11360 | 6973 |  |  | 2007-08-10 08:59 | 2007-08-10 08:59 | 0 | E0495 | GT 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94357 | 11361 | 6974 |  |  | 2007-08-10 10:13 | 2007-08-10 14:17 | 244 | E1051 | SR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94358 | 11362 | 6975 |  |  | 2007-08-10 11:31 | 2007-08-10 18:01 | 390 | E1393 | SD 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94359 | 11363 | 6976 |  |  | 2007-08-10 11:44 | 2007-08-10 12:05 | 21 | E0888 | DE 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94360 | 11364 | 6977 |  |  | 2007-08-10 13:40 | 2007-08-10 13:40 | 0 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94361 | 11366 | 6978 |  |  | 2007-08-10 13:31 | 2007-08-10 13:31 | 0 | E1041 | SD 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94362 | 11367 | 6979 |  |  | 2007-08-10 14:23 | 2007-08-10 14:23 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94363 | 11369 | 6980 |  |  | 2007-08-10 17:06 | 2007-08-10 19:12 | 126 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94364 | 11370 | 6981 |  |  | 2007-08-10 18:58 | 2007-08-10 19:02 | 4 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94365 | 11371 | 6982 |  |  | 2007-08-10 20:21 | 2007-08-10 20:44 | 23 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94366 | 11373 | 6984 |  |  | 2007-08-11 11:38 | 2007-08-11 11:39 | 1 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94367 | 11374 | 6985 |  |  | 2007-08-11 15:18 | 2007-08-11 15:18 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94368 | 11375 | 6986 |  |  | 2007-08-11 16:07 | 2007-08-11 16:07 | 0 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94369 | 11376 | 6987 |  |  | 2007-08-14 07:02 | 2007-08-14 07:21 | 19 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94370 | 11377 | 6989 |  |  | 2007-08-21 10:06 | 2007-08-21 10:39 | 33 | E0081 | CR 33 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94371 | 11378 | 6990 |  |  | 2007-08-23 19:49 | 2007-08-23 20:36 | 47 | E0898 | SD 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94372 | 11379 | 6991 |  |  | 2007-08-24 14:01 | 2007-08-24 14:02 | 1 | E1573 | DP 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94373 | 11380 | 6992 |  |  | 2007-08-24 14:05 | 2007-08-24 15:07 | 62 | E0366 | KI 11 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94374 | 11381 | 6994 |  |  | 2007-08-25 09:14 | 2007-08-25 09:14 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94464 | 11524 | 6997 |  |  | 2007-08-31 15:32 | 2007-08-31 15:32 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94465 | 11525 | 7002 |  |  | 2007-09-03 01:28 | 2007-09-03 01:28 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94466 | 11526 | 7003 |  |  | 2007-09-03 01:28 | 2007-09-03 01:28 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94467 | 11529 | 7006 |  |  | 2007-09-03 22:14 | 2007-09-03 22:17 | 3 | E1592 | CS 11 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94468 | 11530 | 7005 |  |  | 2007-09-03 20:25 | 2007-09-03 21:06 | 41 | E0744 | NH 11 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94469 | 11531 | 7004 |  |  | 2007-09-03 04:45 | 2007-09-03 04:45 | 0 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139296 | 11532 | 6999 |  |  | 2007-09-02 17:02 | 2007-09-02 17:02 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94488 | 11565 | 7011 |  |  | 2007-09-06 13:54 | 2007-09-06 13:54 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94489 | 11566 | 7010 |  |  | 2007-09-05 08:39 | 2007-09-05 08:57 | 18 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94490 | 11567 | 7009 |  |  | 2007-09-05 06:43 | 2007-09-05 06:43 | 0 | E1531 | MY 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94491 | 11568 | 6998 |  |  | 2007-08-31 20:33 | 2007-08-31 23:06 | 153 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94492 | 11569 | 7001 |  |  | 2007-09-02 21:08 | 2007-09-02 21:27 | 19 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94493 | 11570 | 7000 |  |  | 2007-09-02 21:07 | 2007-09-02 21:07 | 0 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94494 | 11572 | 6557 |  |  | 2007-09-16 23:41 | 2007-09-16 23:41 | 0 | E1538 | MY 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94495 | 11573 | 6556 |  |  | 2007-09-16 20:53 | 2007-09-16 21:41 | 48 | E1538 | MY 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94496 | 11574 | 6555 |  |  | 2007-09-15 15:28 | 2007-09-15 15:54 | 26 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94497 | 11575 | 6554 |  |  | 2007-09-15 15:25 | 2007-09-15 15:25 | 0 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94498 | 11576 | 6553 |  |  | 2007-09-15 08:08 | 2007-09-15 08:18 | 10 | E1052 | SR 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94499 | 11577 | 6552 |  |  | 2007-09-15 08:08 | 2007-09-15 08:18 | 10 | E1029 | SR 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94500 | 11578 | 6551 |  |  | 2007-09-15 00:49 | 2007-09-15 01:56 | 67 | E0863 | RB 44 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94501 | 11579 | 6541 |  |  | 2007-09-07 11:44 | 2007-09-07 11:44 | 0 | E1555 | DP 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94502 | 11580 | 6542 |  |  | 2007-09-09 11:52 | 2007-09-09 12:07 | 15 | E0843 | RK 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94503 | 11581 | 6543 |  |  | 2007-09-09 13:38 | 2007-09-09 14:08 | 30 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94504 | 11585 | 6545 |  |  | 2007-09-11 09:06 | 2007-09-11 14:55 | 349 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94505 | 11586 | 6546 |  |  | 2007-09-11 11:14 | 2007-09-11 12:49 | 95 | E1518 | PL 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94506 | 11587 | 6547 |  |  | 2007-09-13 02:33 | 2007-09-13 05:42 | 189 | E0863 | RB 44 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94507 | 11588 | 6548 |  |  | 2007-09-13 11:15 | 2007-09-13 11:15 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94508 | 11589 | 6549 |  |  | 2007-09-14 06:16 | 2007-09-14 06:16 | 0 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94509 | 11590 | 6550 |  |  | 2007-09-14 06:18 | 2007-09-14 06:18 | 0 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94510 | 11591 | 6559 |  |  | 2007-09-19 13:07 | 2007-09-19 15:11 | 124 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94511 | 11592 | 6558 |  |  | 2007-09-19 13:25 | 2007-09-19 14:56 | 91 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94512 | 11593 | 1281 |  |  | 2007-09-23 22:24 | 2007-09-23 23:39 | 75 | E0813 | RA 110/22 kV T1 Transformer Circuit | Transformer | Fault | Wildlife | Transend | Completed | TRUE | 0 | TRUE |  | IR460 - Railton Substation transformer T1 interrupted due to flashover caused by possum in switchyard. | FALSE | Non-Critical
94513 | 11594 | 6567 |  |  | 2007-09-24 11:01 | 2007-09-24 11:01 | 0 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94514 | 11595 | 6566 |  |  | 2007-09-24 06:34 | 2007-09-24 06:34 | 0 | E0197 | SO 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94515 | 11596 | 6565 |  |  | 2007-09-24 02:17 | 2007-09-24 05:13 | 176 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94516 | 11598 | 6563 |  |  | 2007-09-22 21:20 | 2007-09-22 22:48 | 88 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94517 | 11599 | 6562 |  |  | 2007-09-20 21:27 | 2007-09-20 21:27 | 0 | E1552 | DP 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94518 | 11600 | 6561 |  |  | 2007-09-20 14:49 | 2007-09-20 15:09 | 20 | E0156 | MB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94519 | 11601 | 6560 |  |  | 2007-09-20 07:14 | 2007-09-20 07:14 | 0 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94520 | 11602 | 1282 |  |  | 2007-09-24 15:40 | 2007-09-24 17:52 | 132 | E0267 | PO-PM 5 220 kV Transmission Circuit | Transmission | Fault | Generator | Transend | Completed | TRUE | 0 | TRUE |  | IR463 - Poatina-Palmserton No. 5 220 kV transmission circuit interrupted. Cause unknown. | FALSE | Non-Critical
94521 | 11603 | 1283 |  |  | 2007-09-26 08:09 | 2007-09-26 08:45 | 36 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Basslink | Basslink | Completed | TRUE | 7204 | TRUE |  | IR464 - George Town-George Town Converter Station 220 kV transmission circuit interrupted due to sensor failure at George Town Converter Station. | FALSE | Undefined
94522 | 11604 | 1284 |  |  | 2007-09-30 13:52 | 2007-09-30 13:55 | 3 | E0026 | LI-CS 2 220 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR465 - Liapootah-Chapel St No. 2 220 kV transmission circuit interrupted three times due to a combination of poor isolations and incorrect protection settings. Total outage duration 18 minutes. | FALSE | Critical
94523 | 11604 | 1284 |  |  | 2007-09-30 18:03 | 2007-09-30 18:16 | 13 | E0026 | LI-CS 2 220 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR465 - Liapootah-Chapel St No. 2 220 kV transmission circuit interrupted three times due to a combination of poor isolations and incorrect protection settings. Total outage duration 18 minutes. | FALSE | Critical
94524 | 11604 | 1284 |  |  | 2007-09-30 20:57 | 2007-09-30 20:59 | 2 | E0026 | LI-CS 2 220 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR465 - Liapootah-Chapel St No. 2 220 kV transmission circuit interrupted three times due to a combination of poor isolations and incorrect protection settings. Total outage duration 18 minutes. | FALSE | Critical
94559 | 11653 | 6580 |  |  | 2007-10-01 17:54 | 2007-10-01 18:57 | 63 | E0844 | RK 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94560 | 11654 | 6579 |  |  | 2007-10-01 14:52 | 2007-10-01 15:08 | 16 | E0496 | GT 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94561 | 11655 | 6578 |  |  | 2007-09-30 19:30 | 2007-09-30 19:30 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94562 | 11657 | 6575 |  |  | 2007-09-29 22:44 | 2007-09-29 22:44 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94563 | 11658 | 6574 |  |  | 2007-09-24 05:14 | 2007-09-24 05:27 | 13 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94564 | 11660 | 6573 |  |  | 2007-09-28 09:05 | 2007-09-28 09:25 | 20 | E0860 | RB 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94565 | 11661 | 6572 |  |  | 2007-09-27 22:02 | 2007-09-27 22:24 | 22 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94566 | 11662 | 6571 |  |  | 2007-09-27 21:25 | 2007-09-27 22:13 | 48 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94567 | 11663 | 6570 |  |  | 2007-09-27 20:27 | 2007-09-27 22:08 | 101 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94568 | 11664 | 6569 |  |  | 2007-09-27 21:26 | 2007-09-27 21:26 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94569 | 11665 | 6568 |  |  | 2007-09-27 20:26 | 2007-09-27 20:26 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94570 | 11666 | 6581 |  |  | 2007-10-02 13:01 | 2007-10-02 13:20 | 19 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139299 | 11689 | 6582 |  |  | 2007-10-02 18:46 | 2007-10-02 18:46 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94592 | 11690 | 6583 |  |  | 2007-10-03 13:56 | 2007-10-03 14:33 | 37 | E1612 | UL 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94593 | 11691 | 6584 |  |  | 2007-10-03 17:35 | 2007-10-03 17:49 | 14 | E1612 | UL 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94594 | 11692 | 6585 |  |  | 2007-10-04 06:06 | 2007-10-04 06:06 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94595 | 11693 | 6586 |  |  | 2007-10-04 15:32 | 2007-10-04 15:33 | 1 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94596 | 11694 | 6587 |  |  | 2007-10-04 15:55 | 2007-10-04 16:52 | 57 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94597 | 11695 | 6588 |  |  | 2007-10-04 16:40 | 2007-10-04 17:28 | 48 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94598 | 11696 | 6589 |  |  | 2007-10-04 17:36 | 2007-10-04 17:36 | 0 | E0495 | GT 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94599 | 11697 | 6590 |  |  | 2007-10-04 17:05 | 2007-10-04 18:02 | 57 | E0835 | RK 11 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94600 | 11698 | 6591 |  |  | 2007-10-06 00:45 | 2007-10-06 01:44 | 59 | E1530 | MY 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94601 | 11699 | 6592 |  |  | 2007-10-08 06:18 | 2007-10-08 06:18 | 0 | E0643 | ST 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94602 | 11700 | 6596 |  |  | 2007-10-14 10:16 | 2007-10-14 11:37 | 81 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94603 | 11701 | 6595 |  |  | 2007-10-14 10:02 | 2007-10-14 10:02 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94604 | 11702 | 6594 |  |  | 2007-10-11 14:30 | 2007-10-11 14:57 | 27 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94605 | 11703 | 6602 |  |  | 2007-10-19 23:21 | 2007-10-19 23:21 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94606 | 11704 | 6601 |  |  | 2007-10-19 18:57 | 2007-10-19 19:23 | 26 | E0413 | EL 11 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94607 | 11705 | 6600 |  |  | 2007-10-19 17:29 | 2007-10-19 17:29 | 0 | E0413 | EL 11 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94608 | 11706 | 6599 |  |  | 2007-10-19 08:40 | 2007-10-19 08:40 | 0 | E0766 | NW 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94609 | 11707 | 6598 |  |  | 2007-10-19 07:54 | 2007-10-19 07:54 | 0 | E1507 | SD 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94610 | 11708 | 6597 |  |  | 2007-10-18 07:50 | 2007-10-18 08:08 | 18 | E0495 | GT 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94611 | 11709 | 6604 |  |  | 2007-10-22 17:24 | 2007-10-22 17:24 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94612 | 11710 | 6605 |  |  | 2007-10-22 20:45 | 2007-10-22 20:45 | 0 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94613 | 11711 | 6606 |  |  | 2007-10-23 01:46 | 2007-10-23 02:49 | 63 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94614 | 11712 | 6607 |  |  | 2007-10-24 03:42 | 2007-10-24 04:00 | 18 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94615 | 11713 | 6608 |  |  | 2007-10-24 15:53 | 2007-10-24 15:53 | 0 | E0197 | SO 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94616 | 11714 | 6615 |  |  | 2007-10-27 09:28 | 2007-10-27 10:32 | 64 | E0906 | TR 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94617 | 11715 | 6613 |  |  | 2007-10-27 02:19 | 2007-10-27 05:10 | 171 | E1557 | CR 33 kV Z2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94618 | 11716 | 6614 |  |  | 2007-10-27 06:09 | 2007-10-27 06:09 | 0 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94619 | 11717 | 6603 |  |  | 2007-10-22 17:23 | 2007-10-22 17:24 | 1 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94620 | 11718 | 1287 |  |  | 2007-10-28 02:47 | 2007-10-28 03:59 | 72 | E0286 | PO-PM 1 110 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR469 - Poatina-Palmerston No 1 110 kV transmission circuit interrupted due to intertrip from Poatina Station. | FALSE | Non-Critical
94621 | 11719 | 6619 |  |  | 2007-10-29 15:05 | 2007-10-29 15:45 | 40 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94622 | 11720 | 6618 |  |  | 2007-10-29 12:03 | 2007-10-29 12:03 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139300 | 11721 | 6617 |  |  | 2007-10-28 18:03 | 2007-10-28 18:03 | 0 | E1566 | DP 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94624 | 11722 | 6616 |  |  | 2007-10-28 09:22 | 2007-10-28 09:51 | 29 | E0906 | TR 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
158027 | 11801 | 6623 |  |  | 2007-11-04 03:09 | 2007-11-04 03:58 | 49 | E0118 | CS 11 kV T2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94688 | 11803 | 6624 |  |  | 2007-11-06 06:37 | 2007-11-06 06:37 | 0 | E0156 | MB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94689 | 11804 | 6622 |  |  | 2007-11-02 00:48 | 2007-11-02 01:09 | 21 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94690 | 11805 | 6621 |  |  | 2007-11-01 13:13 | 2007-11-01 15:20 | 127 | E0496 | GT 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94705 | 11816 | 1288 |  |  | 2007-11-14 13:36 | 2007-11-14 13:57 | 21 | E0404 | SH-BU 2 110 kV Transmission Circuit | Transmission | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR472 - Sheffield Substation 110 kV 'A' Bus interrupted due to inappropriate temporary protection settings applied during planned work. | FALSE | Non-Critical
94708 | 11816 | 1288 |  |  | 2007-11-14 13:36 | 2007-11-14 13:53 | 17 | E0536 | SH-DG 110 kV Transmission Circuit | Transmission | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 2483 | TRUE |  | IR472 - Sheffield Substation 110 kV 'A' Bus interrupted due to inappropriate temporary protection settings applied during planned work. | FALSE | Non-Critical
94709 | 11816 | 1288 |  |  | 2007-11-14 13:36 | 2007-11-14 14:03 | 27 | E0537 | SH-DP 110 kV Transmission Circuit | Transmission | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR472 - Sheffield Substation 110 kV 'A' Bus interrupted due to inappropriate temporary protection settings applied during planned work. | FALSE | Non-Critical
94710 | 11816 | 1288 |  |  | 2007-11-14 13:36 | 2007-11-14 14:37 | 61 | E0550 | SH-PA Tee 110 kV Transmission Circuit Section | Transmission | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR472 - Sheffield Substation 110 kV 'A' Bus interrupted due to inappropriate temporary protection settings applied during planned work. | FALSE | Non-Critical
94711 | 11816 | 1288 |  |  | 2007-11-14 13:36 | 2007-11-14 13:57 | 21 | E0552 | SH-RA 2 110 kV Transmission Circuit | Transmission | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR472 - Sheffield Substation 110 kV 'A' Bus interrupted due to inappropriate temporary protection settings applied during planned work. | FALSE | Non-Critical
94712 | 11816 | 1288 |  |  | 2007-11-14 13:36 | 2007-11-14 14:10 | 34 | E0554 | SH-WV 110 kV Transmission Circuit | Transmission | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR472 - Sheffield Substation 110 kV 'A' Bus interrupted due to inappropriate temporary protection settings applied during planned work. | FALSE | Non-Critical
94706 | 11816 | 1288 |  |  | 2007-11-14 13:36 | 2007-11-14 13:51 | 15 | E0534 | SH 220/110 kV T1 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR472 - Sheffield Substation 110 kV 'A' Bus interrupted due to inappropriate temporary protection settings applied during planned work. | FALSE | Non-Critical
94707 | 11816 | 1288 |  |  | 2007-11-14 13:36 | 2007-11-14 13:54 | 18 | E0535 | SH 220/110 kV T2 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR472 - Sheffield Substation 110 kV 'A' Bus interrupted due to inappropriate temporary protection settings applied during planned work. | FALSE | Non-Critical
94713 | 11816 | 1288 |  |  | 2007-11-14 13:36 | 2007-11-14 14:06 | 30 | E0815 | RA 22 kV A Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR472 - Sheffield Substation 110 kV 'A' Bus interrupted due to inappropriate temporary protection settings applied during planned work. | FALSE | Undefined
94714 | 11816 | 1288 |  |  | 2007-11-14 13:36 | 2007-11-14 14:06 | 30 | E0816 | RA 22 kV B Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR472 - Sheffield Substation 110 kV 'A' Bus interrupted due to inappropriate temporary protection settings applied during planned work. | FALSE | Undefined
94715 | 11816 | 1288 |  |  | 2007-11-14 13:36 | 2007-11-14 14:06 | 30 | E1546 | DP 22 kV C Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR472 - Sheffield Substation 110 kV 'A' Bus interrupted due to inappropriate temporary protection settings applied during planned work. | FALSE | Undefined
94716 | 11816 | 1288 |  |  | 2007-11-14 13:36 | 2007-11-14 14:15 | 39 | E1553 | WV 11 kV C Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR472 - Sheffield Substation 110 kV 'A' Bus interrupted due to inappropriate temporary protection settings applied during planned work. | FALSE | Undefined
94717 | 11816 | 1288 |  |  | 2007-11-14 13:36 | 2007-11-14 14:06 | 30 | E1571 | DP 22 kV B Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR472 - Sheffield Substation 110 kV 'A' Bus interrupted due to inappropriate temporary protection settings applied during planned work. | FALSE | Undefined
94718 | 11816 | 1288 |  |  | 2007-11-14 13:36 | 2007-11-14 14:15 | 39 | E1572 | WV 11 kV D Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR472 - Sheffield Substation 110 kV 'A' Bus interrupted due to inappropriate temporary protection settings applied during planned work. | FALSE | Undefined
94719 | 11816 | 1288 |  |  | 2007-11-14 13:36 | 2007-11-14 14:06 | 30 | E1581 | DP 22 kV A Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR472 - Sheffield Substation 110 kV 'A' Bus interrupted due to inappropriate temporary protection settings applied during planned work. | FALSE | Undefined
94720 | 11817 | 1289 |  |  | 2007-11-14 22:23 | 2007-11-14 22:43 | 20 | E0286 | PO-PM 1 110 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR473 - Poatina-Palmerston No 1 110 kV transmission circuit interrupted due to intertrip from generator. | FALSE | Non-Critical
94721 | 11818 | 6634 |  |  | 2007-11-18 17:32 | 2007-11-18 17:32 | 0 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94722 | 11819 | 6633 |  |  | 2007-11-15 15:49 | 2007-11-15 17:04 | 75 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94723 | 11820 | 6632 |  |  | 2007-11-15 13:37 | 2007-11-15 13:37 | 0 | E0022 | BW 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94724 | 11821 | 6631 |  |  | 2007-11-14 15:25 | 2007-11-14 16:14 | 49 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94725 | 11822 | 6630 |  |  | 2007-11-14 00:44 | 2007-11-14 00:44 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94726 | 11823 | 6629 |  |  | 2007-11-13 07:46 | 2007-11-13 08:48 | 62 | E0845 | RK 11 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94727 | 11824 | 6628 |  |  | 2007-11-10 16:25 | 2007-11-10 17:41 | 76 | E0760 | NW 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94728 | 11825 | 6627 |  |  | 2007-11-10 16:25 | 2007-11-10 17:41 | 76 | E1531 | MY 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94729 | 11826 | 6626 |  |  | 2007-11-08 23:15 | 2007-11-08 23:15 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94730 | 11827 | 6642 |  |  | 2007-11-21 10:27 | 2007-11-21 10:27 | 0 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94731 | 11828 | 6641 |  |  | 2007-11-21 10:18 | 2007-11-21 10:18 | 0 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94732 | 11829 | 6640 |  |  | 2007-11-21 10:16 | 2007-11-21 10:16 | 0 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94733 | 11830 | 6639 |  |  | 2007-11-21 10:09 | 2007-11-21 10:09 | 0 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94734 | 11831 | 6638 |  |  | 2007-11-21 09:55 | 2007-11-21 09:55 | 0 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94736 | 11833 | 6636 |  |  | 2007-11-20 21:53 | 2007-11-21 00:46 | 173 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94737 | 11834 | 6635 |  |  | 2007-11-20 16:11 | 2007-11-20 16:11 | 0 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94738 | 11835 | 1290 |  |  | 2007-11-16 08:24 | 2007-11-16 13:18 | 294 | E0587 | UL-EB 110 kV Transmission Circuit | Transmission | Fault | Inside Approach Limits | Transend | Completed | TRUE | 0 | TRUE |  | IR474 - Ulverstone-Emu Bay 110 kV transmission circuit interrupted due to irrigator draw wire contact with conductor. | FALSE | Non-Critical
104403 | 11836 | 1291 |  |  | 2007-11-23 10:01 | 2007-11-23 10:54 | 53 | E0587 | UL-EB 110 kV Transmission Circuit | Transmission | Fault | Inside Approach Limits | Transend | Completed | TRUE | 0 | TRUE |  | IR475 - Ulverstone-Emu Bay 110 kV transmission circuit interrupted due to irrigator draw wire contacting conductor. | FALSE | Non-Critical
94817 | 11991 | 6666 |  |  | 2007-12-08 10:46 | 2007-12-08 11:09 | 23 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94819 | 11993 | 6664 |  |  | 2007-12-07 08:05 | 2007-12-07 08:05 | 0 | E1042 | SD 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94820 | 11995 | 6662 |  |  | 2007-12-07 02:13 | 2007-12-07 02:13 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94821 | 11996 | 6661 |  |  | 2007-12-06 19:52 | 2007-12-06 19:52 | 0 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94822 | 11997 | 6660 |  |  | 2007-12-05 16:15 | 2007-12-05 16:15 | 0 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94823 | 11999 | 6658 |  |  | 2007-12-03 16:59 | 2007-12-03 18:46 | 107 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94824 | 12000 | 6657 |  |  | 2007-12-03 17:31 | 2007-12-03 18:25 | 54 | E0819 | RA 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94825 | 12001 | 6656 |  |  | 2007-12-11 | 2007-12-11 01:04 | 64 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94826 | 12002 | 6655 |  |  | 2007-12-02 23:05 | 2007-12-02 23:05 | 0 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94827 | 12003 | 6653 |  |  | 2007-12-02 21:38 | 2007-12-02 22:58 | 80 | E0779 | PL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94828 | 12004 | 6652 |  |  | 2007-12-02 20:03 | 2007-12-02 21:21 | 78 | E0779 | PL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94829 | 12005 | 6651 |  |  | 2007-12-02 20:33 | 2007-12-02 20:40 | 7 | E1518 | PL 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94830 | 12006 | 6650 |  |  | 2007-12-02 06:46 | 2007-12-02 06:46 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185907 | 12007 | 6649 |  |  | 2007-12-01 11:31 | 2007-12-01 11:31 | 0 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94832 | 12008 | 6643 |  |  | 2007-11-22 11:30 | 2007-11-22 12:09 | 39 | E0158 | MB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94833 | 12010 | 6645 |  |  | 2007-11-25 01:08 | 2007-11-25 17:10 | 962 | E0863 | RB 44 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94834 | 12011 | 6646 |  |  | 2007-11-26 03:27 | 2007-11-26 03:27 | 0 | E1535 | MY 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185908 | 12012 | 6648 |  |  | 2007-11-26 22:03 | 2007-11-26 22:03 | 0 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94836 | 12013 | 1292 |  |  | 2007-12-02 21:38 | 2007-12-02 21:38 | 0 | E0772 | PL-ST 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR476 - Port Latta-Smithton 110 kV transmission circuit momentarily interrupted during lightning storms. | FALSE | Non-Critical
94837 | 12014 | 1293 |  |  | 2007-12-06 05:03 | 2007-12-06 06:34 | 91 | E0192 | SO 110/22 kV T1 Transformer Circuit | Transformer | Fault | Unknown | Transend | Completed | TRUE | 472 | TRUE |  | IR477 - Sorell Substation transformer T1 interrupted due to 22 kV CT flashover. Root cause of flashover unknown. | FALSE | Non-Critical
94838 | 12015 | 1294 |  |  | 2007-12-06 08:21 | 2007-12-06 09:34 | 73 | E0586 | EB 110/11 kV T3 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR478 - Emu Bay transformer T3 interrupted due to error during planned work. | FALSE | Non-Critical
146169 | 12017 | 1295 |  |  | 2007-12-06 21:02 | 2007-12-07 17:20 | 1218 | E0169 | TU-BG-DB 110 kV Transmission Circuit | Transmission | Fault | Internal Fault | Transend | Completed | TRUE | 176 | TRUE |  | IR479 - Tungatinah-Butlers Gorge-Derwent Bridge 110 kV transmission circuit interrupted due to current transformer failure. | FALSE | Non-Critical
94840 | 12018 | 6668 |  |  | 2007-12-16 07:41 | 2007-12-16 08:33 | 52 | E0768 | NW 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94841 | 12019 | 6669 |  |  | 2007-12-18 19:32 | 2007-12-18 19:32 | 0 | E0366 | KI 11 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94842 | 12020 | 6670 |  |  | 2007-12-19 19:25 | 2007-12-19 19:25 | 0 | E1535 | MY 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94843 | 12021 | 6671 |  |  | 2007-12-19 22:28 | 2007-12-19 22:28 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94844 | 12022 | 6672 |  |  | 2007-12-20 02:39 | 2007-12-20 02:39 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94845 | 12023 | 6673 |  |  | 2007-12-20 02:43 | 2007-12-20 02:43 | 0 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94846 | 12024 | 6674 |  |  | 2007-12-20 13:49 | 2007-12-20 13:49 | 0 | E1437 | HA 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94847 | 12025 | 6675 |  |  | 2007-12-20 14:37 | 2007-12-20 14:37 | 0 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94848 | 12026 | 6676 |  |  | 2007-12-21 05:36 | 2007-12-21 05:58 | 22 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94849 | 12027 | 6677 |  |  | 2007-12-22 00:50 | 2007-12-22 01:14 | 24 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94850 | 12028 | 6678 |  |  | 2007-12-22 14:28 | 2007-12-22 14:28 | 0 | E1393 | SD 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94851 | 12029 | 6679 |  |  | 2007-12-22 15:12 | 2007-12-22 15:25 | 13 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94852 | 12030 | 6680 |  |  | 2007-12-22 15:10 | 2007-12-22 15:10 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94853 | 12031 | 6681 |  |  | 2007-12-22 15:19 | 2007-12-22 15:19 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94854 | 12032 | 6682 |  |  | 2007-12-23 12:13 | 2007-12-23 12:13 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
89926 | 12116 | 6700 |  |  | 2008-01-07 10:44 | 2008-01-07 10:44 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
89927 | 12117 | 6698 |  |  | 2008-01-04 16:00 | 2008-01-04 16:00 | 0 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
89928 | 12118 | 6697 |  |  | 2008-01-03 09:42 | 2008-01-03 09:42 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
89929 | 12119 | 6696 |  |  | 2008-01-03 05:10 | 2008-01-03 05:10 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
89930 | 12120 | 6695 |  |  | 2008-01-01 21:26 | 2008-01-02 10:27 | 781 | E0186 | TU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139312 | 12121 | 6694 |  |  | 2008-01-01 21:26 | 2008-01-01 22:48 | 82 | E0185 | TU 22 kV X D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
89932 | 12122 | 6693 |  |  | 2008-01-01 05:50 | 2008-01-01 05:50 | 0 | E1531 | MY 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94871 | 12123 | 6692 |  |  | 2007-12-31 11:27 | 2007-12-31 13:25 | 118 | E0779 | PL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94872 | 12123 | 6692 |  |  | 2007-12-31 11:27 | 2007-12-31 13:25 | 118 | E1518 | PL 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94873 | 12124 | 6691 |  |  | 2007-12-31 13:18 | 2007-12-31 14:49 | 91 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94874 | 12125 | 6689 |  |  | 2007-12-31 07:46 | 2007-12-31 09:35 | 109 | E0084 | CR 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94875 | 12126 | 6688 |  |  | 2007-12-30 19:21 | 2007-12-30 20:14 | 53 | E0078 | CR 33 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94876 | 12127 | 6687 |  |  | 2007-12-29 09:44 | 2007-12-29 09:44 | 0 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94877 | 12128 | 6686 |  |  | 2007-12-29 04:30 | 2007-12-29 04:30 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94878 | 12129 | 6685 |  |  | 2007-12-28 00:01 | 2007-12-28 12:01 | 720 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94879 | 12130 | 6684 |  |  | 2007-12-25 21:29 | 2007-12-25 23:18 | 109 | E1533 | MY 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94880 | 12131 | 6683 |  |  | 2007-12-25 12:47 | 2007-12-25 12:47 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94881 | 12145 | 1296 |  |  | 2007-12-13 06:56 | 2007-12-13 07:25 | 29 | E0587 | UL-EB 110 kV Transmission Circuit | Transmission | Fault | Mechanical Failure | Transend | Completed | TRUE | 0 | TRUE |  | IR481 - Ulverstone-Emu Bay 110 kV transmission circuit interrupted due to broken circuit breaker operating arm at Emu Bay Substation. | FALSE | Non-Critical
94882 | 12146 | 1297 |  |  | 2007-12-20 00:55 | 2007-12-20 00:56 | 1 | E0406 | FA-QU-SR-HM 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 25 | TRUE |  | IR482 - Farrell-Que-Savage River-Hampshire 110 kV transmission circuit interrupted during lightning storms. | FALSE | Non-Critical
94883 | 12148 | 1298 |  |  | 2007-12-20 04:13 | 2007-12-20 05:30 | 77 | E0403 | SH-BU 1 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR483 - Sheffield-Burnie No. 1 220 kV and Sheffield-Burnie No. 2 110 kV transmission circuits interrupted during lightning storms. SPS operation also occurred. | FALSE | Critical
94884 | 12148 | 1298 |  |  | 2007-12-20 04:13 | 2007-12-20 05:34 | 81 | E0404 | SH-BU 2 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR483 - Sheffield-Burnie No. 1 220 kV and Sheffield-Burnie No. 2 110 kV transmission circuits interrupted during lightning storms. SPS operation also occurred. | FALSE | Non-Critical
94886 | 12149 | 1301 |  |  | 2007-12-13 12:31 | 2007-12-13 14:45 | 134 | E0028 | GO-CS 1 220 kV Transmission Circuit | Transmission | Fault | Vegetation | Transend | Completed | TRUE | 0 | TRUE |  | IR484 - Gordon-Chapel Street No. 1 220 kV transmission circuit interrupted due to contact between conductors and vegetation. | FALSE | Critical
94885 | 12149 | 1301 |  |  | 2007-12-13 12:24 | 2007-12-13 12:24 | 0 | E0028 | GO-CS 1 220 kV Transmission Circuit | Transmission | Fault | Vegetation | Transend | Completed | TRUE | 0 | TRUE |  | IR484 - Gordon-Chapel Street No. 1 220 kV transmission circuit interrupted due to contact between conductors and vegetation. | FALSE | Critical
175149 | 12150 | 1302 |  |  | 2008-01-01 21:26 | 2008-01-01 23:02 | 96 | E0179 | TU 110/22 kV T9X Transformer Circuit | Transformer | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR485 - Tungatinah Substation transformer T9 and 22 kV 'A' Bus interrupted due to excessive dust on 22 kV feeder earth fault relay contacts causing feeder protection to operate slower than transformer protection. | FALSE | Undefined
89952 | 12151 | 1303 |  |  | 2008-01-07 12:10 | 2008-01-07 12:20 | 10 | E0717 | FA-RC 2 220 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR486 - Farrell-Reece No. 2 220 kV transmission circuit interrupted due to an inadvertent intertrip generated as a result of poor testing process by Hydro Tasmania. | FALSE | Non-Critical
89953 | 12152 | 1304 |  |  | 2008-01-07 15:03 | 2008-01-07 15:06 | 3 | E0772 | PL-ST 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR487 - Port Latta-Smithton 110 kV transmission circuit interrupted during planned work. | FALSE | Non-Critical
90006 | 12209 | 6715 |  |  | 2008-01-19 13:31 | 2008-01-19 13:31 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90007 | 12210 | 6716 |  |  | 2008-01-20 01:16 | 2008-01-20 01:16 | 0 | E1552 | DP 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90008 | 12211 | 6717 |  |  | 2008-01-20 16:57 | 2008-01-20 17:20 | 23 | E0363 | KI 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90009 | 12212 | 6718 |  |  | 2008-01-20 21:22 | 2008-01-20 21:22 | 0 | E0158 | MB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90010 | 12214 | 6721 |  |  | 2008-01-24 02:26 | 2008-01-24 02:26 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90011 | 12215 | 6722 |  |  | 2008-01-26 01:23 | 2008-01-26 01:23 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90012 | 12216 | 6723 |  |  | 2008-01-26 18:18 | 2008-01-26 18:18 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90013 | 12217 | 6714 |  |  | 2008-01-19 05:12 | 2008-01-19 12:10 | 418 | E0655 | SM 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90014 | 12218 | 1305 |  |  | 2008-01-11 08:31 | 2008-01-11 08:36 | 5 | E0770 | PA Tee - UL 110 kV Transmission Circuit Section | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR491 - Paloona-Ulverstone 110 kV transmission circuit interrupted during planned work. | FALSE | Non-Critical
90126 | 12311 | 6741 |  |  | 2008-02-12 00:52 | 2008-02-12 12:52 | 720 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90127 | 12312 | 6740 |  |  | 2008-02-10 22:44 | 2008-02-10 22:44 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90128 | 12313 | 6739 |  |  | 2008-02-09 17:54 | 2008-02-09 17:54 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90129 | 12314 | 6737 |  |  | 2008-02-08 09:16 | 2008-02-08 09:17 | 1 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90130 | 12316 | 6736 |  |  | 2008-02-05 14:21 | 2008-02-05 14:58 | 37 | E0819 | RA 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90131 | 12317 | 6735 |  |  | 2008-02-05 13:45 | 2008-02-05 13:45 | 0 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90132 | 12318 | 6734 |  |  | 2008-02-04 18:24 | 2008-02-04 18:24 | 0 | E1504 | TB 22 KV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90133 | 12319 | 6733 |  |  | 2008-02-04 12:33 | 2008-02-04 13:41 | 68 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90134 | 12320 | 6731 |  |  | 2008-02-04 09:03 | 2008-02-04 10:57 | 114 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90135 | 12321 | 6732 |  |  | 2008-02-04 08:24 | 2008-02-04 09:42 | 78 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90136 | 12322 | 6727 |  |  | 2008-02-02 00:36 | 2008-02-02 12:36 | 720 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90137 | 12323 | 6720 |  |  | 2008-01-23 04:40 | 2008-01-23 05:56 | 76 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90138 | 12324 | 6726 |  |  | 2008-02-01 03:09 | 2008-02-01 03:09 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90139 | 12325 | 6744 |  |  | 2008-02-15 15:48 | 2008-02-15 16:03 | 15 | E0767 | NW 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90140 | 12327 | 6725 |  |  | 2008-02-01 02:00 | 2008-02-01 03:09 | 69 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90141 | 12328 | 6724 |  |  | 2008-01-30 02:31 | 2008-01-30 02:31 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90142 | 12329 | 6742 |  |  | 2008-02-13 05:29 | 2008-02-13 05:29 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90143 | 12330 | 6743 |  |  | 2008-02-14 07:26 | 2008-02-14 09:06 | 100 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90144 | 12331 | 6765 |  |  | 2008-02-25 21:14 | 2008-02-25 21:14 | 0 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90145 | 12333 | 6762 |  |  | 2008-02-24 02:11 | 2008-02-24 02:59 | 48 | E0083 | CR 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90146 | 12334 | 6761 |  |  | 2008-02-23 14:36 | 2008-02-23 14:36 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90147 | 12335 | 6760 |  |  | 2008-02-23 14:26 | 2008-02-23 14:26 | 0 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90148 | 12336 | 6759 |  |  | 2008-02-23 13:27 | 2008-02-23 13:31 | 4 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90149 | 12337 | 6758 |  |  | 2008-02-23 06:05 | 2008-02-23 06:05 | 0 | E1530 | MY 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90150 | 12339 | 6755 |  |  | 2008-02-22 16:44 | 2008-02-22 18:02 | 78 | E0727 | QT 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90151 | 12340 | 6745 |  |  | 2008-02-22 17:24 | 2008-02-22 17:34 | 10 | E0779 | PL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90152 | 12341 | 6753 |  |  | 2008-02-22 17:24 | 2008-02-22 17:34 | 10 | E1518 | PL 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90153 | 12342 | 6752 |  |  | 2008-02-22 17:24 | 2008-02-22 17:24 | 0 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90154 | 12343 | 6751 |  |  | 2008-02-22 16:43 | 2008-02-22 16:43 | 0 | E0727 | QT 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90155 | 12344 | 6750 |  |  | 2008-02-20 21:24 | 2008-02-20 21:24 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90156 | 12345 | 6748 |  |  | 2008-02-20 | 2008-02-20 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90157 | 12346 | 6747 |  |  | 2008-02-18 14:41 | 2008-02-18 14:41 | 0 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90158 | 12347 | 1306 |  |  | 2008-02-18 07:17 | 2008-02-18 12:20 | 303 | E0785 | QU 110/22 kV T1 Transformer Circuit | Transformer | Fault | Unknown | Transend | Completed | TRUE | 1797 | TRUE |  | IR494 - Que Substation transformer T1 interrupted. Cause unknown. | FALSE | Non-Critical
175152 | 12348 | 1307 |  |  | 2008-02-23 16:31 | 2008-02-23 17:17 | 46 | E0179 | TU 110/22 kV T9X Transformer Circuit | Transformer | Fault | Internal Fault | Transend | Completed | TRUE | 21 | TRUE |  | IR495 - Tungatinah 22 kV 'A' Bus and transformer T9 interrupted due to excessive dust on 22 kV feeder earth fault relay contacts causing feeder protection to operate slower than transformer protection. | FALSE | Undefined
139316 | 12348 | 1307 |  |  | 2008-02-23 16:31 | 2008-02-23 17:17 | 46 | E0180 | TU 22 kV X A Bus | Bus | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR495 - Tungatinah 22 kV 'A' Bus and transformer T9 interrupted due to excessive dust on 22 kV feeder earth fault relay contacts causing feeder protection to operate slower than transformer protection. | FALSE | Undefined
90582 | 12660 | 1308 |  |  | 2008-03-02 10:36 | 2008-03-02 15:46 | 310 | E0298 | AV-SM 110 kV Transmission Circuit | Transmission | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR496 - Palmerston-Avoca and Avoca-St Marys 110 kV transmission circuits interrupted due to VT failure at Avoca Substation. | FALSE | Non-Critical
90581 | 12660 | 1308 |  |  | 2008-03-02 10:36 | 2008-03-02 15:38 | 302 | E0274 | PM-AV 110 kV Transmission Circuit | Transmission | Fault | Internal Fault | Transend | Completed | TRUE | 1051 | TRUE |  | IR496 - Palmerston-Avoca and Avoca-St Marys 110 kV transmission circuits interrupted due to VT failure at Avoca Substation. | FALSE | Non-Critical
90583 | 12661 | 1309 |  |  | 2008-03-14 13:16 | 2008-03-14 21:27 | 491 | E0171 | TU-LE-WA 1 110 kV Transmission Circuit (Changed to E1957) | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR497 - Tungatinah-Lake Echo-Waddamana No 1 110 kV transmission circuit interrupted due to conductor on ground. Suspect tree striking conductor has caused conductor to jump out of support. Possible fire start, but unconfirmed by TFS. | FALSE | Critical
94889 | 12760 | 6667 |  |  | 2007-12-12 17:46 | 2007-12-19 16:17 | 9991 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94891 | 12762 | 6654 |  |  | 2007-12-02 23:04 | 2007-12-02 23:59 | 55 | E1518 | PL 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90699 | 12764 | 6772 |  |  | 2008-03-01 19:54 | 2008-03-01 20:38 | 44 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90700 | 12765 | 6771 |  |  | 2008-03-01 06:23 | 2008-03-01 06:49 | 26 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90701 | 12766 | 6770 |  |  | 2008-02-29 20:04 | 2008-02-29 20:05 | 1 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90702 | 12767 | 6769 |  |  | 2008-02-28 22:47 | 2008-02-28 22:47 | 0 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90703 | 12768 | 6768 |  |  | 2008-02-28 16:29 | 2008-02-28 16:29 | 0 | E1530 | MY 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90704 | 12769 | 6767 |  |  | 2008-02-28 14:59 | 2008-02-28 14:59 | 0 | E1538 | MY 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90705 | 12770 | 6766 |  |  | 2008-02-28 09:14 | 2008-02-28 09:14 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90706 | 12771 | 6790 |  |  | 2008-03-18 17:41 | 2008-03-18 18:11 | 30 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90707 | 12772 | 6788 |  |  | 2008-03-17 04:41 | 2008-03-17 04:41 | 0 | E0639 | ST 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90708 | 12774 | 6789 |  |  | 2008-03-18 02:19 | 2008-03-18 02:19 | 0 | E0898 | SD 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90709 | 12775 | 6786 |  |  | 2008-03-16 19:25 | 2008-03-16 19:26 | 1 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault | Unknown | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90710 | 12776 | 6785 |  |  | 2008-03-16 07:15 | 2008-03-16 07:15 | 0 | E0764 | NW 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90711 | 12777 | 6784 |  |  | 2008-03-14 14:22 | 2008-03-14 16:25 | 123 | E0354 | KI 11 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90712 | 12778 | 6783 |  |  | 2008-03-13 20:58 | 2008-03-13 20:58 | 0 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90713 | 12779 | 6781 |  |  | 2008-03-12 02:30 | 2008-03-12 02:30 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90714 | 12780 | 6795 |  |  | 2008-03-21 21:02 | 2008-03-21 21:02 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90715 | 12781 | 6796 |  |  | 2008-03-22 04:43 | 2008-03-22 04:43 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90716 | 12782 | 6797 |  |  | 2008-03-23 03:40 | 2008-03-23 03:40 | 0 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90717 | 12783 | 6798 |  |  | 2008-03-23 11:15 | 2008-03-23 14:48 | 213 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90718 | 12784 | 6799 |  |  | 2008-03-24 01:39 | 2008-03-24 01:39 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90719 | 12785 | 6800 |  |  | 2008-03-24 09:30 | 2008-03-24 09:30 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90720 | 12786 | 6780 |  |  | 2008-03-10 02:05 | 2008-03-10 02:05 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90721 | 12787 | 6779 |  |  | 2008-03-08 11:27 | 2008-03-08 11:27 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90722 | 12788 | 6778 |  |  | 2008-03-07 21:15 | 2008-03-07 22:38 | 83 | E0944 | UL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90723 | 12789 | 6776 |  |  | 2008-03-06 08:03 | 2008-03-06 08:03 | 0 | E0764 | NW 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90724 | 12790 | 6775 |  |  | 2008-03-05 08:34 | 2008-03-05 08:34 | 0 | E0970 | SO 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90725 | 12791 | 6774 |  |  | 2008-03-05 00:26 | 2008-03-05 00:26 | 0 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139323 | 12792 | 6773 |  |  | 2008-03-03 14:22 | 2008-03-03 16:02 | 100 | E0185 | TU 22 kV X D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90727 | 12793 | 6791 |  |  | 2008-03-20 07:51 | 2008-03-20 07:51 | 0 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90728 | 12794 | 6792 |  |  | 2008-03-20 10:14 | 2008-03-20 10:14 | 0 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90729 | 12795 | 6794 |  |  | 2008-03-20 12:20 | 2008-03-20 12:21 | 1 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90730 | 12796 | 6793 |  |  | 2008-03-20 10:56 | 2008-03-20 10:57 | 1 | E0156 | MB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90731 | 12797 | 6814 |  |  | 2008-03-30 23:11 | 2008-03-31 01:05 | 114 | E0789 | QT 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90732 | 12798 | 6813 |  |  | 2008-03-30 18:50 | 2008-03-30 19:19 | 29 | E0909 | TR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90733 | 12799 | 6812 |  |  | 2008-03-30 08:46 | 2008-03-30 08:47 | 1 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90734 | 12800 | 6811 |  |  | 2008-03-30 07:42 | 2008-03-30 07:56 | 14 | E0806 | QT 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90735 | 12801 | 6810 |  |  | 2008-03-29 05:43 | 2008-03-29 06:29 | 46 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90736 | 12802 | 6809 |  |  | 2008-03-29 03:44 | 2008-03-29 04:36 | 52 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90737 | 12803 | 6808 |  |  | 2008-03-29 03:09 | 2008-03-29 03:34 | 25 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90738 | 12804 | 6807 |  |  | 2008-03-29 03:07 | 2008-03-29 03:07 | 0 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90739 | 12805 | 6806 |  |  | 2008-03-27 17:28 | 2008-03-27 17:28 | 0 | E0970 | SO 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90740 | 12806 | 6805 |  |  | 2008-03-26 13:35 | 2008-03-26 13:58 | 23 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90741 | 12807 | 6804 |  |  | 2008-03-25 15:24 | 2008-03-25 16:24 | 60 | E0836 | RK 11 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90742 | 12808 | 6803 |  |  | 2008-03-25 16:11 | 2008-03-25 16:11 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90743 | 12809 | 6802 |  |  | 2008-03-25 04:57 | 2008-03-25 05:42 | 45 | E0836 | RK 11 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90744 | 12810 | 6801 |  |  | 2008-03-25 03:12 | 2008-03-25 03:13 | 1 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90825 | 12880 | 6815 |  |  | 2008-03-31 14:54 | 2008-03-31 14:54 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185930 | 12881 | 6817 |  |  | 2008-04-02 12:29 | 2008-04-02 12:29 | 0 | E0725 | NT 22 kV A2X Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90827 | 12882 | 6818 |  |  | 2008-04-02 13:09 | 2008-04-02 13:09 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90828 | 12883 | 6819 |  |  | 2008-04-02 13:25 | 2008-04-02 13:25 | 0 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90829 | 12884 | 6820 |  |  | 2008-04-02 13:34 | 2008-04-02 13:55 | 21 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90830 | 12885 | 6821 |  |  | 2008-04-02 15:08 | 2008-04-02 15:08 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90831 | 12886 | 6822 |  |  | 2008-04-02 15:18 | 2008-04-02 18:25 | 187 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90832 | 12887 | 6823 |  |  | 2008-04-02 13:57 | 2008-04-02 15:17 | 80 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90833 | 12888 | 6825 |  |  | 2008-04-02 15:32 | 2008-04-02 15:52 | 20 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90834 | 12889 | 6826 |  |  | 2008-04-02 15:28 | 2008-04-02 16:12 | 44 | E1001 | BU 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90835 | 12890 | 6827 |  |  | 2008-04-02 15:28 | 2008-04-02 15:41 | 13 | E0779 | PL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90836 | 12891 | 6828 |  |  | 2008-04-02 15:28 | 2008-04-02 15:41 | 13 | E1518 | PL 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90837 | 12892 | 6829 |  |  | 2008-04-02 16:22 | 2008-04-02 16:22 | 0 | E0820 | RA 22 kV C2 Feeder Circuit | Feeder | Fault | Unknown | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90838 | 12893 | 6830 |  |  | 2008-04-02 15:43 | 2008-04-02 16:28 | 45 | E0465 | KR 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90839 | 12894 | 6831 |  |  | 2008-04-02 17:00 | 2008-04-02 17:00 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90840 | 12895 | 6832 |  |  | 2008-04-02 17:06 | 2008-04-02 17:06 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90841 | 12896 | 6833 |  |  | 2008-04-02 17:09 | 2008-04-02 17:09 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90842 | 12897 | 6834 |  |  | 2008-04-02 17:09 | 2008-04-02 17:09 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90843 | 12898 | 6835 |  |  | 2008-04-02 17:15 | 2008-04-02 20:03 | 168 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90844 | 12899 | 6836 |  |  | 2008-04-02 16:29 | 2008-04-02 18:05 | 96 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90845 | 12900 | 6837 |  |  | 2008-04-02 19:50 | 2008-04-02 21:23 | 93 | E1535 | MY 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90846 | 12901 | 6838 |  |  | 2008-04-02 21:42 | 2008-04-02 21:42 | 0 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90847 | 12902 | 6839 |  |  | 2008-04-02 22:48 | 2008-04-02 22:48 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90848 | 12903 | 6840 |  |  | 2008-04-02 22:50 | 2008-04-02 23:59 | 69 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90849 | 12904 | 6841 |  |  | 2008-04-03 00:17 | 2008-04-03 00:17 | 0 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90850 | 12905 | 6842 |  |  | 2008-04-03 01:22 | 2008-04-03 01:22 | 0 | E0014 | BW 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90851 | 12906 | 6843 |  |  | 2008-04-02 23:48 | 2008-04-03 03:09 | 201 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90852 | 12907 | 6845 |  |  | 2008-04-03 00:24 | 2008-04-03 06:11 | 347 | E0844 | RK 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90853 | 12908 | 6846 |  |  | 2008-04-03 00:54 | 2008-04-03 06:39 | 345 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90854 | 12909 | 6847 |  |  | 2008-04-03 01:01 | 2008-04-03 04:52 | 231 | E1004 | BU 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90855 | 12910 | 6848 |  |  | 2008-04-03 01:29 | 2008-04-03 10:12 | 523 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90856 | 12911 | 6849 |  |  | 2008-04-03 02:02 | 2008-04-03 04:50 | 168 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90857 | 12912 | 6850 |  |  | 2008-04-03 02:11 | 2008-04-03 02:11 | 0 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90858 | 12913 | 6852 |  |  | 2008-04-03 02:21 | 2008-04-03 02:21 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90859 | 12914 | 6854 |  |  | 2008-04-03 02:33 | 2008-04-03 04:47 | 134 | E1479 | RI 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90860 | 12915 | 6855 |  |  | 2008-04-03 02:33 | 2008-04-03 04:36 | 123 | E1482 | RI 33 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90861 | 12916 | 6856 |  |  | 2008-04-03 02:37 | 2008-04-03 02:37 | 0 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90862 | 12917 | 6857 |  |  | 2008-04-03 02:53 | 2008-04-03 03:38 | 45 | E0118 | CS 11 kV T2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90863 | 12918 | 6858 |  |  | 2008-04-03 03:03 | 2008-04-03 03:03 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90864 | 12919 | 6859 |  |  | 2008-04-03 02:17 | 2008-04-03 05:12 | 175 | E1592 | CS 11 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90865 | 12920 | 6860 |  |  | 2008-04-03 02:10 | 2008-04-03 05:27 | 197 | E0085 | CR 33 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90866 | 12921 | 6861 |  |  | 2008-04-03 02:24 | 2008-04-03 09:15 | 411 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90867 | 12922 | 6862 |  |  | 2008-04-03 04:50 | 2008-04-03 14:25 | 575 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90868 | 12923 | 6863 |  |  | 2008-04-03 10:42 | 2008-04-03 10:42 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90870 | 12925 | 6865 |  |  | 2008-04-03 21:42 | 2008-04-03 21:42 | 0 | E1004 | BU 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90871 | 12926 | 6866 |  |  | 2008-04-03 22:19 | 2008-04-03 22:19 | 0 | E1004 | BU 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90872 | 12927 | 6867 |  |  | 2008-04-03 23:05 | 2008-04-03 23:05 | 0 | E1004 | BU 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90873 | 12928 | 6868 |  |  | 2008-04-03 23:14 | 2008-04-03 23:14 | 0 | E1004 | BU 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90874 | 12929 | 6869 |  |  | 2008-04-03 23:45 | 2008-04-04 00:30 | 45 | E1004 | BU 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90885 | 12957 | 1321 |  |  | 2008-04-07 07:53 | 2008-04-07 17:21 | 568 | E1027 | QU 22 kV A Bus | Bus | Fault | Insulation Failure | Transend | Completed | TRUE | 1493 | TRUE |  | IR498 - Que Substation 22 kV bus interruption due to current transformer failure following down stream feeder fault. | FALSE | Undefined
90887 | 12958 | 1310 |  |  | 2008-04-03 02:05 | 2008-04-03 02:16 | 11 | E0030 | CS-KI-KR 110 kV Transmission Circuit (changed to E1955) | Transmission | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 0 | TRUE |  | IR500 - Chapel Street-Kingston-Knights Road 110 kV transmission circuit interrupted during strong winds. | FALSE | Non-Critical
90888 | 12958 | 1310 |  |  | 2008-04-03 02:18 | 2008-04-03 02:22 | 4 | E0030 | CS-KI-KR 110 kV Transmission Circuit (changed to E1955) | Transmission | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 115 | TRUE |  | IR500 - Chapel Street-Kingston-Knights Road 110 kV transmission circuit interrupted during strong winds. | FALSE | Non-Critical
90886 | 12958 | 1310 |  |  | 2008-04-03 02:04 | 2008-04-03 02:04 | 0 | E0030 | CS-KI-KR 110 kV Transmission Circuit (changed to E1955) | Transmission | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 0 | TRUE |  | IR500 - Chapel Street-Kingston-Knights Road 110 kV transmission circuit interrupted during strong winds. | FALSE | Non-Critical
90892 | 12959 | 1313 |  |  | 2008-04-03 03:02 | 2008-04-03 03:02 | 0 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 0 | TRUE |  | IR501 - Lindisfarne-Sorell-Triabunna 110 kV transmission circuit interrupted six times during widespread destructive winds. | FALSE | Non-Critical
90893 | 12959 | 1313 |  |  | 2008-04-03 03:04 | 2008-04-03 03:04 | 0 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 0 | TRUE |  | IR501 - Lindisfarne-Sorell-Triabunna 110 kV transmission circuit interrupted six times during widespread destructive winds. | FALSE | Non-Critical
90894 | 12959 | 1313 |  |  | 2008-04-03 03:08 | 2008-04-03 07:07 | 239 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 676 | TRUE |  | IR501 - Lindisfarne-Sorell-Triabunna 110 kV transmission circuit interrupted six times during widespread destructive winds. | FALSE | Non-Critical
90889 | 12959 | 1313 |  |  | 2008-04-03 02:37 | 2008-04-03 02:37 | 0 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 0 | TRUE |  | IR501 - Lindisfarne-Sorell-Triabunna 110 kV transmission circuit interrupted six times during widespread destructive winds. | FALSE | Non-Critical
90890 | 12959 | 1313 |  |  | 2008-04-03 02:48 | 2008-04-03 02:57 | 9 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 0 | TRUE |  | IR501 - Lindisfarne-Sorell-Triabunna 110 kV transmission circuit interrupted six times during widespread destructive winds. | FALSE | Non-Critical
90891 | 12959 | 1313 |  |  | 2008-04-03 03:00 | 2008-04-03 03:00 | 0 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 0 | TRUE |  | IR501 - Lindisfarne-Sorell-Triabunna 110 kV transmission circuit interrupted six times during widespread destructive winds. | FALSE | Non-Critical
90896 | 12960 | 1316 |  |  | 2008-04-03 08:30 | 2008-04-03 08:39 | 9 | E0832 | RK 11 kV A Bus | Bus | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 96 | TRUE |  | IR502 - Lindisfarne-Rokeby No 1 110 kV transmission circuit interrupted during strong winds. | FALSE | Undefined
90895 | 12960 | 1316 |  |  | 2008-04-03 08:30 | 2008-04-03 11:25 | 175 | E0348 | LF-RK 1 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 0 | TRUE |  | IR502 - Lindisfarne-Rokeby No 1 110 kV transmission circuit interrupted during strong winds. | FALSE | Non-Critical
90897 | 12961 | 6871 |  |  | 2008-04-06 10:33 | 2008-04-06 10:33 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90898 | 12962 | 6872 |  |  | 2008-04-06 16:03 | 2008-04-06 16:03 | 0 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90899 | 12963 | 6873 |  |  | 2008-04-07 06:01 | 2008-04-07 06:58 | 57 | E0569 | EB 11 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90900 | 12964 | 6874 |  |  | 2008-04-07 07:46 | 2008-04-07 07:49 | 3 | E0569 | EB 11 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139326 | 12966 | 6876 |  |  | 2008-04-11 07:55 | 2008-04-11 07:55 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90902 | 12967 | 6877 |  |  | 2008-04-11 20:49 | 2008-04-11 20:49 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90903 | 12968 | 6878 |  |  | 2008-04-13 20:52 | 2008-04-13 20:52 | 0 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90904 | 12969 | 6879 |  |  | 2008-04-13 20:58 | 2008-04-13 20:58 | 0 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90905 | 12970 | 6887 |  |  | 2008-04-19 15:57 | 2008-04-19 16:16 | 19 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90906 | 12971 | 6886 |  |  | 2008-04-19 09:09 | 2008-04-19 09:09 | 0 | E1552 | DP 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90907 | 12972 | 6885 |  |  | 2008-04-17 19:58 | 2008-04-17 20:19 | 21 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90908 | 12973 | 6880 |  |  | 2008-04-15 01:34 | 2008-04-15 01:34 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90909 | 12974 | 6881 |  |  | 2008-04-15 09:55 | 2008-04-15 09:55 | 0 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90910 | 12975 | 6882 |  |  | 2008-04-15 10:29 | 2008-04-15 10:29 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90911 | 12976 | 6883 |  |  | 2008-04-15 11:35 | 2008-04-15 11:35 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90912 | 12977 | 6884 |  |  | 2008-04-15 11:59 | 2008-04-15 12:01 | 2 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90913 | 12978 | 6897 |  |  | 2008-04-26 17:20 | 2008-04-26 18:22 | 62 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90914 | 12979 | 6898 |  |  | 2008-04-26 17:38 | 2008-04-26 17:38 | 0 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90915 | 12980 | 6896 |  |  | 2008-04-26 16:37 | 2008-04-26 17:07 | 30 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90916 | 12981 | 6895 |  |  | 2008-04-26 16:35 | 2008-04-26 16:35 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90917 | 12982 | 6894 |  |  | 2008-04-26 15:52 | 2008-04-26 16:18 | 26 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90918 | 12983 | 6893 |  |  | 2008-04-26 04:18 | 2008-04-26 04:33 | 15 | E1612 | UL 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90919 | 12984 | 6892 |  |  | 2008-04-26 04:04 | 2008-04-26 04:04 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90920 | 12985 | 6891 |  |  | 2008-04-25 18:48 | 2008-04-25 20:54 | 126 | E0415 | EL 11 kV XE2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90921 | 12986 | 6890 |  |  | 2008-04-24 14:03 | 2008-04-24 14:21 | 18 | E1570 | DP 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90922 | 12987 | 6889 |  |  | 2008-04-24 11:32 | 2008-04-24 12:58 | 86 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90923 | 12988 | 6888 |  |  | 2008-04-21 10:07 | 2008-04-21 10:17 | 10 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
90924 | 12989 | 1322 |  |  | 2008-04-15 10:20 | 2008-04-15 11:04 | 44 | E1357 | NN 110 kV C1 Capacitor Circuit | Capacitor | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR503 - New Norfolk Substation capacitor bank C1 interruption due to operator error during protection tests. | FALSE | Non-Critical
91016 | 13080 | 6899 |  |  | 2008-04-28 14:04 | 2008-04-28 14:04 | 0 | E0943 | UL 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91017 | 13081 | 6900 |  |  | 2008-04-29 00:13 | 2008-04-29 00:14 | 1 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91018 | 13082 | 6901 |  |  | 2008-04-29 22:20 | 2008-04-29 22:44 | 24 | E0494 | GT 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91019 | 13083 | 6902 |  |  | 2008-05-03 05:26 | 2008-05-03 05:48 | 22 | E1548 | DP 22 kV C2 Capacitor Circuit | Capacitor | Fault | Unknown | DNSP | Completed | FALSE | 0 | TRUE |  |  | FALSE | Undefined
91020 | 13084 | 6904 |  |  | 2008-05-07 23:01 | 2008-05-07 23:01 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91021 | 13085 | 6905 |  |  | 2008-05-09 15:49 | 2008-05-09 15:49 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91022 | 13086 | 6906 |  |  | 2008-05-10 23:28 | 2008-05-10 23:28 | 0 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91023 | 13087 | 6907 |  |  | 2008-05-11 09:04 | 2008-05-11 09:04 | 0 | E1573 | DP 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91024 | 13088 | 6912 |  |  | 2008-05-20 07:00 | 2008-05-20 07:00 | 0 | E0464 | KR 11 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91025 | 13090 | 6911 |  |  | 2008-05-19 12:04 | 2008-05-19 12:04 | 0 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91026 | 13091 | 6910 |  |  | 2008-05-19 00:04 | 2008-05-19 00:04 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91027 | 13092 | 6909 |  |  | 2008-05-15 01:37 | 2008-05-15 02:28 | 51 | E1535 | MY 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91028 | 13093 | 6908 |  |  | 2008-05-14 03:08 | 2008-05-14 03:08 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91029 | 13095 | 1323 |  |  | 2008-05-23 02:04 | 2008-05-23 03:07 | 63 | E0193 | SO 110/22 kV T2 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR537 - Sorell Substation transformer T2 interrupted due to poor grading between newly upgraded feeder protection and TF protection. | FALSE | Non-Critical
139328 | 13096 | 6918 |  |  | 2008-05-28 08:12 | 2008-05-28 08:12 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91031 | 13097 | 6917 |  |  | 2008-05-27 11:06 | 2008-05-27 11:31 | 25 | E0122 | CS 11 kV X2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91032 | 13098 | 6916 |  |  | 2008-05-26 04:02 | 2008-05-26 16:02 | 720 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91033 | 13100 | 6914 |  |  | 2008-05-23 02:04 | 2008-05-23 02:04 | 0 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91034 | 13101 | 6913 |  |  | 2008-05-22 23:49 | 2008-05-22 23:49 | 0 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
175163 | 13104 | 1325 |  |  | 2008-06-01 09:54 | 2008-06-01 11:32 | 98 | E0177 | TU 110/22 kV T8X Transformer Circuit | Transformer | Fault | Mechanical Failure | Transend | Completed | TRUE | 42 | TRUE |  | IR543 - Tungatinah Substation transformer T9 interrupted due to faulty 22 kV circuit breaker operating mechanism (C252) preventing C252 from tripping. TF protection subsequently operated. Report Number 1325 has been duplicated. See outage ID13559 for another fault report 1325 (LI-PM 220kV) and RIMsys report IR569. D Alimu | FALSE | Non-Critical
175164 | 13104 | 1325 |  |  | 2008-06-01 09:54 | 2008-06-01 11:32 | 98 | E0179 | TU 110/22 kV T9X Transformer Circuit | Transformer | Fault | Mechanical Failure | Transend | Completed | TRUE | 0 | TRUE |  | IR543 - Tungatinah Substation transformer T9 interrupted due to faulty 22 kV circuit breaker operating mechanism (C252) preventing C252 from tripping. TF protection subsequently operated. Report Number 1325 has been duplicated. See outage ID13559 for another fault report 1325 (LI-PM 220kV) and RIMsys report IR569. D Alimu | FALSE | Undefined
91131 | 13196 | 6924 |  |  | 2008-06-07 09:55 | 2008-06-07 09:56 | 1 | E0197 | SO 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91132 | 13197 | 6925 |  |  | 2008-06-08 19:20 | 2008-06-08 19:40 | 20 | E0491 | GT 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91133 | 13198 | 6926 |  |  | 2008-06-09 11:14 | 2008-06-09 11:15 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91134 | 13199 | 6937 |  |  | 2008-06-12 07:52 | 2008-06-12 07:52 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91135 | 13200 | 6929 |  |  | 2008-06-11 05:00 | 2008-06-11 05:00 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91136 | 13201 | 6930 |  |  | 2008-06-11 05:44 | 2008-06-11 05:44 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91137 | 13202 | 6931 |  |  | 2008-06-11 06:17 | 2008-06-11 06:17 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91138 | 13203 | 6932 |  |  | 2008-06-11 06:23 | 2008-06-11 06:23 | 0 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91139 | 13204 | 6933 |  |  | 2008-06-11 06:47 | 2008-06-11 06:47 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91140 | 13205 | 6934 |  |  | 2008-06-11 07:07 | 2008-06-11 07:07 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91141 | 13206 | 6935 |  |  | 2008-06-11 07:10 | 2008-06-11 09:35 | 145 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91142 | 13207 | 6936 |  |  | 2008-06-11 06:21 | 2008-06-11 10:24 | 243 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91143 | 13208 | 6927 |  |  | 2008-06-09 19:10 | 2008-06-09 19:10 | 0 | E0819 | RA 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91144 | 13209 | 6928 |  |  | 2008-06-10 00:53 | 2008-06-10 00:54 | 1 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139330 | 13210 | 6923 |  |  | 2008-06-01 09:54 | 2008-06-01 14:48 | 294 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139331 | 13211 | 6922 |  |  | 2008-06-01 09:54 | 2008-06-01 11:37 | 103 | E0185 | TU 22 kV X D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139332 | 13213 | 6943 |  |  | 2008-06-17 07:45 | 2008-06-17 07:45 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91148 | 13214 | 6941 |  |  | 2008-06-14 16:23 | 2008-06-14 16:23 | 0 | E0014 | BW 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91149 | 13215 | 6940 |  |  | 2008-06-13 23:34 | 2008-06-13 23:52 | 18 | E1505 | TB 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91150 | 13216 | 6939 |  |  | 2008-06-13 15:17 | 2008-06-13 15:17 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91151 | 13217 | 6938 |  |  | 2008-06-12 16:59 | 2008-06-12 16:59 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91152 | 13218 | 6942 |  |  | 2008-06-14 20:42 | 2008-06-14 20:42 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91153 | 13220 | 6944 |  |  | 2008-06-17 10:32 | 2008-06-17 11:45 | 73 | E0022 | BW 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91154 | 13221 | 6945 |  |  | 2008-06-19 17:06 | 2008-06-19 17:06 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91155 | 13222 | 6946 |  |  | 2008-06-21 01:19 | 2008-06-21 01:19 | 0 | E0462 | KR 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91156 | 13223 | 6947 |  |  | 2008-06-21 10:34 | 2008-06-21 11:59 | 85 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91157 | 13224 | 6948 |  |  | 2008-06-22 08:34 | 2008-06-22 08:54 | 20 | E0819 | RA 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91158 | 13225 | 6949 |  |  | 2008-06-23 03:13 | 2008-06-23 03:29 | 16 | E0414 | EL 11 kV XD2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91159 | 13226 | 6952 |  |  | 2008-06-23 08:57 | 2008-06-23 09:13 | 16 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91160 | 13227 | 6953 |  |  | 2008-06-25 03:55 | 2008-06-25 03:55 | 0 | E0413 | EL 11 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91161 | 13228 | 6954 |  |  | 2008-06-25 04:04 | 2008-06-25 04:04 | 0 | E0413 | EL 11 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91162 | 13230 | 6955 |  |  | 2008-06-25 04:13 | 2008-06-25 04:13 | 0 | E0413 | EL 11 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91163 | 13231 | 6956 |  |  | 2008-06-25 04:19 | 2008-06-25 04:19 | 0 | E0413 | EL 11 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
118399 | 13234 | 1327 |  |  | 2008-06-08 00:31 | 2008-06-08 00:53 | 22 | E1621 | RI 110 kV Bus SPS | Bus | Fault | Basslink | Basslink | Completed | TRUE | 973 | TRUE |  | IR538 - Basslink FCSPS operation due to circuit breaker failure at Loy Yang Converter Station resulting in contracted load shedding. This report 1327 have been duplicated with another number ID1356. G.Hwaba | FALSE | Undefined
91167 | 13235 | 1328 |  |  | 2008-06-23 03:13 | 2008-06-23 03:29 | 16 | E0410 | EL 11 kV Bus | Bus | Fault | Internal Fault | Transend | Completed | TRUE | 48 | TRUE |  | IR539 - Electrona Substation 11 kV Bus interruption due to suspected earth voltage rise (resulting from feeder fault) affecting electronics within recloser control cabinet. | FALSE | Undefined
91169 | 13236 | 1329 |  |  | 2008-06-25 04:19 | 2008-06-25 05:31 | 72 | E0418 | EL 110/11 kV T4 Transformer Circuit | Transformer | Fault | Electrical Interference / Noise | Transend | Completed | TRUE | 0 | TRUE |  | IR540 - Electrona Substation 11 kV Bus interruption due to earth voltage rise under lightning conditions inadvertently causing bus protection to operate. | FALSE | Undefined
91168 | 13236 | 1329 |  |  | 2008-06-25 04:19 | 2008-06-25 05:31 | 72 | E0410 | EL 11 kV Bus | Bus | Fault | Electrical Interference / Noise | Transend | Completed | TRUE | 349 | TRUE |  | IR540 - Electrona Substation 11 kV Bus interruption due to earth voltage rise under lightning conditions inadvertently causing bus protection to operate. | FALSE | Undefined
91170 | 13237 | 1330 |  |  | 2008-06-26 07:24 | 2008-06-26 07:24 | 0 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR541 - Farrell-Rosebery-Queenstown 110 kV transmission circuit momentarily interrupted during lightning storms. | FALSE | Non-Critical
91171 | 13238 | 1331 |  |  | 2008-06-26 07:24 | 2008-06-26 07:37 | 13 | E0715 | FA-JB 220 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR542 - Farrell-John Butters 220 kV transmission circuit interrupted during lightning storms. | FALSE | Non-Critical
91214 | 13286 | 6978 |  |  | 2008-07-01 00:52 | 2008-07-01 04:59 | 247 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91215 | 13287 | 6975 |  |  | 2008-07-01 01:03 | 2008-07-01 01:03 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91216 | 13288 | 6974 |  |  | 2008-07-01 00:53 | 2008-07-01 00:53 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139336 | 13289 | 6973 |  |  | 2008-06-30 23:59 | 2008-06-30 23:59 | 0 | E1567 | DP 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139337 | 13290 | 6972 |  |  | 2008-06-30 23:52 | 2008-06-30 23:52 | 0 | E1567 | DP 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91219 | 13291 | 6971 |  |  | 2008-06-30 23:35 | 2008-06-30 23:35 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91220 | 13292 | 6970 |  |  | 2008-06-30 23:08 | 2008-06-30 23:08 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91221 | 13293 | 6969 |  |  | 2008-06-30 16:48 | 2008-06-30 19:31 | 163 | E0358 | KI 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91222 | 13294 | 6968 |  |  | 2008-06-30 13:19 | 2008-06-30 14:27 | 68 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91223 | 13295 | 6967 |  |  | 2008-06-30 13:30 | 2008-06-30 13:30 | 0 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91224 | 13296 | 6966 |  |  | 2008-06-30 13:12 | 2008-06-30 13:12 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91225 | 13297 | 6965 |  |  | 2008-06-30 13:06 | 2008-06-30 13:06 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91226 | 13298 | 6964 |  |  | 2008-06-30 12:20 | 2008-06-30 12:20 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139338 | 13299 | 6963 |  |  | 2008-06-29 00:11 | 2008-06-29 00:11 | 0 | E1568 | DP 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91228 | 13300 | 6962 |  |  | 2008-06-27 11:35 | 2008-06-27 12:21 | 46 | E0158 | MB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91229 | 13301 | 6961 |  |  | 2008-06-26 10:26 | 2008-06-26 11:36 | 70 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139339 | 13302 | 6960 |  |  | 2008-06-26 10:26 | 2008-06-26 11:04 | 38 | E1568 | DP 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91231 | 13303 | 6959 |  |  | 2008-06-26 09:34 | 2008-06-26 09:34 | 0 | E0865 | RB 44 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91232 | 13304 | 6958 |  |  | 2008-06-25 22:54 | 2008-06-25 23:14 | 20 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91233 | 13305 | 6957 |  |  | 2008-06-25 05:31 | 2008-06-25 07:20 | 109 | E0413 | EL 11 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106179 | 13325 | 1335 |  |  | 2008-07-02 04:39 | 2008-07-02 16:40 | 721 | E0351 | WA-LF 2 110 kV Transmission Circuit | Transmission | Fault | Age | Transend | Completed | TRUE | 0 | TRUE |  | IR544 - Waddamana-Lindisfarne No. 2 110 kV transmission circuit interrupted due to conductor on ground during windy and snowy conditions. | FALSE | Undefined
91259 | 13326 | 1333 |  |  | 2008-07-01 17:25 | 2008-07-01 21:55 | 270 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR545 - George Town-George Town Converter Station 220 kV transmission circuit interrupted due to deficient DC wiring design for current comparison relay Z187B. | FALSE | Undefined
91260 | 13327 | 6989 |  |  | 2008-07-09 13:21 | 2008-07-09 13:22 | 1 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91261 | 13328 | 6988 |  |  | 2008-07-08 08:33 | 2008-07-08 08:33 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91262 | 13329 | 6987 |  |  | 2008-07-05 08:37 | 2008-07-05 08:37 | 0 | E1444 | HA 22 kV K2 Feeder Circuit | Feeder | Fault | Unknown | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91263 | 13330 | 6986 |  |  | 2008-07-05 08:37 | 2008-07-05 08:37 | 0 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91264 | 13331 | 6985 |  |  | 2008-07-04 16:41 | 2008-07-04 17:51 | 70 | E0083 | CR 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91265 | 13332 | 6984 |  |  | 2008-07-03 08:38 | 2008-07-03 08:38 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91266 | 13333 | 6983 |  |  | 2008-07-03 07:26 | 2008-07-03 07:26 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91267 | 13334 | 6982 |  |  | 2008-07-02 06:19 | 2008-07-02 06:19 | 0 | E0639 | ST 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91268 | 13335 | 6981 |  |  | 2008-07-02 01:34 | 2008-07-02 04:31 | 177 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91269 | 13336 | 6980 |  |  | 2008-07-02 01:32 | 2008-07-02 01:32 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91270 | 13337 | 6979 |  |  | 2008-07-01 13:38 | 2008-07-01 14:34 | 56 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91271 | 13338 | 6977 |  |  | 2008-07-01 00:03 | 2008-07-01 13:03 | 780 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91272 | 13339 | 6976 |  |  | 2008-07-01 00:03 | 2008-07-01 14:26 | 863 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91273 | 13340 | 6990 |  |  | 2008-07-12 23:14 | 2008-07-13 00:19 | 65 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91274 | 13341 | 6991 |  |  | 2008-07-16 03:03 | 2008-07-16 03:21 | 18 | E1504 | TB 22 KV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91275 | 13342 | 6992 |  |  | 2008-07-17 00:54 | 2008-07-17 03:42 | 168 | E1550 | DP 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91276 | 13343 | 6993 |  |  | 2008-07-17 18:47 | 2008-07-17 18:48 | 1 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91277 | 13344 | 6994 |  |  | 2008-07-18 06:36 | 2008-07-18 06:36 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91278 | 13345 | 6995 |  |  | 2008-07-19 09:10 | 2008-07-19 09:26 | 16 | E0948 | UL 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91279 | 13346 | 6996 |  |  | 2008-07-20 16:14 | 2008-07-20 19:43 | 209 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91280 | 13347 | 6997 |  |  | 2008-07-21 08:05 | 2008-07-21 13:59 | 354 | E0078 | CR 33 kV C2 Feeder Circuit | Feeder | Fault | Age | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91281 | 13348 | 6998 |  |  | 2008-07-21 12:20 | 2008-07-21 12:21 | 1 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106180 | 13349 | 1332 |  |  | 2008-07-01 21:44 | 2008-07-01 21:48 | 4 | E0351 | WA-LF 2 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR546 - Waddamana-Lindisfarne 110 kV transmission circuit interrupted during strong winds. | FALSE | Undefined
91283 | 13350 | 1334 |  |  | 2008-07-02 02:59 | 2008-07-02 03:12 | 13 | E0718 | FA-MA 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR547 - Farrell-Mackintosh 110 kV transmission circuit interrupted during strong winds and lightning storms. | FALSE | Non-Critical
91284 | 13352 | 1337 |  |  | 2008-07-09 04:13 | 2008-07-09 04:13 | 0 | E1072 | LF-RI 2 110 kV Transmission Circuit | Transmission | Fault | Pollution | Transend | Completed | TRUE | 0 | TRUE |  | IR549 - Lindisfarne-Risdon No 2 110 kV transmission circuit tripped and successfully reclosed during foggy conditions. Suspect due to pollution causing insulator flashover. Nyrstar lost 76 MW for 5 minutes (380 MWmins) | FALSE | Non-Critical
91286 | 13354 | 1339 |  |  | 2008-07-24 11:23 | 2008-07-24 14:55 | 212 | E1676 | CS 11 kV C4 Capacitor Circuit | Capacitor | Fault | Poor Design | Transend | Completed | FALSE | 0 | TRUE |  | IR551 - Chapel Street 11 kV capacitor bank circuit breaker D652 tripped open on over voltage. | FALSE | Undefined
91365 | 13450 | 6999 |  |  | 2008-07-22 01:15 | 2008-07-22 03:22 | 127 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91366 | 13451 | 7000 |  |  | 2008-07-23 09:44 | 2008-07-23 09:44 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91367 | 13452 | 7001 |  |  | 2008-07-24 18:52 | 2008-07-24 18:52 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91368 | 13453 | 7002 |  |  | 2008-07-26 17:43 | 2008-07-26 17:43 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91369 | 13454 | 7003 |  |  | 2008-07-28 18:10 | 2008-07-28 18:11 | 1 | E0946 | UL 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91370 | 13455 | 7004 |  |  | 2008-07-28 21:09 | 2008-07-28 22:41 | 92 | E0764 | NW 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91371 | 13456 | 7005 |  |  | 2008-07-29 08:08 | 2008-07-29 08:09 | 1 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91372 | 13457 | 7006 |  |  | 2008-07-29 08:22 | 2008-07-29 08:29 | 7 | E0906 | TR 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91373 | 13458 | 7007 |  |  | 2008-07-31 02:04 | 2008-07-31 07:55 | 351 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91374 | 13459 | 7008 |  |  | 2008-08-01 01:38 | 2008-08-01 01:38 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91375 | 13460 | 7009 |  |  | 2008-08-01 03:51 | 2008-08-01 03:51 | 0 | E0414 | EL 11 kV XD2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91376 | 13461 | 7010 |  |  | 2008-08-01 05:20 | 2008-08-01 05:20 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91377 | 13462 | 7011 |  |  | 2008-08-01 05:20 | 2008-08-01 05:20 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91378 | 13463 | 7012 |  |  | 2008-08-01 06:04 | 2008-08-01 06:04 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139341 | 13464 | 7013 |  |  | 2008-08-02 13:23 | 2008-08-02 14:12 | 49 | E1568 | DP 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91380 | 13465 | 7014 |  |  | 2008-08-02 14:52 | 2008-08-02 16:33 | 101 | E0465 | KR 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91411 | 13520 | 7016 |  |  | 2008-08-04 10:26 | 2008-08-04 10:26 | 0 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91412 | 13521 | 7087 |  |  | 2008-08-06 01:18 | 2008-08-06 01:18 | 0 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91413 | 13522 | 7088 |  |  | 2008-08-07 17:08 | 2008-08-07 17:09 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91414 | 13523 | 7089 |  |  | 2008-08-07 19:18 | 2008-08-07 19:42 | 24 | E0186 | TU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91415 | 13524 | 7090 |  |  | 2008-08-08 09:54 | 2008-08-08 09:54 | 0 | E1535 | MY 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91416 | 13525 | 7091 |  |  | 2008-08-09 18:13 | 2008-08-09 18:13 | 0 | E0356 | KI 11 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91417 | 13526 | 7092 |  |  | 2008-08-10 01:10 | 2008-08-10 01:10 | 0 | E1552 | DP 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91418 | 13527 | 7093 |  |  | 2008-08-10 01:49 | 2008-08-10 03:44 | 115 | E0361 | KI 11 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91419 | 13528 | 7094 |  |  | 2008-08-10 15:44 | 2008-08-10 15:44 | 0 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91420 | 13529 | 7095 |  |  | 2008-08-12 21:06 | 2008-08-12 21:06 | 0 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91421 | 13530 | 7096 |  |  | 2008-08-12 21:23 | 2008-08-12 21:23 | 0 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91422 | 13531 | 7097 |  |  | 2008-08-15 04:18 | 2008-08-15 08:51 | 273 | E0186 | TU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91423 | 13532 | 7098 |  |  | 2008-08-15 11:15 | 2008-08-15 11:54 | 39 | E0186 | TU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91424 | 13533 | 7101 |  |  | 2008-08-18 06:41 | 2008-08-18 06:41 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91425 | 13534 | 7102 |  |  | 2008-08-20 22:17 | 2008-08-20 22:17 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91443 | 13558 | 1323 |  |  | 2008-08-06 14:57 | 2008-08-06 15:07 | 10 | E0585 | EB 110/11 kV T2 Transformer Circuit | Transformer | Fault | Poor Design | Transend | Completed | TRUE | 0 | TRUE |  | IR 568 - Emu Bay Substation transformer T2 interrupted. It is suspected that electromechanical relay B557 inadvertently operated due to vibration resulting from closing of cabinet door. not included in ITOMS as cause on LV side of T2 | FALSE | Non-Critical
91445 | 13559 | 1324 |  |  | 2008-08-14 17:33 | 2008-08-14 19:13 | 100 | E0256 | PM 220 kV E Bus | Bus | Fault | Mechanical Failure | Transend | Completed | TRUE | 0 | TRUE |  | IR569 - PM-SH 220 kV interrupted. LI-PM No.1, PM 220 kV E bus and PM-SH 220 kV tripped when PM-SH 220 kV was being restored after earlier fault. The cause of outage was due to a faulty 220 kV isolator F129E (red phase) at Palmerston Substation. Report Number 1324 has been duplicated. See outage ID13102 for another fault report number 1324. D Alimu | FALSE | Undefined
91444 | 13559 | 1324 |  |  | 2008-08-14 17:33 | 2008-08-14 19:13 | 100 | E0244 | LI-PM 1 220 kV Transmission Circuit | Transmission | Fault | Mechanical Failure | Transend | Completed | TRUE | 0 | TRUE |  | IR569 - PM-SH 220 kV interrupted. LI-PM No.1, PM 220 kV E bus and PM-SH 220 kV tripped when PM-SH 220 kV was being restored after earlier fault. The cause of outage was due to a faulty 220 kV isolator F129E (red phase) at Palmerston Substation. Report Number 1324 has been duplicated. See outage ID13102 for another fault report number 1324. D Alimu | FALSE | Critical
91446 | 13559 | 1324 |  |  | 2008-08-14 14:16 | 2008-08-14 18:09 | 233 | E0291 | PM-SH 220 kV Transmission Circuit | Transmission | Fault | Mechanical Failure | Transend | Completed | TRUE | 0 | TRUE |  | IR569 - PM-SH 220 kV interrupted. LI-PM No.1, PM 220 kV E bus and PM-SH 220 kV tripped when PM-SH 220 kV was being restored after earlier fault. The cause of outage was due to a faulty 220 kV isolator F129E (red phase) at Palmerston Substation. Report Number 1324 has been duplicated. See outage ID13102 for another fault report number 1324. D Alimu | FALSE | Critical
91447 | 13561 | 1327 |  |  | 2008-08-14 23:12 | 2008-08-14 23:12 | 0 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Basslink | Basslink | Completed | TRUE | 0 | TRUE |  | IR573 - Basslink interrupted due to fault at Loy Yang. This report 1327 have been duplicated with the other report ID13234. G Hwaba | FALSE | Undefined
118402 | 13561 | 1327 |  |  | 2008-08-14 23:12 | 2008-08-14 23:12 | 0 | E1621 | RI 110 kV Bus SPS | Bus | Fault | Basslink | Basslink | Completed | TRUE | 924 | TRUE |  | IR573 - Basslink interrupted due to fault at Loy Yang. This report 1327 have been duplicated with the other report ID13234. G Hwaba | FALSE | Undefined
91451 | 13562 | 1333 |  |  | 2008-08-26 14:56 | 2008-08-26 17:27 | 151 | E0721 | QT-NT 110 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 596 | TRUE |  | IR570 - Supply at Newton Substation interrupted due to failure of a generation asset. | FALSE | Non-Critical
91452 | 13562 | 1333 |  |  | 2008-08-26 17:47 | 2008-08-26 18:28 | 41 | E0721 | QT-NT 110 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR570 - Supply at Newton Substation interrupted due to failure of a generation asset. | FALSE | Non-Critical
91467 | 13584 | 7107 |  |  | 2008-09-05 05:33 | 2008-09-05 05:33 | 0 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91468 | 13585 | 7106 |  |  | 2008-09-01 14:38 | 2008-09-01 14:55 | 17 | E1505 | TB 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91469 | 13586 | 7105 |  |  | 2008-09-01 10:46 | 2008-09-01 10:46 | 0 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91470 | 13587 | 7104 |  |  | 2008-08-29 06:05 | 2008-08-29 06:35 | 30 | E0343 | LF 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91471 | 13588 | 7103 |  |  | 2008-08-27 22:20 | 2008-08-27 22:20 | 0 | E0789 | QT 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91472 | 13590 | 7125 |  |  | 2008-09-15 16:29 | 2008-09-15 18:41 | 132 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91473 | 13591 | 7124 |  |  | 2008-09-15 14:10 | 2008-09-15 15:44 | 94 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91474 | 13592 | 7123 |  |  | 2008-09-15 15:12 | 2008-09-15 15:12 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91475 | 13594 | 7121 |  |  | 2008-09-14 13:02 | 2008-09-14 13:02 | 0 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91476 | 13595 | 7120 |  |  | 2008-09-14 12:52 | 2008-09-14 12:52 | 0 | E0970 | SO 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91477 | 13596 | 7119 |  |  | 2008-09-14 11:52 | 2008-09-14 12:36 | 44 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91478 | 13597 | 7118 |  |  | 2008-09-14 08:40 | 2008-09-14 08:40 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91479 | 13598 | 7117 |  |  | 2008-09-12 13:52 | 2008-09-12 13:58 | 6 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91480 | 13599 | 7116 |  |  | 2008-09-12 09:05 | 2008-09-12 11:28 | 143 | E0496 | GT 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91481 | 13600 | 7115 |  |  | 2008-09-12 07:19 | 2008-09-12 09:34 | 135 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91482 | 13601 | 7114 |  |  | 2008-09-12 09:31 | 2008-09-12 09:31 | 0 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91483 | 13602 | 7113 |  |  | 2008-09-12 05:51 | 2008-09-12 05:51 | 0 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91484 | 13603 | 7112 |  |  | 2008-09-10 03:03 | 2008-09-10 04:04 | 61 | E0738 | NH 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91485 | 13604 | 7111 |  |  | 2008-09-10 02:46 | 2008-09-10 02:46 | 0 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91486 | 13605 | 7110 |  |  | 2008-09-08 05:21 | 2008-09-08 05:21 | 0 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91487 | 13606 | 7109 |  |  | 2008-09-07 13:06 | 2008-09-07 13:24 | 18 | E1505 | TB 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91488 | 13607 | 7108 |  |  | 2008-09-07 09:27 | 2008-09-07 09:57 | 30 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91489 | 13609 | 1364 |  |  | 2008-09-16 06:19 | 2008-09-16 06:25 | 6 | E0938 | UL 110/22 kV T1 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 89 | TRUE |  | IR571 - Ulverstone Substation supply interrupted due to wiring error in HV capacitor bank controller. not in ITOMS, cause was 22kV cap bank wiring | FALSE | Non-Critical
91490 | 13609 | 1364 |  |  | 2008-09-16 06:19 | 2008-09-16 06:26 | 7 | E0939 | UL 110/22 kV T2 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR571 - Ulverstone Substation supply interrupted due to wiring error in HV capacitor bank controller. not in ITOMS, cause was 22kV cap bank wiring | FALSE | Non-Critical
91491 | 13610 | 1365 |  |  | 2008-09-17 08:56 | 2008-09-17 08:56 | 0 | E0772 | PL-ST 110 kV Transmission Circuit | Transmission | Fault | Wildlife | Transend | Completed | TRUE | 0 | TRUE |  | IR572 - Port Latta-Smithton 110 kV transmission circuit interrupted due to bird streamer at tower T208. | FALSE | Non-Critical
91496 | 13615 | 7147 |  |  | 2008-09-26 02:59 | 2008-09-26 02:59 | 0 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91497 | 13616 | 7148 |  |  | 2008-09-26 07:15 | 2008-09-26 07:15 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91498 | 13617 | 7127 |  |  | 2008-09-17 16:25 | 2008-09-17 16:25 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91499 | 13618 | 7128 |  |  | 2008-09-17 18:20 | 2008-09-17 18:20 | 0 | E0303 | AV 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91500 | 13619 | 7129 |  |  | 2008-09-17 20:39 | 2008-09-17 20:39 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
118570 | 13620 | 7130 |  |  | 2006-09-20 13:56 | 2006-09-20 13:56 | 0 | E1051 | SR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91502 | 13621 | 7131 |  |  | 2008-09-20 14:55 | 2008-09-20 14:55 | 0 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91503 | 13622 | 7132 |  |  | 2008-09-20 13:11 | 2008-09-20 17:23 | 252 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91504 | 13623 | 7134 |  |  | 2008-09-20 16:42 | 2008-09-20 17:49 | 67 | E0846 | RK 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91507 | 13626 | 7137 |  |  | 2008-09-20 18:53 | 2008-09-20 19:06 | 13 | E0022 | BW 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91508 | 13627 | 7138 |  |  | 2008-09-20 18:53 | 2008-09-20 19:05 | 12 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91509 | 13628 | 7140 |  |  | 2008-09-21 07:34 | 2008-09-21 07:58 | 24 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91510 | 13629 | 7141 |  |  | 2008-09-21 12:05 | 2008-09-21 13:33 | 88 | E0463 | KR 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91511 | 13630 | 7142 |  |  | 2008-09-21 13:41 | 2008-09-21 14:25 | 44 | E0463 | KR 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91512 | 13631 | 7143 |  |  | 2008-09-21 19:51 | 2008-09-21 21:31 | 100 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91513 | 13632 | 7144 |  |  | 2008-09-21 22:59 | 2008-09-21 22:59 | 0 | E1505 | TB 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91514 | 13633 | 7145 |  |  | 2008-09-22 03:28 | 2008-09-22 03:44 | 16 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91515 | 13634 | 7146 |  |  | 2008-09-23 18:25 | 2008-09-23 18:25 | 0 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91516 | 13635 | 7149 |  |  | 2008-09-26 07:15 | 2008-09-26 07:34 | 19 | E1557 | CR 33 kV Z2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139343 | 13637 | 1367 |  |  | 2008-09-26 07:09 | 2008-09-26 07:09 | 0 | E0972 | CS-KI-EL 110 kV Transmission Circuit (Changed to E1956) | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR576 - Chapet Street-Kingston-Electrona 110 kV transmission circuit interrupted during wind storms. | FALSE | Non-Critical
91595 | 13735 | 7150 |  |  | 2008-09-26 07:36 | 2008-09-26 09:17 | 101 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91596 | 13736 | 7151 |  |  | 2008-09-28 06:51 | 2008-09-28 06:52 | 1 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139347 | 13737 | 7152 |  |  | 2008-09-28 15:39 | 2008-09-28 15:40 | 1 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91598 | 13738 | 7153 |  |  | 2008-09-28 21:05 | 2008-09-28 21:05 | 0 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91599 | 13739 | 7154 |  |  | 2008-10-02 20:54 | 2008-10-02 20:54 | 0 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91600 | 13740 | 7155 |  |  | 2008-10-03 22:31 | 2008-10-03 22:31 | 0 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91601 | 13741 | 7156 |  |  | 2008-10-04 13:41 | 2008-10-04 13:41 | 0 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91602 | 13742 | 7157 |  |  | 2008-10-05 08:46 | 2008-10-05 08:46 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91603 | 13744 | 7159 |  |  | 2008-10-06 00:39 | 2008-10-06 00:39 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91604 | 13745 | 7160 |  |  | 2008-10-06 00:42 | 2008-10-06 01:11 | 29 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91618 | 13761 | 7166 |  |  | 2008-10-12 06:44 | 2008-10-12 06:44 | 0 | E0768 | NW 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91619 | 13762 | 7165 |  |  | 2008-10-08 11:28 | 2008-10-08 11:37 | 9 | E0075 | CR 33 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91620 | 13763 | 7164 |  |  | 2008-10-07 16:31 | 2008-10-07 16:31 | 0 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91621 | 13764 | 7163 |  |  | 2008-10-07 01:29 | 2008-10-07 01:29 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91622 | 13765 | 7162 |  |  | 2008-10-07 01:10 | 2008-10-07 01:10 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91623 | 13766 | 7161 |  |  | 2008-10-06 10:22 | 2008-10-06 10:23 | 1 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91624 | 13767 | 7175 |  |  | 2008-10-26 19:04 | 2008-10-26 19:05 | 1 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91625 | 13768 | 7174 |  |  | 2008-10-20 08:44 | 2008-10-20 08:53 | 9 | E0567 | EB 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91626 | 13769 | 7167 |  |  | 2008-10-15 02:05 | 2008-10-15 02:05 | 0 | E0461 | KR 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91627 | 13770 | 7168 |  |  | 2008-10-16 11:51 | 2008-10-16 12:19 | 28 | E0970 | SO 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91628 | 13771 | 7169 |  |  | 2008-10-16 11:51 | 2008-10-16 12:18 | 27 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91629 | 13772 | 7170 |  |  | 2008-10-16 19:50 | 2008-10-16 19:50 | 0 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91630 | 13773 | 7171 |  |  | 2008-10-18 21:48 | 2008-10-18 21:48 | 0 | E1530 | MY 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91631 | 13774 | 7172 |  |  | 2008-10-19 08:26 | 2008-10-19 08:26 | 0 | E0768 | NW 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91632 | 13775 | 1373 |  |  | 2008-10-30 11:55 | 2008-10-30 12:10 | 15 | E0384 | BU 22 kV A Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 294 | TRUE |  | IR588 - Burnie Substation 22 kV Bus A interruption during commissioning of new protection panel. | FALSE | Undefined
91633 | 13776 | 7178 |  |  | 2008-11-03 03:27 | 2008-11-03 03:27 | 0 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91634 | 13777 | 7177 |  |  | 2008-10-30 15:37 | 2008-10-30 15:37 | 0 | E1555 | DP 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92227 | 16462 | 7188 |  |  | 2008-11-16 06:01 | 2008-11-16 06:01 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92228 | 16463 | 7185 |  |  | 2008-11-15 14:41 | 2008-11-15 19:47 | 306 | E0158 | MB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92229 | 16464 | 7184 |  |  | 2008-11-13 21:32 | 2008-11-13 21:32 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92230 | 16465 | 7183 |  |  | 2008-11-11 06:29 | 2008-11-11 07:56 | 87 | E0870 | RB 44 kV B2 Circuit Breaker | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92231 | 16466 | 7182 |  |  | 2008-11-10 23:11 | 2008-11-10 23:28 | 17 | E0870 | RB 44 kV B2 Circuit Breaker | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92232 | 16467 | 7181 |  |  | 2008-11-09 06:17 | 2008-11-09 06:37 | 20 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92233 | 16468 | 7180 |  |  | 2008-11-08 08:35 | 2008-11-08 09:26 | 51 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92234 | 16469 | 7179 |  |  | 2008-11-07 01:40 | 2008-11-07 01:59 | 19 | E0119 | CS 11 kV U2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92235 | 16470 | 6903 |  |  | 2008-05-05 15:27 | 2008-05-05 15:27 | 0 | E0014 | BW 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92236 | 16471 | 7202 |  |  | 2008-11-23 08:54 | 2008-11-23 10:07 | 73 | E0081 | CR 33 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92237 | 16472 | 7201 |  |  | 2008-11-23 07:20 | 2008-11-23 07:20 | 0 | E1444 | HA 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92238 | 16473 | 7199 |  |  | 2008-11-22 20:25 | 2008-11-23 00:41 | 256 | E0491 | GT 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139369 | 16474 | 7198 |  |  | 2008-11-22 12:58 | 2008-11-22 12:58 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92240 | 16475 | 7197 |  |  | 2008-11-21 21:06 | 2008-11-21 21:25 | 19 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92241 | 16476 | 7196 |  |  | 2008-11-21 14:29 | 2008-11-21 14:29 | 0 | E0158 | MB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92242 | 16477 | 7189 |  |  | 2008-11-19 01:58 | 2008-11-19 01:58 | 0 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92243 | 16478 | 7190 |  |  | 2008-11-19 01:58 | 2008-11-19 02:20 | 22 | E0766 | NW 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92244 | 16479 | 7191 |  |  | 2008-11-19 10:13 | 2008-11-19 10:13 | 0 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92245 | 16480 | 7192 |  |  | 2008-11-19 19:13 | 2008-11-19 19:14 | 1 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92246 | 16481 | 7193 |  |  | 2008-11-20 00:54 | 2008-11-20 00:54 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92247 | 16482 | 7194 |  |  | 2008-11-20 03:03 | 2008-11-20 03:03 | 0 | E1554 | DP 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92248 | 16483 | 7195 |  |  | 2008-11-20 08:22 | 2008-11-20 08:42 | 20 | E0389 | BU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92249 | 16484 | 1378 |  |  | 2008-11-27 11:20 | 2008-11-27 11:22 | 2 | E0139 | TA-NN 2 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR597 - Tarraleah-New Norfolk No 2 110 kV transmission circuit interruption due to lightning. | FALSE | Critical
118414 | 16485 | 1379 |  |  | 2008-11-27 16:19 | 2008-11-27 16:41 | 22 | E1621 | RI 110 kV Bus SPS | Bus | Fault | Basslink | Basslink | Completed | TRUE | 44 | TRUE |  | IR600 - Basslink FCSPS operation causing load shedding. Basslink advised trip was caused by a DC line fault. Suspected a lightning strike at Loy Yang. | FALSE | Undefined
92255 | 16486 | 1381 |  |  | 2008-12-02 07:04 | 2008-12-02 07:11 | 7 | E0270 | PM-HA 3 110 kV Transmission Circuit | Transmission | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR601 - Palmerston-Hadspen No 3 110 kV transmission circuit interrupted for four times over a three days period. The total minutes non available for the circuit are 97 minutes. Cause due to faulty relay intertrip input card. | FALSE | Critical
92256 | 16486 | 1381 |  |  | 2008-12-02 11:24 | 2008-12-02 11:29 | 5 | E0270 | PM-HA 3 110 kV Transmission Circuit | Transmission | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR601 - Palmerston-Hadspen No 3 110 kV transmission circuit interrupted for four times over a three days period. The total minutes non available for the circuit are 97 minutes. Cause due to faulty relay intertrip input card. | FALSE | Critical
92253 | 16486 | 1381 |  |  | 2008-11-30 07:02 | 2008-11-30 07:07 | 5 | E0270 | PM-HA 3 110 kV Transmission Circuit | Transmission | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR601 - Palmerston-Hadspen No 3 110 kV transmission circuit interrupted for four times over a three days period. The total minutes non available for the circuit are 97 minutes. Cause due to faulty relay intertrip input card. | FALSE | Critical
92254 | 16486 | 1381 |  |  | 2008-12-01 01:38 | 2008-12-01 02:58 | 80 | E0270 | PM-HA 3 110 kV Transmission Circuit | Transmission | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR601 - Palmerston-Hadspen No 3 110 kV transmission circuit interrupted for four times over a three days period. The total minutes non available for the circuit are 97 minutes. Cause due to faulty relay intertrip input card. | FALSE | Critical
92257 | 16487 | 7214 |  |  | 2008-12-01 04:10 | 2008-12-01 04:10 | 0 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92258 | 16488 | 7212 |  |  | 2008-11-28 21:51 | 2008-11-28 23:41 | 110 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92259 | 16489 | 7211 |  |  | 2008-11-28 21:50 | 2008-11-28 21:51 | 1 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92260 | 16490 | 7210 |  |  | 2008-11-28 21:48 | 2008-11-28 21:48 | 0 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139370 | 16491 | 7203 |  |  | 2008-11-24 23:38 | 2008-11-24 23:38 | 0 | E1567 | DP 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139371 | 16492 | 7204 |  |  | 2008-11-25 02:55 | 2008-11-25 02:55 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92263 | 16493 | 7205 |  |  | 2008-11-26 09:22 | 2008-11-26 10:03 | 41 | E0494 | GT 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92264 | 16494 | 7206 |  |  | 2008-11-26 14:26 | 2008-11-26 14:46 | 20 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92265 | 16495 | 7207 |  |  | 2008-11-26 23:07 | 2008-11-26 23:07 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92266 | 16496 | 7208 |  |  | 2008-11-27 00:09 | 2008-11-27 00:09 | 0 | E0655 | SM 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92267 | 16497 | 7209 |  |  | 2008-11-27 04:10 | 2008-11-27 04:10 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92268 | 16498 | 7217 |  |  | 2008-12-02 02:22 | 2008-12-02 02:22 | 0 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92269 | 16499 | 7215 |  |  | 2008-12-01 15:07 | 2008-12-01 17:45 | 158 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92394 | 16655 | 7222 |  |  | 2008-12-04 22:04 | 2008-12-05 01:28 | 204 | E0820 | RA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92395 | 16657 | 7220 |  |  | 2008-12-02 22:53 | 2008-12-02 22:53 | 0 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92396 | 16659 | 1387 |  |  | 2008-12-08 05:16 | 2008-12-08 14:20 | 544 | E0267 | PO-PM 5 220 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR608 - Poatina-Palmerston No. 5 220 kV transmission circuit interrupted. Intertrip signals were received from Poatina Power Station. The line was tripped twice on 8 December 2008. Under investigation. | FALSE | Non-Critical
92397 | 16659 | 1387 |  |  | 2008-12-08 19:01 | 2008-12-09 15:07 | 1206 | E0267 | PO-PM 5 220 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR608 - Poatina-Palmerston No. 5 220 kV transmission circuit interrupted. Intertrip signals were received from Poatina Power Station. The line was tripped twice on 8 December 2008. Under investigation. | FALSE | Non-Critical
139376 | 16660 | 7230 |  |  | 2008-12-14 01:43 | 2008-12-14 01:43 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92399 | 16661 | 7229 |  |  | 2008-12-13 15:28 | 2008-12-13 15:29 | 1 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92400 | 16662 | 7227 |  |  | 2008-12-10 06:07 | 2008-12-10 06:07 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92401 | 16663 | 7226 |  |  | 2008-12-08 01:58 | 2008-12-08 02:31 | 33 | E0496 | GT 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185953 | 16664 | 7225 |  |  | 2008-12-06 21:55 | 2008-12-07 04:00 | 365 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92403 | 16665 | 7224 |  |  | 2008-12-05 20:56 | 2008-12-05 21:28 | 32 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92404 | 16666 | 7258 |  |  | 2009-01-03 20:51 | 2009-01-03 21:14 | 23 | E0078 | CR 33 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92405 | 16667 | 7257 |  |  | 2008-12-31 15:51 | 2008-12-31 15:52 | 1 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92406 | 16668 | 7256 |  |  | 2008-12-30 17:52 | 2008-12-30 18:05 | 13 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92407 | 16669 | 7255 |  |  | 2008-12-30 12:57 | 2008-12-30 12:57 | 0 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92408 | 16670 | 7254 |  |  | 2008-12-29 07:06 | 2008-12-29 07:06 | 0 | E0643 | ST 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92409 | 16671 | 7253 |  |  | 2008-12-28 01:23 | 2008-12-28 01:23 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92410 | 16672 | 7252 |  |  | 2008-12-26 05:07 | 2008-12-26 05:07 | 0 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92411 | 16673 | 7251 |  |  | 2008-12-24 23:54 | 2008-12-25 01:34 | 100 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92412 | 16674 | 7250 |  |  | 2008-12-24 09:57 | 2008-12-24 09:57 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92413 | 16675 | 7249 |  |  | 2008-12-23 22:39 | 2008-12-23 22:39 | 0 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92414 | 16676 | 7248 |  |  | 2008-12-22 22:42 | 2008-12-22 22:58 | 16 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92415 | 16677 | 7245 |  |  | 2008-12-22 19:58 | 2008-12-22 22:16 | 138 | E1051 | SR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92416 | 16678 | 7244 |  |  | 2008-12-22 17:03 | 2008-12-22 17:03 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92417 | 16679 | 7243 |  |  | 2008-12-22 17:03 | 2008-12-22 17:03 | 0 | E0022 | BW 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92418 | 16680 | 7242 |  |  | 2008-12-22 14:04 | 2008-12-22 22:07 | 483 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92420 | 16683 | 7240 |  |  | 2008-12-22 14:03 | 2008-12-22 14:03 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92421 | 16684 | 7239 |  |  | 2008-12-22 03:17 | 2008-12-22 03:17 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92422 | 16685 | 7238 |  |  | 2008-12-20 22:26 | 2008-12-20 23:01 | 35 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92423 | 16686 | 7237 |  |  | 2008-12-19 03:14 | 2008-12-19 03:33 | 19 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92424 | 16687 | 7236 |  |  | 2008-12-18 17:29 | 2008-12-18 17:50 | 21 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92425 | 16688 | 7235 |  |  | 2008-12-18 17:29 | 2008-12-18 17:29 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92426 | 16689 | 7234 |  |  | 2008-12-18 16:58 | 2008-12-18 17:15 | 17 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92427 | 16690 | 7232 |  |  | 2008-12-17 18:55 | 2008-12-17 18:55 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92428 | 16691 | 7231 |  |  | 2008-12-17 15:21 | 2008-12-17 15:21 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92497 | 16820 | 1383 |  |  | 2008-12-01 03:45 | 2008-12-01 04:02 | 17 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 516 | TRUE |  | IR607 - FA-RB-QT and QT-NT 110 kV transmission circuits interrupted due to lightning. | FALSE | Non-Critical
92498 | 16820 | 1383 |  |  | 2008-12-01 03:45 | 2008-12-01 04:13 | 28 | E0721 | QT-NT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR607 - FA-RB-QT and QT-NT 110 kV transmission circuits interrupted due to lightning. | FALSE | Non-Critical
92501 | 16821 | 1391 |  |  | 2008-12-20 16:39 | 2008-12-20 16:39 | 0 | E0298 | AV-SM 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR614 - PM-HA 1 & 2 220 kV and AV-SM 110 kV transmission circuits interrupted. Successful auto-reclosed in all the three circuits. Suspected due to lightning. | FALSE | Non-Critical
92499 | 16821 | 1391 |  |  | 2008-12-20 16:14 | 2008-12-20 16:14 | 0 | E0259 | PM-HA 1 220 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR614 - PM-HA 1 & 2 220 kV and AV-SM 110 kV transmission circuits interrupted. Successful auto-reclosed in all the three circuits. Suspected due to lightning. | FALSE | Critical
92500 | 16821 | 1391 |  |  | 2008-12-20 16:27 | 2008-12-20 16:27 | 0 | E0260 | PM-HA 2 220 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR614 - PM-HA 1 & 2 220 kV and AV-SM 110 kV transmission circuits interrupted. Successful auto-reclosed in all the three circuits. Suspected due to lightning. | FALSE | Critical
92502 | 16822 | 7268 |  |  | 2009-01-11 19:06 | 2009-01-11 19:06 | 0 | E0389 | BU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92503 | 16823 | 7267 |  |  | 2009-01-11 17:01 | 2009-01-11 17:20 | 19 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92504 | 16824 | 7266 |  |  | 2009-01-09 22:58 | 2009-01-09 22:58 | 0 | E0389 | BU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139379 | 16825 | 7265 |  |  | 2009-01-09 22:41 | 2009-01-09 22:41 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92506 | 16826 | 7264 |  |  | 2009-01-09 12:30 | 2009-01-09 14:16 | 106 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92507 | 16827 | 7263 |  |  | 2009-01-08 20:50 | 2009-01-08 20:59 | 9 | E0767 | NW 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92508 | 16828 | 7262 |  |  | 2009-01-08 06:19 | 2009-01-08 06:56 | 37 | E1612 | UL 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92509 | 16829 | 7261 |  |  | 2009-01-07 00:42 | 2009-01-07 00:42 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92510 | 16830 | 7260 |  |  | 2009-01-07 00:42 | 2009-01-07 00:42 | 0 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92511 | 16831 | 7259 |  |  | 2009-01-06 06:42 | 2009-01-06 06:43 | 1 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92512 | 16832 | 7273 |  |  | 2009-01-16 00:07 | 2009-01-16 00:07 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92513 | 16833 | 7272 |  |  | 2009-01-15 23:16 | 2009-01-15 23:16 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92514 | 16834 | 7271 |  |  | 2009-01-15 07:46 | 2009-01-15 07:46 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92515 | 16835 | 7270 |  |  | 2009-01-13 14:26 | 2009-01-13 14:42 | 16 | E0144 | NN 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92516 | 16836 | 7269 |  |  | 2009-01-13 14:26 | 2009-01-13 14:43 | 17 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92517 | 16837 | 7279 |  |  | 2009-01-18 03:20 | 2009-01-18 03:37 | 17 | E1051 | SR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92518 | 16838 | 7277 |  |  | 2009-01-17 19:13 | 2009-01-17 19:31 | 18 | E0948 | UL 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92519 | 16839 | 7276 |  |  | 2009-01-17 09:42 | 2009-01-17 09:42 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92520 | 16840 | 7275 |  |  | 2009-01-17 01:08 | 2009-01-17 01:08 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92521 | 16841 | 7274 |  |  | 2009-01-16 14:13 | 2009-01-16 14:14 | 1 | E0014 | BW 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92522 | 16842 | 7280 |  |  | 2009-01-19 11:15 | 2009-01-19 12:07 | 52 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92523 | 16843 | 7281 |  |  | 2009-01-19 17:25 | 2009-01-19 17:26 | 1 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92743 | 16929 | 7282 |  |  | 2009-01-21 15:22 | 2009-01-21 15:23 | 1 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93124 | 16930 | 7283 |  |  | 2009-01-22 08:32 | 2009-01-22 09:34 | 62 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93115 | 16931 | 7284 |  |  | 2009-01-22 11:07 | 2009-01-22 11:07 | 0 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92755 | 16932 | 7285 |  |  | 2009-01-22 10:15 | 2009-01-22 11:10 | 55 | E1557 | CR 33 kV Z2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92756 | 16933 | 7287 |  |  | 2009-01-22 11:18 | 2009-01-22 11:18 | 0 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92757 | 16934 | 7288 |  |  | 2009-01-22 11:20 | 2009-01-22 11:20 | 0 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92758 | 16935 | 7295 |  |  | 2009-01-22 10:30 | 2009-01-22 18:14 | 464 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92778 | 16937 | 7302 |  |  | 2009-01-22 11:47 | 2009-01-22 19:52 | 485 | E0354 | KI 11 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92779 | 16938 | 7303 |  |  | 2009-01-22 11:47 | 2009-01-22 17:43 | 356 | E0358 | KI 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93116 | 16939 | 7305 |  |  | 2009-01-22 11:58 | 2009-01-22 11:58 | 0 | E0300 | AV 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92783 | 16942 | 7310 |  |  | 2009-01-22 12:09 | 2009-01-22 12:09 | 0 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92784 | 16943 | 7312 |  |  | 2009-01-22 11:12 | 2009-01-22 11:12 | 0 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92785 | 16944 | 7313 |  |  | 2009-01-22 12:17 | 2009-01-22 12:17 | 0 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92786 | 16945 | 7316 |  |  | 2009-01-22 12:49 | 2009-01-22 19:42 | 413 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92788 | 16947 | 7318 |  |  | 2009-01-22 13:50 | 2009-01-22 13:50 | 0 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92790 | 16949 | 7320 |  |  | 2009-01-22 13:55 | 2009-01-22 18:53 | 298 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92794 | 16953 | 7324 |  |  | 2009-01-22 12:25 | 2009-01-22 15:10 | 165 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92795 | 16954 | 7325 |  |  | 2009-01-22 10:05 | 2009-01-22 15:44 | 339 | E0106 | CS 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93125 | 16960 | 7331 |  |  | 2009-01-22 11:59 | 2009-01-22 16:33 | 274 | E0300 | AV 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92803 | 16962 | 7336 |  |  | 2009-01-22 19:13 | 2009-01-22 19:13 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92804 | 16963 | 7339 |  |  | 2009-01-22 19:14 | 2009-01-22 20:59 | 105 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92805 | 16964 | 7340 |  |  | 2009-01-22 21:58 | 2009-01-22 22:04 | 6 | E0736 | NH 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92806 | 16965 | 7341 |  |  | 2009-01-22 21:58 | 2009-01-22 22:02 | 4 | E0735 | NH 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92858 | 16967 | 7347 |  |  | 2009-01-23 23:01 | 2009-01-23 23:28 | 27 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92859 | 16968 | 7348 |  |  | 2009-01-24 02:18 | 2009-01-24 02:36 | 18 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92860 | 16969 | 7349 |  |  | 2009-01-24 02:49 | 2009-01-24 02:49 | 0 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92861 | 16970 | 7350 |  |  | 2009-01-24 16:09 | 2009-01-24 17:21 | 72 | E0846 | RK 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92862 | 16971 | 7352 |  |  | 2009-01-25 13:18 | 2009-01-25 13:18 | 0 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92863 | 16972 | 7353 |  |  | 2009-01-26 21:08 | 2009-01-26 21:08 | 0 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139382 | 16973 | 7354 |  |  | 2009-01-26 21:24 | 2009-01-26 21:24 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92865 | 16974 | 7342 |  |  | 2009-01-22 19:13 | 2009-01-23 15:54 | 1241 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92929 | 16977 | 7356 |  |  | 2009-01-28 08:12 | 2009-01-28 08:12 | 0 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92930 | 16978 | 7358 |  |  | 2009-01-29 02:31 | 2009-01-29 03:42 | 71 | E1531 | MY 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92931 | 16979 | 7359 |  |  | 2009-01-29 05:02 | 2009-01-29 05:02 | 0 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92933 | 16981 | 7363 |  |  | 2009-01-29 13:38 | 2009-01-29 13:58 | 20 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92934 | 16982 | 7364 |  |  | 2009-01-30 04:41 | 2009-01-30 04:41 | 0 | E0970 | SO 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92935 | 16983 | 7365 |  |  | 2009-01-30 08:46 | 2009-01-30 08:46 | 0 | E1573 | DP 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92936 | 16984 | 7366 |  |  | 2009-01-30 13:27 | 2009-01-30 14:15 | 48 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92937 | 16985 | 7367 |  |  | 2009-01-30 16:52 | 2009-01-30 16:52 | 0 | E0869 | RB 44 kV E4 Circuit Breaker | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92938 | 16986 | 7368 |  |  | 2009-01-30 16:05 | 2009-01-30 17:10 | 65 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92939 | 16987 | 7369 |  |  | 2009-01-30 17:19 | 2009-01-30 17:19 | 0 | E0869 | RB 44 kV E4 Circuit Breaker | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
92940 | 16988 | 7370 |  |  | 2009-01-30 20:53 | 2009-01-30 20:53 | 0 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93029 | 16989 | 7372 |  |  | 2009-01-31 06:58 | 2009-01-31 07:02 | 4 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93030 | 16990 | 7371 |  |  | 2009-01-31 06:36 | 2009-01-31 06:36 | 0 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93031 | 16991 | 7373 |  |  | 2009-01-31 16:49 | 2009-01-31 16:49 | 0 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93032 | 16992 | 7374 |  |  | 2009-01-31 17:04 | 2009-01-31 18:27 | 83 | E0655 | SM 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93100 | 17059 | 1394 |  |  | 2009-01-13 02:26 | 2009-01-13 14:41 | 735 | E0134 | NN 22 kV A Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 77 | TRUE |  | IR616 NN 22kV A Bus tripped during protection testing | FALSE | Undefined
93101 | 17060 | 1395 |  |  | 2009-01-22 13:59 | 2009-01-22 14:14 | 15 | E1614 | KR-HR-KE 110 kV Transmission Circuit | Transmission | Fault | Pending Investigation | Transend | Completed | TRUE | 88 | TRUE |  | IR621 KR-HR-KE 110kV transmission circuit tripped during strong winds. Cause is under investigation. nit in ITOMS as cause unknown. | FALSE | Non-Critical
93150 | 17061 | 1397 |  |  | 2009-01-22 21:03 | 2009-01-22 21:20 | 17 | E1614 | KR-HR-KE 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 114 | TRUE |  | IR621 KR-HR-KE 110kV transmission circuit tripped during strong winds. Cause is under investigation. not in ITOMs as cause unknown. | FALSE | Non-Critical
93151 | 17061 | 1397 |  |  | 2009-01-22 21:31 | 2009-01-22 21:48 | 17 | E1614 | KR-HR-KE 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR621 KR-HR-KE 110kV transmission circuit tripped during strong winds. Cause is under investigation. not in ITOMs as cause unknown. | FALSE | Non-Critical
93117 | 17063 | 1396 |  |  | 2009-01-22 17:36 | 2009-01-22 19:09 | 93 | E0730 | NH 11 kV B Bus | Bus | Fault | Poor Construction | Transend | Completed | TRUE | 0 | TRUE |  | IR619 - NH 11kV A and B Busses tripped tripped when frame leakage protection operated. Cause under investigation. | FALSE | Undefined
93104 | 17063 | 1396 |  |  | 2009-01-22 17:36 | 2009-01-22 19:14 | 98 | E0728 | NH 11 kV A Bus | Bus | Fault | Poor Construction | Transend | Completed | TRUE | 1015 | TRUE |  | IR619 - NH 11kV A and B Busses tripped tripped when frame leakage protection operated. Cause under investigation. | FALSE | Undefined
93107 | 17064 | 1400 |  |  | 2009-01-30 12:41 | 2009-01-30 14:55 | 134 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Basslink | Completed | TRUE | 0 | TRUE |  | IR622 Basslink trips due to high ambient temperature | FALSE | Undefined
93106 | 17064 | 1400 |  |  | 2009-01-29 14:03 | 2009-01-29 14:55 | 52 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Basslink | Completed | TRUE | 0 | TRUE |  | IR622 Basslink trips due to high ambient temperature | FALSE | Undefined
93182 | 17065 | 7375 |  |  | 2009-02-01 05:27 | 2009-02-01 05:27 | 0 | E1554 | DP 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93195 | 17066 | 7376 |  |  | 2009-02-01 07:34 | 2009-02-01 08:02 | 28 | E1478 | RI 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93197 | 17068 | 7379 |  |  | 2009-02-01 23:37 | 2009-02-01 23:37 | 0 | E0768 | NW 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93198 | 17069 | 7380 |  |  | 2009-02-02 23:39 | 2009-02-02 23:39 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93199 | 17070 | 7381 |  |  | 2009-02-02 21:38 | 2009-02-03 00:10 | 152 | E0909 | TR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93200 | 17071 | 7382 |  |  | 2009-02-03 23:56 | 2009-02-04 00:45 | 49 | E0111 | CS 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93201 | 17072 | 7383 |  |  | 2009-02-04 14:20 | 2009-02-04 14:21 | 1 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93202 | 17073 | 7384 |  |  | 2009-02-06 18:21 | 2009-02-07 02:16 | 475 | E1454 | HA 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93203 | 17074 | 7385 |  |  | 2009-02-06 21:39 | 2009-02-06 21:59 | 20 | E0496 | GT 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96032 | 17075 | 7387 |  |  | 2009-02-09 22:18 | 2009-02-09 22:18 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95091 | 17076 | 7388 |  |  | 2009-02-09 22:40 | 2009-02-09 22:41 | 1 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95092 | 17077 | 7389 |  |  | 2009-02-10 10:13 | 2009-02-10 10:13 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95093 | 17078 | 7390 |  |  | 2009-02-10 10:35 | 2009-02-10 11:11 | 36 | E0364 | KI 11 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95094 | 17079 | 7391 |  |  | 2009-02-12 07:42 | 2009-02-12 07:42 | 0 | E1555 | DP 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95095 | 17080 | 7392 |  |  | 2009-02-13 23:35 | 2009-02-13 23:35 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95096 | 17081 | 7393 |  |  | 2009-02-14 11:21 | 2009-02-14 11:53 | 32 | E1505 | TB 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95097 | 17082 | 7394 |  |  | 2009-02-15 03:04 | 2009-02-15 03:05 | 1 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95098 | 17083 | 7395 |  |  | 2009-02-15 22:22 | 2009-02-15 22:22 | 0 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95099 | 17084 | 7233 |  |  | 2008-12-18 11:20 | 2008-12-19 09:49 | 1349 | E0110 | CS 11 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95108 | 17085 | 7286 |  |  | 2009-01-22 10:01 | 2009-01-22 14:25 | 264 | E0747 | NH 11 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95110 | 17087 | 7290 |  |  | 2009-01-22 10:07 | 2009-01-22 21:54 | 707 | E1479 | RI 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95111 | 17088 | 7291 |  |  | 2009-01-22 10:16 | 2009-01-22 12:04 | 108 | E0081 | CR 33 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95112 | 17089 | 7292 |  |  | 2009-01-22 10:17 | 2009-01-22 16:25 | 368 | E0105 | CS 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95113 | 17090 | 7293 |  |  | 2009-01-22 11:34 | 2009-01-22 11:34 | 0 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95114 | 17091 | 7294 |  |  | 2009-01-22 10:18 | 2009-01-22 12:03 | 105 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95115 | 17093 | 7296 |  |  | 2009-01-22 10:36 | 2009-01-22 15:51 | 315 | E0022 | BW 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95116 | 17094 | 7297 |  |  | 2009-01-22 10:42 | 2009-01-22 17:28 | 406 | E0835 | RK 11 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95117 | 17095 | 7298 |  |  | 2009-01-22 10:45 | 2009-01-22 15:49 | 304 | E0366 | KI 11 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95118 | 17096 | 7299 |  |  | 2009-01-22 11:13 | 2009-01-22 14:42 | 209 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95119 | 17097 | 7301 |  |  | 2009-01-22 11:26 | 2009-01-22 16:13 | 287 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95120 | 17098 | 7304 |  |  | 2009-01-22 11:50 | 2009-01-22 15:00 | 190 | E0844 | RK 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95121 | 17099 | 7309 |  |  | 2009-01-22 12:06 | 2009-01-22 15:32 | 206 | E0843 | RK 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95122 | 17100 | 7311 |  |  | 2009-01-22 12:10 | 2009-01-22 13:32 | 82 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95123 | 17101 | 7314 |  |  | 2009-01-22 12:25 | 2009-01-22 15:10 | 165 | E0156 | MB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95124 | 17102 | 7315 |  |  | 2009-01-22 12:38 | 2009-01-22 15:55 | 197 | E1533 | MY 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95125 | 17103 | 7360 |  |  | 2009-01-29 06:57 | 2009-01-29 07:40 | 43 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95126 | 17104 | 7377 |  |  | 2009-02-01 05:37 | 2009-02-01 10:14 | 277 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95151 | 17106 | 7397 |  |  | 2009-02-16 21:57 | 2009-02-16 21:57 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95152 | 17107 | 7398 |  |  | 2009-02-17 08:20 | 2009-02-17 08:43 | 23 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95153 | 17108 | 7399 |  |  | 2009-02-18 08:33 | 2009-02-18 08:34 | 1 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95154 | 17109 | 7401 |  |  | 2009-02-18 21:39 | 2009-02-18 21:39 | 0 | E0764 | NW 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95156 | 17111 | 7421 |  |  | 2009-02-21 00:21 | 2009-02-21 00:21 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95157 | 17112 | 7423 |  |  | 2009-02-21 05:43 | 2009-02-21 05:43 | 0 | E0970 | SO 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95158 | 17113 | 7425 |  |  | 2009-02-21 06:01 | 2009-02-21 06:25 | 24 | E1538 | MY 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95951 | 17438 | 7427 |  |  | 2009-02-23 16:38 | 2009-02-23 17:00 | 22 | E0643 | ST 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139387 | 17440 | 7429 |  |  | 2009-02-23 22:18 | 2009-02-23 22:18 | 0 | E1566 | DP 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95953 | 17441 | 7430 |  |  | 2009-02-24 00:10 | 2009-02-24 00:10 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95954 | 17442 | 7431 |  |  | 2009-02-24 00:10 | 2009-02-24 00:10 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95955 | 17443 | 7432 |  |  | 2009-02-26 04:37 | 2009-02-26 04:37 | 0 | E0820 | RA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95956 | 17444 | 7433 |  |  | 2009-02-26 04:42 | 2009-02-26 04:42 | 0 | E0820 | RA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
95957 | 17445 | 7435 |  |  | 2009-02-27 08:05 | 2009-02-27 08:33 | 28 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101898 | 17446 | 1405 |  |  | 2009-02-07 11:41 | 2009-02-07 12:03 | 22 | E0267 | PO-PM 5 220 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR623 - Poatina-Palmerston No 5 220 kV transmission circuit interrupted. Suspect overspeed protection operation on Poatine No 5 machine which intertripped Palmerston 110 kV circuit breaker B152. | FALSE | Non-Critical
101899 | 17448 | 1410 |  |  | 2009-02-12 14:36 | 2009-02-12 15:19 | 43 | E0286 | PO-PM 1 110 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR625 - Poatina-Palmerston No 1 110 kV transmission circuit interrupted. Cause under investigation. | FALSE | Non-Critical
101900 | 17472 | 1411 |  |  | 2009-02-26 19:45 | 2009-02-26 20:01 | 16 | E0286 | PO-PM 1 110 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR626 - Poatina-Palmerston No 1 110 kV transmission circuit interrupted. Cause under investigation. | FALSE | Non-Critical
96161 | 17473 | 7436 |  |  | 2009-03-01 06:20 | 2009-03-01 06:20 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96162 | 17475 | 7438 |  |  | 2009-03-01 12:00 | 2009-03-01 12:33 | 33 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96163 | 17476 | 7439 |  |  | 2009-03-01 19:32 | 2009-03-01 19:32 | 0 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96164 | 17477 | 7440 |  |  | 2009-03-02 00:18 | 2009-03-02 12:18 | 720 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96165 | 17479 | 7442 |  |  | 2009-03-03 06:08 | 2009-03-03 06:08 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96166 | 17480 | 7443 |  |  | 2009-03-03 07:52 | 2009-03-03 08:44 | 52 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96167 | 17481 | 7445 |  |  | 2009-03-03 10:03 | 2009-03-03 10:03 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96168 | 17482 | 7446 |  |  | 2009-03-03 12:38 | 2009-03-03 12:39 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96169 | 17484 | 7447 |  |  | 2009-03-03 12:44 | 2009-03-03 12:44 | 0 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96170 | 17485 | 7449 |  |  | 2009-03-03 13:12 | 2009-03-03 13:12 | 0 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96171 | 17486 | 7450 |  |  | 2009-03-03 17:39 | 2009-03-03 18:41 | 62 | E0806 | QT 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96190 | 17487 | 7451 |  |  | 2009-03-03 22:36 | 2009-03-03 22:57 | 21 | E0888 | DE 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96191 | 17488 | 7452 |  |  | 2009-03-04 06:56 | 2009-03-04 06:57 | 1 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96192 | 17489 | 7453 |  |  | 2009-03-04 14:53 | 2009-03-04 14:53 | 0 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96193 | 17490 | 7454 |  |  | 2009-03-05 01:30 | 2009-03-05 04:28 | 178 | E0494 | GT 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96194 | 17491 | 7455 |  |  | 2009-03-05 08:13 | 2009-03-05 08:39 | 26 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96195 | 17492 | 7456 |  |  | 2009-03-05 23:59 | 2009-03-06 | 1 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96196 | 17493 | 7457 |  |  | 2009-03-06 00:50 | 2009-03-06 01:16 | 26 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96197 | 17494 | 7458 |  |  | 2009-03-06 07:49 | 2009-03-06 08:06 | 17 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96198 | 17495 | 7459 |  |  | 2009-03-06 12:53 | 2009-03-06 12:54 | 1 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96199 | 17496 | 7460 |  |  | 2009-03-06 13:10 | 2009-03-06 13:10 | 0 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96200 | 17497 | 7461 |  |  | 2009-03-06 13:26 | 2009-03-06 13:45 | 19 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96201 | 17498 | 7462 |  |  | 2009-03-06 20:51 | 2009-03-06 20:51 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96202 | 17499 | 7463 |  |  | 2009-03-07 18:13 | 2009-03-07 18:13 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102135 | 17500 | 1412 |  |  | 2009-03-14 09:35 | 2009-03-14 09:35 | 0 | E0400 | BU-HM 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR628 - Burnie-Hamsphire 110 kV transmission circuit interrupted due to lightning. | FALSE | Non-Critical
96231 | 17501 | 1413 |  |  | 2009-03-14 09:38 | 2009-03-14 09:38 | 0 | E0401 | BU-PL 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR628 - Burnie-Port Latta 110 kV transmission circuit interrupted due to lightning. | FALSE | Non-Critical
96232 | 17502 | 1414 |  |  | 2009-03-14 09:38 | 2009-03-14 09:38 | 0 | E0402 | BU-ST 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR628 - Burnie-Smithton 110 kV transmission circuit interrupted due to lightning. | FALSE | Non-Critical
108419 | 17503 | 1415 |  |  | 2009-03-14 09:38 | 2009-03-14 10:14 | 36 | E1565 | BP-SB-ST 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Generator Request | Completed | TRUE | 0 | TRUE |  | IR628 - Bluff Point-Studland Bay-Smithton 110 kV transmission circuit interrupted due to lightning. | FALSE | Undefined
96234 | 17504 | 1416 |  |  | 2009-03-14 10:08 | 2009-03-14 10:11 | 3 | E0404 | SH-BU 2 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR628 - Sheffield-Burnie No 2 110 kV transmission circuit interrupted due to lightning. | FALSE | Non-Critical
96235 | 17505 | 1418 |  |  | 2009-03-14 10:08 | 2009-03-14 12:19 | 131 | E0534 | SH 220/110 kV T1 Transformer Circuit | Transformer | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR628 - Sheffield Substation supply interrupted due to lightning. | FALSE | Non-Critical
96236 | 17506 | 7464 |  |  | 2009-03-09 06:45 | 2009-03-09 07:04 | 19 | E1530 | MY 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96237 | 17507 | 1419 |  |  | 2009-03-14 10:08 | 2009-03-14 11:03 | 55 | E0587 | UL-EB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR628 - UL-EB 110 kV transmission circuit interrupted due to lightning. | FALSE | Non-Critical
96238 | 17508 | 1420 |  |  | 2009-03-14 10:29 | 2009-03-14 10:29 | 0 | E0538 | SH-FA 1 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR628 - Sheffield-Farrell No 1 220 kV transmission circuit interrupted due to lightning. | FALSE | Critical
102136 | 17508 | 1420 |  |  | 2009-03-14 10:29 | 2009-03-14 10:29 | 0 | E0539 | SH-FA 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR628 - Sheffield-Farrell No 1 220 kV transmission circuit interrupted due to lightning. | FALSE | Critical
96239 | 17509 | 7466 |  |  | 2009-03-10 20:58 | 2009-03-10 20:59 | 1 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
96240 | 17510 | 1422 |  |  | 2009-03-14 10:48 | 2009-03-14 10:52 | 4 | E0537 | SH-DP 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR628 - Sheffield-Devonport 110 kV transmission circuit interrupted due to lightning. | FALSE | Non-Critical
96241 | 17511 | 1423 |  |  | 2009-03-14 12:08 | 2009-03-14 12:13 | 5 | E0027 | LI-CL-RE-CS 1 220 kV Transmission Circuit (Changed to E1958) | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR628 - Liapootah-Cluny-Repulse-Chapel Street No 1 220 kV transmission circuit interrupted due to lightning. | FALSE | Critical
96242 | 17512 | 1424 |  |  | 2009-03-14 13:31 | 2009-03-14 13:31 | 0 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR628 Lindisfarne-Sorell-Triabunna 110 kV transmission circuit interrupted due to lightning. | FALSE | Non-Critical
101295 | 17513 | 7467 |  |  | 2009-03-10 21:39 | 2009-03-10 21:40 | 1 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101296 | 17515 | 7470 |  |  | 2009-03-14 09:38 | 2009-03-14 10:02 | 24 | E0638 | ST 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101297 | 17516 | 7471 |  |  | 2009-03-14 09:38 | 2009-03-14 10:01 | 23 | E0640 | ST 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101298 | 17517 | 7472 |  |  | 2009-03-14 09:38 | 2009-03-14 10:05 | 27 | E0779 | PL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101299 | 17518 | 7473 |  |  | 2009-03-14 09:38 | 2009-03-14 10:05 | 27 | E1518 | PL 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101300 | 17519 | 7474 |  |  | 2009-03-14 09:41 | 2009-03-14 10:04 | 23 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101301 | 17520 | 7475 |  |  | 2009-03-14 10:12 | 2009-03-14 10:12 | 0 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101302 | 17522 | 7476 |  |  | 2009-03-14 10:28 | 2009-03-14 10:28 | 0 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102137 | 17523 | 1425 |  |  | 2009-03-17 14:28 | 2009-03-17 14:38 | 10 | E0286 | PO-PM 1 110 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR629 - Poatina-Palmerston No 1 110 kV transmission circuit interrupted. Transline tripped twice by Operation of Generator emergency stop push button. | FALSE | Non-Critical
102138 | 17523 | 1425 |  |  | 2009-03-17 14:49 | 2009-03-17 14:53 | 4 | E0286 | PO-PM 1 110 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR629 - Poatina-Palmerston No 1 110 kV transmission circuit interrupted. Transline tripped twice by Operation of Generator emergency stop push button. | FALSE | Non-Critical
101455 | 17524 | 7477 |  |  | 2009-03-14 11:20 | 2009-03-14 11:46 | 26 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault | Unknown | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101456 | 17525 | 7478 |  |  | 2009-03-14 11:32 | 2009-03-14 11:47 | 15 | E0909 | TR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101457 | 17526 | 7479 |  |  | 2009-03-14 11:34 | 2009-03-14 11:48 | 14 | E1535 | MY 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101458 | 17527 | 7480 |  |  | 2009-03-14 13:19 | 2009-03-14 13:20 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101459 | 17528 | 7481 |  |  | 2009-03-14 13:41 | 2009-03-14 13:57 | 16 | E0842 | RK 11 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101460 | 17529 | 7483 |  |  | 2009-03-14 10:44 | 2009-03-14 10:44 | 0 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101599 | 17530 | 1427 |  |  | 2009-03-19 13:53 | 2009-03-19 14:17 | 24 | E0322 | BY 6.6 kV D3 Feeder Circuit | Feeder | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR630 - Boyer Substation supply interrupted due to human error during protection testing. Human error during protection testing | FALSE | Undefined
101600 | 17530 | 1427 |  |  | 2009-03-19 13:53 | 2009-03-19 14:16 | 23 | E0329 | BY 6.6 kV H3 Feeder Circuit | Feeder | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR630 - Boyer Substation supply interrupted due to human error during protection testing. Human error during protection testing | FALSE | Undefined
101765 | 17531 | 7486 |  |  | 2009-03-16 15:01 | 2009-03-16 15:01 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101766 | 17532 | 7487 |  |  | 2009-03-18 11:39 | 2009-03-18 11:39 | 0 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139390 | 17533 | 7488 |  |  | 2009-03-18 22:57 | 2009-03-18 22:57 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101768 | 17534 | 7489 |  |  | 2009-03-23 05:27 | 2009-03-23 05:27 | 0 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101769 | 17535 | 7490 |  |  | 2009-03-24 22:34 | 2009-03-24 23:29 | 55 | E0767 | NW 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101770 | 17536 | 7491 |  |  | 2009-03-25 18:28 | 2009-03-25 18:28 | 0 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
101771 | 17537 | 7492 |  |  | 2009-03-26 14:12 | 2009-03-26 16:45 | 153 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
103200 | 17727 | 7493 |  |  | 2009-03-28 22:57 | 2009-03-28 22:57 | 0 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102571 | 17728 | 7494 |  |  | 2009-03-29 14:46 | 2009-03-29 14:47 | 1 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139393 | 17729 | 7495 |  |  | 2009-03-29 17:47 | 2009-03-29 17:47 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102573 | 17730 | 7496 |  |  | 2009-04-01 12:57 | 2009-04-01 14:12 | 75 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102574 | 17731 | 7497 |  |  | 2009-04-03 00:13 | 2009-04-03 00:14 | 1 | E1548 | DP 22 kV C2 Capacitor Circuit | Capacitor | Fault |  | DNSP | Completed | FALSE | 0 | TRUE |  |  | FALSE | Undefined
102575 | 17732 | 7498 |  |  | 2009-04-03 10:00 | 2009-04-03 10:00 | 0 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102576 | 17733 | 7499 |  |  | 2009-04-03 12:27 | 2009-04-03 12:42 | 15 | E0491 | GT 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102577 | 17734 | 7500 |  |  | 2009-04-04 20:41 | 2009-04-04 20:41 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102578 | 17735 | 7501 |  |  | 2009-04-05 13:09 | 2009-04-05 13:09 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102579 | 17736 | 7502 |  |  | 2009-04-05 15:20 | 2009-04-05 15:20 | 0 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102701 | 17774 | 7503 |  |  | 2009-04-06 22:25 | 2009-04-06 22:25 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102702 | 17775 | 7504 |  |  | 2009-04-07 23:32 | 2009-04-07 23:32 | 0 | E0158 | MB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102703 | 17776 | 7505 |  |  | 2009-04-08 04:58 | 2009-04-08 04:58 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102704 | 17777 | 7507 |  |  | 2009-04-11 07:28 | 2009-04-11 07:28 | 0 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102705 | 17778 | 7508 |  |  | 2009-04-11 07:28 | 2009-04-11 07:28 | 0 | E1001 | BU 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139394 | 17779 | 7510 |  |  | 2009-04-12 00:57 | 2009-04-12 12:57 | 720 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102707 | 17780 | 7511 |  |  | 2009-04-12 07:12 | 2009-04-12 07:34 | 22 | E1557 | CR 33 kV Z2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102708 | 17781 | 7512 |  |  | 2009-04-14 06:11 | 2009-04-14 06:11 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102709 | 17782 | 7513 |  |  | 2009-04-15 05:56 | 2009-04-15 06:20 | 24 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102710 | 17783 | 7514 |  |  | 2009-04-15 06:28 | 2009-04-15 06:28 | 0 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102711 | 17784 | 7515 |  |  | 2009-04-15 06:32 | 2009-04-15 06:32 | 0 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102712 | 17786 | 7516 |  |  | 2009-04-15 06:35 | 2009-04-15 06:35 | 0 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102713 | 17787 | 7517 |  |  | 2009-04-15 06:41 | 2009-04-15 06:42 | 1 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102714 | 17788 | 7518 |  |  | 2009-04-15 06:45 | 2009-04-15 06:45 | 0 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102715 | 17789 | 7519 |  |  | 2009-04-15 07:00 | 2009-04-15 07:00 | 0 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102716 | 17790 | 7520 |  |  | 2009-04-15 07:14 | 2009-04-15 07:14 | 0 | E0820 | RA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102717 | 17791 | 7521 |  |  | 2009-04-15 07:25 | 2009-04-15 07:25 | 0 | E0826 | RA 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102718 | 17792 | 7522 |  |  | 2009-04-15 07:56 | 2009-04-15 07:56 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102719 | 17793 | 7524 |  |  | 2009-04-15 08:15 | 2009-04-15 08:15 | 0 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102720 | 17794 | 7526 |  |  | 2009-04-15 08:21 | 2009-04-15 08:21 | 0 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102721 | 17795 | 7529 |  |  | 2009-04-15 07:59 | 2009-04-15 07:59 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102722 | 17796 | 7530 |  |  | 2009-04-15 08:37 | 2009-04-15 08:37 | 0 | E1529 | MY 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104883 | 17797 | 7531 |  |  | 2009-04-15 06:59 | 2009-04-15 06:59 | 0 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102724 | 17798 | 7532 |  |  | 2009-04-15 08:00 | 2009-04-15 08:00 | 0 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102725 | 17799 | 7533 |  |  | 2009-04-15 08:03 | 2009-04-15 08:03 | 0 | E0764 | NW 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102726 | 17800 | 7534 |  |  | 2009-04-15 08:05 | 2009-04-15 08:05 | 0 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102727 | 17801 | 7535 |  |  | 2009-04-15 08:10 | 2009-04-15 08:10 | 0 | E0766 | NW 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102728 | 17802 | 7536 |  |  | 2009-04-15 08:11 | 2009-04-15 08:11 | 0 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102729 | 17804 | 7537 |  |  | 2009-04-15 08:00 | 2009-04-15 08:24 | 24 | E0909 | TR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102730 | 17805 | 7538 |  |  | 2009-04-15 08:00 | 2009-04-15 08:23 | 23 | E1529 | MY 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102731 | 17806 | 7539 |  |  | 2009-04-15 06:36 | 2009-04-15 09:04 | 148 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102732 | 17807 | 7540 |  |  | 2009-04-15 09:07 | 2009-04-15 09:08 | 1 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102774 | 17808 | 7541 |  |  | 2009-04-15 08:36 | 2009-04-15 09:11 | 35 | E0909 | TR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102775 | 17809 | 7542 |  |  | 2009-04-15 08:06 | 2009-04-15 09:21 | 75 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102776 | 17810 | 7543 |  |  | 2009-04-15 07:02 | 2009-04-15 09:55 | 173 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102777 | 17811 | 7544 |  |  | 2009-04-15 06:42 | 2009-04-15 10:05 | 203 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102778 | 17812 | 7545 |  |  | 2009-04-15 08:06 | 2009-04-15 10:11 | 125 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102779 | 17813 | 7546 |  |  | 2009-04-15 08:05 | 2009-04-15 10:17 | 132 | E0760 | NW 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102780 | 17814 | 7547 |  |  | 2009-04-15 07:00 | 2009-04-15 16:48 | 588 | E0944 | UL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102781 | 17815 | 7548 |  |  | 2009-04-15 07:00 | 2009-04-15 11:30 | 270 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102782 | 17816 | 7549 |  |  | 2009-04-15 10:11 | 2009-04-15 11:02 | 51 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102783 | 17817 | 7550 |  |  | 2009-04-15 07:25 | 2009-04-15 17:25 | 600 | E0820 | RA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102784 | 17818 | 7552 |  |  | 2009-04-15 09:16 | 2009-04-15 12:05 | 169 | E1504 | TB 22 KV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102785 | 17819 | 7553 |  |  | 2009-04-15 08:25 | 2009-04-15 12:13 | 228 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102786 | 17820 | 7554 |  |  | 2009-04-15 08:38 | 2009-04-15 17:21 | 523 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102787 | 17821 | 7555 |  |  | 2009-04-15 10:00 | 2009-04-15 13:27 | 207 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102788 | 17822 | 7561 |  |  | 2009-04-16 12:15 | 2009-04-16 12:57 | 42 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102789 | 17823 | 7562 |  |  | 2009-04-16 13:04 | 2009-04-16 13:25 | 21 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102790 | 17824 | 7563 |  |  | 2009-04-16 17:06 | 2009-04-16 17:47 | 41 | E0197 | SO 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102791 | 17825 | 7564 |  |  | 2009-04-17 09:54 | 2009-04-17 11:02 | 68 | E0837 | RK 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139395 | 17826 | 7565 |  |  | 2009-04-18 06:43 | 2009-04-18 06:43 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102793 | 17827 | 7566 |  |  | 2009-04-18 07:23 | 2009-04-18 07:23 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102794 | 17828 | 7567 |  |  | 2009-04-18 21:38 | 2009-04-18 21:38 | 0 | E0943 | UL 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102795 | 17829 | 7568 |  |  | 2009-04-19 03:59 | 2009-04-19 05:08 | 69 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139396 | 17830 | 7569 |  |  | 2009-04-20 17:22 | 2009-04-20 17:22 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102797 | 17831 | 7570 |  |  | 2009-04-20 18:15 | 2009-04-20 18:15 | 0 | E0970 | SO 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102798 | 17832 | 7571 |  |  | 2009-04-22 03:17 | 2009-04-22 03:55 | 38 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102799 | 17833 | 7572 |  |  | 2009-04-22 15:23 | 2009-04-22 15:23 | 0 | E0970 | SO 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102800 | 17834 | 7573 |  |  | 2009-04-23 17:33 | 2009-04-23 17:33 | 0 | E1550 | DP 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102801 | 17835 | 7574 |  |  | 2009-04-24 13:55 | 2009-04-24 14:14 | 19 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102802 | 17836 | 7575 |  |  | 2009-04-24 17:53 | 2009-04-24 17:53 | 0 | E0970 | SO 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102803 | 17837 | 7576 |  |  | 2009-04-24 21:03 | 2009-04-24 23:34 | 151 | E0496 | GT 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102804 | 17838 | 7577 |  |  | 2009-04-25 20:29 | 2009-04-25 20:29 | 0 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102805 | 17839 | 7578 |  |  | 2009-04-26 03:12 | 2009-04-26 05:52 | 160 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
102806 | 17840 | 7579 |  |  | 2009-04-26 07:56 | 2009-04-26 07:56 | 0 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
118462 | 17984 | 1428 |  |  | 2009-03-29 13:26 | 2009-03-29 13:30 | 4 | E1621 | RI 110 kV Bus SPS | Bus | Fault | Insulation Failure | Generator Request | Completed | TRUE | 124 | TRUE |  | IR799 GT-TV No.3 tripped. CTfailure at George Town Substation. | FALSE | Undefined
103225 | 17985 | 1431 |  |  | 2009-04-03 11:10 | 2009-04-03 11:51 | 41 | E0193 | SO 110/22 kV T2 Transformer Circuit | Transformer | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR798 LF-SO-TB and SO T2 tripped to unknown cause due to lightning | FALSE | Non-Critical
103224 | 17985 | 1431 |  |  | 2009-04-03 11:10 | 2009-04-03 11:10 | 0 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR798 LF-SO-TB and SO T2 tripped to unknown cause due to lightning | FALSE | Non-Critical
103226 | 17986 | 1432 |  |  | 2009-04-03 13:12 | 2009-04-03 13:12 | 0 | E1497 | NW-SD 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR797 NW-SD-DE tripped and autoreclose, lightning in area. | FALSE | Non-Critical
103227 | 17987 | 1433 |  |  | 2009-04-07 08:19 | 2009-04-07 08:21 | 2 | E0535 | SH 220/110 kV T2 Transformer Circuit | Transformer | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR796 Sheffield T2 tripped SH 220/110kV T2 was inadvertently removed form service during switching to reconfigure 220kV switchyard for purpose of taking B bus out of service. Operator failed to select correct VT selection | FALSE | Non-Critical
103228 | 17988 | 1434 |  |  | 2009-04-15 07:13 | 2009-04-15 07:17 | 4 | E0540 | SH-FI 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR779 SH-FI trip, adverse weather in area. | FALSE | Non-Critical
103229 | 17989 | 1435 |  |  | 2009-04-15 08:25 | 2009-04-15 08:37 | 12 | E0274 | PM-AV 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 117 | TRUE |  | IR778 PM-AV tripped, lightning in area. | FALSE | Non-Critical
198953 | 17990 | 1437 |  |  | 2009-04-23 15:57 | 2009-04-23 16:25 | 28 | E0206 | RI 110 kV G7 Circuit Breaker | Circuit Breaker | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR777 Risdon 11kV bus zone protection testing being undertaken at time of trip. Under investigation. not in ITOMs as appears to be the reult of 22kV protection testing. | FALSE | Undefined
103231 | 17990 | 1437 |  |  | 2009-04-23 15:57 | 2009-04-23 16:26 | 29 | E0207 | RI 110 kV H7 Circuit Breaker | Circuit Breaker | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR777 Risdon 11kV bus zone protection testing being undertaken at time of trip. Under investigation. not in ITOMs as appears to be the reult of 22kV protection testing. | FALSE | Undefined
103237 | 17991 | 1438 |  |  | 2009-04-26 06:17 | 2009-04-26 06:34 | 17 | E0832 | RK 11 kV A Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR776 trip of LF-RK 1 when c252 energised due to protection grading issue. not in ITOMS, this a 22kV protection blocking issue. | FALSE | Undefined
103236 | 17991 | 1438 |  |  | 2009-04-26 03:27 | 2009-04-26 04:13 | 46 | E0832 | RK 11 kV A Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR776 trip of LF-RK 1 when c252 energised due to protection grading issue. not in ITOMS, this a 22kV protection blocking issue. | FALSE | Undefined
103233 | 17991 | 1438 |  |  | 2009-04-26 06:17 | 2009-04-26 06:33 | 16 | E0348 | LF-RK 1 110 kV Transmission Circuit | Transmission | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR776 trip of LF-RK 1 when c252 energised due to protection grading issue. not in ITOMS, this a 22kV protection blocking issue. | FALSE | Non-Critical
103232 | 17991 | 1438 |  |  | 2009-04-26 03:27 | 2009-04-26 04:13 | 46 | E0348 | LF-RK 1 110 kV Transmission Circuit | Transmission | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 227 | TRUE |  | IR776 trip of LF-RK 1 when c252 energised due to protection grading issue. not in ITOMS, this a 22kV protection blocking issue. | FALSE | Non-Critical
103234 | 17991 | 1438 |  |  | 2009-04-26 03:27 | 2009-04-26 04:13 | 46 | E0830 | RK 110/11 kV T1 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR776 trip of LF-RK 1 when c252 energised due to protection grading issue. not in ITOMS, this a 22kV protection blocking issue. | FALSE | Undefined
103235 | 17991 | 1438 |  |  | 2009-04-26 06:17 | 2009-04-26 06:33 | 16 | E0830 | RK 110/11 kV T1 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR776 trip of LF-RK 1 when c252 energised due to protection grading issue. not in ITOMS, this a 22kV protection blocking issue. | FALSE | Undefined
103517 | 18020 | 7580 |  |  | 2009-04-26 08:12 | 2009-04-26 08:12 | 0 | E0970 | SO 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
103518 | 18021 | 7581 |  |  | 2009-04-26 19:08 | 2009-04-26 20:21 | 73 | E0118 | CS 11 kV T2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
103519 | 18022 | 7582 |  |  | 2009-04-26 19:43 | 2009-04-26 20:34 | 51 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
103520 | 18023 | 7583 |  |  | 2009-04-27 00:26 | 2009-04-27 00:27 | 1 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
103521 | 18024 | 7584 |  |  | 2009-04-27 05:52 | 2009-04-27 05:53 | 1 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139397 | 18068 | 7591 |  |  | 2009-04-27 15:34 | 2009-04-27 15:34 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
103942 | 18069 | 7592 |  |  | 2009-04-28 | 2009-04-28 | 0 | E0764 | NW 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
103943 | 18070 | 7593 |  |  | 2009-04-29 07:43 | 2009-04-29 08:02 | 19 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
103944 | 18071 | 7594 |  |  | 2009-04-26 06:17 | 2009-04-26 07:20 | 63 | E0837 | RK 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
103945 | 18072 | 7595 |  |  | 2009-05-01 20:58 | 2009-05-01 20:58 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
103946 | 18073 | 7596 |  |  | 2009-05-02 19:47 | 2009-05-02 19:47 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
103947 | 18074 | 7597 |  |  | 2009-05-03 09:18 | 2009-05-03 09:29 | 11 | E1004 | BU 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104020 | 18075 | 7598 |  |  | 2009-05-04 07:23 | 2009-05-04 09:21 | 118 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104021 | 18076 | 7599 |  |  | 2009-05-04 09:38 | 2009-05-04 09:38 | 0 | E0354 | KI 11 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104022 | 18077 | 7600 |  |  | 2009-05-05 06:22 | 2009-05-05 06:22 | 0 | E0156 | MB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104023 | 18078 | 7601 |  |  | 2009-05-10 00:06 | 2009-05-10 02:00 | 114 | E0638 | ST 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104024 | 18079 | 7603 |  |  | 2009-05-10 19:09 | 2009-05-10 19:09 | 0 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104025 | 18080 | 7604 |  |  | 2009-05-12 21:02 | 2009-05-12 21:26 | 24 | E0768 | NW 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104026 | 18081 | 7605 |  |  | 2009-05-13 06:43 | 2009-05-13 06:44 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104027 | 18082 | 7606 |  |  | 2009-05-14 15:26 | 2009-05-14 15:27 | 1 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104028 | 18083 | 7607 |  |  | 2009-05-15 08:56 | 2009-05-15 12:26 | 210 | E0870 | RB 44 kV B2 Circuit Breaker | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104029 | 18084 | 7610 |  |  | 2009-05-16 09:02 | 2009-05-16 12:12 | 190 | E1612 | UL 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104826 | 18179 | 1440 |  |  | 2009-05-06 13:45 | 2009-05-06 14:06 | 21 | E0210 | RI 110/11 kV T1 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR775 RI T1 tripped due to a human error during planned protection testing. not in ITOMS as 22kV wiring error found to cause trip. | FALSE | Non-Critical
104829 | 18180 | 1443 |  |  | 2009-05-13 21:40 | 2009-05-13 21:40 | 0 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR774 FA-RB-QT tripped and reclosed due to lightning | FALSE | Non-Critical
104830 | 18181 | 1445 |  |  | 2009-05-15 08:56 | 2009-05-15 09:23 | 27 | E0719 | FA-RB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 898 | TRUE |  | IR773 Farrell-Roseberry 110 kV tripped. | FALSE | Non-Critical
104831 | 18182 | 1446 |  |  | 2009-05-18 18:26 | 2009-05-18 22:13 | 227 | E0594 | DP 110/22 kV T2 Transformer Circuit | Transformer | Fault | Wildlife | Transend | Completed | TRUE | 0 | TRUE |  | IR772 DP T2 tripped due to wildlife. | FALSE | Non-Critical
104917 | 18183 | 7611 |  |  | 2009-05-16 15:43 | 2009-05-16 16:10 | 27 | E1531 | MY 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104918 | 18184 | 7612 |  |  | 2009-05-17 05:59 | 2009-05-17 05:59 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104919 | 18185 | 7613 |  |  | 2009-05-17 06:46 | 2009-05-17 07:47 | 61 | E0738 | NH 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104920 | 18186 | 7614 |  |  | 2009-05-17 17:03 | 2009-05-17 17:03 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104921 | 18187 | 7615 |  |  | 2009-05-18 21:12 | 2009-05-18 21:12 | 0 | E0789 | QT 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104922 | 18188 | 7616 |  |  | 2009-05-18 21:13 | 2009-05-18 22:11 | 58 | E0789 | QT 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104923 | 18189 | 7617 |  |  | 2009-05-19 04:44 | 2009-05-19 05:01 | 17 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104924 | 18190 | 7618 |  |  | 2009-05-20 01:07 | 2009-05-20 02:40 | 93 | E0569 | EB 11 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139398 | 18191 | 7619 |  |  | 2009-05-21 10:13 | 2009-05-21 10:50 | 37 | E1568 | DP 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
104926 | 18192 | 7620 |  |  | 2009-05-22 00:06 | 2009-05-22 00:06 | 0 | E1548 | DP 22 kV C2 Capacitor Circuit | Capacitor | Fault |  | DNSP | Completed | FALSE | 0 | TRUE |  |  | FALSE | Undefined
105215 | 18300 | 7621 |  |  | 2009-05-24 01:18 | 2009-05-24 01:34 | 16 | E0364 | KI 11 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
105216 | 18301 | 7622 |  |  | 2009-05-24 11:03 | 2009-05-24 11:26 | 23 | E1505 | TB 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
105217 | 18302 | 7624 |  |  | 2009-05-25 21:30 | 2009-05-25 22:15 | 45 | E1538 | MY 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
105218 | 18303 | 7625 |  |  | 2009-05-26 05:02 | 2009-05-26 05:28 | 26 | E0075 | CR 33 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
105219 | 18304 | 7626 |  |  | 2009-05-26 06:00 | 2009-05-26 07:59 | 119 | E0075 | CR 33 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
105220 | 18305 | 7628 |  |  | 2009-05-28 07:17 | 2009-05-28 07:17 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
105221 | 18306 | 7629 |  |  | 2009-05-28 14:38 | 2009-05-28 14:38 | 0 | E0820 | RA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
105222 | 18307 | 7630 |  |  | 2009-05-28 19:41 | 2009-05-28 19:41 | 0 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
105223 | 18308 | 7631 |  |  | 2009-05-30 12:48 | 2009-05-30 12:48 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110668 | 18467 | 1448 |  |  | 2009-06-23 20:28 | 2009-08-04 11:47 | 59959 | E1712 | MY 110/22 kV T1 Transformer Circuit | Transformer | Fault | Cable Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR771 MY T1 transformer circuit tripped due to 22kV cable fault. not in ITOMs as 22kV cable fault, times updated to reflect HRS. | FALSE | Undefined
106724 | 18482 | 7509 |  |  | 2009-04-11 12:49 | 2009-04-11 12:49 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106725 | 18484 | 7632 |  |  | 2009-06-01 07:42 | 2009-06-01 07:42 | 0 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106831 | 18485 | 7634 |  |  | 2009-06-01 12:16 | 2009-06-01 12:16 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106832 | 18486 | 7635 |  |  | 2009-06-02 12:03 | 2009-06-02 12:07 | 4 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106833 | 18487 | 7636 |  |  | 2009-06-03 10:43 | 2009-06-03 10:50 | 7 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106834 | 18488 | 7637 |  |  | 2009-06-03 15:41 | 2009-06-03 18:29 | 168 | E0075 | CR 33 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106835 | 18489 | 7638 |  |  | 2009-06-04 09:14 | 2009-06-04 09:29 | 15 | E1505 | TB 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106836 | 18490 | 7639 |  |  | 2009-06-04 09:54 | 2009-06-04 10:00 | 6 | E1505 | TB 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106837 | 18491 | 7640 |  |  | 2009-06-04 19:04 | 2009-06-04 19:04 | 0 | E1505 | TB 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106838 | 18492 | 7641 |  |  | 2009-06-05 04:06 | 2009-06-05 04:25 | 19 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106839 | 18493 | 7642 |  |  | 2009-06-05 13:52 | 2009-06-05 13:52 | 0 | E0898 | SD 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106840 | 18494 | 7643 |  |  | 2009-06-09 23:55 | 2009-06-09 23:55 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106841 | 18495 | 7644 |  |  | 2009-06-11 15:30 | 2009-06-11 15:30 | 0 | E1613 | UL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106842 | 18496 | 7645 |  |  | 2009-06-13 12:28 | 2009-06-13 12:28 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106843 | 18497 | 7646 |  |  | 2009-06-14 23:29 | 2009-06-14 23:46 | 17 | E0084 | CR 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139401 | 18498 | 7647 |  |  | 2009-06-15 08:54 | 2009-06-15 08:54 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
113540 | 18500 | 7648 |  |  | 2009-06-15 11:56 | 2009-06-15 11:56 | 0 | E0867 | RB 22 kV D5 Feeder Circuit | Feeder | Fault | DNSP | DNSP | Completed | TRUE | 0 | TRUE |  | Feeder 97001 fault, D452 trip and reclose. | FALSE | Undefined
106916 | 18501 | 7649 |  |  | 2009-06-19 08:46 | 2009-06-19 08:46 | 0 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106917 | 18502 | 7650 |  |  | 2009-06-19 12:15 | 2009-06-19 13:07 | 52 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106918 | 18503 | 7651 |  |  | 2009-06-22 13:43 | 2009-06-22 13:43 | 0 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106919 | 18504 | 7652 |  |  | 2009-06-24 00:23 | 2009-06-24 00:23 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106920 | 18505 | 7653 |  |  | 2009-06-25 08:06 | 2009-06-25 09:01 | 55 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106921 | 18506 | 7654 |  |  | 2009-06-25 16:07 | 2009-06-25 16:08 | 1 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
106922 | 18507 | 7655 |  |  | 2009-06-25 16:09 | 2009-06-25 16:29 | 20 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107098 | 18508 | 7656 |  |  | 2009-06-25 17:12 | 2009-06-25 17:38 | 26 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107099 | 18509 | 7657 |  |  | 2009-06-25 17:43 | 2009-06-25 18:01 | 18 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107100 | 18510 | 7658 |  |  | 2009-06-25 18:26 | 2009-06-25 19:27 | 61 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107101 | 18511 | 7659 |  |  | 2009-06-27 12:16 | 2009-06-27 12:16 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107102 | 18512 | 7660 |  |  | 2009-06-27 17:35 | 2009-06-27 17:35 | 0 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107103 | 18513 | 7662 |  |  | 2009-06-28 21:16 | 2009-06-28 21:17 | 1 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107104 | 18514 | 7663 |  |  | 2009-06-30 10:50 | 2009-06-30 10:50 | 0 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107105 | 18515 | 7664 |  |  | 2009-06-30 17:19 | 2009-06-30 17:19 | 0 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107106 | 18516 | 7665 |  |  | 2009-06-30 18:01 | 2009-06-30 18:01 | 0 | E0643 | ST 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107107 | 18517 | 7666 |  |  | 2009-06-30 18:47 | 2009-06-30 18:47 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107108 | 18518 | 7667 |  |  | 2009-06-30 18:51 | 2009-06-30 19:13 | 22 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107109 | 18519 | 7668 |  |  | 2009-06-30 18:23 | 2009-06-30 19:35 | 72 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107814 | 18630 | 7669 |  |  | 2009-07-01 04:42 | 2009-07-01 04:42 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107815 | 18631 | 7670 |  |  | 2009-07-01 08:19 | 2009-07-01 08:20 | 1 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107816 | 18632 | 7671 |  |  | 2009-07-01 13:39 | 2009-07-01 13:39 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
108068 | 18633 | 7672 |  |  | 2009-07-01 19:10 | 2009-07-01 19:10 | 0 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107818 | 18634 | 7673 |  |  | 2009-07-02 07:16 | 2009-07-02 07:16 | 0 | E0764 | NW 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107819 | 18635 | 7674 |  |  | 2009-07-03 11:19 | 2009-07-03 11:19 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107820 | 18636 | 7676 |  |  | 2009-07-04 08:50 | 2009-07-04 11:15 | 145 | E0353 | LF 33 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107821 | 18637 | 7677 |  |  | 2009-07-04 12:44 | 2009-07-04 14:35 | 111 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107822 | 18638 | 7678 |  |  | 2009-07-05 18:04 | 2009-07-05 19:25 | 81 | E0412 | EL 11 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
107823 | 18639 | 7679 |  |  | 2009-07-06 23:12 | 2009-07-06 23:13 | 1 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
116450 | 18640 | 1449 |  |  | 2009-07-02 10:47 | 2009-07-02 11:07 | 20 | E1621 | RI 110 kV Bus SPS | Bus | Fault | Load Shedding | Basslink | Completed | TRUE | 1580 | TRUE |  | UFLS block 1 operated when 2530 MW generation tripped on the mainland. | FALSE | Undefined
116451 | 18640 | 1449 |  |  | 2009-07-02 10:47 | 2009-07-02 10:49 | 2 | E1703 | CO 220 kV Bus SPS | Bus | Fault | Load Shedding | Basslink | Completed | TRUE | 0 | TRUE |  | UFLS block 1 operated when 2530 MW generation tripped on the mainland. | FALSE | Not In Wasp
175187 | 18641 | 1454 |  |  | 2009-07-12 08:27 | 2009-07-12 09:31 | 64 | E0179 | TU 110/22 kV T9X Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 39 | TRUE |  | IR751 TU T9 tripped at same time as C252 feeder fault | FALSE | Non-Critical
107893 | 18642 | 1456 |  |  | 2009-07-27 15:05 | 2009-07-27 15:09 | 4 | E0437 | HA-GT 1 220 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR754 Hadspen Substation circuit breaker tripped during protection work. | FALSE | Critical
175188 | 18644 | 1455 |  |  | 2009-07-14 12:21 | 2009-07-14 12:29 | 8 | E0179 | TU 110/22 kV T9X Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 4 | TRUE |  | IR765 TU T9 tripped while P&T personnel on site and during testing. | FALSE | Non-Critical
108374 | 18696 | 1369 |  |  | 2008-09-28 18:23 | 2008-09-29 15:11 | 1248 | E0793 | QT 110/22 kV T1 Transformer Circuit | Transformer | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  | IR? QT 110/22kV T1 tripped to unknown cause. Lightning in area at the time. | FALSE | Non-Critical
108397 | 18697 | 1457 |  |  | 2009-08-03 02:48 | 2009-08-03 04:40 | 112 | E0856 | RB 110/44 kV T1 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 2269 | TRUE |  | IR705 - Rosebery Substation - the Rosebery T1 and T2 110/44 kV transformer circuits tripped following a feeder fault due to incorrect protection grading. | FALSE | Non-Critical
108398 | 18697 | 1457 |  |  | 2009-08-03 02:48 | 2009-08-03 04:40 | 112 | E0857 | RB 110/44 kV T2 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR705 - Rosebery Substation - the Rosebery T1 and T2 110/44 kV transformer circuits tripped following a feeder fault due to incorrect protection grading. | FALSE | Non-Critical
108969 | 18755 | 7680 |  |  | 2009-07-07 02:57 | 2009-07-07 03:55 | 58 | E0354 | KI 11 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
108970 | 18756 | 7681 |  |  | 2009-07-07 05:55 | 2009-07-07 06:10 | 15 | E1042 | SD 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
108971 | 18757 | 7682 |  |  | 2009-07-08 03:41 | 2009-07-08 03:41 | 0 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
108972 | 18758 | 7683 |  |  | 2009-07-11 15:56 | 2009-07-11 16:38 | 42 | E0015 | BW 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
108973 | 18759 | 7684 |  |  | 2009-07-11 22:04 | 2009-07-12 00:12 | 128 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
108974 | 18760 | 7686 |  |  | 2009-07-13 10:53 | 2009-07-13 11:24 | 31 | E0354 | KI 11 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139404 | 18761 | 7687 |  |  | 2009-07-14 15:25 | 2009-07-14 15:29 | 4 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
108976 | 18762 | 7688 |  |  | 2009-07-15 22:45 | 2009-07-16 00:09 | 84 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
108977 | 18763 | 7689 |  |  | 2009-07-16 08:36 | 2009-07-16 08:36 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
108978 | 18764 | 7690 |  |  | 2009-07-16 16:51 | 2009-07-16 16:52 | 1 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
108979 | 18765 | 7691 |  |  | 2009-07-18 15:58 | 2009-07-18 15:59 | 1 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
108980 | 18766 | 7692 |  |  | 2009-07-20 11:17 | 2009-07-20 12:02 | 45 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
108981 | 18767 | 7693 |  |  | 2009-07-20 12:42 | 2009-07-20 12:42 | 0 | E1504 | TB 22 KV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
108982 | 18768 | 7694 |  |  | 2009-07-20 12:49 | 2009-07-20 12:50 | 1 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185970 | 18770 | 1458 |  |  | 2009-08-04 03:52 | 2009-08-04 04:08 | 16 | E0722 | NT 110 kV XBus | Bus | Fault | Adverse Weather | Transend | Completed | TRUE | 102 | TRUE |  | IR753 Newton 110kV bus bar disconnected. Loss of supply. | FALSE | Undefined
109051 | 18771 | 1459 |  |  | 2009-08-16 08:24 | 2009-08-16 08:29 | 5 | E0404 | SH-BU 2 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR756 SH-BU 2 110kV and UL-EB 110kV transmission line circuits tripped due to lightning. | FALSE | Non-Critical
109052 | 18771 | 1459 |  |  | 2009-08-16 08:24 | 2009-08-16 08:26 | 2 | E0587 | UL-EB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR756 SH-BU 2 110kV and UL-EB 110kV transmission line circuits tripped due to lightning. | FALSE | Non-Critical
109055 | 18772 | 1461 |  |  | 2009-08-16 09:02 | 2009-08-16 09:03 | 1 | E0441 | HA-TR 1 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR757 Hadspen transmission line circuits tripped. | FALSE | Critical
109053 | 18772 | 1461 |  |  | 2009-08-16 08:47 | 2009-08-16 08:47 | 0 | E0259 | PM-HA 1 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR757 Hadspen transmission line circuits tripped. | FALSE | Critical
109054 | 18772 | 1461 |  |  | 2009-08-16 08:53 | 2009-08-16 08:53 | 0 | E0438 | HA-GT 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR757 Hadspen transmission line circuits tripped. | FALSE | Critical
109056 | 18774 | 1464 |  |  | 2009-08-16 07:48 | 2009-08-16 15:37 | 469 | E0794 | QT 110/22 kV T2 Transformer Circuit | Transformer | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR755 Queenstown T2 trippeddue to lightning | FALSE | Non-Critical
109079 | 18775 | 1466 |  |  | 2009-08-21 09:02 | 2009-08-21 09:04 | 2 | E0401 | BU-PL 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR758 BU-PL transmission line tripped, lightning in the area. | FALSE | Non-Critical
109080 | 18776 | 1467 |  |  | 2009-08-25 11:25 | 2009-08-25 11:40 | 15 | E0715 | FA-JB 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR759 FA-JB and FA-RB-QT transmission circuits tripped, possibly due to lightning | FALSE | Non-Critical
109081 | 18776 | 1467 |  |  | 2009-08-25 11:25 | 2009-08-25 11:25 | 0 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR759 FA-JB and FA-RB-QT transmission circuits tripped, possibly due to lightning | FALSE | Non-Critical
109082 | 18777 | 1469 |  |  | 2009-08-31 10:28 | 2009-08-31 11:01 | 33 | E0141 | NN 22 kV B Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 348 | TRUE |  | IR726 New Norfolk Substation - the New Norfolk 22kV B bus bar tripped due to protection mal-operation. | FALSE | Undefined
143058 | 18778 | 1471 |  |  | 2009-08-31 10:34 | 2009-08-31 11:20 | 46 | E0169 | TU-BG-DB 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 11 | TRUE |  | IR760 TU-BG-DB tripped during severe wind conditions. | FALSE | Non-Critical
109084 | 18779 | 1472 |  |  | 2009-08-31 11:29 | 2009-08-31 18:33 | 424 | E0171 | TU-LE-WA 1 110 kV Transmission Circuit (Changed to E1957) | Transmission | Fault | Vegetation | Transend | Completed | TRUE | 0 | TRUE |  | IR761 TU-LE-WA 1 transmission line tripped due to tree falling on line. | FALSE | Critical
175189 | 18780 | 1473 |  |  | 2009-08-31 13:47 | 2009-08-31 14:44 | 57 | E0179 | TU 110/22 kV T9X Transformer Circuit | Transformer | Fault | Unknown | Transend | Completed | TRUE | 8 | TRUE |  | IR762 Tungatinah T9 tripped with a 22kV feeder fault. | FALSE | Non-Critical
109739 | 18899 | 7395 |  |  | 2009-07-20 12:50 | 2009-07-20 12:50 | 0 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109740 | 18900 | 7696 |  |  | 2009-07-20 14:14 | 2009-07-20 14:33 | 19 | E0104 | CS 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109741 | 18901 | 7698 |  |  | 2009-07-20 12:51 | 2009-07-20 13:16 | 25 | E1505 | TB 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109742 | 18902 | 7699 |  |  | 2009-07-20 14:44 | 2009-07-20 15:30 | 46 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139411 | 18903 | 7700 |  |  | 2009-07-20 14:42 | 2009-07-20 14:43 | 1 | E1567 | DP 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109744 | 18904 | 7703 |  |  | 2009-07-24 15:42 | 2009-07-24 15:42 | 0 | E0888 | DE 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109745 | 18905 | 7705 |  |  | 2009-07-24 22:51 | 2009-07-24 22:51 | 0 | E0888 | DE 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109746 | 18906 | 7706 |  |  | 2009-07-26 07:48 | 2009-07-26 07:49 | 1 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109747 | 18907 | 7707 |  |  | 2009-07-29 01:34 | 2009-07-29 01:34 | 0 | E0946 | UL 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109748 | 18908 | 7709 |  |  | 2009-07-30 20:21 | 2009-07-30 20:22 | 1 | E0412 | EL 11 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109749 | 18909 | 7711 |  |  | 2009-07-31 14:25 | 2009-07-31 14:45 | 20 | E0902 | TR 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109802 | 18918 | 7712 |  |  | 2009-08-01 01:27 | 2009-08-01 01:27 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109803 | 18919 | 7714 |  |  | 2009-08-02 21:43 | 2009-08-02 21:43 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109804 | 18920 | 7715 |  |  | 2009-08-02 21:58 | 2009-08-02 21:58 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109805 | 18921 | 7716 |  |  | 2009-08-02 22:04 | 2009-08-02 22:04 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109806 | 18922 | 7718 |  |  | 2009-08-02 22:06 | 2009-08-02 23:48 | 102 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109807 | 18923 | 7719 |  |  | 2009-08-02 21:02 | 2009-08-03 00:54 | 232 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109808 | 18924 | 7722 |  |  | 2009-08-03 02:41 | 2009-08-03 02:41 | 0 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109809 | 18925 | 7723 |  |  | 2009-08-03 01:26 | 2009-08-03 02:45 | 79 | E1530 | MY 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109810 | 18926 | 7725 |  |  | 2009-08-03 17:56 | 2009-08-03 18:17 | 21 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109811 | 18929 | 7728 |  |  | 2009-08-04 06:20 | 2009-08-04 07:15 | 55 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109812 | 18930 | 7729 |  |  | 2009-08-04 07:04 | 2009-08-04 07:39 | 35 | E0464 | KR 11 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109813 | 18931 | 7730 |  |  | 2009-08-04 11:07 | 2009-08-04 11:25 | 18 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139412 | 18932 | 7731 |  |  | 2009-08-04 11:42 | 2009-08-04 11:43 | 1 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109815 | 18933 | 7732 |  |  | 2009-08-05 11:07 | 2009-08-05 11:27 | 20 | E0902 | TR 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109816 | 18934 | 7733 |  |  | 2009-08-05 19:29 | 2009-08-05 19:29 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
109840 | 18935 | 7734 |  |  | 2009-08-07 15:27 | 2009-08-07 15:27 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110018 | 18962 | 7726 |  |  | 2009-08-04 04:04 | 2009-08-04 04:04 | 0 | E0869 | RB 44 kV E4 Circuit Breaker | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110019 | 18963 | 7727 |  |  | 2009-08-04 04:05 | 2009-08-04 04:05 | 0 | E0869 | RB 44 kV E4 Circuit Breaker | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110154 | 18964 | 7735 |  |  | 2009-08-07 19:48 | 2009-08-07 19:48 | 0 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139413 | 18965 | 7736 |  |  | 2009-08-10 09:04 | 2009-08-10 09:05 | 1 | E1567 | DP 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110156 | 18966 | 7737 |  |  | 2009-08-11 13:40 | 2009-08-11 13:40 | 0 | E0865 | RB 44 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110157 | 18967 | 7738 |  |  | 2009-08-12 08:12 | 2009-08-12 09:08 | 56 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110158 | 18968 | 7739 |  |  | 2009-08-12 12:35 | 2009-08-12 12:35 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110159 | 18969 | 7740 |  |  | 2009-08-12 12:48 | 2009-08-12 13:15 | 27 | E1570 | DP 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110160 | 18970 | 7741 |  |  | 2009-08-12 13:28 | 2009-08-12 14:18 | 50 | E1570 | DP 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110161 | 18971 | 7742 |  |  | 2009-08-12 16:20 | 2009-08-12 17:07 | 47 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110162 | 18972 | 7744 |  |  | 2009-08-13 10:15 | 2009-08-13 10:25 | 10 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110163 | 18973 | 7743 |  |  | 2009-08-13 10:15 | 2009-08-13 10:27 | 12 | E1444 | HA 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110164 | 18974 | 7745 |  |  | 2009-08-13 14:36 | 2009-08-13 14:40 | 4 | E0111 | CS 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110165 | 18975 | 7747 |  |  | 2009-08-14 07:40 | 2009-08-14 09:01 | 81 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110166 | 18976 | 7748 |  |  | 2009-08-14 22:18 | 2009-08-14 22:18 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110167 | 18977 | 7749 |  |  | 2009-08-15 01:07 | 2009-08-15 01:07 | 0 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110168 | 18978 | 7750 |  |  | 2009-08-15 09:03 | 2009-08-15 09:03 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110292 | 18979 | 7701 |  |  | 2009-07-22 10:55 | 2009-07-22 13:28 | 153 | E0083 | CR 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110293 | 18980 | 7819 |  |  | 2009-08-31 13:47 | 2009-09-01 12:15 | 1348 | E0186 | TU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110294 | 18981 | 7751 |  |  | 2009-08-16 04:16 | 2009-08-16 04:16 | 0 | E0363 | KI 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110295 | 18982 | 7752 |  |  | 2009-08-16 06:50 | 2009-08-16 06:50 | 0 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110296 | 18983 | 7753 |  |  | 2009-08-16 07:48 | 2009-08-16 07:48 | 0 | E0869 | RB 44 kV E4 Circuit Breaker | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110297 | 18984 | 7754 |  |  | 2009-08-16 08:05 | 2009-08-16 08:05 | 0 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110298 | 18985 | 7755 |  |  | 2009-08-16 08:09 | 2009-08-16 08:09 | 0 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110299 | 18986 | 7756 |  |  | 2009-08-16 08:11 | 2009-08-16 08:11 | 0 | E1554 | DP 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
113321 | 19052 | 1478 |  |  | 2009-09-02 10:49 | 2009-09-11 09:16 | 12867 | E1676 | CS 11 kV C4 Capacitor Circuit | Capacitor | Fault |  | Transend | Completed | FALSE | 0 | TRUE |  | IR? Cause is under investigation. | FALSE | Undefined
175192 | 19053 | 1479 |  |  | 2009-09-03 14:21 | 2009-09-03 14:47 | 26 | E0179 | TU 110/22 kV T9X Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 7 | TRUE |  | IR763 TU T9 tripped, loss of supply, cause is under investigation, suspect slow clearance of feeder fault. | FALSE | Non-Critical
110467 | 19054 | 1480 |  |  | 2009-09-12 17:26 | 2009-09-12 17:26 | 0 | E0400 | BU-HM 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR752 BU-HM tripped and autoreclose. Cause is unknown. | FALSE | Non-Critical
111859 | 19055 | 1481 |  |  | 2009-09-14 10:30 | 2009-09-14 18:36 | 486 | E0406 | FA-QU-SR-HM 110 kV Transmission Circuit | Transmission | Fault | Mechanical Failure | Transend | Completed | TRUE | 9194 | TRUE |  | IR722 FA-QU-SR-HM tripped due to broken insulator. Loss of supply at Que and Savage River. | FALSE | Non-Critical
113261 | 19056 | 1487 |  |  | 2009-09-16 11:50 | 2009-09-16 12:29 | 39 | E0487 | GT 22 kV B Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 268 | TRUE |  | IR817 GT supply bus tripped due to inadequate isolation of trip circuits causing loss of supply. | FALSE | Undefined
110470 | 19057 | 1489 |  |  | 2009-09-19 02:28 | 2009-09-19 02:30 | 2 | E0027 | LI-CL-RE-CS 1 220 kV Transmission Circuit (Changed to E1958) | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR728 LI-CL-RE-CS tripped. Load shed at Nyrstar. | FALSE | Critical
110471 | 19058 | 1492 |  |  | 2009-09-23 04:34 | 2009-09-23 04:34 | 0 | E0274 | PM-AV 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR750 PM-AV transmission circuit interrupted. | FALSE | Non-Critical
118473 | 19059 | 1493 |  |  | 2009-09-27 07:24 | 2009-09-27 10:47 | 203 | E0536 | SH-DG 110 kV Transmission Circuit | Transmission | Fault |  | Transend | Completed | TRUE | 0 | TRUE |  | IR?? SH-DG tripped. Cause is under investigation. | FALSE | Non-Critical
122415 | 19060 | 1494 |  |  | 2009-09-27 09:18 | 2009-09-27 11:08 | 110 | E0402 | BU-ST 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR721 BU-ST tripped. | FALSE | Non-Critical
113095 | 19062 | 1499 |  |  | 2009-09-27 12:16 | 2009-09-27 13:50 | 94 | E0401 | BU-PL 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Force Majeure | Completed | TRUE | 1903 | TRUE |  | IR721 BU-ST and BU-PL tripped during severe wind storms. | FALSE | Non-Critical
110855 | 19141 | 7757 |  |  | 2009-08-16 09:19 | 2009-08-16 09:19 | 0 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110856 | 19142 | 7758 |  |  | 2009-08-16 09:03 | 2009-08-16 09:03 | 0 | E0902 | TR 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110857 | 19143 | 7759 |  |  | 2009-08-16 09:03 | 2009-08-16 09:03 | 0 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110858 | 19144 | 7760 |  |  | 2009-08-16 08:38 | 2009-08-16 10:26 | 108 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110859 | 19145 | 7761 |  |  | 2009-08-16 11:49 | 2009-08-16 12:07 | 18 | E0842 | RK 11 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110860 | 19146 | 7762 |  |  | 2009-08-16 11:02 | 2009-08-16 12:18 | 76 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110861 | 19147 | 7763 |  |  | 2009-08-16 12:33 | 2009-08-16 12:33 | 0 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110862 | 19148 | 7764 |  |  | 2009-08-16 13:16 | 2009-08-16 13:16 | 0 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110863 | 19149 | 7765 |  |  | 2009-08-16 12:19 | 2009-08-16 13:04 | 45 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110864 | 19150 | 7766 |  |  | 2009-08-16 13:56 | 2009-08-16 14:51 | 55 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110865 | 19151 | 7768 |  |  | 2009-08-21 08:52 | 2009-08-21 08:53 | 1 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110866 | 19152 | 7769 |  |  | 2009-08-21 09:22 | 2009-08-21 09:23 | 1 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110867 | 19153 | 7770 |  |  | 2009-08-21 09:15 | 2009-08-21 09:28 | 13 | E1570 | DP 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110868 | 19154 | 7772 |  |  | 2009-08-21 14:37 | 2009-08-21 14:38 | 1 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110869 | 19155 | 7773 |  |  | 2009-08-21 14:41 | 2009-08-21 15:54 | 73 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110870 | 19156 | 7774 |  |  | 2009-08-22 13:30 | 2009-08-22 13:30 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139415 | 19159 | 7775 |  |  | 2009-08-23 07:35 | 2009-08-23 07:35 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110990 | 19160 | 7776 |  |  | 2009-08-24 12:36 | 2009-08-24 12:50 | 14 | E0819 | RA 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110991 | 19161 | 7777 |  |  | 2009-08-24 16:34 | 2009-08-24 16:34 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110992 | 19162 | 7778 |  |  | 2009-08-24 17:08 | 2009-08-24 17:08 | 0 | E1552 | DP 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110993 | 19163 | 7779 |  |  | 2009-08-25 14:09 | 2009-08-25 14:31 | 22 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110994 | 19164 | 7780 |  |  | 2009-08-26 10:09 | 2009-08-26 10:16 | 7 | E0111 | CS 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110995 | 19165 | 7781 |  |  | 2009-08-26 11:39 | 2009-08-26 11:39 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110996 | 19166 | 7782 |  |  | 2009-08-26 12:12 | 2009-08-26 12:12 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110997 | 19167 | 7783 |  |  | 2009-08-26 12:10 | 2009-08-26 12:29 | 19 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110998 | 19168 | 7784 |  |  | 2009-08-26 12:42 | 2009-08-26 12:43 | 1 | E1507 | SD 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
110999 | 19169 | 7785 |  |  | 2009-08-26 12:13 | 2009-08-26 12:52 | 39 | E0495 | GT 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111078 | 19198 | 1490 |  |  | 2009-10-01 13:34 | 2009-10-01 13:49 | 15 | E1677 | CS 11 kV C5 Capacitor Circuit | Capacitor | Fault |  | Transend | Completed | FALSE | 0 | TRUE |  | IR?? Chapel St C652 circuit tripped. Unknown cause, under investigation. | FALSE | Undefined
202213 | 19198 | 1490 |  |  | 2009-09-24 10:02 | 2009-09-24 10:22 | 20 | E1678 | CS 11 kV C6 Capacitor Circuit | Capacitor | Fault |  | Transend | Completed | FALSE | 0 | TRUE |  | IR?? Chapel St C652 circuit tripped. Unknown cause, under investigation. | FALSE | Undefined
111151 | 19199 | 7786 |  |  | 2009-08-26 12:02 | 2009-08-26 13:15 | 73 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111152 | 19200 | 7787 |  |  | 2009-08-26 11:37 | 2009-08-26 13:51 | 134 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111153 | 19201 | 7788 |  |  | 2009-08-26 14:47 | 2009-08-26 14:48 | 1 | E0300 | AV 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111154 | 19202 | 7789 |  |  | 2009-08-26 14:17 | 2009-08-26 15:14 | 57 | E0111 | CS 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111155 | 19203 | 7790 |  |  | 2009-08-26 13:27 | 2009-08-26 15:44 | 137 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185977 | 19235 | 1513 |  |  | 2009-10-18 21:33 | 2009-10-18 21:36 | 3 | E0173 | TU-WA 2 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR745 Tungatinah-Lake Echo-Waddamana 2 tripped. Cause is unknown. | FALSE | Critical
111217 | 19236 | 7791 |  |  | 2009-08-26 16:11 | 2009-08-26 16:35 | 24 | E0111 | CS 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111218 | 19237 | 7792 |  |  | 2009-08-26 16:47 | 2009-08-26 16:47 | 0 | E0869 | RB 44 kV E4 Circuit Breaker | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111219 | 19239 | 7794 |  |  | 2009-08-26 16:07 | 2009-08-26 18:37 | 150 | E0789 | QT 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111220 | 19240 | 7795 |  |  | 2009-08-26 19:31 | 2009-08-27 13:40 | 1089 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111221 | 19241 | 7796 |  |  | 2009-08-28 08:45 | 2009-08-28 08:46 | 1 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139418 | 19242 | 7798 |  |  | 2009-08-28 13:11 | 2009-08-28 13:11 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111223 | 19243 | 7800 |  |  | 2009-08-31 09:01 | 2009-08-31 09:02 | 1 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111224 | 19244 | 7801 |  |  | 2009-08-31 10:03 | 2009-08-31 10:03 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111225 | 19245 | 7802 |  |  | 2009-08-31 10:04 | 2009-08-31 10:04 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111241 | 19246 | 1516 |  |  | 2009-10-30 23:26 | 2009-10-30 23:29 | 3 | E0715 | FA-JB 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR747 Farrell-John Butters and Farrell-Rosebery-Queenstown trip, due to lightning. | FALSE | Non-Critical
111242 | 19246 | 1516 |  |  | 2009-10-30 23:26 | 2009-10-30 23:26 | 0 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR747 Farrell-John Butters and Farrell-Rosebery-Queenstown trip, due to lightning. | FALSE | Non-Critical
111247 | 19248 | 1506 |  |  | 2009-10-06 19:38 | 2009-10-06 22:25 | 167 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Unknown | Basslink | Completed | TRUE | 0 | TRUE |  | Basslink tripped at Loy Yang, cause unknown. Nyrstar lost 28MW load on first trip. | FALSE | Undefined
111360 | 19248 | 1506 |  |  | 2009-10-08 12:45 | 2009-10-08 13:45 | 60 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Unknown | Basslink | Completed | TRUE | 0 | TRUE |  | Basslink tripped at Loy Yang, cause unknown. Nyrstar lost 28MW load on first trip. | FALSE | Undefined
111250 | 19251 | 1515 |  |  | 2009-10-25 07:58 | 2009-10-25 09:19 | 81 | E0029 | CS-RI 110 kV Transmission Circuit | Transmission | Fault | Wildlife | Transend | Completed | TRUE | 0 | TRUE |  | IR732 Chapel St-Risdon tripped. Norske Skog lost 33MW and Nystar lost 65MW due to power quality. | FALSE | Non-Critical
111327 | 19277 | 7803 |  |  | 2009-08-31 10:15 | 2009-08-31 10:15 | 0 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111328 | 19278 | 7804 |  |  | 2009-08-31 10:37 | 2009-08-31 10:37 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111329 | 19279 | 7805 |  |  | 2009-08-31 11:07 | 2009-08-31 11:08 | 1 | E0766 | NW 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111330 | 19280 | 7806 |  |  | 2009-08-31 11:10 | 2009-08-31 11:10 | 0 | E0766 | NW 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111331 | 19282 | 7808 |  |  | 2009-08-31 10:28 | 2009-08-31 12:01 | 93 | E0144 | NN 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111332 | 19283 | 7809 |  |  | 2009-08-31 11:09 | 2009-08-31 13:01 | 112 | E0465 | KR 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111333 | 19284 | 7807 |  |  | 2009-08-31 11:15 | 2009-08-31 11:15 | 0 | E0412 | EL 11 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111334 | 19285 | 7811 |  |  | 2009-08-31 11:38 | 2009-08-31 13:06 | 88 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111335 | 19286 | 7812 |  |  | 2009-08-31 11:19 | 2009-08-31 13:25 | 126 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111336 | 19287 | 7813 |  |  | 2009-08-31 13:43 | 2009-08-31 13:43 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111337 | 19288 | 7814 |  |  | 2009-08-31 10:54 | 2009-08-31 14:02 | 188 | E1471 | KE 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139422 | 19290 | 7817 |  |  | 2009-08-31 11:46 | 2009-08-31 19:19 | 453 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111340 | 19291 | 7818 |  |  | 2009-08-31 11:49 | 2009-08-31 20:42 | 533 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111341 | 19292 | 7820 |  |  | 2009-08-31 16:25 | 2009-08-31 16:25 | 0 | E0768 | NW 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111342 | 19293 | 7821 |  |  | 2009-08-31 16:38 | 2009-08-31 16:38 | 0 | E0464 | KR 11 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111434 | 19294 | 7826 |  |  | 2009-09-01 00:37 | 2009-09-01 00:37 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111435 | 19295 | 7829 |  |  | 2009-09-01 01:31 | 2009-09-01 01:31 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111436 | 19296 | 7830 |  |  | 2009-09-01 01:36 | 2009-09-01 03:47 | 131 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111438 | 19298 | 7832 |  |  | 2009-09-01 05:12 | 2009-09-01 05:12 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111439 | 19300 | 7833 |  |  | 2009-09-01 05:24 | 2009-09-01 05:24 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111440 | 19301 | 7834 |  |  | 2009-09-01 05:26 | 2009-09-01 05:26 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111441 | 19302 | 7835 |  |  | 2009-09-01 05:35 | 2009-09-01 05:35 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111442 | 19303 | 7837 |  |  | 2009-09-01 15:33 | 2009-09-01 16:42 | 69 | E1550 | DP 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111443 | 19305 | 7839 |  |  | 2009-09-06 05:25 | 2009-09-06 05:26 | 1 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111444 | 19306 | 7840 |  |  | 2009-09-08 07:12 | 2009-09-08 07:31 | 19 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111559 | 19338 | 7841 |  |  | 2009-09-08 09:17 | 2009-09-08 09:17 | 0 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111560 | 19339 | 7842 |  |  | 2009-09-08 09:18 | 2009-09-08 09:19 | 1 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111561 | 19340 | 7843 |  |  | 2009-09-08 09:38 | 2009-09-08 09:39 | 1 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111562 | 19341 | 7844 |  |  | 2009-09-08 09:40 | 2009-09-08 09:45 | 5 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111563 | 19342 | 7845 |  |  | 2009-09-08 09:21 | 2009-09-08 09:57 | 36 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111564 | 19343 | 7846 |  |  | 2009-09-08 18:38 | 2009-09-08 20:50 | 132 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111565 | 19344 | 7847 |  |  | 2009-09-09 00:20 | 2009-09-09 01:52 | 92 | E0888 | DE 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111566 | 19345 | 7848 |  |  | 2009-09-09 19:08 | 2009-09-09 19:31 | 23 | E0488 | GT 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111567 | 19346 | 7849 |  |  | 2009-09-10 06:18 | 2009-09-10 06:19 | 1 | E0944 | UL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111568 | 19347 | 7851 |  |  | 2009-09-13 18:27 | 2009-09-13 18:27 | 0 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111569 | 19348 | 7852 |  |  | 2009-09-13 21:55 | 2009-09-13 23:02 | 67 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111570 | 19349 | 7853 |  |  | 2009-09-13 23:07 | 2009-09-14 00:37 | 90 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111571 | 19350 | 7854 |  |  | 2009-09-14 05:44 | 2009-09-14 05:44 | 0 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111572 | 19351 | 7855 |  |  | 2009-09-19 10:23 | 2009-09-19 12:51 | 148 | E0075 | CR 33 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111629 | 19352 | 1522 |  |  | 2009-11-16 12:40 | 2009-11-16 12:40 | 0 | E0274 | PM-AV 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR769 Palmerston-Avoca tripped due to lightning. | FALSE | Non-Critical
111725 | 19355 | 7856 |  |  | 2009-09-22 08:40 | 2009-09-22 09:31 | 51 | E1518 | PL 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111726 | 19360 | 7857 |  |  | 2009-09-22 15:37 | 2009-09-22 19:57 | 260 | E0156 | MB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111727 | 19361 | 7859 |  |  | 2009-09-22 21:56 | 2009-09-22 21:57 | 1 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111728 | 19362 | 7860 |  |  | 2009-09-23 02:55 | 2009-09-23 02:56 | 1 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111729 | 19363 | 7862 |  |  | 2009-09-24 15:02 | 2009-09-24 15:03 | 1 | E0014 | BW 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111730 | 19364 | 7863 |  |  | 2009-09-27 04:14 | 2009-09-27 04:40 | 26 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111731 | 19365 | 7864 |  |  | 2009-09-27 07:14 | 2009-09-27 07:51 | 37 | E0970 | SO 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111732 | 19366 | 7865 |  |  | 2009-09-27 07:34 | 2009-09-27 14:37 | 423 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111733 | 19367 | 7866 |  |  | 2009-09-27 05:38 | 2009-09-27 22:16 | 998 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111734 | 19368 | 7867 |  |  | 2009-09-27 05:44 | 2009-09-27 10:53 | 309 | E0843 | RK 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111735 | 19369 | 7869 |  |  | 2009-09-27 07:53 | 2009-09-27 14:11 | 378 | E0412 | EL 11 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111736 | 19370 | 7870 |  |  | 2009-09-27 07:54 | 2009-09-27 09:59 | 125 | E0638 | ST 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
113288 | 19399 | 1525 |  |  | 2009-11-18 09:40 | 2009-11-18 11:12 | 92 | E0327 | BY 6.6 kV G Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 1601 | TRUE |  | IR781 Boyer Substation - the Boyer T14 110/6.6 kV transformer tripped due to inappropriate protection settings. | FALSE | Undefined
111762 | 19400 | 7871 |  |  | 2009-09-27 08:00 | 2009-09-27 17:19 | 559 | E0464 | KR 11 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111763 | 19401 | 7872 |  |  | 2009-09-27 08:10 | 2009-09-27 08:10 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111764 | 19402 | 7873 |  |  | 2009-09-27 08:12 | 2009-09-27 16:16 | 484 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111765 | 19403 | 7875 |  |  | 2009-09-27 08:38 | 2009-09-27 08:38 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111766 | 19404 | 7876 |  |  | 2009-09-27 08:47 | 2009-09-27 08:47 | 0 | E0865 | RB 44 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111767 | 19405 | 7877 |  |  | 2009-09-27 08:50 | 2009-09-27 08:50 | 0 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111768 | 19406 | 7878 |  |  | 2009-09-27 08:51 | 2009-09-27 16:54 | 483 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111770 | 19408 | 7880 |  |  | 2009-09-27 08:55 | 2009-09-27 08:55 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111771 | 19409 | 7881 |  |  | 2009-09-27 09:05 | 2009-09-27 09:05 | 0 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111772 | 19410 | 7882 |  |  | 2009-09-27 09:05 | 2009-09-27 09:06 | 1 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111773 | 19411 | 7883 |  |  | 2009-09-27 09:19 | 2009-09-27 17:11 | 472 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111774 | 19412 | 7884 |  |  | 2009-09-27 09:23 | 2009-09-27 19:59 | 636 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111775 | 19413 | 7885 |  |  | 2009-09-27 09:25 | 2009-09-27 15:49 | 384 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111776 | 19414 | 7888 |  |  | 2009-09-27 10:38 | 2009-09-27 10:38 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111777 | 19415 | 7889 |  |  | 2009-09-27 10:47 | 2009-09-27 10:48 | 1 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111778 | 19416 | 7891 |  |  | 2009-09-27 10:51 | 2009-09-27 10:51 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111779 | 19417 | 7893 |  |  | 2009-09-27 11:10 | 2009-09-27 16:15 | 305 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111780 | 19418 | 7894 |  |  | 2009-09-27 11:12 | 2009-09-27 11:12 | 0 | E0639 | ST 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111781 | 19419 | 7895 |  |  | 2009-09-27 11:13 | 2009-09-27 11:13 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111793 | 19421 | 7890 |  |  | 2009-09-27 10:48 | 2009-09-27 11:23 | 35 | E0144 | NN 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111795 | 19423 | 7898 |  |  | 2009-09-27 12:05 | 2009-09-27 12:05 | 0 | E0495 | GT 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111796 | 19424 | 7899 |  |  | 2009-09-27 11:31 | 2009-09-27 13:50 | 139 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111797 | 19425 | 7900 |  |  | 2009-09-27 13:58 | 2009-09-27 13:58 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111798 | 19426 | 7901 |  |  | 2009-09-27 08:52 | 2009-09-27 14:04 | 312 | E0462 | KR 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111799 | 19427 | 7909 |  |  | 2009-09-27 17:22 | 2009-09-27 17:22 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111800 | 19428 | 7913 |  |  | 2009-09-27 17:34 | 2009-09-27 17:34 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111801 | 19429 | 7915 |  |  | 2009-09-27 19:54 | 2009-09-27 20:42 | 48 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111802 | 19430 | 7917 |  |  | 2009-09-28 12:01 | 2009-09-28 12:22 | 21 | E0789 | QT 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111803 | 19431 | 7920 |  |  | 2009-09-30 05:43 | 2009-09-30 05:43 | 0 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139425 | 19432 | 7921 |  |  | 2009-09-30 06:57 | 2009-09-30 06:57 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111805 | 19433 | 7922 |  |  | 2009-09-30 12:35 | 2009-09-30 12:35 | 0 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111808 | 19436 | 7925 |  |  | 2009-09-30 12:21 | 2009-09-30 13:01 | 40 | E0836 | RK 11 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111809 | 19437 | 7926 |  |  | 2009-09-30 13:08 | 2009-09-30 13:08 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111810 | 19438 | 7927 |  |  | 2009-09-30 13:09 | 2009-09-30 13:09 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111811 | 19439 | 7928 |  |  | 2009-09-30 13:10 | 2009-09-30 13:44 | 34 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111812 | 19440 | 7929 |  |  | 2009-09-30 14:41 | 2009-09-30 15:11 | 30 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111813 | 19441 | 7930 |  |  | 2009-09-30 17:03 | 2009-09-30 17:03 | 0 | E0643 | ST 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
111814 | 19442 | 7931 |  |  | 2009-09-30 16:58 | 2009-09-30 20:24 | 206 | E0902 | TR 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
202220 | 19507 | 1530 |  |  | 2009-12-01 14:32 | 2009-12-01 14:36 | 4 | E1443 | BB-BE-GT 2 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR795 George Town SS- Bell Bay PS Tee 2 110kV tripped due to unknown cause. | FALSE | Non-Critical
112115 | 19509 | 7934 |  |  | 2009-10-05 16:12 | 2009-10-05 18:09 | 117 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139428 | 19510 | 7935 |  |  | 2009-10-06 05:56 | 2009-10-06 05:56 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112117 | 19511 | 7936 |  |  | 2009-10-08 04:49 | 2009-10-08 04:49 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112118 | 19512 | 7937 |  |  | 2009-10-08 13:47 | 2009-10-08 13:48 | 1 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112119 | 19513 | 7938 |  |  | 2009-10-10 09:31 | 2009-10-10 09:31 | 0 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112120 | 19514 | 7939 |  |  | 2009-10-10 13:51 | 2009-10-10 14:09 | 18 | E1613 | UL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112121 | 19515 | 7940 |  |  | 2009-10-10 23:57 | 2009-10-10 23:57 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112122 | 19516 | 7941 |  |  | 2009-10-11 22:54 | 2009-10-12 00:13 | 79 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112123 | 19517 | 7942 |  |  | 2009-10-12 12:23 | 2009-10-12 12:23 | 0 | E0014 | BW 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139429 | 19518 | 7943 |  |  | 2009-10-13 11:07 | 2009-10-13 12:06 | 59 | E1567 | DP 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139430 | 19519 | 7944 |  |  | 2009-10-15 06:45 | 2009-10-15 07:06 | 21 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112126 | 19520 | 7945 |  |  | 2009-10-15 07:31 | 2009-10-15 07:31 | 0 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139431 | 19521 | 7946 |  |  | 2009-10-15 10:14 | 2009-10-15 10:14 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112128 | 19522 | 7947 |  |  | 2009-10-15 13:01 | 2009-10-15 13:01 | 0 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112168 | 19523 | 7948 |  |  | 2009-10-16 07:28 | 2009-10-16 08:14 | 46 | E0106 | CS 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112488 | 19554 | 7949 |  |  | 2009-10-16 12:51 | 2009-10-16 13:58 | 67 | E0118 | CS 11 kV T2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112489 | 19555 | 7950 |  |  | 2009-10-16 18:04 | 2009-10-16 18:04 | 0 | E1535 | MY 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112490 | 19556 | 7951 |  |  | 2009-10-19 13:45 | 2009-10-19 14:05 | 20 | E0023 | BW 11 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112491 | 19557 | 7952 |  |  | 2009-10-21 13:58 | 2009-10-21 13:58 | 0 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112492 | 19558 | 7953 |  |  | 2009-10-21 21:36 | 2009-10-21 21:36 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112493 | 19559 | 7954 |  |  | 2009-10-21 22:53 | 2009-10-21 22:53 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112494 | 19560 | 7955 |  |  | 2009-10-22 21:04 | 2009-10-22 21:20 | 16 | E1613 | UL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112495 | 19561 | 7956 |  |  | 2009-10-23 05:04 | 2009-10-23 05:04 | 0 | E0948 | UL 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112496 | 19562 | 7957 |  |  | 2009-10-26 14:52 | 2009-10-26 14:53 | 1 | E0643 | ST 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112497 | 19563 | 7958 |  |  | 2009-10-26 21:17 | 2009-10-26 21:17 | 0 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112498 | 19564 | 7959 |  |  | 2009-10-27 00:48 | 2009-10-27 01:09 | 21 | E0820 | RA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112499 | 19565 | 7960 |  |  | 2009-10-27 00:48 | 2009-10-27 01:08 | 20 | E0826 | RA 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112500 | 19566 | 7961 |  |  | 2009-10-28 07:58 | 2009-10-28 07:58 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112501 | 19567 | 7962 |  |  | 2009-10-29 13:24 | 2009-10-29 14:14 | 50 | E0944 | UL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195594 | 19569 | 7963 |  |  | 2009-10-30 09:15 | 2009-10-30 10:03 | 48 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112503 | 19570 | 7964 |  |  | 2009-10-31 16:44 | 2009-10-31 17:18 | 34 | E0760 | NW 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112515 | 19571 | 7965 |  |  | 2009-11-02 00:22 | 2009-11-02 00:22 | 0 | E0764 | NW 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112516 | 19572 | 7966 |  |  | 2009-11-02 06:31 | 2009-11-02 06:31 | 0 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112517 | 19573 | 7967 |  |  | 2009-11-03 10:35 | 2009-11-03 11:04 | 29 | E0760 | NW 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112518 | 19574 | 7968 |  |  | 2009-11-03 12:19 | 2009-11-03 12:19 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112519 | 19575 | 7969 |  |  | 2009-11-03 13:24 | 2009-11-03 13:24 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112520 | 19576 | 7970 |  |  | 2009-11-03 13:40 | 2009-11-03 13:57 | 17 | E0843 | RK 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112521 | 19577 | 7971 |  |  | 2009-11-03 14:28 | 2009-11-03 14:28 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112522 | 19578 | 7972 |  |  | 2009-11-03 15:25 | 2009-11-03 15:25 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112523 | 19579 | 7973 |  |  | 2009-11-03 15:28 | 2009-11-03 16:39 | 71 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112524 | 19580 | 7974 |  |  | 2009-11-04 08:39 | 2009-11-04 08:59 | 20 | E0022 | BW 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112525 | 19581 | 7975 |  |  | 2009-11-04 08:39 | 2009-11-04 08:59 | 20 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112938 | 19618 | 1533 |  |  | 2009-12-17 12:12 | 2009-12-17 12:51 | 39 | E0717 | FA-RC 2 220 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR806 FA-RC 2 tripped , suspect protection intertrip from Hydro. note that the line was available for service at 12:51, see SMELT record. | FALSE | Non-Critical
202223 | 19619 | 1535 |  |  | 2009-12-29 10:20 | 2009-12-29 10:30 | 10 | E0751 | NW 110/22 kV T1 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR 809 Norwood Substation T1 Tripped | FALSE | Non-Critical
112789 | 19620 | 7976 |  |  | 2009-11-05 10:52 | 2009-11-05 11:33 | 41 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112790 | 19621 | 7977 |  |  | 2009-11-08 15:16 | 2009-11-08 16:13 | 57 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112791 | 19622 | 7978 |  |  | 2009-11-08 20:20 | 2009-11-08 20:21 | 1 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112792 | 19623 | 7981 |  |  | 2009-11-12 13:17 | 2009-11-12 14:06 | 49 | E1444 | HA 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112794 | 19625 | 7983 |  |  | 2009-11-16 15:02 | 2009-11-16 15:02 | 0 | E0898 | SD 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112795 | 19626 | 7984 |  |  | 2009-11-16 15:14 | 2009-11-16 15:14 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112796 | 19627 | 7985 |  |  | 2009-11-17 22:08 | 2009-11-17 22:08 | 0 | E0944 | UL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112797 | 19628 | 7986 |  |  | 2009-11-18 09:28 | 2009-11-18 10:38 | 70 | E0084 | CR 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112798 | 19629 | 7987 |  |  | 2009-11-19 07:14 | 2009-11-19 08:11 | 57 | E0448 | KE 11 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112799 | 19630 | 7988 |  |  | 2009-11-19 22:42 | 2009-11-19 22:42 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112800 | 19631 | 7989 |  |  | 2009-11-20 13:05 | 2009-11-20 16:40 | 215 | E0360 | KI 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112801 | 19632 | 7990 |  |  | 2009-11-21 08:08 | 2009-11-21 08:48 | 40 | E1550 | DP 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112802 | 19633 | 7992 |  |  | 2009-11-28 09:48 | 2009-11-28 09:48 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112803 | 19634 | 7993 |  |  | 2009-11-29 13:03 | 2009-11-29 13:21 | 18 | E0489 | GT 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112804 | 19635 | 7994 |  |  | 2009-11-29 13:25 | 2009-11-29 13:25 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112805 | 19636 | 7995 |  |  | 2009-11-30 16:10 | 2009-11-30 16:59 | 49 | E0078 | CR 33 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
112942 | 19637 | 1539 |  |  | 2009-12-30 02:46 | 2009-12-30 02:55 | 9 | E0103 | CS 11 kV D Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 11 | TRUE |  | IR813 Chapel Street 11kV D Busbar tripped. Under investigation. Protection system mal-operation | FALSE | Undefined
112943 | 19638 | 1540 |  |  | 2009-12-31 19:30 | 2009-12-31 19:33 | 3 | E0715 | FA-JB 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR815 FA-JB tripped during adverse weather. | FALSE | Non-Critical
112944 | 19639 | 1541 |  |  | 2009-12-31 20:13 | 2009-12-31 20:13 | 0 | E0539 | SH-FA 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR 814 SH-FA tripped with lightning in area. lightning | FALSE | Critical
120089 | 20043 | 1542 |  |  | 2010-01-16 21:45 | 2010-01-16 21:47 | 2 | E0001 | WA-BW 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR820 WA-BW tripped with lightning in area. | FALSE | Non-Critical
114275 | 20044 | 1543 |  |  | 2010-01-16 20:10 | 2010-01-16 22:39 | 149 | E0951 | WA 110/22 kV T1 Transformer Circuit | Transformer | Fault | Adverse Weather | Transend | Completed | TRUE | 46 | TRUE |  | IR819 WA T1 tripped, suspect lightning. | FALSE | Non-Critical
114298 | 20045 | 7996 |  |  | 2009-12-01 19:33 | 2009-12-01 19:51 | 18 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
114299 | 20046 | 7997 |  |  | 2009-12-03 01:01 | 2009-12-03 01:01 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
114300 | 20047 | 7998 |  |  | 2009-12-03 21:09 | 2009-12-03 21:09 | 0 | E1454 | HA 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
114301 | 20048 | 7999 |  |  | 2009-12-05 07:26 | 2009-12-05 08:32 | 66 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
114302 | 20049 | 8000 |  |  | 2009-12-05 09:18 | 2009-12-05 09:42 | 24 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
114303 | 20050 | 8001 |  |  | 2009-12-06 17:42 | 2009-12-06 18:14 | 32 | E0844 | RK 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
114304 | 20051 | 8002 |  |  | 2009-12-06 21:26 | 2009-12-06 21:26 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
114305 | 20052 | 8003 |  |  | 2009-12-10 01:48 | 2009-12-10 02:03 | 15 | E0835 | RK 11 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
114306 | 20053 | 8004 |  |  | 2009-12-10 08:58 | 2009-12-10 08:58 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139443 | 20132 | 8005 |  |  | 2009-12-11 08:18 | 2009-12-11 08:34 | 16 | E0185 | TU 22 kV X D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
114847 | 20133 | 8006 |  |  | 2009-12-12 06:06 | 2009-12-12 06:26 | 20 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
114848 | 20134 | 8007 |  |  | 2009-12-12 06:32 | 2009-12-12 07:52 | 80 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
114849 | 20135 | 8008 |  |  | 2009-12-12 11:34 | 2009-12-12 12:36 | 62 | E0412 | EL 11 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
114850 | 20136 | 8009 |  |  | 2009-12-12 11:09 | 2009-12-12 13:29 | 140 | E0463 | KR 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
114851 | 20137 | 8010 |  |  | 2009-12-13 04:55 | 2009-12-13 04:55 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
114852 | 20138 | 8011 |  |  | 2009-12-13 06:16 | 2009-12-13 06:37 | 21 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
114853 | 20139 | 8012 |  |  | 2009-12-13 08:29 | 2009-12-13 08:29 | 0 | E0762 | NW 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
114854 | 20140 | 8013 |  |  | 2009-12-13 12:31 | 2009-12-13 12:32 | 1 | E1444 | HA 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
114855 | 20141 | 8014 |  |  | 2009-12-13 18:14 | 2009-12-13 19:05 | 51 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
114899 | 20181 | 1544 |  |  | 2010-01-30 17:36 | 2010-01-31 17:56 | 1460 | E0402 | BU-ST 110 kV Transmission Circuit | Transmission | Fault | Vandalism | Transend | Completed | TRUE | 127 | TRUE |  | IR829 BU-ST trip with loss of supply at Smithton Substation | FALSE | Non-Critical
115172 | 20241 | 8015 |  |  | 2009-12-16 18:02 | 2009-12-16 18:02 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115173 | 20242 | 8016 |  |  | 2009-12-17 06:51 | 2009-12-17 08:19 | 88 | E1051 | SR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115174 | 20243 | 8017 |  |  | 2009-12-18 01:22 | 2009-12-18 01:38 | 16 | E1531 | MY 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115175 | 20244 | 8018 |  |  | 2009-12-18 06:41 | 2009-12-18 07:08 | 27 | E0084 | CR 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115176 | 20245 | 8019 |  |  | 2009-12-18 06:38 | 2009-12-18 07:19 | 41 | E1557 | CR 33 kV Z2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115177 | 20246 | 8020 |  |  | 2009-12-19 00:53 | 2009-12-19 02:37 | 104 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115178 | 20247 | 8021 |  |  | 2009-12-19 10:16 | 2009-12-19 10:16 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115186 | 20248 | 8022 |  |  | 2009-12-20 21:24 | 2009-12-20 21:43 | 19 | E0084 | CR 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115187 | 20249 | 8023 |  |  | 2009-12-22 12:05 | 2009-12-22 12:06 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115188 | 20250 | 8024 |  |  | 2009-12-22 17:37 | 2009-12-22 18:46 | 69 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115189 | 20251 | 8025 |  |  | 2009-12-22 23:15 | 2009-12-22 23:15 | 0 | E0760 | NW 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115190 | 20252 | 8026 |  |  | 2009-12-23 06:04 | 2009-12-23 06:04 | 0 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115191 | 20253 | 8027 |  |  | 2009-12-26 07:39 | 2009-12-26 07:59 | 20 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115192 | 20254 | 8028 |  |  | 2009-12-29 18:36 | 2009-12-29 18:37 | 1 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115193 | 20255 | 8029 |  |  | 2009-12-30 09:02 | 2009-12-30 09:02 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115194 | 20256 | 8030 |  |  | 2009-12-30 15:57 | 2009-12-30 16:58 | 61 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115195 | 20257 | 8031 |  |  | 2009-12-31 20:49 | 2009-12-31 20:50 | 1 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115217 | 20258 | 8032 |  |  | 2009-12-31 20:49 | 2009-12-31 20:50 | 1 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115218 | 20259 | 8033 |  |  | 2009-12-31 21:08 | 2009-12-31 21:08 | 0 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185996 | 20260 | 8034 |  |  | 2009-12-31 21:19 | 2009-12-31 21:19 | 0 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115220 | 20261 | 8035 |  |  | 2009-12-31 20:56 | 2009-12-31 21:52 | 56 | E0015 | BW 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115221 | 20262 | 8036 |  |  | 2009-12-31 21:03 | 2009-12-31 22:00 | 57 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115222 | 20263 | 8037 |  |  | 2009-12-31 21:24 | 2009-12-31 22:15 | 51 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115223 | 20264 | 8038 |  |  | 2009-12-31 22:16 | 2009-12-31 22:16 | 0 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115224 | 20265 | 8039 |  |  | 2009-12-31 22:19 | 2009-12-31 22:19 | 0 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115225 | 20266 | 8040 |  |  | 2009-12-31 20:49 | 2009-12-31 22:52 | 123 | E0105 | CS 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115226 | 20267 | 8041 |  |  | 2009-12-31 20:55 | 2010-01-01 01:12 | 257 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115424 | 20268 | 8042 |  |  | 2010-01-01 08:24 | 2010-01-01 09:18 | 54 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115425 | 20270 | 8044 |  |  | 2010-01-03 04:15 | 2010-01-03 04:15 | 0 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115426 | 20271 | 8045 |  |  | 2010-01-03 20:27 | 2010-01-03 20:27 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115524 | 20359 | 1547 |  |  | 2010-02-10 15:28 | 2010-02-10 15:28 | 0 | E0260 | PM-HA 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR832 Palmerston-Hadspen tripped due to lightning | FALSE | Critical
115759 | 20360 | 1548 |  |  | 2010-02-10 11:17 | 2010-02-10 14:14 | 177 | E1565 | BP-SB-ST 110 kV Transmission Circuit | Transmission | Fault |  | Generator Request | Completed | TRUE | 0 | TRUE |  | IR831 BF-SB-ST 110kV transmission line circuit tripped due to unknown cause. | FALSE | Undefined
115635 | 20361 | 8046 |  |  | 2010-01-04 01:08 | 2010-01-04 03:23 | 135 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115760 | 20362 | 8047 |  |  | 2010-01-05 22:31 | 2010-01-05 22:31 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115637 | 20363 | 8048 |  |  | 2010-01-06 16:12 | 2010-01-06 16:13 | 1 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115638 | 20364 | 8051 |  |  | 2010-01-07 06:19 | 2010-01-07 06:19 | 0 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115639 | 20365 | 8052 |  |  | 2010-01-07 09:56 | 2010-01-07 09:56 | 0 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115640 | 20366 | 8053 |  |  | 2010-01-08 20:38 | 2010-01-08 21:29 | 51 | E1538 | MY 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115641 | 20367 | 8054 |  |  | 2010-01-08 23:19 | 2010-01-08 23:19 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115642 | 20368 | 8055 |  |  | 2010-01-09 02:29 | 2010-01-09 02:29 | 0 | E0300 | AV 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115643 | 20369 | 8056 |  |  | 2010-01-10 08:47 | 2010-01-10 08:47 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115644 | 20370 | 8057 |  |  | 2010-01-11 13:21 | 2010-01-11 14:06 | 45 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115645 | 20371 | 8058 |  |  | 2010-01-12 10:01 | 2010-01-12 10:29 | 28 | E1481 | RI 33 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115646 | 20372 | 8059 |  |  | 2010-01-14 01:31 | 2010-01-14 02:23 | 52 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115647 | 20373 | 8060 |  |  | 2010-01-14 07:56 | 2010-01-14 12:41 | 285 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115648 | 20374 | 8063 |  |  | 2010-01-14 22:39 | 2010-01-14 22:39 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115748 | 20447 | 8064 |  |  | 2010-01-15 10:38 | 2010-01-15 10:38 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115749 | 20448 | 8065 |  |  | 2010-01-15 15:53 | 2010-01-15 16:10 | 17 | E0488 | GT 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115750 | 20449 | 8066 |  |  | 2010-01-16 04:14 | 2010-01-16 12:16 | 482 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115751 | 20450 | 8067 |  |  | 2010-01-16 04:14 | 2010-01-16 12:16 | 482 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115752 | 20451 | 8068 |  |  | 2010-01-16 19:12 | 2010-01-16 19:12 | 0 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115753 | 20452 | 8069 |  |  | 2010-01-22 05:14 | 2010-01-22 05:42 | 28 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115754 | 20453 | 8070 |  |  | 2010-01-22 20:51 | 2010-01-22 20:51 | 0 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115755 | 20455 | 8072 |  |  | 2010-01-25 06:58 | 2010-01-25 06:59 | 1 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115756 | 20456 | 8073 |  |  | 2010-01-26 06:40 | 2010-01-26 06:41 | 1 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115757 | 20457 | 8074 |  |  | 2010-01-27 02:41 | 2010-01-27 02:41 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
115935 | 20492 | 1549 |  |  | 2010-03-12 08:19 | 2010-03-12 10:46 | 147 | E0516 | SH-GT 2 220 kV Transmission Circuit | Transmission | Fault | Communication Failure | Transend | Completed | TRUE | 0 | TRUE |  | IR849 SH-GT 2 220 kV tripped | FALSE | Critical
116470 | 20622 | 1550 |  |  | 2010-03-23 09:32 | 2010-03-23 10:00 | 28 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Basslink | Basslink | Completed | TRUE | 0 | TRUE |  | IR850 Basslink tripped due to SPS operation for system security | FALSE | Undefined
116471 | 20623 | 1552 |  |  | 2010-03-23 10:47 | 2010-03-23 11:27 | 40 | E0267 | PO-PM 5 220 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR851 PO-PM 5 transmission circuit tripped following an intertrip from the generator | FALSE | Non-Critical
116472 | 20624 | 1553 |  |  | 2010-03-24 08:27 | 2010-03-24 09:36 | 69 | E0372 | KI 110 kV B Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR860 Kingston 110kV B Bus tripped | FALSE | Undefined
116473 | 20625 | 1554 |  |  | 2010-03-26 14:29 | 2010-03-26 14:39 | 10 | E1443 | BB-BE-GT 2 110 kV Transmission Circuit | Transmission | Fault | Generator | Transend | Completed | TRUE | 0 | TRUE |  | IR861 BB-BE-GT 2 tripped following the opening of a disconnector at Bell Bay 3 | FALSE | Non-Critical
120093 | 20626 | 1556 |  |  | 2010-03-31 06:20 | 2010-03-31 06:20 | 0 | E0274 | PM-AV 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR864 Palmerston-Avoca 110kV transmission circuit tripped and auto reclosed. | FALSE | Non-Critical
116991 | 20683 | 8076 |  |  | 2010-01-28 16:12 | 2010-01-28 16:46 | 34 | E0111 | CS 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
116992 | 20684 | 8077 |  |  | 2010-01-29 06:28 | 2010-01-29 06:47 | 19 | E0078 | CR 33 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124059 | 20685 | 8078 |  |  | 2010-01-29 23:00 | 2010-01-29 23:01 | 1 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124060 | 20686 | 8079 |  |  | 2010-01-30 17:36 | 2010-01-30 17:55 | 19 | E0640 | ST 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124061 | 20687 | 8080 |  |  | 2010-01-30 17:36 | 2010-01-30 17:56 | 20 | E0638 | ST 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124062 | 20688 | 8082 |  |  | 2010-02-01 06:53 | 2010-02-01 08:37 | 104 | E1480 | RI 33 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124063 | 20689 | 8083 |  |  | 2010-02-01 22:55 | 2010-02-01 23:17 | 22 | E0122 | CS 11 kV X2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124064 | 20691 | 8086 |  |  | 2010-02-03 07:29 | 2010-02-03 08:56 | 87 | E1480 | RI 33 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124065 | 20692 | 8087 |  |  | 2010-02-03 09:26 | 2010-02-03 09:27 | 1 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124066 | 20693 | 8089 |  |  | 2010-02-04 04:50 | 2010-02-04 04:51 | 1 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124067 | 20694 | 8090 |  |  | 2010-02-04 15:39 | 2010-02-04 15:40 | 1 | E0462 | KR 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124068 | 20695 | 8091 |  |  | 2010-02-04 17:57 | 2010-02-04 17:58 | 1 | E0389 | BU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124069 | 20696 | 8092 |  |  | 2010-02-04 18:50 | 2010-02-04 18:51 | 1 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124070 | 20697 | 8093 |  |  | 2010-02-04 18:50 | 2010-02-04 18:51 | 1 | E0389 | BU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124071 | 20698 | 8094 |  |  | 2010-02-04 23:16 | 2010-02-05 00:24 | 68 | E1570 | DP 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124072 | 20699 | 8095 |  |  | 2010-02-05 00:55 | 2010-02-05 01:27 | 32 | E1570 | DP 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124073 | 20700 | 8096 |  |  | 2010-02-06 02:15 | 2010-02-06 02:16 | 1 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124074 | 20701 | 8098 |  |  | 2010-02-06 06:27 | 2010-02-06 06:28 | 1 | E1042 | SD 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124075 | 20702 | 8099 |  |  | 2010-02-06 10:32 | 2010-02-06 11:26 | 54 | E0915 | TR 22 kV V2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124076 | 20703 | 8100 |  |  | 2010-02-06 10:31 | 2010-02-06 12:05 | 94 | E0913 | TR 22 kV U2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124077 | 20704 | 8101 |  |  | 2010-02-06 20:12 | 2010-02-06 20:13 | 1 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124078 | 20705 | 8102 |  |  | 2010-02-07 14:28 | 2010-02-07 14:29 | 1 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124079 | 20706 | 8103 |  |  | 2010-02-08 06:28 | 2010-02-08 06:29 | 1 | E1612 | UL 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124080 | 20707 | 8104 |  |  | 2010-02-09 01:13 | 2010-02-09 01:14 | 1 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124081 | 20708 | 8105 |  |  | 2010-02-09 15:39 | 2010-02-09 15:55 | 16 | E0909 | TR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124082 | 20709 | 8106 |  |  | 2010-02-09 16:00 | 2010-02-09 16:01 | 1 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124083 | 20710 | 8107 |  |  | 2010-02-11 07:43 | 2010-02-11 08:00 | 17 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124084 | 20711 | 8108 |  |  | 2010-02-11 07:55 | 2010-02-11 08:10 | 15 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
117491 | 20713 | 1557 |  |  | 2010-04-08 12:28 | 2010-04-08 13:03 | 35 | E0372 | KI 110 kV B Bus | Bus | Fault | Mechanical Failure | Transend | Completed | TRUE | 0 | TRUE |  | IR873 Kingston 110 kV B Bus tripped. Buchholz protection relay | FALSE | Undefined
124085 | 20714 | 8119 |  |  | 2010-02-11 08:57 | 2010-02-11 08:58 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124086 | 20715 | 8111 |  |  | 2010-02-11 14:29 | 2010-02-11 16:12 | 103 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124087 | 20716 | 8112 |  |  | 2010-02-11 16:43 | 2010-02-11 16:44 | 1 | E1437 | HA 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124088 | 20717 | 8113 |  |  | 2010-02-12 21:24 | 2010-02-12 21:25 | 1 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124089 | 20718 | 8114 |  |  | 2010-02-13 00:36 | 2010-02-13 00:37 | 1 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124090 | 20719 | 8115 |  |  | 2010-02-13 01:32 | 2010-02-13 01:33 | 1 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124091 | 20720 | 8116 |  |  | 2010-02-13 11:28 | 2010-02-13 11:29 | 1 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
117044 | 20721 | 1558 |  |  | 2010-04-08 12:39 | 2010-04-08 16:33 | 234 | E0587 | UL-EB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR874Ulverstone-Emu Bay 110kV transmission circuit tripped. | FALSE | Non-Critical
124092 | 20722 | 8117 |  |  | 2010-02-13 11:49 | 2010-02-13 12:25 | 36 | E0016 | BW 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124093 | 20723 | 8118 |  |  | 2010-02-13 12:40 | 2010-02-13 12:45 | 5 | E0016 | BW 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124094 | 20724 | 8119 |  |  | 2010-02-13 13:13 | 2010-02-13 13:14 | 1 | E0016 | BW 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124095 | 20725 | 8120 |  |  | 2010-02-13 21:19 | 2010-02-13 22:11 | 52 | E0353 | LF 33 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124096 | 20726 | 8121 |  |  | 2010-02-14 00:30 | 2010-02-14 00:31 | 1 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124097 | 20727 | 8122 |  |  | 2010-02-14 09:10 | 2010-02-14 09:11 | 1 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124098 | 20728 | 8123 |  |  | 2010-02-14 12:48 | 2010-02-14 12:49 | 1 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124099 | 20729 | 8124 |  |  | 2010-02-14 12:48 | 2010-02-14 13:08 | 20 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124100 | 20730 | 8125 |  |  | 2010-02-14 18:27 | 2010-02-14 19:50 | 83 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124101 | 20731 | 8126 |  |  | 2010-02-15 07:02 | 2010-02-15 07:03 | 1 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139102 | 20732 | 8127 |  |  | 2010-02-15 23:59 | 2010-02-16 | 1 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124103 | 20733 | 8128 |  |  | 2010-02-16 07:18 | 2010-02-16 07:48 | 30 | E1518 | PL 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124104 | 20734 | 8129 |  |  | 2010-02-16 06:20 | 2010-02-16 06:42 | 22 | E1518 | PL 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124105 | 20735 | 8130 |  |  | 2010-02-16 12:12 | 2010-02-16 13:07 | 55 | E0022 | BW 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124106 | 20736 | 8131 |  |  | 2010-02-17 07:56 | 2010-02-17 07:57 | 1 | E1548 | DP 22 kV C2 Capacitor Circuit | Capacitor | Fault |  | DNSP | Completed | FALSE | 0 | TRUE |  |  | FALSE | Undefined
124107 | 20737 | 8132 |  |  | 2010-02-17 16:24 | 2010-02-17 16:29 | 5 | E0779 | PL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124108 | 20738 | 8135 |  |  | 2010-02-18 06:56 | 2010-02-18 07:01 | 5 | E0779 | PL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124109 | 20739 | 8136 |  |  | 2010-02-18 08:58 | 2010-02-18 09:15 | 17 | E0643 | ST 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124110 | 20740 | 8137 |  |  | 2010-02-19 01:12 | 2010-02-19 01:13 | 1 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124111 | 20741 | 8138 |  |  | 2010-02-19 02:40 | 2010-02-19 02:41 | 1 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124112 | 20742 | 8139 |  |  | 2010-02-19 06:57 | 2010-02-19 06:58 | 1 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124113 | 20743 | 8140 |  |  | 2010-02-19 22:56 | 2010-02-19 22:57 | 1 | E0145 | NN 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124114 | 20744 | 8141 |  |  | 2010-02-20 10:21 | 2010-02-20 11:34 | 73 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186001 | 20745 | 8142 |  |  | 2010-02-20 21:36 | 2010-02-21 02:09 | 273 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124116 | 20746 | 8144 |  |  | 2010-02-22 02:59 | 2010-02-22 03:00 | 1 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
117118 | 20747 | 1560 |  |  | 2010-04-15 15:00 | 2010-04-15 15:42 | 42 | E1067 | SR 22 kV F2 Feeder Circuit | Feeder | Fault | Unknown | MI | Completed | TRUE | 0 | TRUE |  | IR875 Savage River Substation 22kV Feeder F252 tripped | FALSE | Undefined
117119 | 20748 | 1561 |  |  | 2010-04-16 07:33 | 2010-04-17 15:35 | 1922 | E1067 | SR 22 kV F2 Feeder Circuit | Feeder | Fault | Mechanical Failure | MI | Completed | TRUE | 0 | TRUE |  | IR876 Feeder F252 at Savage River Substation tripped due to conductor on ground. | FALSE | Undefined
120094 | 20811 | 1564 |  |  | 2010-04-17 14:35 | 2010-04-17 16:51 | 136 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Basslink | Basslink | Completed | TRUE | 0 | TRUE |  | IR877 George Town-George Town Converter 220kV tripped due to equipment failure at the converter station. | FALSE | Undefined
117413 | 20812 | 1565 |  |  | 2010-04-18 17:33 | 2010-04-18 17:33 | 0 | E0972 | CS-KI-EL 110 kV Transmission Circuit (Changed to E1956) | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR878 Chapel St-kingston-Electrona 110kV transmission circuit tripped. | FALSE | Non-Critical
117414 | 20813 | 1566 |  |  | 2010-04-20 09:15 | 2010-04-20 09:15 | 0 | E0406 | FA-QU-SR-HM 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR880 Farrell-Ques-savage River-Hampshire 110kV transmission ciruit tripped and reclosed. | FALSE | Non-Critical
117415 | 20814 | 1568 |  |  | 2010-04-21 03:41 | 2010-04-21 03:41 | 0 | E0554 | SH-WV 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR881 Sheffield-Wesley Vale 110kV transmission circuit tripped. | FALSE | Non-Critical
117492 | 20815 | 1570 |  |  | 2010-04-21 04:57 | 2010-04-21 04:57 | 0 | E0437 | HA-GT 1 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR882 Hadspen-George Town 220kV transmission line circuit tripped and auto reclosed. | FALSE | Critical
117634 | 20816 | 1572 |  |  | 2010-04-26 12:55 | 2010-04-26 18:11 | 316 | E0894 | SD 22 kV A Bus Circuit | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR886 Scottsdale 22kV A bus tripped during protection work. | FALSE | Undefined
124118 | 20856 | 8145 |  |  | 2010-02-23 01:03 | 2010-02-23 01:04 | 1 | E1554 | DP 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124119 | 20857 | 8146 |  |  | 2010-02-23 09:50 | 2010-02-23 10:13 | 23 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124120 | 20858 | 8147 |  |  | 2010-02-23 08:04 | 2010-02-23 10:15 | 131 | E1004 | BU 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139104 | 20859 | 8148 |  |  | 2010-02-23 16:37 | 2010-02-23 16:38 | 1 | E1567 | DP 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
117943 | 20900 | 1580 |  |  | 2010-04-29 14:50 | 2010-04-29 15:10 | 20 | E0700 | FA 220 kV A Bus | Bus | Fault | Internal Fault | Transend | Completed | TRUE | 5524 | TRUE |  | IR903 Farrell 220 kV A Bus tripped during commissioning work causing loss of supply and generation on the West Coast and load shedding of major industrials. The event was caused by mal-operation of an obsolete protection system. | FALSE | Undefined
123972 | 20901 | 1584 |  |  | 2010-04-30 14:02 | 2010-04-30 14:37 | 35 | E0210 | RI 110/11 kV T1 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR904 Risdon 110/11 kV T1 tripped during testing. | FALSE | Non-Critical
124122 | 20902 | 8149 |  |  | 2010-02-23 14:06 | 2010-02-23 16:39 | 153 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124123 | 20903 | 8151 |  |  | 2010-02-23 18:00 | 2010-02-23 18:01 | 1 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124124 | 20904 | 8152 |  |  | 2010-02-24 02:31 | 2010-02-24 03:22 | 51 | E1518 | PL 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124125 | 20905 | 8153 |  |  | 2010-02-24 02:31 | 2010-02-24 03:23 | 52 | E0779 | PL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124126 | 20906 | 8154 |  |  | 2010-02-24 05:38 | 2010-02-24 05:39 | 1 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124127 | 20907 | 8155 |  |  | 2010-02-24 22:59 | 2010-02-24 23:00 | 1 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124128 | 20908 | 8156 |  |  | 2010-02-25 08:37 | 2010-02-25 08:38 | 1 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124129 | 20909 | 8157 |  |  | 2010-02-26 06:01 | 2010-02-26 06:02 | 1 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124130 | 20910 | 8158 |  |  | 2010-02-26 17:00 | 2010-02-26 17:01 | 1 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124131 | 20911 | 8159 |  |  | 2010-02-27 00:17 | 2010-02-27 00:18 | 1 | E0197 | SO 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124132 | 20912 | 8160 |  |  | 2010-02-27 06:04 | 2010-02-27 06:05 | 1 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault | Vegetation | DNSP | Completed | TRUE | 0 | TRUE |  | IR878 Chapel Street-Kingston-Electrona 110kV transmission circuit tripped & auto-reclosed | FALSE | Undefined
124133 | 20913 | 8162 |  |  | 2010-02-27 06:04 | 2010-02-27 06:22 | 18 | E0496 | GT 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124134 | 20914 | 8163 |  |  | 2010-02-27 23:30 | 2010-02-27 23:51 | 21 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124135 | 20915 | 8164 |  |  | 2010-02-28 03:31 | 2010-02-28 03:42 | 11 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124136 | 20916 | 8165 |  |  | 2010-02-28 04:17 | 2010-02-28 04:18 | 1 | E0760 | NW 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186004 | 20917 | 8166 |  |  | 2010-02-28 14:24 | 2010-02-28 16:44 | 140 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124138 | 20918 | 8167 |  |  | 2010-02-28 21:15 | 2010-02-28 21:16 | 1 | E0917 | TR 22 kV X2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186005 | 20919 | 8168 |  |  | 2010-02-28 17:57 | 2010-02-28 17:58 | 1 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186006 | 20920 | 8169 |  |  | 2010-02-28 17:59 | 2010-03-01 00:23 | 384 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124141 | 20922 | 8171 |  |  | 2010-03-02 23:15 | 2010-03-03 00:29 | 74 | E0746 | NH 11 kV R2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124142 | 20923 | 8172 |  |  | 2010-03-04 00:16 | 2010-03-04 00:32 | 16 | E1548 | DP 22 kV C2 Capacitor Circuit | Capacitor | Fault |  | DNSP | Completed | FALSE | 0 | TRUE |  |  | FALSE | Undefined
139105 | 20924 | 8173 |  |  | 2010-03-04 18:43 | 2010-03-04 18:44 | 1 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
118239 | 20925 | 1586 |  |  | 2010-05-10 22:24 | 2010-05-10 22:36 | 12 | E0540 | SH-FI 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR908 Sheffield-Fisher 220 kV transmission circuit tripped. Lightning in area. | FALSE | Non-Critical
118240 | 20926 | 1588 |  |  | 2010-05-10 23:40 | 2010-05-10 23:40 | 0 | E0259 | PM-HA 1 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR914- Palmerston-Hadspen 1 220 kV transmission circuit tripped and automatically reclosed. | FALSE | Critical
124144 | 20978 | 8174 |  |  | 2010-03-04 23:07 | 2010-03-04 23:08 | 1 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139106 | 20979 | 8175 |  |  | 2010-03-05 23:37 | 2010-03-05 23:38 | 1 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186007 | 20980 | 8176 |  |  | 2010-03-06 04:18 | 2010-03-06 08:49 | 271 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124147 | 20981 | 8178 |  |  | 2010-03-06 11:21 | 2010-03-06 11:22 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124148 | 20982 | 8179 |  |  | 2010-03-06 23:08 | 2010-03-06 23:09 | 1 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124149 | 20983 | 8180 |  |  | 2010-03-07 11:13 | 2010-03-07 11:14 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186008 | 20984 | 8181 |  |  | 2010-03-08 01:04 | 2010-03-08 10:38 | 574 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124151 | 20985 | 8182 |  |  | 2010-03-08 05:07 | 2010-03-08 05:07 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124152 | 20987 | 8185 |  |  | 2010-03-09 18:34 | 2010-03-09 20:15 | 101 | E0019 | BW 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139107 | 20988 | 8186 |  |  | 2010-03-10 01:32 | 2010-03-10 01:33 | 1 | E1568 | DP 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124154 | 20989 | 8187 |  |  | 2010-03-10 22:47 | 2010-03-10 22:48 | 1 | E0638 | ST 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124155 | 20990 | 8188 |  |  | 2010-03-10 23:08 | 2010-03-10 23:29 | 21 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139108 | 20991 | 8189 |  |  | 2010-03-10 22:49 | 2010-03-10 23:37 | 48 | E1567 | DP 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124157 | 20992 | 8190 |  |  | 2010-03-14 19:43 | 2010-03-14 19:44 | 1 | E0789 | QT 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124158 | 20994 | 8191 |  |  | 2010-03-14 19:59 | 2010-03-14 20:00 | 1 | E0819 | RA 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124159 | 20995 | 8192 |  |  | 2010-03-15 00:57 | 2010-03-15 00:58 | 1 | E0825 | RA 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124160 | 20996 | 8193 |  |  | 2010-03-16 07:00 | 2010-03-16 07:23 | 23 | E1535 | MY 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124161 | 20997 | 8194 |  |  | 2010-03-16 23:04 | 2010-03-16 23:28 | 24 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124162 | 20998 | 8195 |  |  | 2010-03-17 21:00 | 2010-03-17 21:01 | 1 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186009 | 20999 | 8197 |  |  | 2010-03-18 22:55 | 2010-03-19 09:23 | 628 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124164 | 21000 | 8199 |  |  | 2010-03-21 10:31 | 2010-03-21 10:32 | 1 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186010 | 21001 | 8200 |  |  | 2010-03-21 02:24 | 2010-03-21 11:11 | 527 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124166 | 21002 | 8201 |  |  | 2010-03-21 14:56 | 2010-03-21 15:26 | 30 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124167 | 21004 | 8202 |  |  | 2010-03-21 22:00 | 2010-03-21 22:01 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124168 | 21005 | 8203 |  |  | 2010-03-21 23:46 | 2010-03-22 00:03 | 17 | E1481 | RI 33 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124169 | 21006 | 8204 |  |  | 2010-03-22 | 2010-03-22 00:01 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124170 | 21007 | 8205 |  |  | 2010-03-22 01:40 | 2010-03-22 01:41 | 1 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124171 | 21008 | 8206 |  |  | 2010-03-23 05:02 | 2010-03-23 05:26 | 24 | E1557 | CR 33 kV Z2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124172 | 21009 | 8207 |  |  | 2010-03-24 03:43 | 2010-03-24 05:03 | 80 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124173 | 21010 | 8202 |  |  | 2010-03-24 05:27 | 2010-03-24 06:14 | 47 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124174 | 21011 | 8201 |  |  | 2010-03-25 11:13 | 2010-03-25 11:14 | 1 | E1444 | HA 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124175 | 21012 | 8211 |  |  | 2010-03-26 13:22 | 2010-03-26 13:23 | 1 | E1437 | HA 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124176 | 21013 | 8212 |  |  | 2010-03-28 16:43 | 2010-03-28 16:44 | 1 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139109 | 21014 | 8214 |  |  | 2010-03-28 21:09 | 2010-03-28 21:10 | 1 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139110 | 21015 | 8215 |  |  | 2010-03-28 21:23 | 2010-03-28 21:24 | 1 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124179 | 21018 | 8216 |  |  | 2010-03-28 21:14 | 2010-03-28 21:44 | 30 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186011 | 21019 | 8217 |  |  | 2010-03-28 16:28 | 2010-03-28 23:28 | 420 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124181 | 21020 | 8218 |  |  | 2010-03-28 23:25 | 2010-03-29 01:02 | 97 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139111 | 21021 | 8219 |  |  | 2010-03-29 01:27 | 2010-03-29 01:28 | 1 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
120510 | 21022 | 8220 |  |  | 2010-03-28 23:07 | 2010-03-29 01:38 | 151 | E0118 | CS 11 kV T2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124183 | 21023 | 8221 |  |  | 2010-03-29 22:48 | 2010-03-30 02:08 | 200 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124184 | 21024 | 8224 |  |  | 2010-03-31 08:10 | 2010-03-31 09:05 | 55 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124185 | 21025 | 8225 |  |  | 2010-03-31 09:25 | 2010-03-31 09:26 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124186 | 21026 | 8226 |  |  | 2010-04-01 23:32 | 2010-04-01 23:57 | 25 | E0489 | GT 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124187 | 21027 | 8227 |  |  | 2010-04-02 08:58 | 2010-04-02 08:59 | 1 | E0869 | RB 44 kV E4 Circuit Breaker | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124188 | 21028 | 8228 |  |  | 2010-04-05 01:06 | 2010-04-05 01:07 | 1 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124189 | 21029 | 8229 |  |  | 2010-04-05 16:59 | 2010-04-05 17:00 | 1 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124190 | 21030 | 8230 |  |  | 2010-04-05 23:02 | 2010-04-05 23:03 | 1 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
122656 | 21031 | 8231 |  |  | 2010-04-06 06:18 | 2010-04-06 06:19 | 1 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186012 | 21032 | 8232 |  |  | 2010-04-07 13:30 | 2010-04-07 16:44 | 194 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186013 | 21033 | 8233 |  |  | 2010-04-07 20:48 | 2010-04-07 20:49 | 1 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186014 | 21034 | 8234 |  |  | 2010-04-07 21:26 | 2010-04-08 15:39 | 1093 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124191 | 21035 | 8236 |  |  | 2010-04-09 13:39 | 2010-04-09 13:40 | 1 | E1041 | SD 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124192 | 21036 | 8237 |  |  | 2010-04-09 22:22 | 2010-04-09 22:23 | 1 | E0762 | NW 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124193 | 21037 | 8238 |  |  | 2010-04-10 19:52 | 2010-04-10 19:53 | 1 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186015 | 21038 | 8239 |  |  | 2010-04-12 03:31 | 2010-04-12 03:32 | 1 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124194 | 21039 | 8240 |  |  | 2010-04-12 19:43 | 2010-04-12 19:44 | 1 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124195 | 21040 | 8241 |  |  | 2010-04-14 09:11 | 2010-04-14 10:51 | 100 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
123943 | 21041 | 8242 |  |  | 2010-04-14 22:22 | 2010-04-14 22:23 | 1 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  | TEST with change of fates from 2010 to 2013 | FALSE | Undefined
124196 | 21042 | 8243 |  |  | 2010-04-14 22:30 | 2010-04-14 23:35 | 65 | E1530 | MY 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
119342 | 21090 | 1593 |  |  | 2010-05-17 13:53 | 2010-05-17 14:00 | 7 | E1734 | GT-TV 3 220 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR916 George Town-Tamar Valley 3 tripped during protection testing at Tamar Valley Power Station. | FALSE | Undefined
119343 | 21091 | 1594 |  |  | 2010-05-18 13:36 | 2010-05-18 14:54 | 78 | E0487 | GT 22 kV B Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 514 | TRUE |  | IR917 George Town Substation - the George Town 22kV B Bus tripped during planned work due to incorrect protection isolation. | FALSE | Undefined
120495 | 21138 | 1590 |  |  | 2010-05-12 09:10 | 2010-05-12 09:51 | 41 | E0470 | KR 110/11 kV T1 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 326 | TRUE |  | IR910 Knights Road Substation - the Knights Road 11 kV A Bus tripped during planned work due to incorrect protection settings. | FALSE | Non-Critical
121556 | 21232 | 1596 |  |  | 2010-06-19 08:26 | 2010-06-19 10:24 | 118 | E1734 | GT-TV 3 220 kV Transmission Circuit | Transmission | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR 943 George Town Substation GT-TV3 tripped GT-Tamar Valley No 3 220kV circuit disconnection occurred after the Operator inadvertently removed fuses for VT A797. It resulted in loss of generation at AETV Power Station. Generator Contingency Scheme was initiated and sent a trip signal toTEMCO with approximately 100MW load was interrupted as part of GCS scheme | FALSE | Undefined
142961 | 21270 | 1597 |  |  | 2010-06-26 17:25 | 2010-06-27 10:09 | 1004 | E0169 | TU-BG-DB 110 kV Transmission Circuit | Transmission | Fault | Mechanical Failure | Transend | Completed | TRUE | 120 | TRUE |  | IR945 TU-BG-DB 110kV tripped, possibly due to conductor failure. Conductor failure between towers T46-T47 | FALSE | Non-Critical
122491 | 21403 | 1602 |  |  | 2010-07-22 07:08 | 2010-07-22 08:11 | 63 | E0211 | RI 110/11 kV T2 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR961 Risdon T1, T2 and T3 tripped due to protection maloperation with loss of supply to NyrStar | FALSE | Non-Critical
122492 | 21403 | 1602 |  |  | 2010-07-22 07:03 | 2010-07-22 09:03 | 120 | E0212 | RI 110/11 kV T3 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR961 Risdon T1, T2 and T3 tripped due to protection maloperation with loss of supply to NyrStar | FALSE | Non-Critical
123085 | 21403 | 1602 |  |  | 2010-07-22 07:03 | 2010-07-22 09:02 | 119 | E0210 | RI 110/11 kV T1 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 2051 | TRUE |  | IR961 Risdon T1, T2 and T3 tripped due to protection maloperation with loss of supply to NyrStar | FALSE | Non-Critical
122362 | 21404 | 1595 |  |  | 2010-06-01 13:13 | 2010-06-01 13:14 | 1 | E1442 | BB-BE-GT 1 110 kV Transmission Circuit | Transmission | Fault | Generator | Transend | Completed | TRUE | 0 | TRUE |  | IR927 Bell Bay 3 -George Town transmission circuit tripped. | FALSE | Non-Critical
122493 | 21405 | 1607 |  |  | 2010-07-28 10:50 | 2010-07-28 10:59 | 9 | E0228 | RI 11 kV A Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 847 | TRUE |  | IR963 Risdon 11kV Bus Bar tripped during protection remediation work | FALSE | Undefined
124202 | 21548 | 8245 |  |  | 2010-04-22 17:48 | 2010-04-22 17:49 | 1 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124203 | 21549 | 8247 |  |  | 2010-04-20 17:48 | 2010-04-20 19:20 | 92 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124204 | 21550 | 8249 |  |  | 2010-04-21 02:21 | 2010-04-21 02:22 | 1 | E0826 | RA 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124205 | 21551 | 8250 |  |  | 2010-04-21 03:41 | 2010-04-21 03:42 | 1 | E1554 | DP 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124206 | 21552 | 8251 |  |  | 2010-04-21 04:46 | 2010-04-21 04:47 | 1 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124207 | 21553 | 8253 |  |  | 2010-04-21 04:56 | 2010-04-21 04:57 | 1 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124208 | 21554 | 8254 |  |  | 2010-04-21 04:58 | 2010-04-21 05:23 | 25 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124209 | 21555 | 8255 |  |  | 2010-04-21 05:25 | 2010-04-21 06:06 | 41 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124210 | 21556 | 8256 |  |  | 2010-04-21 05:17 | 2010-04-21 06:22 | 65 | E1529 | MY 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124211 | 21557 | 8258 |  |  | 2010-04-21 13:41 | 2010-04-21 13:42 | 1 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124212 | 21558 | 8259 |  |  | 2010-04-21 13:45 | 2010-04-21 13:57 | 12 | E0760 | NW 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124213 | 21559 | 8260 |  |  | 2010-04-21 15:36 | 2010-04-21 15:38 | 2 | E1554 | DP 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124214 | 21560 | 8261 |  |  | 2010-04-21 22:19 | 2010-04-21 22:20 | 1 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124215 | 21561 | 8262 |  |  | 2010-04-22 02:30 | 2010-04-22 02:31 | 1 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124216 | 21562 | 8263 |  |  | 2010-04-22 04:05 | 2010-04-22 04:06 | 1 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124217 | 21563 | 8264 |  |  | 2010-04-22 04:22 | 2010-04-22 05:57 | 95 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124218 | 21564 | 8266 |  |  | 2010-04-22 06:15 | 2010-04-22 06:32 | 17 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124219 | 21565 | 8267 |  |  | 2010-04-23 02:24 | 2010-04-23 02:25 | 1 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124220 | 21566 | 8268 |  |  | 2010-04-23 03:26 | 2010-04-23 03:37 | 11 | E0902 | TR 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124663 | 21567 | 8269 |  |  | 2010-04-23 03:38 | 2010-04-23 07:15 | 217 | E0902 | TR 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124222 | 21568 | 8271 |  |  | 2010-04-23 16:26 | 2010-04-23 18:10 | 104 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124223 | 21569 | 8272 |  |  | 2010-04-24 10:31 | 2010-04-24 10:32 | 1 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124224 | 21570 | 8273 |  |  | 2010-04-24 14:22 | 2010-04-24 14:23 | 1 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124225 | 21571 | 8274 |  |  | 2010-04-24 15:28 | 2010-04-24 15:29 | 1 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124366 | 21573 | 8275 |  |  | 2010-04-26 07:59 | 2010-04-26 08:00 | 1 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124367 | 21574 | 8276 |  |  | 2010-04-28 10:51 | 2010-04-28 10:52 | 1 | E0826 | RA 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124368 | 21575 | 8277 |  |  | 2010-04-28 11:31 | 2010-04-28 11:32 | 1 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124369 | 21576 | 8280 |  |  | 2010-04-28 13:20 | 2010-04-28 13:21 | 1 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124370 | 21577 | 8279 |  |  | 2010-04-28 11:31 | 2010-04-28 13:23 | 112 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124371 | 21578 | 8278 |  |  | 2010-04-28 11:31 | 2010-04-28 16:19 | 288 | E0496 | GT 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124372 | 21579 | 8283 |  |  | 2010-04-28 14:56 | 2010-04-28 17:03 | 127 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124373 | 21580 | 8285 |  |  | 2010-04-29 12:17 | 2010-04-29 12:18 | 1 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139116 | 21581 | 8288 |  |  | 2010-05-02 14:21 | 2010-05-02 14:22 | 1 | E1567 | DP 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124375 | 21582 | 1609 |  |  | 2010-08-20 16:23 | 2010-08-21 10:15 | 1072 | E0794 | QT 110/22 kV T2 Transformer Circuit | Transformer | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR984 Queenstown Substation transformer T2 tripped due to lightning | FALSE | Non-Critical
139117 | 21583 | 8289 |  |  | 2010-05-02 14:52 | 2010-05-02 14:53 | 1 | E1567 | DP 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139118 | 21584 | 8290 |  |  | 2010-05-02 14:55 | 2010-05-02 14:56 | 1 | E1567 | DP 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124378 | 21585 | 8291 |  |  | 2010-05-03 00:14 | 2010-05-03 00:15 | 1 | E1507 | SD 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124379 | 21586 | 8292 |  |  | 2010-05-03 00:14 | 2010-05-03 00:15 | 1 | E1393 | SD 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124380 | 21587 | 8293 |  |  | 2010-05-03 16:31 | 2010-05-03 16:50 | 19 | E0835 | RK 11 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124381 | 21588 | 8294 |  |  | 2010-05-05 08:30 | 2010-05-05 08:31 | 1 | E0156 | MB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124382 | 21589 | 8295 |  |  | 2010-05-05 16:36 | 2010-05-05 16:54 | 18 | E1533 | MY 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124383 | 21590 | 8297 |  |  | 2010-05-07 06:14 | 2010-05-07 06:15 | 1 | E0727 | QT 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124384 | 21591 | 8298 |  |  | 2010-05-07 10:42 | 2010-05-07 10:43 | 1 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124385 | 21592 | 8299 |  |  | 2010-05-08 01:31 | 2010-05-08 01:32 | 1 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124386 | 21593 | 8300 |  |  | 2010-05-08 09:47 | 2010-05-08 10:12 | 25 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124387 | 21594 | 8301 |  |  | 2010-05-10 01:38 | 2010-05-10 01:39 | 1 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124388 | 21595 | 8302 |  |  | 2010-05-13 07:47 | 2010-05-13 07:48 | 1 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124389 | 21596 | 8303 |  |  | 2010-05-14 10:36 | 2010-05-14 10:37 | 1 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139119 | 21597 | 8304 |  |  | 2010-05-14 23:22 | 2010-05-14 23:23 | 1 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124391 | 21598 | 8305 |  |  | 2010-05-16 13:30 | 2010-05-16 14:06 | 36 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124392 | 21599 | 8306 |  |  | 2010-05-20 10:39 | 2010-05-20 10:40 | 1 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124393 | 21600 | 8307 |  |  | 2010-05-22 21:05 | 2010-05-23 00:22 | 197 | E0566 | EB 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124394 | 21601 | 8308 |  |  | 2010-05-23 00:14 | 2010-05-23 00:22 | 8 | E0567 | EB 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124395 | 21602 | 8309 |  |  | 2010-05-23 00:30 | 2010-05-23 00:36 | 6 | E0568 | EB 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124396 | 21603 | 8310 |  |  | 2010-05-23 09:57 | 2010-05-23 10:33 | 36 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124397 | 21604 | 8311 |  |  | 2010-05-23 09:57 | 2010-05-23 10:45 | 48 | E0745 | NH 11 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124398 | 21605 | 8312 |  |  | 2010-05-25 10:11 | 2010-05-25 10:12 | 1 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124399 | 21606 | 8313 |  |  | 2010-05-25 10:48 | 2010-05-25 11:23 | 35 | E0845 | RK 11 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124400 | 21607 | 8314 |  |  | 2010-05-25 11:30 | 2010-05-25 11:31 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139121 | 21755 | 8315 |  |  | 2010-05-26 15:32 | 2010-05-26 15:33 | 1 | E1567 | DP 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124577 | 21756 | 8316 |  |  | 2010-05-27 15:09 | 2010-05-27 15:10 | 1 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124578 | 21757 | 8317 |  |  | 2010-05-28 16:12 | 2010-05-28 20:10 | 238 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124579 | 21758 | 8319 |  |  | 2010-06-04 07:58 | 2010-06-04 07:59 | 1 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124580 | 21759 | 8320 |  |  | 2010-06-05 05:41 | 2010-06-05 05:42 | 1 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124581 | 21760 | 8321 |  |  | 2010-06-11 15:19 | 2010-06-11 15:20 | 1 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124582 | 21761 | 8322 |  |  | 2010-06-11 15:25 | 2010-06-11 16:07 | 42 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124583 | 21762 | 8323 |  |  | 2010-06-15 08:27 | 2010-06-15 09:27 | 60 | E0906 | TR 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124584 | 21763 | 8324 |  |  | 2010-06-16 07:16 | 2010-06-16 07:17 | 1 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124585 | 21764 | 8325 |  |  | 2010-06-16 20:13 | 2010-06-16 21:50 | 97 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124586 | 21765 | 8326 |  |  | 2010-06-16 21:55 | 2010-06-16 21:56 | 1 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124587 | 21766 | 8328 |  |  | 2010-06-16 23:16 | 2010-06-17 00:51 | 95 | E1529 | MY 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124588 | 21767 | 8329 |  |  | 2010-06-16 23:18 | 2010-06-17 00:51 | 93 | E1530 | MY 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124589 | 21768 | 8330 |  |  | 2010-06-16 20:25 | 2010-06-17 00:57 | 272 | E1051 | SR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124590 | 21769 | 8331 |  |  | 2010-06-17 11:44 | 2010-06-17 12:42 | 58 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124591 | 21770 | 8332 |  |  | 2010-06-23 12:35 | 2010-06-23 12:38 | 3 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124592 | 21771 | 8333 |  |  | 2010-06-23 14:59 | 2010-06-23 15:22 | 23 | E0111 | CS 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124593 | 21772 | 8334 |  |  | 2010-06-24 11:23 | 2010-06-24 12:02 | 39 | E0460 | KR 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124594 | 21773 | 8335 |  |  | 2010-06-28 05:13 | 2010-06-28 06:08 | 55 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124595 | 21774 | 8336 |  |  | 2010-06-28 20:11 | 2010-06-28 21:56 | 105 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124596 | 21775 | 8337 |  |  | 2010-06-28 20:11 | 2010-06-29 02:33 | 382 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124597 | 21776 | 8338 |  |  | 2010-06-30 00:19 | 2010-06-30 00:41 | 22 | E1504 | TB 22 KV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124598 | 21777 | 8339 |  |  | 2010-07-07 06:22 | 2010-07-07 06:39 | 17 | E0465 | KR 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124599 | 21778 | 8340 |  |  | 2010-07-07 12:29 | 2010-07-07 12:32 | 3 | E0197 | SO 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139122 | 21779 | 8341 |  |  | 2010-07-08 15:46 | 2010-07-08 15:47 | 1 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124601 | 21780 | 8342 |  |  | 2010-07-09 02:05 | 2010-07-09 02:06 | 1 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124602 | 21781 | 8343 |  |  | 2010-07-09 20:36 | 2010-07-09 20:37 | 1 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124603 | 21782 | 8344 |  |  | 2010-07-09 20:40 | 2010-07-09 20:41 | 1 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124604 | 21783 | 8345 |  |  | 2010-07-11 20:52 | 2010-07-11 20:53 | 1 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124605 | 21784 | 8350 |  |  | 2010-07-14 11:08 | 2010-07-14 11:09 | 1 | E0412 | EL 11 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124606 | 21785 | 8351 |  |  | 2010-07-14 10:16 | 2010-07-14 11:35 | 79 | E0843 | RK 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139123 | 21786 | 8352 |  |  | 2010-07-14 16:48 | 2010-07-14 16:48 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124608 | 21787 | 8354 |  |  | 2010-07-21 06:47 | 2010-07-21 07:10 | 23 | E0902 | TR 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124609 | 21788 | 8355 |  |  | 2010-07-22 18:36 | 2010-07-22 18:37 | 1 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124610 | 21789 | 8356 |  |  | 2010-07-22 18:36 | 2010-07-22 18:37 | 1 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124611 | 21790 | 8357 |  |  | 2010-07-24 09:42 | 2010-07-24 09:43 | 1 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124612 | 21791 | 8358 |  |  | 2010-07-25 00:40 | 2010-07-25 01:37 | 57 | E0360 | KI 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124613 | 21792 | 8359 |  |  | 2010-07-28 09:47 | 2010-07-28 11:06 | 79 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124614 | 21793 | 8360 |  |  | 2010-07-30 23:55 | 2010-07-30 23:56 | 1 | E0898 | SD 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124615 | 21794 | 8361 |  |  | 2010-07-30 23:55 | 2010-07-30 23:56 | 1 | E1507 | SD 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124616 | 21795 | 8362 |  |  | 2010-07-31 17:17 | 2010-07-31 17:29 | 12 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124617 | 21796 | 8363 |  |  | 2010-08-01 17:30 | 2010-08-01 17:31 | 1 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124618 | 21797 | 8364 |  |  | 2010-08-03 16:55 | 2010-08-03 17:32 | 37 | E0084 | CR 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124619 | 21798 | 8365 |  |  | 2010-08-04 05:21 | 2010-08-04 14:54 | 573 | E0819 | RA 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124620 | 21799 | 8367 |  |  | 2010-08-07 13:27 | 2010-08-07 14:03 | 36 | E1480 | RI 33 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124621 | 21800 | 8369 |  |  | 2010-08-09 14:24 | 2010-08-09 21:14 | 410 | E0359 | KI 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124622 | 21801 | 8371 |  |  | 2010-08-10 09:03 | 2010-08-10 09:04 | 1 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124623 | 21802 | 8372 |  |  | 2010-08-10 10:21 | 2010-08-10 10:22 | 1 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124624 | 21803 | 8373 |  |  | 2010-08-10 18:59 | 2010-08-10 19:00 | 1 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124625 | 21804 | 8368 |  |  | 2010-08-09 14:24 | 2010-08-10 22:54 | 1950 | E0362 | KI 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124626 | 21805 | 8375 |  |  | 2010-08-11 04:04 | 2010-08-11 04:05 | 1 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124627 | 21806 | 8376 |  |  | 2010-08-11 04:16 | 2010-08-11 04:17 | 1 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124628 | 21807 | 8377 |  |  | 2010-08-11 17:36 | 2010-08-12 11:08 | 1052 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124629 | 21808 | 8379 |  |  | 2010-08-14 23:16 | 2010-08-14 23:16 | 0 | E0944 | UL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124630 | 21809 | 8380 |  |  | 2010-08-15 10:06 | 2010-08-15 10:07 | 1 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124631 | 21810 | 8381 |  |  | 2010-08-17 22:16 | 2010-08-17 22:31 | 15 | E0842 | RK 11 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124632 | 21811 | 8382 |  |  | 2010-08-18 14:46 | 2010-08-18 14:47 | 1 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139124 | 21812 | 8383 |  |  | 2010-08-19 10:09 | 2010-08-19 10:10 | 1 | E1567 | DP 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124634 | 21813 | 8385 |  |  | 2010-08-20 10:04 | 2010-08-20 10:57 | 53 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124664 | 21814 | 8386 |  |  | 2010-08-20 07:40 | 2010-08-20 12:54 | 314 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124665 | 21815 | 8387 |  |  | 2010-08-20 14:45 | 2010-08-20 14:55 | 10 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124666 | 21816 | 8388 |  |  | 2010-08-20 16:33 | 2010-08-20 18:12 | 99 | E1482 | RI 33 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124667 | 21817 | 8389 |  |  | 2010-08-23 04:05 | 2010-08-23 05:40 | 95 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
124668 | 21818 | 8390 |  |  | 2010-08-23 10:02 | 2010-08-23 10:03 | 1 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
180170 | 21819 | 8392 |  |  | 2010-08-23 12:06 | 2010-08-23 12:24 | 18 | E0725 | NT 22 kV A2X Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125116 | 21851 | 8394 |  |  | 2010-09-02 09:02 | 2010-09-02 09:25 | 23 | E0746 | NH 11 kV R2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125580 | 21922 | 8403 |  |  | 2010-09-13 18:45 | 2010-09-13 23:19 | 274 | E0826 | RA 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125581 | 21923 | 8405 |  |  | 2010-09-14 05:30 | 2010-09-14 05:31 | 1 | E0766 | NW 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125582 | 21924 | 8406 |  |  | 2010-09-15 11:18 | 2010-09-15 11:48 | 30 | E0888 | DE 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125583 | 21925 | 8407 |  |  | 2010-09-15 12:29 | 2010-09-15 12:30 | 1 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125584 | 21926 | 8409 |  |  | 2010-09-16 02:26 | 2010-09-16 02:27 | 1 | E1657 | EL 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125585 | 21927 | 8414 |  |  | 2010-09-16 09:06 | 2010-09-16 09:07 | 1 | E0906 | TR 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125586 | 21928 | 8415 |  |  | 2010-09-16 09:29 | 2010-09-16 09:30 | 1 | E0906 | TR 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125587 | 21929 | 8416 |  |  | 2010-09-16 09:41 | 2010-09-16 09:42 | 1 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125588 | 21930 | 8418 |  |  | 2010-09-16 10:05 | 2010-09-16 10:33 | 28 | E0906 | TR 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125589 | 21931 | 8419 |  |  | 2010-09-16 10:37 | 2010-09-16 10:38 | 1 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125590 | 21932 | 8422 |  |  | 2010-09-16 13:27 | 2010-09-16 13:28 | 1 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125591 | 21933 | 8424 |  |  | 2010-09-16 14:05 | 2010-09-16 14:06 | 1 | E0906 | TR 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125592 | 21934 | 8428 |  |  | 2010-09-16 15:12 | 2010-09-16 15:13 | 1 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125593 | 21935 | 8429 |  |  | 2010-09-16 15:40 | 2010-09-16 15:41 | 1 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125594 | 21936 | 8430 |  |  | 2010-09-16 13:17 | 2010-09-16 15:43 | 146 | E0496 | GT 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125595 | 21937 | 8431 |  |  | 2010-09-16 13:17 | 2010-09-16 15:41 | 144 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125596 | 21938 | 8432 |  |  | 2010-09-16 16:17 | 2010-09-16 16:18 | 1 | E0387 | BU 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125597 | 21939 | 8437 |  |  | 2010-09-16 18:46 | 2010-09-16 18:47 | 1 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125598 | 21940 | 8438 |  |  | 2010-09-16 19:09 | 2010-09-16 20:03 | 54 | E0655 | SM 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125599 | 21941 | 8441 |  |  | 2010-09-17 00:45 | 2010-09-17 00:46 | 1 | E0655 | SM 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125600 | 21943 | 8443 |  |  | 2010-09-17 14:26 | 2010-09-17 14:27 | 1 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125601 | 21944 | 8444 |  |  | 2010-09-17 15:33 | 2010-09-17 15:34 | 1 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125602 | 21945 | 8445 |  |  | 2010-09-17 15:35 | 2010-09-17 15:36 | 1 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125603 | 21946 | 8446 |  |  | 2010-09-16 16:05 | 2010-09-17 16:26 | 1461 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125604 | 21947 | 8447 |  |  | 2010-09-17 20:07 | 2010-09-17 20:08 | 1 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125605 | 21948 | 8448 |  |  | 2010-09-17 20:09 | 2010-09-17 20:10 | 1 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125606 | 21949 | 8449 |  |  | 2010-09-17 21:20 | 2010-09-17 21:21 | 1 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125607 | 21950 | 8450 |  |  | 2010-09-17 23:24 | 2010-09-17 23:25 | 1 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125608 | 21951 | 8451 |  |  | 2010-09-18 09:51 | 2010-09-18 15:24 | 333 | E0186 | TU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125609 | 21952 | 8452 |  |  | 2010-09-20 15:25 | 2010-09-20 17:13 | 108 | E1444 | HA 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125610 | 21953 | 8453 |  |  | 2010-09-21 14:38 | 2010-09-21 14:39 | 1 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125611 | 21954 | 8454 |  |  | 2010-09-22 02:15 | 2010-09-22 02:37 | 22 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125677 | 21955 | 8455 |  |  | 2010-09-25 00:03 | 2010-09-25 00:04 | 1 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125678 | 21956 | 8456 |  |  | 2010-09-25 03:27 | 2010-09-25 03:28 | 1 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
126080 | 21957 | 8457 |  |  | 2010-09-27 07:55 | 2010-09-27 12:00 | 245 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125706 | 21958 | 8459 |  |  | 2010-09-27 15:39 | 2010-09-27 16:33 | 54 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139126 | 21959 | 8460 |  |  | 2010-09-28 21:52 | 2010-09-28 22:13 | 21 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
125708 | 21960 | 8461 |  |  | 2010-09-28 20:25 | 2010-09-28 22:25 | 120 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139127 | 21961 | 8463 |  |  | 2010-09-29 02:49 | 2010-09-29 09:24 | 395 | E0185 | TU 22 kV X D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
126073 | 21962 | 1619 |  |  | 2010-09-29 08:05 | 2010-09-29 21:23 | 798 | E0193 | SO 110/22 kV T2 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 395 | TRUE |  | IR1012 Sorell 22 kV B bus tripped while A852 bus coupler was disabled due to high load. | FALSE | Non-Critical
137101 | 21963 | 1617 |  |  | 2010-09-15 13:51 | 2010-09-16 01:25 | 694 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Basslink | Basslink | Completed | TRUE | 0 | TRUE |  | IR1004 Basslink tripped at Loy Yang end. This event was due to a failure of cooling equipment at Loy Yand | FALSE | Undefined
125712 | 21964 | 1614 |  |  | 2010-09-11 17:28 | 2010-09-11 18:03 | 35 | E0772 | PL-ST 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 445 | TRUE |  | IR1003 Port Latta-Smithton 110 kV circuit tripped with loss of supply to Port Latta substation due to commissioning error. | FALSE | Non-Critical
125713 | 21965 | 1613 |  |  | 2010-09-08 16:21 | 2010-09-08 16:21 | 0 | E0554 | SH-WV 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1002 Sheffield-Wesley Vale 110 kV circuit tripped and reclosed. | FALSE | Non-Critical
125714 | 21966 | 1612 |  |  | 2010-09-05 07:18 | 2010-09-05 07:18 | 0 | E0441 | HA-TR 1 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1001 Hadspen-Trevallyn-1 110 kV circuit tripped and reclosed. | FALSE | Critical
126033 | 22005 | 8465 |  |  | 2010-09-30 23:58 | 2010-09-30 23:59 | 1 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
126500 | 22007 | 1621 |  |  | 2010-10-02 05:47 | 2010-10-02 05:49 | 2 | E0270 | PM-HA 3 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1013 Palmerston-Hadspen 3 110kV tripped due to unknown cause. | FALSE | Critical
126913 | 22048 | 1625 |  |  | 2010-10-30 08:19 | 2010-10-30 09:34 | 75 | E0721 | QT-NT 110 kV Transmission Circuit | Transmission | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 249 | TRUE |  | IR1021 Newton Substation 110kV bus tripped following a feeder fault. | FALSE | Non-Critical
128189 | 22049 | 1624 |  |  | 2010-10-12 07:56 | 2010-10-12 07:58 | 2 | E0579 | EB 110 kV C Bus | Bus | Fault | Mechanical Failure | Transend | Completed | TRUE | 13 | TRUE |  | IR1015 Emu Bay Substation bus tripped during planned work. The investigations have identified that the root cause of the outege was failure of insulator associated with circuit breaker A752 Sprecher & Schuh HPF 311L. White phase porcelain operating arm sheared on closing at the base of the casting. | FALSE | Undefined
133910 | 22050 | 1622 |  |  | 2010-10-11 06:58 | 2010-10-11 06:58 | 0 | E1585 | GT-BB Tee 1 110 kV Transmission Circuit Section | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | George Town-Bell Bay Tee 1 110kV tripped | FALSE | Undefined
127163 | 22188 | 8474 |  |  | 2010-10-18 00:04 | 2010-10-18 00:34 | 30 | E0737 | NH 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
127164 | 22189 | 8475 |  |  | 2010-10-21 10:53 | 2010-10-21 10:54 | 1 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
127165 | 22190 | 8476 |  |  | 2010-10-21 17:53 | 2010-10-21 18:14 | 21 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
127166 | 22191 | 8478 |  |  | 2010-10-22 01:22 | 2010-10-22 15:23 | 841 | E1480 | RI 33 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
202245 | 22271 | 1627 |  |  | 2010-11-08 07:04 | 2010-11-08 07:05 | 1 | E1588 | GT-BB Tee 2 110 kV Transmission Circuit Section | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1025 GT-BB PS Tee 2 tripped during work undertaken by generator. | FALSE | Undefined
127463 | 22272 | 1630 |  |  | 2010-11-08 13:30 | 2010-11-08 15:16 | 106 | E0066 | CR 110/33 kV T2 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1028 Creek Road 110kV T2 tripped during planned protection work. | FALSE | Non-Critical
127476 | 22273 | 1632 |  |  | 2010-11-11 10:11 | 2010-11-11 10:23 | 12 | E0211 | RI 110/11 kV T2 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 1152 | TRUE |  | IR1036 RI T2 transformer circuit tripped following an over temperature alarm. | FALSE | Non-Critical
132816 | 22326 | 1633 |  |  | 2010-11-30 11:35 | 2010-11-30 11:46 | 11 | E0716 | FA-RC 1 220 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1042 Farrell-Reece PS 1 220kV trip initiated by G1 maintenance | FALSE | Non-Critical
129230 | 22548 | 1634 |  |  | 2010-12-30 03:42 | 2010-12-30 03:43 | 0 | E0001 | WA-BW 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1057 Waddamana-Bridgewater 110kV tripped and reclosed. | FALSE | Non-Critical
129876 | 22653 | 8479 |  |  | 2010-10-24 09:39 | 2010-10-24 09:40 | 1 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129877 | 22654 | 8480 |  |  | 2010-10-26 08:05 | 2010-10-26 08:06 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
141825 | 22655 | 8481 |  |  | 2010-10-29 05:37 | 2010-10-29 05:55 | 18 | E0491 | GT 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139584 | 22656 | 8482 |  |  | 2010-10-30 14:42 | 2010-10-30 14:43 | 1 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129909 | 22657 | 8483 |  |  | 2010-10-31 11:37 | 2010-10-31 16:47 | 310 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
141826 | 22658 | 8484 |  |  | 2010-11-02 12:43 | 2010-11-02 12:44 | 1 | E0356 | KI 11 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129912 | 22659 | 8485 |  |  | 2010-11-02 12:43 | 2010-11-02 12:44 | 1 | E0358 | KI 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139147 | 22660 | 8486 |  |  | 2010-11-05 07:00 | 2010-11-05 07:23 | 23 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129914 | 22661 | 8487 |  |  | 2010-11-05 10:38 | 2010-11-05 10:39 | 1 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129915 | 22662 | 8488 |  |  | 2010-11-07 06:35 | 2010-11-07 06:36 | 1 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129916 | 22663 | 8489 |  |  | 2010-11-07 14:27 | 2010-11-07 14:28 | 1 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129917 | 22664 | 8490 |  |  | 2010-11-07 17:39 | 2010-11-07 17:55 | 16 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129918 | 22665 | 8491 |  |  | 2010-11-07 19:04 | 2010-11-07 19:05 | 1 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129919 | 22666 | 8492 |  |  | 2010-11-08 20:21 | 2010-11-08 20:22 | 1 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129920 | 22667 | 8493 |  |  | 2010-11-09 03:38 | 2010-11-09 04:33 | 55 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129921 | 22668 | 8494 |  |  | 2010-11-09 22:38 | 2010-11-09 22:39 | 1 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129922 | 22669 | 8495 |  |  | 2010-11-10 21:12 | 2010-11-10 21:13 | 1 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129923 | 22670 | 8496 |  |  | 2010-11-11 06:05 | 2010-11-11 06:06 | 1 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129924 | 22671 | 8497 |  |  | 2010-11-12 06:43 | 2010-11-12 07:50 | 67 | E0084 | CR 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129925 | 22672 | 8498 |  |  | 2010-11-13 13:49 | 2010-11-13 14:52 | 63 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129926 | 22673 | 8499 |  |  | 2010-11-14 03:59 | 2010-11-14 10:02 | 363 | E1393 | SD 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129927 | 22674 | 8500 |  |  | 2010-11-14 23:31 | 2010-11-14 23:32 | 1 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129928 | 22675 | 8501 |  |  | 2010-11-15 07:00 | 2010-11-15 07:01 | 1 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129929 | 22676 | 8502 |  |  | 2010-11-16 00:52 | 2010-11-16 00:53 | 1 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129930 | 22677 | 8503 |  |  | 2010-11-18 02:06 | 2010-11-18 02:24 | 18 | E0496 | GT 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129933 | 22680 | 8506 |  |  | 2010-11-19 01:33 | 2010-11-19 01:34 | 1 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129934 | 22681 | 8507 |  |  | 2010-11-23 23:23 | 2010-11-23 23:24 | 1 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129935 | 22682 | 8508 |  |  | 2010-11-24 10:33 | 2010-11-24 10:34 | 1 | E0160 | MB 22 kV G289 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129936 | 22683 | 8509 |  |  | 2010-11-25 09:14 | 2010-11-25 09:48 | 34 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129937 | 22684 | 8511 |  |  | 2010-11-27 00:26 | 2010-11-27 00:44 | 18 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129938 | 22685 | 8512 |  |  | 2010-11-27 14:00 | 2010-11-27 14:01 | 1 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
129939 | 22686 | 8513 |  |  | 2010-11-28 16:45 | 2010-11-28 16:46 | 1 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130212 | 22687 | 8514 |  |  | 2010-11-29 15:13 | 2010-11-29 15:14 | 1 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130213 | 22688 | 8515 |  |  | 2010-11-29 15:46 | 2010-11-29 15:47 | 1 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130214 | 22689 | 8516 |  |  | 2010-11-29 19:43 | 2010-11-29 20:04 | 21 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130215 | 22690 | 8518 |  |  | 2010-12-01 08:11 | 2010-12-01 08:47 | 36 | E0083 | CR 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130216 | 22691 | 8519 |  |  | 2010-12-01 17:10 | 2010-12-01 17:11 | 1 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130217 | 22692 | 8520 |  |  | 2010-12-01 22:56 | 2010-12-01 22:57 | 1 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130218 | 22693 | 8521 |  |  | 2010-12-02 15:29 | 2010-12-02 15:30 | 1 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130219 | 22694 | 8522 |  |  | 2010-12-03 00:09 | 2010-12-03 00:10 | 1 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130220 | 22695 | 8523 |  |  | 2010-12-03 19:11 | 2010-12-03 19:12 | 1 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130221 | 22696 | 8524 |  |  | 2010-12-04 01:33 | 2010-12-04 01:34 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130222 | 22697 | 8526 |  |  | 2010-12-07 08:53 | 2010-12-07 08:54 | 1 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130223 | 22698 | 8527 |  |  | 2010-12-07 11:11 | 2010-12-07 12:19 | 68 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130224 | 22699 | 8528 |  |  | 2010-12-09 04:41 | 2010-12-09 05:41 | 60 | E0819 | RA 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130225 | 22700 | 8529 |  |  | 2010-12-09 06:35 | 2010-12-09 09:00 | 145 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130226 | 22701 | 8530 |  |  | 2010-12-10 20:13 | 2010-12-10 20:14 | 1 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130227 | 22702 | 8531 |  |  | 2010-12-10 22:28 | 2010-12-10 22:29 | 1 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130228 | 22703 | 8532 |  |  | 2010-12-10 23:33 | 2010-12-11 00:01 | 28 | E1533 | MY 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130229 | 22704 | 8533 |  |  | 2010-12-11 00:02 | 2010-12-11 00:44 | 42 | E1533 | MY 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130230 | 22705 | 8534 |  |  | 2010-12-11 14:36 | 2010-12-11 14:37 | 1 | E0023 | BW 11 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130231 | 22706 | 8535 |  |  | 2010-12-11 23:29 | 2010-12-12 01:29 | 120 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130232 | 22707 | 8536 |  |  | 2010-12-15 10:12 | 2010-12-15 10:13 | 1 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130233 | 22708 | 8537 |  |  | 2010-12-16 02:24 | 2010-12-16 02:25 | 1 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130234 | 22709 | 8538 |  |  | 2010-12-16 08:18 | 2010-12-16 08:46 | 28 | E0085 | CR 33 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130235 | 22710 | 8539 |  |  | 2010-12-16 16:11 | 2010-12-16 16:12 | 1 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130236 | 22711 | 8540 |  |  | 2010-12-16 23:45 | 2010-12-17 00:02 | 17 | E0909 | TR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130237 | 22712 | 8541 |  |  | 2010-12-18 02:31 | 2010-12-18 04:46 | 135 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130238 | 22713 | 8542 |  |  | 2010-12-18 17:32 | 2010-12-18 17:59 | 27 | E0865 | RB 44 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130239 | 22714 | 8544 |  |  | 2010-12-18 23:19 | 2010-12-18 23:20 | 1 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130240 | 22715 | 8545 |  |  | 2010-12-19 06:20 | 2010-12-19 06:21 | 1 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130272 | 22716 | 8546 |  |  | 2010-12-19 07:41 | 2010-12-19 07:42 | 1 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130273 | 22717 | 8547 |  |  | 2010-12-19 15:18 | 2010-12-19 15:19 | 1 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
141827 | 22718 | 8548 |  |  | 2010-12-19 15:21 | 2010-12-19 18:15 | 174 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130275 | 22719 | 8549 |  |  | 2010-12-20 09:52 | 2010-12-20 09:53 | 1 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130276 | 22720 | 8550 |  |  | 2010-12-22 06:15 | 2010-12-22 06:16 | 1 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
130277 | 22721 | 8551 |  |  | 2010-12-26 08:13 | 2010-12-26 08:14 | 1 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
131549 | 22943 | 1635 |  |  | 2011-01-12 07:35 | 2011-01-12 14:23 | 408 | E0775 | PL 110 kV A7 Bus Coupler Circuit | Bus Coupler | Fault | Poor Wiring | Transend | Completed | TRUE | 0 | TRUE |  | IR1060 Port Latta A752 bus coupler tripped. Roaring 40s lost 55MW. There was shorted DC trip wiring on relay base B121B/B121BX that may occurred during circuit breaker B1 replacement Project | FALSE | Undefined
134159 | 22944 | 1637 |  |  | 2011-01-14 09:15 | 2011-01-14 09:57 | 42 | E0290 | PO-PM 2 110 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1061 Poatina-Palmerston 2 tripped. Hydro personnel advised that there was maintenance testing underway on the machine at the time the trip occurred but could not confirm that the trip of transmission circuit was due to the ongoing test. | FALSE | Non-Critical
131551 | 22945 | 1638 |  |  | 2011-01-21 09:42 | 2011-01-21 09:46 | 4 | E0538 | SH-FA 1 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1063 Sheffield-Farell No 1 and 2 transmission lines tripped with lightning in the area. | FALSE | Critical
131552 | 22945 | 1638 |  |  | 2011-01-21 09:42 | 2011-01-21 09:42 | 0 | E0539 | SH-FA 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1063 Sheffield-Farell No 1 and 2 transmission lines tripped with lightning in the area. | FALSE | Critical
131553 | 22946 | 1640 |  |  | 2011-01-21 10:00 | 2011-01-21 10:03 | 3 | E0270 | PM-HA 3 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1064 Palmerston-Hadspen 3 transmission circuit tripped with lightning in area. | FALSE | Critical
131554 | 22947 | 1641 |  |  | 2011-01-24 19:50 | 2011-01-25 06:09 | 619 | E0326 | BY 6.6 kV F3 Feeder Circuit | Feeder | Fault | Cable Fault | MI | Completed | TRUE | 0 | TRUE |  | IR1065 Boyer F352 feeder circuit tripped following a customer cable fault. Norske Skog reported to have found an evidence of a fault on one of the cables at Norske Skog. Faulty cable was customer asset. | FALSE | Undefined
131555 | 22948 | 1642 |  |  | 2011-01-25 08:49 | 2011-01-25 08:49 | 0 | E0001 | WA-BW 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1066 Waddamana-Bridgewater 110kV tripped. | FALSE | Non-Critical
131556 | 22949 | 1643 |  |  | 2011-01-31 08:55 | 2011-01-31 08:55 | 0 | E0406 | FA-QU-SR-HM 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1067 FA-QU-SR-HM 110kV transmission circuit tripped and reclosed with lightning in area. | FALSE | Non-Critical
132930 | 23123 | 1645 |  |  | 2011-02-07 12:40 | 2011-02-07 13:07 | 27 | E0135 | NN-BY 1 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 2352 | TRUE |  | IR1068 New Norfolk-Boyer 1 transmission circuit tripped during planned work. | FALSE | Non-Critical
133900 | 23413 | 1657 |  |  | 2011-03-23 20:16 | 2011-03-24 01:01 | 285 | E0193 | SO 110/22 kV T2 Transformer Circuit | Transformer | Fault | Wildlife | Transend | Completed | TRUE | 3556 | TRUE |  | IR1094 Sorell T2 transformer circuit tripped causing loss of supply at Sorell substation, due to wildlife incursion during planned work. | FALSE | Non-Critical
133901 | 23414 | 1646 |  |  | 2011-02-17 04:14 | 2011-02-17 04:14 | 0 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1070 Farrell-Rosebery-Queenstown tripped and reclosed with lightning in the area. | FALSE | Non-Critical
133902 | 23415 | 1647 |  |  | 2011-02-17 04:14 | 2011-02-17 04:35 | 21 | E0715 | FA-JB 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1071 Farrell-John Butters transmission line tripped with lightning in te area. | FALSE | Non-Critical
133903 | 23416 | 1648 |  |  | 2011-02-17 11:44 | 2011-02-17 11:44 | 0 | E0554 | SH-WV 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1073 Sheffield-Wesley Vale transmission line tripped and reclosed with lightning in the area. | FALSE | Non-Critical
150880 | 23417 | 1650 |  |  | 2011-02-19 11:15 | 2011-02-19 11:24 | 9 | E0795 | QT 110/11 kV T3 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 49 | TRUE |  | IR1074 Queenstown T3 and T4 transformer circuits tripped following a feeder reclose with loss of supply. Primary fault was on customer' s disconnector but there was protection coordination issue which occurred during the restoration process of the faulted feeder. | FALSE | Non-Critical
150881 | 23417 | 1650 |  |  | 2011-02-19 11:15 | 2011-02-19 11:25 | 10 | E0796 | QT 110/11 kV T4 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR1074 Queenstown T3 and T4 transformer circuits tripped following a feeder reclose with loss of supply. Primary fault was on customer' s disconnector but there was protection coordination issue which occurred during the restoration process of the faulted feeder. | FALSE | Non-Critical
133906 | 23418 | 1653 |  |  | 2011-02-22 18:26 | 2011-02-22 18:31 | 5 | E1072 | LF-RI 2 110 kV Transmission Circuit | Transmission | Fault | Incorrect Drawings | Transend | Completed | TRUE | 0 | TRUE |  | IR1077 Lindisfarne-Risdon transmission circuit tripped. | FALSE | Non-Critical
134092 | 23419 | 1654 |  |  | 2011-03-03 03:53 | 2011-03-03 04:09 | 16 | E0161 | TA-MB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1079 Tarraleah-Meadowbank transmission circuit tripped during strong winds. | FALSE | Non-Critical
202260 | 23420 | 1655 |  |  | 2011-03-08 12:23 | 2011-03-08 12:23 | 0 | E0539 | SH-FA 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1080 Sheffield-Farrell 2 transmission circuit single pole trip and auto reclose due to bark on red phase at tower T5. Treek bark found on suspension clamps of red phase at Tower T5 | FALSE | Critical
134095 | 23421 | 1659 |  |  | 2011-03-26 13:23 | 2011-03-26 16:49 | 206 | E0467 | KR 110 kV A7 Bus Coupler Circuit | Bus Coupler | Fault | Pending Investigation | Transend | Completed | TRUE | 0 | TRUE |  | IR1095 Knights Road A752 bus coupler tripped. | FALSE | Undefined
134633 | 23489 | 1657 |  |  | 2011-03-24 07:08 | 2011-03-24 10:57 | 229 | E0194 | SO 22 kV A Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 306 | TRUE |  | IR1142 Sorell A Bus feeders trip due to error during planned work. Inadequate vermin control during substation construction works | FALSE | Undefined
135362 | 23599 | 1660 |  |  | 2011-04-02 08:55 | 2011-04-02 10:27 | 92 | E0953 | WY-CA 220 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1097 Wayantinah-Catagunya tripped during generator synchronisation. | FALSE | Non-Critical
135363 | 23600 | 1661 |  |  | 2011-04-08 13:32 | 2011-04-08 13:35 | 3 | E0810 | RA 110 kV A Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 30 | TRUE |  | IR1100 Railton 22kV A Bus tripped during protection testing. | FALSE | Undefined
143775 | 23631 | 1663 |  |  | 2011-05-04 19:21 | 2011-05-07 12:57 | 3936 | E0831 | RK 110/11 kV T2 Transformer Circuit | Transformer | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1108 Lindisfarne-Rokeby Sorell 110kV transmission line tripped causing loss of supply at Rokeby Substation, Suspect cable but cause unknown. | FALSE | Undefined
135853 | 23631 | 1663 |  |  | 2011-05-04 19:21 | 2011-05-04 23:00 | 219 | E0190 | LF-RK 2-SO 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 4121 | TRUE |  | IR1108 Lindisfarne-Rokeby Sorell 110kV transmission line tripped causing loss of supply at Rokeby Substation, Suspect cable but cause unknown. | FALSE | Non-Critical
136429 | 23795 | 8621 |  |  | 2011-01-22 04:01 | 2011-01-22 04:01 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
137126 | 23796 | 8622 |  |  | 2010-01-22 05:02 | 2010-01-22 05:02 | 0 | E0768 | NW 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
137127 | 23797 | 8623 |  |  | 2010-01-23 06:17 | 2010-01-23 06:17 | 0 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136446 | 23798 | 8624 |  |  | 2011-01-23 06:31 | 2011-01-23 06:31 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136447 | 23799 | 8625 |  |  | 2011-01-23 16:02 | 2011-01-23 16:02 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136448 | 23800 | 8626 |  |  | 2011-01-23 18:39 | 2011-01-23 21:20 | 161 | E1557 | CR 33 kV Z2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136449 | 23801 | 8627 |  |  | 2011-01-24 05:05 | 2011-01-24 05:06 | 1 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138821 | 23802 | 8628 |  |  | 2011-01-24 05:18 | 2011-01-24 05:18 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136451 | 23803 | 8629 |  |  | 2011-01-24 05:50 | 2011-01-24 05:50 | 0 | E0888 | DE 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136452 | 23804 | 8630 |  |  | 2011-01-24 09:39 | 2011-01-24 09:39 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136453 | 23805 | 8631 |  |  | 2011-01-25 20:27 | 2011-01-25 20:27 | 0 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136454 | 23806 | 8632 |  |  | 2011-01-26 06:01 | 2011-01-26 06:01 | 0 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136456 | 23808 | 8635 |  |  | 2011-01-28 12:00 | 2011-01-28 12:18 | 18 | E0107 | CS 11 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136457 | 23809 | 8636 |  |  | 2011-01-30 17:29 | 2011-01-30 17:29 | 0 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136458 | 23810 | 8637 |  |  | 2011-01-30 17:34 | 2011-01-30 18:37 | 63 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136459 | 23811 | 8638 |  |  | 2011-02-01 00:12 | 2011-02-01 00:12 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136460 | 23812 | 8640 |  |  | 2011-02-01 07:36 | 2011-02-01 07:36 | 0 | E1613 | UL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136461 | 23813 | 8641 |  |  | 2011-02-01 14:22 | 2011-02-01 14:22 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136462 | 23814 | 8642 |  |  | 2011-02-01 14:30 | 2011-02-01 14:30 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136463 | 23815 | 8643 |  |  | 2011-02-01 14:49 | 2011-02-01 14:49 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136464 | 23816 | 8644 |  |  | 2011-02-01 16:19 | 2011-02-01 16:56 | 37 | E1550 | DP 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136465 | 23817 | 8645 |  |  | 2011-02-02 05:19 | 2011-02-02 05:19 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138822 | 23818 | 8646 |  |  | 2011-02-03 20:44 | 2011-02-03 20:44 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136467 | 23819 | 8647 |  |  | 2011-02-03 23:35 | 2011-02-03 23:35 | 0 | E1454 | HA 22 kV L2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136468 | 23820 | 8649 |  |  | 2011-02-05 16:48 | 2011-02-05 19:09 | 141 | E0567 | EB 11 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136469 | 23821 | 8652 |  |  | 2011-02-06 04:51 | 2011-02-06 06:48 | 117 | E0448 | KE 11 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136470 | 23822 | 8653 |  |  | 2011-02-06 12:59 | 2011-02-06 12:59 | 0 | E0188 | TU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136471 | 23823 | 8654 |  |  | 2011-02-06 14:38 | 2011-02-06 14:38 | 0 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136472 | 23824 | 8655 |  |  | 2011-02-07 08:26 | 2011-02-07 08:26 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155348 | 23826 | 8656 |  |  | 2011-02-08 02:24 | 2011-02-08 02:24 | 0 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136490 | 23827 | 8657 |  |  | 2011-02-08 05:58 | 2011-02-08 05:59 | 1 | E0158 | MB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136491 | 23828 | 8658 |  |  | 2011-02-08 13:24 | 2011-02-08 13:24 | 0 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136492 | 23829 | 8659 |  |  | 2011-02-09 05:42 | 2011-02-09 05:42 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136493 | 23830 | 8661 |  |  | 2011-02-12 02:58 | 2011-02-12 02:58 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136494 | 23831 | 8662 |  |  | 2011-02-12 22:32 | 2011-02-12 22:32 | 0 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136495 | 23832 | 8663 |  |  | 2011-02-12 23:03 | 2011-02-12 23:03 | 0 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138823 | 23833 | 8664 |  |  | 2011-02-13 05:31 | 2011-02-13 05:31 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136497 | 23834 | 8665 |  |  | 2011-02-13 10:57 | 2011-02-13 10:57 | 0 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136498 | 23835 | 8666 |  |  | 2011-02-14 06:28 | 2011-02-14 06:28 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136499 | 23836 | 8667 |  |  | 2011-02-15 09:41 | 2011-02-15 09:41 | 0 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136500 | 23837 | 8668 |  |  | 2011-02-16 23:45 | 2011-02-16 23:45 | 0 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136501 | 23838 | 8669 |  |  | 2011-02-17 04:14 | 2011-02-17 04:14 | 0 | E0806 | QT 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136502 | 23839 | 8670 |  |  | 2011-02-17 04:14 | 2011-02-17 04:14 | 0 | E0807 | QT 11 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136503 | 23840 | 8671 |  |  | 2011-02-17 20:45 | 2011-02-17 20:45 | 0 | E1001 | BU 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136504 | 23841 | 8673 |  |  | 2011-02-19 13:14 | 2011-02-19 13:14 | 0 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136505 | 23842 | 8674 |  |  | 2011-02-19 13:45 | 2011-02-19 13:46 | 1 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136506 | 23843 | 8675 |  |  | 2011-02-19 17:15 | 2011-02-19 17:36 | 21 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136507 | 23844 | 8676 |  |  | 2011-02-20 06:56 | 2011-02-20 06:56 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136508 | 23845 | 8677 |  |  | 2011-02-20 09:30 | 2011-02-20 09:30 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155349 | 23846 | 8678 |  |  | 2011-02-20 10:46 | 2011-02-20 11:39 | 53 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138824 | 23848 | 8679 |  |  | 2011-02-20 11:40 | 2011-02-20 12:05 | 25 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136511 | 23849 | 8680 |  |  | 2011-02-20 13:38 | 2011-02-20 13:38 | 0 | E0898 | SD 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136512 | 23850 | 8681 |  |  | 2011-02-20 14:04 | 2011-02-20 15:44 | 100 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136513 | 23851 | 8682 |  |  | 2011-02-20 17:54 | 2011-02-20 18:33 | 39 | E0865 | RB 44 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139041 | 23852 | 8683 |  |  | 2011-02-21 19:58 | 2011-02-21 19:58 | 0 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136515 | 23853 | 8684 |  |  | 2011-02-21 23:51 | 2011-02-21 23:51 | 0 | E0156 | MB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136516 | 23854 | 8685 |  |  | 2011-02-22 03:32 | 2011-02-22 03:32 | 0 | E0287 | PM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136517 | 23855 | 8686 |  |  | 2011-02-22 10:29 | 2011-02-22 10:29 | 0 | E0865 | RB 44 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136518 | 23856 | 8687 |  |  | 2011-02-22 18:21 | 2011-02-22 18:21 | 0 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136519 | 23857 | 8688 |  |  | 2011-02-22 20:37 | 2011-02-22 20:37 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136520 | 23858 | 8689 |  |  | 2011-02-23 22:49 | 2011-02-23 23:27 | 38 | E0747 | NH 11 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136521 | 23859 | 8690 |  |  | 2011-02-25 08:58 | 2011-02-25 09:36 | 38 | E0745 | NH 11 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136522 | 23860 | 8691 |  |  | 2011-02-26 02:48 | 2011-02-26 02:48 | 0 | E1531 | MY 22 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136523 | 23861 | 8692 |  |  | 2011-02-27 07:03 | 2011-02-27 07:03 | 0 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136652 | 23882 | 8754 |  |  | 2011-03-28 07:39 | 2011-03-28 08:10 | 31 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136653 | 23883 | 8755 |  |  | 2011-03-28 09:35 | 2011-03-28 11:17 | 102 | E1504 | TB 22 KV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136654 | 23884 | 8756 |  |  | 2011-03-29 16:03 | 2011-03-29 16:54 | 51 | E0360 | KI 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136655 | 23885 | 8758 |  |  | 2011-03-29 18:15 | 2011-03-29 18:18 | 3 | E0360 | KI 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136656 | 23886 | 8759 |  |  | 2011-03-30 07:51 | 2011-03-30 07:51 | 0 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136657 | 23887 | 8760 |  |  | 2011-03-30 15:12 | 2011-03-30 16:00 | 48 | E1557 | CR 33 kV Z2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136658 | 23888 | 8761 |  |  | 2011-03-30 23:01 | 2011-03-30 23:01 | 0 | E0389 | BU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136659 | 23889 | 8763 |  |  | 2011-03-31 12:16 | 2011-03-31 12:16 | 0 | E1504 | TB 22 KV F2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136706 | 23931 | 8764 |  |  | 2011-04-01 00:59 | 2011-04-01 00:59 | 0 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139042 | 23932 | 8765 |  |  | 2011-04-01 01:01 | 2011-04-01 01:01 | 0 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136708 | 23933 | 8766 |  |  | 2011-04-01 01:25 | 2011-04-01 02:59 | 94 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
141839 | 23935 | 8678 |  |  | 2011-04-02 06:30 | 2011-04-02 06:30 | 0 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136710 | 23936 | 8769 |  |  | 2011-04-02 21:56 | 2011-04-02 21:56 | 0 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136711 | 23937 | 8770 |  |  | 2011-04-03 01:24 | 2011-04-03 01:24 | 0 | E1454 | HA 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136712 | 23938 | 8771 |  |  | 2011-04-04 02:08 | 2011-04-04 02:08 | 0 | E1454 | HA 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136713 | 23939 | 8772 |  |  | 2011-04-04 16:28 | 2011-04-04 16:29 | 1 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136714 | 23940 | 8773 |  |  | 2011-04-05 01:06 | 2011-04-05 01:06 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136715 | 23941 | 8774 |  |  | 2011-04-05 14:00 | 2011-04-05 14:20 | 20 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136716 | 23942 | 8775 |  |  | 2011-04-06 09:44 | 2011-04-06 09:44 | 0 | E0389 | BU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136717 | 23943 | 8777 |  |  | 2011-04-07 06:42 | 2011-04-07 06:42 | 0 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136718 | 23944 | 8778 |  |  | 2011-04-09 00:59 | 2011-04-09 00:59 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136719 | 23945 | 8779 |  |  | 2011-04-10 22:26 | 2011-04-11 02:11 | 225 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136720 | 23946 | 8780 |  |  | 2011-04-12 10:16 | 2011-04-12 10:38 | 22 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136721 | 23947 | 8782 |  |  | 2011-04-12 17:45 | 2011-04-12 18:41 | 56 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136722 | 23948 | 8781 |  |  | 2011-04-12 15:30 | 2011-04-12 18:55 | 205 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136723 | 23949 | 8785 |  |  | 2011-04-12 21:09 | 2011-04-12 22:32 | 83 | E0496 | GT 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136724 | 23951 | 8752 |  |  | 2011-03-26 01:09 | 2011-04-13 09:45 | 26436 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136725 | 23952 | 8751 |  |  | 2011-03-26 01:09 | 2011-04-13 12:08 | 26579 | E1444 | HA 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136726 | 23953 | 8789 |  |  | 2011-04-13 13:25 | 2011-04-13 13:26 | 1 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136727 | 23956 | 8829 |  |  | 2011-06-08 03:50 | 2011-06-08 10:54 | 424 | E1051 | SR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136728 | 23957 | 8828 |  |  | 2011-06-08 08:42 | 2011-06-08 08:42 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136729 | 23958 | 8827 |  |  | 2011-06-08 07:49 | 2011-06-08 08:32 | 43 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136730 | 23959 | 8826 |  |  | 2011-06-08 06:34 | 2011-06-08 06:51 | 17 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136731 | 23960 | 8825 |  |  | 2011-06-08 06:22 | 2011-06-08 06:34 | 12 | E0083 | CR 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136732 | 23961 | 8824 |  |  | 2011-06-08 05:42 | 2011-06-08 06:12 | 30 | E0078 | CR 33 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136733 | 23962 | 8823 |  |  | 2011-06-08 02:26 | 2011-06-08 02:27 | 1 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136734 | 23963 | 8822 |  |  | 2011-06-08 00:21 | 2011-06-08 00:42 | 21 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136752 | 23965 | 8821 |  |  | 2011-06-07 22:08 | 2011-06-07 23:48 | 100 | E1479 | RI 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136753 | 23966 | 8819 |  |  | 2011-06-07 23:32 | 2011-06-07 23:33 | 1 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136754 | 23967 | 8818 |  |  | 2011-06-07 21:19 | 2011-06-07 21:29 | 10 | E1479 | RI 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136755 | 23968 | 8817 |  |  | 2011-06-07 21:23 | 2011-06-07 21:23 | 0 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136756 | 23969 | 8816 |  |  | 2011-06-07 21:02 | 2011-06-07 21:02 | 0 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136757 | 23970 | 8815 |  |  | 2011-06-07 04:43 | 2011-06-07 07:30 | 167 | E1554 | DP 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136758 | 23971 | 8814 |  |  | 2011-06-07 06:34 | 2011-06-07 06:54 | 20 | E0489 | GT 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136759 | 23972 | 8813 |  |  | 2011-06-06 18:41 | 2011-06-06 19:42 | 61 | E0083 | CR 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136777 | 23973 | 8830 |  |  | 2011-06-08 14:47 | 2011-06-08 15:40 | 53 | E1004 | BU 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136778 | 23974 | 8831 |  |  | 2011-06-08 15:49 | 2011-06-08 15:50 | 1 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136779 | 23975 | 8832 |  |  | 2011-06-08 18:48 | 2011-06-08 19:07 | 19 | E0970 | SO 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136780 | 23976 | 8833 |  |  | 2011-06-09 04:21 | 2011-06-09 05:38 | 77 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186059 | 23977 | 8834 |  |  | 2011-06-07 14:40 | 2011-06-09 14:36 | 2876 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136782 | 23978 | 8835 |  |  | 2011-06-10 08:53 | 2011-06-10 08:54 | 1 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136935 | 24006 | 8660 |  |  | 2011-02-10 17:35 | 2011-04-01 14:34 | 71819 | E0014 | BW 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139079 | 24007 | 8762 |  |  | 2011-03-30 20:29 | 2011-04-04 17:06 | 6997 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136937 | 24008 | 8672 |  |  | 2011-02-19 09:55 | 2011-02-25 11:36 | 8741 | E0807 | QT 11 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
139044 | 24010 | 8650 |  |  | 2011-02-05 15:30 | 2011-02-05 16:29 | 59 | E0156 | MB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136940 | 24011 | 8838 |  |  | 2011-06-12 12:29 | 2011-06-12 12:29 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138825 | 24012 | 8837 |  |  | 2011-06-12 08:28 | 2011-06-12 08:28 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
136942 | 24013 | 8836 |  |  | 2011-06-10 23:44 | 2011-06-10 23:45 | 1 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
137591 | 24058 | 8845 |  |  | 2011-06-17 16:16 | 2011-06-17 17:22 | 66 | E1538 | MY 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
137592 | 24059 | 8846 |  |  | 2011-06-18 03:10 | 2011-06-18 03:10 | 0 | E0638 | ST 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
137593 | 24060 | 8847 |  |  | 2011-06-18 11:11 | 2011-06-18 11:12 | 1 | E1393 | SD 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
137594 | 24061 | 8848 |  |  | 2011-06-18 17:34 | 2011-06-18 17:34 | 0 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
137595 | 24062 | 8849 |  |  | 2011-06-20 14:14 | 2011-06-20 14:14 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
137596 | 24063 | 8850 |  |  | 2011-06-20 14:30 | 2011-06-20 14:30 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
137597 | 24064 | 8851 |  |  | 2011-06-20 15:10 | 2011-06-20 15:10 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
137598 | 24065 | 8852 |  |  | 2011-06-21 00:54 | 2011-06-21 00:54 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
137599 | 24066 | 8853 |  |  | 2011-06-21 00:57 | 2011-06-21 00:57 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
137600 | 24067 | 8854 |  |  | 2011-06-21 00:37 | 2011-06-21 02:09 | 92 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
137601 | 24068 | 8855 |  |  | 2011-06-21 03:12 | 2011-06-21 03:30 | 18 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
137602 | 24069 | 8856 |  |  | 2011-06-22 03:12 | 2011-06-22 03:29 | 17 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138434 | 24167 | 8857 |  |  | 2011-06-22 22:18 | 2011-06-22 22:45 | 27 | E1482 | RI 33 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138435 | 24168 | 8858 |  |  | 2011-06-22 23:41 | 2011-06-22 23:41 | 0 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138436 | 24169 | 8859 |  |  | 2011-06-23 07:53 | 2011-06-23 08:15 | 22 | E0197 | SO 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138437 | 24170 | 8860 |  |  | 2011-06-24 08:20 | 2011-06-24 08:20 | 0 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138438 | 24171 | 8862 |  |  | 2011-07-03 10:30 | 2011-07-03 10:30 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138439 | 24172 | 8863 |  |  | 2011-07-04 15:49 | 2011-07-04 16:18 | 29 | E0489 | GT 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138440 | 24173 | 8864 |  |  | 2011-07-05 03:05 | 2011-07-05 04:35 | 90 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138441 | 24174 | 8865 |  |  | 2011-07-05 06:01 | 2011-07-05 06:01 | 0 | E1051 | SR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138442 | 24175 | 8866 |  |  | 2011-07-05 06:06 | 2011-07-05 06:06 | 0 | E1051 | SR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138538 | 24176 | 8867 |  |  | 2011-07-07 23:27 | 2011-07-07 23:27 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138539 | 24177 | 8868 |  |  | 2011-07-08 05:21 | 2011-07-08 06:34 | 73 | E0837 | RK 11 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138540 | 24178 | 8869 |  |  | 2011-07-08 14:52 | 2011-07-08 15:19 | 27 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138541 | 24179 | 8870 |  |  | 2011-07-09 00:56 | 2011-07-09 00:56 | 0 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138542 | 24180 | 8871 |  |  | 2011-07-09 00:59 | 2011-07-09 01:00 | 1 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138543 | 24181 | 8872 |  |  | 2011-07-09 01:03 | 2011-07-09 01:19 | 16 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138544 | 24182 | 8873 |  |  | 2011-07-09 01:32 | 2011-07-09 01:47 | 15 | E0083 | CR 33 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138545 | 24183 | 8874 |  |  | 2011-07-09 02:29 | 2011-07-09 02:29 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138546 | 24184 | 8875 |  |  | 2011-07-09 01:21 | 2011-07-09 05:00 | 219 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138547 | 24185 | 8879 |  |  | 2011-07-09 14:55 | 2011-07-09 14:55 | 0 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138548 | 24186 | 8880 |  |  | 2011-07-09 22:18 | 2011-07-09 22:18 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138549 | 24187 | 8881 |  |  | 2011-07-10 00:02 | 2011-07-10 01:30 | 88 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138550 | 24188 | 8882 |  |  | 2011-07-10 04:31 | 2011-07-10 04:49 | 18 | E0638 | ST 22 kV J2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138551 | 24189 | 8883 |  |  | 2011-07-10 05:10 | 2011-07-10 05:10 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138552 | 24190 | 8884 |  |  | 2011-07-10 05:24 | 2011-07-10 05:24 | 0 | E0888 | DE 22 kV A2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138553 | 24191 | 8885 |  |  | 2011-07-10 05:48 | 2011-07-10 05:48 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138554 | 24192 | 8886 |  |  | 2011-07-10 06:04 | 2011-07-10 06:04 | 0 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138555 | 24193 | 8887 |  |  | 2011-07-10 07:07 | 2011-07-10 08:50 | 103 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138556 | 24195 | 8889 |  |  | 2011-07-10 17:26 | 2011-07-10 17:26 | 0 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138557 | 24196 | 8890 |  |  | 2011-07-11 04:22 | 2011-07-11 04:22 | 0 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138558 | 24197 | 8891 |  |  | 2011-07-11 15:56 | 2011-07-11 15:56 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138644 | 24198 | 8892 |  |  | 2011-07-11 16:42 | 2011-07-11 16:42 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138645 | 24199 | 8893 |  |  | 2011-07-11 23:39 | 2011-07-11 23:39 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138646 | 24200 | 8894 |  |  | 2011-07-11 23:35 | 2011-07-12 00:03 | 28 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138647 | 24201 | 8896 |  |  | 2011-07-12 00:20 | 2011-07-12 00:20 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138648 | 24202 | 8897 |  |  | 2011-07-12 00:39 | 2011-07-12 00:39 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138649 | 24203 | 8898 |  |  | 2011-07-12 01:04 | 2011-07-12 01:04 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138650 | 24204 | 8899 |  |  | 2011-07-12 01:08 | 2011-07-12 01:08 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138651 | 24205 | 8900 |  |  | 2011-07-12 02:02 | 2011-07-12 02:02 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138652 | 24206 | 8901 |  |  | 2011-07-12 04:57 | 2011-07-12 06:36 | 99 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138653 | 24207 | 8902 |  |  | 2011-07-12 07:38 | 2011-07-12 07:39 | 1 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
138700 | 24241 | 1666 |  |  | 2011-07-02 09:20 | 2011-07-02 09:26 | 6 | E1014 | WA 110 kV F7 Bus Coupler Circuit | Bus Coupler | Fault | Pending Investigation | Transend | Completed | TRUE | 0 | TRUE |  | IR1129 Waddamana F752 110kV circuit breaker tripped on overcurrent due to feeder fault. | FALSE | Undefined
138701 | 24242 | 1667 |  |  | 2011-07-05 16:41 | 2011-07-06 02:48 | 607 | E0260 | PM-HA 2 220 kV Transmission Circuit | Transmission | Fault | Fatigue | Transend | Completed | TRUE | 0 | TRUE |  | IR1130 Palmerston-Hadspen 2 transmission circuit tripped due to broken CT connection. | FALSE | Critical
141840 | 24243 | 1669 |  |  | 2011-07-08 03:42 | 2011-07-08 04:07 | 25 | E0030 | CS-KI-KR 110 kV Transmission Circuit (changed to E1955) | Transmission | Fault | Unknown | Transend | Completed | TRUE | 3457 | TRUE |  | IR1131 CS-KI-KR tripped with loss of supply at Kingston, Knights Road, Kermandie and Huon River substations. | FALSE | Non-Critical
141841 | 24243 | 1669 |  |  | 2011-07-08 09:29 | 2011-07-08 09:29 | 0 | E0030 | CS-KI-KR 110 kV Transmission Circuit (changed to E1955) | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1131 CS-KI-KR tripped with loss of supply at Kingston, Knights Road, Kermandie and Huon River substations. | FALSE | Non-Critical
141842 | 24243 | 1669 |  |  | 2011-07-08 10:24 | 2011-07-08 14:58 | 274 | E0030 | CS-KI-KR 110 kV Transmission Circuit (changed to E1955) | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1131 CS-KI-KR tripped with loss of supply at Kingston, Knights Road, Kermandie and Huon River substations. | FALSE | Non-Critical
141843 | 24243 | 1669 |  |  | 2011-07-08 18:41 | 2011-07-08 18:41 | 0 | E0030 | CS-KI-KR 110 kV Transmission Circuit (changed to E1955) | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1131 CS-KI-KR tripped with loss of supply at Kingston, Knights Road, Kermandie and Huon River substations. | FALSE | Non-Critical
141844 | 24243 | 1669 |  |  | 2011-07-08 19:38 | 2011-07-08 20:23 | 45 | E0030 | CS-KI-KR 110 kV Transmission Circuit (changed to E1955) | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1131 CS-KI-KR tripped with loss of supply at Kingston, Knights Road, Kermandie and Huon River substations. | FALSE | Non-Critical
141845 | 24243 | 1669 |  |  | 2011-07-08 21:02 | 2011-07-11 16:18 | 4036 | E1673 | HR-CF Tee 110 kV Transmission Circuit Section | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1131 CS-KI-KR tripped with loss of supply at Kingston, Knights Road, Kermandie and Huon River substations. | FALSE | Undefined
138750 | 24244 | 8903 |  |  | 2011-07-12 11:35 | 2011-07-12 11:39 | 4 | E0728 | NH 11 kV A Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 33 | TRUE |  | IR1140 North Hobart feeders tripped during planned work IR1140 North Hobart feeders tripped during planned work | FALSE | Undefined
140297 | 24381 | 8903 |  |  | 2011-07-12 23:35 | 2011-07-12 23:38 | 3 | E0734 | NH 11 kV B2 Feeder Circuit | Feeder | Fault | Human Error During Planned Work | DNSP | Completed | TRUE | 0 | TRUE |  | IR1140 North Hobart Substation feeders B, C and D tripped. | FALSE | Undefined
140298 | 24382 | 8904 |  |  | 2011-07-12 11:35 | 2011-07-12 11:39 | 4 | E0735 | NH 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
140299 | 24383 | 8905 |  |  | 2011-07-12 11:35 | 2011-07-12 11:39 | 4 | E0736 | NH 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
140300 | 24384 | 8906 |  |  | 2011-07-12 13:51 | 2011-07-12 14:11 | 20 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
140301 | 24385 | 8907 |  |  | 2011-07-12 12:23 | 2011-07-12 15:15 | 172 | E1665 | EL 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
140302 | 24386 | 8909 |  |  | 2011-07-12 14:26 | 2011-07-12 19:30 | 304 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
140303 | 24387 | 8911 |  |  | 2011-07-10 10:30 | 2011-07-10 17:53 | 443 | E0869 | RB 44 kV E4 Circuit Breaker | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
140304 | 24388 | 8912 |  |  | 2011-07-14 00:13 | 2011-07-14 00:56 | 43 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
140305 | 24389 | 8913 |  |  | 2011-07-14 01:03 | 2011-07-14 01:03 | 0 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
140306 | 24390 | 8914 |  |  | 2011-07-14 01:04 | 2011-07-14 01:04 | 0 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
140308 | 24392 | 8917 |  |  | 2011-07-14 01:08 | 2011-07-14 02:41 | 93 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
140309 | 24393 | 8918 |  |  | 2011-07-15 05:06 | 2011-07-15 08:03 | 177 | E1570 | DP 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
140310 | 24394 | 8920 |  |  | 2011-07-16 08:41 | 2011-07-16 08:41 | 0 | E0820 | RA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
140311 | 24395 | 8921 |  |  | 2011-07-18 02:12 | 2011-07-18 02:31 | 19 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
140312 | 24396 | 8922 |  |  | 2011-07-18 23:09 | 2011-07-18 23:27 | 18 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
140313 | 24397 | 8923 |  |  | 2011-07-19 21:49 | 2011-07-19 21:49 | 0 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
140314 | 24398 | 8924 |  |  | 2011-07-20 18:37 | 2011-07-20 18:37 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
140315 | 24399 | 8925 |  |  | 2011-07-23 09:01 | 2011-07-23 09:01 | 0 | E1531 | MY 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
140316 | 24400 | 8926 |  |  | 2011-07-23 20:50 | 2011-07-23 20:51 | 1 | E1550 | DP 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
140317 | 24401 | 8927 |  |  | 2011-07-26 22:00 | 2011-07-26 22:00 | 0 | E0462 | KR 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
150887 | 24402 | 1678 |  |  | 2011-07-31 01:09 | 2011-07-31 07:13 | 364 | E0715 | FA-JB 220 kV Transmission Circuit | Transmission | Fault | Mechanical Failure | Transend | Completed | TRUE | 0 | TRUE |  | IR1139 FA-JB 220kV line tripped with lightning in area, due to broken earth wire. | FALSE | Non-Critical
142557 | 24403 | 1677 |  |  | 2011-07-14 16:05 | 2011-07-15 22:52 | 1847 | E0374 | KI 110/11 kV T2 Transformer Circuit | Transformer | Fault | Ancillary Equipment Failure | Transend | Completed | TRUE | 2281 | TRUE |  | IR1134 KI T2 tripped on Bucholz alarm and caused loss of supply at Kingston substation. | FALSE | Non-Critical
142751 | 24546 | 8928 |  |  | 2011-07-30 13:17 | 2011-07-30 13:59 | 42 | E1550 | DP 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142752 | 24547 | 8929 |  |  | 2011-07-30 14:10 | 2011-07-30 15:32 | 82 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142753 | 24548 | 8930 |  |  | 2011-07-31 02:02 | 2011-07-31 02:02 | 0 | E0185 | TU 22 kV X D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
143796 | 24549 | 8931 |  |  | 2011-08-01 10:54 | 2011-08-01 11:15 | 21 | E1538 | MY 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142874 | 24550 | 8932 |  |  | 2011-08-01 10:54 | 2011-08-01 12:00 | 66 | E1531 | MY 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142875 | 24551 | 8933 |  |  | 2011-08-01 18:29 | 2011-08-01 19:00 | 31 | E1479 | RI 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142876 | 24552 | 8934 |  |  | 2011-08-02 23:28 | 2011-08-02 23:28 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142877 | 24553 | 8935 |  |  | 2011-08-04 09:22 | 2011-08-04 09:22 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142878 | 24554 | 8936 |  |  | 2011-08-05 10:03 | 2011-08-05 10:03 | 0 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142879 | 24555 | 8937 |  |  | 2011-08-05 12:49 | 2011-08-05 12:50 | 1 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142880 | 24556 | 8938 |  |  | 2011-08-06 22:26 | 2011-08-06 22:46 | 20 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142881 | 24557 | 8939 |  |  | 2011-08-07 04:47 | 2011-08-07 06:21 | 94 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142882 | 24558 | 8940 |  |  | 2011-08-08 07:37 | 2011-08-08 07:37 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142883 | 24559 | 8941 |  |  | 2011-08-08 17:25 | 2011-08-08 17:25 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142884 | 24560 | 8942 |  |  | 2011-08-09 08:14 | 2011-08-09 08:49 | 35 | E0083 | CR 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142885 | 24561 | 8943 |  |  | 2011-08-09 10:08 | 2011-08-09 10:08 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142886 | 24562 | 8946 |  |  | 2011-08-10 00:45 | 2011-08-10 00:46 | 1 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142887 | 24563 | 8947 |  |  | 2011-08-10 07:21 | 2011-08-10 07:37 | 16 | E1538 | MY 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142888 | 24564 | 8948 |  |  | 2011-08-11 14:13 | 2011-08-11 14:13 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142889 | 24565 | 8949 |  |  | 2011-08-12 08:51 | 2011-08-12 08:52 | 1 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142890 | 24566 | 8950 |  |  | 2011-08-14 08:04 | 2011-08-14 08:21 | 17 | E0343 | LF 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186063 | 24567 | 8951 |  |  | 2011-08-14 16:35 | 2011-08-14 16:35 | 0 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142892 | 24568 | 8952 |  |  | 2011-08-14 23:52 | 2011-08-14 23:52 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142893 | 24569 | 8953 |  |  | 2011-08-17 16:31 | 2011-08-17 16:51 | 20 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142894 | 24570 | 8954 |  |  | 2011-08-17 19:44 | 2011-08-17 19:44 | 0 | E0464 | KR 11 kV G2 Feeder Circuit | Feeder | Fault |  |  | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142895 | 24571 | 8955 |  |  | 2011-08-18 11:49 | 2011-08-18 12:08 | 19 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142896 | 24572 | 8956 |  |  | 2011-08-21 10:00 | 2011-08-21 10:01 | 1 | E1000 | BU 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142897 | 24573 | 8957 |  |  | 2011-08-22 23:09 | 2011-08-22 23:09 | 0 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142898 | 24574 | 8958 |  |  | 2011-08-23 06:00 | 2011-08-23 06:43 | 43 | E0494 | GT 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
142899 | 24575 | 8959 |  |  | 2011-08-23 14:16 | 2011-08-23 14:54 | 38 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
143030 | 24623 | 8960 |  |  | 2011-08-25 13:17 | 2011-08-25 13:17 | 0 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
143031 | 24624 | 8961 |  |  | 2011-08-25 13:18 | 2011-08-25 13:18 | 0 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
143032 | 24625 | 8962 |  |  | 2011-08-25 13:56 | 2011-08-25 13:56 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
144461 | 24714 | 8963 |  |  | 2011-08-25 13:20 | 2011-08-25 14:36 | 76 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
144462 | 24715 | 88964 |  |  | 2011-08-25 14:35 | 2011-09-13 15:10 | 27395 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
144463 | 24716 | 8965 |  |  | 2011-08-25 23:01 | 2011-08-25 23:02 | 1 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
144464 | 24717 | 8966 |  |  | 2011-08-25 23:31 | 2011-08-25 23:31 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
144465 | 24718 | 8967 |  |  | 2011-08-28 04:54 | 2011-08-28 04:54 | 0 | E0300 | AV 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
144466 | 24719 | 8968 |  |  | 2011-08-28 04:54 | 2011-08-28 04:54 | 0 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
144467 | 24720 | 8969 |  |  | 2011-08-28 18:56 | 2011-08-28 19:53 | 57 | E1480 | RI 33 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
144468 | 24721 | 8970 |  |  | 2011-08-28 18:56 | 2011-08-28 20:07 | 71 | E1482 | RI 33 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
144469 | 24722 | 8971 |  |  | 2011-08-28 18:56 | 2011-09-13 20:08 | 23112 | E1479 | RI 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
146376 | 24782 | 1688 |  |  | 2011-09-19 14:43 | 2011-09-19 16:29 | 106 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Mechanical Failure | Transend | Completed | TRUE | 0 | TRUE |  | IR1164 Farrell-Rosebery-Queenstown transmission circuit tripped due to equipment failure (A helical dead end failed on FA-RB). | FALSE | Non-Critical
169264 | 24782 | 1688 |  |  | 2011-09-19 09:06 | 2011-09-19 09:31 | 25 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Mechanical Failure | Transend | Completed | TRUE | 1021 | TRUE |  | IR1164 Farrell-Rosebery-Queenstown transmission circuit tripped due to equipment failure (A helical dead end failed on FA-RB). | FALSE | Non-Critical
144696 | 24785 | 8973 |  |  | 2011-08-29 00:50 | 2011-08-29 00:51 | 1 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
144697 | 24787 | 8974 |  |  | 2011-08-29 23:38 | 2011-08-29 23:38 | 0 | E0766 | NW 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
144698 | 24788 | 8975 |  |  | 2011-08-31 11:03 | 2011-08-31 11:03 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
144831 | 24789 | 8976 |  |  | 2011-09-01 18:15 | 2011-09-01 18:15 | 0 | E0819 | RA 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
144832 | 24790 | 8977 |  |  | 2011-09-02 03:13 | 2011-09-02 03:13 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
144833 | 24791 | 8978 |  |  | 2011-09-04 03:40 | 2011-09-04 03:40 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
144834 | 24792 | 8979 |  |  | 2011-09-05 14:38 | 2011-09-05 14:38 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145110 | 24793 | 8980 |  |  | 2011-09-07 11:33 | 2011-09-07 11:33 | 0 | E1041 | SD 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145111 | 24794 | 8981 |  |  | 2011-09-10 17:44 | 2011-09-10 17:44 | 0 | E1550 | DP 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145112 | 24795 | 8982 |  |  | 2011-09-11 07:00 | 2011-09-11 07:19 | 19 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145113 | 24796 | 8983 |  |  | 2011-09-12 02:27 | 2011-09-12 02:27 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145257 | 24877 | 8984 |  |  | 2011-09-14 13:42 | 2011-09-14 14:02 | 20 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145258 | 24878 | 8985 |  |  | 2011-09-14 18:22 | 2011-09-14 18:22 | 0 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145259 | 24879 | 8986 |  |  | 2011-09-15 09:29 | 2011-09-15 09:29 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145260 | 24880 | 8987 |  |  | 2011-09-15 15:56 | 2011-09-15 16:38 | 42 | E0111 | CS 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145261 | 24881 | 8988 |  |  | 2011-09-16 03:20 | 2011-09-16 07:52 | 272 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
147508 | 24882 | 1686 |  |  | 2011-09-11 16:34 | 2011-09-11 20:01 | 207 | E0286 | PO-PM 1 110 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1159 Poatina-Palmerston No 1 tripped, due to generator inter trip. | FALSE | Non-Critical
145511 | 24883 | 1687 |  |  | 2011-09-14 14:13 | 2011-09-14 15:13 | 60 | E0784 | PL 22 kV B Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 533 | TRUE |  | IR1161 Port Latta 22kV B Bus tripped due to error during planned work. | FALSE | Undefined
145613 | 24922 | 1696 |  |  | 2011-09-30 10:02 | 2011-09-30 10:07 | 5 | E0026 | LI-CS 2 220 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1175 LI-CS 2 tripped due to unknown cause. | FALSE | Critical
145638 | 24924 | 1695 |  |  | 2011-09-28 10:10 | 2011-09-28 10:29 | 19 | E0139 | TA-NN 2 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1171 TA-NN 110 kV transmiission circuit tripped due to unknown cause. | FALSE | Critical
145639 | 24925 | 1694 |  |  | 2011-09-20 13:54 | 2011-09-21 18:29 | 1715 | E0382 | BU 110/22 kV T6 Transformer Circuit | Transformer | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1170 Burnie T6 tripped due to unknown cause. | FALSE | Non-Critical
195652 | 24926 | 1690 |  |  | 2011-09-19 19:43 | 2011-09-19 19:59 | 16 | E0772 | PL-ST 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1166 BU-PL, BU-ST, SB-WN-ST and PL-ST 110 kV transmission circuits tripped with lightning in area. Loss of supply at Port Latta Substation. | FALSE | Non-Critical
145640 | 24926 | 1690 |  |  | 2011-09-19 19:43 | 2011-09-19 19:58 | 15 | E0401 | BU-PL 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1166 BU-PL, BU-ST, SB-WN-ST and PL-ST 110 kV transmission circuits tripped with lightning in area. Loss of supply at Port Latta Substation. | FALSE | Non-Critical
145641 | 24926 | 1690 |  |  | 2011-09-19 19:43 | 2011-09-19 19:43 | 0 | E0402 | BU-ST 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 209 | TRUE |  | IR1166 BU-PL, BU-ST, SB-WN-ST and PL-ST 110 kV transmission circuits tripped with lightning in area. Loss of supply at Port Latta Substation. | FALSE | Non-Critical
145643 | 24926 | 1690 |  |  | 2011-09-19 19:43 | 2011-09-19 20:06 | 23 | E1565 | BP-SB-ST 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1166 BU-PL, BU-ST, SB-WN-ST and PL-ST 110 kV transmission circuits tripped with lightning in area. Loss of supply at Port Latta Substation. | FALSE | Undefined
180211 | 24927 | 1689 |  |  | 2011-09-19 06:49 | 2011-09-19 10:17 | 208 | E0722 | NT 110 kV XBus | Bus | Fault | Abnormal Operating Conditions | Transend | Completed | TRUE | 3940 | TRUE |  | IR1165 Newton 110 kV bus bar tripped due to T2 Bucholz trip, causing loss of supply. | FALSE | Undefined
145800 | 24928 | 8989 |  |  | 2011-09-17 08:03 | 2011-09-17 08:58 | 55 | E0343 | LF 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145801 | 24929 | 8990 |  |  | 2011-09-19 09:48 | 2011-09-19 09:48 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145802 | 24930 | 8991 |  |  | 2011-09-19 18:03 | 2011-09-19 18:03 | 0 | E0766 | NW 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145803 | 24931 | 8993 |  |  | 2011-09-20 01:09 | 2011-09-20 01:09 | 0 | E1444 | HA 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145804 | 24932 | 8994 |  |  | 2011-09-20 08:09 | 2011-09-20 09:20 | 71 | E1518 | PL 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145805 | 24933 | 8995 |  |  | 2011-09-20 08:39 | 2011-09-20 09:19 | 40 | E0779 | PL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145806 | 24934 | 8996 |  |  | 2011-09-20 12:35 | 2011-09-20 14:52 | 137 | E0185 | TU 22 kV X D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145807 | 24935 | 8997 |  |  | 2011-09-22 19:39 | 2011-09-22 21:30 | 111 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145832 | 24936 | 8998 |  |  | 2011-09-23 00:55 | 2011-09-23 00:55 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145833 | 24937 | 8999 |  |  | 2011-09-26 10:39 | 2011-09-26 10:39 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145834 | 24938 | 9000 |  |  | 2011-09-26 13:43 | 2011-09-26 14:24 | 41 | E0465 | KR 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145835 | 24939 | 9001 |  |  | 2011-09-29 01:35 | 2011-09-29 02:04 | 29 | E1480 | RI 33 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145836 | 24940 | 9002 |  |  | 2011-09-29 21:28 | 2011-09-29 21:29 | 1 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145837 | 24941 | 9003 |  |  | 2011-09-30 06:07 | 2011-09-30 06:07 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145839 | 24943 | 9005 |  |  | 2011-10-04 01:40 | 2011-10-04 01:58 | 18 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145840 | 24944 | 9006 |  |  | 2011-10-06 16:36 | 2011-10-06 16:37 | 1 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145841 | 24945 | 9007 |  |  | 2011-10-06 10:13 | 2011-10-06 10:13 | 0 | E0768 | NW 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145842 | 24946 | 9008 |  |  | 2011-10-08 10:48 | 2011-10-08 12:28 | 100 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
145843 | 24947 | 9009 |  |  | 2011-10-10 09:36 | 2011-10-10 10:46 | 70 | E1550 | DP 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
147439 | 24948 | 1697 |  |  | 2011-10-12 09:13 | 2011-10-12 09:33 | 20 | E0286 | PO-PM 1 110 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1176 PO-PM No 1 110 kV transmission circuit tripped due to intertrip from Poatina power station. | FALSE | Non-Critical
146783 | 25030 | 9010 |  |  | 2011-10-15 10:54 | 2011-10-15 11:12 | 18 | E0842 | RK 11 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
146784 | 25031 | 9011 |  |  | 2011-10-15 13:58 | 2011-10-15 14:22 | 24 | E1504 | TB 22 KV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
146785 | 25032 | 9012 |  |  | 2011-10-18 11:16 | 2011-10-18 11:25 | 9 | E0342 | LF 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
146786 | 25033 | 9013 |  |  | 2011-10-18 13:36 | 2011-10-18 23:16 | 580 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
147304 | 25082 | 1699 |  |  | 2011-10-26 22:34 | 2011-10-27 00:53 | 139 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Basslink | Basslink | Completed | TRUE | 48480 | TRUE |  | IR1179 GT-GC transmission circuit tripped, suspect filter protection trip at Basslink converter station. | FALSE | Undefined
148427 | 25146 | 1709 |  |  | 2011-11-23 16:14 | 2011-11-23 16:44 | 30 | E0136 | NN-BY 2 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1193 New Norfolk-Boyer No.2 transmission circuit tripped | FALSE | Non-Critical
202275 | 25235 | 1718 |  |  | 2011-11-30 03:15 | 2011-11-30 03:15 | 0 | E0438 | HA-GT 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1206 Hadspen - George Town 2 220kV tripped and auto-reclosed | FALSE | Critical
168659 | 25237 | 1716 |  |  | 2011-11-29 06:22 | 2011-11-29 06:41 | 19 | E0615 | GO 220 kV C7 Bus Coupler Circuit | Bus Coupler | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1199 Gordon Substation 220 kV CB C752 tripped. Cause unknown | FALSE | Undefined
168660 | 25238 | 1719 |  |  | 2012-11-26 13:11 | 2012-11-26 14:54 | 103 | E0614 | GO 220 kV C Bus | Bus | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR?? Gordon Substation 200/22 kV T1 and 220 kV B Bus bar trip | FALSE | Undefined
168661 | 25238 | 1719 |  |  | 2011-11-26 09:00 | 2011-11-26 14:54 | 354 | E0617 | GO 220/22 kV T6 Transformer Circuit | Transformer | Fault | Generator | Generator Request | Completed | TRUE | 110 | TRUE |  | IR?? Gordon Substation 200/22 kV T1 and 220 kV B Bus bar trip | FALSE | Non-Critical
202277 | 25239 | 1717 |  |  | 2011-11-30 04:09 | 2011-11-30 15:24 | 675 | E0615 | GO 220 kV C7 Bus Coupler Circuit | Bus Coupler | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1197 Gordon Substation 220 kV B Bus bar trip due to faulted Hydro asset. | FALSE | Undefined
148435 | 25240 | 1708 |  |  | 2011-11-18 14:09 | 2011-11-23 14:55 | 7247 | E0267 | PO-PM 5 220 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1190 PO-PM 5 220 kV TL intertrip | FALSE | Non-Critical
148436 | 25241 | 1721 |  |  | 2011-11-30 06:00 | 2011-11-30 06:08 | 8 | E0029 | CS-RI 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1221 Chapel St - Risdon 110 kV transmission circuit tripped | FALSE | Non-Critical
148437 | 25242 | 1720 |  |  | 2011-11-30 06:00 | 2011-11-30 06:02 | 1 | E0027 | LI-CL-RE-CS 1 220 kV Transmission Circuit (Changed to E1958) | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1203 Liapootah-Repulse-Cluny-Chapel Street 220 kV tripped | FALSE | Critical
148438 | 25243 | 9014 |  |  | 2011-10-22 03:58 | 2011-10-22 03:58 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148439 | 25244 | 9015 |  |  | 2011-10-22 14:40 | 2011-10-22 14:40 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148440 | 25245 | 9016 |  |  | 2011-10-22 20:22 | 2011-10-22 20:22 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148441 | 25246 | 9017 |  |  | 2011-10-24 00:38 | 2011-10-24 02:20 | 102 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148736 | 25247 | 9019 |  |  | 2011-10-24 12:06 | 2011-10-24 12:12 | 6 | E0342 | LF 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148443 | 25248 | 9020 |  |  | 2011-10-26 05:35 | 2011-10-26 05:35 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148444 | 25249 | 9021 |  |  | 2011-10-26 05:35 | 2011-10-26 06:25 | 50 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148445 | 25250 | 9022 |  |  | 2011-10-27 08:40 | 2011-10-27 08:40 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148446 | 25251 | 9023 |  |  | 2011-10-27 22:43 | 2011-10-27 22:43 | 0 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148447 | 25252 | 9024 |  |  | 2011-10-26 00:46 | 2011-10-28 01:04 | 2898 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148448 | 25253 | 9025 |  |  | 2011-10-28 12:06 | 2011-10-28 12:06 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148449 | 25254 | 9026 |  |  | 2011-10-28 07:58 | 2011-10-28 14:12 | 374 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148450 | 25255 | 9027 |  |  | 2011-10-30 10:34 | 2011-10-30 11:08 | 34 | E0084 | CR 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148451 | 25256 | 9028 |  |  | 2011-11-01 05:03 | 2011-11-01 05:03 | 0 | E0158 | MB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148452 | 25257 | 9029 |  |  | 2011-11-02 23:12 | 2011-11-03 00:11 | 59 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148797 | 25258 | 1712 |  |  | 2011-11-24 09:29 | 2011-11-24 09:58 | 29 | E1702 | TE 110 kV Bus SPS | Bus | Fault | Pending Investigation | Basslink | Completed | TRUE | 818 | TRUE |  | SPS trip Temco load | FALSE | Undefined
148453 | 25259 | 9030 |  |  | 2011-11-04 02:30 | 2011-11-04 02:44 | 14 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148454 | 25260 | 9031 |  |  | 2011-11-04 10:18 | 2011-11-04 22:38 | 740 | E0638 | ST 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148455 | 25261 | 9033 |  |  | 2011-11-10 03:13 | 2011-11-10 03:13 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148456 | 25262 | 9034 |  |  | 2011-11-10 09:25 | 2011-11-10 09:25 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148457 | 25263 | 9035 |  |  | 2011-11-10 20:40 | 2011-11-10 20:40 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148458 | 25265 | 9038 |  |  | 2011-11-15 22:34 | 2011-11-15 22:34 | 0 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148460 | 25267 | 9040 |  |  | 2011-11-17 06:31 | 2011-11-17 06:31 | 0 | E0639 | ST 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148462 | 25269 | 9042 |  |  | 2011-11-20 07:22 | 2011-11-20 07:22 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148463 | 25270 | 9043 |  |  | 2011-11-21 05:52 | 2011-11-21 05:52 | 0 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148465 | 25272 | 9046 |  |  | 2011-11-23 18:42 | 2011-11-23 18:56 | 14 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148466 | 25273 | 9047 |  |  | 2011-11-23 23:39 | 2011-11-24 00:32 | 53 | E1613 | UL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148467 | 25274 | 1707 |  |  | 2011-11-11 14:00 | 2011-11-11 15:27 | 87 | E0210 | RI 110/11 kV T1 Transformer Circuit | Transformer | Fault | Pending Investigation | Transend | Completed | TRUE | 0 | TRUE |  | IR1204 Risdon Substation T1 tripped | FALSE | Non-Critical
148468 | 25276 | 9049 |  |  | 2011-11-26 05:16 | 2011-11-26 06:29 | 73 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148469 | 25277 | 9050 |  |  | 2011-11-26 08:41 | 2011-11-26 09:47 | 66 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148470 | 25278 | 9052 |  |  | 2011-11-28 06:40 | 2011-11-28 06:46 | 6 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148471 | 25279 | 9053 |  |  | 2011-11-28 08:48 | 2011-11-28 08:48 | 0 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148473 | 25282 | 9055 |  |  | 2011-11-29 18:26 | 2011-11-29 18:45 | 19 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148474 | 25283 | 9056 |  |  | 2011-11-29 23:43 | 2011-11-30 | 17 | E0496 | GT 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148475 | 25284 | 9057 |  |  | 2011-11-30 07:48 | 2011-11-30 08:20 | 32 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148476 | 25285 | 9058 |  |  | 2011-12-02 16:50 | 2011-12-02 16:50 | 0 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148477 | 25286 | 9059 |  |  | 2011-12-03 09:22 | 2011-12-03 09:44 | 22 | E0946 | UL 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148478 | 25287 | 9060 |  |  | 2011-12-04 00:37 | 2011-12-04 00:37 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148479 | 25288 | 9061 |  |  | 2011-12-06 06:21 | 2011-12-06 06:56 | 35 | E1454 | HA 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
148480 | 25289 | 9062 |  |  | 2011-12-06 10:10 | 2011-12-06 10:42 | 32 | E0083 | CR 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
149808 | 25354 | 1795 |  |  | 2011-12-19 10:22 | 2011-12-20 21:11 | 2089 | E0193 | SO 110/22 kV T2 Transformer Circuit | Transformer | Fault | Moisture Ingress | Transend | Completed | TRUE | 312 | TRUE |  | IR1211 Sorell Substation 110/22kV transformer T2 tripped due to water ingress. Restoration date and time to be determined | FALSE | Non-Critical
149790 | 25394 | 1797 |  |  | 2011-12-25 19:40 | 2011-12-25 19:40 | 0 | E0274 | PM-AV 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1215 Palmerston-Avoca tranmsmission circuit tripped and reclosed with lightning in area. | FALSE | Non-Critical
149791 | 25394 | 1797 |  |  | 2011-12-25 20:11 | 2011-12-25 20:11 | 0 | E0274 | PM-AV 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1215 Palmerston-Avoca tranmsmission circuit tripped and reclosed with lightning in area. | FALSE | Non-Critical
150863 | 25471 | 9167 |  |  | 2011-12-10 06:57 | 2011-12-10 07:17 | 20 | E0078 | CR 33 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
150864 | 25472 | 9169 |  |  | 2011-12-10 20:57 | 2011-12-10 21:24 | 27 | E1560 | HA 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
150865 | 25473 | 9172 |  |  | 2011-12-11 08:32 | 2011-12-11 08:54 | 22 | E0343 | LF 33 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
150866 | 25474 | 9173 |  |  | 2011-12-11 15:42 | 2011-12-11 16:35 | 53 | E1531 | MY 22 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
150899 | 25479 | 9181 |  |  | 2011-12-16 22:00 | 2011-12-16 22:00 | 0 | E1432 | HA 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
150900 | 25480 | 9183 |  |  | 2011-12-19 06:11 | 2011-12-19 06:34 | 23 | E0970 | SO 22 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
150901 | 25481 | 9185 |  |  | 2011-12-19 12:18 | 2011-12-19 12:40 | 22 | E0083 | CR 33 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
150902 | 25482 | 9186 |  |  | 2011-12-19 14:36 | 2011-12-19 14:53 | 17 | E0105 | CS 11 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
151503 | 25518 | 1804 |  |  | 2012-02-01 09:01 | 2012-02-01 09:35 | 34 | E0717 | FA-RC 2 220 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1227 Farell-Reece 220 kV circuit tripped due to intertripping from Hydro. | FALSE | Non-Critical
153289 | 25519 | 1803 |  |  | 2012-02-01 00:31 | 2012-02-01 00:44 | 13 | E0237 | RI 11 kV Q3 Feeder Circuit | Feeder | Fault | Ancillary Equipment Failure | MI | Completed | TRUE | 272 | TRUE |  | IR1226 Nyrstar feeders tripped, suspect due to operation of harmonic filter. | FALSE | Undefined
153290 | 25519 | 1803 |  |  | 2012-02-01 00:31 | 2012-02-01 00:44 | 13 | E0238 | RI 11 kV R3 Feeder Circuit | Feeder | Fault | Ancillary Equipment Failure | MI | Completed | TRUE | 0 | TRUE |  | IR1226 Nyrstar feeders tripped, suspect due to operation of harmonic filter. | FALSE | Undefined
153291 | 25519 | 1803 |  |  | 2012-02-01 12:31 | 2012-02-01 12:45 | 14 | E0239 | RI 11 kV S3 Feeder Circuit | Feeder | Fault | Ancillary Equipment Failure | MI | Completed | TRUE | 0 | TRUE |  | IR1226 Nyrstar feeders tripped, suspect due to operation of harmonic filter. | FALSE | Undefined
151536 | 25520 | 1802 |  |  | 2012-01-29 13:12 | 2012-01-29 19:20 | 368 | E0539 | SH-FA 2 220 kV Transmission Circuit | Transmission | Fault | Vegetation | Transend | Completed | TRUE | 0 | TRUE |  | IR430 Sheffield-Farrell 2 220 kV circuit tripped due to vegetation during hot weather and high loads. | FALSE | Critical
151575 | 25521 | 1801 |  |  | 2012-01-17 19:26 | 2012-01-17 19:26 | 0 | E0025 | NN-CS 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1220 New Norfolk-Chapel St 110 kV transmission circuit tripped with lightning in area. | FALSE | Critical
151576 | 25522 | 9187 |  |  | 2011-12-20 05:04 | 2011-12-20 05:04 | 0 | E1548 | DP 22 kV C2 Capacitor Circuit | Capacitor | Fault |  |  | Completed | FALSE | 0 | TRUE |  |  | FALSE | Undefined
151577 | 25523 | 1800 |  |  | 2012-01-15 05:14 | 2012-01-15 05:19 | 5 | E0264 | PM-HA 4 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1217 Palmerston-Hadspen 4 110 kV transmissionm circuit tripped. | FALSE | Critical
151614 | 25524 | 1799 |  |  | 2012-01-13 18:40 | 2012-01-21 20:12 | 11612 | E0705 | FA 220/110 kV T2 Transformer Circuit | Transformer | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1216 Farrell 220/110 T2 transformer circuit tripped, investigation pending. | FALSE | Non-Critical
151900 | 25525 | 9188 |  |  | 2011-12-20 07:51 | 2011-12-20 08:09 | 18 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
151901 | 25526 | 9189 |  |  | 2011-12-20 18:25 | 2011-12-20 18:52 | 27 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
151902 | 25527 | 9190 |  |  | 2011-12-21 04:29 | 2011-12-21 04:56 | 27 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
151903 | 25528 | 9191 |  |  | 2011-12-21 08:37 | 2011-12-21 09:30 | 53 | E0342 | LF 33 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
151978 | 25566 | 9194 |  |  | 2011-12-24 04:37 | 2011-12-24 04:38 | 1 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152010 | 25567 | 9195 |  |  | 2011-12-24 16:09 | 2011-12-24 16:09 | 0 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152011 | 25568 | 9196 |  |  | 2011-12-24 16:24 | 2011-12-24 19:21 | 177 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152012 | 25569 | 9197 |  |  | 2011-12-24 19:00 | 2011-12-24 19:24 | 24 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152013 | 25570 | 9198 |  |  | 2011-12-24 21:56 | 2011-12-24 21:56 | 0 | E1555 | DP 22 kV P2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152014 | 25571 | 9199 |  |  | 2011-12-25 08:16 | 2011-12-25 08:17 | 1 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152015 | 25572 | 9200 |  |  | 2011-12-25 10:43 | 2011-12-25 16:25 | 342 | E0075 | CR 33 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186080 | 25573 | 9201 |  |  | 2011-12-26 19:19 | 2011-12-26 19:19 | 0 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152359 | 25640 | 1805 |  |  | 2012-02-10 01:51 | 2012-02-10 17:50 | 959 | E0161 | TA-MB 110 kV Transmission Circuit | Transmission | Fault | Wildlife | Transend | Completed | TRUE | 0 | TRUE |  | IR1126 Tarraleah-Meadowbank 110 kV transmission circuit tripped due to broken conductor following a fault due to bird streamer (?). | FALSE | Non-Critical
177797 | 25641 | 1806 |  |  | 2012-02-12 02:50 | 2012-02-12 02:52 | 2 | E0139 | TA-NN 2 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1129 Tarraleah-New Norfolk 2 110 kV transmission circuit tripped. | FALSE | Critical
152360 | 25642 | 1807 |  |  | 2012-02-13 11:43 | 2012-02-13 11:58 | 15 | E0575 | EB 110 kV A Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1130 Emu Bay B 110kV bus bar tripped during testing under a planned outage. | FALSE | Undefined
152393 | 25643 | 9202 |  |  | 2011-12-27 04:41 | 2011-12-27 04:59 | 18 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152394 | 25644 | 9203 |  |  | 2011-12-28 04:42 | 2011-12-28 05:01 | 19 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152395 | 25645 | 9204 |  |  | 2011-12-28 20:29 | 2011-12-28 20:29 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195664 | 25646 | 9205 |  |  | 2011-12-29 08:42 | 2011-12-29 08:42 | 0 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152397 | 25647 | 9206 |  |  | 2011-12-29 10:34 | 2011-12-29 10:34 | 0 | E1042 | SD 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152431 | 25648 | 9207 |  |  | 2011-12-30 19:27 | 2011-12-30 19:45 | 18 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152432 | 25649 | 9208 |  |  | 2011-12-31 18:30 | 2011-12-31 18:30 | 0 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152433 | 25650 | 9209 |  |  | 2011-12-31 22:56 | 2011-12-31 22:56 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
159687 | 25651 | 9210 |  |  | 2012-01-01 08:15 | 2012-01-01 08:15 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152615 | 25652 | 9211 |  |  | 2012-01-02 00:04 | 2012-01-02 00:04 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152616 | 25653 | 9212 |  |  | 2012-01-02 23:54 | 2012-01-02 23:54 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152617 | 25655 | 9214 |  |  | 2012-01-02 09:43 | 2012-01-02 11:56 | 133 | E0078 | CR 33 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152618 | 25656 | 9215 |  |  | 2012-01-02 16:17 | 2012-01-02 16:17 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155367 | 25657 | 9216 |  |  | 2012-01-04 07:48 | 2012-01-04 08:57 | 69 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152619 | 25658 | 9217 |  |  | 2012-01-05 09:20 | 2012-01-05 09:39 | 19 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152620 | 25659 | 9218 |  |  | 2012-01-05 23:54 | 2012-01-05 23:54 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152651 | 25660 | 1808 |  |  | 2012-02-13 12:40 | 2012-02-13 12:45 | 5 | E0575 | EB 110 kV A Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1131 Emu Bay 110kV Bus tripped during testing under a planned outage. | FALSE | Undefined
152652 | 25661 | 1809 |  |  | 2012-02-14 07:34 | 2012-02-14 07:55 | 21 | E0323 | BY 6.6 kV E Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 20 | TRUE |  | IR1132 Boyer 6.6 kV E Bus Bar tripped during planned work. | FALSE | Undefined
153184 | 25662 | 1810 |  |  | 2012-02-18 10:31 | 2012-02-18 10:40 | 9 | E0717 | FA-RC 2 220 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1133 Farrell-Reece 2 220kV transmission circuit tripped due to intertrip signal from generation. | FALSE | Non-Critical
152654 | 25663 | 1812 |  |  | 2012-02-25 21:08 | 2012-02-25 21:13 | 5 | E0940 | UL 22 kV A Bus | Bus | Fault | Poor Construction | Transend | Completed | TRUE | 153 | TRUE |  | IR1134 Ulverstone feeders (all) tripped during bush fire response, suspect script calc error. | FALSE | Undefined
153294 | 25663 | 1812 |  |  | 2012-02-25 21:08 | 2012-02-25 21:13 | 5 | E0941 | UL 22 kV B Bus | Bus | Fault | Poor Construction | Transend | Completed | TRUE | 0 | TRUE |  | IR1134 Ulverstone feeders (all) tripped during bush fire response, suspect script calc error. | FALSE | Undefined
152666 | 25664 | 9219 |  |  | 2012-01-07 00:57 | 2012-01-07 00:57 | 0 | E0638 | ST 22 kV J2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152667 | 25665 | 9220 |  |  | 2012-01-06 01:09 | 2012-01-06 01:10 | 1 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152668 | 25666 | 9221 |  |  | 2012-01-07 07:16 | 2012-01-07 10:13 | 177 | E0075 | CR 33 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152669 | 25667 | 9222 |  |  | 2012-01-08 07:47 | 2012-01-08 07:47 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152670 | 25668 | 9223 |  |  | 2012-01-12 20:13 | 2012-01-12 20:32 | 19 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152671 | 25669 | 9224 |  |  | 2012-01-13 01:25 | 2012-01-13 01:25 | 0 | E1507 | SD 22 kV J2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152672 | 25670 | 9225 |  |  | 2012-01-14 01:32 | 2012-01-14 01:32 | 0 | E0838 | RK 11 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152673 | 25671 | 9226 |  |  | 2012-01-14 22:38 | 2012-01-14 22:39 | 1 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152674 | 25672 | 9227 |  |  | 2012-01-15 07:53 | 2012-01-15 09:00 | 67 | E1479 | RI 33 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152675 | 25673 | 9228 |  |  | 2012-01-17 08:47 | 2012-01-17 10:32 | 105 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152676 | 25674 | 9229 |  |  | 2012-01-17 10:53 | 2012-01-17 11:30 | 37 | E1481 | RI 33 kV J2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152678 | 25676 | 9232 |  |  | 2012-01-17 19:26 | 2012-01-17 19:46 | 20 | E0197 | SO 22 kV A2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152679 | 25677 | 9233 |  |  | 2012-01-17 20:20 | 2012-01-17 20:20 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153331 | 25854 | 9234 |  |  | 2012-01-17 21:04 | 2012-01-17 21:33 | 29 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153332 | 25855 | 9235 |  |  | 2012-01-18 22:46 | 2012-01-18 22:46 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153333 | 25856 | 9236 |  |  | 2012-01-21 06:13 | 2012-01-21 06:13 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153334 | 25857 | 9237 |  |  | 2012-01-21 20:27 | 2012-01-21 20:27 | 0 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153335 | 25858 | 9238 |  |  | 2012-01-23 12:29 | 2012-01-23 12:29 | 0 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153336 | 25859 | 9239 |  |  | 2012-01-23 22:45 | 2012-01-23 22:46 | 1 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153338 | 25861 | 9241 |  |  | 2012-01-24 09:05 | 2012-01-24 09:05 | 0 | E0764 | NW 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153339 | 25862 | 9242 |  |  | 2012-01-24 19:01 | 2012-01-24 19:23 | 22 | E0844 | RK 11 kV J2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153340 | 25863 | 9243 |  |  | 2012-01-26 01:16 | 2012-01-26 01:17 | 1 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
159705 | 25864 | 9244 |  |  | 2012-01-26 16:54 | 2012-01-26 17:16 | 22 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153342 | 25865 | 9245 |  |  | 2012-01-29 07:14 | 2012-01-29 07:14 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153343 | 25866 | 9246 |  |  | 2012-01-29 13:47 | 2012-01-29 13:47 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153358 | 25867 | 9247 |  |  | 2012-01-29 16:29 | 2012-01-29 16:29 | 0 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153359 | 25868 | 9248 |  |  | 2012-01-29 16:30 | 2012-01-29 18:03 | 93 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153360 | 25869 | 9429 |  |  | 2012-01-29 20:57 | 2012-01-29 20:57 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153361 | 25870 | 9250 |  |  | 2012-01-30 14:25 | 2012-01-30 14:46 | 21 | E0446 | KE 11 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153362 | 25871 | 9251 |  |  | 2012-01-30 15:55 | 2012-01-30 16:45 | 50 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153363 | 25872 | 9252 |  |  | 2012-01-30 19:03 | 2012-01-30 19:03 | 0 | E1613 | UL 22 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153365 | 25874 | 9254 |  |  | 2012-01-30 21:11 | 2012-01-30 21:11 | 0 | E0083 | CR 33 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153368 | 25877 | 9253 |  |  | 2012-01-30 20:12 | 2012-01-30 22:29 | 137 | E0075 | CR 33 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153369 | 25878 | 9256 |  |  | 2012-01-31 06:35 | 2012-01-31 06:35 | 0 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153784 | 25962 | 9257 |  |  | 2011-01-31 07:49 | 2012-01-31 08:09 | 525620 | E0012 | BW 11 kV A2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153786 | 25964 | 9258 |  |  | 2012-02-01 17:35 | 2012-02-01 17:56 | 21 | E0488 | GT 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153787 | 25965 | 9259 |  |  | 2012-02-01 18:43 | 2012-02-01 18:43 | 0 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153788 | 25966 | 9260 |  |  | 2012-02-01 20:46 | 2012-02-01 20:46 | 0 | E0389 | BU 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153789 | 25967 | 9261 |  |  | 2012-02-01 22:46 | 2012-02-01 22:46 | 0 | E0764 | NW 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153790 | 25968 | 9262 |  |  | 2012-02-01 23:14 | 2012-02-01 23:33 | 19 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153791 | 25969 | 9263 |  |  | 2012-02-02 03:14 | 2012-02-02 03:14 | 0 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153956 | 25970 | 9265 |  |  | 2012-02-02 17:47 | 2012-02-02 17:47 | 0 | E0766 | NW 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153957 | 25971 | 9266 |  |  | 2012-02-05 02:26 | 2012-02-05 02:47 | 21 | E0123 | CS 11 kV Y2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153958 | 25972 | 9268 |  |  | 2012-02-05 18:29 | 2012-02-05 20:15 | 106 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153959 | 25973 | 9269 |  |  | 2012-02-05 21:10 | 2012-02-05 21:10 | 0 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153960 | 25974 | 9270 |  |  | 2012-02-05 21:22 | 2012-02-05 21:22 | 0 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153961 | 25975 | 9271 |  |  | 2012-02-05 23:11 | 2012-02-05 23:11 | 0 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153962 | 25976 | 9272 |  |  | 2012-02-05 23:11 | 2012-02-05 23:29 | 18 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153963 | 25977 | 9273 |  |  | 2012-02-05 23:12 | 2012-02-05 23:29 | 17 | E0491 | GT 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153964 | 25978 | 9274 |  |  | 2012-02-06 17:57 | 2012-02-06 18:20 | 23 | E0489 | GT 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153965 | 25979 | 9276 |  |  | 2012-02-07 22:34 | 2012-02-07 22:49 | 15 | E0842 | RK 11 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153966 | 25980 | 9277 |  |  | 2012-02-08 08:54 | 2012-02-08 09:15 | 21 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153967 | 25981 | 9278 |  |  | 2012-02-09 20:39 | 2012-02-09 20:39 | 0 | E0387 | BU 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
153968 | 25982 | 9279 |  |  | 2012-02-09 20:39 | 2012-02-09 20:39 | 0 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
159707 | 26044 | 9240 |  |  | 2012-01-23 22:05 | 2012-02-11 09:00 | 26575 | E0014 | BW 11 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154349 | 26045 | 9280 |  |  | 2012-02-11 21:36 | 2012-02-11 21:36 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154350 | 26046 | 9281 |  |  | 2012-02-12 00:06 | 2012-02-12 00:07 | 1 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154351 | 26047 | 9282 |  |  | 2012-02-12 20:29 | 2012-02-12 20:50 | 21 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154353 | 26049 | 9284 |  |  | 2012-02-12 21:05 | 2012-02-12 21:05 | 0 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154422 | 26050 | 9285 |  |  | 2012-02-13 06:15 | 2012-02-13 06:15 | 0 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154423 | 26051 | 9286 |  |  | 2012-02-13 12:21 | 2012-02-13 12:21 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154424 | 26052 | 9287 |  |  | 2012-02-13 12:59 | 2012-02-13 13:00 | 1 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154425 | 26053 | 9288 |  |  | 2012-02-13 16:47 | 2012-02-13 17:43 | 56 | E0081 | CR 33 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154426 | 26054 | 9289 |  |  | 2012-02-13 21:12 | 2012-02-13 21:12 | 0 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154729 | 26055 | 9290 |  |  | 2012-02-13 21:29 | 2012-02-13 21:29 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
159689 | 26056 | 9291 |  |  | 2012-02-14 06:31 | 2012-02-14 06:31 | 0 | E1555 | DP 22 kV P2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154731 | 26057 | 9292 |  |  | 2012-02-14 04:32 | 2012-02-14 06:07 | 95 | E1538 | MY 22 kV P2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154732 | 26058 | 9293 |  |  | 2012-02-14 06:51 | 2012-02-14 06:52 | 1 | E0904 | TR 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154733 | 26059 | 9294 |  |  | 2012-02-14 09:52 | 2012-02-14 10:45 | 53 | E0845 | RK 11 kV K2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186084 | 26060 | 9295 |  |  | 2012-02-15 10:26 | 2012-02-15 10:27 | 1 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154735 | 26061 | 9296 |  |  | 2012-02-15 19:30 | 2012-02-15 19:46 | 16 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154736 | 26062 | 9297 |  |  | 2012-02-16 18:59 | 2012-02-16 19:25 | 26 | E0488 | GT 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154737 | 26063 | 9298 |  |  | 2012-02-17 03:09 | 2012-02-17 03:09 | 0 | E1454 | HA 22 kV L2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154738 | 26064 | 9299 |  |  | 2012-02-17 07:36 | 2012-02-17 07:36 | 0 | E0727 | QT 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154739 | 26065 | 9300 |  |  | 2012-02-17 18:13 | 2012-02-17 18:13 | 0 | E1573 | DP 22 kV M2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154740 | 26066 | 9301 |  |  | 2012-02-18 20:27 | 2012-02-18 20:27 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154741 | 26067 | 9302 |  |  | 2012-02-19 10:37 | 2012-02-19 11:52 | 75 | E0496 | GT 22 kV N2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154742 | 26068 | 9303 |  |  | 2012-02-19 10:37 | 2012-02-19 11:48 | 71 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
154743 | 26069 | 9304 |  |  | 2012-02-19 14:45 | 2012-02-19 14:45 | 0 | E0496 | GT 22 kV N2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155180 | 26070 | 9305 |  |  | 2012-02-20 11:25 | 2012-02-20 11:30 | 5 | E0197 | SO 22 kV A2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155181 | 26071 | 9307 |  |  | 2012-02-22 00:28 | 2012-02-22 00:28 | 0 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155182 | 26072 | 9308 |  |  | 2012-02-20 23:54 | 2012-02-21 00:39 | 45 | E0744 | NH 11 kV P2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155184 | 26074 | 9310 |  |  | 2012-02-22 02:03 | 2012-02-22 02:25 | 22 | E0489 | GT 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155185 | 26075 | 9311 |  |  | 2012-02-23 03:00 | 2012-02-23 03:01 | 1 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155186 | 26076 | 9312 |  |  | 2012-02-23 23:58 | 2012-02-23 23:58 | 0 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155187 | 26077 | 9314 |  |  | 2012-02-25 05:31 | 2012-02-25 05:31 | 0 | E1432 | HA 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155188 | 26078 | 9317 |  |  | 2012-02-26 05:55 | 2012-02-26 06:49 | 54 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155604 | 26119 | 9318 |  |  | 2012-02-26 09:30 | 2012-02-26 10:25 | 55 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155605 | 26120 | 9319 |  |  | 2012-02-26 14:22 | 2012-02-26 14:53 | 31 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155607 | 26122 | 9321 |  |  | 2012-02-27 06:25 | 2012-02-27 06:44 | 19 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155608 | 26123 | 9316 |  |  | 2012-02-25 17:54 | 2012-02-27 15:34 | 2740 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155609 | 26124 | 9315 |  |  | 2012-02-25 17:54 | 2012-02-27 15:37 | 2743 | E0156 | MB 22 kV A2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155610 | 26125 | 9322 |  |  | 2012-02-27 22:52 | 2012-02-27 22:52 | 0 | E0944 | UL 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155963 | 26127 | 9325 |  |  | 2012-03-01 00:03 | 2012-03-01 00:03 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
155983 | 26160 | 9326 |  |  | 2012-03-01 09:49 | 2012-03-01 10:27 | 38 | E0012 | BW 11 kV A2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
168502 | 26161 | 1813 |  |  | 2012-03-15 23:18 | 2012-03-15 23:25 | 7 | E0276 | PM-AL 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 45 | TRUE |  | IR1276 Palmerston-Arthurs Lake 110kV transmission circuit tripped with lightning in the area, suspect lightning. | FALSE | Non-Critical
156103 | 26162 | 1814 |  |  | 2012-03-20 14:33 | 2012-03-20 14:46 | 13 | E0373 | KI 110/11 kV T1 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 136 | TRUE |  | IR1273 Kingston T2 tripped due to an error during commissioning. | FALSE | Non-Critical
156513 | 26180 | 1815 |  |  | 2012-04-06 20:43 | 2012-04-06 20:43 | 0 | E0438 | HA-GT 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1279 HA-GT 2 220 kV transmission circuit tripped and autoreclosed due to lightning. MI Rio lost load. | FALSE | Critical
156520 | 26182 | 9327 |  |  | 2012-03-02 00:08 | 2012-03-02 00:08 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
156521 | 26184 | 9329 |  |  | 2012-03-02 00:25 | 2012-03-02 02:23 | 118 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173808 | 26185 | 9330 |  |  | 2012-03-03 05:49 | 2012-03-03 07:15 | 86 | E0391 | BU 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
156774 | 26186 | 1816 |  |  | 2012-04-06 19:35 | 2012-04-06 21:14 | 99 | E0397 | BU 220/110 kV T2 Transformer Circuit | Transformer | Fault | Adverse Weather | Transend | Completed | TRUE | 1174 | TRUE |  | IR1135 Burnie 110 kV transmission line circuits tripped during severe lightning with LOS at Burnie, Ulverstone, Emu Bay, Port Latta, Smithton and Hampshire substations. | FALSE | Non-Critical
156775 | 26186 | 1816 |  |  | 2012-04-06 19:35 | 2012-04-06 19:47 | 12 | E0399 | BU-EB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1135 Burnie 110 kV transmission line circuits tripped during severe lightning with LOS at Burnie, Ulverstone, Emu Bay, Port Latta, Smithton and Hampshire substations. | FALSE | Non-Critical
156776 | 26186 | 1816 |  |  | 2012-04-06 19:35 | 2012-04-06 19:59 | 24 | E0400 | BU-HM 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1135 Burnie 110 kV transmission line circuits tripped during severe lightning with LOS at Burnie, Ulverstone, Emu Bay, Port Latta, Smithton and Hampshire substations. | FALSE | Non-Critical
156777 | 26186 | 1816 |  |  | 2012-04-06 19:35 | 2012-04-06 19:55 | 20 | E0401 | BU-PL 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1135 Burnie 110 kV transmission line circuits tripped during severe lightning with LOS at Burnie, Ulverstone, Emu Bay, Port Latta, Smithton and Hampshire substations. | FALSE | Non-Critical
156778 | 26186 | 1816 |  |  | 2012-04-06 19:35 | 2012-04-06 19:57 | 22 | E0402 | BU-ST 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1135 Burnie 110 kV transmission line circuits tripped during severe lightning with LOS at Burnie, Ulverstone, Emu Bay, Port Latta, Smithton and Hampshire substations. | FALSE | Non-Critical
156779 | 26186 | 1816 |  |  | 2012-04-06 19:35 | 2012-04-06 19:41 | 6 | E0404 | SH-BU 2 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1135 Burnie 110 kV transmission line circuits tripped during severe lightning with LOS at Burnie, Ulverstone, Emu Bay, Port Latta, Smithton and Hampshire substations. | FALSE | Non-Critical
156760 | 26240 | 9331 |  |  | 2012-03-03 18:10 | 2012-03-03 18:10 | 0 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186554 | 26242 | 9332 |  |  | 2012-03-04 02:40 | 2012-03-04 02:40 | 0 | E0655 | SM 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
158209 | 26243 | 9334 |  |  | 2012-03-07 21:18 | 2012-03-07 21:37 | 19 | E0015 | BW 11 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
156781 | 26244 | 1822 |  |  | 2012-04-11 12:46 | 2012-04-11 12:56 | 10 | E0030 | CS-KI-KR 110 kV Transmission Circuit (changed to E1955) | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 145 | TRUE |  | IR1275 CS-KI-KR 110 kV transmission line circuit tripped during planned work when a tree contacted line. | FALSE | Non-Critical
156782 | 26245 | 1828 |  |  | 2012-04-18 15:49 | 2012-04-18 16:09 | 20 | E0291 | PM-SH 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1278 PM-SH 220kV tripped during planned work causing NCSPS operation and shedding of Reece generation. | FALSE | Critical
156783 | 26246 | 9336 |  |  | 2012-03-09 06:42 | 2012-03-09 06:43 | 1 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
159690 | 26247 | 9337 |  |  | 2012-03-12 07:39 | 2012-03-12 09:13 | 94 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
156786 | 26248 | 9338 |  |  | 2012-03-12 09:35 | 2012-03-12 09:57 | 22 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
156787 | 26249 | 9340 |  |  | 2012-03-13 18:44 | 2012-03-13 18:44 | 0 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
156788 | 26250 | 9340 |  |  | 2012-03-14 23:49 | 2012-03-15 00:41 | 52 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186085 | 26251 | 9342 |  |  | 2012-03-15 23:18 | 2012-03-15 23:33 | 15 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
156790 | 26252 | 9344 |  |  | 2012-03-17 06:08 | 2012-03-17 06:14 | 6 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
156791 | 26253 | 9347 |  |  | 2012-03-18 19:36 | 2012-03-18 19:38 | 2 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
157099 | 26330 | 9348 |  |  | 2012-03-19 18:30 | 2012-03-19 18:30 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191439 | 26331 | 9350 |  |  | 2012-03-21 06:00 | 2012-03-21 06:00 | 0 | E0820 | RA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
157101 | 26332 | 9351 |  |  | 2012-03-21 10:06 | 2012-03-21 10:06 | 0 | E0760 | NW 22 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
157102 | 26333 | 9352 |  |  | 2012-03-21 10:06 | 2012-03-21 10:06 | 0 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
157103 | 26335 | 9355 |  |  | 2012-03-23 17:59 | 2012-03-23 18:09 | 10 | E1555 | DP 22 kV P2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
157104 | 26336 | 9356 |  |  | 2012-03-23 11:23 | 2012-03-23 20:06 | 523 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
157105 | 26337 | 9357 |  |  | 2012-03-25 16:10 | 2012-03-25 16:10 | 0 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
157106 | 26338 | 9358 |  |  | 2012-03-26 22:31 | 2012-03-26 22:31 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
157107 | 26339 | 9359 |  |  | 2012-03-27 06:37 | 2012-03-27 06:37 | 0 | E1041 | SD 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
157108 | 26340 | 9361 |  |  | 2012-03-29 11:27 | 2012-03-29 12:05 | 38 | E1538 | MY 22 kV P2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
157109 | 26341 | 9362 |  |  | 2012-03-30 04:30 | 2012-03-30 04:49 | 19 | E1481 | RI 33 kV J2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
157110 | 26342 | 9364 |  |  | 2012-04-01 02:24 | 2012-04-01 02:24 | 0 | E1531 | MY 22 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
160352 | 26501 | 1830 |  |  | 2012-05-07 23:47 | 2012-05-08 02:06 | 139 | E0316 | BY 6.6 kV A Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 1586 | TRUE |  | IR1282 Boyer 6.6kV A and B bus circuits tripped due to a protection deficiency following faulted customer feeder. | FALSE | Undefined
160353 | 26501 | 1830 |  |  | 2012-05-07 23:47 | 2012-05-08 02:04 | 137 | E0318 | BY 6.6 kV B Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR1282 Boyer 6.6kV A and B bus circuits tripped due to a protection deficiency following faulted customer feeder. | FALSE | Undefined
160354 | 26502 | 1832 |  |  | 2012-05-11 23:02 | 2012-05-12 00:11 | 69 | E0316 | BY 6.6 kV A Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 771 | TRUE |  | IR1284 Boyer 6.6 kV A and B bus circuits tripped due to protection deficiency following faulted customer feeder. | FALSE | Undefined
160355 | 26502 | 1832 |  |  | 2012-05-11 23:02 | 2012-05-12 00:07 | 65 | E0318 | BY 6.6 kV B Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR1284 Boyer 6.6 kV A and B bus circuits tripped due to protection deficiency following faulted customer feeder. | FALSE | Undefined
168181 | 26504 | 9365 |  |  | 2012-04-01 22:29 | 2012-04-01 22:51 | 22 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
158245 | 26505 | 9366 |  |  | 2012-04-02 14:30 | 2012-04-02 14:30 | 0 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191443 | 26506 | 9367 |  |  | 2012-04-03 22:07 | 2012-04-03 22:07 | 0 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
168182 | 26507 | 9368 |  |  | 2012-04-04 09:18 | 2012-04-04 12:01 | 163 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
158248 | 26508 | 9369 |  |  | 2012-04-05 00:40 | 2012-04-05 00:41 | 1 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
158249 | 26509 | 9370 |  |  | 2012-04-05 06:29 | 2012-04-05 06:29 | 0 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
158250 | 26510 | 9371 |  |  | 2012-04-05 16:52 | 2012-04-05 16:52 | 0 | E1548 | DP 22 kV C2 Capacitor Circuit | Capacitor | Fault |  |  | Completed | FALSE | 0 | TRUE |  |  | FALSE | Undefined
158251 | 26511 | 9372 |  |  | 2012-04-06 19:48 | 2012-04-06 20:32 | 44 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
158252 | 26512 | 9374 |  |  | 2012-04-06 19:49 | 2012-04-06 20:31 | 42 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
158253 | 26513 | 9375 |  |  | 2012-04-06 20:39 | 2012-04-06 20:39 | 0 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
158488 | 26515 | 9376 |  |  | 2012-04-06 20:47 | 2012-04-06 20:47 | 0 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
158256 | 26516 | 9377 |  |  | 2012-04-06 20:57 | 2012-04-06 20:57 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
168183 | 26517 | 9378 |  |  | 2012-04-06 20:57 | 2012-04-06 20:57 | 0 | E0495 | GT 22 kV M2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
158258 | 26518 | 9379 |  |  | 2012-04-06 21:05 | 2012-04-06 21:05 | 0 | E1444 | HA 22 kV K2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
158259 | 26519 | 9380 |  |  | 2012-04-06 20:48 | 2012-04-06 21:06 | 18 | E0491 | GT 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
158260 | 26520 | 9381 |  |  | 2012-03-06 21:11 | 2012-03-06 21:11 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
158261 | 26521 | 9382 |  |  | 2012-04-06 20:41 | 2012-04-06 21:13 | 32 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
158330 | 26555 | 1835 |  |  | 2012-05-13 01:44 | 2012-05-13 01:53 | 9 | E0029 | CS-RI 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1144 GO-CS 2 220kV tripped due to lightning and CS-RI 110kV transmission circuits tripped due to protection error. Load shed at Norske and Nyrstar. GO-CS out due to lightning, however CS-RI tripped too due to protection error. Nyrstar and Norske dropped off about 15MW and 10MW respectively. | FALSE | Non-Critical
158331 | 26555 | 1835 |  |  | 2012-05-13 01:44 | 2012-05-13 01:53 | 9 | E0243 | GO-CS 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1144 GO-CS 2 220kV tripped due to lightning and CS-RI 110kV transmission circuits tripped due to protection error. Load shed at Norske and Nyrstar. GO-CS out due to lightning, however CS-RI tripped too due to protection error. Nyrstar and Norske dropped off about 15MW and 10MW respectively. | FALSE | Critical
158332 | 26556 | 1837 |  |  | 2012-05-23 21:42 | 2012-05-23 21:42 | 0 | E0406 | FA-QU-SR-HM 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1146 FA-QU-SR-HM 110kV transmission circuit tripped and automatically reclosed with lightning in area, with load shed at Que and Savage River. Savage River and Que shed about 20MW and 6MW respectively. | FALSE | Non-Critical
158334 | 26557 | 1834 |  |  | 2012-05-12 05:46 | 2012-05-12 06:00 | 14 | E0721 | QT-NT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 41 | TRUE |  | IR1142 FA-RB-QT and QT-NT 110kV transmission circuit tripped with lightning in area with loss of supply to Aurora (Henty Gold) | FALSE | Non-Critical
158333 | 26557 | 1834 |  |  | 2012-05-12 05:46 | 2012-05-12 05:46 | 0 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1142 FA-RB-QT and QT-NT 110kV transmission circuit tripped with lightning in area with loss of supply to Aurora (Henty Gold) | FALSE | Non-Critical
186091 | 26558 | 1831 |  |  | 2012-05-10 10:36 | 2012-05-10 11:53 | 77 | E0293 | AL 110/6.6 kV T1 Transformer Circuit | Transformer | Fault | Unknown | Transend | Completed | TRUE | 493 | TRUE |  | IR1140 Arthurs Lake T1 transformer circuit tripped with loss of supply at Arthurs Lake when Hydro Pumps were started. investigation not conclusive due to lack of SOE data and lack of protection testing/ investigation. | FALSE | Non-Critical
158336 | 26559 | 1829 |  |  | 2012-04-06 20:09 | 2012-04-06 20:09 | 0 | E0291 | PM-SH 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1139 PM-SH 220kV transmission circuit tripped and auto reclosed with lightning in area. | FALSE | Critical
159672 | 26635 | 1838 |  |  | 2012-05-28 06:04 | 2012-05-28 06:08 | 4 | E0437 | HA-GT 1 220 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1147 HA-GT 220kV transmission circuit tripped. Under investigation. | FALSE | Critical
173817 | 26673 | 9383 |  |  | 2012-04-06 21:11 | 2012-04-06 21:34 | 23 | E1560 | HA 22 kV P2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162480 | 26674 | 9384 |  |  | 2012-04-06 21:08 | 2012-04-06 21:58 | 50 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162481 | 26675 | 9385 |  |  | 2012-04-06 21:35 | 2012-04-06 21:53 | 18 | E1518 | PL 22 kV J2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166081 | 26676 | 9386 |  |  | 2012-04-06 22:25 | 2012-04-06 22:25 | 0 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162483 | 26677 | 9387 |  |  | 2012-04-06 21:02 | 2012-04-06 23:03 | 121 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162484 | 26678 | 9388 |  |  | 2012-04-06 21:14 | 2012-04-06 23:35 | 141 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162485 | 26679 | 9389 |  |  | 2012-04-07 02:02 | 2012-04-07 02:02 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162486 | 26680 | 9390 |  |  | 2012-04-07 22:44 | 2012-04-07 22:44 | 0 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162487 | 26681 | 9391 |  |  | 2012-04-10 07:03 | 2012-04-10 07:04 | 1 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191444 | 26682 | 9392 |  |  | 2012-04-11 13:14 | 2012-04-11 13:15 | 1 | E0825 | RA 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173818 | 26683 | 9393 |  |  | 2012-04-12 11:07 | 2012-04-12 11:07 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162489 | 26684 | 9394 |  |  | 2012-04-14 19:09 | 2012-04-14 19:37 | 28 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162490 | 26685 | 9395 |  |  | 2012-04-16 16:08 | 2012-04-16 16:08 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162491 | 26686 | 9396 |  |  | 2012-04-16 22:47 | 2012-04-16 22:47 | 0 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162492 | 26687 | 9397 |  |  | 2012-04-17 08:53 | 2012-04-17 08:53 | 0 | E0943 | UL 22 kV A2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162493 | 26688 | 9440 |  |  | 2012-05-13 19:41 | 2012-05-13 20:12 | 31 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162494 | 26689 | 9398 |  |  | 2012-04-17 09:09 | 2012-04-17 09:09 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162495 | 26691 | 9400 |  |  | 2012-04-20 13:49 | 2012-04-20 15:02 | 73 | E0446 | KE 11 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162496 | 26692 | 9401 |  |  | 2012-04-20 18:20 | 2012-04-20 18:20 | 0 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162497 | 26693 | 9402 |  |  | 2012-04-21 06:57 | 2012-04-21 06:57 | 0 | E0450 | KE 11 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
180236 | 26694 | 9403 |  |  | 2012-04-22 23:04 | 2012-04-22 23:04 | 0 | E0725 | NT 22 kV A2X Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162499 | 26695 | 9404 |  |  | 2012-04-23 07:10 | 2012-04-23 07:28 | 18 | E1504 | TB 22 KV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162500 | 26696 | 9405 |  |  | 2012-04-23 11:48 | 2012-04-23 11:48 | 0 | E1444 | HA 22 kV K2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162653 | 26697 | 9407 |  |  | 2012-04-23 16:34 | 2012-04-23 16:34 | 0 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162654 | 26698 | 9410 |  |  | 2012-04-24 11:59 | 2012-04-24 11:59 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
162807 | 26699 | 9412 |  |  | 2012-04-25 07:42 | 2012-04-25 07:42 | 0 | E1826 | TU 22kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
173819 | 26700 | 9413 |  |  | 2012-04-26 20:25 | 2012-04-26 21:50 | 85 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163417 | 26701 | 9414 |  |  | 2012-04-27 21:04 | 2012-04-27 21:04 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163418 | 26702 | 9415 |  |  | 2012-04-27 21:04 | 2012-04-27 21:04 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
176748 | 26703 | 9416 |  |  | 2012-04-28 11:46 | 2012-04-28 14:42 | 176 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163420 | 26704 | 9417 |  |  | 2012-04-28 16:31 | 2012-04-28 16:31 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163421 | 26705 | 9418 |  |  | 2012-04-28 22:42 | 2012-04-29 00:02 | 80 | E1478 | RI 33 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163422 | 26706 | 9419 |  |  | 2012-04-28 23:05 | 2012-04-29 00:01 | 56 | E1480 | RI 33 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163424 | 26708 | 9420 |  |  | 2012-04-29 02:07 | 2012-04-29 19:20 | 1033 | E1482 | RI 33 kV K2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163425 | 26709 | 9422 |  |  | 2012-04-29 20:09 | 2012-04-29 20:09 | 0 | E1531 | MY 22 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163426 | 26710 | 9423 |  |  | 2012-04-30 12:42 | 2012-04-30 12:42 | 0 | E1004 | BU 22 kV P2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163427 | 26711 | 9424 |  |  | 2012-05-02 00:59 | 2012-05-02 01:17 | 18 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163428 | 26712 | 9425 |  |  | 2012-05-02 01:21 | 2012-05-02 01:21 | 0 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163429 | 26713 | 9426 |  |  | 2012-05-02 09:35 | 2012-05-02 10:00 | 25 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163430 | 26714 | 9428 |  |  | 2012-05-02 17:19 | 2012-05-02 17:19 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163431 | 26715 | 9429 |  |  | 2012-05-03 23:18 | 2012-05-03 23:19 | 1 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163432 | 26716 | 9430 |  |  | 2012-05-04 08:32 | 2012-05-04 08:33 | 1 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163433 | 26717 | 9432 |  |  | 2012-05-05 18:00 | 2012-05-06 02:55 | 535 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163434 | 26718 | 9433 |  |  | 2012-05-06 07:31 | 2012-05-06 07:31 | 0 | E1826 | TU 22kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
163435 | 26719 | 9434 |  |  | 2012-05-07 01:41 | 2012-05-07 01:41 | 0 | E1826 | TU 22kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
163436 | 26720 | 9435 |  |  | 2012-05-09 12:22 | 2012-05-09 13:53 | 91 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163437 | 26721 | 9436 |  |  | 2012-05-11 06:20 | 2012-05-11 07:07 | 47 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173820 | 26722 | 9437 |  |  | 2012-05-12 00:09 | 2012-05-12 00:09 | 0 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163438 | 26723 | 9438 |  |  | 2012-05-13 08:34 | 2012-05-13 09:29 | 55 | E1482 | RI 33 kV K2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
163439 | 26724 | 9439 |  |  | 2012-05-13 11:16 | 2012-05-13 11:32 | 16 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
164192 | 26725 | 9335 |  |  | 2012-03-08 16:43 | 2012-03-08 17:41 | 58 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
164193 | 26726 | 9343 |  |  | 2012-03-17 03:44 | 2012-03-17 04:04 | 20 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
164194 | 26727 | 9345 |  |  | 2012-03-18 14:50 | 2012-03-18 14:51 | 1 | E1000 | BU 22 kV K2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
164195 | 26728 | 9346 |  |  | 2012-03-18 18:22 | 2012-03-18 18:43 | 21 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
164196 | 26729 | 9360 |  |  | 2012-03-29 07:04 | 2012-03-29 07:05 | 1 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
165402 | 26846 | 9442 |  |  | 2012-05-16 22:08 | 2012-05-16 22:08 | 0 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
165403 | 26847 | 9443 |  |  | 2012-05-18 17:34 | 2012-05-18 17:34 | 0 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
165404 | 26848 | 9444 |  |  | 2012-05-19 00:57 | 2012-05-19 00:57 | 0 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
165405 | 26849 | 9445 |  |  | 2012-05-21 17:41 | 2012-05-21 19:00 | 79 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
165406 | 26850 | 9446 |  |  | 2012-05-23 02:07 | 2012-05-23 02:22 | 15 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
165407 | 26851 | 9447 |  |  | 2012-05-23 07:06 | 2012-05-23 07:27 | 21 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
165408 | 26852 | 9448 |  |  | 2012-05-23 21:06 | 2012-05-23 21:38 | 32 | E0845 | RK 11 kV K2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
165409 | 26853 | 9449 |  |  | 2012-05-24 21:48 | 2012-05-24 22:13 | 25 | E1482 | RI 33 kV K2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
165410 | 26854 | 9450 |  |  | 2012-05-25 12:04 | 2012-05-25 12:04 | 0 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
165411 | 26855 | 9451 |  |  | 2012-05-27 11:34 | 2012-05-27 11:34 | 0 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
165412 | 26856 | 9452 |  |  | 2012-05-28 10:15 | 2012-05-28 10:18 | 3 | E0107 | CS 11 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
165573 | 26857 | 9453 |  |  | 2012-05-28 10:16 | 2012-05-28 10:18 | 2 | E1592 | CS 11 kV S2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
165574 | 26858 | 9454 |  |  | 2012-05-28 18:16 | 2012-05-28 18:36 | 20 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
165575 | 26859 | 9455 |  |  | 2012-05-30 07:29 | 2012-05-30 07:47 | 18 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
165576 | 26860 | 9456 |  |  | 2012-05-30 11:10 | 2012-05-30 11:11 | 1 | E1568 | DP 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166059 | 26861 | 1839 |  |  | 2012-06-19 20:53 | 2012-06-19 21:19 | 26 | E1621 | RI 110 kV Bus SPS | Bus | Fault | Generator | Basslink | Completed | TRUE | 0 | TRUE |  | IR1148 Basslink HVDC link tripped following earthquake and tripping of generators in Victoria. load shed at Rio Tinto and Nyrstar. | FALSE | Undefined
166060 | 26861 | 1839 |  |  | 2012-06-19 20:53 | 2012-06-19 21:12 | 19 | E1703 | CO 220 kV Bus SPS | Bus | Fault | Generator | Basslink | Completed | TRUE | 0 | TRUE |  | IR1148 Basslink HVDC link tripped following earthquake and tripping of generators in Victoria. load shed at Rio Tinto and Nyrstar. | FALSE | Not In Wasp
166061 | 26862 | 1841 |  |  | 2012-06-28 07:27 | 2012-06-28 11:26 | 239 | E0404 | SH-BU 2 110 kV Transmission Circuit | Transmission | Fault | Insulation Failure | Transend | Completed | TRUE | 0 | TRUE |  | IR1152 Sheffield-Burnie No 2 110kV transmission circuit tripped due to failed insulator disc. | FALSE | Non-Critical
166062 | 26863 | 1842 |  |  | 2012-07-01 21:26 | 2012-07-01 22:55 | 89 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Overload | Basslink | Completed | TRUE | 0 | TRUE |  | IR1153 GT-GC 220kV transmission circuit tripped due to over temperature at George Town converter station. FCSPS action caused generator tripping. | FALSE | Undefined
166063 | 26864 | 1843 |  |  | 2012-07-02 12:17 | 2012-07-02 13:31 | 74 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Basslink | Basslink | Completed | TRUE | 0 | TRUE |  | IR1154 GT-GC tripped and FCSPS action caused loss of 595 MW of generation. | FALSE | Undefined
166064 | 26865 | 1782 |  |  | 2012-07-05 17:51 | 2012-07-05 21:25 | 214 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Intertrip | Basslink | Completed | TRUE | 0 | TRUE |  | IR1155 GT-GC 220 kV and Basslink tripped due to an issue with Basslink. | FALSE | Undefined
198654 | 26866 | 1845 |  |  | 2012-07-06 09:53 | 2012-07-06 10:03 | 10 | E1712 | MY 110/22 kV T1 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1156 Mowbray T1 transformar circuit tripped during planned testing. | FALSE | Non-Critical
166372 | 26867 | 9457 |  |  | 2012-05-30 11:33 | 2012-05-30 11:33 | 0 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166373 | 26868 | 9458 |  |  | 2012-05-31 23:16 | 2012-05-31 23:16 | 0 | E0727 | QT 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166374 | 26869 | 9459 |  |  | 2012-06-02 06:03 | 2012-06-02 06:03 | 0 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166375 | 26870 | 9460 |  |  | 2012-06-02 14:23 | 2012-06-02 14:44 | 21 | E0104 | CS 11 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166376 | 26871 | 9463 |  |  | 2012-06-04 11:30 | 2012-06-04 12:44 | 74 | E1393 | SD 22 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166377 | 26872 | 9464 |  |  | 2012-06-04 23:36 | 2012-06-04 23:36 | 0 | E1041 | SD 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166378 | 26873 | 9465 |  |  | 2012-06-04 22:54 | 2012-06-04 23:50 | 56 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166379 | 26874 | 9466 |  |  | 2012-06-05 | 2012-06-05 00:18 | 18 | E0495 | GT 22 kV M2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166470 | 26926 | 9467 |  |  | 2012-06-05 06:53 | 2012-06-05 07:55 | 62 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166471 | 26927 | 9468 |  |  | 2012-06-05 08:59 | 2012-06-05 09:27 | 28 | E0491 | GT 22 kV F2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166472 | 26928 | 9469 |  |  | 2012-06-05 08:26 | 2012-06-05 10:14 | 108 | E0495 | GT 22 kV M2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166473 | 26929 | 9470 |  |  | 2012-06-05 10:17 | 2012-06-05 10:17 | 0 | E0495 | GT 22 kV M2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166474 | 26930 | 9471 |  |  | 2012-06-05 10:24 | 2012-06-05 11:32 | 68 | E0495 | GT 22 kV M2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166490 | 26931 | 9472 |  |  | 2012-06-07 08:57 | 2012-06-07 09:29 | 32 | E0085 | CR 33 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166491 | 26932 | 9473 |  |  | 2012-06-07 12:09 | 2012-06-07 12:52 | 43 | E0843 | RK 11 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166492 | 26933 | 9474 |  |  | 2012-06-07 21:42 | 2012-06-07 21:59 | 17 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166493 | 26934 | 9475 |  |  | 2012-06-08 04:14 | 2012-06-08 04:14 | 0 | E0389 | BU 22 kV D2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166494 | 26935 | 9476 |  |  | 2012-06-08 23:00 | 2012-06-08 23:00 | 0 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166495 | 26936 | 9477 |  |  | 2012-06-11 08:29 | 2012-06-11 08:29 | 0 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
166871 | 26985 | 1846 |  |  | 2012-07-13 16:25 | 2012-07-13 16:29 | 4 | E0438 | HA-GT 2 220 kV Transmission Circuit | Transmission | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR1157 HA-GT 2 220 kV transmission circuit tripped following a disconnector operation. | FALSE | Critical
166872 | 26986 | 1847 |  |  | 2012-07-16 13:37 | 2012-07-16 13:55 | 18 | E1763 | LF-MT-RK 2 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1158 LF-MT-RK 110 kV transmission circuit tripped during planned protection testing. | FALSE | Non-Critical
168472 | 27177 | 1118480 |  |  | 2012-07-11 23:29 | 2012-07-12 06:46 | 437 | E1616 | HR 11 kV A Bus Circuit | Bus | Fault | Switching error | Transend | Completed | TRUE | 105 | TRUE |  | IR1217 Huon River customer lost supply for a planned outage with no notification. | FALSE | Undefined
171280 | 27345 | 1848 |  |  | 2012-08-04 08:00 | 2012-08-04 11:40 | 220 | E0407 | DB 110/22 kV T1 Transformer Circuit | Transformer | Fault | Wildlife | Transend | Completed | TRUE | 29 | TRUE |  | IR1159 DB T1 transformer circuit tripped with LOS at Derwent Bridge | FALSE | Non-Critical
171165 | 27346 | 1849 |  |  | 2012-08-08 21:59 | 2012-08-08 22:12 | 13 | E0717 | FA-RC 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1160 FA-RC 1 & 2 220kV transmission circuits tripped, suspect lightning strike. Reece dropped 40 MW | FALSE | Non-Critical
185851 | 27346 | 1849 |  |  | 2012-08-08 21:59 | 2012-08-08 22:12 | 13 | E0716 | FA-RC 1 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1160 FA-RC 1 & 2 220kV transmission circuits tripped, suspect lightning strike. Reece dropped 40 MW | FALSE | Non-Critical
171075 | 27347 | 1852 |  |  | 2012-08-15 12:46 | 2012-08-15 12:56 | 10 | E0053 | CS 110 kV C1 Capacitor Circuit | Capacitor | Fault | Abnormal Operating Conditions | Transend | Completed | TRUE | 0 | TRUE |  | IR1164 Risdon C4 and Chapel St C1 capacitor circuits tripped on over voltage after Nyrstar load trip. | FALSE | Non-Critical
171076 | 27347 | 1852 |  |  | 2012-08-15 12:46 | 2012-08-15 12:56 | 10 | E1756 | RI 110 kV C4 Capacitor Circuit | Capacitor | Fault | Abnormal Operating Conditions | Transend | Completed | TRUE | 0 | TRUE |  | IR1164 Risdon C4 and Chapel St C1 capacitor circuits tripped on over voltage after Nyrstar load trip. | FALSE | Non-Critical
171166 | 27348 | 1795 |  |  | 2012-08-23 18:03 | 2012-08-24 15:35 | 1292 | E0030 | CS-KI-KR 110 kV Transmission Circuit (changed to E1955) | Transmission | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR1165 CS-KI-KR tripped, suspect faulty protection relay at Kingston. | FALSE | Non-Critical
181310 | 27349 | 1858 |  |  | 2012-09-04 13:44 | 2012-09-04 13:48 | 4 | E0115 | CS 11 kV Q2 Feeder Circuit | Feeder | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 10 | TRUE |  | IR1169 Chapel Street feeders (2) tripped during protection testing. | FALSE | Undefined
181311 | 27349 | 1858 |  |  | 2012-09-04 13:44 | 2012-09-04 13:48 | 4 | E1592 | CS 11 kV S2 Feeder Circuit | Feeder | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1169 Chapel Street feeders (2) tripped during protection testing. | FALSE | Undefined
171636 | 27417 | 1857 |  |  | 2012-09-09 15:38 | 2012-09-09 19:16 | 218 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Fault | Insulation Failure | Transend | Completed | TRUE | 540 | TRUE |  | IR1168 LF-SO-TB 110kV transmission circuit was forced out due to insulator damage by shooting. | FALSE | Non-Critical
173011 | 27479 | 9482 |  |  | 2012-06-14 10:28 | 2012-06-14 10:47 | 19 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172496 | 27480 | 9485 |  |  | 2012-06-14 19:21 | 2012-06-14 20:58 | 97 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172497 | 27481 | 9489 |  |  | 2012-06-17 15:13 | 2012-06-17 15:13 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172498 | 27482 | 9481 |  |  | 2012-06-14 09:05 | 2012-06-14 09:25 | 20 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172500 | 27484 | 9488 |  |  | 2012-06-17 10:55 | 2012-06-17 11:43 | 48 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172501 | 27485 | 9483 |  |  | 2012-06-14 13:31 | 2012-06-14 13:31 | 0 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172502 | 27486 | 9486 |  |  | 2012-06-15 00:14 | 2012-06-15 00:15 | 1 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172503 | 27487 | 9487 |  |  | 2012-06-17 10:46 | 2012-06-17 10:47 | 1 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172504 | 27488 | 9490 |  |  | 2012-06-17 15:15 | 2012-06-17 16:38 | 83 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172505 | 27489 | 9491 |  |  | 2012-06-17 17:54 | 2012-06-17 17:54 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172506 | 27490 | 9492 |  |  | 2012-06-18 20:06 | 2012-06-18 20:06 | 0 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172507 | 27491 | 9493 |  |  | 2012-06-19 00:30 | 2012-06-19 00:31 | 1 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172508 | 27492 | 9494 |  |  | 2012-06-21 23:50 | 2012-06-21 23:50 | 0 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172509 | 27493 | 9495 |  |  | 2012-06-23 08:35 | 2012-06-23 08:57 | 22 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172510 | 27494 | 9496 |  |  | 2012-06-23 19:38 | 2012-06-23 19:39 | 1 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172511 | 27495 | 9497 |  |  | 2012-06-24 23:23 | 2012-06-25 00:59 | 96 | E1471 | KE 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172512 | 27496 | 9498 |  |  | 2012-06-27 09:22 | 2012-06-27 09:22 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172513 | 27497 | 9499 |  |  | 2012-06-29 17:01 | 2012-06-29 17:21 | 20 | E1560 | HA 22 kV P2 Feeder Circuit | Feeder | Fault |  |  | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172514 | 27498 | 9500 |  |  | 2012-06-30 09:20 | 2012-06-30 09:41 | 21 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172823 | 27499 | 9478 |  |  | 2012-06-11 10:06 | 2012-06-11 10:06 | 0 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172824 | 27500 | 9479 |  |  | 2012-06-11 13:38 | 2012-06-11 13:39 | 1 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172825 | 27501 | 9480 |  |  | 2012-06-12 01:09 | 2012-06-12 01:59 | 50 | E1592 | CS 11 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172826 | 27502 | 9502 |  |  | 2012-07-10 15:30 | 2012-07-10 15:51 | 21 | E0083 | CR 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173873 | 27503 | 9501 |  |  | 2012-07-01 11:35 | 2012-07-01 11:53 | 18 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172828 | 27504 | 9503 |  |  | 2012-07-11 04:48 | 2012-07-11 04:48 | 0 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172829 | 27506 | 9505 |  |  | 2012-07-14 18:23 | 2012-07-14 18:23 | 0 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172830 | 27507 | 9506 |  |  | 2012-07-16 07:38 | 2012-07-16 08:15 | 37 | E0904 | TR 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172831 | 27508 | 9507 |  |  | 2012-07-16 10:25 | 2012-07-16 10:57 | 32 | E0123 | CS 11 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172832 | 27509 | 9508 |  |  | 2012-07-19 11:14 | 2012-07-19 11:33 | 19 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172833 | 27510 | 9509 |  |  | 2012-07-21 14:30 | 2012-07-21 14:30 | 0 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172939 | 27603 | 9510 |  |  | 2012-07-22 12:20 | 2012-07-22 12:40 | 20 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172940 | 27604 | 9511 |  |  | 2012-07-22 19:24 | 2012-07-22 20:59 | 95 | E0119 | CS 11 kV U2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172941 | 27605 | 9512 |  |  | 2012-07-23 07:24 | 2012-07-23 07:24 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172942 | 27606 | 9513 |  |  | 2012-07-23 20:40 | 2012-07-23 20:42 | 2 | E0119 | CS 11 kV U2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172943 | 27607 | 9514 |  |  | 2012-07-26 10:47 | 2012-07-26 10:47 | 0 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172944 | 27608 | 9515 |  |  | 2012-07-26 11:17 | 2012-07-26 11:41 | 24 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173519 | 27609 | 9516 |  |  | 2012-07-26 12:14 | 2012-07-26 12:14 | 0 | E1393 | SD 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172945 | 27610 | 9517 |  |  | 2012-07-27 12:31 | 2012-07-27 12:31 | 0 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172946 | 27611 | 9518 |  |  | 2012-07-26 13:04 | 2012-07-26 13:04 | 0 | E0490 | GT 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172947 | 27612 | 9519 |  |  | 2012-07-26 19:59 | 2012-07-26 19:59 | 0 | E1042 | SD 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172948 | 27613 | 9520 |  |  | 2012-07-28 20:52 | 2012-07-28 20:53 | 1 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172949 | 27614 | 9521 |  |  | 2012-07-28 21:02 | 2012-07-28 21:03 | 1 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172950 | 27615 | 9522 |  |  | 2012-07-30 10:41 | 2012-07-30 11:02 | 21 | E0019 | BW 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172951 | 27616 | 9523 |  |  | 2012-07-30 15:14 | 2012-07-30 15:14 | 0 | E1613 | UL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172952 | 27617 | 9524 |  |  | 2012-07-31 07:42 | 2012-07-31 08:00 | 18 | E0364 | KI 11 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172953 | 27618 | 9525 |  |  | 2012-07-31 10:20 | 2012-07-31 10:20 | 0 | E1393 | SD 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
172971 | 27619 | 1859 |  |  | 2012-09-13 11:31 | 2012-09-13 13:17 | 106 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Poor Construction | Transend | Completed | TRUE | 4353 | TRUE |  | IR1113 Farrell-Rosebery-Queenstown 110kV transmission circuit tripped with loss of supply to West Coast. | FALSE | Non-Critical
172972 | 27620 | 1856 |  |  | 2012-09-07 18:23 | 2012-09-07 18:39 | 16 | E0721 | QT-NT 110 kV Transmission Circuit | Transmission | Fault | Fatigue | Transend | Completed | TRUE | 114 | TRUE |  | IR1167 Queenstown-Newton 110 kV transmission circuit tripped with loss of supply at Newton Substation. | FALSE | Non-Critical
181625 | 27621 | 1860 |  |  | 2012-09-26 16:32 | 2012-09-26 16:50 | 18 | E0261 | PO-PM 3 220 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1170 Poatina-Palmerston 220 kV transmission circuit tripped with intertrip from Hydro | FALSE | Non-Critical
173520 | 27622 | 9526 |  |  | 2012-07-31 23:11 | 2012-07-31 23:11 | 0 | E1393 | SD 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173521 | 27623 | 9528 |  |  | 2012-08-03 04:33 | 2012-08-03 04:58 | 25 | E0943 | UL 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173522 | 27624 | 9527 |  |  | 2012-08-01 10:14 | 2012-08-01 10:32 | 18 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173523 | 27625 | 9529 |  |  | 2012-08-04 03:23 | 2012-08-04 03:44 | 21 | E0491 | GT 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173524 | 27626 | 9530 |  |  | 2012-08-04 08:19 | 2012-08-04 08:20 | 1 | E0727 | QT 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173525 | 27627 | 9531 |  |  | 2012-08-04 15:04 | 2012-08-04 15:27 | 23 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173526 | 27628 | 9532 |  |  | 2012-08-04 18:04 | 2012-08-04 19:05 | 61 | E0465 | KR 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173527 | 27629 | 9533 |  |  | 2012-08-05 13:56 | 2012-08-05 15:08 | 72 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173528 | 27630 | 9534 |  |  | 2012-08-05 17:24 | 2012-08-05 18:32 | 68 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173529 | 27631 | 9535 |  |  | 2012-08-05 19:12 | 2012-08-05 19:12 | 0 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173530 | 27632 | 9536 |  |  | 2012-08-05 20:31 | 2012-08-05 20:31 | 0 | E0727 | QT 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173531 | 27633 | 9537 |  |  | 2012-08-05 20:35 | 2012-08-05 20:35 | 0 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173532 | 27634 | 9538 |  |  | 2012-08-05 23:36 | 2012-08-05 23:55 | 19 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173533 | 27635 | 9539 |  |  | 2012-08-06 05:35 | 2012-08-06 05:35 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173534 | 27636 | 9540 |  |  | 2012-08-06 09:12 | 2012-08-06 09:50 | 38 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173535 | 27637 | 9541 |  |  | 2012-08-06 11:48 | 2012-08-06 11:48 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173536 | 27638 | 9542 |  |  | 2012-08-06 12:17 | 2012-08-06 12:17 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173537 | 27639 | 9543 |  |  | 2012-08-08 22:15 | 2012-08-08 22:16 | 1 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195878 | 27640 | 9544 |  |  | 2012-08-09 07:03 | 2012-08-09 07:03 | 0 | E1826 | TU 22kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
173539 | 27641 | 9545 |  |  | 2012-08-09 14:47 | 2012-08-09 16:33 | 106 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173540 | 27642 | 9546 |  |  | 2012-08-11 11:03 | 2012-08-11 11:35 | 32 | E0909 | TR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173541 | 27643 | 9547 |  |  | 2012-08-11 18:52 | 2012-08-11 18:53 | 1 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173542 | 27644 | 9548 |  |  | 2012-08-14 06:52 | 2012-08-14 06:52 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173543 | 27645 | 9549 |  |  | 2012-08-16 14:13 | 2012-08-16 14:13 | 0 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173544 | 27646 | 9550 |  |  | 2012-08-16 16:44 | 2012-08-16 16:57 | 13 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173545 | 27647 | 9551 |  |  | 2012-08-18 05:22 | 2012-08-18 09:30 | 248 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173546 | 27648 | 9552 |  |  | 2012-08-18 12:10 | 2012-08-18 12:10 | 0 | E1826 | TU 22kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
173547 | 27649 | 9553 |  |  | 2012-08-22 06:58 | 2012-08-22 07:18 | 20 | E1533 | MY 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173548 | 27650 | 9555 |  |  | 2012-08-25 16:09 | 2012-08-25 16:10 | 1 | E1393 | SD 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173549 | 27651 | 9556 |  |  | 2012-08-25 20:11 | 2012-08-25 21:35 | 84 | E1570 | DP 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173550 | 27652 | 9557 |  |  | 2012-08-26 07:59 | 2012-08-26 07:59 | 0 | E0760 | NW 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173592 | 27682 | 9558 |  |  | 2012-08-26 21:09 | 2012-08-26 21:09 | 0 | E0768 | NW 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195879 | 27683 | 9559 |  |  | 2012-08-30 13:16 | 2012-08-30 14:30 | 74 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195880 | 27684 | 9560 |  |  | 2012-08-31 06:18 | 2012-08-31 06:18 | 0 | E1444 | HA 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195881 | 27685 | 9561 |  |  | 2012-09-02 02:57 | 2012-09-02 02:57 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195882 | 27686 | 9563 |  |  | 2012-09-02 17:27 | 2012-09-02 17:50 | 23 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195883 | 27687 | 9564 |  |  | 2012-09-03 01:36 | 2012-09-03 01:36 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195884 | 27690 | 9567 |  |  | 2012-09-05 10:49 | 2012-09-05 11:13 | 24 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195885 | 27691 | 9568 |  |  | 2012-09-05 11:14 | 2012-09-05 11:24 | 10 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195886 | 27692 | 9570 |  |  | 2012-09-06 00:28 | 2012-09-06 00:28 | 0 | E1004 | BU 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195887 | 27693 | 9571 |  |  | 2012-09-06 15:42 | 2012-09-06 15:42 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195888 | 27694 | 9572 |  |  | 2012-09-07 14:50 | 2012-09-07 15:17 | 27 | E1504 | TB 22 KV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195889 | 27696 | 9575 |  |  | 2012-09-08 08:10 | 2012-09-08 08:10 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195890 | 27697 | 9576 |  |  | 2012-09-08 09:16 | 2012-09-08 09:16 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195891 | 27698 | 9578 |  |  | 2012-09-07 18:23 | 2012-09-07 18:23 | 0 | E0725 | NT 22 kV A2X Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195892 | 27700 | 9579 |  |  | 2012-09-08 14:21 | 2012-09-08 14:21 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195893 | 27701 | 9580 |  |  | 2012-09-08 15:15 | 2012-09-08 15:15 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173612 | 27702 | 9581 |  |  | 2012-09-08 12:28 | 2012-09-08 18:43 | 375 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173613 | 27703 | 9582 |  |  | 2012-09-01 23:39 | 2012-09-09 00:10 | 10111 | E1557 | CR 33 kV Z2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174120 | 27704 | 9584 |  |  | 2012-09-08 23:33 | 2012-09-09 02:25 | 172 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195894 | 27705 | 9585 |  |  | 2012-09-09 01:15 | 2012-09-09 01:15 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173616 | 27706 | 9586 |  |  | 2012-09-09 09:31 | 2012-09-09 09:31 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173617 | 27707 | 9587 |  |  | 2012-09-08 22:50 | 2012-09-09 11:17 | 747 | E0078 | CR 33 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173618 | 27708 | 9588 |  |  | 2012-09-09 16:20 | 2012-09-09 16:20 | 0 | E1471 | KE 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173826 | 27709 | 9590 |  |  | 2012-09-09 17:58 | 2012-09-09 17:58 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173620 | 27710 | 9591 |  |  | 2012-09-09 17:52 | 2012-09-09 18:17 | 25 | E1557 | CR 33 kV Z2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173621 | 27711 | 9592 |  |  | 2012-09-09 19:35 | 2012-09-09 20:06 | 31 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173622 | 27712 | 9593 |  |  | 2012-09-09 20:20 | 2012-09-09 20:20 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173623 | 27713 | 9594 |  |  | 2012-09-10 00:13 | 2012-09-10 00:13 | 0 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173624 | 27715 | 9596 |  |  | 2012-09-09 20:41 | 2012-09-10 13:30 | 1009 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173625 | 27716 | 9597 |  |  | 2012-09-09 19:16 | 2012-09-09 20:29 | 73 | E1505 | TB 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173626 | 27717 | 9598 |  |  | 2012-09-11 18:16 | 2012-09-11 18:16 | 0 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173627 | 27718 | 9599 |  |  | 2012-09-12 16:05 | 2012-09-12 16:05 | 0 | E0463 | KR 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173628 | 27719 | 9600 |  |  | 2012-09-13 13:06 | 2012-09-13 13:06 | 0 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173629 | 27720 | 9601 |  |  | 2012-09-13 01:13 | 2012-09-13 01:32 | 19 | E0343 | LF 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173630 | 27721 | 9602 |  |  | 2012-09-13 16:32 | 2012-09-13 16:32 | 0 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173631 | 27722 | 9603 |  |  | 2012-09-14 18:35 | 2012-09-14 18:35 | 0 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173632 | 27723 | 9604 |  |  | 2012-09-14 21:57 | 2012-09-14 22:49 | 52 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173634 | 27725 | 9606 |  |  | 2012-09-16 14:32 | 2012-09-16 15:41 | 69 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173635 | 27726 | 9608 |  |  | 2012-09-19 05:21 | 2012-09-19 05:21 | 0 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173637 | 27728 | 9610 |  |  | 2012-09-20 00:27 | 2012-09-20 00:27 | 0 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173638 | 27729 | 9607 |  |  | 2012-09-18 00:11 | 2012-09-18 00:28 | 17 | E1826 | TU 22kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
173639 | 27730 | 9609 |  |  | 2012-09-19 23:18 | 2012-09-19 23:18 | 0 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173640 | 27731 | 9611 |  |  | 2012-09-20 10:49 | 2012-09-20 10:49 | 0 | E0644 | ST 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173641 | 27732 | 9612 |  |  | 2012-09-21 12:47 | 2012-09-21 12:47 | 0 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173642 | 27733 | 9613 |  |  | 2012-09-24 07:15 | 2012-09-24 07:15 | 0 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173827 | 27734 | 9614 |  |  | 2012-09-25 13:16 | 2012-09-25 13:58 | 42 | E0343 | LF 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173644 | 27735 | 9615 |  |  | 2012-09-28 04:16 | 2012-09-28 07:29 | 193 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182437 | 27736 | 9616 |  |  | 2012-09-28 19:15 | 2012-09-28 19:16 | 1 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173646 | 27737 | 9617 |  |  | 2012-09-29 10:15 | 2012-09-29 10:15 | 0 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173647 | 27738 | 9618 |  |  | 2012-09-29 23:08 | 2012-09-29 23:41 | 33 | E0343 | LF 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173648 | 27739 | 9619 |  |  | 2012-09-30 00:07 | 2012-09-30 00:07 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173649 | 27740 | 9620 |  |  | 2012-10-01 14:39 | 2012-10-01 14:39 | 0 | E1567 | DP 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173722 | 27829 | 9624 |  |  | 2012-10-04 10:02 | 2012-10-04 10:30 | 28 | E1557 | CR 33 kV Z2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173723 | 27830 | 9625 |  |  | 2012-10-04 10:45 | 2012-10-04 10:45 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173724 | 27831 | 9626 |  |  | 2012-10-04 10:50 | 2012-10-04 10:50 | 0 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173725 | 27832 | 9627 |  |  | 2012-10-04 10:50 | 2012-10-04 10:50 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173727 | 27834 | 9632 |  |  | 2012-10-04 12:02 | 2012-10-04 12:02 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174409 | 27835 | 9628 |  |  | 2012-10-04 10:46 | 2012-10-04 12:41 | 115 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173729 | 27836 | 9634 |  |  | 2012-10-04 12:52 | 2012-10-04 12:52 | 0 | E0835 | RK 11 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173730 | 27837 | 9635 |  |  | 2012-10-04 13:24 | 2012-10-04 13:24 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173731 | 27838 | 9631 |  |  | 2012-10-04 11:02 | 2012-10-04 13:31 | 149 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173732 | 27839 | 9623 |  |  | 2012-10-04 10:07 | 2012-10-04 13:51 | 224 | E0412 | EL 11 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173733 | 27840 | 9637 |  |  | 2012-10-04 13:57 | 2012-10-04 13:57 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173734 | 27841 | 9630 |  |  | 2012-10-04 10:31 | 2012-10-04 14:03 | 212 | E0197 | SO 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174121 | 27842 | 9629 |  |  | 2012-10-04 10:40 | 2012-10-04 15:06 | 266 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
173736 | 27843 | 9633 |  |  | 2012-10-04 12:10 | 2012-10-04 19:28 | 438 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174912 | 27904 | 1862 |  |  | 2012-10-11 09:24 | 2012-10-11 09:28 | 4 | E0274 | PM-AV 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 62 | TRUE |  | IR1171 PM-AV 110 kV transmission line circuit tripped due to incorrect VT selection during planned work. LOS at Avoca and St Marys. | FALSE | Non-Critical
173968 | 27905 | 1863 |  |  | 2012-10-17 08:59 | 2012-10-17 09:12 | 13 | E1810 | GT-TV 1 110 kV Transmission Circuit | Transmission | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR1172 GT-TV 110 kV transmission line circuit tripped due to operation of CAS during planned work. | FALSE | Non-Critical
173969 | 27905 | 1863 |  |  | 2012-10-17 08:59 | 2012-10-17 09:12 | 13 | E1811 | GT-TV 2 110 kV Transmission Circuit | Transmission | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR1172 GT-TV 110 kV transmission line circuit tripped due to operation of CAS during planned work. | FALSE | Non-Critical
173974 | 27906 | 1865 |  |  | 2012-10-24 13:37 | 2012-10-24 13:40 | 3 | E0441 | HA-TR 1 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1174 Hadspen 110kV A Bus tripped due to protection operation due to error during planned work. | FALSE | Critical
173971 | 27906 | 1865 |  |  | 2012-10-24 13:37 | 2012-10-24 13:40 | 3 | E0422 | HA 110 kV A Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1174 Hadspen 110kV A Bus tripped due to protection operation due to error during planned work. | FALSE | Undefined
173970 | 27906 | 1865 |  |  | 2012-10-24 13:37 | 2012-10-24 13:40 | 3 | E0264 | PM-HA 4 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1174 Hadspen 110kV A Bus tripped due to protection operation due to error during planned work. | FALSE | Critical
173973 | 27906 | 1865 |  |  | 2012-10-24 13:37 | 2012-10-24 13:41 | 4 | E0440 | HA-NW 2 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1174 Hadspen 110kV A Bus tripped due to protection operation due to error during planned work. | FALSE | Non-Critical
173972 | 27906 | 1865 |  |  | 2012-10-24 13:37 | 2012-10-24 13:41 | 4 | E0436 | HA 220/110 kV T2 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1174 Hadspen 110kV A Bus tripped due to protection operation due to error during planned work. | FALSE | Non-Critical
174086 | 27907 | 1866 |  |  | 2012-10-30 13:47 | 2012-10-30 14:09 | 22 | E0718 | FA-MA 110 kV Transmission Circuit | Transmission | Fault | Fire (Bush) | Transend | Completed | TRUE | 0 | TRUE |  | IR1175 SH-FA 1 and 2 220 kV transmission line circuits tripped due smoke from to Forestry burn off, causing the West Coast to be islanded. Some industrial load was shed. | FALSE | Non-Critical
194087 | 27907 | 1866 |  |  | 2012-10-30 13:47 | 2012-10-30 14:07 | 20 | E0714 | FA-TI 220 kV Transmission Circuit | Transmission | Fault | Fire (Bush) | Transend | Completed | TRUE | 0 | TRUE |  | IR1175 SH-FA 1 and 2 220 kV transmission line circuits tripped due smoke from to Forestry burn off, causing the West Coast to be islanded. Some industrial load was shed. | FALSE | Non-Critical
173975 | 27907 | 1866 |  |  | 2012-10-30 13:47 | 2012-10-30 14:05 | 18 | E0538 | SH-FA 1 220 kV Transmission Circuit | Transmission | Fault | Fire (Bush) | Transend | Completed | TRUE | 0 | TRUE |  | IR1175 SH-FA 1 and 2 220 kV transmission line circuits tripped due smoke from to Forestry burn off, causing the West Coast to be islanded. Some industrial load was shed. | FALSE | Critical
173976 | 27907 | 1866 |  |  | 2012-10-30 13:47 | 2012-10-30 14:06 | 19 | E0539 | SH-FA 2 220 kV Transmission Circuit | Transmission | Fault | Fire (Bush) | Transend | Completed | TRUE | 0 | TRUE |  | IR1175 SH-FA 1 and 2 220 kV transmission line circuits tripped due smoke from to Forestry burn off, causing the West Coast to be islanded. Some industrial load was shed. | FALSE | Critical
173978 | 27907 | 1866 |  |  | 2012-10-30 13:47 | 2012-10-30 14:08 | 21 | E0715 | FA-JB 220 kV Transmission Circuit | Transmission | Fault | Fire (Bush) | Transend | Completed | TRUE | 0 | TRUE |  | IR1175 SH-FA 1 and 2 220 kV transmission line circuits tripped due smoke from to Forestry burn off, causing the West Coast to be islanded. Some industrial load was shed. | FALSE | Non-Critical
195895 | 27908 | 9621 |  |  | 2012-10-04 09:58 | 2012-10-04 09:59 | 1 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195896 | 27909 | 9622 |  |  | 2012-10-04 09:43 | 2012-10-04 11:46 | 123 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195897 | 27910 | 9638 |  |  | 2012-10-04 15:17 | 2012-10-04 18:03 | 166 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195898 | 27911 | 9639 |  |  | 2012-10-05 03:05 | 2012-10-05 03:37 | 32 | E1557 | CR 33 kV Z2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195899 | 27912 | 9640 |  |  | 2012-10-06 06:00 | 2012-10-06 07:38 | 98 | E0366 | KI 11 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195900 | 27913 | 9641 |  |  | 2012-10-07 10:52 | 2012-10-07 10:52 | 0 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195901 | 27914 | 9642 |  |  | 2012-10-07 13:24 | 2012-10-07 13:49 | 25 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195902 | 27915 | 9643 |  |  | 2012-10-07 14:13 | 2012-10-07 18:03 | 230 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195903 | 27916 | 9644 |  |  | 2012-10-08 02:32 | 2012-10-08 02:32 | 0 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195904 | 27917 | 9645 |  |  | 2012-10-08 02:34 | 2012-10-08 02:34 | 0 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195907 | 27950 | 9647 |  |  | 2012-10-08 23:25 | 2012-10-08 23:25 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195908 | 27951 | 9649 |  |  | 2012-10-12 19:32 | 2012-10-14 23:07 | 3095 | E1595 | LF 33 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174656 | 27952 | 9650 |  |  | 2012-10-14 08:57 | 2012-10-14 08:57 | 0 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174657 | 27953 | 9651 |  |  | 2012-10-14 12:25 | 2012-10-14 12:25 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174658 | 27954 | 9652 |  |  | 2012-10-20 08:34 | 2012-10-20 08:54 | 20 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174659 | 27955 | 9653 |  |  | 2012-10-22 00:04 | 2012-10-22 00:04 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174660 | 27956 | 9654 |  |  | 2012-10-22 00:06 | 2012-10-22 00:06 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174661 | 27957 | 9655 |  |  | 2012-10-25 10:41 | 2012-10-25 10:58 | 17 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174662 | 27958 | 9656 |  |  | 2012-10-27 11:30 | 2012-10-27 11:30 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174663 | 27959 | 9657 |  |  | 2012-10-29 18:48 | 2012-10-29 21:02 | 134 | E0083 | CR 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174664 | 27960 | 9658 |  |  | 2012-11-01 13:36 | 2012-11-01 13:36 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174665 | 27961 | 9659 |  |  | 2012-11-01 14:21 | 2012-11-01 14:21 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174666 | 27962 | 9660 |  |  | 2012-11-03 00:29 | 2012-11-03 00:29 | 0 | E1613 | UL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174667 | 27963 | 9661 |  |  | 2012-11-04 09:42 | 2012-11-04 10:09 | 27 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174668 | 27964 | 9662 |  |  | 2012-11-05 12:18 | 2012-11-05 12:59 | 41 | E0639 | ST 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174669 | 27965 | 9663 |  |  | 2012-11-05 13:22 | 2012-11-05 13:42 | 20 | E0111 | CS 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174670 | 27966 | 9664 |  |  | 2012-11-06 12:25 | 2012-11-06 12:25 | 0 | E1444 | HA 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174671 | 27967 | 9665 |  |  | 2012-11-09 07:11 | 2012-11-09 07:11 | 0 | E1826 | TU 22kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
174672 | 27968 | 9666 |  |  | 2012-11-09 11:41 | 2012-11-09 11:41 | 0 | E0358 | KI 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174674 | 27970 | 9667 |  |  | 2012-11-10 14:56 | 2012-11-10 14:56 | 0 | E1554 | DP 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174675 | 27971 | 9668 |  |  | 2012-11-10 14:56 | 2012-11-10 14:56 | 0 | E1552 | DP 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174676 | 27972 | 9669 |  |  | 2012-11-11 17:32 | 2012-11-11 18:21 | 49 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174821 | 27973 | 1867 |  |  | 2012-11-09 12:01 | 2012-11-09 12:07 | 6 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 13 | TRUE |  | IR1176 LF-SO-TB 110 kV transmission circuit tripped with lightning in area. | FALSE | Non-Critical
176924 | 27974 | 1868 |  |  | 2012-11-12 11:05 | 2012-11-12 11:46 | 41 | E0857 | RB 110/44 kV T2 Transformer Circuit | Transformer | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1177 SH-FA 1 and 2 220 kV transmission circuits tripped due to lightning strike with loss of supply to West Coast. | FALSE | Non-Critical
196293 | 27974 | 1868 |  |  | 2012-11-12 11:05 | 2012-11-12 11:14 | 9 | E0538 | SH-FA 1 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 1405 | TRUE |  | IR1177 SH-FA 1 and 2 220 kV transmission circuits tripped due to lightning strike with loss of supply to West Coast. | FALSE | Critical
174823 | 27974 | 1868 |  |  | 2012-11-12 11:05 | 2012-11-12 11:15 | 10 | E0539 | SH-FA 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1177 SH-FA 1 and 2 220 kV transmission circuits tripped due to lightning strike with loss of supply to West Coast. | FALSE | Critical
174889 | 27989 | 9671 |  |  | 2012-11-12 16:02 | 2012-11-12 16:05 | 3 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
174890 | 27990 | 9672 |  |  | 2012-11-13 10:50 | 2012-11-13 10:51 | 1 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
175007 | 27991 | 9673 |  |  | 2012-11-17 10:22 | 2012-11-17 10:22 | 0 | E0639 | ST 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
175008 | 27992 | 9674 |  |  | 2012-11-17 20:41 | 2012-11-17 21:02 | 21 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
176759 | 28113 | 9675 |  |  | 2012-11-21 00:46 | 2012-11-21 00:46 | 0 | E1444 | HA 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
176760 | 28114 | 9676 |  |  | 2012-11-23 00:06 | 2012-11-23 00:06 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
176761 | 28115 | 9678 |  |  | 2012-11-24 00:43 | 2012-11-24 01:02 | 19 | E0765 | NW 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
176762 | 28117 | 9680 |  |  | 2012-11-25 17:18 | 2012-11-25 18:11 | 53 | E0844 | RK 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
176927 | 28118 | 1870 |  |  | 2012-11-14 12:46 | 2012-11-14 13:11 | 25 | E0857 | RB 110/44 kV T2 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 599 | TRUE |  | IR1178 Rosebery T2 tripped possibly due to grading error with new T2 protection. | FALSE | Non-Critical
176928 | 28119 | 1872 |  |  | 2012-11-30 04:12 | 2012-11-30 04:15 | 3 | E1497 | NW-SD 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1181 NW-SD 110 kV transmission circuit tripped due to unknown cause. | FALSE | Non-Critical
177848 | 28120 | 1871 |  |  | 2012-11-27 07:32 | 2012-11-27 07:49 | 17 | E0510 | GT-CO 4 220 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1180 George Town 220 kV Bus Bar tripped due to testing error | FALSE | Non-Critical
177849 | 28120 | 1871 |  |  | 2012-11-27 07:32 | 2012-11-27 08:03 | 31 | E1734 | GT-TV 3 220 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1180 George Town 220 kV Bus Bar tripped due to testing error | FALSE | Undefined
177847 | 28120 | 1871 |  |  | 2012-11-27 07:32 | 2012-11-27 07:47 | 15 | E0504 | GT 220 kV B Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 1901 | TRUE |  | IR1180 George Town 220 kV Bus Bar tripped due to testing error | FALSE | Undefined
177030 | 28121 | 1875 |  |  | 2012-11-30 20:37 | 2012-11-30 20:59 | 22 | E0470 | KR 110/11 kV T1 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 173 | TRUE |  | IR1187 Knights Road transformer circuits tripped with loss of supply. | FALSE | Non-Critical
177031 | 28121 | 1875 |  |  | 2012-11-30 20:37 | 2012-11-30 20:59 | 22 | E0471 | KR 110/11 kV T2 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR1187 Knights Road transformer circuits tripped with loss of supply. | FALSE | Non-Critical
179541 | 28122 | 1876 |  |  | 2012-11-30 21:17 | 2012-12-05 17:21 | 6964 | E0276 | PM-AL 110 kV Transmission Circuit | Transmission | Fault | Fire (Bush) | Force Majeure | Completed | TRUE | 45092 | TRUE |  | IR1188 PM-AL 110 kV transmission circuit tripped due to bushfire, with loss of supply at Arthurs Lake. | FALSE | Non-Critical
177153 | 28123 | 1877 |  |  | 2012-12-01 11:26 | 2012-12-01 11:31 | 5 | E1731 | LI-WA-PM 2 220 kV Transmission Circuit | Transmission | Fault | Fire (Bush) | Transend | Completed | TRUE | 0 | TRUE |  | IR1192 LI-WA-PM 2 220 kv transmission circuit tripped during bush fire. Load shed at Nyrstar and Norske Skog. | FALSE | Critical
207579 | 28125 | 1878 |  |  | 2012-12-01 12:31 | 2012-12-01 12:33 | 2 | E1723 | LI-WA-PM 1 220 kV Transmission Circuit | Transmission | Fault | Fire (Bush) | Transend | Completed | TRUE | 0 | TRUE |  | IR1190 LI-WA-PM 1 & 2 220 kV transmission circuits tripped several times during bush fire. Load shed at Norske and Nyrstar. | FALSE | Critical
177156 | 28125 | 1878 |  |  | 2012-12-01 12:27 | 2012-12-01 12:32 | 5 | E1731 | LI-WA-PM 2 220 kV Transmission Circuit | Transmission | Fault | Fire (Bush) | Transend | Completed | TRUE | 0 | TRUE |  | IR1190 LI-WA-PM 1 & 2 220 kV transmission circuits tripped several times during bush fire. Load shed at Norske and Nyrstar. | FALSE | Critical
177495 | 28157 | 9681 |  |  | 2012-11-22 22:02 | 2012-11-22 22:02 | 0 | E0389 | BU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
177496 | 28158 | 9682 |  |  | 2012-11-29 22:02 | 2012-11-29 22:02 | 0 | E1000 | BU 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
177497 | 28159 | 9683 |  |  | 2012-12-30 04:45 | 2012-12-30 04:45 | 0 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
177498 | 28160 | 9684 |  |  | 2012-12-30 19:57 | 2012-12-30 19:57 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
177499 | 28161 | 9685 |  |  | 2012-12-31 08:06 | 2012-12-31 08:06 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
177500 | 28162 | 9686 |  |  | 2012-12-01 10:54 | 2012-12-01 10:54 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
177501 | 28163 | 9687 |  |  | 2012-12-01 12:32 | 2012-12-01 12:32 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
177502 | 28164 | 9688 |  |  | 2012-12-01 17:56 | 2012-12-01 18:28 | 32 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
177503 | 28165 | 9689 |  |  | 2012-12-01 22:36 | 2012-12-01 22:37 | 1 | E1613 | UL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
177504 | 28166 | 9690 |  |  | 2012-12-03 07:11 | 2012-12-03 07:11 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
177505 | 28167 | 9694 |  |  | 2012-12-04 13:34 | 2012-12-04 13:34 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
177506 | 28168 | 9697 |  |  | 2012-12-05 12:49 | 2012-12-05 12:49 | 0 | E0768 | NW 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
177507 | 28169 | 9698 |  |  | 2012-12-06 20:01 | 2012-12-06 20:01 | 0 | E1555 | DP 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
177596 | 28170 | 1881 |  |  | 2012-12-03 14:51 | 2012-12-03 15:01 | 10 | E0261 | PO-PM 3 220 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1193 PO-PM 3 220 kV transmission circuit tripped due to intertrip from Hydro. | FALSE | Non-Critical
196298 | 28171 | 1882 |  |  | 2012-12-04 14:12 | 2012-12-04 14:27 | 15 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 301 | TRUE |  | IR1194 Farrell-Rosebery-Queenstown 110 kV transmission circuit tripped - Suspected Lightning | FALSE | Non-Critical
177629 | 28172 | 1883 |  |  | 2012-12-08 19:32 | 2012-12-08 19:32 | 0 | E0549 | SH-LM 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1195 Sheffield-Lemonthyme tripped and reclosed - Lightning Suspected | FALSE | Non-Critical
177630 | 28173 | 1884 |  |  | 2012-12-08 19:41 | 2012-12-08 19:48 | 7 | E0538 | SH-FA 1 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1196 SH-FA 1 and 2 220kV transmission circuits tripped with lightning in area. | FALSE | Critical
177631 | 28173 | 1884 |  |  | 2012-12-08 19:41 | 2012-12-08 19:51 | 10 | E0539 | SH-FA 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1196 SH-FA 1 and 2 220kV transmission circuits tripped with lightning in area. | FALSE | Critical
198671 | 28173 | 1884 |  |  | 2012-12-08 19:41 | 2012-12-08 19:41 | 0 | E0409 | SH-CE 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1196 SH-FA 1 and 2 220kV transmission circuits tripped with lightning in area. | FALSE | Non-Critical
198672 | 28173 | 1884 |  |  | 2012-12-08 19:41 | 2012-12-08 19:41 | 0 | E0553 | SH-WI 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1196 SH-FA 1 and 2 220kV transmission circuits tripped with lightning in area. | FALSE | Non-Critical
196363 | 28176 | 1887 |  |  | 2012-12-13 06:06 | 2012-12-13 06:12 | 6 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 145 | TRUE |  | IR1199 FA-RB-QT 110 kV transmission circuit tripped with Lightning in area. | FALSE | Non-Critical
177818 | 28177 | 9700 |  |  | 2012-12-08 05:38 | 2012-12-08 05:38 | 0 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198674 | 28296 | 1888 |  |  | 2012-12-15 11:05 | 2012-12-17 18:08 | 3303 | E0785 | QU 110/22 kV T1 Transformer Circuit | Transformer | Fault | Internal Fault | Transend | Completed | TRUE | 142 | TRUE |  | IR1200 Que T1 transformer tripped | FALSE | Non-Critical
178990 | 28297 | 1889 |  |  | 2012-12-24 14:18 | 2012-12-24 14:38 | 20 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 70 | TRUE |  | IR1201 LF-SO-TB 110 kV transmission circuit tripped with lightning in area | FALSE | Non-Critical
180375 | 28344 | 9701 |  |  | 2012-12-08 06:18 | 2012-12-08 06:18 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
180417 | 28345 | 9702 |  |  | 2012-12-08 17:12 | 2012-12-08 17:12 | 0 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191508 | 28347 | 9703 |  |  | 2012-12-08 19:40 | 2012-12-08 19:40 | 0 | E0943 | UL 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
180377 | 28348 | 9704 |  |  | 2012-12-10 11:57 | 2012-12-10 12:17 | 20 | E0353 | LF 33 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181323 | 28349 | 9705 |  |  | 2012-12-11 05:46 | 2012-12-11 05:46 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
186579 | 28350 | 9706 |  |  | 2012-12-13 06:23 | 2012-12-13 06:23 | 0 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181324 | 28351 | 9708 |  |  | 2012-12-14 06:05 | 2012-12-14 06:42 | 37 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181325 | 28352 | 9709 |  |  | 2012-12-15 04:52 | 2012-12-15 05:18 | 26 | E0084 | CR 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
180378 | 28353 | 9710 |  |  | 2012-12-16 05:57 | 2012-12-16 06:14 | 17 | E0343 | LF 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
180379 | 28354 | 9711 |  |  | 2012-12-17 06:32 | 2012-12-17 07:50 | 78 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182505 | 28355 | 9712 |  |  | 2012-12-17 15:25 | 2012-12-17 15:43 | 18 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
180094 | 28356 | 9713 |  |  | 2012-12-18 06:01 |  |  | E0142 | NN 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
180418 | 28357 | 9714 |  |  | 2012-12-18 23:09 | 2012-12-18 23:09 | 0 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
187971 | 28358 | 9715 |  |  | 2012-12-19 09:54 | 2012-12-19 09:54 | 0 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193211 | 28359 | 9716 |  |  | 2012-12-22 00:19 | 2012-12-22 00:38 | 19 | E0906 | TR 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182506 | 28360 | 9717 |  |  | 2012-12-22 01:51 | 2012-12-22 03:24 | 93 | E0012 | BW 11 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
180380 | 28361 | 9718 |  |  | 2012-12-22 17:13 | 2012-12-22 17:13 | 0 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
180100 | 28362 | 9719 |  |  | 2012-12-22 19:06 | 2012-12-22 19:06 | 0 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181326 | 28363 | 9720 |  |  | 2012-12-22 19:51 | 2012-12-22 19:51 | 0 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
180381 | 28364 | 9721 |  |  | 2012-12-23 15:05 | 2012-12-23 15:20 | 15 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
180382 | 28365 | 9722 |  |  | 2012-12-23 16:58 | 2012-12-23 16:58 | 0 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181327 | 28366 | 9723 |  |  | 2012-12-25 03:37 | 2012-12-25 03:37 | 0 | E1554 | DP 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181328 | 28367 | 9724 |  |  | 2012-12-25 17:00 | 2012-12-25 17:00 | 0 | E1827 | TU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
181329 | 28368 | 9725 |  |  | 2012-12-26 08:24 | 2012-12-26 08:24 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195913 | 28369 | 9726 |  |  | 2012-12-26 10:40 | 2012-12-26 10:59 | 19 | E1496 | LF 33 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182740 | 28370 | 9727 |  |  | 2012-12-27 00:09 | 2012-12-27 00:09 | 0 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
180384 | 28371 | 9728 |  |  | 2012-12-28 05:46 | 2012-12-28 05:46 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181330 | 28372 | 9729 |  |  | 2012-12-29 22:21 | 2012-12-29 22:21 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
180385 | 28373 | 9732 |  |  | 2012-12-30 20:39 | 2012-12-30 20:39 | 0 | E1886 | SL 22 kV D2 Feeder | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
185826 | 28422 | 9735 |  |  | 2013-01-03 17:41 | 2013-01-03 19:04 | 83 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181332 | 28423 | 9736 |  |  | 2013-01-03 13:50 | 2013-01-03 19:18 | 328 | E1826 | TU 22kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
181333 | 28424 | 9737 |  |  | 2013-01-03 18:04 | 2013-01-03 21:37 | 213 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181334 | 28425 | 9738 |  |  | 2013-01-03 19:01 | 2013-01-03 21:42 | 161 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
184923 | 28426 | 9739 |  |  | 2013-01-03 17:36 | 2013-01-03 21:45 | 249 | E0078 | CR 33 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191510 | 28427 | 9740 |  |  | 2013-01-03 17:39 | 2013-01-03 21:45 | 246 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
190512 | 28428 | 9741 |  |  | 2013-01-04 05:53 | 2013-01-04 05:53 | 0 | E1535 | MY 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
202516 | 28429 | 9742 |  |  | 2013-01-04 10:40 | 2013-01-04 11:19 | 39 | E1533 | MY 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
184924 | 28430 | 9743 |  |  | 2013-01-04 12:46 | 2013-01-04 16:16 | 210 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181335 | 28431 | 9744 |  |  | 2013-01-04 16:22 | 2013-01-04 17:22 | 60 | E0640 | ST 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182742 | 28432 | 9745 |  |  | 2013-01-04 15:33 | 2013-01-04 15:39 | 6 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181336 | 28433 | 9748 |  |  | 2013-01-04 16:29 | 2013-01-04 20:23 | 234 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
180606 | 28434 | 9750 |  |  | 2013-01-05 05:54 | 2013-01-05 05:54 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181337 | 28435 | 9751 |  |  | 2013-01-05 07:13 | 2013-01-05 07:13 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181338 | 28437 | 9753 |  |  | 2013-01-05 08:34 | 2013-01-05 08:34 | 0 | E0865 | RB 44 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181339 | 28438 | 9754 |  |  | 2013-01-05 18:54 | 2013-01-05 18:54 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181340 | 28439 | 9755 |  |  | 2013-01-06 16:57 | 2013-01-06 16:57 | 0 | E1826 | TU 22kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
181341 | 28440 | 9756 |  |  | 2013-01-06 17:52 | 2013-01-06 17:53 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181342 | 28441 | 9757 |  |  | 2013-01-07 16:53 | 2013-01-07 19:14 | 141 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181343 | 28442 | 9758 |  |  | 2013-01-07 21:29 | 2013-01-07 21:29 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
203615 | 28443 | 9760 |  |  | 2013-01-08 09:11 | 2013-01-08 09:56 | 45 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
184925 | 28444 | 9761 |  |  | 2013-01-08 11:06 | 2013-01-08 12:08 | 62 | E1454 | HA 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181344 | 28445 | 9763 |  |  | 2013-01-09 01:44 | 2013-01-09 07:41 | 357 | E0865 | RB 44 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181345 | 28446 | 9764 |  |  | 2013-01-10 05:55 | 2013-01-10 05:55 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182519 | 28447 | 9765 |  |  | 2013-01-11 00:56 | 2013-01-11 00:56 | 0 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182743 | 28448 | 9767 |  |  | 2013-01-11 07:24 | 2013-01-11 07:24 | 0 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181346 | 28449 | 9768 |  |  | 2013-01-11 04:34 | 2013-01-11 08:03 | 209 | E0640 | ST 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182520 | 28450 | 9769 |  |  | 2013-01-11 13:25 | 2013-01-11 13:25 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181347 | 28451 | 9770 |  |  | 2013-01-12 05:30 | 2013-01-12 05:45 | 15 | E0084 | CR 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181348 | 28452 | 9771 |  |  | 2013-01-15 17:24 | 2013-01-15 17:24 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181349 | 28453 | 9772 |  |  | 2013-01-16 15:31 | 2013-01-16 16:46 | 75 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189032 | 28454 | 9773 |  |  | 2013-01-16 18:25 | 2013-01-16 18:25 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
180626 | 28455 | 9774 |  |  | 2013-01-18 00:42 |  |  | E1041 | SD 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185827 | 28457 | 9776 |  |  | 2013-01-18 12:51 | 2013-01-18 13:56 | 65 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
192028 | 28458 | 9777 |  |  | 2013-01-18 23:55 | 2013-01-18 23:55 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
184926 | 28459 | 9778 |  |  | 2013-01-21 01:07 | 2013-01-21 01:07 | 0 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181350 | 28460 | 9780 |  |  | 2013-01-21 18:07 | 2013-01-21 18:11 | 4 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189033 | 28461 | 9781 |  |  | 2013-01-21 21:14 | 2013-01-21 21:14 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
184927 | 28462 | 9782 |  |  | 2013-01-21 22:04 | 2013-01-21 22:04 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181351 | 28509 | 9783 |  |  | 2013-01-23 03:17 | 2013-01-23 03:38 | 21 | E1613 | UL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181352 | 28510 | 9784 |  |  | 2013-01-23 23:34 | 2013-01-23 23:34 | 0 | E1613 | UL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183103 | 28511 | 9785 |  |  | 2013-01-25 05:44 | 2013-01-25 05:44 | 0 | E0656 | SM 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182537 | 28512 | 9786 |  |  | 2013-01-25 07:05 | 2013-01-25 08:50 | 105 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
184928 | 28513 | 9787 |  |  | 2013-01-25 10:31 | 2013-01-25 10:31 | 0 | E1042 | SD 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181391 | 28514 | 9788 |  |  | 2013-01-25 22:50 | 2013-01-25 23:24 | 34 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182744 | 28515 | 9790 |  |  | 2013-01-26 17:37 | 2013-01-26 17:37 | 0 | E0464 | KR 11 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185828 | 28516 | 9791 |  |  | 2013-01-26 22:57 | 2013-01-26 22:57 | 0 | E0149 | NN 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181354 | 28517 | 9792 |  |  | 2013-01-28 05:16 | 2013-01-28 05:16 | 0 | E1554 | DP 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181355 | 28518 | 9794 |  |  | 2013-01-28 23:56 | 2013-01-29 00:14 | 18 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182538 | 28519 | 9796 |  |  | 2013-01-30 00:51 | 2013-01-30 00:51 | 0 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181356 | 28520 | 9797 |  |  | 2013-01-30 05:36 | 2013-01-30 05:36 | 0 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181358 | 28524 | 9800 |  |  | 2013-01-31 08:17 | 2013-01-31 08:17 | 0 | E1827 | TU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
182911 | 28525 | 1891 |  |  | 2013-02-02 12:00 | 2013-02-02 13:23 | 83 | E0701 | FA 220 kV B Bus | Bus | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1210 Farrell 220 kV transmission circuits tripped during planned work due to intertrip from generator. Hydro initiated protection operation. | FALSE | Undefined
182912 | 28525 | 1891 |  |  | 2013-02-02 12:00 | 2013-02-02 13:25 | 85 | E0704 | FA 220/110 kV T1 Transformer Circuit | Transformer | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1210 Farrell 220 kV transmission circuits tripped during planned work due to intertrip from generator. Hydro initiated protection operation. | FALSE | Non-Critical
182910 | 28525 | 1891 |  |  | 2013-02-02 12:00 | 2013-02-02 13:24 | 84 | E0539 | SH-FA 2 220 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1210 Farrell 220 kV transmission circuits tripped during planned work due to intertrip from generator. Hydro initiated protection operation. | FALSE | Critical
182913 | 28525 | 1891 |  |  | 2013-02-02 12:00 | 2013-02-02 13:25 | 85 | E0715 | FA-JB 220 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1210 Farrell 220 kV transmission circuits tripped during planned work due to intertrip from generator. Hydro initiated protection operation. | FALSE | Non-Critical
182914 | 28525 | 1891 |  |  | 2013-02-02 12:00 | 2013-02-02 13:25 | 85 | E0717 | FA-RC 2 220 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1210 Farrell 220 kV transmission circuits tripped during planned work due to intertrip from generator. Hydro initiated protection operation. | FALSE | Non-Critical
181133 | 28526 | 1890 |  |  | 2013-01-28 11:45 | 2013-01-28 16:38 | 293 | E0587 | UL-EB 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1209 UL-EB 110 kV transmission circuit tripped due to equipment failure. | FALSE | Non-Critical
198676 | 28549 | 1873 |  |  | 2012-11-30 20:37 | 2012-11-30 21:20 | 43 | E1731 | LI-WA-PM 2 220 kV Transmission Circuit | Transmission | Fault | Fire (Bush) | Transend | Completed | TRUE | 0 | TRUE |  | IR1185 LI-WA-PM 1&2 110 kV transmission ciruits tripped due to fire. | FALSE | Critical
181392 | 28549 | 1873 |  |  | 2012-11-30 20:37 | 2012-11-30 21:20 | 43 | E1723 | LI-WA-PM 1 220 kV Transmission Circuit | Transmission | Fault | Fire (Bush) | Transend | Completed | TRUE | 0 | TRUE |  | IR1185 LI-WA-PM 1&2 110 kV transmission ciruits tripped due to fire. | FALSE | Critical
181548 | 28550 | 9801 |  |  | 2013-02-01 19:36 | 2013-02-01 19:37 | 1 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181549 | 28551 | 9802 |  |  | 2013-02-01 18:16 | 2013-02-01 19:57 | 101 | E1479 | RI 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181550 | 28552 | 9803 |  |  | 2013-02-02 09:25 | 2013-02-02 09:25 | 0 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181551 | 28553 | 9804 |  |  | 2013-02-03 06:37 | 2013-02-03 06:37 | 0 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181552 | 28554 | 9805 |  |  | 2013-02-03 08:17 | 2013-02-03 11:08 | 171 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182544 | 28555 | 9806 |  |  | 2013-02-03 12:17 | 2013-02-03 12:18 | 1 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181554 | 28556 | 9807 |  |  | 2013-02-03 21:37 | 2013-02-03 21:38 | 1 | E1886 | SL 22 kV D2 Feeder | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
181555 | 28557 | 9808 |  |  | 2013-02-05 10:33 | 2013-02-05 10:33 | 0 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181556 | 28558 | 9809 |  |  | 2013-02-05 16:39 | 2013-02-05 16:39 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
184929 | 28559 | 9810 |  |  | 2013-02-05 20:44 | 2013-02-05 20:44 | 0 | E0766 | NW 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181558 | 28560 | 9811 |  |  | 2013-02-05 22:21 | 2013-02-05 22:21 | 0 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181559 | 28561 | 9812 |  |  | 2013-02-06 20:37 | 2013-02-06 21:07 | 30 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181560 | 28562 | 9813 |  |  | 2013-02-07 01:09 | 2013-02-07 04:04 | 175 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181561 | 28563 | 9814 |  |  | 2013-02-07 05:19 | 2013-02-07 08:22 | 183 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181562 | 28564 | 9815 |  |  | 2013-02-07 15:02 | 2013-02-07 16:39 | 97 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181564 | 28566 | 9817 |  |  | 2013-02-07 21:30 | 2013-02-07 23:30 | 120 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181565 | 28567 | 9818 |  |  | 2013-02-08 00:43 | 2013-02-08 00:43 | 0 | E0643 | ST 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181566 | 28568 | 9819 |  |  | 2013-02-07 21:48 | 2013-02-07 21:48 | 0 | E0497 | GT 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181567 | 28569 | 9820 |  |  | 2013-02-08 09:45 | 2013-02-08 11:53 | 128 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181568 | 28570 | 9821 |  |  | 2013-02-09 05:24 | 2013-02-09 05:24 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181569 | 28571 | 9822 |  |  | 2013-02-09 09:01 | 2013-02-09 09:01 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181570 | 28572 | 9823 |  |  | 2013-02-09 09:06 | 2013-02-09 09:06 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181571 | 28573 | 9824 |  |  | 2013-02-09 09:40 | 2013-02-09 11:29 | 109 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
181572 | 28575 | 9826 |  |  | 2013-02-09 15:28 | 2013-02-09 15:28 | 0 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182930 | 28635 | 1892 |  |  | 2013-02-06 06:26 | 2013-02-06 07:29 | 63 | E1878 | SL 110/22 kV T1 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 299 | TRUE |  | IR1215 St Leonards T1 and T2 transformer circuits tripped folllowing a feeder fault due to a protection grading issue.. | FALSE | Non-Critical
182931 | 28635 | 1892 |  |  | 2013-02-06 06:26 | 2013-02-06 07:29 | 63 | E1879 | SL 110/22 kV T2 Transformer | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR1215 St Leonards T1 and T2 transformer circuits tripped folllowing a feeder fault due to a protection grading issue.. | FALSE | Non-Critical
182209 | 28636 | 1893 |  |  | 2013-02-09 11:44 | 2013-02-09 14:30 | 166 | E0397 | BU 220/110 kV T2 Transformer Circuit | Transformer | Fault | Insulation Failure | Transend | Completed | TRUE | 0 | TRUE |  | IR1220 Burnie T2 transformer circuit tripped, due to insulation failure on control circuit. | FALSE | Non-Critical
182245 | 28637 | 9827 |  |  | 2013-02-09 13:38 | 2013-02-09 17:00 | 202 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182246 | 28638 | 9828 |  |  | 2013-02-09 21:55 | 2013-02-09 21:55 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182576 | 28639 | 9803 |  |  | 2013-02-11 00:12 | 2013-02-11 00:12 | 0 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182577 | 28640 | 9831 |  |  | 2013-02-12 05:54 | 2013-02-12 05:54 | 0 | E1548 | DP 22 kV C2 Capacitor Circuit | Capacitor | Fault |  | DNSP | Completed | FALSE | 0 | TRUE |  |  | FALSE | Undefined
182578 | 28641 | 9832 |  |  | 2013-02-12 23:02 | 2013-02-12 23:02 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182579 | 28642 | 9833 |  |  | 2013-02-13 00:45 | 2013-02-13 01:03 | 18 | E0085 | CR 33 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182580 | 28643 | 9834 |  |  | 2013-02-13 05:24 | 2013-02-13 05:45 | 21 | E0496 | GT 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182581 | 28644 | 9836 |  |  | 2013-02-13 20:01 | 2013-02-13 20:01 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182582 | 28645 | 9837 |  |  | 2013-02-14 19:04 | 2013-02-14 19:04 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182584 | 28647 | 9839 |  |  | 2013-02-16 07:14 | 2013-02-16 07:15 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182585 | 28648 | 9840 |  |  | 2013-02-16 06:59 | 2013-02-16 12:54 | 355 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182586 | 28649 | 9841 |  |  | 2013-02-16 17:24 | 2013-02-16 21:03 | 219 | E0104 | CS 11 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182587 | 28650 | 9842 |  |  | 2013-02-16 20:40 | 2013-02-16 20:40 | 0 | E1827 | TU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
182588 | 28651 | 9843 |  |  | 2013-02-16 23:49 | 2013-02-16 23:49 | 0 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182589 | 28652 | 9844 |  |  | 2013-02-17 01:44 | 2013-02-17 02:36 | 52 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182590 | 28653 | 9845 |  |  | 2013-02-18 06:40 | 2013-02-18 07:06 | 26 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182591 | 28654 | 9846 |  |  | 2013-02-19 06:06 | 2013-02-19 06:06 | 0 | E0823 | RA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182592 | 28655 | 9847 |  |  | 2013-02-19 08:50 | 2013-02-19 08:51 | 1 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182593 | 28656 | 9848 |  |  | 2013-02-20 00:11 | 2013-02-20 00:11 | 0 | E1548 | DP 22 kV C2 Capacitor Circuit | Capacitor | Fault |  | DNSP | Completed | FALSE | 0 | TRUE |  |  | FALSE | Undefined
182594 | 28657 | 9849 |  |  | 2013-02-21 07:39 | 2013-02-21 07:39 | 0 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182595 | 28658 | 9850 |  |  | 2013-02-22 06:01 | 2013-02-22 06:01 | 0 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182596 | 28659 | 9851 |  |  | 2013-02-22 09:00 | 2013-02-22 09:00 | 0 | E1827 | TU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
182649 | 28711 | 1894 |  |  | 2013-02-26 23:22 | 2013-02-27 00:13 | 51 | E1870 | NW-SL 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1229 NW-SL 110 kV transmission circuit tripped due to relay failure. | FALSE | Non-Critical
182650 | 28712 | 9829 |  |  | 2013-02-10 22:13 | 2013-02-10 22:13 | 0 | E1826 | TU 22kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
182652 | 28714 | 9852 |  |  | 2013-02-23 00:43 | 2013-02-23 00:43 | 0 | E1552 | DP 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182653 | 28715 | 9853 |  |  | 2013-02-23 14:18 | 2013-02-23 14:18 | 0 | E0639 | ST 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182654 | 28716 | 9854 |  |  | 2013-02-24 06:50 | 2013-02-24 06:50 | 0 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182655 | 28717 | 9855 |  |  | 2013-02-24 06:57 | 2013-02-24 06:57 | 0 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182656 | 28718 | 9856 |  |  | 2013-02-24 07:05 | 2013-02-24 07:05 | 0 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182657 | 28719 | 9857 |  |  | 2013-02-24 07:30 | 2013-02-24 07:30 | 0 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182658 | 28722 | 9860 |  |  | 2013-02-24 16:13 | 2013-02-24 16:13 | 0 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182659 | 28723 | 9861 |  |  | 2013-02-24 21:30 | 2013-02-24 21:30 | 0 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182660 | 28724 | 9862 |  |  | 2013-02-25 02:48 | 2013-02-25 02:48 | 0 | E0946 | UL 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182661 | 28725 | 9863 |  |  | 2013-02-25 19:57 | 2013-02-25 20:57 | 60 | E0357 | KI 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182662 | 28726 | 9864 |  |  | 2013-02-25 22:16 | 2013-02-25 22:16 | 0 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182663 | 28727 | 9865 |  |  | 2013-02-25 22:17 | 2013-02-25 22:17 | 0 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182664 | 28728 | 9866 |  |  | 2013-02-26 17:31 | 2013-02-26 17:45 | 14 | E1826 | TU 22kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
182665 | 28729 | 9867 |  |  | 2013-02-27 22:01 | 2013-02-27 22:25 | 24 | E0494 | GT 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182666 | 28730 | 9868 |  |  | 2013-02-28 13:10 | 2013-02-28 13:35 | 25 | E1560 | HA 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182667 | 28731 | 9869 |  |  | 2013-03-02 18:57 | 2013-03-02 18:57 | 0 | E0152 | NN 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182668 | 28732 | 9870 |  |  | 2013-03-03 00:18 | 2013-03-03 00:18 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
182669 | 28733 | 9871 |  |  | 2013-03-03 12:14 | 2013-03-03 13:00 | 46 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
184422 | 28734 | 9872 |  |  | 2013-03-04 01:05 | 2013-03-04 01:05 | 0 | E1663 | EL 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183267 | 28765 | 9873 |  |  | 2013-03-04 20:26 | 2013-03-04 20:26 | 0 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183268 | 28766 | 9874 |  |  | 2013-03-04 20:26 | 2013-03-04 20:26 | 0 | E1444 | HA 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183269 | 28767 | 9875 |  |  | 2013-03-06 08:28 | 2013-03-06 08:28 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183270 | 28768 | 9876 |  |  | 2013-03-06 23:01 | 2013-03-06 23:01 | 0 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183271 | 28769 | 9877 |  |  | 2013-03-06 23:43 | 2013-03-07 00:03 | 20 | E1538 | MY 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183272 | 28770 | 9878 |  |  | 2013-03-07 00:46 | 2013-03-07 00:46 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183273 | 28771 | 9880 |  |  | 2013-03-07 14:36 | 2013-03-08 01:36 | 660 | E0915 | TR 22 kV V2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183274 | 28772 | 9883 |  |  | 2013-03-11 05:15 | 2013-03-11 05:33 | 18 | E0303 | AV 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183275 | 28773 | 9885 |  |  | 2013-03-11 04:21 | 2013-03-11 07:32 | 191 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183276 | 28774 | 9886 |  |  | 2013-03-12 02:28 | 2013-03-12 02:28 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183277 | 28775 | 9887 |  |  | 2013-03-12 06:01 | 2013-03-12 06:01 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183354 | 28827 | 9888 |  |  | 2013-03-13 07:18 | 2013-03-13 11:37 | 259 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183355 | 28828 | 9889 |  |  | 2013-03-14 21:14 | 2013-03-14 21:14 | 0 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183356 | 28829 | 9890 |  |  | 2013-03-15 01:14 | 2013-03-15 01:14 | 0 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183357 | 28830 | 9891 |  |  | 2013-03-15 03:16 | 2013-03-15 03:16 | 0 | E0023 | BW 11 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183358 | 28831 | 9892 |  |  | 2013-03-15 03:16 | 2013-03-15 03:35 | 19 | E0019 | BW 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183359 | 28832 | 9893 |  |  | 2013-03-15 09:43 | 2013-03-15 09:43 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183442 | 28833 | 1895 |  |  | 2013-03-05 07:25 | 2013-03-05 07:38 | 13 | E1518 | PL 22 kV J2 Feeder Circuit | Feeder | Fault | Intertrip | MI | Completed | TRUE | 0 | TRUE |  | IR1230 Port Latta feeders tripped, suspect Grange Resources misoperation in their yard. | FALSE | Undefined
183441 | 28833 | 1895 |  |  | 2013-03-05 07:25 | 2013-03-05 07:37 | 12 | E0779 | PL 22 kV B2 Feeder Circuit | Feeder | Fault | Intertrip | MI | Completed | TRUE | 95 | TRUE |  | IR1230 Port Latta feeders tripped, suspect Grange Resources misoperation in their yard. | FALSE | Undefined
183451 | 28834 | 1898 |  |  | 2013-03-10 14:15 | 2013-03-10 14:23 | 8 | E0400 | BU-HM 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1233 FA-QU-SR-HM 110 kV line tripped due to lightning. | FALSE | Non-Critical
183452 | 28834 | 1898 |  |  | 2013-03-10 14:15 | 2013-03-10 14:23 | 8 | E0406 | FA-QU-SR-HM 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 165 | TRUE |  | IR1233 FA-QU-SR-HM 110 kV line tripped due to lightning. | FALSE | Non-Critical
183453 | 28835 | 1902 |  |  | 2013-03-21 19:05 | 2013-03-21 19:05 | 0 | E0404 | SH-BU 2 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1254 Lightning storm trips multiple 220 and 110 kV lines in the North West. | FALSE | Non-Critical
183456 | 28835 | 1902 |  |  | 2013-03-21 18:34 | 2013-03-21 18:46 | 12 | E0538 | SH-FA 1 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1254 Lightning storm trips multiple 220 and 110 kV lines in the North West. | FALSE | Critical
183457 | 28835 | 1902 |  |  | 2013-03-21 18:34 | 2013-03-21 18:48 | 14 | E0539 | SH-FA 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1254 Lightning storm trips multiple 220 and 110 kV lines in the North West. | FALSE | Critical
183458 | 28835 | 1902 |  |  | 2013-03-21 19:05 | 2013-03-21 19:07 | 2 | E0550 | SH-PA Tee 110 kV Transmission Circuit Section | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1254 Lightning storm trips multiple 220 and 110 kV lines in the North West. | FALSE | Non-Critical
183459 | 28835 | 1902 |  |  | 2013-03-21 18:48 | 2013-03-21 18:48 | 0 | E0554 | SH-WV 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1254 Lightning storm trips multiple 220 and 110 kV lines in the North West. | FALSE | Non-Critical
183460 | 28835 | 1902 |  |  | 2013-03-21 18:34 | 2013-03-21 18:49 | 15 | E0715 | FA-JB 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1254 Lightning storm trips multiple 220 and 110 kV lines in the North West. | FALSE | Non-Critical
183461 | 28835 | 1902 |  |  | 2013-03-21 18:34 | 2013-03-21 18:49 | 15 | E0717 | FA-RC 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1254 Lightning storm trips multiple 220 and 110 kV lines in the North West. | FALSE | Non-Critical
183998 | 28835 | 1902 |  |  | 2013-03-21 19:01 | 2013-03-21 19:02 | 1 | E0516 | SH-GT 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1254 Lightning storm trips multiple 220 and 110 kV lines in the North West. | FALSE | Critical
183939 | 28929 | 9894 |  |  | 2013-03-16 13:25 | 2013-03-16 13:25 | 0 | E1001 | BU 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183940 | 28930 | 9895 |  |  | 2013-03-16 13:13 | 2013-03-16 14:03 | 50 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183941 | 28931 | 9897 |  |  | 2013-03-16 13:34 | 2013-03-16 17:28 | 234 | E0303 | AV 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183942 | 28932 | 9898 |  |  | 2013-03-16 17:32 | 2013-03-16 20:40 | 188 | E0303 | AV 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183943 | 28933 | 9900 |  |  | 2013-03-17 19:03 | 2013-03-17 19:05 | 2 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183944 | 28934 | 9902 |  |  | 2013-03-17 20:28 | 2013-03-17 20:54 | 26 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183945 | 28935 | 9903 |  |  | 2013-03-17 21:41 | 2013-03-17 21:41 | 0 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183946 | 28936 | 9904 |  |  | 2013-03-18 04:00 | 2013-03-18 04:00 | 0 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183947 | 28937 | 9905 |  |  | 2013-03-18 06:38 | 2013-03-18 06:53 | 15 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183948 | 28938 | 9906 |  |  | 2013-03-18 19:46 | 2013-03-18 19:46 | 0 | E0389 | BU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183949 | 28939 | 9907 |  |  | 2013-03-20 05:58 | 2013-03-20 18:39 | 761 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183950 | 28940 | 9909 |  |  | 2013-03-21 04:49 | 2013-03-21 04:49 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183951 | 28941 | 9910 |  |  | 2013-03-21 07:56 | 2013-03-21 07:56 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183952 | 28942 | 9911 |  |  | 2013-03-21 15:19 | 2013-03-21 15:48 | 29 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183953 | 28943 | 9912 |  |  | 2013-03-21 15:58 | 2013-03-21 15:59 | 1 | E1051 | SR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183954 | 28944 | 9913 |  |  | 2013-03-21 18:34 | 2013-03-21 18:35 | 1 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183955 | 28945 | 9914 |  |  | 2013-03-21 17:45 | 2013-03-21 19:19 | 94 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183956 | 28946 | 9915 |  |  | 2013-03-21 19:05 | 2013-03-21 19:05 | 0 | E0819 | RA 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183975 | 28958 | 9908 |  |  | 2013-03-21 03:11 | 2013-03-21 03:11 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183976 | 28959 | 9916 |  |  | 2013-03-21 19:15 | 2013-03-21 19:16 | 1 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183977 | 28960 | 9917 |  |  | 2013-03-21 19:18 | 2013-03-21 19:18 | 0 | E1552 | DP 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183978 | 28961 | 9919 |  |  | 2013-03-21 20:17 | 2013-03-21 20:17 | 0 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183979 | 28962 | 9918 |  |  | 2013-03-21 20:04 | 2013-03-21 20:05 | 1 | E0820 | RA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183980 | 28963 | 9920 |  |  | 2013-03-23 15:09 | 2013-03-23 15:11 | 2 | E1893 | SL 22 kV J2 Feeder | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
183981 | 28964 | 9921 |  |  | 2013-03-23 15:13 | 2013-03-24 00:15 | 542 | E0489 | GT 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183982 | 28965 | 9922 |  |  | 2013-03-24 02:25 | 2013-03-24 02:25 | 0 | E1826 | TU 22kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
183983 | 28966 | 9924 |  |  | 2013-03-26 23:31 | 2013-03-26 23:32 | 1 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183984 | 28967 | 9926 |  |  | 2013-03-28 19:26 | 2013-03-28 19:26 | 0 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183985 | 28968 | 9927 |  |  | 2013-03-28 23:03 | 2013-03-28 23:03 | 0 | E1042 | SD 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183986 | 28969 | 9928 |  |  | 2013-03-29 02:09 | 2013-03-29 02:09 | 0 | E0946 | UL 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183987 | 28970 | 9929 |  |  | 2013-03-31 07:00 | 2013-03-31 07:01 | 1 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183988 | 28971 | 9930 |  |  | 2013-03-31 14:43 | 2013-03-31 14:44 | 1 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
183989 | 28972 | 9931 |  |  | 2013-03-31 20:39 | 2013-03-31 20:39 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
184000 | 28974 | 1897 |  |  | 2013-03-08 20:32 | 2013-03-09 12:50 | 978 | E0585 | EB 110/11 kV T2 Transformer Circuit | Transformer | Fault | Pollution | Transend | Completed | TRUE | 0 | TRUE |  | IR1232 Emu Bay T2 110/11 kV and BU-EB 110 kV transmission circuits tripped due to a fault in a CB control board. | FALSE | Non-Critical
183999 | 28974 | 1897 |  |  | 2013-03-08 20:32 | 2013-03-08 21:39 | 67 | E0399 | BU-EB 110 kV Transmission Circuit | Transmission | Fault | Pollution | Transend | Completed | TRUE | 0 | TRUE |  | IR1232 Emu Bay T2 110/11 kV and BU-EB 110 kV transmission circuits tripped due to a fault in a CB control board. | FALSE | Non-Critical
184001 | 28975 | 1901 |  |  | 2013-03-18 13:04 | 2013-03-18 13:34 | 30 | E1762 | LF-MT-RK 1 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1253 LF-MT-RK 110 kV transmission circuit tripped due to poor isolation. | FALSE | Non-Critical
184002 | 28976 | 1910 |  |  | 2013-03-21 20:57 | 2013-03-22 13:27 | 990 | E0516 | SH-GT 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1258 SH-GT 2 220 kV transmission circuit tripped with lightning in area. Rio Tinto dropped 226 MW load. | FALSE | Critical
184003 | 28977 | 1912 |  |  | 2013-03-27 00:02 | 2013-03-27 02:24 | 142 | E1927 | MR-DE 110 kV Transmission Circuit | Transmission | Fault | Protection Design / Calculations Incorrect | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1259 MR-DE 110 kV transmission circuit tripped due to protection error. | FALSE | Undefined
184004 | 28978 | 1913 |  |  | 2013-03-27 09:03 | 2013-03-27 09:16 | 13 | E0721 | QT-NT 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 34 | TRUE |  | IR1260 QT-NT 110 kV transmission circuit tripped during work for new Newton T2 circuit. | FALSE | Non-Critical
184005 | 28979 | 1914 |  |  | 2013-03-28 09:19 | 2013-03-28 09:56 | 37 | E0282 | PM 220/110 kV T1 Transformer Circuit | Transformer | Fault | Mechanical Failure | Transend | Completed | TRUE | 0 | TRUE |  | IR1261 Palmerston T1 tripped manually by local operator due to arcing incident after disconnector got stuck while opening due to loss on interlock supply. | FALSE | Non-Critical
185120 | 29081 | 9932 |  |  | 2013-04-01 08:00 | 2013-04-01 08:01 | 1 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185121 | 29082 | 9933 |  |  | 2013-04-02 19:25 | 2013-04-02 19:25 | 0 | E1531 | MY 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185122 | 29083 | 9934 |  |  | 2013-04-03 23:13 | 2013-04-03 23:13 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185123 | 29084 | 9935 |  |  | 2013-04-05 09:53 | 2013-04-05 09:53 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185124 | 29085 | 9936 |  |  | 2013-04-06 15:42 | 2013-04-06 15:42 | 0 | E0908 | TR 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185125 | 29086 | 9937 |  |  | 2013-04-09 22:54 | 2013-04-09 22:54 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185126 | 29087 | 9938 |  |  | 2013-04-10 17:45 | 2013-04-10 17:45 | 0 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185127 | 29088 | 9940 |  |  | 2013-04-11 03:48 | 2013-04-11 04:32 | 44 | E0075 | CR 33 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185128 | 29089 | 9941 |  |  | 2013-04-11 08:08 | 2013-04-11 08:08 | 0 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185129 | 29090 | 9942 |  |  | 2013-04-11 23:10 | 2013-04-11 23:10 | 0 | E1613 | UL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185130 | 29091 | 9943 |  |  | 2013-04-17 07:45 | 2013-04-17 08:03 | 18 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185131 | 29092 | 9945 |  |  | 2013-04-18 09:12 | 2013-04-18 09:38 | 26 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185132 | 29093 | 9946 |  |  | 2013-04-18 10:20 | 2013-04-18 10:21 | 1 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185133 | 29094 | 9947 |  |  | 2013-04-18 09:13 | 2013-04-18 10:25 | 72 | E0357 | KI 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185134 | 29095 | 9948 |  |  | 2013-04-18 11:14 | 2013-04-18 11:15 | 1 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185135 | 29096 | 9949 |  |  | 2013-04-20 18:07 | 2013-04-20 18:07 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185136 | 29097 | 9950 |  |  | 2013-04-21 04:01 | 2013-04-21 04:02 | 1 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185137 | 29098 | 9952 |  |  | 2013-04-22 14:18 | 2013-04-22 14:18 | 0 | E0823 | RA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185138 | 29099 | 9954 |  |  | 2013-04-23 00:45 | 2013-04-23 00:46 | 1 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185139 | 29100 | 9956 |  |  | 2013-04-24 06:05 | 2013-04-24 06:06 | 1 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185140 | 29101 | 9957 |  |  | 2013-04-25 04:27 | 2013-04-25 05:04 | 37 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185141 | 29102 | 9958 |  |  | 2013-04-25 12:25 | 2013-04-25 12:25 | 0 | E0197 | SO 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185142 | 29103 | 9959 |  |  | 2013-04-25 14:37 | 2013-04-25 14:37 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185143 | 29104 | 9960 |  |  | 2013-04-25 18:29 | 2013-04-25 18:30 | 1 | E0149 | NN 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185144 | 29105 | 9961 |  |  | 2013-04-26 18:38 | 2013-04-26 18:38 | 0 | E1554 | DP 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
185385 | 29190 | 1916 |  |  | 2013-04-17 07:42 | 2013-04-17 07:42 | 0 | E0785 | QU 110/22 kV T1 Transformer Circuit | Transformer | Fault | Customer | Transend | Completed | TRUE | 0 | TRUE |  | IR1298 Que T1 transformer tripped and reclosed due to relay failure. | FALSE | Non-Critical
185512 | 29191 | 1915 |  |  | 2013-04-09 12:19 | 2013-04-09 12:32 | 13 | E0233 | RI 11 kV D3 Feeder Circuit | Feeder | Fault | Intertrip | MI | Completed | TRUE | 180 | TRUE |  | IR1262 Risdon D352A 11 kV feeder tripped due to intertrip from Nyrstar. | FALSE | Undefined
185640 | 29225 | 9965 |  |  | 2013-04-27 13:18 | 2013-04-27 13:18 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188751 | 29380 | 9965 |  |  | 2013-04-27 01:18 | 2013-04-27 01:18 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188752 | 29381 | 9966 |  |  | 2013-04-27 02:46 | 2013-04-27 02:47 | 1 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188753 | 29382 | 9967 |  |  | 2013-04-27 09:05 | 2013-04-27 11:05 | 120 | E0644 | ST 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188754 | 29383 | 9968 |  |  | 2013-04-27 12:58 | 2013-04-27 12:58 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188755 | 29384 | 9969 |  |  | 2013-04-27 14:38 | 2013-04-27 14:39 | 1 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188756 | 29385 | 9970 |  |  | 2013-04-27 14:56 | 2013-04-27 14:57 | 1 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188757 | 29386 | 9971 |  |  | 2013-04-27 15:39 | 2013-04-27 15:39 | 0 | E0017 | BW 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188758 | 29387 | 9972 |  |  | 2013-04-27 18:04 | 2013-04-27 18:04 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188759 | 29388 | 9973 |  |  | 2013-04-27 18:09 | 2013-04-27 18:09 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188760 | 29389 | 9974 |  |  | 2013-04-27 18:17 | 2013-04-27 18:17 | 0 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188761 | 29390 | 9975 |  |  | 2013-04-27 18:18 | 2013-04-27 18:18 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188762 | 29391 | 9976 |  |  | 2013-04-27 18:47 | 2013-04-27 18:47 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188763 | 29392 | 9977 |  |  | 2013-04-27 19:22 | 2013-04-27 21:50 | 148 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188764 | 29393 | 9978 |  |  | 2013-04-27 21:52 | 2013-04-27 21:52 | 0 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188765 | 29394 | 9979 |  |  | 2013-04-27 22:18 | 2013-04-27 22:18 | 0 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188766 | 29395 | 9980 |  |  | 2013-04-27 23:18 | 2013-04-27 23:18 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188767 | 29396 | 9981 |  |  | 2013-04-27 23:06 | 2013-04-27 23:27 | 21 | E0820 | RA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188768 | 29397 | 9982 |  |  | 2013-04-27 23:12 | 2013-04-27 23:28 | 16 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188769 | 29398 | 9983 |  |  | 2013-04-27 21:39 | 2013-04-27 23:52 | 133 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188770 | 29399 | 9984 |  |  | 2013-04-28 00:07 | 2013-04-28 00:28 | 21 | E0494 | GT 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188771 | 29400 | 9985 |  |  | 2013-04-28 00:57 | 2013-04-28 00:58 | 1 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188772 | 29401 | 9986 |  |  | 2013-04-28 01:22 | 2013-04-28 01:22 | 0 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188773 | 29402 | 9987 |  |  | 2013-04-28 02:54 | 2013-04-28 02:54 | 0 | E1042 | SD 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188774 | 29403 | 9988 |  |  | 2013-04-28 07:16 | 2013-04-28 07:35 | 19 | E0366 | KI 11 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188775 | 29404 | 9958 |  |  | 2013-04-25 12:25 | 2013-04-25 12:25 | 0 | E0200 | SO 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189021 | 29405 | 9989 |  |  | 2013-04-28 19:31 | 2013-04-28 19:32 | 1 | E1531 | MY 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188939 | 29406 | 9990 |  |  | 2013-04-28 23:30 | 2013-04-28 23:31 | 1 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188940 | 29407 | 9991 |  |  | 2013-04-29 16:12 | 2013-04-29 16:12 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188941 | 29408 | 9992 |  |  | 2013-05-29 18:14 | 2013-05-29 18:33 | 19 | E0300 | AV 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188942 | 29409 | 9993 |  |  | 2013-05-30 02:10 | 2013-05-30 02:10 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188943 | 29410 | 9994 |  |  | 2013-05-30 09:07 | 2013-05-30 09:07 | 0 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188944 | 29411 | 9995 |  |  | 2013-05-30 22:22 | 2013-05-30 23:19 | 57 | E1531 | MY 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188945 | 29412 | 9996 |  |  | 2013-05-30 23:51 | 2013-05-30 23:51 | 0 | E1042 | SD 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188946 | 29413 | 9997 |  |  | 2013-05-01 03:12 | 2013-05-01 05:50 | 158 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188947 | 29414 | 9998 |  |  | 2013-05-01 21:53 | 2013-05-01 21:54 | 1 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188948 | 29415 | 9999 |  |  | 2013-05-02 08:46 | 2013-05-02 21:04 | 738 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188949 | 29416 | 10000 |  |  | 2013-05-03 11:03 | 2013-05-03 12:13 | 70 | E0075 | CR 33 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188950 | 29417 | 10001 |  |  | 2013-05-03 12:37 | 2013-05-03 12:37 | 0 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188951 | 29418 | 10002 |  |  | 2013-05-03 22:32 | 2013-05-03 23:49 | 77 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
188952 | 29419 | 10003 |  |  | 2013-05-04 11:03 | 2013-05-04 11:03 | 0 | E0300 | AV 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189080 | 29420 | 1918 |  |  | 2013-04-27 13:58 | 2013-04-28 12:22 | 1344 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Fault | Mechanical Failure | Transend | Completed | TRUE | 538 | TRUE |  | IR1300 LF-SO-TB 110 kV transmission line circuit tripped due to broken conductor at a time of severe winds | FALSE | Non-Critical
188953 | 29421 | 1919 |  |  | 2013-05-01 03:47 | 2013-05-01 06:40 | 173 | E0407 | DB 110/22 kV T1 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 18 | TRUE |  | IR1301 Derwent Bridge 110/22 kV T1 transformer circuit tripped following a feeder fault due to a protection grading issue. | FALSE | Non-Critical
188955 | 29422 | 1920 |  |  | 2013-05-09 16:33 | 2013-05-09 17:11 | 38 | E0793 | QT 110/22 kV T1 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR1302 Queenstown 110 kV A Bus tripped due to incorrect protection settings at QT after an inter-trip caused by incorrect isolation for planned work at Newton. | FALSE | Non-Critical
188956 | 29422 | 1920 |  |  | 2013-05-09 16:33 | 2013-05-09 16:33 | 0 | E0794 | QT 110/22 kV T2 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR1302 Queenstown 110 kV A Bus tripped due to incorrect protection settings at QT after an inter-trip caused by incorrect isolation for planned work at Newton. | FALSE | Non-Critical
188957 | 29422 | 1920 |  |  | 2013-05-09 16:33 | 2013-05-09 16:33 | 0 | E0795 | QT 110/11 kV T3 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR1302 Queenstown 110 kV A Bus tripped due to incorrect protection settings at QT after an inter-trip caused by incorrect isolation for planned work at Newton. | FALSE | Non-Critical
188958 | 29422 | 1920 |  |  | 2013-05-09 16:33 | 2013-05-09 17:14 | 41 | E0796 | QT 110/11 kV T4 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR1302 Queenstown 110 kV A Bus tripped due to incorrect protection settings at QT after an inter-trip caused by incorrect isolation for planned work at Newton. | FALSE | Non-Critical
188954 | 29422 | 1920 |  |  | 2013-05-09 16:33 | 2013-05-09 17:10 | 37 | E0792 | QT 110 kV Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 464 | TRUE |  | IR1302 Queenstown 110 kV A Bus tripped due to incorrect protection settings at QT after an inter-trip caused by incorrect isolation for planned work at Newton. | FALSE | Undefined
188959 | 29423 | 1921 |  |  | 2013-05-11 10:16 | 2013-05-11 11:39 | 83 | E1734 | GT-TV 3 220 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1303 GT-TV 220 kV transmission line circuit tripped following an intertrip from the generator. | FALSE | Undefined
189276 | 29424 | 1922 |  |  | 2013-05-22 11:16 | 2013-05-22 11:33 | 17 | E0234 | RI 11 kV E3 Feeder Circuit | Feeder | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 262 | TRUE |  | IR1304 Risdon E352 feeder tripped due to error during planned work on SCADA. The consequent overload of customer plant caused a loss of supply. | FALSE | Undefined
202596 | 29448 | 1923 |  |  | 2013-05-24 16:11 | 2013-05-28 16:22 | 5771 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Intertrip | Basslink | Completed | TRUE | 0 | TRUE |  | IR1305 GT-GC 220 kV transmission line circuit tripped due to fault on Basslink, with FCSPS tripping Gordon and John Butters generation. | FALSE | Undefined
189001 | 29449 | 1925 |  |  | 2013-05-31 10:51 | 2013-05-31 11:13 | 22 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Intertrip | Basslink | Completed | TRUE | 0 | TRUE |  | IR1307 GT-GC 220 kV transmission line circuit tripped due to interrtrip from Basslink. | FALSE | Undefined
190755 | 29450 | 1926 |  |  | 2013-06-03 01:11 | 2013-06-03 11:17 | 606 | E1927 | MR-DE 110 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1308 MR-DE 110 kV transmission line circuit tripped following .................. generator dropped 4 MW | FALSE | Undefined
189524 | 29478 | 10006 |  |  | 2013-05-07 17:26 | 2013-05-07 17:26 | 0 | E0823 | RA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189525 | 29479 | 10007 |  |  | 2013-05-07 20:36 | 2013-05-07 20:36 | 0 | E0654 | SM 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189526 | 29480 | 10008 |  |  | 2013-05-10 09:43 | 2013-05-10 21:44 | 721 | E0823 | RA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189527 | 29481 | 10010 |  |  | 2013-05-12 22:56 | 2013-05-12 23:17 | 21 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189528 | 29482 | 10011 |  |  | 2013-05-13 20:33 | 2013-05-13 20:33 | 0 | E1000 | BU 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189529 | 29483 | 10012 |  |  | 2013-05-14 14:17 | 2013-05-14 14:44 | 27 | E1530 | MY 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189530 | 29484 | 10014 |  |  | 2013-05-14 21:35 | 2013-05-15 01:01 | 206 | E1535 | MY 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189531 | 29485 | 10015 |  |  | 2013-05-15 21:01 | 2013-05-15 21:01 | 0 | E0823 | RA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189532 | 29486 | 10016 |  |  | 2013-05-16 02:29 | 2013-05-16 02:29 | 0 | E1886 | SL 22 kV D2 Feeder | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
189533 | 29487 | 10017 |  |  | 2013-05-16 20:20 | 2013-05-16 20:20 | 0 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189534 | 29488 | 10018 |  |  | 2013-05-16 22:47 | 2013-05-16 22:47 | 0 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189535 | 29489 | 10019 |  |  | 2013-05-17 00:07 | 2013-05-17 00:18 | 11 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189536 | 29490 | 10020 |  |  | 2013-05-17 13:39 | 2013-05-17 13:57 | 18 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189537 | 29491 | 10021 |  |  | 2013-05-18 14:51 | 2013-05-18 14:51 | 0 | E0898 | SD 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189538 | 29492 | 10022 |  |  | 2013-05-20 11:25 | 2013-05-20 11:25 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189539 | 29493 | 10023 |  |  | 2013-05-21 13:38 | 2013-05-21 13:38 | 0 | E0825 | RA 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
190518 | 29494 | 10024 |  |  | 2013-05-24 03:39 | 2013-05-24 04:45 | 66 | E0644 | ST 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189541 | 29495 | 10025 |  |  | 2013-05-25 08:36 | 2013-05-25 08:36 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189542 | 29496 | 10026 |  |  | 2013-05-25 08:44 | 2013-05-25 08:44 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189543 | 29497 | 10027 |  |  | 2013-05-25 09:01 | 2013-05-25 09:01 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189544 | 29498 | 10028 |  |  | 2013-05-25 09:05 | 2013-05-25 09:05 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189545 | 29499 | 10029 |  |  | 2013-05-25 13:17 | 2013-05-25 13:17 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189546 | 29500 | 10030 |  |  | 2013-05-25 13:48 | 2013-05-25 13:48 | 0 | E1662 | EL 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189547 | 29501 | 10031 |  |  | 2013-05-25 16:38 | 2013-05-25 17:01 | 23 | E0014 | BW 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189548 | 29502 | 10032 |  |  | 2013-05-26 07:08 | 2013-05-26 07:25 | 17 | E1505 | TB 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
189549 | 29503 | 10034 |  |  | 2013-05-26 18:49 | 2013-05-26 20:03 | 74 | E0644 | ST 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
190441 | 29624 | 1927 |  |  | 2013-06-04 10:02 | 2013-06-04 10:34 | 32 | E0404 | SH-BU 2 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1329 SH-BU 2 110 kV transmission circuit tripped dueunknown cause. | FALSE | Non-Critical
190480 | 29626 | 1929 |  |  | 2013-06-12 14:54 | 2013-06-13 12:38 | 1304 | E0406 | FA-QU-SR-HM 110 kV Transmission Circuit | Transmission | Fault | Insulation Failure | Transend | Completed | TRUE | 26638 | TRUE |  | IR1334 FA-QU-SR-HM 110 kV transmission circuit tripped due to failed insulator. | FALSE | Non-Critical
190482 | 29644 | 1931 |  |  | 2013-06-28 12:14 | 2013-06-28 12:14 | 0 | E0402 | BU-ST 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1336 BU-ST 110 kV transmission circuit tripped and reclosed due to unknown cause | FALSE | Non-Critical
190665 | 29645 | 10036 |  |  | 2013-05-28 06:40 | 2013-05-28 06:41 | 1 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
190666 | 29646 | 10037 |  |  | 2013-05-28 16:29 | 2013-05-28 16:29 | 0 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
190667 | 29647 | 10038 |  |  | 2013-05-29 14:43 | 2013-05-29 14:43 | 0 | E0869 | RB 44 kV E4 Circuit Breaker | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
190669 | 29649 | 10043 |  |  | 2013-06-03 13:57 | 2013-06-03 15:16 | 79 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191377 | 29650 | 10044 |  |  | 2013-06-03 16:35 | 2013-06-03 16:36 | 1 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
190671 | 29651 | 10045 |  |  | 2013-06-03 16:58 | 2013-06-03 16:59 | 1 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
190672 | 29652 | 10046 |  |  | 2013-06-03 17:23 | 2013-06-03 17:23 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
190673 | 29653 | 10047 |  |  | 2013-06-03 18:06 | 2013-06-03 18:08 | 2 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191018 | 29669 | 1933 |  |  | 2013-07-04 22:25 | 2013-07-04 22:25 | 0 | E0587 | UL-EB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1339 UL-EB 110 kV transmission line circuit tripped with lightning in area. | FALSE | Non-Critical
191378 | 29670 | 10048 |  |  | 2013-06-07 08:58 | 2013-06-07 11:44 | 166 | E0943 | UL 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191379 | 29671 | 10049 |  |  | 2013-06-07 16:12 | 2013-06-07 16:34 | 22 | E0943 | UL 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191380 | 29672 | 10048 |  |  | 2013-06-07 08:58 | 2013-06-07 11:44 | 166 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191381 | 29673 | 10049 |  |  | 2013-06-07 16:12 | 2013-06-07 16:33 | 21 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191382 | 29674 | 10050 |  |  | 2013-06-07 16:34 | 2013-06-07 17:07 | 33 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191383 | 29675 | 10051 |  |  | 2013-06-08 04:58 | 2013-06-08 05:30 | 32 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191384 | 29676 | 10052 |  |  | 2013-06-08 06:45 | 2013-06-08 06:45 | 0 | E0639 | ST 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191385 | 29677 | 10055 |  |  | 2013-06-11 15:25 | 2013-06-11 15:32 | 7 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191386 | 29678 | 10056 |  |  | 2013-06-11 15:25 | 2013-06-11 15:46 | 21 | E0387 | BU 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191387 | 29679 | 10057 |  |  | 2013-06-11 18:23 | 2013-06-11 18:24 | 1 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191388 | 29680 | 10058 |  |  | 2013-06-13 03:27 | 2013-06-13 15:44 | 737 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191389 | 29681 | 10059 |  |  | 2013-06-13 19:40 | 2013-06-13 20:01 | 21 | E1560 | HA 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191390 | 29682 | 10060 |  |  | 2013-06-15 12:58 | 2013-06-15 12:58 | 0 | E1826 | TU 22kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
191391 | 29683 | 10061 |  |  | 2013-06-17 09:37 | 2013-06-17 09:57 | 20 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191392 | 29684 | 10062 |  |  | 2013-06-22 22:17 | 2013-06-22 22:17 | 0 | E1659 | EL 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191393 | 29685 | 10063 |  |  | 2013-06-24 05:45 | 2013-06-24 06:10 | 25 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191394 | 29686 | 10064 |  |  | 2013-06-26 10:12 | 2013-06-26 10:12 | 0 | E1504 | TB 22 KV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191395 | 29687 | 10066 |  |  | 2013-06-30 15:44 | 2013-06-30 19:56 | 252 | E1560 | HA 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
192035 | 29688 | 10068 |  |  | 2013-07-01 10:53 | 2013-07-01 11:17 | 24 | E1557 | CR 33 kV Z2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191396 | 29690 | 10054 |  |  | 2013-06-08 07:39 | 2013-06-08 07:40 | 1 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191397 | 29719 | 1924 |  |  | 2013-05-28 09:05 | 2013-05-28 09:08 | 3 | E0314 | BY 6.6 kV 9DE Bus Coupler Circuit | Bus Coupler | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1306 Boyer 952DE circuit breaker tripped by on site personnel. | FALSE | Undefined
191469 | 29720 | 1917 |  |  | 2013-04-23 07:27 | 2013-04-23 07:32 | 5 | E0878 | SR 110/22 kV T3 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1299 Savage River T3 tripped due to error during planned work. | FALSE | Non-Critical
191088 | 29721 | 10069 |  |  | 2013-07-01 12:09 | 2013-07-01 12:43 | 34 | E1557 | CR 33 kV Z2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191089 | 29722 | 10070 |  |  | 2013-07-01 12:35 | 2013-07-01 13:04 | 29 | E1482 | RI 33 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191090 | 29723 | 10071 |  |  | 2013-07-01 12:35 | 2013-07-01 14:13 | 98 | E1479 | RI 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191091 | 29724 | 10073 |  |  | 2013-07-01 11:39 | 2013-07-01 20:05 | 506 | E1480 | RI 33 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191092 | 29725 | 10074 |  |  | 2013-07-02 14:44 | 2013-07-02 17:47 | 183 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191093 | 29726 | 10075 |  |  | 2013-07-04 07:10 | 2013-07-04 07:10 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191094 | 29727 | 10076 |  |  | 2013-07-04 23:45 | 2013-07-05 00:19 | 34 | E1530 | MY 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191095 | 29728 | 10077 |  |  | 2013-07-05 00:47 | 2013-07-05 00:47 | 0 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191096 | 29729 | 10078 |  |  | 2013-07-05 12:25 | 2013-07-05 12:26 | 1 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191097 | 29730 | 10079 |  |  | 2013-07-05 21:17 | 2013-07-05 22:07 | 50 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191098 | 29731 | 10083 |  |  | 2013-07-06 08:55 | 2013-07-06 10:24 | 89 | E0360 | KI 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191099 | 29732 | 10081 |  |  | 2013-07-05 22:44 | 2013-07-06 13:12 | 868 | E1827 | TU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
191100 | 29733 | 10084 |  |  | 2013-07-06 20:27 | 2013-07-06 20:27 | 0 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191102 | 29735 | 10086 |  |  | 2013-07-09 00:40 | 2013-07-09 00:40 | 0 | E1393 | SD 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191103 | 29736 | 10087 |  |  | 2013-07-11 16:38 | 2013-07-14 15:08 | 4230 | E0110 | CS 11 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191104 | 29737 | 10088 |  |  | 2013-07-14 15:04 | 2013-07-14 15:23 | 19 | E0303 | AV 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191105 | 29739 | 10089 |  |  | 2013-07-15 04:48 | 2013-07-15 04:49 | 1 | E0389 | BU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191106 | 29740 | 10090 |  |  | 2013-07-15 04:50 | 2013-07-15 17:58 | 788 | E0389 | BU 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191107 | 29741 | 10091 |  |  | 2013-07-15 09:54 | 2013-07-15 09:54 | 0 | E1550 | DP 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191189 | 29770 | 10082 |  |  | 2013-07-06 04:47 | 2013-07-06 04:47 | 0 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191190 | 29771 | 10092 |  |  | 2013-07-16 11:34 | 2013-07-16 12:15 | 41 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191199 | 29772 | 1932 |  |  | 2013-07-04 15:09 | 2013-07-05 11:32 | 1223 | E0382 | BU 110/22 kV T6 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1338 Burnie T6 transformer circuit tripped during planned work due to a cut cable. | FALSE | Non-Critical
191212 | 29773 | 10093 |  |  | 2013-07-21 07:54 | 2013-07-21 19:36 | 702 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191213 | 29774 | 10094 |  |  | 2013-07-21 07:54 | 2013-07-21 16:43 | 529 | E0083 | CR 33 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
191407 | 29847 | 1934 |  |  | 2013-07-09 15:08 | 2013-07-09 15:35 | 27 | E0138 | TA-NN 1 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1340 TA-NN 1 110 kV transmission circuit tripped, suspect testing error. | FALSE | Critical
192428 | 29848 | 1935 |  |  | 2013-07-16 12:50 | 2013-07-16 15:36 | 166 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Fault | Intertrip | Transend | Completed | TRUE | 1 | TRUE |  | IR1341 Arthurs Lake T1 transformer tripped due to intertrip from Hydro at pump start. fault oput against feeder as T1 out of service at the time | FALSE | Undefined
194841 | 29849 | 1938 |  |  | 2013-07-16 18:31 | 2013-09-01 12:00 | 67289 | E1788 | MT 33 kV D2 Station Service Transformer | Station Service Transformer | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR1342 Mornington 33kV D252 tripped due to equipment failure, with smoke causing forced outage of 33 kV A and B buses. 33kV B Bus energised at 1941. Howrah Zone energised at 1952. Cambridge Zone backfed by Aurora at 1958. Fire Brigade have left site. | FALSE | Not in WASP
191409 | 29849 | 1938 |  |  | 2013-07-16 19:11 | 2013-07-17 14:29 | 1158 | E1782 | MT 33 kV A Bus | Bus | Fault | Internal Fault | Transend | Completed | TRUE | 535 | TRUE |  | IR1342 Mornington 33kV D252 tripped due to equipment failure, with smoke causing forced outage of 33 kV A and B buses. 33kV B Bus energised at 1941. Howrah Zone energised at 1952. Cambridge Zone backfed by Aurora at 1958. Fire Brigade have left site. | FALSE | Not in WASP
191410 | 29849 | 1938 |  |  | 2013-07-16 19:11 | 2013-07-16 19:41 | 30 | E1783 | MT 33 kV B Bus | Bus | Fault | Internal Fault | Transend | Completed | TRUE | 0 | TRUE |  | IR1342 Mornington 33kV D252 tripped due to equipment failure, with smoke causing forced outage of 33 kV A and B buses. 33kV B Bus energised at 1941. Howrah Zone energised at 1952. Cambridge Zone backfed by Aurora at 1958. Fire Brigade have left site. | FALSE | Not in WASP
191411 | 29850 | 1939 |  |  | 2013-07-19 01:50 | 2013-07-19 02:34 | 44 | E0540 | SH-FI 220 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1343 SH-FI 220 kV transmission circuit tripped with lightning in area. Fisher generation lost 43 MW | FALSE | Non-Critical
191597 | 29851 | 1940 |  |  | 2013-07-29 11:19 | 2013-07-29 11:35 | 16 | E1769 | MT 110 kV A Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR Mornington 110 kV A Bus tripped on Bucholz following during planned work on oil sampling pipework. Summary of Events: Contractors were on site undertaking work on transformer oil sampling pipework and the OLTC oil flow trip has been generated opening off the two breakers connecting supply transformer T1 A152 and A752. Bucholz trip appears to be linked to work being undertaken on transformer oil sampling pipework onPROMS 123290.Suspected Cause of Outage: Failure to isolate trip circuits of Buchholz relay of out of service transformer that does not have a dedicated EHV breaker. | FALSE | Not in WASP
193357 | 30086 | 10095 |  |  | 2013-07-22 21:42 | 2013-07-22 22:09 | 27 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193400 | 30087 | 10096 |  |  | 2013-07-26 03:14 | 2013-07-26 03:14 | 0 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193401 | 30088 | 10097 |  |  | 2013-07-29 18:42 | 2013-07-29 19:06 | 24 | E1504 | TB 22 KV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193402 | 30089 | 10098 |  |  | 2013-07-31 09:48 | 2013-07-31 09:48 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193403 | 30090 | 10099 |  |  | 2013-07-31 09:39 | 2013-07-31 10:30 | 51 | E0084 | CR 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193404 | 30091 | 10100 |  |  | 2013-08-02 18:05 | 2013-08-02 18:43 | 38 | E0737 | NH 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193405 | 30092 | 10101 |  |  | 2013-08-03 13:10 | 2013-08-03 14:22 | 72 | E0737 | NH 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193406 | 30093 | 10102 |  |  | 2013-08-04 01:43 | 2013-08-04 01:43 | 0 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193407 | 30094 | 10103 |  |  | 2013-08-04 01:46 | 2013-08-04 01:46 | 0 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193408 | 30095 | 10104 |  |  | 2013-08-04 00:06 | 2013-08-04 05:47 | 341 | E0357 | KI 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193409 | 30096 | 10105 |  |  | 2013-08-05 06:47 | 2013-08-05 06:47 | 0 | E0464 | KR 11 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193410 | 30097 | 10106 |  |  | 2013-08-05 20:00 | 2013-08-05 20:00 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193411 | 30098 | 10107 |  |  | 2013-08-05 20:02 | 2013-08-05 20:02 | 0 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193412 | 30099 | 10108 |  |  | 2013-08-05 22:05 | 2013-08-05 22:05 | 0 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193413 | 30100 | 10109 |  |  | 2013-08-07 14:38 | 2013-08-07 14:38 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193414 | 30101 | 10110 |  |  | 2013-08-07 14:38 | 2013-08-07 14:38 | 0 | E0906 | TR 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193415 | 30102 | 10111 |  |  | 2013-08-09 15:37 | 2013-08-09 15:37 | 0 | E1548 | DP 22 kV C2 Capacitor Circuit | Capacitor | Fault |  | DNSP | Completed | FALSE | 0 | TRUE |  |  | FALSE | Undefined
193416 | 30103 | 10112 |  |  | 2013-08-10 04:09 | 2013-08-10 18:27 | 858 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193417 | 30104 | 10113 |  |  | 2013-08-10 07:05 | 2013-08-10 07:24 | 19 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193418 | 30105 | 10114 |  |  | 2013-08-10 10:29 | 2013-08-10 10:47 | 18 | E0888 | DE 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193419 | 30106 | 10115 |  |  | 2013-08-10 12:08 | 2013-08-10 12:24 | 16 | E1893 | SL 22 kV J2 Feeder | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
193420 | 30107 | 10116 |  |  | 2013-08-10 14:22 | 2013-08-10 16:21 | 119 | E0366 | KI 11 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193421 | 30108 | 10117 |  |  | 2013-08-10 16:27 | 2013-08-10 16:29 | 2 | E0366 | KI 11 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193422 | 30109 | 10118 |  |  | 2013-08-10 16:34 | 2013-08-10 16:35 | 1 | E0366 | KI 11 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193423 | 30110 | 10119 |  |  | 2013-08-12 03:42 | 2013-08-12 03:42 | 0 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193424 | 30111 | 10122 |  |  | 2013-08-12 07:36 | 2013-08-12 19:37 | 721 | E0888 | DE 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193425 | 30112 | 10121 |  |  | 2013-08-12 04:45 | 2013-08-12 14:25 | 580 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
193591 | 30113 | 10120 |  |  | 2013-08-12 03:47 | 2013-08-12 04:05 | 18 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
194761 | 30274 | 1942 |  |  | 2013-08-05 19:51 | 2013-08-05 20:07 | 16 | E0407 | DB 110/22 kV T1 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 2 | TRUE |  | IR22 Derwent Bridge T1 transformer circuit tripped due to a protection grading issue following a feeder fault. | FALSE | Non-Critical
195009 | 30275 | 1944 |  |  | 2013-08-18 21:33 | 2013-08-18 22:32 | 59 | E1927 | MR-DE 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Generator Request | Completed | TRUE | 0 | TRUE |  | IR? DE-MR 110 kV transmission circuit tripped with lightning in area. | FALSE | Undefined
194763 | 30276 | 1945 |  |  | 2013-08-18 22:40 | 2013-08-19 05:43 | 423 | E0794 | QT 110/22 kV T2 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR25 Queenstown 110/22 kV transformer T2 circuit tripped with lightning in area. | FALSE | Non-Critical
194764 | 30277 | 1946 |  |  | 2013-08-19 01:36 | 2013-08-19 03:20 | 104 | E0721 | QT-NT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 527 | TRUE |  | IR26 QT-NT 110 kV transmission circuit tripped with lightning in area. | FALSE | Non-Critical
195010 | 30308 | 1948 |  |  | 2013-08-19 07:40 | 2013-08-19 09:50 | 130 | E1565 | BP-SB-ST 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Generator Request | Completed | TRUE | 0 | TRUE |  | IR? BP-SB-ST 110 kV transmission circuit tripped with lightning in area. Woolnorth dropped 106 MW generation. | FALSE | Undefined
194843 | 30310 | 1950 |  |  | 2013-08-30 14:31 | 2013-08-30 14:41 | 10 | E1734 | GT-TV 3 220 kV Transmission Circuit | Transmission | Fault | Generator | Generator Request | Completed | TRUE | 0 | TRUE |  | IR? GT-TV 3 220 kV transmission circuit tripped, suspect incorrect switching by AETV. | FALSE | Undefined
194844 | 30311 | 1951 |  |  | 2013-08-30 15:59 | 2013-08-30 16:14 | 15 | E0290 | PO-PM 2 110 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1398 PO-PM 2 110 kV transmission circuit tripped due to an intertrip during Hydro commissioning of Poatina T2. | FALSE | Non-Critical
206858 | 30312 | 1943 |  |  | 2013-08-15 11:40 | 2013-08-15 11:40 | 0 | E1621 | RI 110 kV Bus SPS | Bus | Fault | Intertrip | Basslink | Completed | TRUE | 0 | TRUE |  | IR23 Loss of Basslink signal received and FCSPS operated. | FALSE | Undefined
195691 | 30314 | 1949 |  |  | 2013-08-20 06:49 | 2013-08-20 06:53 | 4 | E0407 | DB 110/22 kV T1 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 1 | TRUE |  | IR30 DB T1 transformer circuit tripped following a feeder fault due to SEF protection being out of service. | FALSE | Non-Critical
195918 | 30315 | 10123 |  |  | 2013-08-13 15:36 | 2013-08-13 16:42 | 66 | E1825 | TU 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
195919 | 30316 | 10124 |  |  | 2013-08-13 17:43 | 2013-08-13 17:44 | 1 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195920 | 30317 | 10125 |  |  | 2013-08-13 19:37 | 2013-08-13 19:37 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195921 | 30318 | 10126 |  |  | 2013-08-13 17:19 | 2013-08-13 20:28 | 189 | E0725 | NT 22 kV A2X Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195922 | 30319 | 10127 |  |  | 2013-08-13 20:35 | 2013-08-13 20:35 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195923 | 30320 | 10128 |  |  | 2013-08-13 20:35 | 2013-08-13 20:35 | 0 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
197885 | 30321 | 10129 |  |  | 2013-08-13 22:57 | 2013-08-13 23:19 | 22 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195925 | 30322 | 10130 |  |  | 2013-08-14 13:04 | 2013-08-14 13:04 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195926 | 30323 | 10131 |  |  | 2013-08-17 22:21 | 2013-08-17 22:22 | 1 | E1555 | DP 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195927 | 30324 | 10132 |  |  | 2013-08-18 03:08 | 2013-08-18 04:31 | 83 | E1393 | SD 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195928 | 30325 | 10133 |  |  | 2013-08-18 05:52 | 2013-08-18 05:52 | 0 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
195929 | 30326 | 10134 |  |  | 2013-08-18 06:33 | 2013-08-18 06:33 | 0 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196164 | 30327 | 10135 |  |  | 2013-08-18 06:45 | 2013-08-18 08:42 | 117 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196165 | 30328 | 10136 |  |  | 2013-08-18 17:21 | 2013-08-18 17:21 | 0 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196166 | 30329 | 10137 |  |  | 2013-08-18 20:42 | 2013-08-18 20:42 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196167 | 30330 | 10138 |  |  | 2013-08-18 20:42 | 2013-08-18 21:34 | 52 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196168 | 30331 | 10139 |  |  | 2013-08-18 23:11 | 2013-08-18 23:11 | 0 | E0761 | NW 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196169 | 30332 | 10140 |  |  | 2013-08-18 23:16 | 2013-08-18 23:16 | 0 | E1051 | SR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196170 | 30333 | 10141 |  |  | 2013-08-18 20:12 | 2013-08-18 23:36 | 204 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196171 | 30334 | 10142 |  |  | 2013-08-19 00:15 | 2013-08-19 00:51 | 36 | E0084 | CR 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196172 | 30335 | 10143 |  |  | 2013-08-19 01:48 | 2013-08-19 02:10 | 22 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196173 | 30336 | 10144 |  |  | 2013-08-19 10:43 | 2013-08-19 11:10 | 27 | E1557 | CR 33 kV Z2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196174 | 30337 | 10145 |  |  | 2013-08-19 14:37 | 2013-08-19 15:54 | 77 | E1003 | BU 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196175 | 30338 | 10146 |  |  | 2013-08-19 22:46 | 2013-08-19 22:46 | 0 | E1042 | SD 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196176 | 30339 | 10147 |  |  | 2013-08-20 07:19 | 2013-08-20 13:07 | 348 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196177 | 30340 | 10148 |  |  | 2013-08-27 18:36 | 2013-08-27 18:36 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196178 | 30341 | 10149 |  |  | 2013-08-27 15:40 | 2013-08-27 17:27 | 107 | E0122 | CS 11 kV X2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196179 | 30342 | 10150 |  |  | 2013-08-27 18:10 | 2013-08-27 18:11 | 1 | E0365 | KI 11 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196180 | 30343 | 10151 |  |  | 2013-08-29 20:27 | 2013-08-29 20:27 | 0 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196181 | 30344 | 10152 |  |  | 2013-08-30 01:10 | 2013-08-30 01:10 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196182 | 30345 | 10153 |  |  | 2013-08-31 08:15 | 2013-08-31 08:46 | 31 | E0078 | CR 33 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196683 | 30417 | 10156 |  |  | 2013-09-06 16:57 | 2013-09-06 16:57 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196684 | 30418 | 10157 |  |  | 2013-09-06 16:57 | 2013-09-06 16:57 | 0 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196685 | 30419 | 10158 |  |  | 2013-09-07 17:03 | 2013-09-07 17:04 | 1 | E0907 | TR 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
196686 | 30420 | 10161 |  |  | 2013-09-11 20:28 | 2013-09-11 20:29 | 1 | E0819 | RA 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
197784 | 30466 | 1957 |  |  | 2013-09-30 21:28 | 2013-09-30 21:28 | 0 | E0406 | FA-QU-SR-HM 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1448 FA-QU-SR-HM 110 kV transmission circuit tripped and autoreclosed due to lightning. | FALSE | Non-Critical
197786 | 30467 | 1956 |  |  | 2013-09-24 16:33 | 2013-09-24 16:54 | 21 | E0792 | QT 110 kV Bus | Bus | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1430 RB T1 and FA-RB-QT 110 kV circuits tripped following a human error during planned maintenance work, with loss of supply at Rosebery, Queenstown and Newton. | FALSE | Undefined
197785 | 30467 | 1956 |  |  | 2013-09-24 16:33 | 2013-09-24 16:57 | 24 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 925 | TRUE |  | IR1430 RB T1 and FA-RB-QT 110 kV circuits tripped following a human error during planned maintenance work, with loss of supply at Rosebery, Queenstown and Newton. | FALSE | Non-Critical
197787 | 30467 | 1956 |  |  | 2013-09-24 16:33 | 2013-09-24 16:52 | 19 | E0856 | RB 110/44 kV T1 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1430 RB T1 and FA-RB-QT 110 kV circuits tripped following a human error during planned maintenance work, with loss of supply at Rosebery, Queenstown and Newton. | FALSE | Non-Critical
197788 | 30468 | 1955 |  |  | 2013-09-24 12:24 | 2013-09-24 12:24 | 0 | E0025 | NN-CS 110 kV Transmission Circuit | Transmission | Fault | Wildlife | Transend | Completed | TRUE | 0 | TRUE |  | IR1419 NN-CS 110 kV transmission circuit tripped and reclosed. | FALSE | Critical
197789 | 30469 | 1954 |  |  | 2013-09-12 08:31 | 2013-09-12 08:31 | 0 | E0439 | HA-NW 1 110 kV Transmission Circuit | Transmission | Fault | Insulation Failure | Transend | Completed | TRUE | 0 | TRUE |  | IR1409 HA-NW 1 110 kV transmission circuit tripped and reclosed due to insulator flashover. Norwood 110 kV bus tripped concurrently due to ptotection error. | FALSE | Non-Critical
197790 | 30471 | 1954 |  |  | 2013-09-12 08:31 | 2013-09-12 09:20 | 49 | E0424 | HA 110 kV B Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR1409 Hadspen 110 kV B Bus tripped due to a protection error following a HA-NW 1 110 kV transmission circuit trip and reclose | FALSE | Undefined
197791 | 30471 | 1954 |  |  | 2013-09-12 08:31 | 2013-09-12 09:20 | 49 | E1424 | HA 110/22 kV T4 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR1409 Hadspen 110 kV B Bus tripped due to a protection error following a HA-NW 1 110 kV transmission circuit trip and reclose | FALSE | Non-Critical
198689 | 30508 | 10162 |  |  | 2013-09-14 23:31 | 2013-09-15 00:21 | 50 | E0909 | TR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198690 | 30509 | 10163 |  |  | 2013-09-16 15:21 | 2013-09-16 15:22 | 1 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198691 | 30510 | 10164 |  |  | 2013-09-18 15:15 | 2013-09-18 15:15 | 0 | E0150 | NN 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198692 | 30511 | 10165 |  |  | 2013-09-19 09:50 | 2013-09-19 10:10 | 20 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198693 | 30512 | 10166 |  |  | 2013-09-20 12:58 | 2013-09-20 16:16 | 198 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198695 | 30514 | 10168 |  |  | 2013-09-22 21:56 | 2013-09-22 23:23 | 87 | E1570 | DP 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198696 | 30515 | 10169 |  |  | 2013-09-23 00:12 | 2013-09-23 00:12 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198697 | 30516 | 10170 |  |  | 2013-09-23 08:53 | 2013-09-23 08:53 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198698 | 30517 | 10172 |  |  | 2013-09-25 06:52 | 2013-09-25 06:52 | 0 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198699 | 30518 | 10173 |  |  | 2013-09-25 09:17 | 2013-09-25 09:56 | 39 | E1557 | CR 33 kV Z2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198700 | 30519 | 10174 |  |  | 2013-09-26 11:51 | 2013-09-26 11:51 | 0 | E0638 | ST 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198701 | 30520 | 10175 |  |  | 2013-09-26 12:24 | 2013-09-26 12:24 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198702 | 30521 | 10176 |  |  | 2013-09-26 13:38 | 2013-09-26 13:38 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198703 | 30522 | 10177 |  |  | 2013-09-26 14:28 | 2013-09-26 19:10 | 282 | E0945 | UL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198704 | 30523 | 10178 |  |  | 2013-09-27 04:42 | 2013-09-27 04:42 | 0 | E1548 | DP 22 kV C2 Capacitor Circuit | Capacitor | Fault |  | DNSP | Completed | FALSE | 0 | TRUE |  |  | FALSE | Undefined
198705 | 30524 | 10179 |  |  | 2013-09-27 20:46 | 2013-09-27 20:46 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198706 | 30525 | 10180 |  |  | 2013-09-30 18:44 | 2013-09-30 18:44 | 0 | E0465 | KR 11 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198707 | 30526 | 10181 |  |  | 2013-10-01 00:15 | 2013-10-01 00:15 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198708 | 30527 | 10182 |  |  | 2013-10-01 00:21 | 2013-10-01 00:22 | 1 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198709 | 30528 | 10183 |  |  | 2013-10-01 00:28 | 2013-10-01 03:00 | 152 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198710 | 30529 | 10184 |  |  | 2013-10-01 03:27 | 2013-10-01 03:27 | 0 | E1550 | DP 22 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198711 | 30530 | 10185 |  |  | 2013-10-01 01:52 | 2013-10-01 03:41 | 109 | E0360 | KI 11 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198712 | 30531 | 10186 |  |  | 2013-10-01 01:52 | 2013-10-01 03:51 | 119 | E0357 | KI 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198713 | 30532 | 10187 |  |  | 2013-10-01 05:54 | 2013-10-01 05:54 | 0 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198714 | 30533 | 10188 |  |  | 2013-10-01 06:07 | 2013-10-01 06:07 | 0 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198715 | 30534 | 10189 |  |  | 2013-10-01 18:39 | 2013-10-01 18:39 | 0 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198788 | 30535 | 10190 |  |  | 2013-10-02 05:42 | 2013-10-02 06:57 | 75 | E1552 | DP 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198789 | 30536 | 10191 |  |  | 2013-10-02 07:30 | 2013-10-02 07:30 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198790 | 30537 | 10192 |  |  | 2013-10-02 07:35 | 2013-10-02 07:50 | 15 | E0366 | KI 11 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198791 | 30538 | 10193 |  |  | 2013-10-02 07:51 | 2013-10-02 07:51 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198792 | 30539 | 10194 |  |  | 2013-10-02 08:37 | 2013-10-02 08:37 | 0 | E1568 | DP 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198793 | 30540 | 10195 |  |  | 2013-10-02 09:21 | 2013-10-02 09:21 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198794 | 30541 | 10196 |  |  | 2013-10-02 09:52 | 2013-10-02 09:52 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198795 | 30542 | 10197 |  |  | 2013-10-02 10:15 | 2013-10-02 10:15 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198796 | 30543 | 10198 |  |  | 2013-10-02 10:42 | 2013-10-02 10:42 | 0 | E0392 | BU 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198797 | 30544 | 10199 |  |  | 2013-10-02 10:47 | 2013-10-02 10:47 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
202443 | 30545 | 10200 |  |  | 2013-10-02 11:08 | 2013-10-02 11:08 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198799 | 30546 | 10201 |  |  | 2013-10-02 10:39 | 2013-10-02 11:10 | 31 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
198800 | 30547 | 10202 |  |  | 2013-10-02 11:12 | 2013-10-02 11:12 | 0 | E1556 | DP 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199185 | 30548 | 10203 |  |  | 2013-10-02 11:21 | 2013-10-02 11:21 | 0 | E0818 | RA 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199186 | 30549 | 10204 |  |  | 2013-10-02 11:17 | 2013-10-02 11:26 | 9 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199187 | 30550 | 10205 |  |  | 2013-10-02 11:28 | 2013-10-02 11:28 | 0 | E0819 | RA 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199188 | 30551 | 10209 |  |  | 2013-10-02 12:44 | 2013-10-02 12:44 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199189 | 30552 | 10210 |  |  | 2013-10-02 13:00 | 2013-10-02 13:00 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199190 | 30553 | 1442 |  |  | 2009-05-06 15:04 | 2009-05-06 15:41 | 37 | E0211 | RI 110/11 kV T2 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR775 Risdon T2 transformer circuit tripped during protection testing due to a construction error | FALSE | Non-Critical
199191 | 30554 | 10211 |  |  | 2013-10-02 13:37 | 2013-10-02 18:16 | 279 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199543 | 30555 | 10212 |  |  | 2013-10-02 11:18 | 2013-10-02 17:35 | 377 | E1613 | UL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199544 | 30556 | 10213 |  |  | 2013-10-02 13:01 | 2013-10-02 17:52 | 291 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199545 | 30557 | 10214 |  |  | 2013-10-02 11:06 | 2013-10-02 18:49 | 463 | E0944 | UL 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199546 | 30558 | 10215 |  |  | 2013-10-02 11:33 | 2013-10-02 19:17 | 464 | E0946 | UL 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199547 | 30559 | 10216 |  |  | 2013-10-02 20:32 | 2013-10-02 20:32 | 0 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199548 | 30560 | 10217 |  |  | 2013-10-02 21:04 | 2013-10-02 22:59 | 115 | E0285 | PM 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199549 | 30561 | 10218 |  |  | 2013-10-02 22:56 | 2013-10-03 01:36 | 160 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199550 | 30562 | 10219 |  |  | 2013-10-03 20:31 | 2013-10-03 20:31 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199551 | 30563 | 10220 |  |  | 2013-10-03 19:58 | 2013-10-04 18:26 | 1348 | E0491 | GT 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199552 | 30564 | 10221 |  |  | 2013-10-04 22:00 | 2013-10-04 22:00 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199553 | 30565 | 10222 |  |  | 2013-10-05 09:43 | 2013-10-05 22:25 | 762 | E1557 | CR 33 kV Z2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199554 | 30566 | 10223 |  |  | 2013-10-06 06:16 | 2013-10-06 06:45 | 29 | E0109 | CS 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199555 | 30567 | 10224 |  |  | 2013-10-06 08:27 | 2013-10-06 08:27 | 0 | E0109 | CS 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199556 | 30568 | 10225 |  |  | 2013-10-06 15:21 | 2013-10-06 16:01 | 40 | E0909 | TR 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199557 | 30569 | 10226 |  |  | 2013-10-13 14:04 | 2013-10-13 14:24 | 20 | E0780 | PL 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199558 | 30570 | 10227 |  |  | 2013-10-15 13:11 | 2013-10-15 13:37 | 26 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
199941 | 30602 | 1961 |  |  | 2013-10-01 00:25 | 2013-10-01 00:38 | 13 | E0715 | FA-JB 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1449 FA-JB 220 kV and FA-RB-QT 110 kV transmission circuits tripped with LOS at Queenstown and Newton, suspect lightning. | FALSE | Non-Critical
204064 | 30602 | 1961 |  |  | 2013-10-01 00:25 | 2013-10-01 00:36 | 11 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 1051 | TRUE |  | IR1449 FA-JB 220 kV and FA-RB-QT 110 kV transmission circuits tripped with LOS at Queenstown and Newton, suspect lightning. | FALSE | Non-Critical
199943 | 30603 | 1959 |  |  | 2013-10-01 03:47 | 2013-10-01 03:59 | 12 | E0169 | TU-BG-DB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1450 TU-BG-DB 110 kV transmission ciruit tripped with lightning in area. | FALSE | Non-Critical
200307 | 30604 | 1960 |  |  | 2013-10-01 03:47 | 2013-10-01 03:54 | 7 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 126 | TRUE |  | IR1451 FA-RB-QT 110 kV transmission circuit tripped due to lightning with LOS at Queenstown. | FALSE | Non-Critical
200308 | 30605 | 1962 |  |  | 2013-10-01 16:39 | 2013-10-01 17:22 | 43 | E0210 | RI 110/11 kV T1 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1452 Risdon 110/11 kV transfiormer circuit tripped due to protection testing error with no loss of supply. | FALSE | Non-Critical
200715 | 30650 | 1964 |  |  | 2013-10-07 10:31 | 2013-10-07 10:31 | 0 | E0291 | PM-SH 220 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1465 PM-SH 220 kV transmission circuit tripped and auto reclosed with unknown cause. | FALSE | Critical
200716 | 30652 | 1965 |  |  | 2013-10-13 12:32 | 2013-10-13 12:42 | 10 | E0401 | BU-PL 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1467 BU-PL 110 kV transmission circuit tripped and Woolnorth runback scheme operated. | FALSE | Non-Critical
200717 | 30653 | 1966 |  |  | 2013-10-15 15:18 | 2013-10-15 15:24 | 6 | E0098 | CS 11 kV B Bus | Bus | Fault | Internal Fault | Transend | Completed | TRUE | 23 | TRUE |  | IR1484 Chapel St 11 kV B Bus tripped during planned work due to an incorrect CB status indication caused by an internal wiring failure. | FALSE | Undefined
201561 | 30655 | 10228 |  |  | 2013-10-16 09:46 | 2013-10-16 11:32 | 106 | E1436 | HA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
201563 | 30657 | 10230 |  |  | 2013-10-16 13:54 | 2013-10-16 13:54 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
201564 | 30658 | 10231 |  |  | 2013-10-16 14:12 | 2013-10-16 14:12 | 0 | E0888 | DE 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
201565 | 30659 | 10232 |  |  | 2013-10-16 14:09 | 2013-10-16 14:09 | 0 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
201566 | 30660 | 10233 |  |  | 2013-10-16 14:25 | 2013-10-16 14:26 | 1 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
203138 | 30787 | 1971 |  |  | 2013-11-01 23:06 | 2013-11-01 23:22 | 16 | E0169 | TU-BG-DB 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Completed | TRUE | 0 | TRUE |  | IR1450 TU-BG-DB 110 kV transmission circuit tripped due to an unknown transmission circuit fault. generation loss = 9.2 MW | FALSE | Non-Critical
203139 | 30788 | 1973 |  |  | 2013-11-20 13:27 | 2013-11-20 13:27 | 0 | E0400 | BU-HM 110 kV Transmission Circuit | Transmission | Fault | Pending Investigation | Transend | Completed | TRUE | 0 | TRUE |  | IR1505 BU-HM 110 kV transmission circuit tripped and reclosed, suspect lightning. | FALSE | Non-Critical
203220 | 30789 | 1974 |  |  | 2013-11-22 17:27 | 2013-11-22 17:27 | 0 | E0259 | PM-HA 1 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1502 PM-HA 220 kV transmission circuit tripped and reclosed with lightning in area, and SPS operation shedding 100 MW at Rio Tinto Alcan. 2692 MWmins lost at Rio Tinto Alcan | FALSE | Critical
203221 | 30790 | 1975 |  |  | 2013-11-22 18:51 | 2013-11-22 18:51 | 0 | E0243 | GO-CS 2 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1503 GO-CS 2 220 kV transmission circuit tripped and reclosed with lightning in area. | FALSE | Critical
207688 | 30791 | 1976 |  |  | 2013-11-23 12:48 | 2013-11-23 12:48 | 0 | E1497 | NW-SD 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1504 NW-SD, NW-SD-DE and DE-MR 110 kV transmission circuits tripped with lightning in area. | FALSE | Non-Critical
207689 | 30791 | 1976 |  |  | 2013-11-23 12:48 | 2013-11-23 12:48 | 0 | E1635 | NW-SD-DE 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1504 NW-SD, NW-SD-DE and DE-MR 110 kV transmission circuits tripped with lightning in area. | FALSE | Non-Critical
207690 | 30791 | 1976 |  |  | 2013-11-23 12:48 | 2013-11-23 12:48 | 0 | E1927 | MR-DE 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1504 NW-SD, NW-SD-DE and DE-MR 110 kV transmission circuits tripped with lightning in area. | FALSE | Undefined
203848 | 30847 | 1979 |  |  | 2013-11-28 14:44 | 2013-11-28 15:12 | 28 | E0263 | PO-PM 4 220 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1510 PO-PM 4 220 kV transmission circuit tripped following an intertrip from the generator. | FALSE | Non-Critical
203849 | 30848 | 1980 |  |  | 2013-11-28 15:32 | 2013-11-28 15:32 | 0 | E0264 | PM-HA 4 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1509 PM-HA 4 110 kV transmission circuit tripped and auto reclosed due to (suspect) lightning. | FALSE | Critical
203896 | 30851 | 1981 |  |  | 2013-12-03 14:21 | 2013-12-03 14:24 | 3 | E1713 | MY 110 kV A7 Bus Coupler Circuit | Bus Coupler | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1514 Mowbray B152 and A752 circuit breakers tripped due to human error during planned protection testing. | FALSE | Not In Wasp
203895 | 30851 | 1981 |  |  | 2013-12-03 14:04 | 2013-12-03 14:25 | 21 | E0646 | TR-MY 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Completed | TRUE | 0 | TRUE |  | IR1514 Mowbray B152 and A752 circuit breakers tripped due to human error during planned protection testing. | FALSE | Non-Critical
206626 | 30852 | 1983 |  |  | 2013-12-04 09:31 | 2013-12-04 09:47 | 16 | E0235 | RI 11 kV F3 Feeder Circuit | Feeder | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR1516 Risdon 110/11 kV T1 transformer tripped following a fault at Nyrstar. Nyrstar dropped approx 68 MW of load. discuss this with customer, probably not an LOS event. | FALSE | Undefined
206625 | 30852 | 1983 |  |  | 2013-12-04 09:31 | 2013-12-04 11:11 | 100 | E0210 | RI 110/11 kV T1 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 0 | TRUE |  | IR1516 Risdon 110/11 kV T1 transformer tripped following a fault at Nyrstar. Nyrstar dropped approx 68 MW of load. discuss this with customer, probably not an LOS event. | FALSE | Non-Critical
203899 | 30853 | 1984 |  |  | 2013-12-05 11:23 | 2013-12-05 11:24 | 0 | E0540 | SH-FI 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Completed | TRUE | 0 | TRUE |  | IR1517 SH-FI 220 kV transmission circuit tripped with lightning in area. Generator lost 32 MW. | FALSE | Non-Critical
204103 | 30855 | 10235 |  |  | 2013-10-16 13:02 | 2013-10-16 16:43 | 221 | E0304 | AV 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204104 | 30856 | 10237 |  |  | 2013-10-16 14:43 | 2013-10-16 18:18 | 215 | E0557 | DE 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204105 | 30857 | 10238 |  |  | 2013-10-17 16:38 | 2013-10-17 16:38 | 0 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204106 | 30858 | 10239 |  |  | 2013-10-20 16:30 | 2013-10-20 18:29 | 119 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204107 | 30859 | 10240 |  |  | 2013-10-21 07:29 | 2013-10-21 08:00 | 31 | E0084 | CR 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204108 | 30860 | 10241 |  |  | 2013-10-25 15:11 | 2013-10-25 15:28 | 17 | E0014 | BW 11 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204109 | 30861 | 10242 |  |  | 2013-10-26 00:07 | 2013-10-26 01:09 | 62 | E0737 | NH 11 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204110 | 30862 | 10243 |  |  | 2013-10-27 04:10 | 2013-10-27 04:32 | 22 | E0491 | GT 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204111 | 30863 | 10244 |  |  | 2013-10-29 20:58 | 2013-10-29 21:56 | 58 | E0906 | TR 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204112 | 30864 | 10245 |  |  | 2013-10-30 22:43 | 2013-10-30 23:03 | 20 | E0353 | LF 33 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204115 | 30867 | 10248 |  |  | 2013-11-03 12:03 | 2013-11-03 12:03 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204116 | 30868 | 10249 |  |  | 2013-11-03 12:16 | 2013-11-03 12:16 | 0 | E1888 | SL 22 kV F2 Feeder | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
204117 | 30869 | 10250 |  |  | 2013-11-03 15:12 | 2013-11-03 15:12 | 0 | E0388 | BU 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204118 | 30870 | 10251 |  |  | 2013-11-03 17:51 | 2013-11-03 17:51 | 0 | E0788 | QT 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204119 | 30871 | 10252 |  |  | 2013-11-04 19:54 | 2013-11-04 19:54 | 0 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204120 | 30872 | 10253 |  |  | 2013-11-05 18:22 | 2013-11-05 18:39 | 17 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204121 | 30873 | 10254 |  |  | 2013-11-06 04:40 | 2013-11-06 04:57 | 17 | E1538 | MY 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204122 | 30874 | 10255 |  |  | 2013-11-07 20:02 | 2013-11-07 20:02 | 0 | E0905 | TR 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204123 | 30875 | 10256 |  |  | 2013-11-07 22:39 | 2013-11-07 22:39 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204125 | 30877 | 10258 |  |  | 2013-11-10 12:43 | 2013-11-10 12:43 | 0 | E0918 | TR 22 kV Y2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204126 | 30878 | 10259 |  |  | 2013-11-10 18:26 | 2013-11-10 18:46 | 20 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204127 | 30879 | 10260 |  |  | 2013-11-12 07:31 | 2013-11-12 07:32 | 1 | E0199 | SO 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204128 | 30880 | 10261 |  |  | 2013-11-13 18:33 | 2013-11-13 18:59 | 26 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204129 | 30881 | 10263 |  |  | 2013-11-13 18:59 | 2013-11-14 19:29 | 1470 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204130 | 30882 | 10265 |  |  | 2013-11-15 10:01 | 2013-11-15 10:01 | 0 | E1001 | BU 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204131 | 30883 | 10266 |  |  | 2013-11-15 19:23 | 2013-11-15 19:40 | 17 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204132 | 30884 | 10267 |  |  | 2013-11-18 18:33 | 2013-11-18 18:50 | 17 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204133 | 30885 | 10268 |  |  | 2013-11-18 18:52 | 2013-11-18 19:59 | 67 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204134 | 30886 | 10269 |  |  | 2013-11-21 10:55 | 2013-11-21 10:55 | 0 | E1535 | MY 22 kV L2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204135 | 30887 | 10270 |  |  | 2013-11-21 18:26 | 2013-11-21 18:46 | 20 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204136 | 30888 | 10271 |  |  | 2013-11-21 19:06 | 2013-11-21 19:25 | 19 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204137 | 30889 | 10272 |  |  | 2013-11-22 04:56 | 2013-11-22 06:38 | 102 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204138 | 30890 | 10274 |  |  | 2013-11-23 11:50 | 2013-11-23 11:50 | 0 | E0640 | ST 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204139 | 30891 | 10275 |  |  | 2013-11-24 04:32 | 2013-11-24 04:32 | 0 | E1455 | HA 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204140 | 30892 | 10276 |  |  | 2013-11-24 04:32 | 2013-11-24 04:32 | 0 | E0911 | TR 22 kV S2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204143 | 30895 | 10278 |  |  | 2013-11-28 07:07 | 2013-11-28 08:58 | 111 | E0835 | RK 11 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204144 | 30896 | 1986 |  |  | 2013-12-11 00:42 | 2013-12-11 01:52 | 70 | E0318 | BY 6.6 kV B Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Completed | TRUE | 855 | TRUE |  | IR1532 Boyer 6.6 kV B Bus tripped. | FALSE | Undefined
204145 | 30897 | 1985 |  |  | 2013-12-10 19:21 | 2013-12-10 19:21 | 0 | E0404 | SH-BU 2 110 kV Transmission Circuit | Transmission | Fault | Pending Investigation | Transend | Completed | TRUE | 0 | TRUE |  | IR1531 SH-BU 110 kV transmission circuit tripped and auto reclosed. | FALSE | Non-Critical
204210 | 30898 | 10279 |  |  | 2013-11-29 04:58 | 2013-11-29 05:17 | 19 | E1504 | TB 22 KV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204211 | 30899 | 10280 |  |  | 2013-11-29 09:38 | 2013-11-29 10:19 | 41 | E1434 | HA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204212 | 30900 | 10281 |  |  | 2013-12-01 16:05 | 2013-12-01 16:05 | 0 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204213 | 30901 | 10282 |  |  | 2013-12-02 13:26 | 2013-12-02 13:26 | 0 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204214 | 30902 | 10284 |  |  | 2013-12-02 18:25 | 2013-12-02 18:25 | 0 | E0305 | AV 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204215 | 30903 | 10285 |  |  | 2013-12-04 10:06 | 2013-12-04 10:30 | 24 | E0657 | SM 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204216 | 30904 | 10286 |  |  | 2013-12-05 12:14 | 2013-12-05 12:14 | 0 | E0824 | RA 22 kV F2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204217 | 30905 | 10287 |  |  | 2013-12-06 06:06 | 2013-12-06 06:25 | 19 | E0084 | CR 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204218 | 30906 | 10289 |  |  | 2013-12-08 00:13 | 2013-12-08 00:13 | 0 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204219 | 30907 | 10290 |  |  | 2013-12-08 12:38 | 2013-12-08 12:38 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204220 | 30908 | 10291 |  |  | 2013-12-08 14:57 | 2013-12-08 14:57 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204221 | 30909 | 10292 |  |  | 2013-12-08 15:00 | 2013-12-08 15:00 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204222 | 30910 | 10294 |  |  | 2013-12-09 05:28 | 2013-12-09 05:28 | 0 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204223 | 30911 | 10295 |  |  | 2013-12-10 02:29 | 2013-12-10 02:29 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204224 | 30912 | 10296 |  |  | 2013-12-12 06:05 | 2013-12-12 06:05 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
204225 | 30913 | 10297 |  |  | 2013-12-12 16:24 | 2013-12-12 16:43 | 19 | E0084 | CR 33 kV G2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207692 | 30915 | 1987 |  |  | 2013-12-13 10:18 | 2013-12-13 11:59 | 101 | E1017 | NH 110/11 kV T1 Transformer Circuit | Transformer | Fault | Poor Construction | Transend | Completed | TRUE | 0 | TRUE |  | IR1533 North Hobart T1 transformer circuit tripped twice during planned work due to incorrect isolation. | FALSE | Undefined
205239 | 30916 | 1990 |  |  | 2013-12-16 11:48 | 2013-12-16 14:18 | 150 | E0261 | PO-PM 3 220 kV Transmission Circuit | Transmission | Fault | Intertrip | Generator Request | Completed | TRUE | 0 | TRUE |  | IR1535 PO-PM 3 transmission circuit tripped following reception of an intertrip signal. | FALSE | Non-Critical
207125 | 31029 | 9789 |  |  | 2013-01-26 15:48 | 2013-01-26 15:49 | 1 | E1551 | DP 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207126 | 31030 | 9795 |  |  | 2013-01-29 01:25 | 2013-01-29 02:38 | 73 | E1560 | HA 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207127 | 31031 | 9882 |  |  | 2013-03-10 21:38 | 2013-03-10 22:30 | 52 | E1501 | TB 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207128 | 31032 | 10154 |  |  | 2013-09-05 03:20 | 2013-09-05 03:54 | 34 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207129 | 31033 | 10155 |  |  | 2013-09-05 04:10 | 2013-09-05 04:27 | 17 | E0408 | DB 22 kV A2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207130 | 31034 | 10159 |  |  | 2013-09-09 16:32 | 2013-09-09 16:32 | 0 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207606 | 31035 | 10160 |  |  | 2013-09-10 04:05 | 2013-09-10 04:05 | 0 | E1002 | BU 22 kV M2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207133 | 31037 | 10299 |  |  | 2013-12-14 02:41 | 2013-12-14 02:41 | 0 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207134 | 31038 | 10300 |  |  | 2013-12-15 00:51 | 2013-12-15 00:51 | 0 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207135 | 31039 | 10301 |  |  | 2013-12-17 01:08 | 2013-12-17 01:08 | 0 | E1567 | DP 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207136 | 31040 | 10302 |  |  | 2013-12-17 02:53 | 2013-12-17 02:53 | 0 | E0822 | RA 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207140 | 31044 | 10306 |  |  | 2013-12-20 11:11 | 2013-12-20 11:11 | 0 | E1896 | SL 22 kV M2 Feeder | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Not in WASP
207141 | 31045 | 10307 |  |  | 2013-12-20 20:45 | 2013-12-20 20:46 | 1 | E0903 | TR 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207142 | 31046 | 10308 |  |  | 2013-12-21 00:43 | 2013-12-21 00:43 | 0 | E0946 | UL 22 kV D2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207143 | 31047 | 10309 |  |  | 2013-12-21 16:57 | 2013-12-21 16:57 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207144 | 31048 | 10310 |  |  | 2013-12-21 06:05 | 2013-12-21 06:05 | 0 | E1004 | BU 22 kV P2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207145 | 31050 | 10312 |  |  | 2013-12-22 06:30 | 2013-12-22 07:04 | 34 | E0075 | CR 33 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207146 | 31051 | 10313 |  |  | 2013-12-25 00:30 | 2013-12-25 00:31 | 1 | E0198 | SO 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207147 | 31052 | 10314 |  |  | 2013-12-25 14:59 | 2013-12-25 16:25 | 86 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207148 | 31053 | 10315 |  |  | 2013-12-25 17:12 | 2013-12-25 18:01 | 49 | E1456 | HA 22 kV N2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207149 | 31054 | 10316 |  |  | 2013-12-26 00:06 | 2013-12-26 00:06 | 0 | E1433 | HA 22 kV C2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207150 | 31055 | 10317 |  |  | 2013-12-26 05:13 | 2013-12-26 05:13 | 0 | E1517 | PL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207151 | 31056 | 10318 |  |  | 2013-12-26 06:38 | 2013-12-26 07:37 | 59 | E1432 | HA 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207152 | 31057 | 10319 |  |  | 2013-12-26 17:23 | 2013-12-26 18:20 | 57 | E1613 | UL 22 kV H2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207153 | 31058 | 10320 |  |  | 2013-12-27 11:48 | 2013-12-27 11:48 | 0 | E1005 | BU 22 kV Q2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207154 | 31059 | 10321 |  |  | 2013-12-27 15:55 | 2013-12-27 15:55 | 0 | E0412 | EL 11 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207155 | 31060 | 10322 |  |  | 2013-12-28 05:08 | 2013-12-28 05:08 | 0 | E1444 | HA 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207156 | 31061 | 10323 |  |  | 2013-12-28 12:32 | 2013-12-28 12:33 | 1 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207157 | 31062 | 10324 |  |  | 2013-12-28 13:33 | 2013-12-28 13:52 | 19 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207158 | 31063 | 10325 |  |  | 2013-12-28 13:57 | 2013-12-28 13:57 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207159 | 31064 | 10326 |  |  | 2013-12-28 14:32 | 2013-12-28 14:32 | 0 | E0020 | BW 11 kV J2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207161 | 31066 | 10328 |  |  | 2013-12-31 06:22 | 2013-12-31 06:23 | 1 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207162 | 31067 | 10329 |  |  | 2014-01-01 16:24 | 2014-01-01 16:24 | 0 | E0303 | AV 22 kV B2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
207163 | 31068 | 10330 |  |  | 2014-01-01 19:01 | 2014-01-01 19:19 | 18 | E1534 | MY 22 kV K2 Feeder Circuit | Feeder | Fault |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94419 | 11461 | 108536 | 2007-08-16 19:00 | 2007-08-16 22:00 | 2007-08-16 20:00 | 2007-08-16 20:38 | 38 | E1027 | QU 22 kV A Bus | Bus | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:22kV Isolated as requiredWorkPlanned:Isolate 22kV Hellyer Mine feeder to repair Links on spur line. | FALSE | Undefined
94430 | 11489 | 108490 | 2007-08-10 13:34 | 2007-08-11 16:00 | 2007-08-10 13:34 | 2007-08-11 08:59 | 1165 | E0435 | HA 220/110 kV T1 Transformer Circuit | Transformer | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:T1 isolated & earthed as required.WorkPlanned:Investigate cause of trip. | FALSE | Non-Critical
94676 | 11791 | 108816 | 2007-10-09 10:30 | 2007-10-09 11:30 | 2007-10-09 10:35 | 2007-10-09 10:50 | 15 | E0286 | PO-PM 1 110 kV Transmission Circuit | Transmission | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Transmission line opened off. Isolated as required.WorkPlanned:Investigate cause of Palmerston 110 kV bus zone alarms. | FALSE | Non-Critical
94812 | 11962 | 108922 | 2007-11-09 16:51 | 2007-11-10 19:00 | 2007-11-09 16:51 | 2007-11-10 05:09 | 738 | E0291 | PM-SH 220 kV Transmission Circuit | Transmission | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Nil.WorkPlanned:An ariel inspection by Aeropower of this line has turned up a bird net structure over paddocks impinging on ground clearances. This is unsafe and the structures must be shortened.The line will be opened off at both ends for reasons of safety. It is available for service if required. An observer will be sent to site in this event. | FALSE | Critical
90202 | 12423 | 109815 | 2008-02-29 09:00 | 2008-02-29 14:00 | 2008-02-29 09:25 | 2008-02-29 10:50 | 85 | E1545 | DP 110 kV B7 Bus Coupler Circuit | Bus Coupler | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:DP 110 kV B7 Bus Coupler Circuit isolated and earthed if required.22kV bus couplers A852 and B852 to be opened.Local area risk notice to be issued.WorkPlanned:Top up SF6 gas in B752 | FALSE | Undefined
90875 | 12930 | 6870 |  |  | 2008-04-04 23:46 | 2008-04-04 23:47 | 1 | E0789 | QT 22 kV B2 Feeder Circuit | Feeder | Emergency |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
91910 | 14328 | 109814 | 2008-03-04 09:00 | 2008-03-04 13:00 | 2008-03-04 08:32 | 2008-03-04 12:40 | 248 | E1066 | QU 22 kV B2 Feeder Circuit | Feeder | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:22kV Hellyer Mine feeder Isolated & Earthed if requiredConfirm with Hellyer mine prior to proceeding with outage Outage arranged with Hellyer mines. WorkPlanned:QU 22 kV B2 Feeder CircuitHigh Priority Hot Connection repairs on B229, CT B296A & B296B | FALSE | Undefined
92024 | 14482 | 109256 | 2007-12-31 12:31 | 2008-01-01 16:00 | 2007-12-31 12:31 | 2008-01-01 16:00 | 1649 | E0028 | GO-CS 1 220 kV Transmission Circuit | Transmission | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Both end of GO-CS 1 220 kV Transmission if required.WorkPlanned:Investigate and repair if necessay faulted Transmission Line | FALSE | Critical
94922 | 14579 | 108965 | 2007-11-15 12:00 | 2007-11-15 15:00 | 2007-11-15 12:51 | 2007-11-15 19:05 | 374 | E0517 | SH 110 kV A Bus | Bus | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:All 110kV circuits transfered to 110kV B Bus (110kV capacitor to remain out of service)110kV A bus to be earthed for inspection.WorkPlanned:Inspection of 110kV A Bus equipment including isolator A629A after fault | FALSE | Undefined
94923 | 14580 | 108964 | 2007-11-14 13:36 | 2007-11-15 18:00 | 2007-11-14 14:36 | 2007-11-15 18:00 | 1644 | E0519 | SH 110 kV B Bus | Bus | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:All equipment on 110kV A bus. B752 opened off. No earthing applied.WorkPlanned:Investigate B bus for evidence of busfault which caused trip of both 110kV busses on 14/11/07. | FALSE | Undefined
95022 | 14849 | 108086 | 2007-06-22 08:00 | 2007-06-22 18:00 | 2007-06-22 08:11 | 2007-06-22 16:08 | 477 | E0878 | SR 110/22 kV T3 Transformer Circuit | Transformer | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Transformer T3 is required to be Opened Off, Isolated and Earthed.WorkPlanned:Transformer T3 Cable Replacement | FALSE | Non-Critical
118412 | 14905 | 107900 | 2007-05-31 00:01 | 2007-05-31 16:00 | 2007-05-30 09:30 | 2007-05-31 17:40 | 1930 | E0268 | PO-PM 6 220 kV Transmission Circuit | Transmission | Emergency | HV Equipment Maintenance | Generator Request | Completed | TRUE | 0 | TRUE |  | Isolation Points:Palmerston 220kV Circuit Breaker A152 Opened on fault, Poatina 220 kV F29 Isolator opened.WorkPlanned:At Hydro's request, PO-PM 6 220 kV Transmission Circuit left out of servcie after Poatina 220 kV Circuit Breaker F52 failed | FALSE | Non-Critical
95047 | 14973 | 107772 | 2007-05-02 10:00 | 2007-05-02 14:00 | 2007-05-02 10:05 | 2007-05-02 13:55 | 230 | E0249 | LI-PM 2 220 kV Transmission Circuit | Transmission | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:D196 Required isolated and earthed. NOTE: Outage to be in conjunction with Palmerston outage 107628"WorkPlanned:"Shorting of CT cores at CT junction box following report from site that a set of terminals in D196 are badly chared and there are signs of smoke damage in the box. | FALSE | Critical
92370 | 16615 | 111391 | 2008-11-20 14:55 | 2008-11-25 18:00 | 2008-11-20 14:55 | 2008-11-26 18:16 | 8841 | E0196 | SO 22 kV A8 Bus Coupler Circuit | Bus Coupler | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:A852 to be isolated. Earthed as required.WorkPlanned:Investigate and repair cause of discharge on A852 | FALSE | Undefined
92442 | 16711 | 111662 | 2008-12-22 14:30 | 2008-12-22 16:00 | 2008-12-22 13:30 | 2008-12-22 14:42 | 72 | E0646 | TR-MY 110 kV Transmission Circuit | Transmission | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:TR-MB T/L to be isolated if deemed necessary be the work crew.WorkPlanned:Remove tangled party balloons from line conductors. | FALSE | Non-Critical
185957 | 16816 | 111528 | 2008-12-06 21:55 | 2008-12-12 16:00 | 2008-12-06 21:55 | 2008-12-09 13:58 | 3843 | E0293 | AL 110/6.6 kV T1 Transformer Circuit | Transformer | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | not included in ITOMS as no fault found. Isolation Points:As required.WorkPlanned:Inspection and testing of 110/6.6kV T1 transformer after trip. | FALSE | Non-Critical
102206 | 17618 | 112418 | 2009-03-28 07:30 | 2009-03-28 16:30 | 2009-03-28 08:34 | 2009-03-28 20:10 | 696 | E0512 | GT-SW 110 kV Transmission Circuit | Transmission | Emergency | HV Equipment Maintenance | MI | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate GT-SW 110 kV Transmission Circuit, earth as and when requiredRequested by MI, FEA Bell bayWorkPlanned:HV equipment maintenance by FEA Bell Bay Transline 110kV CB A152 Locked out on Low SF6 Gas - to repair | FALSE | Non-Critical
116467 | 20561 | 115111 | 2010-03-12 09:19 | 2010-03-12 16:00 | 2010-03-12 10:46 | 2010-03-12 18:13 | 447 | E0516 | SH-GT 2 220 kV Transmission Circuit | Transmission | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:As requiredWorkPlanned:Investigate the trip of B152 at the GT end | FALSE | Critical
153723 | 20584 | 115085 | 2010-03-10 12:46 | 2010-03-11 11:00 | 2010-03-10 12:46 | 2010-03-11 11:39 | 1373 | E0718 | FA-MA 110 kV Transmission Circuit | Transmission | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:T/L opened off and isolated.WorkPlanned:Repair damage to insulators. | FALSE | Non-Critical
120670 | 21118 | 115613 | 2010-06-01 | 2010-06-01 01:00 | 2010-05-31 23:13 | 2010-06-01 03:19 | 246 | E0383 | BU 110/22 kV T7 Transformer Circuit | Transformer | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:All 22kV CB's on BU 22 kV B Bus to be Opened off and racked out.Dist Op's to Field parallel all 22kV CB's on Burnie 22kV B Bus -J252,K252,L252,M252, N252, P252 and Q252so that B897 can be removed from service. Tranformer T7 via CB G552 to be opern off.WorkPlanned:Repair 22kV VT B897 (Fault blow fuses) | FALSE | Non-Critical
120671 | 21118 | 115613 | 2010-06-01 | 2010-06-01 01:00 | 2010-05-31 23:13 | 2010-06-01 03:19 | 246 | E0386 | BU 22 kV B Bus | Bus | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:All 22kV CB's on BU 22 kV B Bus to be Opened off and racked out.Dist Op's to Field parallel all 22kV CB's on Burnie 22kV B Bus -J252,K252,L252,M252, N252, P252 and Q252so that B897 can be removed from service. Tranformer T7 via CB G552 to be opern off.WorkPlanned:Repair 22kV VT B897 (Fault blow fuses) | FALSE | Undefined
120672 | 21118 | 115613 | 2010-06-01 | 2010-06-01 01:00 | 2010-05-31 23:13 | 2010-06-01 03:19 | 246 | E0405 | BU 22 kV A8 Bus Coupler Circuit | Bus Coupler | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:All 22kV CB's on BU 22 kV B Bus to be Opened off and racked out.Dist Op's to Field parallel all 22kV CB's on Burnie 22kV B Bus -J252,K252,L252,M252, N252, P252 and Q252so that B897 can be removed from service. Tranformer T7 via CB G552 to be opern off.WorkPlanned:Repair 22kV VT B897 (Fault blow fuses) | FALSE | Undefined
132208 | 23078 | 117378 | 2011-02-05 16:30 | 2011-02-07 17:00 | 2011-02-05 16:30 | 2011-02-10 20:48 | 7458 | E0156 | MB 22 kV A2 Feeder Circuit | Feeder | Emergency | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:A252 to be isolated and earthedWorkPlanned:Carry out repairs on feeder No. 45001. | FALSE | Undefined
134748 | 23313 | 117746 | 2011-03-06 16:15 | 2011-03-11 16:30 | 2011-03-06 16:15 | 2011-03-09 15:43 | 4288 | E0629 | WV 110/11 kV T3 Transformer Circuit | Transformer | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:T3 as requiredWorkPlanned:Investigate and analyse gassing within 110/11 Transformer T3 | FALSE | Non-Critical
141154 | 23637 | 118084 | 2011-05-09 11:00 | 2011-05-09 18:00 | 2011-05-09 11:32 | 2011-05-09 17:00 | 328 | E1763 | LF-MT-RK 2 110 kV Transmission Circuit | Transmission | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate LF-MT-RK 2 110 kV Transmission Circuit, earth as required.WorkPlanned:To investigate reason for trip on TFMR T2 that occurred on Wednesday 4th May 2011 and to proceed with the protection upgrade at both ends (Lindisfarne and Rokeby.) | TRUE | Non-Critical
141328 | 23637 | 118084 | 2011-05-10 08:00 | 2011-05-10 17:00 | 2011-05-10 07:58 | 2011-05-10 21:24 | 806 | E1763 | LF-MT-RK 2 110 kV Transmission Circuit | Transmission | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate LF-MT-RK 2 110 kV Transmission Circuit, earth as required.WorkPlanned:To investigate reason for trip on TFMR T2 that occurred on Wednesday 4th May 2011 and to proceed with the protection upgrade at both ends (Lindisfarne and Rokeby.) | TRUE | Non-Critical
141234 | 24414 | 118733 | 2011-07-31 15:45 | 2011-08-01 17:00 | 2011-07-31 18:38 | 2011-07-31 19:24 | 46 | E0476 | GT 110 kV B Bus | Bus | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110kV B Bus opened offWorkPlanned:Take 110kV B Bus out of service until repairs can be completed on the 110kV B bus zone protection | FALSE | Undefined
141235 | 24415 | 118732 | 2011-07-31 09:03 | 2011-07-31 19:00 | 2011-07-31 09:03 | 2011-07-31 16:24 | 441 | E0715 | FA-JB 220 kV Transmission Circuit | Transmission | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:FA-JB 220kV to be isolated and earthed.WorkPlanned:Investigate and repair fallen earthwire on the 220kV Farrell - John Butters transmission line. | FALSE | Non-Critical
146730 | 24993 | 119233 | 2011-10-12 10:13 | 2011-10-13 16:00 | 2011-10-12 10:13 | 2011-10-13 17:06 | 1853 | E0286 | PO-PM 1 110 kV Transmission Circuit | Transmission | Emergency | HV Equipment Maintenance | Generator Request | Completed | TRUE | 0 | TRUE |  | Isolation Points:as requiredWorkPlanned:Isolate for Bucholz trip | FALSE | Non-Critical
149309 | 25315 | 119551 | 2011-12-13 09:50 | 2011-12-13 17:00 | 2011-12-13 10:04 | 2011-12-15 09:39 | 2855 | E0202 | SO 22 kV F2 Feeder Circuit | Feeder | Emergency | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:F252WorkPlanned:Feeder isolated to repair cable fault | FALSE | Undefined
149732 | 25393 | 119582 | 2011-12-21 23:05 | 2011-12-22 16:30 | 2011-12-20 23:00 | 2011-12-21 10:55 | 715 | E0971 | SO 22 kV H2 Feeder Circuit | Feeder | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:CB H252 racked out at the momentWorkPlanned:Investigate 22kV Circuit Breaker H252 "rack in" Mechanism | FALSE | Undefined
150414 | 25448 | 119641 | 2012-01-11 09:00 | 2012-01-11 16:00 | 2012-01-11 09:28 | 2012-01-11 10:43 | 75 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:as required by on site operatorWorkPlanned:Circuit Breaker W252 gass top up | FALSE | Undefined
198351 | 25468 | 119685 | 2012-01-18 09:00 | 2012-01-18 16:00 | 2012-01-18 14:48 | 2012-01-18 16:00 | 72 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
152996 | 25752 | 119967 | 2012-02-25 14:59 | 2012-02-25 16:00 | 2012-02-25 14:59 | 2012-02-25 15:31 | 32 | E1762 | LF-MT-RK 1 110 kV Transmission Circuit | Transmission | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Transmission line de-energised only at request of asset officer.WorkPlanned:Remove tree in close proximity to line | FALSE | Non-Critical
158305 | 26534 | 120654 | 2012-05-21 12:00 | 2012-05-21 13:00 | 2012-05-21 13:37 | 2012-05-21 16:30 | 173 | E0972 | CS-KI-EL 110 kV Transmission Circuit (Changed to E1956) | Transmission | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110 kV Chapel St - Kingston - Electrona Transmission circuit isolated and earthed WorkPlanned:Emergency repair on Tower 49 near Kinston - Crevis pin loose | FALSE | Non-Critical
161233 | 26653 | 120786 | 2012-06-08 07:20 | 2012-06-08 12:00 | 2012-06-08 07:20 | 2012-06-08 10:13 | 173 | E0505 | GT 220 kV C2 Capacitor Circuit | Capacitor | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:AS requiredWorkPlanned:Investigate fail to operate on 220 kV Capacitor bank C2. | FALSE | Non-Critical
172841 | 27520 | 121668 | 2012-10-02 05:00 | 2012-10-02 05:15 | 2012-10-02 04:53 | 2012-10-02 05:14 | 21 | E0512 | GT-SW 110 kV Transmission Circuit | Transmission | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open and isolate GT-SW 110 kV Transmission Circuit as required.WorkPlanned:Top up SF6 gas in CB T152.MI customer Gunns have agree on date and time for this outage. | FALSE | Non-Critical
173562 | 27665 | 121700 | 2012-10-06 14:00 | 2012-10-06 15:00 | 2012-10-06 14:03 | 2012-10-06 16:28 | 145 | E0267 | PO-PM 5 220 kV Transmission Circuit | Transmission | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:PO-PM No 5 & 6 220 kV Transmission Circuits required de-energised, isloated and earthed for issue of clearance to line crew.WorkPlanned:Reattach broken suspension arm on overhead earth wire at top of tower. | FALSE | Non-Critical
173563 | 27665 | 121700 | 2012-10-06 14:00 | 2012-10-06 15:00 | 2012-10-06 14:03 | 2012-10-06 16:28 | 145 | E0268 | PO-PM 6 220 kV Transmission Circuit | Transmission | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:PO-PM No 5 & 6 220 kV Transmission Circuits required de-energised, isloated and earthed for issue of clearance to line crew.WorkPlanned:Reattach broken suspension arm on overhead earth wire at top of tower. | FALSE | Non-Critical
174325 | 27924 | 121897 | 2012-11-06 09:30 | 2012-11-06 16:00 | 2012-11-06 09:19 | 2012-11-06 15:04 | 345 | E0902 | TR 22 kV C2 Feeder Circuit | Feeder | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:C252WorkPlanned:Normally out of service breaker. Investigate E/F on closing. | FALSE | Undefined
177168 | 28140 | 122087 | 2012-11-30 15:30 | 2012-11-30 17:30 | 2012-11-30 16:14 | 2012-11-30 20:41 | 267 | E0275 | WA-PM 2 110 kV Transmission Circuit | Transmission | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:NilWorkPlanned:De-energise the WA-PM 2 110kV Transmission Line due to threat of fire. | FALSE | Critical
181357 | 28523 | 9799 |  |  | 2013-01-31 02:32 | 2013-01-31 02:32 | 0 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Emergency |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
190042 | 28840 | 122764 | 2013-03-27 07:00 | 2013-05-31 23:59 | 2013-03-27 20:00 | 2013-06-20 14:18 | 122058 | E0766 | NW 22 kV C2 Feeder Circuit | Feeder | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:As requestedWorkPlanned:Investigate fault associated with C252 Aurora feeder 65062. | FALSE | Undefined
188608 | 29267 | 123038 | 2013-05-13 08:30 | 2013-07-13 16:00 | 2013-05-13 07:35 | 2013-05-28 11:46 | 21851 | E1432 | HA 22 kV B2 Feeder Circuit | Feeder | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate and Earth 22kV CB B252WorkPlanned:Find and repair Feeder Cable | FALSE | Undefined
188616 | 29296 | 123099 | 2013-05-20 16:15 | 2013-05-22 12:00 | 2013-05-20 16:15 | 2013-05-22 12:44 | 2669 | E0209 | RI 110 kV C2 Capacitor Circuit | Capacitor | Emergency | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:C2 unavailable for service.Secondary isolations as required.WorkPlanned:Replace faulty K627/659 relay. | FALSE | Non-Critical
198694 | 30513 | 10167 |  |  | 2013-09-22 21:56 | 2013-09-22 21:56 | 0 | E1550 | DP 22 kV J2 Feeder Circuit | Feeder | Emergency |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
105705 | 8843 | 6782 |  |  | 2007-03-23 22:46 | 2007-03-23 23:24 | 38 | E0157 | MB 22 kV B2 Feeder Circuit | Feeder | Forced |  | DNSP | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
93747 | 8992 | 107717 | 2007-04-20 09:30 | 2007-04-24 14:30 | 2007-04-20 09:08 | 2007-04-30 17:52 | 14925 | E1392 | BU 110 kV C1 Capacitor Circuit | Capacitor | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate BU 110 kV C1 Capacitor Circuit, earth if required.One disconnector status will be inverted to allow operation of F652.CB fail links to be opened during testing.WorkPlanned:Investigation of closing fault on red phase of CB F652. | FALSE | Non-Critical
93754 | 9000 | 107701 | 2007-04-17 10:00 | 2007-04-17 14:00 | 2007-04-17 09:37 | 2007-04-17 14:20 | 283 | E0785 | QU 110/22 kV T1 Transformer Circuit | Transformer | Forced | Secondary Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110/22 kV Transformer T1 Isolated and Earthed as required22 kV Bus Isolated and Earthed as requiredIntec Site contact Wayne Keygan 6439 1155 to be advised prior to outage and prior to return to serviceWorkPlanned:Rewire A596A and A596B and test. Commission new overcurrent (A551) and Differential relay (A487). Decommission temporary overcurrent protection. | FALSE | Non-Critical
93794 | 9066 | 107777 | 2007-04-27 02:30 | 2007-05-03 18:00 | 2007-04-27 08:00 | 2007-05-04 07:50 | 10070 | E0452 | KE 110/11 kV T1 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:As required.WorkPlanned:Investigate and repair faulty relay K10. This relay responsible for false low gas alarm on A452,prevent opening of A431,prevent closing of A452. Additional work on A431 and bay controller A499C. | FALSE | Non-Critical
93830 | 9101 | 107856 | 2007-05-09 11:00 | 2007-05-09 16:00 | 2007-05-09 11:25 | 2007-05-09 15:34 | 249 | E0247 | LI 220 kV A Bus | Bus | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate LI 220 kV A Bus, earth if required.LI-PM 1 220 kV Transmission Circuit isolated and earthed on PROMS 107400.WorkPlanned:Repairs to Disconnector C129A. | FALSE | Undefined
93917 | 10881 | 108002 | 2007-06-04 08:00 | 2007-06-04 16:00 | 2007-06-04 11:48 | 2007-06-04 14:14 | 146 | E0755 | NW 110 kV A Bus | Bus | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110 kV A Bus Isolated as requiredWorkPlanned:Final Commissioning of new NW-SD-DE 110 kV Transmission Circuit as per Commissioning Program ND 0519_004_CPThis proms in conjuntion with Norwood PROMS 107910, Scottsdale PROMS 107862 and Derby PROMS 107863 | FALSE | Undefined
93919 | 10883 | 108000 | 2007-06-06 08:00 | 2007-06-06 16:00 | 2007-06-06 07:36 | 2007-06-06 12:43 | 307 | E0514 | GT-TE 2 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:GT-TE 2 110 kV Transmission Circuit Isolated and EarthedWorkPlanned:Repairs to damaged conductor A Phase at Tower T8 on GT-TE 110 kV Transmission Circuit | FALSE | Non-Critical
94070 | 10980 | 107874 | 2007-05-16 10:00 | 2007-05-16 15:00 |  |  |  | E0027 | LI-CL-RE-CS 1 220 kV Transmission Circuit (Changed to E1958) | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate and earth LI-CL-RE-CS 1 Transmission Circuit.Operator will be on site for the duration of the outage.WorkPlanned:Install new Lightning Protection Air Terminal (AT 3) on Tower T3A as part of the substation lightning protection upgrade.Transline insulator changes unable to be done Live Line due to weight calculation being too high. | FALSE | Critical
139287 | 10997 | 6887 |  |  | 2007-05-16 12:03 | 2007-05-16 12:03 | 0 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Forced |  | DNSP | New | TRUE | 0 | TRUE |  |  | FALSE | Undefined
94108 | 11032 | 108130 | 2007-06-28 09:00 | 2007-06-28 13:00 |  |  |  | E0877 | SR 110/22 kV T2 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110/22 kV Transformer T2 Isolated ans Earthed as requiredWorkPlanned:Inspection of 110/22 kV Transformer T2 22 kV Cables in switchgear cable trench for indications of cable damage | FALSE | Non-Critical
94125 | 11057 | 108096 | 2007-06-19 00:47 | 2007-06-19 16:00 | 2007-06-19 00:47 | 2007-06-19 11:16 | 629 | E1497 | NW-SD 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Transmission Line opened at both ends.WorkPlanned:Locate and rectify fault on 110kV Transmission Line | FALSE | Non-Critical
94136 | 11077 | 108066 | 2007-06-14 09:00 | 2007-06-14 15:00 | 2007-06-14 11:10 | 2007-06-14 13:59 | 169 | E1545 | DP 110 kV B7 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110 kV Circuit Breaker B752 Isolated and Earthed as requiredWorkPlanned:Top up Sf6 gas in 110 kV Bus Coupler CB B752 to clear alarm status | FALSE | Undefined
94142 | 11088 | 108040 | 2007-06-09 08:00 | 2007-06-09 16:00 | 2007-06-09 08:43 | 2007-06-09 16:00 | 437 | E0538 | SH-FA 1 220 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:SH-FA 1 220 kv Transmission Circuit Isolated and Earthed as requiredWorkPlanned:Forced outage to repair Hot Joints and opportune maintenance on SH-FA 1 220 kV Transmission Circuit | FALSE | Critical
94143 | 11089 | 108039 | 2007-06-08 08:00 | 2007-06-08 16:00 | 2007-06-08 07:46 | 2007-06-08 16:09 | 503 | E0539 | SH-FA 2 220 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:SH-FA 2 220 kV Transmission Circuit to be Isolated and Earthed as requiredWorkPlanned:Forced outage to repair Hot Joint at Tower 57 and opportune maintenance on SH-FA 2 220 kV Transmission Circuit | FALSE | Critical
94156 | 11099 | 108026 | 2007-06-07 08:00 | 2007-06-07 16:00 | 2007-06-07 08:03 | 2007-06-07 12:54 | 291 | E1497 | NW-SD 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:NW-SD 110 kV Transmission Circuit Isolated110/22 kV Transformer T2 IsolatedWorkPlanned:Alterations to wiring of 110 kV Circuit Breaker B152 and A752 Trip circuitsFinallisation of commissioning requirements | FALSE | Non-Critical
94157 | 11099 | 108026 | 2007-06-07 08:00 | 2007-06-07 16:00 | 2007-06-07 08:03 | 2007-06-07 12:54 | 291 | E1625 | SD 110 kV A7 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:NW-SD 110 kV Transmission Circuit Isolated110/22 kV Transformer T2 IsolatedWorkPlanned:Alterations to wiring of 110 kV Circuit Breaker B152 and A752 Trip circuitsFinallisation of commissioning requirements | FALSE | Undefined
94158 | 11099 | 108026 | 2007-06-07 08:00 | 2007-06-07 16:00 | 2007-06-07 08:03 | 2007-06-07 12:54 | 291 | E1628 | SD 110/22 kV T2 Transformer Circuit | Transformer | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:NW-SD 110 kV Transmission Circuit Isolated110/22 kV Transformer T2 IsolatedWorkPlanned:Alterations to wiring of 110 kV Circuit Breaker B152 and A752 Trip circuitsFinallisation of commissioning requirements | FALSE | Non-Critical
94203 | 11159 | 108411 | 2007-08-08 08:00 | 2007-08-08 16:00 | 2007-08-08 08:10 | 2007-08-08 13:50 | 340 | E0937 | UL 110 kV A7 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110 kV Circuit Breaker A752 Isolated and Earthed as required22 kV Bus splitWorkPlanned:110 kV Bus Coupler CB A752 to be de-gassed to enable Sf6 gas densiometer to be replaced. | FALSE | Undefined
94224 | 11191 | 108369 | 2007-08-01 10:00 | 2007-08-01 14:00 | 2007-08-01 10:14 | 2007-08-01 14:00 | 226 | E0877 | SR 110/22 kV T2 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110/22 kV Transformer T2 Isolated and Earthed as requiredWorkPlanned:Contractor/Manufacturer Inspection of 22kv cable terminations on 110/22 kV Transformer T2 | FALSE | Non-Critical
94225 | 11193 | 108367 | 2007-07-31 10:00 | 2007-07-31 14:00 | 2007-07-31 09:30 | 2007-07-31 14:00 | 270 | E0776 | PL 110/22 kV T1 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110/22 kV Transformer T1 Isolated and Earthed as requiredWorkPlanned:Contractor/Manufacturer Inspection of 22kv cable terminations on 110/22 kV Transformer T1 | FALSE | Non-Critical
94228 | 11197 | 108362 | 2007-07-24 14:00 | 2007-07-31 16:00 | 2007-07-24 15:23 | 2007-07-31 16:00 | 10117 | E0267 | PO-PM 5 220 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Generator Request | Completed | TRUE | 0 | TRUE |  | Isolation Points:220 kV B152 Circuit Breaker Open and Tagged as requiredWorkPlanned:Hydro Tasmania PO5 Generator Brushgear maintenance isolation required. As per Hydro Tasmania eGO 40559 | FALSE | Non-Critical
94245 | 11219 | 108334 | 2007-07-23 12:00 | 2007-07-23 13:00 | 2007-07-23 12:00 | 2007-07-23 13:16 | 76 | E0512 | GT-SW 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Circuit Breaker T152 isolated and earthed.WorkPlanned:Top up Low SF6 Gas. | FALSE | Non-Critical
94284 | 11263 | 108288 | 2007-07-30 12:00 | 2007-07-30 16:00 | 2007-07-30 11:35 | 2007-07-30 14:01 | 147 | E0630 | WV 110/11 kV T4 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110/11 kV Transformer T4 Isolated and Earthed as requiredWorkPlanned:110/11kv T4 Transformer Inspection of 11kv cable termations (work to be completed for Areva)Outage to occurr during notified load reduction of AP Wesley Vale mill | FALSE | Non-Critical
94285 | 11264 | 108287 | 2007-07-30 08:00 | 2007-07-30 12:00 |  |  |  | E0629 | WV 110/11 kV T3 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110/11kv T3 Transformer to Isolated and Earthed WorkPlanned:110/11kv T3 Transformer Inspection of 11kv cable termations (work to be completed for Areva)Outage to occurr during notified load reduction of AP Wesley Vale mill | FALSE | Non-Critical
94301 | 11304 | 108236 | 2007-07-24 08:30 | 2007-07-24 16:00 | 2007-07-24 08:36 | 2007-07-24 14:24 | 348 | E0776 | PL 110/22 kV T1 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110/22 kV Transformer T1 Isolated and Earthed as requiredWorkPlanned:Inspection of 22 kV cable box and installation of Silca gel following previous failure of Transformer T2 | FALSE | Non-Critical
94308 | 11314 | 108224 | 2007-07-18 08:30 | 2007-07-18 20:00 | 2007-07-18 11:46 | 2007-07-18 18:56 | 430 | E0878 | SR 110/22 kV T3 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110/22 kV Transformer T3 Isolated and Earthed as required.This outage aligns with advised reduction in load at Savage River mineWorkPlanned:Terminate replacement 22 kV Cables between 110/22 kV Transformer T3 and C552 installed on Proms 108223 | FALSE | Non-Critical
94398 | 11420 | 108589 | 2007-09-06 09:00 | 2007-09-06 15:00 | 2007-09-06 12:31 | 2007-09-06 15:00 | 149 | E0422 | HA 110 kV A Bus | Bus | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:T1 to remain in service - A487B, A464, A421 and T1 guard protection unaffected. Secondary isolations to be performed by P & T Services. A521/A487A trips to be isolated for duration of investigation WorkPlanned:T1 protection relay - A521/A487A , 110kV coupler breaker A752 Corrective Maintenance - Investigate the cause of A521/A487A mal-operation experienced during switching operations on 21/8/07. Switching to be performed to replicate the conditions of 21/8/07 ( ie. all 110kV circuits transferred to bus B , A752 to be opened off ). | FALSE | Undefined
94400 | 11423 | 108585 | 2007-09-05 08:00 | 2007-09-08 16:00 | 2007-09-05 08:29 | 2007-09-08 16:00 | 4771 | E1635 | NW-SD-DE 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:NW-SD-DE 110 kV transmission Circuit Isolated and Earthed as requiredTransfromer T1A Isolated.This is a continuous outage and will not return overnight.WorkPlanned:Earth system commissioning tests at Derby, by injection testing of substation earth mat utilising NW-SD-DE 110 kV Transmission Circuit as per test procedureRADS submitted BJ 24/08/07 | FALSE | Non-Critical
94399 | 11423 | 108585 | 2007-09-05 08:00 | 2007-09-08 16:00 | 2007-09-05 08:29 | 2007-09-08 16:00 | 4771 | E1622 | DE 110/22 kV T1A Transformer Circuit | Transformer | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:NW-SD-DE 110 kV transmission Circuit Isolated and Earthed as requiredTransfromer T1A Isolated.This is a continuous outage and will not return overnight.WorkPlanned:Earth system commissioning tests at Derby, by injection testing of substation earth mat utilising NW-SD-DE 110 kV Transmission Circuit as per test procedureRADS submitted BJ 24/08/07 | FALSE | Non-Critical
94425 | 11484 | 108495 | 2007-08-12 11:00 | 2007-08-17 18:00 | 2007-08-12 11:00 | 2007-08-17 12:30 | 7290 | E0140 | NN 22 kV A8 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:CB A852 racked out.WorkPlanned:Re-gas circuit breaker | FALSE | Undefined
94428 | 11486 | 108493 | 2007-08-11 11:00 | 2007-08-11 12:00 | 2007-08-11 10:12 | 2007-08-11 11:21 | 69 | E0436 | HA 220/110 kV T2 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:T2 Isolated and earthed as required.WorkPlanned:Inspect droppers to T2 following trip of T1 due to detached dropper. Note T1 to be returned to service before this outage commences. | FALSE | Non-Critical
94474 | 11538 | 108675 | 2007-09-08 08:45 | 2007-09-08 10:00 | 2007-09-08 08:45 | 2007-09-08 09:24 | 39 | E0255 | PM 220 kV A Bus | Bus | Forced | Secondary Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:"A" Bus isolated while replacing fuses. As per Anthony Januba.WorkPlanned:Replace all 16 Amp fuses on VT A797 "A" Bus. | FALSE | Undefined
94575 | 11671 | 108798 | 2007-10-10 08:00 | 2007-10-10 16:00 |  |  |  | E0251 | PM 110 kV A Bus | Bus | Forced | Secondary Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110kV A Bus to be opened off.All 110kV Load on B Bus for duration of Step 3WorkPlanned:During 110kV bus zone tests on PROMS 107019. All load to be transferred to 110kV B Bus to allow operation of 110kV Bus coupler B752 at Step 3. | FALSE | Undefined
94647 | 11748 | 108866 | 2007-10-29 09:30 | 2007-10-29 14:30 | 2007-10-29 08:58 | 2007-10-29 12:25 | 207 | E0718 | FA-MA 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Generator Shared | Completed | TRUE | 0 | TRUE |  | Isolation Points:FA-MA 110 kV Transmission Circuit isolatedFA-RB-QT 110 kV Transmission Circuit IsolatedRosebery Disconnector A129 to be closedHydro operator at Newton Pump Station requestedWorkPlanned:Maintain 110 kV transfer Disconnector PT129Re scheduled maintenance with Hydro Tasmania agreed Mackintosh P/S shutdown | FALSE | Non-Critical
94648 | 11748 | 108866 | 2007-10-29 09:30 | 2007-10-29 14:30 | 2007-10-29 08:58 | 2007-10-29 12:25 | 207 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Generator Shared | Completed | TRUE | 0 | TRUE |  | Isolation Points:FA-MA 110 kV Transmission Circuit isolatedFA-RB-QT 110 kV Transmission Circuit IsolatedRosebery Disconnector A129 to be closedHydro operator at Newton Pump Station requestedWorkPlanned:Maintain 110 kV transfer Disconnector PT129Re scheduled maintenance with Hydro Tasmania agreed Mackintosh P/S shutdown | FALSE | Non-Critical
94692 | 11807 | 108919 | 2007-11-15 10:00 | 2007-11-15 14:00 | 2007-11-15 09:00 | 2007-11-15 10:06 | 66 | E0785 | QU 110/22 kV T1 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110 kV Circuit Breaker A152 Isolated and Earthed as requiredWorkPlanned:Top up Sf6 gas in 110 kV CB A152 inconjunction with advised Hellyer Mill maintenance Site contact Wayne Keygan Phone 64391155 | FALSE | Non-Critical
94701 | 11809 | 108909 | 2007-11-19 09:00 | 2007-11-19 16:00 | 2007-11-19 10:30 | 2007-11-19 14:00 | 209 | E0451 | KE 11 kV ST1 Station Service Transformer Circuit | Station Service Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Each Station Service Transformer will be isolated in turn Station service supplies shall be switched from ST1 to ST2 and back WorkPlanned:Reduce station voltage from 253 Volts to approximately 230 Volts | FALSE | Undefined
94702 | 11809 | 108909 | 2007-11-19 09:00 | 2007-11-19 16:00 |  |  |  | E1469 | KE 11 kV ST2 Station Service Transformer Circuit | Station Service Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Each Station Service Transformer will be isolated in turn Station service supplies shall be switched from ST1 to ST2 and back WorkPlanned:Reduce station voltage from 253 Volts to approximately 230 Volts | FALSE | Undefined
94748 | 11855 | 109076 | 2007-12-04 11:00 | 2007-12-04 15:00 | 2007-12-04 09:58 | 2007-12-04 14:18 | 260 | E0030 | CS-KI-KR 110 kV Transmission Circuit (changed to E1955) | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:CS-KI-KR 110 kV Transmission Circuit to be isolated, earthed and assurance issuedNoteKR to be fed from EL for this outageWorkPlanned:Replacement of broken insulators Tower T69 | FALSE | Non-Critical
94755 | 11874 | 109048 | 2007-12-11 09:00 | 2007-12-11 17:00 | 2007-12-11 08:50 | 2007-12-11 16:15 | 445 | E0538 | SH-FA 1 220 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:SH-FA 1 220 kV Transmission Circuit Isolated on PROMS 109046220 kV CT Y196 Isolated and Earthed as requiredWorkPlanned:Electrical Tests 220 kVB CT Y196 | FALSE | Critical
94756 | 11875 | 109047 | 2007-12-12 09:00 | 2007-12-12 17:00 | 2007-12-12 09:12 | 2007-12-12 14:31 | 318 | E0539 | SH-FA 2 220 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:SH-FA 2 220 kV Transmission Circuit Isolated220 kV CT J196 Isolated and Earthed as requiredWorkPlanned:Re test 220 kV CT J196 | FALSE | Critical
94765 | 11892 | 109021 | 2007-12-04 10:00 | 2007-12-04 14:00 | 2007-12-04 09:45 | 2007-12-04 13:06 | 201 | E1565 | BP-SB-ST 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Generator Request | Completed | TRUE | 0 | TRUE |  | Isolation Points:BP-SB-ST 110 kV Transmission Circuit Isolated and Earthed as requiredWorkPlanned:Repair of damaged conductor on BP-SB-ST 110 kV T/LSwitching to be coordinated with Nick Cole of R40's. Mob 0409 864 135 | FALSE | Undefined
94774 | 11914 | 108986 | 2007-11-27 08:00 | 2007-11-27 16:00 | 2007-11-27 07:22 | 2007-11-27 14:45 | 443 | E0587 | UL-EB 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:UL-EB 110 Kv Transmission Circuit Isolated and Earthed as required WorkPlanned:Repair damaged conductors by Installation of repair rods | FALSE | Non-Critical
94791 | 11929 | 108969 | 2007-11-19 07:30 | 2007-11-19 16:00 | 2007-11-19 06:45 | 2007-11-20 13:32 | 1847 | E1424 | HA 110/22 kV T4 Transformer Circuit | Transformer | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110/22 kv T4 isolated, D531 closed.Satendra has advised that the Casino load may be fed from Trevallyn 22 kV Bus through Hadspen 22 kV Bus upon loss of Hadspen T3Distribution operations (Tony Fenner)has arranged for load to be switched back to Trevallyn for this outage.WorkPlanned:Installation of CVI tapped insulators to connections of T4 22 kV cable termination within D552 switchgear section | FALSE | Non-Critical
94799 | 11940 | 108952 | 2007-11-22 12:00 | 2007-11-22 18:00 | 2007-11-22 06:40 | 2007-11-22 18:00 | 680 | E0664 | TE 110 kV A7 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110 kV B Bus Isolated and Earthed as required110 kV Bus Coupler Isolated and Earthed as requiredWorkPlanned:Clean insulators 110 kV B Bus and Bus Coupler A752Note: this outage only to proceed on completion of PROMS 108951 | FALSE | Undefined
94798 | 11940 | 108952 | 2007-11-22 12:00 | 2007-11-22 18:00 | 2007-11-22 06:40 | 2007-11-22 18:00 | 680 | E0663 | TE 110 kV B Bus | Bus | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110 kV B Bus Isolated and Earthed as required110 kV Bus Coupler Isolated and Earthed as requiredWorkPlanned:Clean insulators 110 kV B Bus and Bus Coupler A752Note: this outage only to proceed on completion of PROMS 108951 | FALSE | Undefined
94801 | 11941 | 108951 | 2007-11-22 07:00 | 2007-11-22 12:00 | 2007-11-22 06:40 | 2007-11-22 12:01 | 321 | E0666 | TE 110 kV BB429 Transfer Disconnector | Transfer Disconnector | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:GT-TE 2 110 kV Transmission Circuit Isolated and Earthed as requiredTemmco 110/22 kV F2 Furnace Transformer Circuit Isolated and Earthed as requiredWorkPlanned:Clean 110 kV B152 Bay equipment and transfer Disconnector BB429 during advise shutdown of Furnace 3 at Temmco. (Transformer T2) | FALSE | Undefined
94800 | 11941 | 108951 | 2007-11-22 07:00 | 2007-11-22 12:00 | 2007-11-22 06:40 | 2007-11-22 12:01 | 321 | E0514 | GT-TE 2 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:GT-TE 2 110 kV Transmission Circuit Isolated and Earthed as requiredTemmco 110/22 kV F2 Furnace Transformer Circuit Isolated and Earthed as requiredWorkPlanned:Clean 110 kV B152 Bay equipment and transfer Disconnector BB429 during advise shutdown of Furnace 3 at Temmco. (Transformer T2) | FALSE | Non-Critical
94855 | 12044 | 109255 | 2007-12-26 11:45 | 2007-12-28 16:00 | 2007-12-26 11:45 | 2007-12-26 17:02 | 317 | E0050 | CS 110 kV C2 Capacitor Circuit | Capacitor | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:As requiredWorkPlanned:Repair CB B652 closing spring fault. | FALSE | Non-Critical
89990 | 12188 | 109311 | 2008-01-10 20:00 | 2008-01-12 18:00 | 2008-01-10 20:00 | 2008-01-12 15:45 | 2625 | E0935 | UL 110 kV A Bus | Bus | Forced | Secondary Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Removal of trip linksWorkPlanned:Replacement of faulty protection relay A121B. | FALSE | Undefined
90036 | 12240 | 109458 | 2008-01-31 10:00 | 2008-01-31 14:00 | 2008-01-31 09:07 | 2008-01-31 09:44 | 37 | E0813 | RA 110/22 kV T1 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate RA 110/22 kV T1 Transformer Circuit, Earth as required.T2 is rated at 60MVA, load expected to be 45MVA.Local Area Risk Notice 1432 sent.Not to proceed with the forecast of thunder storms. RCCWorkPlanned:22kv Circuit Breaker A552 top up low SF6 gas levels. | FALSE | Non-Critical
90696 | 12754 | 109906 | 2008-03-06 09:00 | 2008-03-06 15:00 | 2008-03-06 09:29 | 2008-03-06 13:34 | 245 | E1392 | BU 110 kV C1 Capacitor Circuit | Capacitor | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110 kV Capacitor Bank C1 to be Ioslated and Earthed as requiredWorkPlanned:Perform tests on individual Capacitor Bank units as per RFW 1964/16 | FALSE | Non-Critical
90938 | 13005 | 110234 | 2008-04-30 09:00 | 2008-04-30 13:00 | 2008-04-30 09:14 | 2008-04-30 11:21 | 127 | E1565 | BP-SB-ST 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Generator Request | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate BP-SB-ST 110 kV Transmission Circuit, Earth as required.Aurora operator to issue assuance to Roaring 40's operator, Lance Lovell 0439 380 410Requested by Roaring 40'sWorkPlanned:Repairs of isolator stand off insulator | FALSE | Undefined
90950 | 13017 | 110217 | 2008-04-23 08:00 | 2008-04-23 12:00 | 2008-04-23 09:00 | 2008-04-23 13:10 | 250 | E0554 | SH-WV 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Primary plant SH-WV 110 kV Transmission Circuit to be isolated and earthed if required.proms 110198 to be in conjunction to this promsWorkPlanned:Install new droppers between transline and U129A | FALSE | Non-Critical
91121 | 13189 | 110288 | 2008-05-12 21:30 | 2008-05-13 16:00 | 2008-05-12 22:04 | 2008-05-13 16:33 | 1109 | E0382 | BU 110/22 kV T6 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:T6 to be isolated. F597 to be isolated and earthed.WorkPlanned:Replace white phase VT fuse on F597. | FALSE | Non-Critical
91208 | 13278 | 110427 | 2008-06-11 15:00 | 2008-06-11 18:00 | 2008-06-11 16:20 | 2008-06-11 17:52 | 92 | E0339 | LF 110 kV A Bus | Bus | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:All in service circuits to be on 110 kV B Bus as per comm doc LF D196-001WA-LF 2 is OOS on 110330WorkPlanned:Commission new CT D196 blue phase | FALSE | Undefined
91236 | 13310 | 110569 | 2008-07-11 09:00 | 2008-07-11 12:00 | 2008-07-11 09:08 | 2008-07-11 11:43 | 155 | E1545 | DP 110 kV B7 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate DP 110 kV B752 Bus Coupler Circuit, Earth as requiredWorkPlanned:Top up Low SF6 gas level in 110kv CB B752 | FALSE | Undefined
91349 | 13425 | 110605 | 2008-07-24 08:30 | 2008-07-24 15:00 | 2008-07-24 08:34 | 2008-07-24 15:07 | 393 | E0525 | SH 220 kV B Bus | Bus | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate SH 220 kV B Bus, Earth as required WorkPlanned:220kv Disconnector A729B - Remove currently bridged out phase and replace with new disconnector heads | FALSE | Undefined
91390 | 13479 | 110706 | 2008-08-12 09:00 | 2008-08-12 16:30 | 2008-08-12 09:49 | 2008-08-12 12:42 | 173 | E1545 | DP 110 kV B7 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110 kV Bus Coupler B752 Isolated as requiredCircuit Breaker B752 to be returned to service overnightWorkPlanned:Investigate and repair Sf6 gas leakage 110 kV Bus Coupler B752 | FALSE | Undefined
101809 | 13492 | 110692 | 2008-08-06 07:30 | 2008-08-25 16:00 | 2008-08-06 07:44 | 2008-08-22 12:07 | 23303 | E0267 | PO-PM 5 220 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Generator Request | Completed | TRUE | 0 | TRUE |  | Isolation Points:220 kV PO-PM 5 Transmission Circuit opened off to allow maintenance isolation at PoatinaCB B152 to be Open and TaggedWorkPlanned:Outage Hydro tasmania Poatina 5 Generator for maintenance on eGO43416 | FALSE | Non-Critical
185935 | 13552 | 110782 | 2008-08-26 18:28 | 2008-08-27 18:00 | 2008-08-26 18:28 | 2008-09-04 15:49 | 12801 | E0724 | NT 110/11 kV T2X Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | not included in ITOMS as this investigation was a result of the failure of a generation asset. Isolation Points:As requiredWorkPlanned:Find/Investigate/repair faulty Hardware | FALSE | Non-Critical
185936 | 13552 | 110782 | 2008-08-26 18:28 | 2008-08-27 18:00 | 2008-08-26 18:28 | 2008-09-04 15:49 | 12801 | E1023 | NT 11 kV ST2X Station Service Transformer Circuit | Station Service Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | not included in ITOMS as this investigation was a result of the failure of a generation asset. Isolation Points:As requiredWorkPlanned:Find/Investigate/repair faulty Hardware | FALSE | Undefined
91524 | 13651 | 110964 | 2008-09-27 05:30 | 2008-09-27 12:00 | 2008-09-27 05:40 | 2008-09-27 13:42 | 482 | E1565 | BP-SB-ST 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Generator Request | Completed | TRUE | 0 | TRUE |  | Isolation Points:BP-SB-ST 110 kV Transmission Circuit to be Isolated and Earthed as requiredWorkPlanned:Outage required by R40's to perform BP-SB-ST 110 kV Transmission Circuit maintenance utilising helicopter for access | FALSE | Undefined
91568 | 13698 | 110889 | 2008-09-18 12:00 | 2008-09-18 13:00 | 2008-09-18 12:00 | 2008-09-18 14:17 | 137 | E0550 | SH-PA Tee 110 kV Transmission Circuit Section | Transmission | Forced | HV Equipment Commissioning | Generator Shared | Completed | TRUE | 0 | TRUE |  | Isolation Points:SH-PA 110 kV Transmisssion Circuit to be Opened Off at Paloona Circuit Breaker C752 DC supply to be Isolated with DC Board DC1 outageWorkPlanned:Outage required to allow access to Paloona Power Station DC Board D1 for installation of new MCB for SH-PA T/L Protection upgrade projectOpen off 110 kV C752 with Paloona Generator shutdown (A752 and B752 Open) to access Station DC Board D1 In conjunction with PROMS 110852Outage coordinated with Hydro on eGO43623 | FALSE | Non-Critical
91584 | 13717 | 110868 | 2008-09-12 11:45 | 2008-09-26 16:00 | 2008-09-12 11:52 | 2008-09-26 12:49 | 20217 | E0267 | PO-PM 5 220 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Generator Request | Completed | TRUE | 0 | TRUE |  | Isolation Points:PO-PM No.5 Circuit Breaker B152 at Palmerston open & tagged for duration of repairs by Hydro.WorkPlanned:Repairs to Poatina #5 Generator. | FALSE | Non-Critical
92829 | 13725 | 110852 | 2008-09-18 12:00 | 2008-09-18 13:00 | 2008-09-18 12:00 | 2008-09-18 14:17 | 137 | E0770 | PA Tee - UL 110 kV Transmission Circuit Section | Transmission | Forced | HV Equipment Maintenance | Generator Request | Completed | TRUE | 0 | TRUE |  | Isolation Points:PA-UL 110 kV Transmission Circuit opened off at Paloona with Paloona Generator shutdown as per Hydro eGO 43623(rescheduled)WorkPlanned:Outage required to allow access to Paloona Power Station DC Board D1 for installation of new MCB for SH-PA T/L Protection upgrade project | FALSE | Non-Critical
91833 | 14143 | 110490 | 2008-07-03 08:30 | 2008-07-03 16:00 | 2008-07-03 09:00 | 2008-07-03 14:18 | 318 | E1465 | BU 110 kV H1 Circuit Breaker | Circuit Breaker | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110 kV CB H152 Isolated and Earthed as required.All other load transferred to A Bus, with BU-PL 110 kV T/L supplied via B Bus and Bypass H129DRadialising the NW cannot be performed with this configuration. As such this PROMS must not proceed if lightning is forecast.WorkPlanned:Take urgent Oil samples and minor maintenance 110 kV CB H152 | FALSE | Undefined
91861 | 14228 | 110273 | 2008-05-14 08:30 | 2008-05-14 15:00 | 2008-05-14 09:16 | 2008-05-14 15:30 | 374 | E0546 | SH 110 kV S1 Circuit Breaker | Circuit Breaker | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:S152 isolatedSH-PA to be on bypassvia S129D and B752WorkPlanned:Forced maintenance on S152 | FALSE | Undefined
91862 | 14232 | 110250 | 2008-05-08 08:00 | 2008-05-08 14:00 | 2008-05-08 08:55 | 2008-05-08 14:31 | 336 | E0545 | SH 110 kV R1 Circuit Breaker | Circuit Breaker | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate SH 110 kV R1 Circuit Breaker, earth as required.In conjunction with Sheffield PROMS 110188.WorkPlanned:Maintain 110kV circuit breaker R152 | FALSE | Undefined
91896 | 14287 | 110070 | 2008-03-28 09:00 | 2008-04-06 16:00 | 2008-03-28 07:58 | 2008-04-06 17:27 | 13529 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Primary plant CR 33 kV J2 Feeder Circuit isolated and earthed if requiredWorkPlanned:DNSP cable repairs | FALSE | Undefined
91932 | 14361 | 109727 | 2008-03-02 08:30 | 2008-03-02 16:00 | 2008-03-02 08:18 | 2008-03-02 15:23 | 426 | E0075 | CR 33 kV B2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:CR 33 kV B2 Feeder Circuit to be isolated and earthed as required.RAD number 101490WorkPlanned:DNSP repairs to overhead line | FALSE | Undefined
91984 | 14430 | 109443 | 2008-02-06 08:00 | 2008-02-07 16:00 | 2008-02-06 09:02 | 2008-02-07 15:07 | 1805 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:DNSP requests Feeder 22 (J252)isolated but not earthedWorkPlanned:Repairs to leaking oil filled cable.Note may be returned to service overnight if requiredrefer RADS 101149 | FALSE | Undefined
94900 | 14483 | 109253 | 2007-12-28 09:00 | 2007-12-28 15:00 | 2007-12-28 09:13 | 2007-12-28 11:10 | 117 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate only CR 33 kV J2 Feeder CircuitRequested by Aurora Networks on RADS 100890WorkPlanned:Distribution maintenance by Aurora Networks including Oil Filled cable pump up leaking section. | FALSE | Undefined
94907 | 14520 | 109148 | 2007-12-17 09:00 | 2007-12-17 15:00 | 2007-12-17 08:47 | 2007-12-17 14:56 | 369 | E0201 | SO 22 kV E2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:SO 22 kV E2 Feeder Circuit isolated and earthed as pe RADS 100556WorkPlanned:DNSP maintenance | FALSE | Undefined
94908 | 14521 | 109145 | 2007-12-06 07:00 | 2007-12-07 17:00 |  |  |  | E0197 | SO 22 kV A2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:A252 Open OffWorkPlanned:Repair CT fault Line side A252. | FALSE | Undefined
94909 | 14532 | 109104 | 2007-12-06 09:00 | 2007-12-06 12:00 | 2007-12-06 07:00 | 2007-12-06 08:30 | 90 | E0768 | NW 22 kV A2 Feeder Circuit | Feeder | Forced | HV Equipment Commissioning | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:22 kV Feeder Circuit Breaker A252 Isolated as requiredWorkPlanned:Aurora Distribution re commissioning Norwood Feeder 60 as per RADS 100700 | FALSE | Undefined
94912 | 14548 | 109061 | 2007-12-10 10:00 | 2007-12-12 16:00 | 2007-12-10 12:00 | 2007-12-10 20:54 | 534 | E1481 | RI 33 kV J2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:RI 33 kV J2 Feeder Circuit isolated but not earthedWorkPlanned:Upgrade existing AVR's hardware & software. Testing and commissioning the upgraded AVR's. Testing I/O points with Kirksway Place SCADA centre | FALSE | Undefined
94913 | 14549 | 109060 | 2007-12-05 14:00 | 2007-12-08 16:00 | 2007-12-05 14:00 | 2007-12-10 09:47 | 6947 | E1478 | RI 33 kV F2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:RI 33 kV F2 Feeder Circuit isolated but not earthedWorkPlanned:Upgrade existing AVR's hardware & software. Testing and commissioning the upgraded AVR's. Testing I/O points with Kirksway Place SCADA centre | FALSE | Undefined
94918 | 14574 | 108996 | 2007-11-21 12:11 | 2007-11-21 15:00 | 2007-11-21 12:15 | 2007-11-21 13:22 | 67 | E0151 | NN 22 kV K2 Feeder Circuit | Feeder | Forced | Secondary Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Feeder #39570, via K252WorkPlanned:Relace suspect relay K251/64 and test. | FALSE | Undefined
94919 | 14575 | 108985 | 2007-11-27 23:00 | 2007-11-27 23:45 | 2007-11-27 22:10 | 2007-11-28 00:51 | 161 | E0767 | NW 22 kV B2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:22 kV Circuit Breaker B252 Racked out, Feeder 61 Isolated and Earthed as requiredWorkPlanned:Aurora Feeder 61 required Isolated and Earthed as per RADS 100550 | FALSE | Undefined
94924 | 14582 | 108959 | 2007-11-15 09:00 | 2007-11-15 15:00 | 2007-11-15 08:49 | 2007-11-16 01:12 | 983 | E0913 | TR 22 kV U2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:22 kV Circuit Breaker U252 Isolated and Feeder Earthed as requiredWorkPlanned:Aurora Distribution to perform repairs on Feeder 39Feeder to be Isolated and Earthed as requiredRADS submitted Dist Ops Hobart | FALSE | Undefined
94931 | 14615 | 108850 | 2007-10-23 09:00 | 2007-10-23 15:00 | 2007-10-23 10:30 | 2007-10-23 13:00 | 150 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate CR 33 kV J2 Feeder Circuit.Ref RADS 100252WorkPlanned:Pump up oil filled cable and adjust alarms | FALSE | Undefined
94973 | 14727 | 108486 | 2007-08-23 13:00 | 2007-08-23 15:00 | 2007-08-23 13:00 | 2007-08-23 15:40 | 160 | E0947 | UL 22 kV E2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:CB E252 open and racked outFeeder live inWorkPlanned:Exchange existing 22 kV Circuit Breaker E252 with spare unitRADS submitted BJ 10/08/07 | FALSE | Undefined
94975 | 14765 | 108400 | 2007-08-03 12:00 | 2007-08-03 15:00 | 2007-08-03 09:50 | 2007-08-03 14:20 | 270 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate CR 33 kV J2 Feeder Circuit, earth if required.Requested by Aurora Networks.WorkPlanned:Distribution maintenance including pumping up Oil Filled Cable, by Aurora Networks. | FALSE | Undefined
94977 | 14777 | 108335 | 2007-08-06 09:00 | 2007-08-06 12:00 | 2007-08-06 08:57 | 2007-08-06 11:16 | 139 | E0820 | RA 22 kV C2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:22 kV Circuit Breaker C252 Open and racked outFeeder 3 load transferred in fieldRADS submitted BJ 23/07/07WorkPlanned:Top up SF6 Gas 22 kV Circuit Breaker C252 | FALSE | Undefined
94980 | 14786 | 108273 | 2007-07-24 12:00 | 2007-07-24 15:00 | 2007-07-24 13:15 | 2007-07-24 14:47 | 92 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate CR 33 kV J2 Feeder Circuit, earth if required.Requested by Aurora Networks.WorkPlanned:Distribution line maintenance including maintenance to oil filled cable by Aurora Networks. | FALSE | Undefined
94989 | 14805 | 108201 | 2007-07-10 09:00 | 2007-07-12 09:00 | 2007-07-10 07:46 | 2007-07-12 09:00 | 2955 | E1435 | HA 22 kV E2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate HA 22 kV K2 and E2 Feeder Circuits, earth if required.Requested by Aurora Networks.WorkPlanned:Distribution maintenance and repairs by Aurora Networks. | FALSE | Undefined
94990 | 14805 | 108201 | 2007-07-10 09:00 | 2007-07-12 09:00 | 2007-07-10 07:46 | 2007-07-12 09:00 | 2955 | E1444 | HA 22 kV K2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate HA 22 kV K2 and E2 Feeder Circuits, earth if required.Requested by Aurora Networks.WorkPlanned:Distribution maintenance and repairs by Aurora Networks. | FALSE | Undefined
94991 | 14806 | 108200 | 2007-07-16 09:30 | 2007-07-16 13:30 | 2007-07-16 09:19 | 2007-07-16 13:05 | 226 | E0556 | DE 22 kV B2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate DE 22 kV B2 Feeder Circuit, earth if required.Requested by Aurora Networks.WorkPlanned:Distribution line maintenance and repairs by Aurora Networks. | FALSE | Undefined
94992 | 14807 | 108199 | 2007-08-01 08:00 | 2007-08-01 15:00 | 2007-08-01 09:15 | 2007-08-01 10:34 | 80 | E0390 | BU 22 kV E2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate BU 22 kV E2 Feeder Circuit, earth if required.Requested by Aurora Networks.WorkPlanned:Distribution maintenance and repairs by Aurora Networks. | FALSE | Undefined
94993 | 14808 | 108197 | 2007-07-06 09:00 | 2007-07-06 15:00 | 2007-07-06 09:15 | 2007-07-06 15:52 | 397 | E0086 | CR 33 kV J2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate CR 33 kV J2 Feeder Circuit, earth if required.Requested by Aurora Networks.WorkPlanned:Distribution line maintenance by Aurora Networks including repairs to oil filled cable. | FALSE | Undefined
95012 | 14832 | 108144 | 2007-07-23 12:00 | 2007-07-23 15:00 | 2007-07-11 09:01 | 2007-07-11 16:37 | 456 | E0917 | TR 22 kV X2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:22 kV X2 Feeder Circuit Isolated and Earthed as requiredRADS submitted BJ 27/06/07WorkPlanned:22 kV Circuit Breaker X252 and E/Switch X231. Modify bus zone CT wiring to integrate CT switching relay that is driven by the status of the feeder earth switch. The earth switch will need to be operated to demonstrate correct operation of new relay. | FALSE | Undefined
95013 | 14833 | 108143 | 2007-07-11 09:00 | 2007-07-11 12:00 | 2007-07-11 09:01 | 2007-07-11 16:37 | 456 | E0912 | TR 22 kV T2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:22 kV T2 Feeder Circuit Isolated and Earthed as requiredRADS submitted BJ 27/06/07WorkPlanned:22 kV Circuit Breaker T252, Cable Earth Switch T231Modify bus zone CT wiring to integrate CT switching relay that is driven by the status of the feeder earth switch. The earth switch will need to be operated to demonstrate correct operation of new relay. | FALSE | Undefined
95014 | 14834 | 108142 | 2007-07-04 08:00 | 2007-07-04 13:00 | 2007-07-04 08:00 | 2007-07-04 12:39 | 279 | E0672 | TE 110 kV D4 Circuit Breaker | Circuit Breaker | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110 kv B Bus Isolated and Earthed110/22 kv Transformer TO4 Isolated and Earthed as requiredWorkPlanned:Opportune maintenance Disconnector D429B during advised outage of Temco Furnace 5 | FALSE | Undefined
92496 | 16818 | 111525 | 2008-12-11 12:30 | 2008-12-11 16:00 | 2008-12-11 11:34 | 2008-12-11 12:53 | 79 | E1549 | DP 22 kV C3 Capacitor Circuit | Capacitor | Forced | HV Equipment Maintenance | Transend | Completed | FALSE | 0 | TRUE |  | Isolation Points:22 kV Capacitor C3 to be Isolated and EarthedWorkPlanned:22 kV Capacitor C3 Bay Airconditioner servicing | FALSE | Undefined
95425 | 17054 | 111806 | 2009-01-28 05:30 | 2009-01-28 06:00 | 2009-01-28 05:39 | 2009-01-28 06:43 | 64 | E0728 | NH 11 kV A Bus | Bus | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:C252, D252, A852 & A552 open & tagged.Other isolations as required.WorkPlanned:Megger test earth bar.Operate B252 & rectify spring charge problem to allow isolation of faulted feeder. | FALSE | Undefined
95614 | 17258 | 112088 | 2009-02-14 09:30 | 2009-02-16 16:00 | 2009-02-14 09:30 | 2009-02-14 15:45 | 375 | E0517 | SH 110 kV A Bus | Bus | Forced | Secondary Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:As required by the on site personel.WorkPlanned:Investigate and repair the 110kV bus zone protection fail. | FALSE | Undefined
95615 | 17258 | 112088 | 2009-02-14 09:30 | 2009-02-16 16:00 | 2009-02-14 09:30 | 2009-02-14 15:45 | 375 | E0519 | SH 110 kV B Bus | Bus | Forced | Secondary Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:As required by the on site personel.WorkPlanned:Investigate and repair the 110kV bus zone protection fail. | FALSE | Undefined
95719 | 17345 | 111994 | 2009-02-19 09:00 | 2009-02-19 14:00 | 2009-02-19 09:41 | 2009-02-19 12:40 | 179 | E0901 | TR 22 kV B2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate TR 22kV V2 Feeder Circuit, earth as required.RADS 105785 submitted.WorkPlanned:Isolate Circuit Breaker V252, earth as required. | FALSE | Undefined
102197 | 17605 | 112438 | 2009-03-20 16:30 | 2009-03-25 16:30 | 2009-03-20 16:48 | 2009-03-25 13:58 | 7030 | E0319 | BY 6.6 kV B3 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | MI | Completed | TRUE | 0 | TRUE |  | Isolation Points:Boyer 6.6kV No 2 feeder B352 isolated and earthed.WorkPlanned:Boyer Mill Site Electrical Engineer Lee Johnson requests clearance on Boyer 6.6kV No 2 feeder B352 to allow for cable repairs within the Boyer Mill. | FALSE | Undefined
107213 | 17611 | 112427 | 2009-03-23 18:00 | 2009-03-24 16:00 | 2009-03-23 18:00 | 2009-03-24 18:12 | 1452 | E1442 | BB-BE-GT 1 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Commissioning | Generator Shared | Completed | TRUE | 0 | TRUE |  | Isolation Points:BB-BE-GT 1 110 kV Transmission Circuit Isolated and Earthed as requiredIsolation and Earthing to be co ordinated with AETV Power BB3 and Bell Bay Power Station operatorsThis outage will follow on from PROMS 112369WorkPlanned:Installation of steel structures for 110kV primary equipment associated with George Town H bay upgrade.eGO 112427 refers for generator outage | TRUE | Non-Critical
102202 | 17613 | 112425 | 2009-03-29 09:30 | 2009-03-29 16:00 | 2009-03-29 11:28 | 2009-03-29 19:45 | 497 | E0534 | SH 220/110 kV T1 Transformer Circuit | Transformer | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:SH 220/110 kV Transformer T1 Isolated and Earthed as requiredSH Transformer Contingency Arming Scheme to be 'in service'WorkPlanned:Investigate false trip of 220/110 kV Transformer T1 | TRUE | Non-Critical
102267 | 17679 | 112348 | 2009-03-12 09:30 | 2009-03-12 11:30 | 2009-03-12 08:59 | 2009-03-12 11:36 | 157 | E0703 | FA 110 kV B Bus | Bus | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Disconnectors B729A and B729BWorkPlanned:Top up SF6 levels of Circuit Breaker B752. | FALSE | Undefined
102268 | 17679 | 112348 | 2009-03-12 09:30 | 2009-03-12 11:30 | 2009-03-12 08:59 | 2009-03-12 11:36 | 157 | E0707 | FA 110 kV B7 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Disconnectors B729A and B729BWorkPlanned:Top up SF6 levels of Circuit Breaker B752. | FALSE | Undefined
107215 | 17741 | 112567 | 2009-04-16 07:00 | 2009-04-16 18:00 | 2009-04-16 08:13 | 2009-04-16 17:11 | 538 | E1442 | BB-BE-GT 1 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Commissioning | Generator Shared | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate BB-BE-GT 1 110 kV Transmission Circuit, earth as requiredIsolate BB-BE-GT 2 110 kV Transmission Circuit, earth as requiredNotified and Confirmed Bell Bay Power and AETV TVPP Generation will be out of service for outageWorkPlanned:Erect new landing gantry at the I & H Bays inside George Town switchyard. eGO 44197 refers. | TRUE | Non-Critical
107216 | 17741 | 112567 | 2009-04-16 07:00 | 2009-04-16 18:00 | 2009-04-16 08:13 | 2009-04-16 17:11 | 538 | E1443 | BB-BE-GT 2 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Commissioning | Generator Shared | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate BB-BE-GT 1 110 kV Transmission Circuit, earth as requiredIsolate BB-BE-GT 2 110 kV Transmission Circuit, earth as requiredNotified and Confirmed Bell Bay Power and AETV TVPP Generation will be out of service for outageWorkPlanned:Erect new landing gantry at the I & H Bays inside George Town switchyard. eGO 44197 refers. | TRUE | Non-Critical
102924 | 17747 | 112561 | 2009-04-21 08:00 | 2009-04-21 16:00 | 2009-04-21 08:43 | 2009-04-21 11:27 | 164 | E0573 | EB 11 kV L2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate EB 11 kV L252 Feeder Circuit, earth as requiredWorkPlanned:11kV CB L252 maintenance (APPM feeder 17) | FALSE | Undefined
104595 | 18013 | 112742 | 2009-05-15 11:00 | 2009-05-15 16:00 | 2009-05-15 12:56 | 2009-05-15 15:47 | 171 | E0525 | SH 220 kV B Bus | Bus | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | not included in ITOMS as this is a routine maintenance task. Isolation Points:220 kV B Bus Isolated and Earthed as requiredWorkPlanned:Maintain 220 kV Disconnector L129B in conjunction with outage of SH-GT 2 220 kV Transmission Circuit on PROMS 112743 | FALSE | Undefined
105011 | 18035 | 112818 | 2009-05-20 08:00 | 2009-05-20 15:00 | 2009-05-20 08:20 | 2009-05-20 14:44 | 384 | E0126 | NN 110 kV A Bus | Bus | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate NN 110 kV A Bus, earth as required. WorkPlanned:Investigate & repair high resistance joint on Disconnector A729A. | FALSE | Undefined
139400 | 18359 | 113252 | 2009-07-06 09:00 | 2009-07-06 16:00 | 2009-07-06 10:22 | 2009-07-06 18:03 | 461 | E0184 | TU 22 kV XC2 Feeder Circuit | Feeder | Forced | Secondary Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate CB C252, earth as required.Aurora feeder to remain in service via TU 22 kV By-Pass Bus and CB S252.WorkPlanned:C252 Protection wiring modifications to swap protection relays with B252. | FALSE | Undefined
200323 | 18361 | 113250 | 2009-06-24 10:45 | 2009-06-25 16:00 | 2009-06-24 08:00 | 2009-06-25 16:00 | 1920 | E0123 | CS 11 kV Y2 Feeder Circuit | Feeder | Forced | HV Equipment Commissioning | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:Switch feeder Y252 circuit as requested by Aurora Distribution Operations on SWOPO 106376WorkPlanned:Aurora to commission new feederThis PROMS takes over from 113234 Aurora to commission new feederThis PROMS takes over from 113234 | FALSE | Undefined
106003 | 18363 | 113248 | 2009-06-25 09:00 | 2009-06-30 16:00 | 2009-06-25 09:59 | 2009-06-25 14:03 | 244 | E0459 | KR 11 kV B2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate KR 11kV B2 Feeder Circuit, earth as required.Please note this CB is a spare.WorkPlanned:Repair / replace faulty motor | FALSE | Undefined
108028 | 18659 | 113462 | 2009-07-31 08:00 | 2009-07-31 12:30 | 2009-07-31 14:42 | 2009-07-31 17:32 | 170 | E0916 | TR 22 kV W2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate TR 22 kV W252 Feeder Circuit, earth as requiredWorkPlanned:Investigate damage to 22kv HV cable and repair as required | FALSE | Undefined
109964 | 18858 | 113676 | 2009-09-16 09:00 | 2009-09-16 15:00 | 2009-09-16 09:31 | 2009-09-16 15:06 | 335 | E0343 | LF 33 kV F2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:LF 33 kV F2 Feeder Circuit to be isolated and earthedWorkPlanned:Cable sheath repair | FALSE | Undefined
110278 | 18872 | 113716 | 2009-09-24 08:00 | 2009-09-24 09:00 | 2009-09-24 14:00 | 2009-09-24 15:00 | 60 | E1719 | MY 110 kV A Bus | Bus | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate (future) 110kV "A" Bay Transmission circuit earth as required.Isolations required 110kV disconnectors A129A & A129C - openedWorkPlanned:Installation of earthing stirrups on the new 110kV A Bay | TRUE | Not In Wasp
198995 | 18889 | 113693 | 2009-09-14 07:30 | 2009-11-30 16:00 | 2009-10-08 11:35 | 2009-11-30 16:00 | 76585 | E0328 | BY 6.6 kV G3 Feeder Circuit | Feeder | Forced | HV Equipment Commissioning | MI | Completed | TRUE | 0 | TRUE |  | Isolation Points:1; Isolate BY 6.6 kV G3 Feeder Circuit,and rack out and earth as required.2: Commission new feeder cable and protection upgrades installation associated with 'G-Bay' in accordance with energising sequence REF.No. BY G352WorkPlanned:Instal new protection CT's in G Bay associated with new feeder cable - If Required.New feeder cable to be terminated and earth at field end prior to any work being carried out in the SubstationEarths to be removed for testing purposes only.Test feeder cable and Fit Terminated Feeder cable to switchgearProtection Work - If requiredNew protection panel & relays maybe required to be installed, all supplied for the G bay relays from G bay.THIS PROMS IS TO REPLACE PROMS #113066 Instal new protection CT's in G Bay associated with new feeder cable - If Required.New feeder cable to be terminated and earth at field end prior to any work being carried out in the SubstationEarths to be removed for testing purposes only.Test feeder cable and Fit Terminated Feeder cable to switchgearProtection Work - If requiredNew protection panel & relays maybe required to be installed, all supplied for the G bay relays from G bay.THIS PROMS IS TO REPLACE PROMS #113066 | FALSE | Undefined
110775 | 18891 | 113691 | 2009-09-14 07:30 | 2009-11-30 16:00 | 2009-09-25 07:30 | 2009-10-09 16:34 | 20704 | E0329 | BY 6.6 kV H3 Feeder Circuit | Feeder | Forced | HV Equipment Commissioning | MI | Completed | TRUE | 0 | TRUE |  | Isolation Points:1: Isolate BY 6.6 kV H3 Feeder Circuit,and rack out and earth as required.2: Commission new feeder cable and protection upgrades installation associated with 'H-Bay' in accordance with energising sequence REF.No. BY H352WorkPlanned:Instal new protection CT's in H Bay associated with new feeder cable - If Required.New feeder cable to be terminated and earth at field end prior to any work being carried out in the SubstationEarths to be removed for testing purposes only.Test feeder cable and Fit Terminated Feeder cable to switchgearProtection Work - If requiredNew protection relays maybe required to be installed, all supplied for the H bay relays from H bay. | FALSE | Undefined
110622 | 18913 | 113723 | 2009-09-24 09:00 | 2009-10-10 16:00 | 2009-09-24 11:15 | 2009-10-05 15:31 | 16096 | E0106 | CS 11 kV F2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate CS 11 kV F2 Feeder Circuit, earth as required.RADS submitted requesting CS 11 kV F2 Feeder Circuit to be de-energised and earthed back into Substation.WorkPlanned:Investigate and repair circuit breaker after fail to operate. | FALSE | Undefined
109972 | 18914 | 113722 | 2009-09-16 07:30 | 2009-09-18 16:20 | 2009-09-16 07:45 | 2009-09-18 16:19 | 3394 | E0484 | GT 110/22 kV T5 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:110/22 kV TF GT-T5WorkPlanned:Isolate & Earth Transformer T5 to allow for internal inspections. | FALSE | Non-Critical
109973 | 18917 | 113718 | 2009-09-17 10:00 | 2009-09-17 12:00 | 2009-09-17 10:39 | 2009-09-17 11:16 | 37 | E0324 | BY 6.6 kV E3 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | MI | Completed | TRUE | 0 | TRUE |  | Isolation Points:E3 Feeder Circuit (Norske Skog Feeder 5) isolated and earthed. Operational earthing applied as required to access to Feeder 5 "cable joint shed".WorkPlanned:The purpose of the outage is to enable the front cover to be taken off the F5 cable joint shed (inside the Transend’s switchyard) so Norkse Skog’s contractor can inspect the cables inside. | FALSE | Undefined
110641 | 19073 | 113860 | 2009-10-06 10:30 | 2009-10-06 11:30 | 2009-10-06 10:33 | 2009-10-06 11:19 | 46 | E0511 | GT-CO 5 220 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:GT-CO 5 220 kV Transmission Circuit IsolatedWorkPlanned:Forced outage to top up Sf6 gas to 220 kV Circuit Breaker G152 at George Town sub | FALSE | Non-Critical
199229 | 19234 | 113956 | 2009-10-20 20:54 | 2009-10-21 18:00 | 2009-10-20 20:54 | 2009-10-21 18:00 | 1266 | E0061 | CR 110 kV D7 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:as requiredWorkPlanned:Investigate Bus Zone Bias alarm present at completion of replacement of 110kV CT D796A on Proms 113843. Carry out non-intrusive remedial works to CT D796A. Investigate Bus Zone Bias alarm present at completion of replacement of 110kV CT D796A on Proms 113843. Carry out non-intrusive remedial works to CT D796A. | FALSE | Undefined
112432 | 19496 | 114107 | 2009-11-20 10:30 | 2009-12-04 16:00 | 2009-12-02 09:15 | 2009-12-02 10:32 | 77 | E1681 | RA 22 kV C1 Capacitor Circuit | Capacitor | Forced | HV Equipment Commissioning | Transend | Completed | FALSE | 0 | TRUE |  | Isolation Points:Isolate RA 22 kV C1 Capacitor Circuit(CB A652 Opened), earth as requiredWorkPlanned:Change over of white phase reactor with new replacement, and testing of new one once installed | FALSE | Undefined
112673 | 19613 | 114204 | 2009-12-09 13:30 | 2009-12-09 14:30 | 2009-12-09 14:10 | 2009-12-09 14:26 | 16 | E0856 | RB 110/44 kV T1 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:T1 to be opned off only.WorkPlanned:T1 to be opened off to allow exercising of A429 which is not completely closed. | FALSE | Non-Critical
113149 | 19715 | 114308 | 2010-01-01 12:30 | 2010-01-01 18:00 | 2010-01-01 13:29 | 2010-01-01 16:48 | 199 | E0068 | CR 110/33 kV T4 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:T4 opened off only.WorkPlanned:Replace air compressor on D452. | FALSE | Non-Critical
113158 | 19733 | 114290 | 2009-12-21 16:44 | 2009-12-21 17:15 | 2009-12-21 16:44 | 2009-12-21 17:03 | 19 | E0286 | PO-PM 1 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Generator Request | Completed | TRUE | 0 | TRUE |  | Isolation Points:PO-PM 1 110 kV transmission opened off & taggedWorkPlanned:Isolate oil leak on generator transformer bucholz | FALSE | Non-Critical
113159 | 19734 | 114289 | 2009-12-22 10:00 | 2009-12-22 16:00 | 2009-12-22 10:00 | 2009-12-22 15:07 | 307 | E0505 | GT 220 kV C2 Capacitor Circuit | Capacitor | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:GT 220 kV C2 Capacitor Circuit Isolated and Earthed as requiredWorkPlanned:Repair detected Hot Joint 220 kV Capacitor bank | FALSE | Non-Critical
115992 | 19931 | 114628 | 2010-01-15 09:00 | 2010-03-11 17:00 | 2010-01-15 09:36 | 2010-03-11 18:03 | 79707 | E0208 | RI 110 kV C1 Capacitor Circuit | Capacitor | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate RI 110 kV C1 Capacitor Circuit.Earth cable side of J631B and earth J652 on J631 side.No earths to Capacitor cans required unless requested by PIC.WorkPlanned:General civil works for 110kV Capacitor Bank C3 & C4 installation project.Erection of Supports and Equipment for safety clearance (electrical install).No connections to in service equipment | TRUE | Non-Critical
115761 | 20143 | 114785 | 2010-02-01 14:20 | 2010-02-01 18:00 | 2010-02-01 14:20 | 2010-02-01 21:31 | 431 | E0250 | LI-WY 220 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | NEMMCO | Completed | TRUE | 0 | TRUE |  | refer D11/3796 - Isolation Points:NilWorkPlanned:De-energised at the request of Tasmanian Fire Service to allow machinery access to clear break near line 507, T6 (LI-WY T/L). | FALSE | Non-Critical
199072 | 20621 | 115186 | 2010-03-23 15:00 | 2010-03-24 16:00 | 2010-03-23 15:00 | 2010-03-24 16:00 | 1500 | E0691 | TR 22 kV A8 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:CB to be racked out for repairs or replacement, till testing in situe is required.WorkPlanned:Repair or replace the faulty A852 CB. Repair or replace the faulty A852 CB. | FALSE | Undefined
116695 | 20648 | 115227 | 2010-03-31 06:00 | 2010-04-01 16:00 | 2010-03-31 08:45 | 2010-04-01 16:05 | 1880 | E0834 | RK 11 kV A8 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  |  | FALSE | Undefined
120354 | 21134 | 115595 | 2010-05-28 14:45 | 2010-05-30 18:00 | 2010-05-28 14:45 | 2010-05-29 15:21 | 1476 | E0522 | SH 220 kV A Bus | Bus | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:220 kV A Bus Isolated and Earthed as requiredWorkPlanned:1/ Replace all 220 kV A Bus terminal and support hardware, utilising Live Line work methods2/ Remove O/H Earth wires between T10 and T11.*Replaces PROMS 115197 which was accidently marked Complete | TRUE | Undefined
121496 | 21342 | 115821 | 2010-07-01 10:58 | 2010-07-01 18:00 | 2010-07-01 10:58 | 2010-07-01 15:07 | 249 | E0776 | PL 110/22 kV T1 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:BU-PL 110kV T/L will need to be open at Pt Latta end.110kV A bus and transformer T1 will need to be OOS for isolation.WorkPlanned:Repair disconnector A429A | FALSE | Non-Critical
121494 | 21342 | 115821 | 2010-07-01 10:58 | 2010-07-01 18:00 | 2010-07-01 12:39 | 2010-07-01 15:05 | 146 | E0401 | BU-PL 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:BU-PL 110kV T/L will need to be open at Pt Latta end.110kV A bus and transformer T1 will need to be OOS for isolation.WorkPlanned:Repair disconnector A429A | FALSE | Non-Critical
121495 | 21342 | 115821 | 2010-07-01 10:58 | 2010-07-01 18:00 | 2010-07-01 12:39 | 2010-07-01 15:05 | 146 | E0773 | PL 110 kV A Bus | Bus | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:BU-PL 110kV T/L will need to be open at Pt Latta end.110kV A bus and transformer T1 will need to be OOS for isolation.WorkPlanned:Repair disconnector A429A | FALSE | Undefined
125488 | 21864 | 116333 | 2010-09-18 13:00 | 2010-09-18 17:00 | 2010-09-18 13:48 | 2010-09-18 14:12 | 24 | E1074 | PM 22 kV F2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:F252 opened and racked out.Line earthed as required by Aurora.WorkPlanned:Isolate feeder No.1 for Aurora line work | FALSE | Undefined
137103 | 21972 | 116383 | 2010-09-29 08:30 | 2010-09-29 12:00 | 2010-09-29 08:29 | 2010-09-29 12:00 | 211 | E0166 | TA 110 kV 7 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:NilWorkPlanned:752 and F152 required open due to low air alarms as they will not open if they go into lockout. D252 at Tungatinah which supplies station service to Tarraleah is open due to a fault. | FALSE | Undefined
137102 | 21972 | 116383 | 2010-09-29 08:30 | 2010-09-29 12:00 | 2010-09-29 08:29 | 2010-09-29 12:00 | 211 | E0164 | TA-TU 2 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:NilWorkPlanned:752 and F152 required open due to low air alarms as they will not open if they go into lockout. D252 at Tungatinah which supplies station service to Tarraleah is open due to a fault. | FALSE | Critical
127406 | 22231 | 116643 | 2010-11-12 17:23 | 2010-11-13 17:00 | 2010-11-12 17:23 | 2010-11-12 21:05 | 222 | E1748 | WA 110 kV D7 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:NilWorkPlanned:Investigate and rectify issue with D752 closing | FALSE | Not In Wasp
131062 | 22320 | 116741 | 2010-11-30 16:00 | 2010-11-30 17:00 | 2010-11-30 16:02 | 2010-11-30 16:25 | 23 | E0171 | TU-LE-WA 1 110 kV Transmission Circuit (Changed to E1957) | Transmission | Forced | Secondary Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:TU-LE-WA1 110kV Transmission Circuit Open All EndsTU-LE-WA2 110kV Transmission Circuit Open All EndsWorkPlanned:Replace Faulty communications equipment | FALSE | Critical
186035 | 22320 | 116741 | 2010-11-30 16:00 | 2010-11-30 17:00 | 2010-11-30 16:02 | 2010-11-30 16:25 | 23 | E0173 | TU-WA 2 110 kV Transmission Circuit | Transmission | Forced | Secondary Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:TU-LE-WA1 110kV Transmission Circuit Open All EndsTU-LE-WA2 110kV Transmission Circuit Open All EndsWorkPlanned:Replace Faulty communications equipment | FALSE | Critical
128285 | 22391 | 116778 | 2010-12-05 12:08 | 2010-12-06 16:00 | 2010-12-05 13:08 | 2010-12-06 16:35 | 1647 | E1573 | DP 22 kV M2 Feeder Circuit | Feeder | Forced | Secondary Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:M252 opened off and isolated.WorkPlanned:Investigate M299 protection relay failure. | FALSE | Undefined
132171 | 23032 | 117432 | 2011-02-11 12:00 | 2011-02-11 18:00 | 2011-02-11 12:52 | 2011-02-11 15:10 | 138 | E0326 | BY 6.6 kV F3 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | MI | Completed | TRUE | 0 | TRUE |  | Isolation Points:F352 Isolated and earthedWorkPlanned:Isolate F352 to allow Norske Skog to inspect their plantr connected to the feeder | FALSE | Undefined
138145 | 24113 | 118418 | 2011-06-29 09:00 | 2011-06-29 15:00 | 2011-06-29 10:53 | 2011-06-29 16:07 | 314 | E0836 | RK 11 kV B2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:RK 11 kV B2 Feeder Circuit and RK 11 kV H2 Feeder Circuit are to be opened off only.WorkPlanned:To enable PD testing on T2 these feeders are required opened off to stop possible stray inputs. | FALSE | Undefined
138146 | 24113 | 118418 | 2011-06-29 09:00 | 2011-06-29 15:00 | 2011-06-29 10:53 | 2011-06-29 16:07 | 314 | E0843 | RK 11 kV H2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:RK 11 kV B2 Feeder Circuit and RK 11 kV H2 Feeder Circuit are to be opened off only.WorkPlanned:To enable PD testing on T2 these feeders are required opened off to stop possible stray inputs. | FALSE | Undefined
138154 | 24127 | 118400 | 2011-06-24 09:00 | 2011-06-24 11:00 | 2011-06-24 09:15 | 2011-06-24 11:13 | 118 | E0513 | GT-TE 1 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:GT-TE 1 110 kV Transmission Circuit IsolatedWorkPlanned:Top-up SF6 gas on 110kV CT TE-A196A.TEMCO aware of outage requirement | FALSE | Non-Critical
142439 | 24542 | 118798 | 2011-08-11 12:30 | 2011-08-11 14:30 | 2011-08-11 13:53 | 2011-08-11 16:03 | 130 | E0646 | TR-MY 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:TR-MY 110 kV Transmission Circuit Isolated and EarthedWorkPlanned:Investigate and repair loose thermo couple wire on Pole 5 TR-MY cable circuit | FALSE | Non-Critical
142951 | 24620 | 118845 | 2011-08-17 23:00 | 2011-08-18 16:00 | 2011-08-17 23:00 | 2011-08-18 13:20 | 860 | E0405 | BU 22 kV A8 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:22kV circuit Breaker A852 racked out and isolated as requiredWorkPlanned:Investigate fail to close on 22kV circuit Breaker A852 | FALSE | Undefined
143890 | 24660 | 118942 | 2011-08-30 10:00 | 2011-08-30 13:00 | 2011-08-30 11:15 | 2011-08-30 13:37 | 142 | E0939 | UL 110/22 kV T2 Transformer Circuit | Transformer | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:UL 110/22 kV T2 Transformer Circuit IsolatedRequires A729B and B129B Open and isolatedWorkPlanned:Outage of Transformer T2 for Safety work Clearance to draw in and terminate OPGW utilising helicopter | TRUE | Non-Critical
143891 | 24660 | 118942 | 2011-09-01 09:00 | 2011-09-01 12:00 | 2011-09-01 08:01 | 2011-09-01 12:52 | 291 | E0939 | UL 110/22 kV T2 Transformer Circuit | Transformer | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:UL 110/22 kV T2 Transformer Circuit IsolatedRequires A729B and B129B Open and isolatedWorkPlanned:Outage of Transformer T2 for Safety work Clearance to draw in and terminate OPGW utilising helicopter | TRUE | Non-Critical
145079 | 24727 | 119064 | 2011-09-13 09:00 | 2011-09-13 16:30 | 2011-09-13 09:22 | 2011-09-14 11:57 | 1595 | E0342 | LF 33 kV G2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:In conjunction with SWOP 36679WorkPlanned:To Isolate and Earth 33kV Circuit Breaker G252 feeder 25307 for Geilston Bay Zone Transformer T1 Repairs | FALSE | Undefined
180203 | 24834 | 119113 | 2011-09-19 06:49 | 2011-09-20 18:00 | 2011-09-19 10:18 | 2011-09-20 13:26 | 1628 | E0722 | NT 110 kV XBus | Bus | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:N/AWorkPlanned:Investigate Loss of Supply to Newton substation.Suspect T2 Buchholz Trip | FALSE | Undefined
180204 | 24834 | 119113 | 2011-09-19 06:49 | 2011-09-20 18:00 | 2011-09-19 06:49 | 2011-09-20 13:26 | 1837 | E0724 | NT 110/11 kV T2X Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:N/AWorkPlanned:Investigate Loss of Supply to Newton substation.Suspect T2 Buchholz Trip | FALSE | Non-Critical
148302 | 25129 | 119385 | 2011-11-21 08:30 | 2011-11-21 16:30 | 2011-11-21 09:02 | 2011-11-21 15:26 | 384 | E0362 | KI 11 kV H2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate KI 11 kV H2 Feeder Circuit, earth as required.Circuitbreaker H252 Kingston sub controlling feeder 258 Isolated and EarthedWorkPlanned:Commission new Ground Mounted Substation | FALSE | Undefined
148337 | 25194 | 119461 | 2011-11-24 13:00 | 2011-11-24 16:00 | 2011-11-24 13:05 | 2011-11-24 13:58 | 53 | E0538 | SH-FA 1 220 kV Transmission Circuit | Transmission | Forced | Secondary Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Farrell Bus Zone B 220 kV, Bus zone A 220 is still in service.Nil Primary isolationsWorkPlanned:repair broken wire on SH-FA #1 T/L CT H196 | FALSE | Critical
149666 | 25346 | 119564 | 2011-12-23 07:00 | 2011-12-23 10:00 | 2011-12-23 07:15 | 2011-12-23 10:10 | 175 | E0326 | BY 6.6 kV F3 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | MI | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate BY 6.6 kV F3 Feeder Circuit, earth as required.WorkPlanned:inspect the incomer cable connections at the TMP2 plant | FALSE | Undefined
150047 | 25408 | 119626 | 2012-01-08 15:00 | 2012-01-09 15:00 | 2012-01-08 18:07 | 2012-01-09 18:58 | 1491 | E0259 | PM-HA 1 220 kV Transmission Circuit | Transmission | Forced | Secondary Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:K187/T187 Transline differential protection. WorkPlanned:Fix K187/T187 Protection communications failure. Distance Protection and Back-up Overcurrent Protection still in service. | FALSE | Critical
151882 | 25483 | 119754 | 2012-02-01 08:00 | 2012-02-01 11:00 | 2012-02-01 09:17 | 2012-02-01 10:34 | 77 | E0513 | GT-TE 1 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate and earth GT-TE 1 110 kV Transmission Circuit as required WorkPlanned:Top up SF6 gas 110kV CT A196A | FALSE | Non-Critical
151898 | 25516 | 119712 | 2012-01-30 14:00 | 2012-01-30 17:00 | 2012-01-30 14:05 | 2012-01-30 16:55 | 170 | E0163 | TA-TU 1 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Commissioning | Generator Shared | Completed | TRUE | 0 | TRUE |  | Isolation Points:Tarraleah end of the TA-MB 110 kV Transmission Circuit and the TA-TU 1 110 kV Transmission Circuit and Bus Coupler 752 to be opened prior to new Hydro CB A452 being energisedWorkPlanned: Energise new 110 kV CB A452 for first time and existing Hydro T1 transformer via TA-NN 1 110 kV Transmission Circuit CB D152 at New Norfolk | TRUE | Critical
151896 | 25516 | 119712 | 2012-01-30 14:00 | 2012-01-30 17:00 | 2012-01-30 14:05 | 2012-01-30 16:55 | 170 | E0138 | TA-NN 1 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Commissioning | Generator Shared | Completed | TRUE | 0 | TRUE |  | Isolation Points:Tarraleah end of the TA-MB 110 kV Transmission Circuit and the TA-TU 1 110 kV Transmission Circuit and Bus Coupler 752 to be opened prior to new Hydro CB A452 being energisedWorkPlanned: Energise new 110 kV CB A452 for first time and existing Hydro T1 transformer via TA-NN 1 110 kV Transmission Circuit CB D152 at New Norfolk | TRUE | Critical
151897 | 25516 | 119712 | 2012-01-30 14:00 | 2012-01-30 17:00 | 2012-01-30 14:05 | 2012-01-30 16:55 | 170 | E0161 | TA-MB 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Commissioning | Generator Shared | Completed | TRUE | 0 | TRUE |  | Isolation Points:Tarraleah end of the TA-MB 110 kV Transmission Circuit and the TA-TU 1 110 kV Transmission Circuit and Bus Coupler 752 to be opened prior to new Hydro CB A452 being energisedWorkPlanned: Energise new 110 kV CB A452 for first time and existing Hydro T1 transformer via TA-NN 1 110 kV Transmission Circuit CB D152 at New Norfolk | TRUE | Non-Critical
151899 | 25516 | 119712 | 2012-01-30 14:00 | 2012-01-30 17:00 | 2012-01-30 14:05 | 2012-01-30 16:55 | 170 | E0166 | TA 110 kV 7 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Commissioning | Generator Shared | Completed | TRUE | 0 | TRUE |  | Isolation Points:Tarraleah end of the TA-MB 110 kV Transmission Circuit and the TA-TU 1 110 kV Transmission Circuit and Bus Coupler 752 to be opened prior to new Hydro CB A452 being energisedWorkPlanned: Energise new 110 kV CB A452 for first time and existing Hydro T1 transformer via TA-NN 1 110 kV Transmission Circuit CB D152 at New Norfolk | TRUE | Undefined
152319 | 25631 | 119804 | 2012-02-14 10:00 | 2012-02-14 14:00 | 2012-02-14 11:25 | 2012-02-14 13:18 | 113 | E0164 | TA-TU 2 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Commissioning | Generator Shared | Completed | TRUE | 0 | TRUE |  | Isolation Points:Tarraleah end of the TA-TU 2 110 kV Transmission Circuit and Bus Coupler 752 to be opened prior to new Hydro CB A452 being energisedWorkPlanned:Energise new 110 kV CB B452 for first time and existing Hydro T1 transformer via TA-NN 2 110 kV Transmission Circuit CB F152 at New Norfolk | TRUE | Critical
152318 | 25631 | 119804 | 2012-02-14 10:00 | 2012-02-14 14:00 | 2012-02-14 11:25 | 2012-02-14 11:46 | 21 | E0139 | TA-NN 2 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Commissioning | Generator Shared | Completed | TRUE | 0 | TRUE |  | Isolation Points:Tarraleah end of the TA-TU 2 110 kV Transmission Circuit and Bus Coupler 752 to be opened prior to new Hydro CB A452 being energisedWorkPlanned:Energise new 110 kV CB B452 for first time and existing Hydro T1 transformer via TA-NN 2 110 kV Transmission Circuit CB F152 at New Norfolk | TRUE | Critical
152320 | 25631 | 119804 | 2012-02-14 10:00 | 2012-02-14 14:00 | 2012-02-14 11:29 | 2012-02-14 11:46 | 17 | E0165 | TA 110 kV A Bus | Bus | Forced | HV Equipment Commissioning | Generator Shared | Completed | TRUE | 0 | TRUE |  | Isolation Points:Tarraleah end of the TA-TU 2 110 kV Transmission Circuit and Bus Coupler 752 to be opened prior to new Hydro CB A452 being energisedWorkPlanned:Energise new 110 kV CB B452 for first time and existing Hydro T1 transformer via TA-NN 2 110 kV Transmission Circuit CB F152 at New Norfolk | TRUE | Undefined
152321 | 25631 | 119804 | 2012-02-14 10:00 | 2012-02-14 14:00 | 2012-02-14 11:29 | 2012-02-14 13:17 | 108 | E0166 | TA 110 kV 7 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Commissioning | Generator Shared | Completed | TRUE | 0 | TRUE |  | Isolation Points:Tarraleah end of the TA-TU 2 110 kV Transmission Circuit and Bus Coupler 752 to be opened prior to new Hydro CB A452 being energisedWorkPlanned:Energise new 110 kV CB B452 for first time and existing Hydro T1 transformer via TA-NN 2 110 kV Transmission Circuit CB F152 at New Norfolk | TRUE | Undefined
154223 | 25890 | 120137 | 2012-03-12 19:00 | 2012-03-13 17:00 | 2012-03-12 19:00 | 2012-03-15 12:43 | 3943 | E1567 | DP 22 kV D2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:D252 to be isolated and earthed.WorkPlanned:Allow aurora to carry out cable repairs. | FALSE | Undefined
153586 | 25920 | 120102 | 2012-03-13 07:00 | 2012-03-13 18:00 | 2012-03-13 07:31 | 2012-03-13 14:27 | 416 | E0504 | GT 220 kV B Bus | Bus | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate and earth 220kV disconnector E729FIsolate GT 220 kV B BusWorkPlanned:Re-align 220kV disconnector E729F | TRUE | Undefined
153587 | 25920 | 120102 | 2012-03-13 07:00 | 2012-03-13 18:00 | 2012-03-13 07:31 | 2012-03-13 14:27 | 416 | E1737 | GT 220 kV F Bus | Bus | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate and earth 220kV disconnector E729FIsolate GT 220 kV B BusWorkPlanned:Re-align 220kV disconnector E729F | TRUE | Undefined
153585 | 25920 | 120102 | 2012-03-13 07:00 | 2012-03-13 18:00 | 2012-03-13 07:31 | 2012-03-13 14:27 | 416 | E0503 | GT 220 kV XA7 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate and earth 220kV disconnector E729FIsolate GT 220 kV B BusWorkPlanned:Re-align 220kV disconnector E729F | TRUE | Undefined
155156 | 26000 | 120199 | 2012-03-20 08:00 | 2012-03-20 18:00 | 2012-03-20 13:57 | 2012-03-20 18:03 | 246 | E0972 | CS-KI-EL 110 kV Transmission Circuit (Changed to E1956) | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate CS-KI-EL 110 kV Transmission Circuit, earth as required.WorkPlanned:Commission new B452, B429A and B Bay side of new Bus Coupler Panel.Restore T2 to service on completion of this work. | TRUE | Non-Critical
157246 | 26354 | 120503 | 2012-05-01 13:00 | 2012-05-01 16:00 | 2012-05-01 13:13 | 2012-05-01 17:00 | 227 | E0275 | WA-PM 2 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate and earth P152WorkPlanned:Repair seal on accumulator tank on P152. | FALSE | Critical
157787 | 26403 | 120527 | 2012-05-07 07:00 | 2012-05-08 17:00 | 2012-05-07 07:30 | 2012-05-07 14:43 | 433 | E1867 | KI 11 kV ST2 Station Service Transformer | Station Service Transformer | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate KI 11 kV G2 Feeder Circuit, earth as required.Isolate KI 11 kV ST2 Station Service Transformer, earth as required.WorkPlanned:To separately identify each phase conductor from the 11kV switch gear to each of the new station services transformers. We currently have a 60 degree phase shift between the transformers. We also need to align the each of the phase conductors in the 11kV switch gear with the phase conductors on the transformer LV side. Because of an in line joint in the cables it is not possible to identify each conductor without belling out each conductor separately. | TRUE | Not in WASP
157786 | 26403 | 120527 | 2012-05-07 07:00 | 2012-05-08 17:00 | 2012-05-07 07:30 | 2012-05-07 14:43 | 433 | E0361 | KI 11 kV G2 Feeder Circuit | Feeder | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate KI 11 kV G2 Feeder Circuit, earth as required.Isolate KI 11 kV ST2 Station Service Transformer, earth as required.WorkPlanned:To separately identify each phase conductor from the 11kV switch gear to each of the new station services transformers. We currently have a 60 degree phase shift between the transformers. We also need to align the each of the phase conductors in the 11kV switch gear with the phase conductors on the transformer LV side. Because of an in line joint in the cables it is not possible to identify each conductor without belling out each conductor separately. | TRUE | Undefined
159882 | 26446 | 120590 | 2012-05-12 07:30 | 2012-05-14 10:00 | 2012-05-12 08:11 | 2012-05-14 12:28 | 3137 | E1734 | GT-TV 3 220 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate GT-TV 3 220 kV Transmission Circuit and Earth at GT end only.AETV end of GT-TV 3 220 kV Transmission Circuit is isolated as part of AETV 220kV CCGT yearly maintenance.Please notify AETV prior to outage starting and when GT-TV 3 220 kV Transmission Circuit is Isolated as they require A431 Earth switch to be closed.WorkPlanned:Urgent repairs to 220kV Disconnector X129C | FALSE | Undefined
164263 | 26767 | 120864 | 2012-06-25 13:30 | 2012-06-26 16:00 | 2012-06-25 13:30 | 2012-06-25 15:23 | 113 | E0772 | PL-ST 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate and earth 110 kV B BusWorkPlanned:110 kV VT B797 oil leak investigation | FALSE | Non-Critical
164264 | 26767 | 120864 | 2012-06-25 13:30 | 2012-06-26 16:00 | 2012-06-25 13:30 | 2012-06-25 15:23 | 113 | E0774 | PL 110 kV B Bus | Bus | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate and earth 110 kV B BusWorkPlanned:110 kV VT B797 oil leak investigation | FALSE | Undefined
164265 | 26767 | 120864 | 2012-06-25 13:30 | 2012-06-26 16:00 | 2012-06-25 13:30 | 2012-06-25 15:23 | 113 | E0775 | PL 110 kV A7 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate and earth 110 kV B BusWorkPlanned:110 kV VT B797 oil leak investigation | FALSE | Undefined
164266 | 26767 | 120864 | 2012-06-25 13:30 | 2012-06-26 16:00 | 2012-06-25 13:30 | 2012-06-25 15:25 | 115 | E0777 | PL 110/22 kV T2 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate and earth 110 kV B BusWorkPlanned:110 kV VT B797 oil leak investigation | FALSE | Non-Critical
164328 | 26814 | 120805 | 2012-06-13 15:40 | 2012-06-14 17:00 | 2012-06-14 11:19 | 2012-06-14 15:19 | 240 | E0165 | TA 110 kV A Bus | Bus | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:D129BF129AA729B429AHydro T2 generator transformer required opened off and isolated. Hydro operators are aware and scheduled to begin offloading at 0800.'A' bus available for isolation around 1100WorkPlanned:Repair hot spot on D129A | FALSE | Undefined
164326 | 26814 | 120805 | 2012-06-13 15:40 | 2012-06-14 17:00 | 2012-06-14 11:19 | 2012-06-14 15:19 | 240 | E0139 | TA-NN 2 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:D129BF129AA729B429AHydro T2 generator transformer required opened off and isolated. Hydro operators are aware and scheduled to begin offloading at 0800.'A' bus available for isolation around 1100WorkPlanned:Repair hot spot on D129A | FALSE | Critical
164327 | 26814 | 120805 | 2012-06-13 15:40 | 2012-06-14 17:00 | 2012-06-14 11:19 | 2012-06-14 15:19 | 240 | E0164 | TA-TU 2 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:D129BF129AA729B429AHydro T2 generator transformer required opened off and isolated. Hydro operators are aware and scheduled to begin offloading at 0800.'A' bus available for isolation around 1100WorkPlanned:Repair hot spot on D129A | FALSE | Critical
166734 | 26953 | 121018 | 2012-07-13 16:00 | 2012-07-16 14:00 | 2012-07-13 15:53 | 2012-07-16 14:12 | 4219 | E1842 | GT 220 kV D1 Circuit Breaker | Circuit Breaker | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate and Earth GT 220 kV D1 Circuit BreakerSH-GT 2 220 kV Transmission Circuit will be in service via D752 and B BusWorkPlanned:George Town 220kV Security upgrade projectCT D196 secodary checks | FALSE | Not in WASP
167085 | 27017 | 121070 | 2012-07-21 08:00 | 2012-07-21 16:00 | 2012-07-21 07:42 | 2012-07-21 14:55 | 433 | E0504 | GT 220 kV B Bus | Bus | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:220kV B Bus isolated and earthedCapacitor Bank C2 isolatedWorkPlanned:Inspect and repair as required 220 kV B629B motorised disconnector | FALSE | Undefined
167086 | 27017 | 121070 | 2012-07-21 08:00 | 2012-07-21 16:00 | 2012-07-21 07:42 | 2012-07-21 14:55 | 433 | E0505 | GT 220 kV C2 Capacitor Circuit | Capacitor | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:220kV B Bus isolated and earthedCapacitor Bank C2 isolatedWorkPlanned:Inspect and repair as required 220 kV B629B motorised disconnector | FALSE | Non-Critical
170475 | 27205 | 121320 | 2012-08-24 07:00 | 2012-08-25 18:00 | 2012-08-24 09:00 | 2012-08-25 15:06 | 1806 | E0504 | GT 220 kV B Bus | Bus | Forced | HV Equipment Commissioning | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open, Isolate and Earth GT 220 kV B Bus.GT 220 kV A Bus is Isolated and earthed on Proms 120958WorkPlanned:George Town 220kV Security upgrade project. Refer to Stages B2 and C2Replace faulty B797 B Bus VT's with VT's from A Bus A797 | TRUE | Undefined
172852 | 27538 | 121648 | 2012-09-26 18:15 | 2012-10-01 17:00 | 2012-09-26 18:22 | 2012-10-01 10:04 | 6702 | E0208 | RI 110 kV C1 Capacitor Circuit | Capacitor | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Nil Primary. PIC to carry out secondary isolations as required.WorkPlanned:Investigate and repair communication problem with data and controls to the J652 and K652 110kV circuit breakers at Risdon Substation. C1 and C2 at Risdon will not be available for service until repairs are completed.(possible faulty fibre optic converter) | FALSE | Non-Critical
172853 | 27538 | 121648 | 2012-09-26 18:15 | 2012-10-01 17:00 | 2012-09-26 18:22 | 2012-10-01 10:04 | 6702 | E0209 | RI 110 kV C2 Capacitor Circuit | Capacitor | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Nil Primary. PIC to carry out secondary isolations as required.WorkPlanned:Investigate and repair communication problem with data and controls to the J652 and K652 110kV circuit breakers at Risdon Substation. C1 and C2 at Risdon will not be available for service until repairs are completed.(possible faulty fibre optic converter) | FALSE | Non-Critical
173561 | 27664 | 121702 | 2012-10-11 08:00 | 2012-10-11 10:00 | 2012-10-11 07:55 | 2012-10-11 09:06 | 71 | E0146 | NN 22 kV E2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate NN 22 kV E2 Feeder Circuit as required.WorkPlanned:Replace faulty E252 circuit breaker carriage with spare unit. | FALSE | Undefined
173574 | 27674 | 121688 | 2012-10-04 23:40 | 2012-10-05 06:00 | 2012-10-04 23:45 | 2012-10-05 06:04 | 379 | E1735 | WA-LF 1 220 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:T/L opened off onlyWorkPlanned:Transmission line opened off for voltage control | FALSE | Critical
188463 | 28315 | 122236 | 2013-01-07 12:00 | 2013-01-07 16:00 | 2013-01-07 10:25 | 2013-01-07 14:14 | 229 | E0294 | AL 6.6 kV A3 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:A352 isolated & earthedWorkPlanned:Top up SF6 on A352 | FALSE | Undefined
206228 | 28616 | 122438 | 2013-02-09 20:10 | 2013-02-11 08:00 | 2013-02-09 21:15 | 2013-02-11 09:25 | 2170 | E0028 | GO-CS 1 220 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Fire Service | Completed | TRUE | 0 | TRUE |  | Isolation Points:Nil, removed from service only.WorkPlanned:Remove from Service the GO-CS 1 & 2 220kV transmission lines for safety reasons due to bushfires.. Requested by Tas Fire and Peter Johnson (Transend). | FALSE | Critical
206229 | 28616 | 122438 | 2013-02-09 20:10 | 2013-02-11 08:00 | 2013-02-09 21:16 | 2013-02-11 09:25 | 2169 | E0243 | GO-CS 2 220 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Fire Service | Completed | TRUE | 0 | TRUE |  | Isolation Points:Nil, removed from service only.WorkPlanned:Remove from Service the GO-CS 1 & 2 220kV transmission lines for safety reasons due to bushfires.. Requested by Tas Fire and Peter Johnson (Transend). | FALSE | Critical
183836 | 28903 | 122694 | 2013-03-19 08:30 | 2013-03-19 12:30 | 2013-03-19 08:49 | 2013-03-19 14:07 | 318 | E1770 | MT 110/33 kV T1 Transformer | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate MT 110/33 kV T1 Transformer, earth as required.Isolate 33kV Switchgear incomerWorkPlanned:Investigate source of Partial Discharge suspected to be from A597 with equipment manufacturer. | TRUE | Non-Critical
183855 | 28914 | 122683 | 2013-03-15 07:30 | 2013-03-15 17:00 | 2013-03-15 07:51 | 2013-03-15 10:29 | 158 | E1779 | MT 110/33 kV T2 Transformer | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Isolate and earth as required.WorkPlanned:Repair B597. | FALSE | Non-Critical
206235 | 28973 | 1896 |  |  | 2013-03-06 15:36 | 2013-03-06 17:32 | 116 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Forced | Fire Fighting | Fire Service | Completed | TRUE | 982 | TRUE |  | IR1231 LF-SO-TB and LF-SO 110 kV lines OOS due to fire services direction. | FALSE | Non-Critical
206236 | 28973 | 1896 |  |  | 2013-03-06 15:36 | 2013-03-06 17:32 | 116 | E1796 | LF-SO 110 kV Transmission Circuit | Transmission | Forced | Fire Fighting | Fire Service | Completed | TRUE | 0 | TRUE |  | IR1231 LF-SO-TB and LF-SO 110 kV lines OOS due to fire services direction. | FALSE | Non-Critical
184285 | 28998 | 122810 | 2013-04-08 18:00 | 2013-04-09 02:00 | 2013-04-08 18:53 | 2013-04-09 02:50 | 477 | E0250 | LI-WY 220 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:The loss of the comms link removes protection intertripping and results in unacceptable fault clearance times on the LI-WY and WY-CA transmission lines. Therefore the lines must opened off only to maintain a secure operating state.WorkPlanned:Investigate and repair fault causing intermittent comms failures on the comms link to Wayatinah and Catagunya stations. | FALSE | Non-Critical
184286 | 28998 | 122810 | 2013-04-08 18:00 | 2013-04-09 02:00 | 2013-04-08 18:53 | 2013-04-09 02:50 | 477 | E0953 | WY-CA 220 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:The loss of the comms link removes protection intertripping and results in unacceptable fault clearance times on the LI-WY and WY-CA transmission lines. Therefore the lines must opened off only to maintain a secure operating state.WorkPlanned:Investigate and repair fault causing intermittent comms failures on the comms link to Wayatinah and Catagunya stations. | FALSE | Non-Critical
185375 | 29057 | 122878 | 2013-05-01 09:15 | 2013-05-01 09:45 | 2013-05-01 09:10 | 2013-05-01 09:54 | 44 | E0693 | TR 22 kV C8 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open and withdraw Breaker TR 22 kV C8 Bus Coupler Circuit onlyWorkPlanned:PD issue inspection by Transend and Schneider | FALSE | Undefined
187796 | 29284 | 123017 | 2013-05-09 12:00 | 2013-05-09 16:00 | 2013-05-09 10:28 | 2013-05-09 15:32 | 304 | E1835 | GT 220 kV B7 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open and isolate GT 220 kV B7 Bus Coupler Circuit via 220kV Motorised Disconnectors B729F and B729BWorkPlanned:Top up 220kV CT B796 with SF6 gas | FALSE | Not in WASP
203888 | 29991 | 123878 | 2013-08-07 15:00 | 2013-08-07 22:00 | 2013-08-07 15:28 | 2013-08-07 18:01 | 153 | E0401 | BU-PL 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Switch auto reclose as requestedWorkPlanned: Auto Reclose on Burnie - Port Latta and Burnie - Smithton 110kV Transmission Lines required out of service to allow replacement of tower section damage during a motor vehicle accident. | FALSE | Non-Critical
203889 | 29991 | 123878 | 2013-08-07 15:00 | 2013-08-07 22:00 | 2013-08-07 15:28 | 2013-08-07 18:01 | 153 | E0402 | BU-ST 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Switch auto reclose as requestedWorkPlanned: Auto Reclose on Burnie - Port Latta and Burnie - Smithton 110kV Transmission Lines required out of service to allow replacement of tower section damage during a motor vehicle accident. | FALSE | Non-Critical
203890 | 30290 | 124102 | 2013-09-02 10:45 | 2013-09-02 12:45 | 2013-09-02 10:51 | 2013-09-02 13:04 | 133 | E0290 | PO-PM 2 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Commissioning | Generator Request | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open onlyWorkPlanned: PO-PM #2 T/L OOS at Tas Hydro's request for wiring mods at Poatina. | FALSE | Non-Critical
203891 | 30359 | 124182 | 2013-09-12 09:20 | 2013-09-13 18:00 | 2013-09-12 09:20 | 2013-09-13 16:18 | 1858 | E0439 | HA-NW 1 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open onlyWorkPlanned:HA-NW 1 Transmission Circuit opened at Hadspen end only. Investigate incorrect operation of 110kV CB J152 protection under fault conditions. J152 has emergency availbilty and can be closed after the next contingency if required. HA-NW 1 Transmission Circuit opened at Hadspen end only. Investigate incorrect operation of 110kV CB J152 protection under fault conditions. J152 has emergency availbilty and can be closed after the next contingency if required. | FALSE | Non-Critical
200571 | 30620 | 124393 | 2013-10-21 09:57 | 2013-10-21 20:00 | 2013-10-21 08:03 | 2013-10-21 16:10 | 487 | E0377 | BU 110 kV B7 Bus Coupler Circuit | Bus Coupler | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open and isolateWorkPlanned: Emergency isolation of 110kV Bus Coupler to investigate noise from protection cubicle. | FALSE | Undefined
200575 | 30623 | 124389 | 2013-10-19 08:30 | 2013-10-19 16:30 | 2013-10-19 07:47 | 2013-10-19 12:29 | 282 | E0553 | SH-WI 220 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Generator Request | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open, isolate and earthWorkPlanned:Hydro request Isol and Earth SH-WI 220 kV T/L Hydro request Isol and Earth SH-WI 220 kV T/L to access replacement 22 kV feeder poles in easment at Wilmot PS | FALSE | Non-Critical
200596 | 30645 | 124356 | 2013-10-16 08:30 | 2013-10-16 20:00 | 2013-10-16 10:35 | 2013-10-16 19:11 | 516 | E0044 | CS 110/11 kV T6 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open, isolate and earthWorkPlanned: Investigate and repair fault on CB F552. | FALSE | Non-Critical
201579 | 30672 | 124443 | 2013-10-28 10:30 | 2013-10-28 14:00 | 2013-10-28 10:40 | 2013-10-28 11:35 | 55 | E1756 | RI 110 kV C4 Capacitor Circuit | Capacitor | Forced | Secondary Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open onlyWorkPlanned: CB Fail Contact Output Repairs | FALSE | Non-Critical
202413 | 30704 | 124465 | 2013-10-31 12:00 | 2013-10-31 14:00 | 2013-10-31 11:51 | 2013-10-31 12:10 | 19 | E0646 | TR-MY 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open onlyWorkPlanned: Corrective maint - Top up SF6 gas in VT B197 | FALSE | Non-Critical
202426 | 30712 | 124456 | 2013-10-30 09:00 | 2013-10-30 16:00 | 2013-10-30 10:50 | 2013-10-30 15:20 | 270 | E0912 | TR 22 kV T2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open, isolate and withdraw breakerWorkPlanned: Investigate T252 Gas Pressure Low alarm and top up if required. | FALSE | Undefined
205739 | 30751 | 124482 | 2013-11-05 19:20 | 2013-11-08 17:00 | 2013-11-05 19:45 | 2013-11-13 09:32 | 10907 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open onlyWorkPlanned:C252 bypassed to Aurora System. Bypass CB C252 due low SF6 gas pressure. Arrange repairs. | FALSE | Undefined
207091 | 30753 | 124480 | 2013-11-05 11:55 | 2013-11-05 12:30 | 2013-11-05 11:55 | 2013-11-05 12:53 | 58 | E1958 | LI-CL-RE-CS 1 220 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Generator Request | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open onlyWorkPlanned: Cluny PS intake gate closing, M/C CB low air pressure and will not open - emergency request to open Chapel St and Liapootah ends of LI-RE-CL-CS 1 220kV T/L. | FALSE | Critical
203082 | 30767 | 124555 | 2013-11-18 09:00 | 2013-11-18 16:00 | 2013-11-18 10:48 | 2013-11-18 17:29 | 401 | E0038 | CS 220 kV By-Pass Bus | Bus | Forced | HV Equipment Maintenance | Generator Request | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open and isolateWorkPlanned: | FALSE | Undefined
203083 | 30767 | 124555 | 2013-11-19 07:00 | 2013-11-19 17:00 | 2013-11-19 07:47 | 2013-11-19 16:10 | 503 | E0038 | CS 220 kV By-Pass Bus | Bus | Forced | HV Equipment Maintenance | Generator Request | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open and isolateWorkPlanned: | FALSE | Undefined
203084 | 30768 | 124553 | 2013-11-18 09:00 | 2013-11-18 15:30 | 2013-11-18 08:08 | 2013-11-18 16:22 | 494 | E1479 | RI 33 kV G2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open, isolate and earthWorkPlanned: Distribution Line Maintenance | FALSE | Undefined
203591 | 30838 | 124568 | 2013-11-23 09:00 | 2013-11-24 15:00 | 2013-11-24 07:39 | 2013-11-24 08:59 | 80 | E1040 | PM 22 kV G2 Feeder Circuit | Feeder | Forced | HV Equipment Maintenance | DNSP | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open, isolate and earthWorkPlanned: Urgent repairs required to HV loops at C540296 | FALSE | Undefined
205938 | 30977 | 124657 | 2013-12-11 04:21 | 2013-12-11 09:00 | 2013-12-11 04:21 | 2013-12-12 13:00 | 1959 | E0318 | BY 6.6 kV B Bus | Bus | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open onlyWorkPlanned:Boyer are aware of outage. De-energise 6.6kV B Bus then rack out and inspect Feeder Breakers B352 and C352 after Bus Zone operation. | FALSE | Undefined
205939 | 30978 | 124656 | 2013-12-11 10:30 | 2013-12-11 15:00 | 2013-12-11 10:53 | 2013-12-11 14:40 | 227 | E0794 | QT 110/22 kV T2 Transformer Circuit | Transformer | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open onlyWorkPlanned:No LARN needed, Distribution Operations advised. 110 / 22 kV Transformer Circuit T2 opened off to investigate Restrictive Earth Fault per S French | FALSE | Non-Critical
205943 | 30982 | 124652 | 2013-12-09 11:44 | 2013-12-13 16:00 | 2013-12-09 11:44 | 2013-12-10 15:59 | 1695 | E0400 | BU-HM 110 kV Transmission Circuit | Transmission | Forced | HV Equipment Maintenance | Transend | Completed | TRUE | 0 | TRUE |  | Isolation Points:Open, isolate and earthWorkPlanned: | FALSE | Non-Critical

## TQS0101-0115 cct numbers
Circuit numbers from circuit availability report
|  | No of TL Circuits | CY av | No of TF Circuits | CY av | No of Cap Circuits | CY av
Jan 2006 |  | 104 |  | 100 |  | 9
Feb 2006 |  | 104 |  | 100 |  | 9
Mar 2006 |  | 102 |  | 100 |  | 9
Apr 2006 |  | 102 |  | 100 |  | 9
May 2006 |  | 102 |  | 100 |  | 9
Jun 2006 |  | 102 |  | 101 |  | 9
Jul 2006 |  | 102 |  | 101 |  | 9
Aug 2006 |  | 102 |  | 101 |  | 9
Sep 2006 |  | 102 |  | 101 |  | 9
Oct 2006 |  | 102 |  | 101 |  | 9
Nov 2006 |  | 102 |  | 101 |  | 9
Dec 2006 | 2006 | 102 | 102.3333 | 101 | 100.5833 | 9 | 9
Jan 2007 |  | 102 |  | 100 |  | 9
Feb 2007 |  | 102 |  | 100 |  | 10
Mar 2007 |  | 102 |  | 100 |  | 10
Apr 2007 |  | 102 |  | 100 |  | 10
May 2007 |  | 102 |  | 100 |  | 10
Jun 2007 |  | 102 |  | 97 |  | 10
Jul 2007 |  | 102 |  | 100 |  | 10
Aug 2007 |  | 102 |  | 100 |  | 10
Sep 2007 |  | 102 |  | 100 |  | 10
Oct 2007 |  | 103 |  | 100 |  | 10
Nov 2007 |  | 103 |  | 100 |  | 10
Dec 2007 | 2007 | 103 | 102.25 | 100 | 99.75 | 10 | 9.9167
Jan 2008 |  | 103 |  | 100 |  | 10
Feb 2008 |  | 103 |  | 101 |  | 10
Mar 2008 |  | 103 |  | 101 |  | 10
Apr 2008 |  | 103 |  | 101 |  | 10
May 2008 |  | 103 |  | 101 |  | 10
Jun 2008 |  | 103 |  | 101 |  | 10
Jul 2008 |  | 103 |  | 101 |  | 10
Aug 2008 |  | 103 |  | 101 |  | 10
Sep 2008 |  | 103 |  | 101 |  | 10
Oct 2008 |  | 103 |  | 101 |  | 10
Nov 2008 |  | 103 |  | 101 |  | 10
Dec 2008 | 2008 | 103 | 103 | 102 | 101 | 10 | 10
Jan 2009 |  | 103 |  | 103 |  | 10
Feb 2009 |  | 103 |  | 103 |  | 10
Mar 2009 |  | 103 |  | 103 |  | 10
Apr 2009 |  | 104 |  | 103 |  | 10
May 2009 |  | 104 |  | 103 |  | 10
Jun 2009 |  | 103 |  | 103 |  | 10
Jul 2009 |  | 103 |  | 104 |  | 10
Aug 2009 |  | 103 |  | 104 |  | 10
Sep 2009 |  | 103 |  | 104 |  | 10
Oct 2009 |  | 103 |  | 104 |  | 10
Nov 2009 |  | 103 |  | 104 |  | 10
Dec 2009 | 2009 | 103 | 103.1667 | 104 | 103.5 | 10 | 10
Jan 2010 |  | 103 |  | 104 |  | 10
Feb 2010 |  | 102 |  | 104 |  | 10
Mar 2010 |  | 102 |  | 104 |  | 10
Apr 2010 |  | 102 |  | 104 |  | 10
May 2010 |  | 102 |  | 104 |  | 10
Jun 2010 |  | 102 |  | 104 |  | 10
Jul 2010 |  | 102 |  | 104 |  | 10
Aug 2010 |  | 102 |  | 104 |  | 10
Sep 2010 |  | 102 |  | 104 |  | 10
Oct 2010 |  | 102 |  | 104 |  | 10
Nov 2010 |  | 102 |  | 104 |  | 10
Dec 2010 | 2010 | 102 | 102.0833 | 104 | 104 | 10 | 10
Jan 2011 |  | 102 |  | 103 |  | 10
Feb 2011 |  | 102 |  | 103 |  | 12
Mar 2011 |  | 102 |  | 103 |  | 12
Apr 2011 |  | 102 |  | 103 |  | 12
May 2011 |  | 106 |  | 107 |  | 12
Jun 2011 |  | 106 |  | 107 |  | 12
Jul 2011 |  | 106 |  | 107 |  | 12
Aug 2011 |  | 106 |  | 107 |  | 12
Sep 2011 |  | 106 |  | 107 |  | 12
Oct 2011 |  | 106 |  | 107 |  | 12
Nov 2011 |  | 106 |  | 107 |  | 12
Dec 2011 | 2011 | 106 | 104.6667 | 107 | 105.6667 | 12 | 11.8333
Jan 2012 |  | 106 |  | 106 |  | 12
Feb 2012 |  | 106 |  | 106 |  | 12
Mar 2012 |  | 106 |  | 106 |  | 12
Apr 2012 |  | 106 |  | 106 |  | 12
May 2012 |  | 106 |  | 108 |  | 12
Jun 2012 |  | 106 |  | 108 |  | 12
Jul 2012 |  | 106 |  | 108 |  | 12
Aug 2012 |  | 108 |  | 108 |  | 12
Sep 2012 |  | 108 |  | 108 |  | 12
Oct 2012 |  | 108 |  | 110 |  | 12
Nov 2012 |  | 108 |  | 110 |  | 12
Dec 2012 | 2012 | 108 | 106.8333 | 110 | 107.8333 | 12 | 12
Jan 2013 |  | 108 |  | 110 |  | 12
Feb 2013 |  | 108 |  | 110 |  | 12
Mar 2013 |  | 108 |  | 110 |  | 12
Apr 2013 |  | 108 |  | 110 |  | 12
May 2013 |  | 108 |  | 110 |  | 12
Jun 2013 |  | 108 |  | 110 |  | 12
Jul 2013 |  | 107 |  | 110 |  | 12
Aug 2013 |  | 107 |  | 110 |  | 12
Sep 2013 |  | 107 |  | 110 |  | 12
Oct 2013 |  | 107 |  | 110 |  | 12
Nov 2013 |  | 107 |  | 109 |  | 12
Dec 2013 | 2013 | 107 | 107.5 | 109 | 109.8333 | 12 | 12

## TQS0116-0117 LOS table
LOS > 1.0 sysmin | 1
Count of System Minutes | Instigator
Date/Time | Basslink | Force Majeure | NEMMCO | Transend | Total Result
2006 | 4 |  | 1 | 3 | 8
2007 | 1 | 1 |  | 1 | 3
2008 | 2 |  |  |  | 2
2009 |  | 1 |  | 2 | 3
2010 |  |  |  | 2 | 2
2011 | 1 |  |  | 6 | 7
2012 |  | 1 |  | 2 | 3
2013 |  |  |  | 1 | 1
Total Result | 8 | 3 | 1 | 17 | 29
[9 empty] | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013
[6 empty] | TQS0116 | Number of events greater than 0.1 system minutes per annum | number | 16 | 10 | 6 | 8 | 9 | 11 | 10 | 10
[6 empty] | TQS0117 | Number of events greater than 1.0 system minutes per annum | number | 3 | 1 |  | 2 | 2 | 6 | 2 | 1

## TQS0116-0117 LOS>0.1 Events
Loss of Supply Event Summary - Jan 2006 and Dec 2013
Event No. | WASP Outage Key | Date/Time | Duration (mins) | Description | System Minutes | LOS > 1.0 sysmin | Fault / Scheduled | Instigator
1 | 4104 | 2006-01-09 06:57 | 211 | IR208 - PL-ST 110 kV and PL T2 interrupted due to faulty directional overcurrent relay element at PL. | 0.1089 | 0 | Fault | Transend
2 | 4143 | 2006-01-17 13:39 | 539 | IR209 - BU-PL 110 kV interrupted due to broken conductor loop. | 3.265 | 1 | Fault | Transend
3 | 4145 | 2006-01-20 04:45 | 207 | IR223 - Kermandie Substation transformer T2 interrupted due to incorrect CT secondary connections (during commissioning). This resulted in feeder faults causing TF REF protection operation. | 0.3571 | 0 | Fault | Transend
4 | 4147 | 2006-01-20 05:18 | 827 | IR219 - WA-BW 110 kV interrupted due to lightning strike causing two conductors to break. | 1.886 | 1 | Fault | Transend
5 | 4214 | 2006-01-27 10:43 | 37 | IR230 - Load shedding occurred at Risdon Substation due to incorrectly applied ScriptCalc during planned work. | 0.5154 | 0 | Fault | Transend
6 | 4212 | 2006-02-27 18:03 | 73 | IR237 - Port Latta T1 transformer isolated due to protection operations resulting from incorrect protection settings applied prior to commissioning of new plant. | 0.5379 | 0 | Fault | Transend
7 | 4280 | 2006-03-17 12:08 | 7 | IR263 - Load shed within Zinifex installation due to ScriptCalc switching error in control room. | 0.16 | 0 | Fault | Transend
8 | 5092 | 2006-04-08 12:44 | 64 | IR270 - George Town Substation 22 kV 'A' Bus interrupted. 22 kV circuit breaker (E252) failure. Under investigation by manufacturer. | 0.2796 | 0 | Fault | Transend
9 | 5107 | 2006-04-23 12:37 | 18 | IR276 - FA-QU-SR-HM 110 kV interrupted. LV feeder fault (tree across feeder) at Que Substation caused transmission line protection to operate. Cause of maloperation unknown. | 0.2779 | 0 | Fault | Transend
10 | 5495 | 2006-05-23 07:59 | 36 | IR300 - UFLS initiated at Comalco, Zinifex, Temco and Boyer due to drop in system frequency resulting from Generator and NEMMCO activities. | 3.5441 | 1 | Fault | NEMMCO
11 | 5557 | 2006-06-02 22:01 | 45 | IR313 - Trevallyn 22 kV 'B' Bus isolated due to failure by DNSP Operators to follow agreed feeder earthing practices during planned work. | 0.4396 | 0 | Fault | Transend
12 | 5645 | 2006-06-28 12:40 | 61 | IR326 - Supply interrupted to Palmerston Substation 22 kV 'B' bus due to incorrect SCADA configuration applied by Contractor during pre-commissioning. | 0.2072 | 0 | Fault | Transend
13 | 7383 | 2006-07-22 11:51 | 91 | IR344 - Basslink circuit interrupted resulting in FCSPS operation. Transend did not cause or contribute to the outage. | 0.2532 | 0 | Fault | Basslink
14 | 7384 | 2006-07-22 14:52 | 620 | IR344 - Basslink circuit interrupted resulting in FCSPS operation. Transend did not cause or contribute to the outage. | 2.1364 | 1 | Fault | Basslink
15 | 5862 | 2006-08-01 12:32 | 73 | IR337 - Supply interrupted to transformer T4 and 22 kV 'A' and 'B' buses at Hadspen Substation due to transformer fault. | 0.6788 | 0 | Fault | Transend
16 | 7382 | 2006-08-18 11:56 | 39 | Basslink tripped at Loy Yang when importing 299MW initiating FCSPS action at Comalco, Zinifex and Temco. | 2.9231 | 1 | Fault | Basslink
17 | 7573 | 2006-09-14 10:33 | 107 | IR347 - Basslink trip due to loss of supply to valve house cooling fans at Loy Yang converter station. FCSPS initiated resulting in load shedding at Comalco, Temco and Zinifex as designed. | 3.3902 | 1 | Fault | Basslink
18 | 7744 | 2006-10-04 14:38 | 74 | IR355 - Palmerston Substation transformer T4 interrupted. Contractor left TF neutral CT links open resulting in transformer trip in response to a feeder fault. ITOMS: Not included as the CT in question is integral to protection systems that are protecting against LV faults only. | 0.2487 | 0 | Fault | Transend
19 | 7746 | 2006-10-05 15:51 | 243 | IR357 - Norwood-Scottsdale-Derby 88 kV interrupted. No cause identified. | 1.6502 | 1 | Fault | Transend
20 | 8613 | 2006-10-12 15:31 | 257 | IR359 - Lindisfarne-Rokeby No 1 110 kV transmission circuit interrupted due to bushfire. Lindisfarne-Rokeby No 2-Sorell 110 kV transmission circuit interrupted due to incorrect substation configuration. ITOMS: Not included as bus coupler CB is on 22 kV. | 0.5514 | 0 | Fault | Transend
21 | 7890 | 2006-11-09 19:45 | 35 | IR366 - Mowbray Substation 22 kV B Bus and transformer T2 were interrupted in response to a 22 kV feeder fault due to incorrect protection wiring design. | 0.1314 | 0 | Fault | Transend
22 | 8098 | 2006-12-10 12:32 | 48 | IR375 - Basslink loss of link signal received due to extreme temperatures in Victoria, resulting in SPS load shedding at Comalco and TEMCO. | 1.3841 | 1 | Fault | Basslink
23 | 8332 | 2007-01-09 18:27 | 17 | IR379 - Queenstown Substation interrupted due to inadvertent protection operation. Source of protection operation unknown. | 0.1926 | 0 | Fault | Transend
24 | 8337 | 2007-01-12 22:17 | 103 | IR380 - Risdon Substation transformer T5 and T6 interrupted due to faulty relay causing inadvertent circuit breaker fail (CBF) operation. | 0.9034 | 0 | Fault | Transend
25 | 8346 | 2007-01-16 09:56 | 899 | IR382 - Queenstown Substation transformers T3 and T4 interrupted due to a partially decommissioned control cable causing inadvertent trip signals. | 0.1179 | 0 | Fault | Transend
26 | 8351 | 2007-01-21 00:15 | 2225 | IR384 - Sorell Substation interrupted due to poor circuit breaker design resulting in a cracked bus coupler circuit breaker shutter. Resultant partial discharge and ozone corrosion caused flashover of CT in D252 switchgear cubicle. ITOMS: Not included as CB is low voltage. | 0.4453 | 0 | Fault | Transend
27 | 8795 | 2007-02-22 17:02 | 50 | IR391 - SH-FA 1 and SH-FA 2 220 kV transmission circuits interrupted due to lightning strike. Supply to west coast interrupted. | 1.0371 | 1 | Fault | Force Majeure
28 | 8644 | 2007-02-22 18:54 | 61 | IR388 - Rosebery Substation 44/22 kV T4 and T5 transformer circuits interrupted during severe lightning storms. | 0.123 | 0 | Fault | Transend
29 | 8798 | 2007-02-27 06:20 | 18 | IR394 - Load shedding intitiated at Risdon Substation due to incorrect drawings utilised during transformer maintenance and metering testing. | 0.4054 | 0 | Fault | Transend
30 | 9038 | 2007-04-14 04:52 | 224 | IR405 - Mowbray Substation 22 kV 'A' and 'B' buses interrupted due to faulty current transformer. Cause of CT failure unknown. | 0.7855 | 0 | Fault | Transend
31 | 9039 | 2007-04-15 17:28 | 77 | IR406 - Palmerston-Avoca 110 kV transmission circuit interrupted due to lightning. | 0.4172 | 0 | Fault | Transend
32 | 11603 | 2007-09-26 08:09 | 79 | IR464 - George Town-George Town Converter Station 220 kV transmission circuit interrupted due to sensor failure at George Town Converter Station. | 3.9431 | 1 | Fault | Basslink
33 | 11816 | 2007-11-14 13:36 | 61 | IR472 - Sheffield Substation 110 kV 'A' Bus interrupted due to inappropriate temporary protection settings applied during planned work. | 1.3591 | 1 | Fault | Transend
34 | 12014 | 2007-12-06 05:03 | 91 | IR477 - Sorell Substation transformer T1 interrupted due to 22 kV CT flashover. Root cause of flashover unknown. | 0.2583 | 0 | Fault | Transend
35 | 12347 | 2008-02-18 07:17 | 303 | IR494 - Que Substation transformer T1 interrupted. Cause unknown. | 0.9836 | 0 | Fault | Transend
36 | 12660 | 2008-03-02 10:36 | 292 | IR496 - Palmerston-Avoca and Avoca-St Marys 110 kV transmission circuits interrupted due to VT failure at Avoca Substation. | 0.5753 | 0 | Fault | Transend
37 | 12959 | 2008-04-03 02:37 | 270 | IR501 - Lindisfarne-Sorell-Triabunna 110 kV transmission circuit interrupted six times during widespread destructive winds. | 0.37 | 0 | Fault | Force Majeure
38 | 12957 | 2008-04-07 07:53 | 568 | IR498 - Que Substation 22 kV bus interruption due to current transformer failure following down stream feeder fault. | 0.8172 | 0 | Fault | Transend
39 | 13234 | 2008-06-08 00:31 | 25 | IR538 - Basslink FCSPS operation due to circuit breaker failure at Loy Yang Converter Station resulting in contracted load shedding. This report 1327 have been duplicated with another number ID1356. G.Hwaba | 3.323 | 1 | Fault | Basslink
40 | 13236 | 2008-06-25 04:19 | 72 | IR540 - Electrona Substation 11 kV Bus interruption due to earth voltage rise under lightning conditions inadvertently causing bus protection to operate. | 0.191 | 0 | Fault | Transend
41 | 13561 | 2008-08-14 23:12 | 65 | IR573 - Basslink interrupted due to fault at Loy Yang. This report 1327 have been duplicated with the other report ID13234. G Hwaba | 3.6734 | 1 | Fault | Basslink
42 | 13562 | 2008-08-26 14:56 | 212 | IR570 - Supply at Newton Substation interrupted due to failure of a generation asset. | 0.318 | 0 | Fault | Generator Request
43 | 13775 | 2008-10-30 11:55 | 15 | IR588 - Burnie Substation 22 kV Bus A interruption during commissioning of new protection panel. | 0.1569 | 0 | Fault | Transend
44 | 16485 | 2008-11-27 16:19 | 33 | IR600 - Basslink FCSPS operation causing load shedding. Basslink advised trip was caused by a DC line fault. Suspected a lightning strike at Loy Yang. | 0.1751 | 0 | Fault | Basslink
45 | 16820 | 2008-12-01 03:45 | 28 | IR607 - FA-RB-QT and QT-NT 110 kV transmission circuits interrupted due to lightning. | 0.2753 | 0 | Fault | Transend
46 | 17063 | 2009-01-22 17:36 | 98 | IR619 - NH 11kV A and B Busses tripped tripped when frame leakage protection operated. Cause under investigation. | 0.5416 | 0 | Fault | Transend
47 | 17991 | 2009-04-26 03:27 | 187 | IR776 trip of LF-RK 1 when c252 energised due to protection grading issue. not in ITOMS, this a 22kV protection blocking issue. | 0.1211 | 0 | Fault | Transend
48 | 18181 | 2009-05-15 08:56 | 27 | IR773 Farrell-Roseberry 110 kV tripped. | 0.4792 | 0 | Fault | Transend
49 | 18640 | 2009-07-02 10:47 | 0 | UFLS block 1 operated when 2530 MW generation tripped on the mainland. | 0.8431 | 0 | Fault | Basslink
50 | 18697 | 2009-08-03 02:48 | 112 | IR705 - Rosebery Substation - the Rosebery T1 and T2 110/44 kV transformer circuits tripped following a feeder fault due to incorrect protection grading. | 1.2108 | 1 | Fault | Transend
51 | 18777 | 2009-08-31 10:28 | 33 | IR726 New Norfolk Substation - the New Norfolk 22kV B bus bar tripped due to protection mal-operation. | 0.1857 | 0 | Fault | Transend
52 | 19055 | 2009-09-14 10:30 | 498 | IR722 FA-QU-SR-HM tripped due to broken insulator. Loss of supply at Que and Savage River. | 4.9061 | 1 | Fault | Transend
53 | 19056 | 2009-09-16 11:50 | 39 | IR817 GT supply bus tripped due to inadequate isolation of trip circuits causing loss of supply. | 0.143 | 0 | Fault | Transend
54 | 19062 | 2009-09-27 11:53 | 1810 | IR721 BU-ST and BU-PL tripped during severe wind storms. | 1.0155 | 1 | Fault | Force Majeure
55 | 19399 | 2009-11-18 09:40 | 93 | IR781 Boyer Substation - the Boyer T14 110/6.6 kV transformer tripped due to inappropriate protection settings. | 0.8543 | 0 | Fault | Transend
56 | 20900 | 2010-04-29 14:50 | 84 | IR903 Farrell 220 kV A Bus tripped during commissioning work causing loss of supply and generation on the West Coast and load shedding of major industrials. The event was caused by mal-operation of an obsolete protection system. | 2.9477 | 1 | Fault | Transend
57 | 21138 | 2010-05-12 09:10 | 41 | IR910 Knights Road Substation - the Knights Road 11 kV A Bus tripped during planned work due to incorrect protection settings. | 0.174 | 0 | Fault | Transend
58 | 21091 | 2010-05-18 13:36 | 78 | IR917 George Town Substation - the George Town 22kV B Bus tripped during planned work due to incorrect protection isolation. | 0.2743 | 0 | Fault | Transend
59 | 21403 | 2010-07-22 07:03 | 120 | IR961 Risdon T1, T2 and T3 tripped due to protection maloperation with loss of supply to NyrStar | 1.0945 | 1 | Fault | Transend
60 | 21405 | 2010-07-28 10:50 | 13 | IR963 Risdon 11kV Bus Bar tripped during protection remediation work | 0.452 | 0 | Fault | Transend
61 | 21964 | 2010-09-11 17:28 | 35 | IR1003 Port Latta-Smithton 110 kV circuit tripped with loss of supply to Port Latta substation due to commissioning error. | 0.2375 | 0 | Fault | Transend
62 | 21962 | 2010-09-29 08:05 | 30 | IR1012 Sorell 22 kV B bus tripped while A852 bus coupler was disabled due to high load. | 0.2108 | 0 | Fault | Transend
63 | 22048 | 2010-10-30 08:19 | 75 | IR1021 Newton Substation 110kV bus tripped following a feeder fault. | 0.1329 | 0 | Fault | Transend
64 | 22273 | 2010-11-11 10:11 | 12 | IR1036 RI T2 transformer circuit tripped following an over temperature alarm. | 0.6147 | 0 | Fault | Transend
65 | 23123 | 2011-02-07 12:40 | 26 | IR1068 New Norfolk-Boyer 1 transmission circuit tripped during planned work. | 1.2551 | 1 | Fault | Transend
66 | 23413 | 2011-03-23 20:16 | 298 | IR1094 Sorell T2 transformer circuit tripped causing loss of supply at Sorell substation, due to wildlife incursion during planned work. | 1.8975 | 1 | Fault | Transend
67 | 23489 | 2011-03-24 07:08 | 135 | IR1142 Sorell A Bus feeders trip due to error during planned work. Inadequate vermin control during substation construction works | 0.1633 | 0 | Fault | Transend
68 | 23631 | 2011-05-04 19:21 | 219 | IR1108 Lindisfarne-Rokeby Sorell 110kV transmission line tripped causing loss of supply at Rokeby Substation, Suspect cable but cause unknown. | 2.199 | 1 | Fault | Transend
69 | 24243 | 2011-07-08 03:42 | 5070 | IR1131 CS-KI-KR tripped with loss of supply at Kingston, Knights Road, Kermandie and Huon River substations. | 1.8447 | 1 | Fault | Transend
70 | 24403 | 2011-07-14 16:05 | 114 | IR1134 KI T2 tripped on Bucholz alarm and caused loss of supply at Kingston substation. | 1.2172 | 1 | Fault | Transend
71 | 24883 | 2011-09-14 14:13 | 60 | IR1161 Port Latta 22kV B Bus tripped due to error during planned work. | 0.2844 | 0 | Fault | Transend
72 | 24927 | 2011-09-19 06:49 | 208 | IR1165 Newton 110 kV bus bar tripped due to T2 Bucholz trip, causing loss of supply. | 2.1025 | 1 | Fault | Transend
73 | 24782 | 2011-09-19 09:06 | 25 | IR1164 Farrell-Rosebery-Queenstown transmission circuit tripped due to equipment failure (A helical dead end failed on FA-RB). | 0.5448 | 0 | Fault | Transend
74 | 24926 | 2011-09-19 19:43 | 16 | IR1166 BU-PL, BU-ST, SB-WN-ST and PL-ST 110 kV transmission circuits tripped with lightning in area. Loss of supply at Port Latta Substation. | 0.1115 | 0 | Fault | Transend
75 | 25082 | 2011-10-26 22:34 | 139 | IR1179 GT-GC transmission circuit tripped, suspect filter protection trip at Basslink converter station. | 25.8698 | 1 | Fault | Basslink
76 | 25258 | 2011-11-24 09:29 | 29 | SPS trip Temco load | 0.4365 | 0 | Fault | Basslink
77 | 25354 | 2011-12-19 10:22 | 818 | IR1211 Sorell Substation 110/22kV transformer T2 tripped due to water ingress. Restoration date and time to be determined | 0.1665 | 0 | Fault | Transend
78 | 25519 | 2012-02-01 00:31 | 14 | IR1226 Nyrstar feeders tripped, suspect due to operation of harmonic filter. | 0.1451 | 0 | Fault | MI
79 | 26186 | 2012-04-06 19:35 | 24 | IR1135 Burnie 110 kV transmission line circuits tripped during severe lightning with LOS at Burnie, Ulverstone, Emu Bay, Port Latta, Smithton and Hampshire substations. | 0.6265 | 0 | Fault | Transend
80 | 26501 | 2012-05-07 23:47 | 139 | IR1282 Boyer 6.6kV A and B bus circuits tripped due to a protection deficiency following faulted customer feeder. | 0.8463 | 0 | Fault | Transend
81 | 26558 | 2012-05-10 10:36 | 77 | IR1140 Arthurs Lake T1 transformer circuit tripped with loss of supply at Arthurs Lake when Hydro Pumps were started. investigation not conclusive due to lack of SOE data and lack of protection testing/ investigation. | 0.2631 | 0 | Fault | Transend
82 | 26502 | 2012-05-11 23:02 | 69 | IR1284 Boyer 6.6 kV A and B bus circuits tripped due to protection deficiency following faulted customer feeder. | 0.4114 | 0 | Fault | Transend
83 | 27417 | 2012-09-09 15:38 | 218 | IR1168 LF-SO-TB 110kV transmission circuit was forced out due to insulator damage by shooting. | 0.2882 | 0 | Fault | Transend
84 | 27619 | 2012-09-13 11:31 | 106 | IR1113 Farrell-Rosebery-Queenstown 110kV transmission circuit tripped with loss of supply to West Coast. | 2.3228 | 1 | Fault | Transend
85 | 27974 | 2012-11-12 11:05 | 44 | IR1177 SH-FA 1 and 2 220 kV transmission circuits tripped due to lightning strike with loss of supply to West Coast. | 0.7497 | 0 | Fault | Transend
86 | 28118 | 2012-11-14 12:46 | 25 | IR1178 Rosebery T2 tripped possibly due to grading error with new T2 protection. | 0.3196 | 0 | Fault | Transend
87 | 28120 | 2012-11-27 07:32 | 15 | IR1180 George Town 220 kV Bus Bar tripped due to testing error | 1.0144 | 1 | Fault | Transend
88 | 28122 | 2012-11-30 21:17 | 7024 | IR1188 PM-AL 110 kV transmission circuit tripped due to bushfire, with loss of supply at Arthurs Lake. | 24.0619 | 1 | Fault | Force Majeure
89 | 28171 | 2012-12-04 14:12 | 15 | IR1194 Farrell-Rosebery-Queenstown 110 kV transmission circuit tripped - Suspected Lightning | 0.1606 | 0 | Fault | Transend
90 | 28635 | 2013-02-06 06:26 | 63 | IR1215 St Leonards T1 and T2 transformer circuits tripped folllowing a feeder fault due to a protection grading issue.. | 0.1596 | 0 | Fault | Transend
91 | 28973 | 2013-03-06 15:36 | 116 | IR1231 LF-SO-TB and LF-SO 110 kV lines OOS due to fire services direction. | 0.524 | 0 | Scheduled | Fire Service
92 | 29420 | 2013-04-27 13:58 | 1344 | IR1300 LF-SO-TB 110 kV transmission line circuit tripped due to broken conductor at a time of severe winds | 0.2871 | 0 | Fault | Transend
93 | 29422 | 2013-05-09 16:33 | 41 | IR1302 Queenstown 110 kV A Bus tripped due to incorrect protection settings at QT after an inter-trip caused by incorrect isolation for planned work at Newton. | 0.2476 | 0 | Fault | Transend
94 | 29424 | 2013-05-22 11:16 | 17 | IR1304 Risdon E352 feeder tripped due to error during planned work on SCADA. The consequent overload of customer plant caused a loss of supply. | 0.1398 | 0 | Fault | Transend
95 | 29626 | 2013-06-12 14:54 | 1304 | IR1334 FA-QU-SR-HM 110 kV transmission circuit tripped due to failed insulator. | 14.2145 | 1 | Fault | Transend
97 | 29849 | 2013-07-16 19:11 | 30 | IR1342 Mornington 33kV D252 tripped due to equipment failure, with smoke causing forced outage of 33 kV A and B buses. 33kV B Bus energised at 1941. Howrah Zone energised at 1952. Cambridge Zone backfed by Aurora at 1958. Fire Brigade have left site. | 0.2855 | 0 | Fault | Transend
98 | 30277 | 2013-08-19 01:36 | 104 | IR26 QT-NT 110 kV transmission circuit tripped with lightning in area. | 0.2812 | 0 | Fault | Transend
99 | 30467 | 2013-09-24 16:33 | 24 | IR1430 RB T1 and FA-RB-QT 110 kV circuits tripped following a human error during planned maintenance work, with loss of supply at Rosebery, Queenstown and Newton. | 0.4936 | 0 | Fault | Transend
100 | 30602 | 2013-10-01 00:25 | 220 | IR1449 FA-JB 220 kV and FA-RB-QT 110 kV transmission circuits tripped with LOS at Queenstown and Newton, suspect lightning. | 0.5608 | 0 | Fault | Transend
101 | 30896 | 2013-12-11 00:42 | 70 | IR1532 Boyer 6.6 kV B Bus tripped. | 0.4562 | 0 | Fault | Transend

## TQS0118 avoutdur ptable
Data
Date/Time | Count of LOS duration | Average of LOS duration2
2006 | 26 | 53.8462
2007 | 21 | 142.7619
2008 | 10 | 112.9
2009 | 19 | 67.1579
2010 | 13 | 127.7692
2011 | 15 | 90.8667
2012 | 26 | 110.8846
2013 | 17 | 160.9412
Total Result | 147 | 105.0748
2013 high duration due to failed TL insulator
[6 empty] | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013
|  |  | TQS0118 | Average outage duration | minutes | 53.8462 | 142.7619 | 112.9 | 67.1579 | 127.7692 | 90.8667 | 110.8846 | 160.9412

## TQS0118 All LOS Event Summary
Loss of Supply Event Summary - Jan 2006 and Dec 2013
Event No. | WASP Outage Key | Date/Time | Duplicate? | Duration (mins) | LOS duration | Description | System Minutes | Fault / Scheduled | Instigator
1 | 4104 | 2006-01-09 06:57 |  | 211 | 12 | IR208 - PL-ST 110 kV and PL T2 interrupted due to faulty directional overcurrent relay element at PL. | 0.1089 | Fault | Transend
2 | 4143 | 2006-01-17 13:39 | 11922 | 539 | 260 | IR209 - BU-PL 110 kV interrupted due to broken conductor loop. | 3.265 | Fault | Transend
3 | 4145 | 2006-01-20 04:45 | 3786 | 207 | 185 | IR223 - Kermandie Substation transformer T2 interrupted due to incorrect CT secondary connections (during commissioning). This resulted in feeder faults causing TF REF protection operation. | 0.3571 | Fault | Transend
4 | 4147 | 2006-01-20 05:18 | 33 | 827 |  | IR219 - WA-BW 110 kV interrupted due to lightning strike causing two conductors to break. | 1.886 | Fault | Transend
5 | 4149 | 2006-01-20 05:39 | 21 | 218 |  | IR233 - LF-RK 2-SO interrupted during severe lightning storms. Lindisfarne circuit breaker F152 failed to reclose due to incorrect auto reclose settings. | 0.0163 | Fault | Transend
6 | 4152 | 2006-01-20 07:40 | 121 | 6 |  | IR233 - SH-WV and DP-WV 110 kV interrupted during severe lightning storms. | 0.091 | Fault | Transend
7 | 4155 | 2006-01-24 04:45 | 5585 | 130 | 19 | IR223 - Kermandie Substation transformer T2 interrupted due to incorrect CT secondary connections (during commissioning). This resulted in feeder faults causing TF REF protection operation. | 0.0382 | Fault | Transend
8 | 4214 | 2006-01-27 10:43 | 4678 | 37 | 12 | IR230 - Load shedding occurred at Risdon Substation due to incorrectly applied ScriptCalc during planned work. | 0.5154 | Fault | Transend
9 | 4211 | 2006-02-20 11:45 | 34622 | 3 | 3 | IR236 - Three 11 kV feeders (FZ9, FZ10, FZ11) tripped due to incorrect switching during planned work at the Risdon Substation. | 0.014 | Fault | Transend
10 | 4212 | 2006-02-27 18:03 | 10458 | 73 | 74 | IR237 - Port Latta T1 transformer isolated due to protection operations resulting from incorrect protection settings applied prior to commissioning of new plant. | 0.5379 | Fault | Transend
11 | 4282 | 2006-03-01 08:15 | 2292 | 8 | 9 | IR238 - Burnie Substation 110 kV 'B' bus and Smithton Substation interrupted during planned work due to protection scheme design error. | 0.0859 | Fault | Transend
12 | 4280 | 2006-03-17 12:08 | 23273 | 7 | 7 | IR263 - Load shed within Zinifex installation due to ScriptCalc switching error in control room. | 0.16 | Fault | Transend
13 | 5092 | 2006-04-08 12:44 | 31716 | 64 | 63 | IR270 - George Town Substation 22 kV 'A' Bus interrupted. 22 kV circuit breaker (E252) failure. Under investigation by manufacturer. | 0.2796 | Fault | Transend
14 | 5107 | 2006-04-23 12:37 | 21593 | 18 | 24 | IR276 - FA-QU-SR-HM 110 kV interrupted. LV feeder fault (tree across feeder) at Que Substation caused transmission line protection to operate. Cause of maloperation unknown. | 0.2779 | Fault | Transend
15 | 5495 | 2006-05-23 07:59 | 42922 | 36 | 28 | IR300 - UFLS initiated at Comalco, Zinifex, Temco and Boyer due to drop in system frequency resulting from Generator and NEMMCO activities. | 3.5441 | Fault | NEMMCO
16 | 5557 | 2006-06-02 22:01 | 15242 | 45 | 45 | IR313 - Trevallyn 22 kV 'B' Bus isolated due to failure by DNSP Operators to follow agreed feeder earthing practices during planned work. | 0.4396 | Fault | Transend
17 | 5558 | 2006-06-08 11:47 | 8026 | 9 | 9 | IR315 - Burnie-Port Latta 110 kV, Port Latta transformer T2 and two 22 kV feeders interrupted due to a commissioning error resulting from incorrect optical fibre labelling. | 0.0444 | Fault | Transend
18 | 5647 | 2006-06-15 14:34 | 10247 | 23 | 23 | IR322 - 22 kV Feeder No. 2 at Meadowbank Substation interrupted due to Contractor striking underground cable during post hole excavations. | 0.0073 | Fault | Transend
19 | 5643 | 2006-06-28 07:15 | 18281 | 225 | 62 | IR325 - BU-HM 110 kV interrupted due to bird streamer causing insulator flashover at tower 78. | 0.0225 | Fault | Transend
20 | 5645 | 2006-06-28 12:40 | 325 | 61 | 62 | IR326 - Supply interrupted to Palmerston Substation 22 kV 'B' bus due to incorrect SCADA configuration applied by Contractor during pre-commissioning. | 0.2072 | Fault | Transend
21 | 5698 | 2006-07-09 13:22 | 15882 | 13 | 13 | IR328 - Hadspen Substation 22 kV feeder M252 interrupted due to poor secondary isolation processes by Contractor while downloading feeder protection configuration. | 0.027 | Fault | Transend
22 | 5680 | 2006-07-09 14:33 | 71 | 13 | 13 | IR328 - Hadspen Substation 22 kV 'B' Bus interrupted due to poor secondary isolation processes utilised by Contractor while downloading feeder protection configuration. | 0.0786 | Fault | Transend
23 | 7383 | 2006-07-22 11:51 | 18558 | 91 |  | IR344 - Basslink circuit interrupted resulting in FCSPS operation. Transend did not cause or contribute to the outage. | 0.2532 | Fault | Basslink
24 | 7384 | 2006-07-22 14:52 | 181 | 620 |  | IR344 - Basslink circuit interrupted resulting in FCSPS operation. Transend did not cause or contribute to the outage. | 2.1364 | Fault | Basslink
25 | 5862 | 2006-08-01 12:32 | 14260 | 73 | 79 | IR337 - Supply interrupted to transformer T4 and 22 kV 'A' and 'B' buses at Hadspen Substation due to transformer fault. | 0.6788 | Fault | Transend
26 | 7382 | 2006-08-18 11:56 | 24444 | 39 |  | Basslink tripped at Loy Yang when importing 299MW initiating FCSPS action at Comalco, Zinifex and Temco. | 2.9231 | Fault | Basslink
27 | 7573 | 2006-09-14 10:33 | 38797 | 107 |  | IR347 - Basslink trip due to loss of supply to valve house cooling fans at Loy Yang converter station. FCSPS initiated resulting in load shedding at Comalco, Temco and Zinifex as designed. | 3.3902 | Fault | Basslink
28 | 7744 | 2006-10-04 14:38 | 29045 | 74 | 72 | IR355 - Palmerston Substation transformer T4 interrupted. Contractor left TF neutral CT links open resulting in transformer trip in response to a feeder fault. ITOMS: Not included as the CT in question is integral to protection systems that are protecting against LV faults only. | 0.2487 | Fault | Transend
29 | 7746 | 2006-10-05 15:51 | 1513 | 243 | 204 | IR357 - Norwood-Scottsdale-Derby 88 kV interrupted. No cause identified. | 1.6502 | Fault | Transend
30 | 8613 | 2006-10-12 15:31 | 10060 | 257 | 74 | IR359 - Lindisfarne-Rokeby No 1 110 kV transmission circuit interrupted due to bushfire. Lindisfarne-Rokeby No 2-Sorell 110 kV transmission circuit interrupted due to incorrect substation configuration. ITOMS: Not included as bus coupler CB is on 22 kV. | 0.5514 | Fault | Transend
31 | 7855 | 2006-10-13 12:36 | 1265 | 16 | 14 | IR361 - Devonport 22 kV 'C' Bus interrupted due to Contractor isolations error during commissioning tests for 110 kV bus zone protection. | 0.0994 | Fault | Transend
32 | 7890 | 2006-11-09 19:45 | 39309 | 35 | 32 | IR366 - Mowbray Substation 22 kV B Bus and transformer T2 were interrupted in response to a 22 kV feeder fault due to incorrect protection wiring design. | 0.1314 | Fault | Transend
33 | 8098 | 2006-12-10 12:32 | 44207 | 48 |  | IR375 - Basslink loss of link signal received due to extreme temperatures in Victoria, resulting in SPS load shedding at Comalco and TEMCO. | 1.3841 | Fault | Basslink
34 | 8314 | 2006-12-20 12:39 | 14407 | 2 | 2 | IR377 - Burnie-Port Latta 110 kV transmission circuit interrupted due to human error during protection testing. | 0.0275 | Fault | Transend
35 | 8332 | 2007-01-09 18:27 | 29148 | 17 | 17 | IR379 - Queenstown Substation interrupted due to inadvertent protection operation. Source of protection operation unknown. | 0.1926 | Fault | Transend
36 | 8337 | 2007-01-12 22:17 | 4550 | 103 | 102 | IR380 - Risdon Substation transformer T5 and T6 interrupted due to faulty relay causing inadvertent circuit breaker fail (CBF) operation. | 0.9034 | Fault | Transend
37 | 8346 | 2007-01-16 09:56 | 5019 | 899 | 16 | IR382 - Queenstown Substation transformers T3 and T4 interrupted due to a partially decommissioned control cable causing inadvertent trip signals. | 0.1179 | Fault | Transend
38 | 8350 | 2007-01-19 13:27 | 4531 | 63 | 63 | IR383 - Tungatinah Substation transformer T9 interrupted due to suspected lightning. | 0.0264 | Fault | Transend
39 | 8351 | 2007-01-21 00:15 | 2088 | 2225 | 242 | IR384 - Sorell Substation interrupted due to poor circuit breaker design resulting in a cracked bus coupler circuit breaker shutter. Resultant partial discharge and ozone corrosion caused flashover of CT in D252 switchgear cubicle. ITOMS: Not included as CB is low voltage. | 0.4453 | Fault | Transend
40 | 8654 | 2007-02-16 15:10 | 38335 | 84 | 85 | IR389 - Liapootah-Wayatinah 220 kV transmission circuit interrupted due to lightning. The failure of the single protection and telecommunications scheme between Wayatinah and Catagunya caused the circuit breaker A152 to remain closed extending the outage time of the circuit. | 0.0415 | Fault | Transend
41 | 8795 | 2007-02-22 17:02 | 8752 | 50 |  | IR391 - SH-FA 1 and SH-FA 2 220 kV transmission circuits interrupted due to lightning strike. Supply to west coast interrupted. | 1.0371 | Fault | Force Majeure
42 | 8644 | 2007-02-22 18:54 | 112 | 61 | 56 | IR388 - Rosebery Substation 44/22 kV T4 and T5 transformer circuits interrupted during severe lightning storms. | 0.123 | Fault | Transend
43 | 8798 | 2007-02-27 06:20 | 6446 | 18 | 19 | IR394 - Load shedding intitiated at Risdon Substation due to incorrect drawings utilised during transformer maintenance and metering testing. | 0.4054 | Fault | Transend
44 | 9038 | 2007-04-14 04:52 | 66152 | 224 | 224 | IR405 - Mowbray Substation 22 kV 'A' and 'B' buses interrupted due to faulty current transformer. Cause of CT failure unknown. | 0.7855 | Fault | Transend
45 | 9039 | 2007-04-15 17:28 | 2196 | 77 | 79 | IR406 - Palmerston-Avoca 110 kV transmission circuit interrupted due to lightning. | 0.4172 | Fault | Transend
46 | 9040 | 2007-04-18 07:08 | 3700 | 4 | 9 | IR407 - Farrell-Rosebery-Queenstown 110 kV transmission circuit interrupted due to lightning. | 0.0882 | Fault | Transend
47 | 9052 | 2007-04-19 08:44 | 1536 | 640 | 640 | IR411 - Transformer T1 at Que Substation interrupted due to suspected relay failure. | 0.0359 | Fault | Transend
48 | 9173 | 2007-05-04 23:46 | 22502 | 80 | 6 | IR416 - Tungatinah-Butlers Gorge-Derwent Bridge 110 kV transmission circuit interrupted. | 0.0039 | Fault | Transend
49 | 9175 | 2007-05-17 16:32 | 18286 | 79 | 80 | IR421 - Meadowbank Substation transformer T4 interrupted due to incorrect protection settings. ITOMS: Not included as the protection settings that had been applied incorrectly were for low voltage assets only (ie. outside ITOMS scope). | 0.0853 | Fault | Transend
50 | 9176 | 2007-05-18 08:59 | 987 | 1 | 1 | IR422 - Avoca-St Marys 110 kV transmission circuit momentarily interrupted due to lightning strike. | 0.0006 | Fault | Transend
51 | 11331 | 2007-08-06 07:05 | 115086 | 0 | 0 | IR439 - Chapel Street-Kingston-Electrona 110 kV transmission circuit momentarily interrupted during strong winds. | 0.0005 | Fault | Transend
52 | 11332 | 2007-08-09 21:51 | 5206 | 666 | 14 | IR453 - Norwood-Scottsdale-Derby 110 kV transmission circuit interrupted during severe weather. Total outage duration 17 minutes. | 0.0213 | Fault | Transend
53 | 11603 | 2007-09-26 08:09 | 68298 | 79 |  | IR464 - George Town-George Town Converter Station 220 kV transmission circuit interrupted due to sensor failure at George Town Converter Station. | 3.9431 | Fault | Basslink
54 | 11816 | 2007-11-14 13:36 | 70887 | 61 | 33 | IR472 - Sheffield Substation 110 kV 'A' Bus interrupted due to inappropriate temporary protection settings applied during planned work. | 1.3591 | Fault | Transend
55 | 12014 | 2007-12-06 05:03 | 31167 | 91 | 92 | IR477 - Sorell Substation transformer T1 interrupted due to 22 kV CT flashover. Root cause of flashover unknown. | 0.2583 | Fault | Transend
56 | 12017 | 2007-12-06 21:02 | 959 | 802 | 1219 | IR479 - Tungatinah-Butlers Gorge-Derwent Bridge 110 kV transmission circuit interrupted due to current transformer failure. | 0.0963 | Fault | Transend
57 | 12146 | 2007-12-20 00:55 | 18953 | 720 | 1 | IR482 - Farrell-Que-Savage River-Hampshire 110 kV transmission circuit interrupted during lightning storms. | 0.0137 | Fault | Transend
58 | 12347 | 2008-02-18 07:17 | 86782 | 303 | 305 | IR494 - Que Substation transformer T1 interrupted. Cause unknown. | 0.9836 | Fault | Transend
59 | 12348 | 2008-02-23 16:31 | 7754 | 48 | 48 | IR495 - Tungatinah 22 kV 'A' Bus and transformer T9 interrupted due to excessive dust on 22 kV feeder earth fault relay contacts causing feeder protection to operate slower than transformer protection. | 0.0115 | Fault | Transend
60 | 12660 | 2008-03-02 10:36 | 11165 | 292 | 305 | IR496 - Palmerston-Avoca and Avoca-St Marys 110 kV transmission circuits interrupted due to VT failure at Avoca Substation. | 0.5753 | Fault | Transend
61 | 12958 | 2008-04-03 02:04 | 45568 | 18 |  | IR500 - Chapel Street-Kingston-Knights Road 110 kV transmission circuit interrupted during strong winds. | 0.0629 | Fault | Force Majeure
62 | 12959 | 2008-04-03 02:37 | 33 | 270 |  | IR501 - Lindisfarne-Sorell-Triabunna 110 kV transmission circuit interrupted six times during widespread destructive winds. | 0.37 | Fault | Force Majeure
63 | 12960 | 2008-04-03 08:30 | 353 | 176 |  | IR502 - Lindisfarne-Rokeby No 1 110 kV transmission circuit interrupted during strong winds. | 0.0525 | Fault | Force Majeure
64 | 12957 | 2008-04-07 07:53 | 5723 | 568 | 231 | IR498 - Que Substation 22 kV bus interruption due to current transformer failure following down stream feeder fault. | 0.8172 | Fault | Transend
65 | 13104 | 2008-06-01 09:54 | 79321 | 98 | 98 | IR543 - Tungatinah Substation transformer T9 interrupted due to faulty 22 kV circuit breaker operating mechanism (C252) preventing C252 from tripping. TF protection subsequently operated. Report Number 1325 has been duplicated. See outage ID13559 for another fault report 1325 (LI-PM 220kV) and RIMsys report IR569. D Alimu | 0.023 | Fault | Transend
66 | 13234 | 2008-06-08 00:31 | 9517 | 25 |  | IR538 - Basslink FCSPS operation due to circuit breaker failure at Loy Yang Converter Station resulting in contracted load shedding. This report 1327 have been duplicated with another number ID1356. G.Hwaba | 3.323 | Fault | Basslink
67 | 13235 | 2008-06-23 03:13 | 21762 | 16 | 16 | IR539 - Electrona Substation 11 kV Bus interruption due to suspected earth voltage rise (resulting from feeder fault) affecting electronics within recloser control cabinet. | 0.0263 | Fault | Transend
68 | 13236 | 2008-06-25 04:19 | 2946 | 72 | 72 | IR540 - Electrona Substation 11 kV Bus interruption due to earth voltage rise under lightning conditions inadvertently causing bus protection to operate. | 0.191 | Fault | Transend
69 | 13561 | 2008-08-14 23:12 | 73133 | 65 |  | IR573 - Basslink interrupted due to fault at Loy Yang. This report 1327 have been duplicated with the other report ID13234. G Hwaba | 3.6734 | Fault | Basslink
70 | 13562 | 2008-08-26 14:56 | 16784 | 212 |  | IR570 - Supply at Newton Substation interrupted due to failure of a generation asset. | 0.318 | Fault | Generator Request
71 | 13609 | 2008-09-16 06:19 | 29723 | 7 | 6 | IR571 - Ulverstone Substation supply interrupted due to wiring error in HV capacitor bank controller. not in ITOMS, cause was 22kV cap bank wiring | 0.0475 | Fault | Transend
72 | 13775 | 2008-10-30 11:55 | 63696 | 15 | 17 | IR588 - Burnie Substation 22 kV Bus A interruption during commissioning of new protection panel. | 0.1569 | Fault | Transend
73 | 16485 | 2008-11-27 16:19 | 40584 | 33 |  | IR600 - Basslink FCSPS operation causing load shedding. Basslink advised trip was caused by a DC line fault. Suspected a lightning strike at Loy Yang. | 0.1751 | Fault | Basslink
74 | 16820 | 2008-12-01 03:45 | 5006 | 28 | 31 | IR607 - FA-RB-QT and QT-NT 110 kV transmission circuits interrupted due to lightning. | 0.2753 | Fault | Transend
75 | 17059 | 2009-01-13 02:26 | 61841 | 737 | 16 | IR616 NN 22kV A Bus tripped during protection testing | 0.0411 | Fault | Transend
76 | 17060 | 2009-01-22 13:59 | 13653 | 15 | 20 | IR621 KR-HR-KE 110kV transmission circuit tripped during strong winds. Cause is under investigation. nit in ITOMS as cause unknown. | 0.047 | Fault | Transend
77 | 17063 | 2009-01-22 17:36 | 217 | 98 | 98 | IR619 - NH 11kV A and B Busses tripped tripped when frame leakage protection operated. Cause under investigation. | 0.5416 | Fault | Transend
78 | 17061 | 2009-01-22 21:03 | 207 | 45 | 35 | IR621 KR-HR-KE 110kV transmission circuit tripped during strong winds. Cause is under investigation. not in ITOMs as cause unknown. | 0.0608 | Fault | Transend
79 | 17984 | 2009-03-29 13:26 | 94583 | 4 |  | IR799 GT-TV No.3 tripped. CTfailure at George Town Substation. | 0.0662 | Fault | Generator Request
80 | 17989 | 2009-04-15 08:25 | 24179 | 12 | 10 | IR778 PM-AV tripped, lightning in area. | 0.0624 | Fault | Transend
81 | 17991 | 2009-04-26 03:27 | 15542 | 187 | 60 | IR776 trip of LF-RK 1 when c252 energised due to protection grading issue. not in ITOMS, this a 22kV protection blocking issue. | 0.1211 | Fault | Transend
82 | 18181 | 2009-05-15 08:56 | 27689 | 27 | 42 | IR773 Farrell-Roseberry 110 kV tripped. | 0.4792 | Fault | Transend
83 | 18640 | 2009-07-02 10:47 | 69231 | 0 |  | UFLS block 1 operated when 2530 MW generation tripped on the mainland. | 0.8431 | Fault | Basslink
84 | 18641 | 2009-07-12 08:27 | 14260 | 64 | 66 | IR751 TU T9 tripped at same time as C252 feeder fault | 0.0208 | Fault | Transend
85 | 18644 | 2009-07-14 12:21 | 3114 | 8 | 9 | IR765 TU T9 tripped while P&T personnel on site and during testing. | 0.0021 | Fault | Transend
86 | 18697 | 2009-08-03 02:48 | 28227 | 112 | 112 | IR705 - Rosebery Substation - the Rosebery T1 and T2 110/44 kV transformer circuits tripped following a feeder fault due to incorrect protection grading. | 1.2108 | Fault | Transend
87 | 18770 | 2009-08-03 03:52 | 64 | 16 | 17 | IR753 Newton 110kV bus bar disconnected. Loss of supply. | 0.0544 | Fault | Transend
88 | 18777 | 2009-08-31 10:28 | 40716 | 33 | 33 | IR726 New Norfolk Substation - the New Norfolk 22kV B bus bar tripped due to protection mal-operation. | 0.1857 | Fault | Transend
89 | 18778 | 2009-08-31 10:34 | 6 | 46 | 47 | IR760 TU-BG-DB tripped during severe wind conditions. | 0.0059 | Fault | Transend
90 | 18780 | 2009-08-31 13:47 | 193 | 57 | 57 | IR762 Tungatinah T9 tripped with a 22kV feeder fault. | 0.0043 | Fault | Transend
91 | 19053 | 2009-09-03 14:21 | 4354 | 26 | 26 | IR763 TU T9 tripped, loss of supply, cause is under investigation, suspect slow clearance of feeder fault. | 0.0037 | Fault | Transend
92 | 19055 | 2009-09-14 10:30 | 15609 | 498 | 489 | IR722 FA-QU-SR-HM tripped due to broken insulator. Loss of supply at Que and Savage River. | 4.9061 | Fault | Transend
93 | 19056 | 2009-09-16 11:50 | 2960 | 39 | 37 | IR817 GT supply bus tripped due to inadequate isolation of trip circuits causing loss of supply. | 0.143 | Fault | Transend
94 | 19062 | 2009-09-27 11:53 | 15843 | 1810 |  | IR721 BU-ST and BU-PL tripped during severe wind storms. | 1.0155 | Fault | Force Majeure
95 | 19399 | 2009-11-18 09:40 | 74747 | 93 | 93 | IR781 Boyer Substation - the Boyer T14 110/6.6 kV transformer tripped due to inappropriate protection settings. | 0.8543 | Fault | Transend
96 | 19637 | 2009-12-30 02:46 | 60066 | 9 | 9 | IR813 Chapel Street 11kV D Busbar tripped. Under investigation. Protection system mal-operation | 0.0059 | Fault | Transend
97 | 20044 | 2010-01-16 20:10 | 25524 | 149 | 149 | IR819 WA T1 tripped, suspect lightning. | 0.0245 | Fault | Transend
98 | 20181 | 2010-01-30 17:36 | 20006 | 1460 | 20 | IR829 BU-ST trip with loss of supply at Smithton Substation | 0.0678 | Fault | Transend
99 | 20900 | 2010-04-29 14:50 | 127994 | 84 | 53 | IR903 Farrell 220 kV A Bus tripped during commissioning work causing loss of supply and generation on the West Coast and load shedding of major industrials. The event was caused by mal-operation of an obsolete protection system. | 2.9477 | Fault | Transend
100 | 21138 | 2010-05-12 09:10 | 18380 | 41 | 31 | IR910 Knights Road Substation - the Knights Road 11 kV A Bus tripped during planned work due to incorrect protection settings. | 0.174 | Fault | Transend
101 | 21091 | 2010-05-18 13:36 | 8906 | 78 | 76 | IR917 George Town Substation - the George Town 22kV B Bus tripped during planned work due to incorrect protection isolation. | 0.2743 | Fault | Transend
102 | 21270 | 2010-06-26 17:25 | 56389 | 1004 | 1042 | IR945 TU-BG-DB 110kV tripped, possibly due to conductor failure. Conductor failure between towers T46-T47 | 0.064 | Fault | Transend
103 | 21403 | 2010-07-22 07:03 | 36818 | 120 | 111 | IR961 Risdon T1, T2 and T3 tripped due to protection maloperation with loss of supply to NyrStar | 1.0945 | Fault | Transend
104 | 21405 | 2010-07-28 10:50 | 8867 | 13 | 9 | IR963 Risdon 11kV Bus Bar tripped during protection remediation work | 0.452 | Fault | Transend
105 | 21964 | 2010-09-11 17:28 | 65198 | 35 | 35 | IR1003 Port Latta-Smithton 110 kV circuit tripped with loss of supply to Port Latta substation due to commissioning error. | 0.2375 | Fault | Transend
106 | 21962 | 2010-09-29 08:05 | 25357 | 30 | 33 | IR1012 Sorell 22 kV B bus tripped while A852 bus coupler was disabled due to high load. | 0.2108 | Fault | Transend
107 | 22049 | 2010-10-12 07:56 | 18711 | 2 | 2 | IR1015 Emu Bay Substation bus tripped during planned work. The investigations have identified that the root cause of the outege was failure of insulator associated with circuit breaker A752 Sprecher & Schuh HPF 311L. White phase porcelain operating arm sheared on closing at the base of the casting. | 0.0069 | Fault | Transend
108 | 22048 | 2010-10-30 08:19 | 25943 | 75 | 85 | IR1021 Newton Substation 110kV bus tripped following a feeder fault. | 0.1329 | Fault | Transend
109 | 22273 | 2010-11-11 10:11 | 17392 | 12 | 15 | IR1036 RI T2 transformer circuit tripped following an over temperature alarm. | 0.6147 | Fault | Transend
110 | 23123 | 2011-02-07 12:40 | 126869 | 26 | 27 | IR1068 New Norfolk-Boyer 1 transmission circuit tripped during planned work. | 1.2551 | Fault | Transend
111 | 23417 | 2011-02-19 11:15 | 17195 | 10 | 13 | IR1074 Queenstown T3 and T4 transformer circuits tripped following a feeder reclose with loss of supply. Primary fault was on customer' s disconnector but there was protection coordination issue which occurred during the restoration process of the faulted feeder. | 0.0261 | Fault | Transend
112 | 23413 | 2011-03-23 20:16 | 46621 | 298 | 318 | IR1094 Sorell T2 transformer circuit tripped causing loss of supply at Sorell substation, due to wildlife incursion during planned work. | 1.8975 | Fault | Transend
113 | 23489 | 2011-03-24 07:08 | 652 | 135 | 135 | IR1142 Sorell A Bus feeders trip due to error during planned work. Inadequate vermin control during substation construction works | 0.1633 | Fault | Transend
114 | 23600 | 2011-04-08 13:32 | 21984 | 3 | 4 | IR1100 Railton 22kV A Bus tripped during protection testing. | 0.016 | Fault | Transend
115 | 23631 | 2011-05-04 19:21 | 37789 | 219 | 214 | IR1108 Lindisfarne-Rokeby Sorell 110kV transmission line tripped causing loss of supply at Rokeby Substation, Suspect cable but cause unknown. | 2.199 | Fault | Transend
116 | 24243 | 2011-07-08 03:42 | 92661 | 5070 | 34 | IR1131 CS-KI-KR tripped with loss of supply at Kingston, Knights Road, Kermandie and Huon River substations. | 1.8447 | Fault | Transend
116 | 24243 | 2011-07-08 03:42 | 92661 | 5070 | 14 | IR1131 CS-KI-KR tripped with loss of supply at Kingston, Knights Road, Kermandie and Huon River substations. | 1.8447 | Fault | Transend
117 | 24244 | 2011-07-12 11:37 | 6235 | 2 | 4 | IR1140 North Hobart feeders tripped during planned work IR1140 North Hobart feeders tripped during planned work | 0.0176 | Fault | Transend
118 | 24403 | 2011-07-14 16:05 | 3148 | 114 | 89 | IR1134 KI T2 tripped on Bucholz alarm and caused loss of supply at Kingston substation. | 1.2172 | Fault | Transend
119 | 24883 | 2011-09-14 14:13 | 89168 | 60 | 56 | IR1161 Port Latta 22kV B Bus tripped due to error during planned work. | 0.2844 | Fault | Transend
120 | 24927 | 2011-09-19 06:49 | 6756 | 208 | 208 | IR1165 Newton 110 kV bus bar tripped due to T2 Bucholz trip, causing loss of supply. | 2.1025 | Fault | Transend
121 | 24782 | 2011-09-19 09:06 | 137 | 25 | 146 | IR1164 Farrell-Rosebery-Queenstown transmission circuit tripped due to equipment failure (A helical dead end failed on FA-RB). | 0.5448 | Fault | Transend
122 | 24926 | 2011-09-19 19:43 | 637 | 16 | 17 | IR1166 BU-PL, BU-ST, SB-WN-ST and PL-ST 110 kV transmission circuits tripped with lightning in area. Loss of supply at Port Latta Substation. | 0.1115 | Fault | Transend
123 | 25082 | 2011-10-26 22:34 | 53451 | 139 |  | IR1179 GT-GC transmission circuit tripped, suspect filter protection trip at Basslink converter station. | 25.8698 | Fault | Basslink
124 | 25258 | 2011-11-24 09:29 | 40975.1333 | 29 |  | SPS trip Temco load | 0.4365 | Fault | Basslink
126 | 25238 | 2011-11-26 09:00 | 2851.25 | 354 |  | IR?? Gordon Substation 200/22 kV T1 and 220 kV B Bus bar trip | 0.0587 | Fault | Generator Request
127 | 25354 | 2011-12-19 10:22 | 33201.6167 | 818 | 84 | IR1211 Sorell Substation 110/22kV transformer T2 tripped due to water ingress. Restoration date and time to be determined | 0.1665 | Fault | Transend
128 | 25519 | 2012-02-01 00:31 | 62769 | 14 |  | IR1226 Nyrstar feeders tripped, suspect due to operation of harmonic filter. | 0.1451 | Fault | MI
129 | 25661 | 2012-02-14 07:34 | 19143 | 21 | 21 | IR1132 Boyer 6.6 kV E Bus Bar tripped during planned work. | 0.0107 | Fault | Transend
130 | 25663 | 2012-02-25 09:08 | 15934 | 761 | 41 | IR1134 Ulverstone feeders (all) tripped during bush fire response, suspect script calc error. | 0.0816 | Fault | Transend
131 | 26161 | 2012-03-15 23:18 | 28210 | 7 | 7 | IR1276 Palmerston-Arthurs Lake 110kV transmission circuit tripped with lightning in the area, suspect lightning. | 0.024 | Fault | Transend
132 | 26162 | 2012-03-20 14:33 | 6675 | 13 | 13 | IR1273 Kingston T2 tripped due to an error during commissioning. | 0.0726 | Fault | Transend
133 | 26186 | 2012-04-06 19:35 | 24782 | 24 | 30 | IR1135 Burnie 110 kV transmission line circuits tripped during severe lightning with LOS at Burnie, Ulverstone, Emu Bay, Port Latta, Smithton and Hampshire substations. | 0.6265 | Fault | Transend
134 | 26244 | 2012-04-11 12:46 | 6791 | 37 | 11 | IR1275 CS-KI-KR 110 kV transmission line circuit tripped during planned work when a tree contacted line. | 0.0774 | Fault | Transend
135 | 26501 | 2012-05-07 23:47 | 38101 | 139 | 139 | IR1282 Boyer 6.6kV A and B bus circuits tripped due to a protection deficiency following faulted customer feeder. | 0.8463 | Fault | Transend
136 | 26558 | 2012-05-10 10:36 | 3529 | 77 | 77 | IR1140 Arthurs Lake T1 transformer circuit tripped with loss of supply at Arthurs Lake when Hydro Pumps were started. investigation not conclusive due to lack of SOE data and lack of protection testing/ investigation. | 0.2631 | Fault | Transend
137 | 26502 | 2012-05-11 23:02 | 2186 | 69 | 65 | IR1284 Boyer 6.6 kV A and B bus circuits tripped due to protection deficiency following faulted customer feeder. | 0.4114 | Fault | Transend
138 | 26557 | 2012-05-12 05:45 | 403 | 15 | 12 | IR1142 FA-RB-QT and QT-NT 110kV transmission circuit tripped with lightning in area with loss of supply to Aurora (Henty Gold) | 0.0219 | Fault | Transend
139 | 27177 | 2012-07-11 23:29 | 87464 | 437 | 438 | IR1217 Huon River customer lost supply for a planned outage with no notification. | 0.056 | Fault | Transend
140 | 27345 | 2012-08-04 08:00 | 33631 | 220 | 220 | IR1159 DB T1 transformer circuit tripped with LOS at Derwent Bridge | 0.0155 | Fault | Transend
141 | 27349 | 2012-09-04 13:44 | 44984 | 4 | 4 | IR1169 Chapel Street feeders (2) tripped during protection testing. | 0.0053 | Fault | Transend
142 | 27620 | 2012-09-07 18:23 | 4599 | 16 | 16 | IR1167 Queenstown-Newton 110 kV transmission circuit tripped with loss of supply at Newton Substation. | 0.0608 | Fault | Transend
143 | 27417 | 2012-09-09 15:38 | 2715 | 218 | 221 | IR1168 LF-SO-TB 110kV transmission circuit was forced out due to insulator damage by shooting. | 0.2882 | Fault | Transend
144 | 27619 | 2012-09-13 11:31 | 5513 | 106 | 121 | IR1113 Farrell-Rosebery-Queenstown 110kV transmission circuit tripped with loss of supply to West Coast. | 2.3228 | Fault | Transend
145 | 27904 | 2012-10-11 09:24 | 40193 | 6 | 6 | IR1171 PM-AV 110 kV transmission line circuit tripped due to incorrect VT selection during planned work. LOS at Avoca and St Marys. | 0.0331 | Fault | Transend
146 | 27973 | 2012-11-09 12:01 | 41917 | 3 | 5 | IR1176 LF-SO-TB 110 kV transmission circuit tripped with lightning in area. | 0.0069 | Fault | Transend
147 | 27974 | 2012-11-12 11:05 | 4264 | 44 | 40 | IR1177 SH-FA 1 and 2 220 kV transmission circuits tripped due to lightning strike with loss of supply to West Coast. | 0.7497 | Fault | Transend
148 | 28118 | 2012-11-14 12:46 | 2981 | 25 | 32 | IR1178 Rosebery T2 tripped possibly due to grading error with new T2 protection. | 0.3196 | Fault | Transend
149 | 28120 | 2012-11-27 07:32 | 18406 | 15 | 18 | IR1180 George Town 220 kV Bus Bar tripped due to testing error | 1.0144 | Fault | Transend
150 | 28121 | 2012-11-30 20:37 | 5105 | 23 | 21 | IR1187 Knights Road transformer circuits tripped with loss of supply. | 0.0923 | Fault | Transend
151 | 28122 | 2012-11-30 21:17 | 40 | 7024 |  | IR1188 PM-AL 110 kV transmission circuit tripped due to bushfire, with loss of supply at Arthurs Lake. | 24.0619 | Fault | Force Majeure
152 | 28171 | 2012-12-04 14:12 | 5335 | 15 | 22 | IR1194 Farrell-Rosebery-Queenstown 110 kV transmission circuit tripped - Suspected Lightning | 0.1606 | Fault | Transend
153 | 28176 | 2012-12-13 06:06 | 12474 | 6 | 12 | IR1199 FA-RB-QT 110 kV transmission circuit tripped with Lightning in area. | 0.0774 | Fault | Transend
154 | 28296 | 2012-12-15 11:05 | 3179 | 59 | 1267 | IR1200 Que T1 transformer tripped | 0.0758 | Fault | Transend
155 | 28297 | 2012-12-24 14:18 | 13153 | 20 | 24 | IR1201 LF-SO-TB 110 kV transmission circuit tripped with lightning in area | 0.0374 | Fault | Transend
156 | 28635 | 2013-02-06 06:26 | 62888 | 63 | 63 | IR1215 St Leonards T1 and T2 transformer circuits tripped folllowing a feeder fault due to a protection grading issue.. | 0.1596 | Fault | Transend
157 | 28833 | 2013-03-05 07:35 | 38949 | 3 |  | IR1230 Port Latta feeders tripped, suspect Grange Resources misoperation in their yard. | 0.0507 | Fault | MI
158 | 28973 | 2013-03-06 15:36 | 1921 | 116 |  | IR1231 LF-SO-TB and LF-SO 110 kV lines OOS due to fire services direction. | 0.524 | Scheduled | Fire Service
159 | 28834 | 2013-03-10 14:15 | 5679 | 8 | 8 | IR1233 FA-QU-SR-HM 110 kV line tripped due to lightning. | 0.088 | Fault | Transend
160 | 28978 | 2013-03-27 09:03 | 24168 | 13 | 13 | IR1260 QT-NT 110 kV transmission circuit tripped during work for new Newton T2 circuit. | 0.0181 | Fault | Transend
161 | 29191 | 2013-04-09 12:19 | 18916 | 13 |  | IR1262 Risdon D352A 11 kV feeder tripped due to intertrip from Nyrstar. | 0.0961 | Fault | MI
162 | 29420 | 2013-04-27 13:58 | 26019 | 1344 | 503 | IR1300 LF-SO-TB 110 kV transmission line circuit tripped due to broken conductor at a time of severe winds | 0.2871 | Fault | Transend
163 | 29421 | 2013-05-01 03:47 | 5149 | 173 | 173 | IR1301 Derwent Bridge 110/22 kV T1 transformer circuit tripped following a feeder fault due to a protection grading issue. | 0.0096 | Fault | Transend
164 | 29422 | 2013-05-09 16:33 | 12286 | 41 | 48 | IR1302 Queenstown 110 kV A Bus tripped due to incorrect protection settings at QT after an inter-trip caused by incorrect isolation for planned work at Newton. | 0.2476 | Fault | Transend
165 | 29424 | 2013-05-22 11:16 | 18403 | 17 | 18 | IR1304 Risdon E352 feeder tripped due to error during planned work on SCADA. The consequent overload of customer plant caused a loss of supply. | 0.1398 | Fault | Transend
166 | 29626 | 2013-06-12 14:54 | 30458 | 1304 | 1298 | IR1334 FA-QU-SR-HM 110 kV transmission circuit tripped due to failed insulator. | 14.2145 | Fault | Transend
167 | 29848 | 2013-07-16 12:50 | 48836 | 166 |  | IR1341 Arthurs Lake T1 transformer tripped due to intertrip from Hydro at pump start. fault oput against feeder as T1 out of service at the time | 0.0005 | Fault | Generator Request
169 | 29849 | 2013-07-16 19:11 | 381 | 30 | 47 | IR1342 Mornington 33kV D252 tripped due to equipment failure, with smoke causing forced outage of 33 kV A and B buses. 33kV B Bus energised at 1941. Howrah Zone energised at 1952. Cambridge Zone backfed by Aurora at 1958. Fire Brigade have left site. | 0.2855 | Fault | Transend
170 | 30274 | 2013-08-05 19:51 | 28840 | 15 | 15 | IR22 Derwent Bridge T1 transformer circuit tripped due to a protection grading issue following a feeder fault. | 0.0011 | Fault | Transend
171 | 30277 | 2013-08-19 01:36 | 19065 | 104 | 176 | IR26 QT-NT 110 kV transmission circuit tripped with lightning in area. | 0.2812 | Fault | Transend
172 | 30314 | 2013-08-20 06:49 | 1753 | 4 | 3 | IR30 DB T1 transformer circuit tripped following a feeder fault due to SEF protection being out of service. | 0.0005 | Fault | Transend
173 | 30467 | 2013-09-24 16:33 | 50984 | 24 | 60 | IR1430 RB T1 and FA-RB-QT 110 kV circuits tripped following a human error during planned maintenance work, with loss of supply at Rosebery, Queenstown and Newton. | 0.4936 | Fault | Transend
174 | 30602 | 2013-10-01 00:25 | 9112 | 220 | 220 | IR1449 FA-JB 220 kV and FA-RB-QT 110 kV transmission circuits tripped with LOS at Queenstown and Newton, suspect lightning. | 0.5608 | Fault | Transend
175 | 30604 | 2013-10-01 03:47 | 202 | 14 | 14 | IR1451 FA-RB-QT 110 kV transmission circuit tripped due to lightning with LOS at Queenstown. | 0.0672 | Fault | Transend
176 | 30653 | 2013-10-15 15:18 | 20851 | 6 | 6 | IR1484 Chapel St 11 kV B Bus tripped during planned work due to an incorrect CB status indication caused by an internal wiring failure. | 0.0123 | Fault | Transend
177 | 30896 | 2013-12-11 00:42 | 81204 | 70 | 71 | IR1532 Boyer 6.6 kV B Bus tripped. | 0.4562 | Fault | Transend
Note on F2: Author: from LOS calculation spreadsheets
Note on F6: Author: cannot find calc sheet
Note on F7: Author: cannot find calc sheet
Note on F8: Author: cannot find calc sheet
Note on G119: Author: 2 outages this day

## TQS0119 and 0121
This data sourced from WASP outage module
| Table 7.1.4 System Parameter 4 – Proper operation of equipment – number of failure events |  | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013
TQS0119 | Failure of protection system | number | 22 | 19 | 8 | 12 | 6 | 5 | 10 | 13
TQS0120 | Material failure of Supervisory Control and Data Acquisition (SCADA) system | number
TQS0121 | Incorrect operational isolation of primary or secondary equipment | number | 4 | 3 | 4 | 4 | 4 | 3 | 3 | 2
| Incorrect operational isolation of primary or secondary equipment |  | 3 | 0 | 0 | 1 | 1 | 1 | 1 | 0
| Incorrect operational isolation of primary or secondary equipment |  | 7 | 3 | 4 | 5 | 5 | 4 | 4 | 2
Info from D13/58901
TQS0119 – Failure of protection system
Network outages are investigated and reported within the TRIM folder 8-16, all incidents investigations within the prescribed period were analysed and any outage that aligned with the following two statements was included.
1. Any protection initiated outage whereby investigations have concluded that no primary fault occurred.
2. Any protection initiated outage whereby investigations have concluded that circuit breaker operations occurred within plant that was not directly connected to the faulted asset.
TQS0121 – Incorrect operational isolation of primary and secondary equipment
Included in the scope
1. Incorrect secondary isolations that resulted in a primary plant operations
2. Incorrect isolations that resulted in a safety incident
3. Incorrect switching operations
Excluded from the scope
1. Incorrect primary and secondary isolations that did not result in a primary plant operations
2. Incorrect isolations whereby the error was identified during work practices and rectified prior to the occurrence of either a primary plant operation or a safety incident.
3. Safety incidents whereby the electrical technician specifically chose not to isolate (live work is permitted within our work procedures)
Info from Deloites
Information contained in table 7.1.4 for the number of failure events has been extracted from the performance reporting system. Included within the scope of incorrect operational isolation of primary or secondary equipment are incorrect secondary isolations resulting in a primary plant operation, incorrect isolations resulting in a safety incident and incorrect switching incidents. Excluded from the scope of incorrect operational isolation of primary or secondary equipment are incorrect secondary isolations that did not result in a primary plant operation, incorrect isolations whereby the error identified was rectified prior to the occurrence of a primary plant operation and safety incidents whereby the electrical technician specifically chose not to isolate.
Note on B7: Author: see prim plant sheet

## TQS0120 SML
From Terry Day AEMO, see D14/4016
Start | Finish | Outage | Outage Mins
2006-09-28 11:26 | 2006-09-28 11:29 | 3:52 | 3.8667
2006-10-12 11:58 | 2006-10-12 12:01 | 3:04 | 3.0667
2006-10-17 13:02 | 2006-10-17 13:05 | 3:40 | 3.6667
2006-12-13 07:57 | 2006-12-13 08:05 | 7:50 | 7.8333 | Start | Count of Outage Mins
2006-12-13 14:17 | 2006-12-13 14:20 | 3:20 | 3.3333 | 2006 | 5
2007-04-26 10:42 | 2007-04-26 10:45 | 3:10 | 3.1667 | 2007 | 2
2007-08-22 12:47 | 2007-08-22 12:51 | 4:08 | 4.1333 | 2008 | 8
2008-09-11 09:31 | 2008-09-11 09:37 | 6:17 | 6.2833 | 2009 | 6
2008-09-11 13:21 | 2008-09-11 13:28 | 7:10 | 7.1667 | 2010 | 9
2008-09-16 09:35 | 2008-09-16 09:38 | 3:08 | 3.1333 | 2011 | 6
2008-09-30 13:12 | 2008-09-30 13:23 | 10:49 | 10.8167 | 2012 | 17
2008-10-01 09:20 | 2008-10-01 09:25 | 5:40 | 5.6667 | 2013 | 2
2008-10-01 09:25 | 2008-10-01 09:29 | 3:50 | 3.8333 | Total Result | 55
2008-10-01 09:29 | 2008-10-01 09:48 | 19:10 | 19.1667
2008-12-09 13:51 | 2008-12-09 13:54 | 3:30 | 3.5
2009-02-17 12:36 | 2009-02-17 12:42 | 6:17 | 6.2833
2009-03-17 14:31 | 2009-03-17 14:34 | 3:10 | 3.1667
2009-09-09 11:35 | 2009-09-09 11:40 | 5:20 | 5.3333
2009-11-05 10:32 | 2009-11-05 10:50 | 17:30 | 17.5
2009-11-11 10:32 | 2009-11-11 10:49 | 17:09 | 17.15
2009-12-10 14:16 | 2009-12-10 14:20 | 3:53 | 3.8833
2010-03-23 09:33 | 2010-03-23 09:38 | 5:00 | 5
2010-03-30 09:31 | 2010-03-30 09:34 | 3:09 | 3.15 |  |  |  | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013
2010-03-30 10:00 | 2010-03-30 10:03 | 3:10 | 3.1667 | TQS0120 | Material failure of Supervisory Control and Data Acquisition (SCADA) system | number | 5 | 2 | 8 | 6 | 9 | 6 | 17 | 2
2010-04-27 10:31 | 2010-04-27 10:35 | 4:06 | 4.1
2010-06-01 10:31 | 2010-06-01 10:34 | 3:40 | 3.6667
2010-09-07 10:31 | 2010-09-07 10:37 | 5:40 | 5.6667
2010-09-28 10:31 | 2010-09-28 10:34 | 3:09 | 3.15
2010-10-05 09:31 | 2010-10-05 09:34 | 3:10 | 3.1667
2010-11-02 09:31 | 2010-11-02 09:35 | 3:45 | 3.75
2011-01-11 10:16 | 2011-01-11 10:21 | 5:27 | 5.45
2011-02-23 11:04 | 2011-02-23 11:09 | 5:30 | 5.5
2011-02-23 14:22 | 2011-02-23 14:26 | 4:45 | 4.75
2011-03-01 09:06 | 2011-03-01 09:09 | 3:29 | 3.4833
2011-03-03 10:01 | 2011-03-03 10:04 | 3:40 | 3.6667
2011-03-03 12:01 | 2011-03-03 12:04 | 3:19 | 3.3167
2012-04-03 10:31 | 2012-04-03 10:35 | 3:21 | 3.35
2012-04-16 13:28 | 2012-04-16 13:33 | 4:13 | 4.2167
2012-04-24 10:31 | 2012-04-24 10:34 | 3:07 | 3.1167
2012-05-01 10:41 | 2012-05-01 10:44 | 3:09 | 3.15
2012-05-22 11:16 | 2012-05-22 11:20 | 3:16 | 3.2667
2012-06-26 15:11 | 2012-06-26 15:14 | 3:29 | 3.4833
2012-07-17 10:31 | 2012-07-17 10:34 | 3:17 | 3.2833
2012-07-31 11:31 | 2012-07-31 11:34 | 3:19 | 3.3167
2012-08-07 12:31 | 2012-08-07 12:34 | 3:20 | 3.3333
2012-08-14 11:21 | 2012-08-14 11:24 | 3:18 | 3.3
2012-08-21 11:51 | 2012-08-21 11:54 | 3:10 | 3.1667
2012-09-12 14:06 | 2012-09-12 14:10 | 4:09 | 4.15
2012-09-18 15:07 | 2012-09-18 15:10 | 3:21 | 3.35
2012-09-20 15:06 | 2012-09-20 15:10 | 4:10 | 4.1667
2012-10-30 11:48 | 2012-10-30 11:53 | 5:10 | 5.1667
2012-11-20 09:57 | 2012-11-20 10:02 | 4:42 | 4.7
2012-11-20 10:56 | 2012-11-20 10:59 | 3:04 | 3.0667
2013-02-05 11:02 | 2013-02-05 11:06 | 3:41 | 3.6833
2013-09-18 14:01 | 2013-09-18 14:07 | 6:22 | 6.3667

## TQS02 MIC
for MIC historical data see TRIM 12/6650/6/4/2

## Prim Plant switching errors
Outage Query
Outage ID | WASP Outage Key | Source ID | Planned Start Time | Planned End Time | Year | Actual Start Time | Actual End Time | Duration (Min) | Element ID | Element Name | Element Type | Request Type | Request Reason | Request Instigator | Status | Out of Service | Unserved MW Min | Included | Reason | Comment | CAPEX | AER STPIS
98866 | 4211 | 1148 |  |  | 2006 | 2006-02-20 11:45 | 2006-02-20 11:48 | 3 | E0240 | RI 11 kV T3 Feeder Circuit | Feeder | Fault | Switching Error | Transend | Completed | TRUE | 25 | TRUE |  | IR236 - Three 11 kV feeders (FZ9, FZ10, FZ11) tripped due to incorrect switching during planned work at the Risdon Substation. | FALSE | Undefined
98867 | 4211 | 1148 |  |  |  | 2006-02-20 11:45 | 2006-02-20 11:48 | 3 | E0241 | RI 11 kV U3 Feeder Circuit | Feeder | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR236 - Three 11 kV feeders (FZ9, FZ10, FZ11) tripped due to incorrect switching during planned work at the Risdon Substation. | FALSE | Undefined
98868 | 4211 | 1148 |  |  |  | 2006-02-20 11:45 | 2006-02-20 11:48 | 3 | E0242 | RI 11 kV V3 Feeder Circuit | Feeder | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR236 - Three 11 kV feeders (FZ9, FZ10, FZ11) tripped due to incorrect switching during planned work at the Risdon Substation. | FALSE | Undefined
98874 | 4214 | 1141 |  |  | 2006 | 2006-01-27 10:43 | 2006-01-27 11:20 | 37 | E0231 | RI 11 kV D Bus | Bus | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR230 - Load shedding occurred at Risdon Substation due to incorrectly applied ScriptCalc during planned work. | FALSE | Undefined
98871 | 4214 | 1141 |  |  |  | 2006-01-27 10:43 | 2006-01-27 11:20 | 37 | E0228 | RI 11 kV A Bus | Bus | Fault | Switching Error | Transend | Completed | TRUE | 918 | TRUE |  | IR230 - Load shedding occurred at Risdon Substation due to incorrectly applied ScriptCalc during planned work. | FALSE | Undefined
98872 | 4214 | 1141 |  |  |  | 2006-01-27 10:43 | 2006-01-27 11:20 | 37 | E0229 | RI 11 kV B Bus | Bus | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR230 - Load shedding occurred at Risdon Substation due to incorrectly applied ScriptCalc during planned work. | FALSE | Undefined
98873 | 4214 | 1141 |  |  |  | 2006-01-27 10:43 | 2006-01-27 11:20 | 37 | E0230 | RI 11 kV C Bus | Bus | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR230 - Load shedding occurred at Risdon Substation due to incorrectly applied ScriptCalc during planned work. | FALSE | Undefined
98936 | 4280 | 1153 |  |  | 2006 | 2006-03-17 12:08 | 2006-03-17 12:15 | 7 | E0231 | RI 11 kV D Bus | Bus | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR263 - Load shed within Zinifex installation due to ScriptCalc switching error in control room. | FALSE | Undefined
98933 | 4280 | 1153 |  |  |  | 2006-03-17 12:08 | 2006-03-17 12:15 | 7 | E0228 | RI 11 kV A Bus | Bus | Fault | Switching Error | Transend | Completed | TRUE | 285 | TRUE |  | IR263 - Load shed within Zinifex installation due to ScriptCalc switching error in control room. | FALSE | Undefined
98934 | 4280 | 1153 |  |  |  | 2006-03-17 12:08 | 2006-03-17 12:15 | 7 | E0229 | RI 11 kV B Bus | Bus | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR263 - Load shed within Zinifex installation due to ScriptCalc switching error in control room. | FALSE | Undefined
98935 | 4280 | 1153 |  |  |  | 2006-03-17 12:08 | 2006-03-17 12:15 | 7 | E0230 | RI 11 kV C Bus | Bus | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR263 - Load shed within Zinifex installation due to ScriptCalc switching error in control room. | FALSE | Undefined
103227 | 17987 | 1433 |  |  | 2009 | 2009-04-07 08:19 | 2009-04-07 08:21 | 2 | E0535 | SH 220/110 kV T2 Transformer Circuit | Transformer | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR796 Sheffield T2 tripped SH 220/110kV T2 was inadvertently removed form service during switching to reconfigure 220kV switchyard for purpose of taking B bus out of service. Operator failed to select correct VT selection | FALSE | Non-Critical
121556 | 21232 | 1596 |  |  | 2010 | 2010-06-19 08:26 | 2010-06-19 10:24 | 118 | E1734 | GT-TV 3 220 kV Transmission Circuit | Transmission | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR 943 George Town Substation GT-TV3 tripped GT-Tamar Valley No 3 220kV circuit disconnection occurred after the Operator inadvertently removed fuses for VT A797. It resulted in loss of generation at AETV Power Station. Generator Contingency Scheme was initiated and sent a trip signal toTEMCO with approximately 100MW load was interrupted as part of GCS scheme | FALSE | Undefined
148383 | 25147 | 1713 |  |  | 2011 | 2011-11-25 05:59 | 2011-11-25 06:12 | 13 | E0125 | MB-NN 110 kV Transmission Circuit | Transmission | Fault | Switching Error | Transend | Completed | TRUE | 0 | TRUE |  | IR1194 Meadowbank-New Norfolk 110kV transmission circuit tripped | FALSE | Non-Critical
168472 | 27177 | 1118480 |  |  | 2012 | 2012-07-11 23:29 | 2012-07-12 06:46 | 437 | E1616 | HR 11 kV A Bus Circuit | Bus | Fault | Switching error | Transend | Completed | TRUE | 105 | TRUE |  | IR1217 Huon River customer lost supply for a planned outage with no notification. | FALSE | Undefined