## Contents
Electricity Distribution Network Service Provider F-factor Reporting Template
Table of contents
| Cover sheet | 2. Fire start report
| 1. F-factor summary | 3. Systems and Audit
Cover sheet
1. F-factor summary
3. Systems and Audit
2. Fire start report

## Cover
Distribution Network Service Provider
Fire start report
This template is to be used by a DNSP to provide a fire start report to the AER in accordance with section 5 of the F-factor Order in Council.
Colour coding of input sheets:
Dark blue = AER headings
Grey = AER instructions
Yellow = Input cells
Light orange = Automatically-generated cells
Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so.
The cells and structure of the spreadsheet is locked to prevent inadvertent interference with the automated settings.
All dollar amounts are to be unrounded, and in nominal terms.
DNSP: |  | United Energy
DNSP - trading name: |  | United Energy Distribution Pty Ltd
DNSP - Australian business number: |  | 70 064 651 029
Reporting year: |  | 2019/20
Business address | Address |  | 43 - 45 Centreway
| Suburb |  | Mt Waverley
|  | State | Victoria | Postcode | 3149
Postal address | Address |  | P.O Box 449
| Suburb |  | Mt Waverley
|  | State | Victoria | Postcode | 3149
Contact name/s | Trevor Fisher
Contact phone/s | 0418993821
Contact email address/s | trevor.fisher@ue.com.au

## 1. F-Factor summary
United Energy | IRU target: | 22.3 |  | AusNet Services | CitiPower | Jemena | Powercor | United Energy
F-factor data reporting | IRU amount: | 15.24 | 2016/17 | 247.7 | 3.4 | 9.7 | 468 | 22.3
2019/20 | Revenue adjustment: | 105900 | 2017/18 | 247.7 | 3.4 | 9.7 | 468 | 22.3
|  |  | 2018/19 | 247.7 | 3.4 | 9.7 | 468 | 22.3
Table 2: Summary of total fire starts by F factor Order definition |  |  | 2019/20 | 221.1 | 3.4 | 9.7 | 412.8 | 22.3
This is a summary of data in worksheet "2. Fire Start Report" | [7 empty] | 22.3
Kind of Fire Start by definition of fire start under clause 5 of F-factor Order | Total fires by cause
Started in or originated from a distribution system | 88
Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | 15 |  | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system : 15
Started by any person, bird, reptile or other animal coming into contact with a distribution system | 2 |  | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system : 2
Started by lightning striking a distribution system or a part of a distribution system | 3 |  | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system : 3
Started by any other thing forming part of or coming into contact with a distribution system | 2 |  | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system : 2
Otherwise started by a distribution system | 0 |  | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system : 0
Total | 110 |  | Total : 110
Total :
Total :
:
:
:
:
:
:
Overhead conductors
- overhead conductor (bare; aluminium core steel reinforced)
- overhead conductor (bare; all aluminium conductor)
- overhead conductor (bare; copper)
- overhead conductor (bare; steel)
- overhead conductor (ABC)
- overhead conductor (covered uninsulated)
- overhead conductor (insulated)
Service lines
- overhead service conductor (residential)
- overhead service conductor (commercial / industrial)
- overhead service conductor (subdivision / construction)
- overhead service conductor (other)
- underground service cable (residential)
- underground service cable (commercial / industrial)
- underground service cable (subdivision / construction)
- underground service cable (other)
Underground cables
- underground cable
- underground communications cable
Poles
- pole (concrete)
- pole (steel)
- pole (wood)
Crossarms
- crossarm (wood)
- crossarm (steel)
- crossarm (other)
Overhead assets
- capacity balancing units
- connector / termination
- dropper / bridge
- guy wire
- insulator tie wires / connections
- insulators
- tower
- traction lines
Underground assets
- LV pillar
- services pit
Transformers
- transformer (pole mounted)
- transformer (kiosk mounted)
- transformer (ground outdoor mounted)
- transformer (indoor chamber mounted)
- transformer (any other type)
- measurement transformer (current transformer)
- measurement transformer (voltage transformer)
- measurement transformer (capacitive voltage transformer)
Fuses and switchgear
- fuse (boric acid)
- fuse (EDO fuse)
- fuse (Fault Tamer)
- fuse (powder filled)
- fuse (any other type)
- circuit breaker
- switch (disconnector/isolator)
- switch (earth)
- switch (FuseSaver)
- switch (any other type)
SCADA, network control and protection systems
- audio frequency load controller (AFLC)
- arc suppresion coil
- automatic circuit recloser (ACR)
- communications linear assets
- communications network assets
- communications site infrastructure
- field devices
- local network wiring assets
- master station assets
- neutral earthing resistor
- oil-filled circuit recloser (OCR)
- rapid earth fault current limiter (REFCL)
- surge diverter
- voltage regulator
Public lighting
- brackets (major road)
- brackets (minor road)
- lamps (major road)
- lamps (minor road)
- luminaries (major road)
- luminaries (minor road)
- poles / columns (major road)
- poles / columns (minor road)
Other
- connection box
- earth / earthing
Extra low voltage AC (<50V)
Low voltage AC (<1kV)
2.2kV AC
6.6kV AC
11kV AC
12.7kV AC (SWER)
22kV AC
33kV AC
66kV AC
132kV AC
220kV AC
330kV AC
500kV AC
Extra low voltage DC (<120V ripple free)
Low voltage DC (<1.5kV)
600V DC
1500V DC
Earthing cable
single wire earth return (SWER)
single phase
two phase
three phase
Negligible: no ground fire
Localised: less than 10 sq.m
Small: 10 - 1000 aq.m
Medium: 1000 sq.m - 10 ha
Large: more than 10 ha
Contents

## 2. Individual fire start info
United Energy
F-factor data reporting
2019/20
Instructions:
Enter into this worksheet fire start data, from any IT system, which have been recorded by [DNSP Name]. Note that fire starts must be in accordance with the definition of a fire start in the Order In Council.
"Fire" should be interpreted using its common meaning and can be defined as a process in which substances combine chemically with oxygen from the air and typically give out bright light, heat and smoke. A fire should be recorded where there is evidence of smoking, charring, scorching, burning or any other evidence that a fire had occurred.
[DNSP Name] must provide:
Table 3 - Individual Fire Starts
(1) Date - dd/mm/yyyy
(2) Time - if known, the 24-hour time of the fire start hh:mm
(3) Latitude and longitude of the fire start as decimal coordinates
(4) Address of the property on which the incident occurred or closest to the incident
(5) Asset number for the asset nearest the fire start
#REF!
(7) Voltage on the line in which the fire start occurred (note: this may not be the nearest polyphase overhead line)
(8) Network categorisation - CBD, Urban, Rural Long or Rural Short
(9) Asset type of primary asset causing fire in accordance with OSIRIS asset categories
(10) Where the asset involved in the fire is a transformer or an overhead or underground line, provide the phase, or phases, of the line or transformer
(11) Kind of fire start in accordance with categories specified in Clause 5 of the F-factor Order-In-Council
(12) Identify the location of the fire start in accordance with the categories specified in Clause 11(b) of the F-factor Order-In-Council
(13) Provide the BOM fire danger rating applicable at the time of the fire start (data is available on the EM-COP website)
(14) [DNSP Name]'s record number for the incident
(15) ESV's OSIRIS reference number for the incident
(16) Free text description of the fault containing relevant comments from field reports
Table 2: Individual Fire Starts
Number | Fire starts | [8 empty] | Fire Type |  |  | Risk Factors |  |  |  | IRU amount | Addition Information
Column1 | Date 1 | Time 2 | Latitude 3 | Longitude 3 | Address of incident 4 | ID of nearest asset 5 | ID of nearest polyphase line 6 | Voltage of line in which fire start occurred 7 | Network categorisation 8 | Type of primary asset involved in fire start 9 | Phase(s) of line or transformer 10 | Kind of fire start as per Clause 5 of F-factor Order-In-Council 11 | Location area 12 | Location multiplier | Fire danger rating 13 | Danger multiplier | Product of multipliers | DNSP record number 14 | OSIRIS (ESV) reference number 15 | Fault description 16 | Overhead conductors
1 | 2019-07-01 | 11:41 | -38.2188 | 145.1724 | 1003 FRANKSTON-FLINDERS ROAD, SOMERVILLE VIC 3912 | 8822258 | HGS22 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1308097 | 20190705UTD_01 | Council Tree branch (undeclared area so UE) brought down HV in Ftn Flinders Rd on tee cond & caused sparking which caused approx 1m sq grass fire on O/H between LIS# PO-8822258. Fire report # 6565 | - overhead conductor (bare; aluminium core steel reinforced)
2 | 2019-07-11 | 9:33 | -38.0089 | 145.2068 | 221-231 HAMMOND ROAD, DANDENONG SOUTH VIC 3175 | 8830311 | DSH23 | 22kV AC | Urban | - capacity balancing units | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1311704 | 20190813UTD_01 | CAP HAMMOND N221 RHUR reported as arcing / sparking/fire coming from vacuum switch (es). | - overhead conductor (bare; all aluminium conductor)
3 | 2019-07-17 | 6:27 | -37.8511 | 145.1233 | 326-328 BURWOOD HIGHWAY, BURWOOD VIC 3125 | 7002221 | EB11 | Low voltage AC (<1kV) | Urban | - services pit | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1313896 | 20190725UTD_01 | Pit is at tram pole # 88. On sth side of Tram track 50 mtrs east of Renow st Burwood. Fire in the pit and wires are fire damaged. Fire start but no damage to anything other than our wiring in the pit. Closest LIS 7002221 | - overhead conductor (bare; steel)
4 | 2019-07-29 | 19:36 | -38.314 | 145.1388 | 96 COOLART ROAD, TUERONG VIC 3915 | 1110660 | HGS22 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1318437 | 20190808UTD_02 | ABICARE N90 COOLART single phase S/Stn: Crew replaced 5 amp EDO on south side phase. Cause: HV fuse was candling and finally failed. Note: S/Stn pole has animal proofing installed. | - overhead conductor (ABC)
5 | 2019-08-07 | 7:19 | -37.908 | 145.098 | 102 HAUGHTON ROAD, OAKLEIGH VIC 3166 | 8804026 | OE04 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1321009 | 20191004UTD_01 | isolated SL pole. SL head burnt out, head req replacement. LIS# 8804026. | - overhead conductor (covered uninsulated)
6 | 2019-08-08 | 2:13 | -38.2749 | 145.1597 | LOT 16 GERARDS WAY, TYABB VIC 3913 | 1112692 | HGS22 | 22kV AC | Rural Short | - transformer (pole mounted) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1321638 | 20190821UTD_02 | 5kVA single phase Tx requires replacement ASAP on 8/8/19, Birds nest on Bushings has caught fire, at some stage and burnt bushings/2 x LV bushings cracked and broken. Fire report 6828. HV/LV isolated and burnt birds next removed. | - overhead conductor (insulated)
7 | 2019-08-09 | 8:56 | -38.3692 | 144.7773 | 22 HARLEIAN STREET, BLAIRGOWRIE VIC 3942 | 1304484 | STO14 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1322158 | 20190821UTD_03 | Pole fire at HV inter LV strain normal open point pole down lis 1304484. possible HVI HV fuse at RB0578 Open. | Service lines
8 | 2019-08-09 | 11:23 | -38.2149 | 145.1164 | 280 ERAMOSA ROAD W, MOOROODUC VIC 3933 | 1103528 | MTN22 | 22kV AC | Rural Short | - overhead conductor (ABC) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1322299 | 20190903UTD_01 | Severe storm high winds at time of outage . Large tree thru HV ABC 257 Eramosa Rd. cHV ABC & LV ABC damaged between MT7286 ERAMOSA RD & MT7287 ERAMOSA RD.(5 Bays) and a small fire start on ground | - overhead service conductor (residential)
9 | 2019-08-25 | 23:50 | -38.1402 | 145.1271 | 15 FLETCHER ROAD, FRANKSTON VIC 3199 | 8819028 | FTN11 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1327197 | 20190828UTD_03 | isolated at base of pole, new 250w HPS required, traffic control required to replace, refer #1327197 | - overhead service conductor (commercial / industrial)
10 | 2019-09-10 | 5:35 | -37.8801 | 145.1406 | 289 LAWRENCE ROAD, MOUNT WAVERLEY VIC 3149 | 602198 | EB12 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1331551 | 20190923UTD_01 | Part of EB12 feeder fault to#1331552, crossarm fire due to insulator failure | - overhead service conductor (subdivision / construction)
11 | 2019-09-21 | 5:14 | -37.7579 | 145.1131 | 420 THOMPSONS ROAD, TEMPLESTOWE LOWER VIC 3107 | 7068425 | BU14 | 11kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1335344 | 20191001UTD_01 | During strong winds a council tree branch and fell into HV conductors which caused a HV injection. The resulting surge cause a flashover at kiosk S/Stn THOMSON-FOOTE which ignited a small grass fire. Closest LIS = 7068425 | - overhead service conductor (other)
12 | 2019-10-06 | 21:25 | -38.0427 | 145.1114 | 255 STATION STREET, EDITHVALE VIC 3196 | 3303709 | CRM35 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1340098 | 20191106UTD_01 | Broken Hv Xarm LIS#3303709 Short interruption to replace | - underground service cable (residential)
13 | 2019-10-28 | 15:54 | -37.8847 | 145.2067 | QUARRY, 191 GEORGE STREET, WANTIRNA SOUTH VIC 3152 | 619559 | GW7 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 1346112 | 20191106UTD_02 | Originally recorded as abird/Animal it was subsequently determined after investigation a vehicle has contacted the conductors and laft a scorch mark on the ground <1m | - underground service cable (commercial / industrial)
14 | 2019-10-30 | 14:35 | -37.9762 | 145.0215 | 533 BALCOMBE ROAD, BLACK ROCK VIC 3193 | 1820222 | BR4 | 11kV AC | Urban | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1346876 | 20191127UTD_04 | Refer also to T/E#1346872. CrCrew also reports hole blown in HV UGC at CHP #1812587 c/t BALCOMBE EBDEN S/S, this was likely the primary fault. Faulty HV cable disconnected, isolated and earthed and A/P issued to UGC crew from ZNX. Customers ex BALC | - underground service cable (subdivision / construction)
15 | 2019-11-04 | 23:03 | -37.8467 | 145.1042 | 45 PARER STREET, BURWOOD VIC 3125 | 7048034 | BW22 | 11kV AC | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1348043 | 20191203UTD_02 | Gas switch bh7267 needs replacement. the leads and bushing are b/out. LIS # 7048034 Crew have isolated supply and issued permits and crew are replacing gas switch. Refer TE 1348055 A smaill amount of debris caused a 100X 100mm ground fire | - underground cable
16 | 2019-11-18 | 0:06 | -37.9275 | 145.0677 | 3 GREENDALE ROAD, BENTLEIGH EAST VIC 3165 | 1801649 | CDA24 | Low voltage AC (<1kV) | Urban | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1351867 | 20191203UTD_03 | MFB reported Pole Fire but was out when crew arrived replaced burntout J/Box on pole. | - underground communications cable
17 | 2019-11-21 | 15:23 | -37.9202 | 145.0854 | 18 DELIA STREET, OAKLEIGH SOUTH VIC 3167 | 2328854 | OR33 | Low voltage AC (<1kV) | Urban | - pole (wood) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1353529 | 20200110UTD_01 | PART OF south circuit isolated, pole to be repalced as struck by lightning . Fire Report # 02526. lv t-off pole replaced. LIS#2328854. PM not#1000735445 | Poles
18 | 2019-11-21 | 16:53 | -38.4128 | 145.014 | 389 TUCKS ROAD, SHOREHAM VIC 3916 | 1313635 | DMA23 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Very High | 1 | 1 | 1353670 | 20191122UTD_01 | DMA23 tripped and reclosed DMA #2 22kV BUEL stage 2 operated. Fault traced to tree over HV at lis 1313635 Tucks Rd. Small fire started ESV advised ref#12847040 TUCKS LYNCROFT is isolated LV. | - pole (concrete)
19 | 2019-11-26 | 5:26 | -37.8079 | 145.1211 | 140 NELSON ROAD, BOX HILL NORTH VIC 3129 | 7035489 | DC12 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1355201 | 20191204UTD_02 | South cct of SAXTON-SHANNON S/S 22Kv X-Arm broken at Isolator pole BH0405, HV conductors down in Nelson St North of Tyne St. LIS#7035489. | - pole (steel)
20 | 2019-11-26 | 6:11 | -37.9176 | 145.1493 | 226-236 WELLINGTON ROAD, CLAYTON VIC 3168 | 622882 | SVTS-EB | 66kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1355208 | 20191203UTD_04 | 66KV termination xarm burnt through at insulator. lis #0622882, P/M #1000725805 | - pole (wood)
21 | 2019-11-26 | 8:34 | -37.9286 | 144.9995 | 99 SOUTH ROAD, BRIGHTON VIC 3186 | 1805014 | MR13 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1355246 | 20200110UTD_02 | No fire when crews arrived, fire report done #4455 - HV strain arm and 3x 11kv HV isolator req replacing PM#1000735918 - lis 1805014 CH0769 switch pole - works completed | Crossarms
22 | 2019-11-26 | 10:53 | -38.3239 | 144.7322 | 3572-3574 POINT NEPEAN ROAD, PORTSEA VIC 3944 | 1302728 | STO22 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1355337 | 20191204UTD_01 | CFA reported tree branch on fire but was out when crew arrived. Crew found tree branch resting on HV conductors. Private tree from 3568 Point Nep Rd. | - crossarm (wood)
23 | 2019-11-27 | 4:32 | -37.9103 | 144.9863 | 218B ESPLANADE, BRIGHTON VIC 3186 | 1806095 | NB33 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1355658 | 20200114UTD_01 | FiRef #1357042 replcd red phase fuse base & 100a service fuse at the pole lis# 1806095 fire report: 1569 caused very small fire at base of pole supply left on - email sent from analytics @ 02:00 on 1/12/19 | - crossarm (steel)
24 | 2019-11-30 | 12:04 | -38 | 145.1072 | 19 MALCOLM ROAD, BRAESIDE VIC 3195 | 616892 | MC4 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1356774 | 20191210UTD_02 | End of x/arm had burnt through at MALCOLM N13 BOUNDARY S/stn LIS#0616892, HV conductor resting in tree small fire in canopy. installed on same x/arm. X/Arm to be replaced at a later date. Notification 1000736622 - Fire Report number 03074. | - crossarm (other)
25 | 2019-12-04 | 8:00 | -38.2758 | 145.0134 | 46 GLENISLA DRIVE, MOUNT MARTHA VIC 3934 | 1103211 | DMA24 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1358310 | 20191213UTD_01 | Found White Phase HV EDO with black marks on tube. Suspect fuse hung up and possibly candled. Fire report No 7023 completed. No cause found. LBRA area - no fire present - LIS 1103211 | - capacity balancing units
26 | 2019-12-08 | 11:17 | -38.0164 | 145.1188 | 54 SUTHERLAND AVENUE, ASPENDALE GARDENS VIC 3195 | 3305055 | KBH-M-MC | 66kV AC | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1359403 | 20191213UTD_04 | KBH to M to MC 66kV line, AL to CU amapac failure. as Lis# 3305055 is on bike track at rear of # 54 - confirmed fire start, 2m2 grass fire 66kv sub t pole - steel xarm, concrete pole - large tower required to change ampacs - fire report #04454 | - connector / termination
27 | 2019-12-09 | 20:27 | -37.8884 | 144.9958 | BENT AVE BRIGHTON 3186 [Cnr New St] | 2308461 | EW14 | 11kV AC | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1359943 | 20191213UTD_02 | Cause: Large pine tree in Elsternwick golf course dropped branch onto HV CHP LIS# 2308461 in Bent Ave, Tree branch was sparking / burning at time of fault. No fire at ground level. Crew will submit fire report #1099... | - dropper / bridge
28 | 2019-12-10 | 6:53 | -37.9301 | 145.1018 | 18 THE PARADE, CLARINDA VIC 3169 | 2333349 | CDA-SVTS | 66kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1359994 | 20200211UTD_01 | End of Xarm burnt off... post type 11 shed grey porcelain.... No fire on arrival...Switched out line to replace Xarm.Pole # 2333349 - Wayne Highmore in attendance - O/S 18 The Parade Clarinda | - insulator tie wires / connections
29 | 2019-12-10 | 6:56 | -37.8978 | 145.1234 | 5 BELLERIVE AVENUE, MOUNT WAVERLEY VIC 3149 | 2300779 | NO7 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1359995 | 20200128UTD_01 | Broken xarm HV inter needs replacement 1 nth Bellvue. Const adv. LIS # 2300779 Hv x-arm broke, Swung into LV. | - insulators
30 | 2019-12-10 | 7:29 | -37.954 | 145.0765 | 371-373 WARRIGAL ROAD, CHELTENHAM VIC 3192 | 1825384 | HT11 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1360013 | 20191218UTD_01 | HV Pole burnt fire report 5243 .Pole # 1825384 -o/s 371 Warrigal Rd | - tower
31 | 2019-12-10 | 12:05 | -37.9563 | 145.0077 | 153-155 BEACH ROAD, SANDRINGHAM VIC 3191 | 1817434 | SR11 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1360185 | 20191217UTD_02 | construction crew required, crew returning to depot get, new HV anchor arm. X-arm is boken and conductor hanging low but not dangerous. | - traction lines
32 | 2019-12-14 | 10:16 | -37.9255 | 145.1562 | 821 SPRINGVALE ROAD, MULGRAVE VIC 3170 | 619973 | SVW53 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1361411 | 20200114UTD_03 | HV x-arm fire & snapped PM#1000738403, DN1225 LIS#0619973.. Wood pole & arm, Brown pin type insulators. Small flame visible adjacent to kingbolt in xarm.. Xarm replaced.. fire report no. 02527. photos attached to file as per crew. | - services pit
33 | 2019-12-17 | 13:09 | -38.1589 | 145.1541 | 42 LIPTON DRIVE, FRANKSTON VIC 3199 | 8819961 | FSH22 | Low voltage AC (<1kV) | Urban | - underground service cable (residential) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1362369 | 20200114UTD_02 | Pillar o/s 42 Lipton is blown up and requires repair. parralelling pillar on the n/strip. supply. Fire report number is 03823. Small fire in the garden bed approx 1 meter x 1 meter . Closest LIS 8819961 | - transformer (pole mounted)
34 | 2019-12-20 | 17:18 | -38.1595 | 145.1091 | 38 BRUARONG CRESCENT, FRANKSTON SOUTH VIC 3199 | 3315975 | FSH13 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 1363600 | 20200117UTD_01 | replaced white phase LV krone box isolator and blade which was arcing and sparking , this caused a grass fire @ pole lis # 3315975 approx 1m x 1m - fire report # 08002notification # 1000739449 Reported to ESV - (Cody) @ 20:10 hrs 20/1/219 ESV Ref # 13036024 . | - transformer (ground outdoor mounted)
35 | 2019-12-20 | 17:44 | -38.1864 | 145.0901 | 129 MOUNT ELIZA WAY, MOUNT ELIZA VIC 3930 | 3313700 | FSH12 | Low voltage AC (<1kV) | Rural Short | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 1363609 | 20200218UTD_01 | Replaced red phase burnt out IPC Connection @ the transformer -There is a report in regards to a object falling onto a car o/s 129 MT Eliza Way Mt Eliza there is no car on arrival but sebesequent claim confirmed a fire start | - measurement transformer (current transformer)
36 | 2019-12-21 | 11:50 | -38.3875 | 144.7894 | 11 DOROTHY STREET, RYE VIC 3941 | 1305665 | STO21 | Low voltage AC (<1kV) | Rural Short | - connector / termination | single phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 1364062 | 20200114UTD_04 | Blue ph ampact connection to OH line at sub pole melted (LIS#1305665 - o/s 11 Dorothy St, Rye). Small fire evident at base of pole. approx 0.5m2. fire report 6829. fire started from molten metal dropping to ground. supply restored 1330. | - transformer (indoor chamber mounted)
37 | 2019-12-21 | 24:00 | -38.1373 | 145.1239 | 377 NEPEAN HIGHWAY, FRANKSTON VIC 3199 | 3308817 | FTN22 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1364161 | 20200114UTD_05 | TX LV Krone Box has melted (red phase contact failed, however it shorted to white phase.). Outage to substation to replace krone box. Fire Report #6830 - smal fire started nature strip area 1/2 metre square, crew have sent photos to dispatch. LIS 3308817 | - transformer (any other type)
38 | 2019-12-24 | 10:09 | -37.9588 | 145.1226 | 550-570 HEATHERTON ROAD, CLAYTON SOUTH VIC 3169 | 610198 | SS21 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1364424 | 20200114UTD_06 | Replaced x-arm burnt at one end Heatherton Rd. Lis 0610198. Fire report No 1100. No fire on ground. | - measurement transformer (voltage transformer)
39 | 2019-12-27 | 18:46 | -38.3951 | 144.8178 | 347 BROWNS ROAD, RYE VIC 3941 | 1315973 | STO21 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 1364824 | 20200114UTD_07 | Pole lis 1315973 is ok.. no damage, just blackening from fire..Fire report 7041, unable to determine if fire was caused by our asset but as reclose and feeder and call to CFA was 4 minutes apart it appears likely cause is a bird | - measurement transformer (capacitive voltage transformer)
40 | 2019-12-30 | 12:46 | -37.8219 | 145.1113 | 427 MONT ALBERT ROAD, BOX HILL VIC 3128 | 7023862 | BH23 | 22kV AC | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | 1365109 | 20200211UTD_04 | Also Refer to TE# 1365107. ACR BH7390 was initial tripping device. Tree on O/H tee to BLACK MONT ALBERT and also white phase ampac failed to the east of this location LIS#7023862. Small ground fire indicated by Linesman | Fuses and switchgear
41 | 2019-12-30 | 14:34 | -37.8243 | 145.1228 | 500 STATION STREET, BOX HILL VIC 3128 | 7027380 | BH23 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | 1365273 | 20200114UTD_09 | P/M #1000739715 to replace x/arm and insulator. Feeder BH23 lis 7027380. Fire on x.arm only, fire report #9401. replaced burnt out hv angle type 1 intermediate cross arm | - fuse (boric acid)
42 | 2019-12-30 | 18:37 | -37.7927 | 145.1862 | 60-62 MCGOWANS ROAD, DONVALE VIC 3111 | 7067313 | NW13 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Extreme | 3.5 | 0.7 | 1365271 | 20200114UTD_08 | possibly cause of reclose on TBL#1365241, large council tree thru lv, started grassfire aprox 4 mtrs x 2 mtrs. caused by lv hitting ground. Fire report to come from Rod Parker hv fuse needs to be replaced | - fuse (EDO fuse)
43 | 2019-12-31 | 4:51 | -37.7636 | 145.1193 | 317 HIGH STREET, TEMPLESTOWE LOWER VIC 3107 | 7058574 | BU1 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1365627 | 20200211UTD_03 | Confirmed fire start cause of broken HV inter x arm at lis 7058574. Notification 1000739729. ESV Ref 13086092 Intermediate x arm in High St at Tee to Linton LIS#7058574. end of X arm burnt off. Iss and can A/P , X arm replaced | - fuse (powder filled)
44 | 2019-12-31 | 5:31 | -37.8406 | 145.1114 | 2 NEVILLE STREET, BOX HILL SOUTH VIC 3128 | 7029573 | BH31 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1365634 | 20200114UTD_10 | Broken x-arm reported by MFB, Road side Rph HV resting in Rph LV. Possible HVI - Fire Ignition report #8081 filled out by D Glen, Confirmed HVI HVI#BWD1915, Polynumeric insulator tracked and burnt x-arm. PM Notification 1000739728. ESV ref 13086073. | - circuit breaker
45 | 2019-12-31 | 8:28 | -37.9094 | 145.0199 | 111 UNION STREET, BRIGHTON EAST VIC 3187 | 2333173 | BT-NB | 66kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1365679 | 20200211UTD_02 | Confirmed fire star NB-BT 66kv line. ESV Ref 13086105 Poss broken x arm per mfb TE#1365697. N No apparent cause between 11kv and 66 KV Iss and can A/P . LIS = 2333173 | - switch (disconnector/isolator)
46 | 2020-01-01 | 11:26 | -38.3374 | 144.9705 | 79 PIER STREET, DROMANA VIC 3936 | 1311099 | DMA21 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1365879 | 20200122UTD_01 | At lis 1317021.cut away la's at 2 x tx pier nepean, gibson beach and council pier. insert lv parralels for council pier as bearer burnt as a result of helium ballons into 22+66 fire report 7042 started a 1ms ground fire | - switch (earth)
47 | 2020-01-03 | 16:11 | -37.9193 | 145.0216 | 759 NEPEAN HIGHWAY, BRIGHTON EAST VIC 3187 | 1805698 | MR31 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1366293 | 20200122UTD_02 | LIS= 1805698, HV Inter arm. ESV ref 13107094. Crew replaced xarm LL method. Fire ignition report #: 01543. | - switch (FuseSaver)
48 | 2020-01-05 | 8:45 | -37.8522 | 145.1329 | 10 BURWOOD HIGHWAY, BURWOOD VIC 3125 | 7037580 | EB11 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1366531 | 20200122UTD_04 | X-arm broken at switch pole BH7256 Burwood Rd LIS#7037580. HV has hit the neutral wire, LV OK. No HV injection, Chemist shop OK and power on, all other shops are closed. ASR AT 13:24HRS - ESV 13116347 | SCADA, network control and protection systems
49 | 2020-01-05 | 9:33 | -37.868 | 145.0282 | 33 ARTHUR STREET, CAULFIELD NORTH VIC 3161 | 9490012 | MTS-EL-EM | 66kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1366542 | 20200122UTD_05 | MTS-EL/EM 66Kv line X-Arm broken in Arthur St 1pole West of Carnavan Rd LIS#9490012. Fire report # 8082 - ESV 13116340 | - automatic circuit recloser (ACR)
50 | 2020-01-05 | 10:17 | -38.3301 | 144.7136 | 26 ELIZABETH ROAD, PORTSEA VIC 3944 | 1307150 | STO13 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1366547 | 20200122UTD_06 | ELIZABETH AVE, LIS:1307150 HV LV Inter, 9 Shed insulators. Xarm requires replacement broken at strap bolt. fire report #7043 -ESV #13140653 | - communications linear assets
51 | 2020-01-05 | 11:05 | -38.1203 | 145.1485 | 4 WINDOO STREET, FRANKSTON NORTH VIC 3200 | 3316011 | FTN13 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1366559 | 20200122UTD_07 | Xarm fire in Windoo, Lis# 93316011, Grey fogs... SNumber 7 Windoo Frankston North hv interxarm to be replaced. ire report# 04457 - ESV 13116335 | - communications network assets
52 | 2020-01-05 | 11:15 | -38.01 | 145.2128 | 22 STEPHEN ROAD, KEYSBOROUGH VIC 3173 | 635167 | DSH23 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1366564 | 20200122UTD_08 | peFire report 01544 - ESV 13116331 - Xarm fire at switch pole DN0295 CORRIGAN RD, xarm fell onto switch breaking switch insulator. Xarm and switch replaced, supply restored. lis = 0635167 | - communications site infrastructure
53 | 2020-01-05 | 11:45 | -37.9883 | 145.1005 | 29 DE HAVILLAND ROAD, MORDIALLOC VIC 3195 | 1806826 | MC9 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1366571 | 20200122UTD_09 | Xarm burnt off at G/T S/S, Glass discs & Grey fog dressing down... LIS#1806826... fire report# 04456... hv termination xarm on the sub pole being replaced... - ESV 13116343 | - field devices
54 | 2020-01-05 | 14:53 | -37.939 | 145.0665 | 16 NELLBERN ROAD, MOORABBIN VIC 3189 | 1816585 | HT8 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1366606 | 20200122UTD_10 | X/Arm / Pole burnt in Nellbern, LIS#1816585...Grey Fogs.. - ESV 13116345 - Fire report 01545 | - local network wiring assets
55 | 2020-01-05 | 15:39 | -37.8097 | 145.1453 | 32 SPRINGFIELD ROAD, BLACKBURN VIC 3130 | 639430 | BH12 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1366612 | 20200203UTD_01 | Customer rang to say pole 0639430 had a burning piece of wood on the ground. Looks like part of cross arm. Was still smoldering. Wires still up.Tee-off cross-arm in Springfield Rd corner of Beverley, broken LIS#0639430 Fire report 3030 | - master station assets
56 | 2020-01-09 | 4:25 | -37.9473 | 145.0744 | 5 POWLETT STREET, MOORABBIN VIC 3189 | 1816317 | HT13 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1367602 | 20200203UTD_02 | Patrol found burnt off X arm at Powlett-Simpson S/S. Switched out for Emg A/P to make repairs Fire report ESV#13142340 lis=1816317 | - neutral earthing resistor
57 | 2020-01-10 | 16:09 | -38.1196 | 145.1541 | 18 LINDSAY STREET, FRANKSTON NORTH VIC 3200 | 3309505 | FTN13 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1368166 | 20200204UTD_01 | Per MFB Lis# 3309505. Broken HV inter x-arm, LINDSAY cnr MORETON. LIS 3309505. Dropped onto HV t-off x-arm. (x-arm burnt through). O/S 18 LINDSAY ST FRANKSTON NORTH Po ESV advised (ref #13151279) - pole fire. \ | - oil-filled circuit recloser (OCR)
58 | 2020-01-10 | 16:34 | -37.9276 | 145.1491 | 2215-2221 DANDENONG ROAD, MULGRAVE VIC 3170 | 620496 | SVW53 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1368194 | 20200304UTD_03 | X-arm fire at Tx at LAWFORDS KALIMNA. Fire report # Fi's at DN2903 KALIMNA STREET did not operate - (Notification 1000740495 for FI's) - crew replaced (hv term arm @ lis: 0636681 - Notification 1000740496) ESV advised ref#13151298 | - rapid earth fault current limiter (REFCL)
59 | 2020-01-11 | 18:36 | -37.7786 | 145.112 | 6 ROSINE COURT, DONCASTER VIC 3108 | 7069742 | WD34 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1368574 | 20200402UTD_01 | A LV service wore through on a xarm strap and caused fire damage to the top aof a pole that needed replacement, Fire report #9606, no fire on ground only on pole. LIS 7069742 | Public lighting
60 | 2020-01-11 | 19:12 | -37.881 | 144.9856 | 2 SHELLEY STREET, ELWOOD VIC 3184 | 2306140 | EW12 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1368580 | 20200304UTD_01 | broken hv anchor x-arm being replaced today . x arm failed due to fire damage. suspect from yesterday. damage looked old. lis 2306140. fire report2528 | - lamps (major road)
61 | 2020-01-15 | 23:14 | -38.2081 | 145.101 | 38 EUMERALLA GROVE, MOUNT ELIZA VIC 3930 | 3313495 | MTN22 | 22kV AC | Rural Short | - switch (disconnector/isolator) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1370130 | 20200204UTD_02 | FS0857 EUMERALLA ROAD has failed.MFB on site due to smoke coming from switch. Suspect damaged by earlier lightning strike at Eumaralla Banool s/s. Fire report # 6767. PM 1000741380. Switch replaced. Lis=3313495 | - lamps (minor road)
62 | 2020-01-17 | 20:08 | -37.9581 | 145.207 | 211 GLADSTONE ROAD, DANDENONG NORTH VIC 3175 | 619701 | LD4 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1370827 | 20200304UTD_02 | Tree from school into HV. Bought down conductors. Suspect HVI. Confirmed HVI, #KEY2003, Whispir & 1st email sent/DAO, Emer Mgr & Cust Rel adv LIS#0619701 | - luminaires (minor road)
63 | 2020-01-19 | 18:42 | -37.8201 | 145.1856 | UNIT 1 24 ROOKS ROAD, NUNAWADING VIC 3131 | 7033741 | NW22 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1371239 | 20200204UTD_06 | BPh FI' up at BH1964 HV CABINET 444 WHORSE Both xarms burnt off t/pole LIS#7033741 PM # 1000742130... S | - poles / columns (major road)
64 | 2020-01-20 | 5:36 | -38.0276 | 145.2235 | 47 HEALEY ROAD, DANDENONG SOUTH VIC 3175 | 623699 | DVY32 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1371335 | 20200205UTD_01 | CFA attended and extinguished pole fire between HV+LV xarms. D Glen states "pole is stable, requires closer inspection and either insulators or pole + insulators replaced" Fire report #2706. | - poles / columns (minor road)
65 | 2020-01-20 | 8:06 | -38.0017 | 145.1104 | 61-65 JARRAH DRIVE, BRAESIDE VIC 3195 | 624869 | MC10 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1371549 | 20200205UTD_02 | - REPLACED BURNT OUT IPC CONNECTION ON WHITE PHASE.- REPLACED BURNING OUT CU - AL D CONNECTION TO TX LEAD.- REPAIRED BURNT OUT CONDUCTOR WITH SLEEVE. no fire on arrival - fire report done #08023 | - connection box
66 | 2020-01-20 | 21:53 | -38.1995 | 145.1042 | 13 BELLBIRD ROAD, MOUNT ELIZA VIC 3930 | 3311834 | FSH12 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1371880 | 20200205UTD_04 | crew replaced HV/LV strain arms, . Lower LV x-arm and lowered/ replaced HV x-arm. New #5 HV Stay. Cut burnt pole top off. No ground fire damage observed. LIS=3311834 | - earth / earthing
67 | 2020-01-21 | 6:18 | -37.8898 | 145.0623 | 364 NEERIM ROAD, CARNEGIE VIC 3163 | 2327323 | EM10 | 11kV AC | Urban | - fuse (powder filled) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1371932 | 20200205UTD_05 | Found to be a candling fuse 206v on blue, at sub bus 192v at sub 216 on blue. R & W 243 & 245…LIS 2327323
68 | 2020-01-23 | 6:49 | -38.3987 | 144.9395 | 33A BROWNS ROAD, MAIN RIDGE VIC 3928 | 8831401 | RBD12 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | Very High | 1 | 1 | 1372960 | 20200124UTD_01 | replaced 3 phase fmb on service pole, caught fire, fire report no 01981. box supplying no 35. nst passed and left on ncia. ESV REF# 13241384 - lis 8831401
69 | 2020-01-27 | 9:34 | -37.9413 | 145.1024 | 101 ELDER STREET S, CLARINDA VIC 3169 | 2331012 | CDA22 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1373908 | 20200205UTD_03 | Broken hv strain x-arm as above at LIS#2331012...... Crew replaced x-arm today - After the event, determined to be x-arm fire (time unknown) Appears to be old x-arm fire caused by tracking grey fog insulator on red phase. Arm replaced on day under A/P. | Extra low voltage AC (<50V)
70 | 2020-01-31 | 23:54 | -38.3769 | 145.1488 | 307 SANDY POINT ROAD, SOMERS VIC 3927 | 1108966 | HGS23 | 22kV AC | Rural Short | - fuse (boric acid) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Severe | 2 | 2 | 1375847 | 20200204UTD_04 | MT7722 opened auto reclosed and held, cause was the Blue phase BA fuse unit at MT512 which failed and burnt the bottom contact off; which started a 1m2 ground fire. Fire report 9607. | Low voltage AC (<1kV)
71 | 2020-02-07 | 0:51 | -37.8584 | 145.0659 | 6 KERFERD ROAD, GLEN IRIS VIC 3146 | 2310294 | K13 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1377883 | 20200218UTD_02 | West cct krone box b/out & tx lv isols damaged -O/S 6 Kerferd st. Crew repl a 3 ph fmb at pole end feeding a pit. LV transformer krone switch 1000a blades is melted and a small grass fire occurred. Fire ignition report # 02943. LIS=2310294 | 6kV AC
72 | 2020-02-13 | 8:55 | -38.3523 | 144.9178 | 769 POINT NEPEAN ROAD, ROSEBUD VIC 3939 | 1309797 | DMA21 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1379761 | 20200218UTD_04 | Tree private in #769 Point Nepean Rd, UE responsible, LIS#1309797 and LIS#1309796. Wph and Bph conductor damage - wrap-ons fitted, FIRE Report #1982 completed by onsite crew. Clashing on 22Kv from Pole LIS#13017011 2 bays to pole LIS#13017013. | 11kV AC
73 | 2020-02-13 | 14:12 | -37.7983 | 145.1843 | 1 WARROCK AVENUE, DONVALE VIC 3111 | 7067545 | NW13 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1379971 | 20200218UTD_03 | Large tree branch broke and fell on HV. No damage. 2x65A BA fuses blown at DT1434. Tree branch fell clear before it could be manualy removed. Fire report #03013 - LIS = 7067545 | 12.7kV AC
74 | 2020-02-14 | 18:14 | -37.9274 | 145.2507 | 1090 WELLINGTON ROAD, ROWVILLE VIC 3178 | 3413682 | FGY21 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1380454 | 20200226UTD_01 | Customers reported fire when crew arrived fire was out but they had to replace a burnt out white ph 1000a krone box on LIS# 3413682….likely flames present at some point | 22kV AC
75 | 2020-02-18 | 8:41 | -38.0175 | 145.2214 | 13 LANYON STREET, DANDENONG SOUTH VIC 3175 | 600027 | DSH31 | Low voltage AC (<1kV) | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1381166 | 20200331UTD_01 | Customer stated a small fire had begun at his POA - Fire out on arrival but replaced the white ph active connection on service, burnt out - LIS 0600027 | 66kV AC
76 | 2020-02-18 | 19:03 | -38.0143 | 145.2629 | 11-13 WESTPOOL DRIVE, HALLAM VIC 3803 | 639074 | DN08 | 22kV AC | Urban | - switch (disconnector/isolator) | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1381450 | 20200331UTD_02 | Customer adved switch opposite hit by lightning and exploded. Was on fire for short time. Now out. Switch replaced lis 0639074 | 330kV AC
77 | 2020-02-19 | 7:23 | -37.8871 | 145.0463 | 172A NEERIM ROAD, CARNEGIE VIC 3163 | 2328360 | CFD26 | 11kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1381586 | 20200304UTD_05 | refer to t/o #: 1381651 (part of larger fault) unable to group. pole fire due to glass disc insulator failure at pole lis#2328360. CFD26 was shortened, interupted, insulator replaced. fire report # 09421. ESV#13435748, LIS 2328360 | 500kV AC
78 | 2020-02-20 | 10:10 | -38.4842 | 145.0304 | 92 THE ESPLANADE, FLINDERS VIC 3929 | 9864733 | RBD21 | 22kV AC | Rural Short | - connector / termination | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 1382078 | 20200324UTD_01 | Crew replaced 31.5A PFF Rph including top and bottom connection rings which were damaged due to fuse not being latched correctly. No a HV "fuse"sue - a HV connection issue | Extra low voltage DC (<120V ripple free)
79 | 2020-02-27 | 9:13 | -37.9399 | 145.04 | 1037 NEPEAN HIGHWAY, MOORABBIN VIC 3189 | 1815697 | MR24 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1383685 | 20200304UTD_06 | Crossarm Fire LIS 1815697 - 2nd call completed xarm replacement, did not provide any details of poss firestart | Low voltage DC (<1.5kV)
80 | 2020-03-02 | 5:44 | -38.3674 | 144.8093 | 2549 POINT NEPEAN ROAD, RYE VIC 3941 | 1303874 | STO23 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1384438 | 20200310UTD_01 | xarm fire at tee pole Pt Nepean rd tee to TAROOK WHITECLIFFS. Zinfra crew changed pole. Fire Ignition Report #7061. - lis 1303874 | 600V DC
81 | 2020-03-02 | 12:01 | -37.9939 | 145.235 | 15 MATIPO STREET, DOVETON VIC 3177 | 623092 | DN11 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1384525 | 20200306UTD_01 | replaced service, burning at simpy crimp. sign of fire on service, melting and burn marks. fire report#05245. fire was out when crew arrived. WISPIR sent. ESV #: 13517982. | 1500V DC
82 | 2020-03-04 | 1:52 | -37.9831 | 145.08 | 46 LOWER DANDENONG RD MENTONE VIC 3194, | 1822639 | M33 | 11kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1384996 | 20200409UTD_03 | Tree branch from #46 Lower Dandenong Rd fell over HV conductors. Secondary damage to Bph HV isol at CH6334. MFB reported branch was on fire - LIS 1822639 | Earthing cable
83 | 2020-03-11 | 4:47 | -37.7908 | 145.174 | 5 MITCHAM ROAD, DONVALE VIC 3111 | 7066918 | NW13 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1387113 | 20200325UTD_01 | Street light fire Disconected light and made safe Light head requires replacement LIS 7066918
84 | 2020-03-17 | 2:28 | -37.9748 | 145.2488 | 8 NICHOLSON CLOSE, ENDEAVOUR HILLS VIC 3802 | 638159 | LD2 | Low voltage AC (<1kV) | Urban | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1388956 | 20200327UTD_02 | A // pillar blew up and u/g crew are repairing after an LVIBS was issued. see also TO # 1388955 - crew have repaired // switch in pillar Clsest LIS 0638159
85 | 2020-03-17 | 12:15 | -38.3746 | 145.0514 | 101 STANLEYS ROAD, RED HILL SOUTH VIC 3937 | 1318468 | DMA13 | 22kV AC | Urban | - fuse (boric acid) | two phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 1389174 | 20200409UTD_02 | RPh BA at RB0510 was found broken in 1/2 with obvious signs of candling... Replaced barrell... LIS#1318468... 1Ph supply. | single wire earth return (SWER)
86 | 2020-03-20 | 23:33 | -38.0088 | 145.0983 | 51A GOVERNOR ROAD, MORDIALLOC VIC 3195 | 1807866 | MC3 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1390226 | 20200327UTD_01 | Pole fire at LIS#1807866. Awaiting daylight assessment of damage and replacement parts required. Fire report number #03748. ESV fire report to be made within 48hrs | single phase
87 | 2020-04-03 | 11:56 | -37.8925 | 145.232 | 8 BARRY COURT, SCORESBY VIC 3179 | 619620 | BRA21 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1394037 | 20200427UTD_03 | Customer reported fronds from Palm tree were intermittently sparking/burning when touching wires…….Tree trimmed. LIS 0619620 | two phase
88 | 2020-04-04 | 5:14 | -37.9984 | 145.0742 | 141 BEACH ROAD, PARKDALE VIC 3195 | 1808847 | M25 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1394207 | 20200406UTD_01 | MFB reported a pole fire outside premises, on arrival a Krone box had caught fire. Fire report # 03749, UE Emergency ESV notified ESV Ref #13753960 Crew re attended next day and repl krone box LIS 1808847 | three phase
89 | 2020-04-09 | 12:05 | -37.8797 | 145.0444 | 94 QUEENS AVENUE, CAULFIELD EAST VIC 3145 | 2327650 | CFD24 | 11kV AC | Urban | - capacity balancing units | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1395899 | 20200427UTD_06 | Customer reported box on pole on fire. Structure was "Queen Derby" Cap Bank. There was no fire on ground - fire report #08024. LIS 2327650
90 | 2020-04-15 | 18:28 | -38.2114 | 145.0506 | 6-8 KALIMNA DRIVE, MORNINGTON VIC 3931 | 1100802 | MTN35 | Low voltage AC (<1kV) | Rural Short | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1397340 | 20200427UTD_05 | CFA advise approx halfway down pole was on fire, but now out. LV Isolator krone box melted suspect due to corrosion & loose connection. 1/2 sqm fire at base of pole fire report #6831 LIS 1100802
91 | 2020-04-17 | 18:24 | -38.152 | 145.1333 | 7 MCMAHONS ROAD, FRANKSTON VIC 3199 | 3306626 | FTS-FTN | 66kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1398177 | 20200427UTD_01 | ESV report #13834428 Fire report #6965 - Confirmed fire start, Fire is on pole, about 3M down from top of pole. Suspected cause maybe 66kV tracking as brown insulator appeared broken. LIS 3306626 | Negligible: no ground fire
92 | 2020-04-22 | 9:37 | -38.2002 | 145.1162 | 58-62 ALLISON ROAD, MOUNT ELIZA VIC 3930 | 3315364 | FSH12 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 1399254 | 20200427UTD_02 | Customer tree branch at 62 Alison Rd fell through HV and was resting on LV when crew arrived. Branch removed under shutdown. No damage to HV/LV conductors. 20CFA had reported sparking and flames. LIS 3315364 | Localised: less than 10 sq.m
93 | 2020-05-05 | 18:23 | -37.8353 | 145.1759 | 422 CANTERBURY ROAD, FOREST HILL VIC 3131 | 7020345 | NW33 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1402844 | 20200512UTD_01 | LV red phase fuse isolator Debris from the melting pieces of the isolator this caused a small area fire on ground in some plants- as per customer on site MFB had already attended - too dark to take photos Fire report created- LIS 7020345 | Small: 10 - 1000 aq.m
94 | 2020-05-06 | 19:01 | -37.8821 | 144.9784 | UNIT 1 1 ORMOND ESPLANADE, ELWOOD VIC 3184 | 2308954 | EW12 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1403253 | 20200512UTD_02 | Replaced 3 phase FMB @ pole end that was on fire o/s 1 Ormond Esplanade Elwood- Fire Report #9615 - LIS 2308954 | Medium: 1000 sq.m - 10 ha
95 | 2020-05-09 | 18:22 | -37.8714 | 144.9962 | 19 THE AVENUE, BALACLAVA VIC 3183 | 2304444 | BC11 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1404071 | 20200514UTD_01 | MFB reported a minor fire at the POA. Crew arrived and replaced the UE owned porcelain box which was believes to have ignited the small fire as well as the neutral service with black 2/c service. LIS 2304444 | Large: more than 10 ha
96 | 2020-05-13 | 15:48 | -38.4724 | 144.8947 | 164 CAPE SCHANCK ROAD, CAPE SCHANCK VIC 3939 | 1312552 | RBD21 | 22kV AC | Rural Short | - fuse (EDO fuse) | two phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1405093 | 20200518UTD_01 | Crew replaced 10A EDO fuse at CAPE SCHANCK -ISO S/S B phase. Fuse had candled. SWER ACR RB7329 was opened by NCC to enable fuse change on the 22kV side of ACR. - fire report #6832, no ground fire. - ESV ref 13971860. LIS 1312552
97 | 2020-05-14 | 13:43 | -38.3092 | 145.0698 | 166 FOXEYS ROAD, TUERONG VIC 3915 | 1105620 | MTN32 | 22kV AC | Rural Short | - fuse (boric acid) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1405386 | 20200518UTD_02 | A HV fuse at "Ellerina P5-Junction" s/stn has candled.S/S is fully animal proofed. Fire report #6841 - no ground fire start - ESV ref 13971883 - LIS 11056203 Crew replaced a 6 Amp BA on White phase.
98 | 2020-05-14 | 17:48 | -37.8822 | 145.0111 | 54 ALLISON ROAD, ELSTERNWICK VIC 3185 | 2303150 | EL13 | Low voltage AC (<1kV) | Urban | - switch (disconnector/isolator) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1405473 | 20200518UTD_03 | MFB was on site at "Morton-Leslie" S/Stn when crew arrived and reported fire on assets but had gone out on its own - Source of fire at red phase isol (equip too melted to determine). ESV advised ref # 13978228 - LIS 2303150 | Started in or originated from a distribution system
99 | 2020-05-20 | 10:08 | -38.4232 | 144.8761 | 112 MAXWELL ROAD, FINGAL VIC 3939 | 1318609 | STO14 | 22kV AC | Urban | - fuse (boric acid) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1406965 | 20200521UTD_01 | Punshon Maxwell S/S 2 HV fuses candled, R and W phase , single phase S/S ,P/P ,conc pole, 6K BA fuses, fire report and ESV to be notified. ESV Ref 14001255 - LIS = 1318609 | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system
100 | 2020-05-21 | 11:13 | -37.8831 | 144.9901 | 128 GLEN HUNTLY ROAD, ELWOOD VIC 3184 | 2311320 | EW02 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1407345 | 20200525UTD_01 | Service line rubbing up against tree at pole end & had sparks & flames from it, Council has cut back tree form service line to units replaced 25 metres of 35mm 4c service....Fire evident on adjacent council vegetation ...Fire report 3846, LIS = 2311320 | Started by any person, bird, reptile or other animal coming into contact with a distribution system
101 | 2020-06-06 | 11:13 | -38.3657 | 144.7593 | 42 CENTRAL AVENUE, BLAIRGOWRIE VIC 3942 | 1304267 | STO21 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1412201 | 20200611UTD_01 | A resident at number 45 Central Ave Blairgowrie advised she saw something on the pole on fire. On arrival the crew identified a fire damaged FOLCB outside # 42 Central Ave which they replaced - LIS 1304267 | Started by lightning striking a distribution system or a part of a distribution system
102 | 2020-06-08 | 6:52 | -37.8581 | 145.1509 | 390 BLACKBURN ROAD, BURWOOD EAST VIC 3151 | 7025054 | EB33 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1412367 | 20200629UTD_02 | MFB reported a street light on fire.....crew attended and isolated a 250W HPS. To be replaced by street light crew. LIS 7025054 | Started by any other thing forming part of or coming into contact with a distribution system
103 | 2020-06-09 | 18:39 | -37.9053 | 144.9881 | 301 ST KILDA STREET, BRIGHTON VIC 3186 | 1806162 | NB33 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1413040 | 20200611UTD_02 | A report came in to UE of a FMB sparking at 310 St Kilda St, Brighton. On arrival the crew identified a fire damaged FOLCB on pole LIS 1806162. The likely cause was determined by EIO to be a earth defect within the customers installation at 301 St Kilda St | Otherwise started by a distribution system
104 | 2020-06-11 | 8:41 | -38.0002 | 145.0762 | 155 BEACH ROAD, PARKDALE VIC 3195 | 1807524 | M25 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1413538 | 20200629UTD_01 | Customer reported a fire on the pole. Crew attended and and reported the fire was actually a FOLCB feeding underground services on LIS 1807524.
105 | 2020-06-11 | 23:33 | -37.9593 | 145.0601 | 64A WILSON STREET, CHELTENHAM VIC 3192 | 1815005 | HT11 | Low voltage AC (<1kV) | Urban | - dropper / bridge | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1413845 | 20200629UTD_08 | Customer advised pole in front of property was sparking and arcing. Turned into flames but went out quickly. Black scorch marks near the powerlines and x-arm. Crew arrived and replaced a blackened LV IPC, LIS=1815005
106 | 2020-06-15 | 1:47 | -38.173 | 145.1872 | 240 WARRANDYTE ROAD, LANGWARRIN VIC 3910 | 8816167 | FSH21 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1414449 | 20200629UTD_07 | CFA reported a branch failed and was resting on the HV conductors -and requested tree require to be cut prior to fire brigade extinguishing fire. Crew arrived and cut tree branch clear, small branch was smoldering on ground - no fire start on the ground. | 1
107 | 2020-06-17 | 0:16 | -38.2003 | 145.2428 | 65 EVANS STREET, PEARCEDALE VIC 3912 | 3321507 | LWN21 | 22kV AC | Rural Short | - dropper / bridge | single phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1415152 | 20200629UTD_03 | Customer at no.65 Evans St said he saw flames on transformer. When the crew arrived they found a melted HV bushing cover caused by loose connection. They carried out repairs and replaced 6 k BA , Red phase. | 2
108 | 2020-06-22 | 16:57 | -38.2588 | 145.1818 | 4 CANNERY COURT, TYABB VIC 3913 | 9923466 | HGS33 | Low voltage AC (<1kV) | Rural Short | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1416801 | 20200629UTD_04 | LV pillar box caught fire after 160amp cct breakers failed, replacement of pillar box and breakers R & W 250 amp LV fuses blew at dist cabinet that feeds 5 Cannery ct Tyabb . ESV notified # 14201906 Small amount <0.5m of grass burnt. | 3
109 | 2020-06-23 | 21:37 | -38.3291 | 144.7169 | 55 FRIMMELL WAY, PORTSEA VIC 3944 | 1307407 | STO22 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1417207 | 20200629UTD_06 | 3PH fmjb to UG supply (53 & 55 Frimmell Way) caught fire due to corrosion, caused 2 x 250amp din LV fuses to FRANKLIN PARKVILLE s/s on white/blue phase. Damaged 2 wire service to 60 Frimmell Way repl. Repaired 2 wire service to 58 Frimmell Way. Services height compliant, premises tested ok & left, no damage to pole, only to fmjb that burnt out/caught fire. Fire ignition report 04460. Details emailed to RC (TS) and Eric C, whispir required, NCC Mgt to send. | 4
110 | 2020-06-27 | 19:01 | -38.176 | 145.1902 | 262 WARRANDYTE ROAD, LANGWARRIN VIC 3910 | 3301774 | FSH21 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1418250 | 20200629UTD_05 | Customer reported that the Service fuse box on pole in front of property (enter off Anthoney's Lane) has caught fire. Crew arrived (no fire on arrival) and replaced a melted transformer FMB at "WARRANDYTE T44 NTH 2" substation. | 5
6
7
8
10
11
12
13
14
15
16
17
18
19
20
Contents
ADD MORE ROWS
DELETE EXTRANEOUS ROWS

## 3. Systems and Audit
United Energy
F-factor data reporting
2019/20
Instructions:
United Energy must provide:
Table 4 - Information or reporting systems
(1) Name of any IT system used to collect fire start data or fault event data - i.e. SCADA system, or fault reporting system
(2) Whether the fire recording or fault recording process has been audited or complies with a relevant Australian or industry standard - Yes or No
(3) List any relevant Australian or industry standards that the fire recording or fault recording process complies with
(4) Whether the data entered into or removed from the IT system has been audited - Yes or No
Table 4: Information or reporting systems
Information or reporting systems | Name | System Audited | Relevant Standards
System 1 | Geographical Information System (GIS) | Yes | N/A
System 2 | Distribution Management System (DMS) | Yes | N/A
System 3
System 4
System 5
System 6
System 7
System 8
The SGSPAA Internal Audit function undertakes a programme of work in accordance with the SGSPAA Group Internal Audit Plan. This internal audit activity covers elements of the systems and process used for capturing, recording and maintaining fire start data.
Contents