## Contents
Electricity Distribution Network Service Provider F-factor Reporting Template
Table of contents
| Cover sheet | 2. Fire start report
| 1. F-factor summary | 3. Systems and Audit
Cover sheet
1. F-factor summary
3. Systems and Audit
2. Fire start report

## Cover
Distribution Network Service Provider
Fire start report
This template is to be used by a DNSP to provide a fire start report to the AER in accordance with section 5 of the F-factor Order in Council.
Colour coding of input sheets:
Dark blue = AER headings
Grey = AER instructions
Yellow = Input cells
Light orange = Automatically-generated cells
Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so.
The cells and structure of the spreadsheet is locked to prevent inadvertent interference with the automated settings.
All dollar amounts are to be unrounded, and in nominal terms.
DNSP: |  | United Energy
DNSP - trading name: |  | United Energy Distribution Pty Ltd
DNSP - Australian business number: |  | 70 064 651 029
Reporting year: |  | 2018/19
Business address | Address |  | 43 - 45 Centreway
| Suburb |  | Mt Waverley
|  | State | Victoria | Postcode | 3149
Postal address | Address |  | P.O Box 449
| Suburb |  | Mt Waverley
|  | State | Victoria | Postcode | 3149
Contact name/s | Trevor Fisher
Contact phone/s | 0418993821
Contact email address/s | trevor.fisher@ue.com.au

## 1. F-Factor summary
United Energy | IRU target: | 22.3
F-factor data reporting | IRU amount: | 18.14
2018/19 | Revenue adjustment: | 62400
Table 2: Summary of total fire starts by F factor Order definition
Kind of Fire Start by definition of fire start under clause 5 of F-factor Order | Total fires by cause
Started in or originated from a distribution system | 74
Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | 14
Started by any person, bird, reptile or other animal coming into contact with a distribution system | 6
Started by lightning striking a distribution system or a part of a distribution system | 2
Started by any other thing forming part of or coming into contact with a distribution system | 8
Otherwise started by a distribution system | 0
Total | 104
Contents

## 2. Individual fire start info
United Energy
F-factor data reporting
2018/19
Instructions:
Enter into this worksheet fire start data, from any IT system, which have been recorded by [DNSP Name]. Note that fire starts must be in accordance with the definition of a fire start in the Order In Council.
"Fire" should be interpreted using its common meaning and can be defined as a process in which substances combine chemically with oxygen from the air and typically give out bright light, heat and smoke. A fire should be recorded where there is evidence of smoking, charring, scorching, burning or any other evidence that a fire had occurred.
[DNSP Name] must provide:
Table 3 - Individual Fire Starts
(1) Date - dd/mm/yyyy
(2) Time - if known, the 24-hour time of the fire start hh:mm
(3) Latitude and longitude of the fire start as decimal coordinates
(4) Address of the property on which the incident occurred or closest to the incident
(5) Asset number for the asset nearest the fire start
#REF!
(7) Voltage on the line in which the fire start occurred (note: this may not be the nearest polyphase overhead line)
(8) Network categorisation - CBD, Urban, Rural Long or Rural Short
(9) Asset type of primary asset causing fire in accordance with OSIRIS asset categories
(10) Where the asset involved in the fire is a transformer or an overhead or underground line, provide the phase, or phases, of the line or transformer
(11) Kind of fire start in accordance with categories specified in Clause 5 of the F-factor Order-In-Council
(12) Identify the location of the fire start in accordance with the categories specified in Clause 11(b) of the F-factor Order-In-Council
(13) Provide the BOM fire danger rating applicable at the time of the fire start (data is available on the EM-COP website)
(14) [DNSP Name]'s record number for the incident
(15) ESV's OSIRIS reference number for the incident
(16) Free text description of the fault containing relevant comments from field reports
Table 2: Individual Fire Starts
Number | Fire starts | [8 empty] | Fire Type |  |  | Risk Factors |  |  |  | IRU amount | Addition Information
Column1 | Date 1 | Time 2 | Latitude 3 | Longitude 3 | Address of incident 4 | ID of nearest asset 5 | ID of nearest polyphase line 6 | Voltage of line in which fire start occurred 7 | Network categorisation 8 | Type of primary asset involved in fire start 9 | Phase(s) of line or transformer 10 | Kind of fire start as per Clause 5 of F-factor Order-In-Council 11 | Location area 12 | Location multiplier | Fire danger rating 13 | Danger multiplier | Product of multipliers | DNSP record number 14 | OSIRIS (ESV) reference number 15 | Fault description 16
1 | 2018-07-09 | 0:58 | -37.8179 | 145.1761 | SPRINGVALE ROAD, NUNAWADING VIC 3131 | 9751815 | NW 14 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1196382 | 20180716UTD_04 | Street light pole on fire as per MFB spring rd 1n whitehorse, center median. opp ambulance depot. light head nth bound side - LIS = 9751815
2 | 2018-07-23 | 12:08 | -38.3195 | 144.7105 | 3804 POINT NEPEAN ROAD, PORTSEA VIC 3944 | 1307193 | STO13 | 22kV AC | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1201097 | 20180725UTD_01 | Tree was on fire as per CFA road side hv condcutor property boundary of 3804 & 3808 - lis#1307193 conductor fire repot# 6826 council tree -no fire when crew arrived
3 | 2018-07-23 | 19:32 | -38.0672 | 145.1585 | THOMPSONS ROAD, BANGHOLME VIC 3175 | 9679025 | CRM11 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1201286 | 20180727UTD_01 | Probable conductor clashing Thompsons rd adjacent THOMPSON P277 MMBW S/S, small fire which CFA attended.R Clarke fire report. Suspect conductor clash due to high winds - LIS 9679025
4 | 2018-07-24 | 18:53 | -37.8751 | 145.1246 | MILLER CRESCENT, MOUNT WAVERLEY VIC 3149 | 8802801 | BW 33 | 11kV AC | Urban | - fuse (powder filled) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1201917 | 20180810UTD_01 | Candling PF Fuse Sub placed under LV // prior to opening of the the HV fuses. Footpath side PFF unit requires replacement. LIS= 8802801
5 | 2018-07-28 | 18:03 | -37.9049 | 145.1234 | 73 CLAYTON ROAD, OAKLEIGH EAST VIC 3166 | 600362 | CDA23 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1203802 | 20180730UTD_01 | Cust reported Pole fire, crew isolated supply at the j/box on the pole fed by an o/head service. street light head (150HPS) needs replacement. LIS # 600362 which is o/s of 73 Clayton Rd Oakleigh east.
6 | 2018-07-31 | 21:24 | -37.8994 | 145.0953 | UNIT 8 105 ATHERTON ROAD, OAKLEIGH VIC 3166 | 8803853 | OAK32 | Low voltage AC (<1kV) | Urban | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1204647 | 20180828UTD_05 | Closest LIS 8803853 - repl burnt out 501 mtr - old mtr 0962856 - no display, new 1362954 - 0 - internal fire - faulty mtr - fire out on arrival
7 | 2018-08-10 | 18:22 | -38.4572 | 144.9901 | 2150 MORNINGTON-FLINDERS ROAD, FLINDERS VIC 3929 | 1314698 | DMA23 | 22kV AC | Rural Short | - dropper / bridge | single phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1207722 | 20180929UTD_01 | LIS - 1314698. Its actually on MTN Flinders RD and Boyds. Its not at Frank Flinders. Damage high up on pole. Transformer needs to be replaced. 1single ph 50kva pole mount. feeding 2 customer - no fire on arrival - cct dropper blackened only. PM # 1000668807 - Sub Mtn Fldrs P10 Boyd - per Trent Wilson - 3rd call to attend Sat am - VPN advised. Replaced a single phase 50kva transformer, and 1 burnt out lead on the white phase. Tested and left on 238V. ref job 1207724 for further details
8 | 2018-08-17 | 19:38 | -37.9821 | 145.2151 | CLEELAND STREET, DANDENONG VIC 3175 | 637203 | LD 07 | 22kV AC | Urban | - dropper / bridge | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1210051 | 20180828UTD_01 | lis: 37203 out front of #56 - issues possible from fuse on pole.Crew found the centre phase HV dropper from the bottom of the fuse unit to the vaccum switch. Cap bank has old stile vaccum switches and requires a load buster to isolate. will require operator to attend tomorrow with said load buster to isolate cap bank completely. Is safe for tonight.
9 | 2018-08-18 | 1:26 | -38.1261 | 145.13 | 45 BOONONG AVENUE, SEAFORD VIC 3198 | 3308283 | FTN14 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1210065 | 20180828UTD_02 | LIS - 3308283, fire brigade leaving, fire out, disconnected street light for safety, s/l head burnt out, new head & globe req'd, Casey & Rod to attend over the weekend - replaced 80w sl head and rewired
10 | 2018-08-24 | 3:54 | -37.9467 | 145.0063 | 22 QUEENS SQUARE, SANDRINGHAM VIC 3191 | 1817885 | SR 13 | Low voltage AC (<1kV) | Urban | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1211952 | 20180828UTD_03 | LIS - 1817885, FMJB on lis#1817885 burnt out and start a small pole fire, damaged to property #22 Queens Sq - Fire report #01542
11 | 2018-08-26 | 22:07 | -38.0614 | 145.1179 | 10 NEWBERRY AVENUE, BONBEACH VIC 3196 | 3303088 | CRM22 | Low voltage AC (<1kV) | Urban | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1212546 | 20180828UTD_04 | replaced 3 phase FMB on lis # 3303088, replaced 2w service to #10 Newberry Ave, height comp, issued 5 day defect on FMB left on, CIA and getting REC tomorrow to do repairs, NST tested and passed, also replaced 2 x 250a din phase white and blue phases
12 | 2018-08-28 | 19:43 | -37.9033 | 145.0453 | 7 ORMOND ROAD, ORMOND VIC 3204 | 2322622 | BT 09 | 11kV AC | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1213290 | 20180909UTD_02 | HV LA needs to be cut clear, LIS# 2322622, crew to return later to cut clear. crew also replaced copper D on the blue phs.
13 | 2018-09-04 | 19:00 | -37.8513 | 145.125 | 344 BURWOOD HIGHWAY, BURWOOD VIC 3125 | 7050956 | EB 11 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1215353 | 20180909UTD_06 | LIS# 7050956 Public lighting pole in centre mediam strip (tramways pole)250a HPS lantern will need to be replaced.
14 | 2018-09-07 | 18:50 | -37.787 | 145.1344 | 732 DONCASTER ROAD, DONCASTER VIC 3108 | 7061755 | DC 04 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1216628 | 20180916UTD_04 | Disconnected burnt out p/light head on lis: 7061755 - refer to s/light crew to replace 150w hps light - supply on to 1/732 when crew arrived - crew carried out nst and passed at unit - no fire when crew arrvied.
15 | 2018-09-09 | 18:48 | -38.3376 | 145.1751 | 16 SUDHOLZ STREET, BITTERN VIC 3918 | 8823764 | HGS23 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1216829 | 20180916UTD_06 | Repl UG fuse boxes #11 and 14 Sudholz at lis 8823764 -fire was out on arrival - 3ph fuse box at #14 shorted and cause fire at pole - poss loose connection
16 | 2018-09-11 | 20:18 | -38.2841 | 145.1887 | FRANKSTON-FLINDERS ROAD, HASTINGS VIC 3915 | 1105560 | HGS33 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1217573 | 20180929UTD_04 | LIS#= 1105560 - due to an earlier animal fault on ACR 7521, HV conductors clashed started small grass fire, 6mtrs sq approx. Fire report filled out #05633.
17 | 2018-09-12 | 10:16 | -37.8803 | 144.9974 | HOTHAM STREET, ELSTERNWICK VIC 3185 | 2306611 | EW 08 | 11kV AC | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1217844 | 20181001UTD_02 | Fault current from a nearby fault caused a HV bridge to blow on anchor pole in Hotham st corner of Hotham Ave spitting molten metal into the grass below causing a small ground fire.
18 | 2018-09-15 | 9:43 | -37.9626 | 145.0602 | 26 WILSON STREET, CHELTENHAM VIC 3192 | 1814983 | HT 11 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1219025 | 20181001UTD_03 | LIS - 1814983. operator found HV strain xarm burned through at the xarm strap, the LV xarm was also damaged. Both x-arms replaced
19 | 2018-09-25 | 11:53 | -37.8415 | 145.2001 | CARLINGA DRIVE, VERMONT VIC 3133 | 7031165 | RWT35 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1222030 | 20181002UTD_01 | Truck hit tree which caused branches to make contact and catch fire (MFB) with HV O/H conductors at LIS#7031165.
20 | 2018-09-27 | 13:20 | -37.8113 | 145.1742 | GLADYS STREET, NUNAWADING VIC 3131 | 7032815 | NW 21 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1222712 | 20181019UTD_02 | Refer to t/o : 1222705 - no fire when crew arrived - fire ignition report not required - unable to group due to abnormal switching (this job was cause of NW21 feeder reclose) - address now 30 gladys av as per mfb. Crew found the remains of a bunch of helium balloons in the HV at LIS#7032815. Caused damage to HV disc insulators and 2 X HV X-arms. AP#45935 issued at 1600 to replace x-arms & discs - crew repalced x2 us21 hv x-arms (strain) on lis: 7032815 - Notification 1000678128.
21 | 2018-09-27 | 19:55 | -37.8894 | 145.2204 | 31 WESTBURN GROVE, SCORESBY VIC 3179 | 617315 | MGE21 | 22kV AC | Urban | - fuse (powder filled) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1222828 | 20181002UTD_03 | Centre phase white HV fuse candelling... to lv// and isolate. Fuse unit was not properly closed, replaced 16a pff... no interruption.
22 | 2018-10-09 | 20:38 | -37.902 | 145.1499 | 509 FERNTREE GULLY ROAD, GLEN WAVERLEY VIC 3150 | 611790 | GW 05 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1225875 | 20181012UTD_01 | Pole fire lis 0611790 O/S 509 FTG Rd Glen Waverly. Dual cct 66kv pole with GW5 22KV FDR & LV. CFA attended. Small section of GW5 between DN0594 & Fault crew replaced burnt x arm.
23 | 2018-10-15 | 10:37 | -37.8976 | 145.0361 | 196 BOORAN ROAD, ORMOND VIC 3204 | 2322822 | CFD25 | 11kV AC | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1227219 | 20181016UTD_01 | Cap Bank "Booran-Beaty" lis2322822, red phase lead burnt off ……a caller reported a fire at the top of the pole but there was no fire damage
24 | 2018-10-16 | 9:28 | -38.4627 | 144.9946 | 2216 MORNINGTON-FLINDERS ROAD, FLINDERS VIC 3929 | 8827247 | DMA23 | 22kV AC | Rural Short | - fuse (EDO fuse) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 1227570 | 20181018UTD_03 | HV fuse candelled... to open and replace..LIS 8827247 "MTN Flind P7 - Boyds"
25 | 2018-10-16 | 20:29 | -38.3166 | 145.1941 | 42 SALMON STREET, HASTINGS VIC 3915 | 1109493 | HGS32 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1227966 | 20181018UTD_04 | LIS 1109493, 22kV HV strain/LV term pole, caught on fire due to tracking/salt air, burnt behind LV arm/kingbolt, tracking marks down pole to LV arm.Fire contained to upper section of pole/xarm only.
26 | 2018-10-20 | 10:52 | -37.8901 | 145.0652 | 396 NEERIM ROAD, CARNEGIE VIC 3163 | 2327331 | EM 10 | 11kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1229633 | 20181022UTD_01 | Pole will req replacing - burnt of behind the LV x arm - traffic control will be req - HV Strain pole with HV isolators and off set lv x arm with LV undergound - lis 2327331 - ok to change next couple of weeks.
27 | 2018-10-31 | 11:30 | -37.9286 | 145.149 | 893-895 PRINCES HIGHWAY, SPRINGVALE VIC 3171 | 9227806 | SVW45 | 22kV AC | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1232005 | 20181101UTD_01 | See TE#1231733 Succ Recl. Damage to WPh PF Fuse unit at DN0545 PRINCES HWY and replaced Damaged fuse unit caused by flashover - LIS 9227806
28 | 2018-11-05 | 11:59 | -37.9816 | 145.2024 | 27 WILMA AVENUE, DANDENONG VIC 3175 | 633695 | NP 36 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1233104 | 20181109UTD_01 | Broken X/ARM, crossarm fire lis#0633695 Wilma Ave.
29 | 2018-11-06 | 10:19 | -37.9756 | 145.0166 | 611 BALCOMBE ROAD, BLACK ROCK VIC 3193 | 1812587 | BR 04 | 11kV AC | Urban | - underground cable | three phase | Started by lightning striking a distribution system or a part of a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1233313 | 20181224UTD_01 | Lightning struck CHP in Bluff cnr of Beach rd, all 6 S/D's failed and require replacement. S/D's cut clear and ASR. PN#1000685078
30 | 2018-11-20 | 17:34 | -37.8629 | 145.0359 | 53 THANET STREET, MALVERN VIC 3144 | 2313937 | K 06 | 11kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1238291 | 20181206UTD_03 | Emergency switching to remove council tree branch from across HV/LV, LIS=2313937
31 | 2018-11-21 | 2:02 | -38.1395 | 145.1206 | 122 GOULD STREET, FRANKSTON VIC 3199 | 3309214 | FTN14 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1238431 | 20181206UTD_04 | Confirmed fire start, krone box caught on fire, cause of ignition unknown. Crew cut clear abc and krone box in gould st at LIS# 33009214.
32 | 2018-11-21 | 21:23 | -38.3656 | 145.2016 | COOK ROAD, HMAS CERBERUS VIC 3920 | 8826921 | HGS31 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1238816 | 20181206UTD_06 | large cypress hedge on defense land growing close to HV. LIS# 8826921 to LIS# 1110586 branch has burnt through & has been removed by fire crew, tree clearers on site assessing any further follow up required.
33 | 2018-11-23 | 16:42 | -38.3203 | 144.7135 | NEPEAN PLACE, PORTSEA VIC 3944 | 1307258 | STO22 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1239371 | 20181206UTD_05 | Pole fire at LV x arm on pole Lis#1307258. P/N #1000687738 fire report #6725, also refer #1239371
34 | 2018-11-29 | 1:42 | -37.9878 | 145.1007 | DE HAVILLAND ROAD, MORDIALLOC VIC 3195 | 1806824 | MC 06 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1241272 | 20181206UTD_10 | Light misty rain at time of outage.Pole fire & broken x arm at CH4083 NOP between MC9 & MC6. lis 1806824.
35 | 2018-12-05 | 15:51 | -37.8129 | 145.1733 | 303 SPRINGFIELD ROAD, NUNAWADING VIC 3131 | 7037165 | NW 21 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1243691 | 20190114UTD_01 | A possum contacted live asseyts caught fire and landed on top of krone box LIS 7037165
36 | 2018-12-13 | 12:43 | -37.8279 | 145.1585 | 5 NAUGHTON GROVE, BLACKBURN VIC 3130 | 7035862 | NW 21 | 22kV AC | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1246753 | 20190121UTD_01 | private tree ok at the moment abt 400ml from HV, was only touching HV due to heavy rain, tracking caused smoke where tree was touching HV. 1 branch had burnt through & was on the groun
37 | 2018-12-14 | 17:48 | -38.2755 | 145.0243 | 14 GREENLAW CRESCENT, MOUNT MARTHA VIC 3934 | 1102908 | DMA24 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1247316 | 20181227UTD_01 | Cause was car into pole LIS# 1102908 in Greenlaw Cres. Wood pole with steel x-arm Inter /angle. HV conductor was knocked off insulator and made contact with Cypress tree and burnt 2 braches
38 | 2018-12-15 | 23:02 | -37.9156 | 145.0604 | 198 EAST BOUNDARY ROAD, BENTLEIGH EAST VIC 3165 | 2334491 | OR 24 | 11kV AC | Urban | - dropper / bridge | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1247640 | 20190121UTD_02 | Possum flashed over and caused a flashover on a pole -MFB reported pole on fire but was out by the time crew arrived.
39 | 2018-12-17 | 7:01 | -37.9162 | 145.0048 | 18 HAMMOND STREET, BRIGHTON VIC 3186 | 1804900 | NB 25 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1247853 | 20181227UTD_02 | A Pole Mounted FMJB for neutral screen cable across road out of HAMMOND HAMPTON blew up. Athis caused a small grass fire which was promptly extinguished
40 | 2018-12-22 | 2:07 | -38.2571 | 145.1896 | 1510 FRANKSTON-FLINDERS ROAD, TYABB VIC 3913 | 1108044 | HGS33 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1249550 | 20181227UTD_03 | 22kv insultor polymeric need to be replaced and also the LV tee off xarm fire report # 6827. LIS # 1108044. Pole missing 1/3 thickness at LV t off x arm.
41 | 2018-12-27 | 21:58 | -37.8969 | 145.1043 | FERNTREE GULLY ROAD, OAKLEIGH VIC 3166 | 2324619 | OAK35 | 11kV AC | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1250584 | 20190111UTD_01 | A possum flashed over HV at anchor pole PO-2324619 breaking wrap on and dropping conductor into the LV dropping the OHC to the ground causing a small grass fire.
42 | 2018-12-29 | 16:14 | -37.7668 | 145.1362 | 16 BAMFIELD CLOSE, TEMPLESTOWE VIC 3106 | 7060057 | BU 09 | Low voltage AC (<1kV) | Urban | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1250886 | 20181231UTD_01 | UG pillar has melted upillar had caught fire due to failed connection inside wall next to pillar was blackened. no burn marks on ground. fire report# 3010. Lis 7060057 - street light pole next to Pillar
43 | 2019-01-01 | 1:47 | -37.9026 | 145.0436 | UNIT 2 14 ULUPNA ROAD, ORMOND VIC 3204 | 2322759 | BT 09 | Low voltage AC (<1kV) | Urban | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1251214 | 20190102UTD_01 | Removed the jbox from poa and rapaired active and neutral connection at poa. UE j/box caused fire and damaged cust fascia and smoke damage to house.Supply on Fire ignition report num is 01567. LIS 8803375
44 | 2019-01-15 | 8:35 | -38.3776 | 144.8065 | 58 PENINSULA AVENUE, RYE VIC 3941 | 1303949 | STO14 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1254645 | 20190115UTD_01 | HV inter x-arm needs to be changed, LIS# 1303949, fire start, fire report to be provided by crew, cause elements mist/fog
45 | 2019-01-16 | 14:45 | -37.8503 | 145.0697 | 20 CUSDIN STREET, GLEN IRIS VIC 3146 | 2310837 | K 08 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1255253 | 20190118UTD_01 | fire start report#TBA fmb at pole end caught fire, replaced fmb and reterminated leads. test and left on. cause unknown
46 | 2019-01-18 | 15:37 | -38.3001 | 145.1536 | 265A HODGINS ROAD, HASTINGS VIC 3915 | 1106008 | HGS23 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | single phase | Started by lightning striking a distribution system or a part of a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 1255946 | 20190211UTD_06 | EIV advised 1540pm. new mter required. damage appears to be caused by lightning. Closest LIS 1106008
47 | 2019-01-24 | 8:30 | -38.3778 | 145.1404 | 8 LUXTON DRIVE, SOMERS VIC 3927 | 1107139 | HGS23 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Very High | 1 | 1 | 1257480 | 20190124UTD_01 | UE responsible gum tree branch broken and resting on the HV OHC at LUXTON 1 SANDY POINT s/s. SSummer Auditor (Brett)witnessed Flames on branch whilst it was resting on the OHC. LIS 1107139
48 | 2019-01-24 | 11:12 | -38.1356 | 145.1291 | 78 DANDENONG ROAD W, FRANKSTON VIC 3199 | 3308696 | FTN14 | Low voltage AC (<1kV) | Urban | - connection box | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1257579 | 20190125UTD_01 | 3ph folcb at pole end, burnt out due to deterioration, tested ok & left on, lis 33008696,
49 | 2019-01-24 | 13:23 | -37.9067 | 145.0092 | MILROY STREET, BRIGHTON EAST VIC 3187 | 2333154 | NB 34 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1257657 | 20190125UTD_02 | An Ampact Connection failed on LV CHP BLUE PHASE. Caused a grass fire which was quickly extinguished, beleive it is UE grass outside ZSS. LIS 2333154
50 | 2019-01-24 | 19:46 | -37.9025 | 145.0686 | 31 DALNY ROAD, MURRUMBEENA VIC 3163 | 2315112 | OR 35 | Low voltage AC (<1kV) | Urban | - dropper / bridge | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1257876 | 20190125UTD_03 | Replaced blue phs tx lead, lead burnt off and started ground fire, 1-1.5 sqr mtr on nature strip, was out on arrival. Fire start report , photos obtained, LIS 2315112
51 | 2019-01-27 | 15:39 | -37.9988 | 145.2561 | 41 FRAWLEY ROAD, HALLAM VIC 3803 | 616529 | DN 22 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1259338 | 20190130UTD_01 | LIS#: 0616529 - Fire ignition report filled out (9740) - small grass fire started where conductors met ground <2m sq out front of #41 Frawley Rd after truck brought them down
52 | 2019-01-28 | 14:48 | -38.0824 | 145.186 | FRANKSTON-DANDENONG ROAD, CARRUM DOWNS VIC 3201 | 3318989 | DVY24 | 22kV AC | Rural Short | - dropper / bridge | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | Very High | 1 | 1 | 1259452 | 20190130UTD_02 | Lis3318989, bird across LA's @ FS0047. LA's slightly blackened on sth side of switch. still intact and in service. remains of small grass fire observed in the vacinity. Fire report#00711. est 50m2, Grass.
53 | 2019-01-30 | 13:28 | -37.934 | 145.2173 | ILLAWARRA AVENUE, ROWVILLE VIC 3178 | 9339466 | LD 06 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1260132 | 20190131UTD_02 | Boom from excavator into HV, started small fire, photos obtained, LIS 9339466
54 | 2019-01-30 | 16:59 | -37.7744 | 145.1831 | SPRINGVALE RD, DONVALE | 7071454 | NW 13 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1260218 | 20190205UTD_02 | Tree on HV overhead Springvale Rd causing cable to fail and broken crossarms starting a small 2msq ground fire LIS 7071454 -near DT1208. HV conductors down, this is a separate event to Creek Rd Event
55 | 2019-01-30 | 17:05 | -37.8184 | 145.1961 | CREEK ROAD, MITCHAM VIC 3132 | 7030642 | RWT12 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1260219 | 20190201UTD_01 | Tree on HV overhead Creek Rd repoteted as burning (separate evnt to Springvale Rd Event) near LIS 7030642
56 | 2019-01-30 | 17:38 | -38.046 | 145.2266 | 875 TAYLORS ROAD, DANDENONG SOUTH VIC 3175 | 622594 | DVY24 | 22kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Very High | 1 | 1 | 1260279 | 20190131UTD_03 | Fire igition report 9741 - small grass fire approx 2m sq was cause by hv conductors hitting the ground due to council tree - LIS 0622594
57 | 2019-01-30 | 21:37 | -37.9134 | 145.1167 | NORTH ROAD, CLAYTON VIC 3168 | 2332439 | OE-SVTS | 66kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1260234 | 20190201UTD_02 | 66kv h/v x-arm was on fire (not on fire when crew arrived) - fire ignition report #04451 (fire contained to x-arm only) - h/v term x-arm to be replaced - LIS 2332439
58 | 2019-02-01 | 1:27 | -38.1776 | 145.1656 | 250 ROBINSONS ROAD, LANGWARRIN VIC 3910 | 3310277 | TBTS-FTS | 66kV AC | Rural Short | - insulators | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 1261024 | 20190211UTD_03 | Also refer #1261039 per MFB, grass fire in area has damaged lis # 3310277 fire start whispir to be sent, Blue phase 66kv insul damaged causing leakage to base of pole small grass fire.
59 | 2019-02-03 | 16:43 | -37.8397 | 145.1836 | STEVENS ROAD, VERMONT VIC 3133 | 7031909 | NW 33 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Severe | 2 | 0.4 | 1261667 | 20190211UTD_04 | White phase LV ampac connection for the south cct had burnt off @ lis # 7031909 - repaired - small burnt area approx 12inches X 12 inches fire report #03093 - caused by melting metal falling on ground.
60 | 2019-02-04 | 17:50 | -37.7583 | 145.1083 | PAMELA GROVE, TEMPLESTOWE LOWER VIC 3107 | 7068515 | BU 06 | 22kV AC | Urban | - fuse (powder filled) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1262122 | 20190211UTD_05 | replaced 20a pff blue phase hv fuse... small fire on ground possible due to fuse candelling and garbage bin fire. Fire report # 03094 - crew emailed photos to NCC Control Hv fuse had blown and fuse had candelled . Scorch marks on ground from fuse elements & poreclain . 23 Airds Rd Templestowe LIS 7068515
61 | 2019-02-06 | 21:31 | -37.9842 | 145.2446 | MARIE STREET, DOVETON VIC 3177 | 621692 | DN 10 | 22kV AC | Urban | - pole (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1263336 | 20190214UTD_01 | Pole fire in Marie St, 1 north of Louis St. Centre phase insulator breaking down and pole burning. Pole was burning down to the Telstra box. Replaced HV and LV x-arms on pole LIS 0621692. Asset only fire.
62 | 2019-02-06 | 22:05 | -38.3679 | 144.7696 | MELBOURNE ROAD, BLAIRGOWRIE VIC 3942 | 1316290 | STO21 | 22kV AC | Rural Short | - crossarm (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 1263429 | 20190214UTD_02 | T-off x-arm burnt through Melbourne Rd, cnr Kirkwood, LIS 1316290. HV conductor resting near LV. Splash marks on blue phase LV -
63 | 2019-02-07 | 13:37 | -37.95 | 145.175 | PRINCES HIGHWAY, SPRINGVALE VIC 3171 | 618315 | SVW55 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1263568 | 20190214UTD_03 | Pole lis # 0618315 fire ignition report #: 1097. Fire damage obseved in the vacinity of 10x5m - A vehicle has hit a telecommunications cable between lis 0618315 and 0629124 causing wire strand to flick up to the HV.
64 | 2019-02-07 | 17:22 | -37.9966 | 145.0737 | MONACO STREET, PARKDALE VIC 3195 | 9864653 | M 35 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1263632 | 20190214UTD_04 | LV leads have burnt out, likely flames at some point due to 1st call comments and damage. No fire started on ground per crew, refer #1263633 - lis 9864653
65 | 2019-02-11 | 11:54 | -38.0331 | 145.2018 | HAMMOND ROAD, DANDENONG VIC 3175 | 623109 | DVY31 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1264499 | 20190218UTD_01 | Truck has hit LV slack span causing Red phase conductor to fall to the ground starting a 30sqm grass fire. LIS 0624964
66 | 2019-02-15 | 12:35 | -38.1496 | 145.1152 | NEPEAN HIGHWAY, FRANKSTON VIC 3199 | 8819481 | FSH31 | Low voltage AC (<1kV) | Urban | - lamps (major road) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1266284 | 20190220UTD_01 | 150W HP Sodium street light fire - LIS 8819481
67 | 2019-02-18 | 7:13 | -37.9141 | 145.1846 | COLUMBIA PARK PRE SCHOOL, 26-28 COLUMBIA DRIVE, WHEELERS HILL VIC 3150 | 614322 | MGE34 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1266695 | 20190305UTD_01 | Gum tree on Private property at 26-28 Columbia Dve dropped 3m branch across HV and was starting to burn. C/R shortened feeder and opened MGE34 CB and branch was flicked off with operating stick
68 | 2019-02-25 | 20:05 | -38.1061 | 145.1722 | 44 OGRADYS ROAD, CARRUM DOWNS VIC 3201 | 8814069 | FTN24 | Low voltage AC (<1kV) | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1269387 | 20190227UTD_02 | Replcd white phase lv fused isolator 315 amp hrc white phase fuse & copper lead to the mains had burnt out and caused a small 1m grass fire under pole fire report # 6961 - O'Grady - Shearwater S/Stn lIS 8814069
69 | 2019-02-25 | 23:11 | -38.356 | 144.7584 | 2 LABUAN STREET, SORRENTO VIC 3943 | 1306287 | STO13 | 22kV AC | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1269343 | 20190226UTD_02 | White phase 15a BA fuse blown and HV ABC dropper from bottom fuse unit burnt out. (assumed molten metal caused ignition as small ground fire around base of pole (4m2). LIS 1306287 Labuan-Hughes S/Stn
70 | 2019-02-28 | 20:02 | -37.9364 | 145.0997 | 34 DALBEATTIE DRIVE, CLARINDA VIC 3169 | 2330277 | CDA22 | Low voltage AC (<1kV) | Urban | - dropper / bridge | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1270485 | 20190304UTD_01 | t/x was not on fire - Repaired burnt red phs isol lead on t/x and also neutral lead - replaced 1phs grey twisted service to #25 Delbeattie Dr with new 2c black twisted service - nst'ed and passed - cuse: red phs and neutral rubbing together over time LIS 2330277
71 | 2019-03-01 | 10:29 | -38.2321 | 145.1911 | 6 BUSHY COURT, SOMERVILLE VIC 3912 | 1109065 | HGS33 | 22kV AC | Rural Short | - fuse (powder filled) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1270642 | 20190304UTD_03 | HV PFF operation . Fuse malfunction broken PF causing small fire at base of pole crew taking photos & doing fire report rep# 6941. 1 ph sub LIS 1108611
72 | 2019-03-01 | 13:00 | -37.9014 | 145.1033 | 5 WILLIAM STREET, OAKLEIGH VIC 3166 | 2325899 | OE 15 | Low voltage AC (<1kV) | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 19000090760 | 20190304UTD_02 | Human Error - LV Catenery flicked up into LV causing splashing and a small grass fire 2mSQ - lis 2325899
73 | 2019-03-01 | 18:53 | -37.8588 | 145.0711 | Brownell Rd between Ashburton Rd and Rosedale Rd | 2336334 | RD 04 | Low voltage AC (<1kV) | Urban | - connector / termination | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1270887 | 20190423UTD_01 | Crew replaced burnt out Transformer LV Isol blade on White phase. Cause was combination of heat and elec overload.
74 | 2019-03-02 | 8:42 | -38.3608 | 144.8871 | 1491 POINT NEPEAN ROAD, ROSEBUD VIC 3939 | 1301093 | RBD22 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1271001 | 20190304UTD_04 | Mechanical failure of HV & LV x arms in Pt Nepean Rd RBD. see event 1271005 lis 1301093 & at 1301094 small fire started at base of pole 1X1 M. fire report being done by fault crew
75 | 2019-03-02 | 16:57 | -37.9008 | 145.0129 | 240 NORTH ROAD, BRIGHTON EAST VIC 3187 | 2305826 | BT 10 | Low voltage AC (<1kV) | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1271119 | 20190305UTD_02 | Burnt out red ph IPC connection - 150mm copper thru 19325 Alum - fire cause council tree to catch fire - small fire only on branch - fire report #03665 - lis 2305826 - whisper sent
76 | 2019-03-02 | 18:08 | -37.9831 | 145.0713 | UNIT 1 112 WARRIGAL ROAD, PARKDALE VIC 3195 | 1809079 | M 35 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1271164 | 20190306UTD_01 | Xarm fire - replaced HV inter x-arm. 3 x HV insulators, and replaced 10mtrs of 19/200 copper conductor, restored 2300 - lis 1809079
77 | 2019-03-03 | 18:26 | -38.1861 | 145.1733 | 120 BARRETTS ROAD, LANGWARRIN SOUTH VIC 3911 | 3321371 | FSH32 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | Severe | 2 | 2 | 1271399 | 20190306UTD_02 | Fire ignition report Number 6727, caused by sparks from melted folcb, small grass fire approx 1 mtr square. whispir sent - lis 3321371
78 | 2019-03-04 | 3:18 | -38.3084 | 145.0323 | OLD MOOROODUC ROAD, DROMANA VIC 3936 | 1104930 | DMA24 | 66kV AC | Rural Short | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 1271429 | 20190306UTD_03 | REF TO# 1271428 -report of fire start by cfa see event 1271429. Patrol found bark on DMA 24 centre ph at lis 1104930. Old Moorooduc rd After emergency switching bark removed and appears to have significant burn marks. MTN-DMA 66kv line in on same pole. fire approx 30 X 40 M. Grass burn only no asset damage. Whispir sent, UE Emerg manager advised. Crew adv Photos obtained/fire report raised and details provided to NC.
79 | 2019-03-05 | 1:04 | -38.3352 | 144.9764 | PALM GROVE, DROMANA VIC 3936 | 8825277 | DMA21 | 66kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1271730 | 20190308UTD_01 | Sleeve let go at Heales RD & Pt Nepean Rd Dromana. This caused the conductor to clash LIS#8825277 Seacombe and Pen link freeway,starting a small grass fire. Fire Ignition report 04453, Photos Taken.
80 | 2019-03-10 | 16:30 | -37.9267 | 144.9943 | 44 NEW STREET, BRIGHTON VIC 3186 | 1805858 | MR 32 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1273660 | 20190320UTD_03 | X arm fire at LIS#1805858, req replacement. ASR except sth cct out of NEW N51-WOLSELEY - Fire Ignition Report #: 02525 EAP #47848 issued @ 1745 by DVL. Crew replaced hv inter x-arm and sleaved out damaged lv mains on red phs on south cct of NEW N51 WOLSELEY - Notification 1000701147. U/E Mgr: N Sequeira adv x-arm had burn marks but did not cause a fire elsewhere.
81 | 2019-03-12 | 11:35 | -37.9885 | 145.1025 | 17 SIBTHORPE STREET, MORDIALLOC VIC 3195 | 9116184 | MC 09 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1273955 | 20190328UTD_01 | X arm fire failed, light rain rotten, AP issued and repairs complteted. LIS = 9116184
82 | 2019-03-19 | 12:24 | -38.3334 | 145.0192 | 675 DUNNS CREEK ROAD, DROMANA VIC 3936 | 1307507 | DMA15 | 22kV AC | Rural Short | - overhead conductor (bare; steel) | three phase | Started by any other thing forming part of or coming into contact with a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 1275359 | 20190321UTD_01 | Truck pulled down Hv O/H ex Tee off conductors on private property LIS#1307507.. Can isolate spur via L/L/C's for repair. Tip truck has brought down HV conductors, HV to be repaired, SUB VINEYARD BITTERN isolated, Winery left off supply whilst repairs undertaken, details passed onto Tony Sidney to arrange urgent repairs to HV. DUEA# 1515, photos obtained. Emailed details to Wayne Kelly, mgmt to sent whispir RWORKS# 1000702729. OHC repaired / replaced and ASR to VINEYARDS BITTERN @20:10
83 | 2019-03-25 | 15:18 | -38.3531 | 145.0249 | 31 BOWRINGS ROAD, RED HILL VIC 3937 | 1308142 | DMA13 | 22kV AC | Urban | - overhead conductor (bare; steel) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | HBRA only | 1 | Very High | 1 | 1 | 1277685 | 20190328UTD_04 | Also ref TBL 1277502. Fire start whisper sent. High wind brought down council tree in Bald Hills Nature Reserve fell on HV line sparking grass fire, fire report #6962, photos sent to NCC Dispatch. NSR, 2 subs off for duration of repairs, damage bw lis 1308142 - 43. HV conductors brought down/damaged and require repair/resag, PM notification 1000703555 Zinfra DAO org construction to atend tonight, operator will be req to restore after works compl, repairs made and supply restoredsee T/E#1277502. replaced a 40a BA on blue phase
84 | 2019-03-25 | 16:13 | -38.0603 | 145.1828 | 316 Worsley Rd, Bangholme VIC 3175, Australia | 623721 | DVY24 | 22kV AC | Rural Short | - insulator tie wires / connections | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1277714 | 20190416UTD_01 | Wire down Worsley Rd. Small fire 2mx2m fire brigade on site when crew arrived. Whisper sent fire start. Fire Report #03745. replaced 1m of 7/080 cu OHC, cause failed at the HV Tie.
85 | 2019-03-25 | 17:49 | -38.3283 | 144.9737 | 2 NEPEAN HIGHWAY, DROMANA VIC 3936 | 8825074 | DMA14 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1277811 | 20190328UTD_02 | Refer # 1277759 HV crossarm broken at LIS#8825074. Pole + xarm fire, fire report #02543. crew replaced pole lis#8825074.
86 | 2019-03-29 | 16:10 | -37.8911 | 145.1884 | 71 Madigan Dve, Glen Waverley | 612985 | MGE23 | 22kV AC | Urban | - overhead conductor (bare; all aluminium conductor) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | Very High | 1 | 0.2 | 1279282 | 20190429UTD_01 | Private Tree branch over HV in Madigan Cnr Waverly Rd & conductor damaged requiring repair. LIS 0612985
87 | 2019-03-30 | 7:41 | -37.9192 | 144.9905 | 12 Dendy St, Brighton | 1804866 | NB 35 | 11kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1279435 | 20190416UTD_05 | HV inter x-arm burnt off at arm strap at T-Off pole LIS 1804866 DENDY ST, cnr RAMSAY ST. Replaced Inter x-arm at T-off, Insulators replaced and conductor sleeved. Work completed under Access Permit. Fire Start- Fire Ignition report # 3095 not # 1000704184 Whispir sent
88 | 2019-03-31 | 18:18 | -38.3616 | 144.7807 | 2811 POINT NEPEAN ROAD, BLAIRGOWRIE VIC 3942 | 1302637 | STO23 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1279708 | 20190424UTD_01 | REF TO# 1279731 no fire strat - xarm burnt through via consistant tracking on the 22Kv - replaced HV inter x-arm. Replaced burnt out 400a krone box LIS# 1302637 PN# 1000704256
89 | 2019-04-03 | 2:58 | -37.9368 | 145.1428 | 24A Westall Rd, Westall | 629253 | SV 16 | 22kV AC | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1280721 | 20190424UTD_04 | Approx 8m squared grass fire caused by this fault, fire brigade attended and extinguished duty officer advised @ pole 0629253 - FHV spreaders required lis 0629253-0629254
90 | 2019-04-03 | 8:26 | -38.37 | 145.0072 | 241 Arthurs Seat Rd, Red Hill | 9863702 | DMA15 | 22kV AC | Rural Short | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any person, bird, reptile or other animal coming into contact with a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 1280756 | 20190416UTD_06 | LIS 9863702, opp 241 Arthurs Seat Rd, Crew insp pole, no damage to pole, grass fire at base of pole (approx 40m sq), fire caused by possum. Fire out when crew arrived/MFB on site. Fire report #02045.
91 | 2019-04-04 | 9:22 | -38.2189 | 145.2415 | Opposite 71 East Rd, Somerville | 3300039 | HGS33 | 22kV AC | Rural Short | - transformer (pole mounted) | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 1281179 | 20190429UTD_02 | Leaking oil from tx, and small grass fire started at base of pole, mfb have extinguished. 1m2 fire start. 5-6m2 of oil on ground. Fire repor# 02046 photo's taken and emailed.
92 | 2019-04-06 | 11:46 | -37.9111 | 145.0378 | 169 MCKINNON ROAD, MCKINNON VIC 3204 | 2326708 | BT 15 | Low voltage AC (<1kV) | Urban | - overhead service conductor (residential) | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1281852 | 20190520UTD_01 | Servicewire has caught fire at poa, supply is off, fire is out. business name is Som of a Burch, next to train station.replaced simpi crimp on active connection at POA, supply restored, overlaod LIS 2326708
93 | 2019-04-21 | 21:55 | -38.4777 | 144.9931 | 2080 BONEO ROAD, FLINDERS VIC 3929 | 1313131 | DMA23 | 22kV AC | Rural Short | - pole (wood) | three phase | Started in or originated from a distribution system | HBRA only | 1 | High | 0.5 | 0.5 | 1285605 | 20190506UTD_02 | Top of pole broken and fell down, pole top fire extinguished by CFA on site. center ph dressing down insulator tracking onto x-arm caused fire due to dirt on insulator and light rain at the time. LIS 1313131
94 | 2019-04-24 | 8:01 | -38.0028 | 145.2268 | 23-25 SOUTH GIPPSLAND HIGHWAY, DANDENONG SOUTH VIC 3175 | 8813163 | DN 02 | Low voltage AC (<1kV) | Urban | - connection box | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1285992 | 20190510UTD_01 | LIS 8813163 FOLCB burnt out/no fire present other than at FOLCB, MFB attended to extinguish. Crew repl FOLCB, repaired cables, rFire report 01484, Photos taken, to be sent to NCC Dispatch inbox
95 | 2019-04-26 | 7:39 | -38.3612 | 144.7816 | 2801 POINT NEPEAN ROAD, BLAIRGOWRIE VIC 3942 | 1302382 | STO23 | 22kV AC | Urban | - crossarm (wood) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1286296 | 20190510UTD_02 | lis# 1302382 - point nepean rd 1 pole east of st johns wood. opp 2801 Pt Nepean Rd Blairgowrie Crossarm Fire at strap bolt
96 | 2019-05-07 | 22:00 | -37.8659 | 145.0758 | 32 MUNRO AVENUE, ASHBURTON VIC 3147 | 8802981 | EM 05 | 11kV AC | Urban | - overhead conductor (bare; aluminium core steel reinforced) | three phase | Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system | LBRA only | 0.2 | High | 0.5 | 0.1 | 1289623 | 20190514UTD_01 | Tree on HV 28 Munro Av. Council tree o/s 32 Munro, white & red phase conductor repaired, Tree Branch caught fire within 1 metre of lines
97 | 2019-05-13 | 14:18 | -37.8682 | 145.06 | 1889 MALVERN ROAD, MALVERN EAST VIC 3145 | 2317286 | K 13 | Low voltage AC (<1kV) | Urban | - connector / termination | single phase | Started in or originated from a distribution system | LBRA only | 0.2 | Low-moderate | 0.2 | 0.04 | 1291106 | 20190523UTD_01 | lis: 2317286 ipc connection caught fire and needs to be replaced 1889 malvern rd malvern east
98 | 2019-05-17 | 20:40 | -38.3753 | 144.774 | 31 MUNRO STREET, BLAIRGOWRIE VIC 3942 | 1304717 | STO21 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | Low-moderate | 0.2 | 0.2 | 1292812 | 20190523UTD_02 | replaced 3 phase folcb at pole end severely melted so lokely fire starts
99 | 2019-06-03 | 18:57 | -38.369 | 144.7712 | 403 MELBOURNE ROAD, BLAIRGOWRIE VIC 3942 | 1316285 | STO21 | Low voltage AC (<1kV) | Rural Short | - lamps (major road) | single phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1298656 | 20190702UTD_01 | At LIS # 1316285 there was a melted street light. needs replacement. street light isolated at the mains. See new TO # 1298672
100 | 2019-06-06 | 9:21 | -37.9395 | 145.1313 | 29 ROSEBANK AVENUE, CLAYTON SOUTH VIC 3169 | 629670 | SV 33 | 22kV AC | Urban | - fuse (powder filled) | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1300030 | 20190704UTD_01 | crews have at rank rosebank - crew have replaced pff fuse at switch 810 caused by candling. LIS 0629670 Nomaly Feeder SV 33 but SV 20 on day of event
101 | 2019-06-06 | 16:42 | -38.3829 | 145.1703 | 46 SANDY POINT ROAD, SOMERS VIC 3927 | 1108920 | HGS21 | 22kV AC | Rural Short | - fuse (boric acid) | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1300276 | 20190702UTD_02 | Centre phase (White) BA fuse unit damaged. F/Path side (Red phase) BA fuse blown. MT0513 LIS (1108920) is open and LLC's lifted on East side (fuse units). BA fuse had candled.
102 | 2019-06-07 | 7:59 | -38.395 | 144.8035 | 30 COORAMINTA ROAD, RYE VIC 3941 | 1305535 | STO21 | Low voltage AC (<1kV) | Rural Short | - connection box | three phase | Started in or originated from a distribution system | HBRA only | 1 | No forecast | 0.1 | 0.1 | 1300406 | 20190617UTD_01 | replaced 3ph FMB at lis # 1305535, Fire Report #6728, NST tested and left on
103 | 2019-06-22 | 18:06 | -37.9257 | 145.0352 | 94-106 PATTERSON ROAD, BENTLEIGH VIC 3204 | 1803554 | MR 14 | 22kV AC | Urban | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1305265 | 20190704UTD_03 | Cause: HV UGC steel box termination bushing failed at HV CHP in Patterson Rd corner North Ave (LIS# 1803554) c/t CH7638 PATTERSON N120 RAILWAY. (identified as not Cabus)
104 | 2019-06-22 | 21:43 | -37.7742 | 145.1478 | 8 FARRER COURT, DONCASTER EAST VIC 3109 | 7063437 | DC 02 | Low voltage AC (<1kV) | Urban | - underground cable | three phase | Started in or originated from a distribution system | LBRA only | 0.2 | No forecast | 0.1 | 0.02 | 1305363 | 20190704UTD_02 | lis: 7063437 - Crew isolated west cct out of s/s WOODLEA-GAUDION so that u/g crew can replace pillar out front off #8-#9 - Pillar Fire
Contents
ADD MORE ROWS
DELETE EXTRANEOUS ROWS

## 3. Systems and Audit
United Energy
F-factor data reporting
2018/19
Instructions:
United Energy must provide:
Table 4 - Information or reporting systems
(1) Name of any IT system used to collect fire start data or fault event data - i.e. SCADA system, or fault reporting system
(2) Whether the fire recording or fault recording process has been audited or complies with a relevant Australian or industry standard - Yes or No
(3) List any relevant Australian or industry standards that the fire recording or fault recording process complies with
(4) Whether the data entered into or removed from the IT system has been audited - Yes or No
Table 4: Information or reporting systems
Information or reporting systems | Name | System Audited | Relevant Standards
System 1 | Distribution Management System (DMS) | Yes | None
System 2 | GIS | Yes | None
System 3 | OSIRIS | Yes | None
System 4
System 5
System 6
System 7
System 8
The SGSPAA Internal Audit function undertakes a programme of work in accordance with the SGSPAA Group Internal Audit Plan. This internal audit activity covers elements of the systems and process used for capturing, recording and maintaining fire start data.
Contents