{"text_format":"1","workbook":"xlsx","n_sheets":5,"sheets":["Contents","Cover","1. F-Factor summary","2. Individual fire start info","3. Systems and Audit"],"not_rendered":{"charts":0,"images":2,"macros":1,"external_links":2,"defined_names":97,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Contents","index":0,"n_rows":12,"n_cols":6,"rows_kept":12,"cut":false,"hidden":false,"merged":[[8,2,9,3],[2,1,2,10],[4,1,4,10]]}
[" "]
[]
[null,"Electricity Distribution Network Service Provider\nF-factor Reporting Template"]
[]
[null,"Table of contents"]
[]
[]
[null,null,"Cover sheet",null,null,"2. Fire start report"]
[]
[]
[]
[null,null,"1. F-factor summary",null,null,"3. Systems and Audit"]

{"sheet":"Cover","index":1,"n_rows":49,"n_cols":7,"rows_kept":49,"cut":false,"hidden":false,"merged":[[31,3,31,5],[14,1,14,8],[16,1,16,8],[17,1,17,8],[21,1,21,8],[19,1,19,8],[10,1,11,8],[13,1,13,8],[42,2,42,3],[42,4,42,7],[38,2,38,3],[38,4,38,7],[41,2,41,3],[41,4,41,7],[37,2,37,3],[37,4,37,7],[32,3,32,8],[30,3,30,8],[15,1,15,8],[26,3,26,8],[28,3,28,8],[26,1,26,2]]}
[]
[]
[]
[]
[]
[]
[]
[null,"Distribution Network Service Provider"]
[null,"Fire start report"]
[]
[null,"This template is to be used by a DNSP to provide a fire start report to the AER in accordance with section 5 of the F-factor Order in Council.  "]
[]
[]
[null,"Colour coding of input sheets:"]
[null,"Dark blue = AER headings"]
[null,"Grey = AER instructions"]
[null,"Yellow = Input cells"]
[null,"Light orange = Automatically-generated cells"]
[]
[null,"Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so."]
[null,"The cells and structure of the spreadsheet is locked to prevent inadvertent interference with the automated settings."]
[null,"All dollar amounts are to be unrounded, and in nominal terms."]
[]
[]
[]
[]
[null,"DNSP:",null,"United Energy"]
[]
[null,"DNSP - trading name:",null,"United Energy Distribution Pty Ltd"]
[]
[null,"DNSP - Australian business number: ",null,"70 064 651 029"]
[]
[null,"Reporting year:",null,"2017/18"]
[]
[]
[]
[]
[null,"Business address","Address",null,"43 - 45 Centreway"]
[null,null,"Suburb",null,"Mt Waverley"]
[null,null,null,"State","Victoria","Postcode",3149]
[]
[null,"Postal address","Address",null,"P.O Box 449"]
[null,null,"Suburb",null,"Mt Waverley"]
[null,null,null,"State","Victoria","Postcode",3149]
[]
[]
[null,"Contact name/s","Mark de Villiers"]
[null,"Contact phone/s",396834907]
[null,"Contact email address/s","mdevilliers@powercor.com.au"]

{"sheet":"1. F-Factor summary","index":2,"n_rows":14,"n_cols":15,"rows_kept":14,"cut":false,"hidden":false,"merged":[[12,2,12,3],[13,2,13,3],[6,2,6,3],[7,2,7,3],[8,2,8,3],[9,2,9,3],[10,2,10,3],[5,1,5,2],[3,6,3,8],[4,6,4,8],[5,6,5,8],[11,2,11,3]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"United Energy"},"IRU target:",{"$f":"IF(SUM(K6:O6)=0,\"\",SUM(K6:O6))","v":22.3},null,null,null,null,null,null,"AusNet Services","CitiPower","Jemena","Powercor","United Energy"]
[null,"F-factor data reporting","IRU amount:",{"$f":"IF(SUM('2. Individual fire start info'!S38:S1914)=0,\"\",SUM('2. Individual fire start info'!S38:S1914))","v":21.86000000000001},null,null,null,null,null,"2016/17",247.7,3.4,9.6999999999999993,468,22.3]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2017/18"},"Revenue adjustment:",{"$f":"IF(OR(D1=\"\",D2=\"\"),\"\",15000*(D1-D2))","v":6599.999999999859},null,null,null,null,null,"2017/18",247.7,3.4,9.6999999999999993,468,22.3]
[null,null,null,null,null,null,null,null,null,"2018/19",247.7,3.4,9.6999999999999993,468,22.3]
[null,"Table 2: Summary of total fire starts by F factor Order definition",null,null,null,null,null,null,null,"2019/20",221.1,3.4,9.6999999999999993,412.8,22.3]
[null,"This is a summary of data in worksheet \"2. Fire Start Report\"",null,null,null,null,null,null,null,null,{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>K1),\"\",LOOKUP($B3,$J2:$J5,K2:K5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>L1),\"\",LOOKUP($B3,$J2:$J5,L2:L5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>M1),\"\",LOOKUP($B3,$J2:$J5,M2:M5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>N1),\"\",LOOKUP($B3,$J2:$J5,N2:N5))","v":""},{"$f":"IF(OR($B3=\"[Year]\",$B1=\"[DNSP Name]\",$B1<>O1),\"\",LOOKUP($B3,$J2:$J5,O2:O5))","v":22.3}]
[null,"Kind of Fire Start by definition of fire start under clause 5 of F-factor Order","Total fires by cause"]
[null,"Started in or originated from a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1914,'1. F-Factor summary'!$B8)","v":86}]
[null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1914,'1. F-Factor summary'!$B9)","v":19}]
[null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1914,'1. F-Factor summary'!$B10)","v":8}]
[null,"Started by lightning striking a distribution system or a part of a distribution system ",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1914,'1. F-Factor summary'!$B11)","v":0}]
[null,"Started by any other thing forming part of or coming into contact with a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1914,'1. F-Factor summary'!$B12)","v":1}]
[null,"Otherwise started by a distribution system",{"$f":"COUNTIF('2. Individual fire start info'!$N$38:$N$1914,'1. F-Factor summary'!$B13)","v":0}]
[null,"Total",{"$f":"SUM(C8:C13)","v":114}]

{"sheet":"2. Individual fire start info","index":3,"n_rows":187,"n_cols":25,"rows_kept":187,"cut":false,"hidden":false,"merged":[[3,22,3,24],[4,22,4,24],[5,22,5,24],[7,1,7,21],[11,1,11,2],[9,1,9,21],[13,1,13,11],[22,1,22,21],[24,1,24,21],[14,1,14,20],[15,1,15,18],[16,1,16,18],[18,1,18,18],[21,1,21,18],[19,1,19,18],[23,1,23,18],[20,1,20,18],[17,1,17,18],[25,1,25,18],[27,1,27,20],[26,1,26,21],[35,19,35,21],[33,1,33,4],[35,2,35,10],[28,1,28,18],[29,1,29,18],[35,11,35,13],[35,14,35,17]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"United Energy"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2017/18"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"\"Enter into this worksheet fire start data, from any IT system, which have been recorded by \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\". Note that fire starts must be in accordance with the definition of a fire start in the Order In Council.\"","v":"Enter into this worksheet fire start data, from any IT system, which have been recorded by United Energy. Note that fire starts must be in accordance with the definition of a fire start in the Order In Council."}]
[]
[null,"\"Fire\" should be interpreted using its common meaning and can be defined as a process in which substances combine chemically with oxygen from the air and typically give out bright light, heat and smoke. A fire should be recorded where there is evidence of smoking, charring, scorching, burning or any other evidence that a fire had occurred.  "]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"United Energy must provide:"}]
[]
[null,"Table 3 - Individual Fire Starts"]
[null,"   (1) Date - dd/mm/yyyy"]
[null,"   (2) Time - if known, the 24-hour time of the fire start hh:mm"]
[null,"   (3) Latitude and longitude of the fire start as decimal coordinates"]
[null,"   (4) Address of the property on which the incident occurred or closest to the incident"]
[null,"   (5) Asset number for the asset nearest the fire start"]
[null,{"$f":"\"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the \"&B1&\" network\"","v":"   (6) Feeder ID for the polyphase overhead line or underground cable nearest the fire start in the United Energy network"}]
[null,"   (7) Voltage on the line in which the fire start occurred (note: this may not be the nearest polyphase overhead line)"]
[null,"   (8) Network categorisation - CBD, Urban, Rural Long or Rural Short"]
[null,"   (9) Asset type of primary asset causing fire in accordance with OSIRIS asset categories"]
[null,"   (10) Where the asset involved in the fire is a transformer or an overhead or underground line, provide the phase, or phases, of the line or transformer"]
[null,"   (11) Kind of fire start in accordance with categories specified in Clause 5 of the F-factor Order-In-Council"]
[null,"   (12) Identify the location of the fire start in accordance with the categories specified in Clause 11(b) of the F-factor Order-In-Council"]
[null,"   (13) Provide the BOM fire danger rating applicable at the time of the fire start (data is available on the EM-COP website)"]
[null,{"$f":"\"   (14) \"&IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)&\"'s record number for the incident\"","v":"   (14) United Energy's record number for the incident"}]
[null,"   (15) ESV's OSIRIS reference number for the incident"]
[null,"   (16) Free text description of the fault containing relevant comments from field reports "]
[]
[]
[]
[null,"Table 2: Individual Fire Starts"]
[]
[null,"Number","Fire starts",null,null,null,null,null,null,null,null,"Fire Type",null,null,"Risk Factors",null,null,null,"IRU \namount","Additional information"]
[null,null,"Date 1","Time 2","Latitude 3","Longitude 3","Address of incident 4","ID of \nnearest \nasset 5","ID of nearest \npolyphase \nline 6","Voltage of line in which \nfire start \noccurred 7","Network categorisation 8","Type of primary asset \ninvolved in fire start 9","Phase(s) of \nline or \ntransformer 10","Kind of fire start as per Clause 5\nof F-factor Order-In-Council 11","Location \narea 12","Location\nmultiplier","Fire \ndanger \nrating 13","Danger multiplier","Product of multipliers","DNSP record number 14","OSIRIS \n(ESV) reference \nnumber 15","Fault \ndescription 16"]
[{"$f":"COUNTA(C38:O38,Q38,T38:V38)","v":17},1,"2017-07-05","17:39:00",-38.253405549999997,145.0308708,"31 CLARKES AVENUE MOUNT MARTHA",1102020,"MTN31","Low voltage AC (<1kV)","Urban"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O38=\"\",\"\",IF(O38=\"LBRA only\",0.2,IF(O38=\"HBRA only\",1,IF(O38=\"within electric line construction area\",19.8,IF(O38=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"No forecast",{"$f":"IF(Q38=\"\",\"\",IF(Q38=\"No forecast\",0.1,IF(Q38=\"Low-moderate\",0.2,IF(Q38=\"High\",0.5,IF(Q38=\"Very high\",1,IF(Q38=\"Severe\",2,IF(Q38=\"Extreme\",3.5,5)))))))","v":0.1},{"$f":"IF(OR(P38=\"\",R38=\"\"),\"\",IF(AND(O38=\"within electric line construction area\",Q38=\"No forecast\"),1,P38*R38))","v":2.0000000000000004E-2},5261,"20170724UTD_02","Fault crew arrived on site and found JB caught fire and damaged LV ABC Service connections - and 2 x bays of LV ABC @ lis 1102020 ",null,null,"Overhead conductors"]
[17,2,"2017-07-06","04:58:03",-38.176525120000001,145.08081440000001,"19 ROSSERDALE CRESCENT MOUNT ELIZA",3313863,"FSH33","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5277,"20170809UTD_01","Fire brigade advised pole # L is 3313863 - LV FMB connection on fire. Crew repl a b/out 3 ph fmb aup the pole end.",null,null," - overhead conductor (bare; aluminium core steel reinforced)"]
[17,3,"2017-07-08","17:38:26",-38.331319649999998,144.71454170000001,"298 HOTHAM ROAD PORTSEA",1307139,"STO13","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5278,"20170809UTD_02","Cnr franklin & Hotham, lis # 1307139 replaced 3ph FMB and also replaced neutral LV pin and insulator, did ignite LV xarm but is ok, Fire Report # 02284",null,null," - overhead conductor (bare; all aluminium conductor)"]
[17,4,"2017-08-11","03:12:00",-37.924268329999997,145.0439398,"29B LONDON STREET BENTLEIGH",1802621,"BT 04","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5281,"20170811UTD_02","sparking pole, cause possum as per MFB, - fire report completed out by crew- fire @ pole lis # 1802621 and crew reported when plastic came down caused approx 6 inch diameter circle burnt mark on the grass",null,null," - overhead conductor (bare; copper)"]
[17,5,"2017-08-19","11:25:49",-38.062838249999999,145.11785040000001,"16 WILLIAMS GROVE BONBEACH",3303133,"CRM22","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5305,"20170912UTD_01","Replaced burnt out 3phs pole box at LIS #3303133 - due to birds nest inside - supply feeding unit 1 and 2 /#13",null,null," - overhead conductor (bare; steel)"]
[17,6,"2017-08-21","21:27:34",-37.872905699999997,145.205375,"229 BALACLAVA ROAD, CAULFIELD NORTH VIC 3161",2334727,"EL 09","Low voltage AC (<1kV)","Urban"," - luminaries (major road)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5287,"20170831UTD_01","Disconnected 250w HP sodium PE street light head on LIS # 2334727 PWC Pole closest UE Pole 2301427 - head had been on fire but was extinguished by MFB - caused by birds nest",null,null," - overhead conductor (ABC)"]
[17,7,"2017-08-24","06:07:42",-38.023741919999999,145.19246939999999,"80 ORDISH ROAD DANDENONG SOUTH",3425946,"DSH33","22kV AC","Urban"," - transformer (pole mounted)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5306,"20170912UTD_02","Removed large bird nest from top of tx. cleaned HV transformer bushings. Installed new centre phs bushing covers. LIS# 3425946.",null,null," - overhead conductor (covered uninsulated)"]
[17,8,"2017-08-31","19:29:38",-37.850607500000002,145.10181040000001,"114 BURWOOD HIGHWAY BURWOOD",7050090,"BW 22","11kV AC","Urban"," - capacity balancing units","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5302,"20170908UTD_01","LIS 7050090, CAP BURWOOD-MILICENT has blown up, follow up required Fri 1/9 to have cap bank replaced. Crew to advised depot.",null,null," - overhead conductor (insulated)"]
[17,9,"2017-09-28","13:37:14",-38.354684329999998,144.7596427,"8 TADJI STREET SORRENTO",1306299,"STO13","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5314,"20171003UTD_03","Fire Start @  lis # 1306299 LV ABC Inter Pole with a 3 phase  junction box located @ 6 Tadji St Sorrento Junction Box melted and caused a fire on top of the pole - debris on ground but no grass fire was involved",null,null,"Service lines"]
[17,10,"2017-10-01","19:35:11",-37.880638609999998,144.98702019999999,"130 MITFORD STREET ELWOOD",2332245,"EW 01","Low voltage AC (<1kV)","Urban"," - fuse (any other type)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5318,"20171012UTD_02","replaced 100a fuse box, burnt out. And 100 a fuse. Tested and left on, CIA LIS# 2332245",null,null," - overhead service conductor (residential)"]
[17,11,"2017-10-05","10:42:55",-38.223760509999998,145.24957910000001,"1 SOUTH BOUNDARY ROAD SOMERVILLE",9498509,"HGS33","22kV AC","Rural Short"," - guy wire","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,5317,"20171012UTD_01","Appears Guy rod pulled out of log and guy wire contacted LA at MEALY STH BOUNDARY S/S LIS#9498509. Confirmed pole fire & CFA called. Fire Report # 04448 emailed  photos to NCC",null,null," - overhead service conductor (commercial / industrial)"]
[17,12,"2017-10-06","04:26:11",-38.170862249999999,145.10584080000001,"22 HUMPHRIES ROAD MOUNT ELIZA",3314196,"FSH13","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5330,"20171103UTD_01","Cons crew on the way to replace burnt hv x-arm...poly/plastic insulators, LIS - 3314196 HV strain arm replaced cut off top of pole, chse up with James Q & Rod L for fire start report.",null,null," - overhead service conductor (subdivision / construction)"]
[17,13,"2017-10-19","02:49:19",-37.977097299999997,145.0666258,"56 NEPEAN HIGHWAY, MENTONE",1822129,"M  23","11kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5322,"20171012UTD_02","HV O/Head Wph down onto LV X-Arm Corner of Nepean Hwy and Flinders St. Maybe a HV sleeve has failed and let go.  Sparks from cond started small fire in garden bed at BP petrol station, Fire Start report - 00344. ",null,null," - overhead service conductor (other)"]
[17,14,"2017-10-19","11:01:13",-38.037869129999997,145.19904360000001,"97-105 BANGHOLME ROAD, BANGHOLME",623176,"DVY34","22kV AC","Urban"," - fuse (boric acid)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5323,"20171012UTD_03","Fuse candled. white phase on Cap  BANGHOLME HAMMOND. Vaccum switch damaged.  Cap  BANGHOLME HAMMOND isolated . LIS#3441333. fire ignition report # 00199 - no fire on grass",null,null," - underground service cable (residential)"]
[17,15,"2017-11-07","11:04:19",-37.899190830000002,145.17239979999999,"28 COOPER AVENUE GLEN WAVERLEY",608953,"MGE34","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5333,"20171108UTD_01","hv/lv #1258 strain pole needs to be replaced ZNX Duty Officer Peter Marsh advd. W.Highmore doing fire report fire report No3007 ",null,null," - underground service cable (commercial / industrial)"]
[17,16,"2017-11-07","12:11:00",-37.901822770000003,145.17463670000001,"26 ENTALLY DRIVE WHEELERS HILL",607733,"MGE34","22kV AC","Urban"," - fuse (powder filled)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5334,"20171108UTD_02","Whisper sent for fire start, candling fuse. replaced 15 B ph PFF at lis 0607733 no cause identified at sub. no wires down as reported by mfb. fire report No3008 per W Highmore",null,null," - underground service cable (subdivision / construction)"]
[17,17,"2017-11-23","02:48:34",-37.818552099999998,145.11481019999999,"434 ELGAR ROAD BOX HILL",7024750,"BH 23","22kV AC","Urban"," - underground cable","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,{"$f":"IF(OR(P54=\"\",R54=\"\"),\"\",IF(AND(O54=\"within electric line construction area\",Q54=\"No forecast\"),1,P54*R54))","v":0.1},5351,"20171204UTD_03","HVUG fault from lis 7024750 cnr Elgar & Hopetoun Pde HV Blue phase on the deck in Kent st lis..7037195. Fire report#3870.  Possibly the fault current for cause of wire down.",null,null," - underground service cable (other)"]
[17,18,"2017-11-24","06:53:32",-38.368365660000002,144.87172609999999,"2 BROADWAY  CAPEL SOUND",1300184,"RBD23","22kV AC","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,5353,"20171206UTD_01","Copper to Al Ampact connection failed at LIS#1300184 strain pole Elizabeth cnr of Broadway, the preform connection at same location has failed and this let the HV conductor fall. ...HV conductor fell alive onto ground,   MFB reported flames 1-2 metres high from the failing ampact connection prior to hv conductor falling to ground.  ",null,null,"Underground cables"]
[17,19,"2017-12-02","23:26:04",-37.898463499999998,144.9949536,"60 NORTH ROAD BRIGHTON",2304847,"NB 22","11kV AC","Urban"," - crossarm (wood)","three phase","Started by any other thing forming part of or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5358,"20171211UTD_02","Truck hit pole and broke HV Tie which fell onto crossarm causing a fire - LIS 2304847",null,null," - underground cable"]
[17,20,"2017-12-06","12:44:11",-37.936835879999997,145.0026943,"452A HAMPTON STREET HAMPTON",1818498,"SR 23","Low voltage AC (<1kV)","Urban"," - luminaries (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5389,"20180109UTD_03","HPS 250 Watt Lantern had burnt out - Lis 1818498",null,null," - underground communications cable"]
[17,21,"2017-12-11","09:13:00",-37.907852779999999,145.16060820000001,"594 SPRINGVALE ROAD, WHEELERS HILL",8805524,"MGE21","Low voltage AC (<1kV)","Urban"," - luminaries (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5390,"20180109UTD_04","HPS 250 Watt Lantern had burnt out - Lis 8805524",null,null,"Poles"]
[17,22,"2017-12-13","17:55:22",-38.031210870000002,145.1042626,"188 NEPEAN HIGHWAY ASPENDALE",3302395,"MC 01","Low voltage AC (<1kV)","Urban"," - switch (disconnector/isolator)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,5369,"20171218UTD_04","During hot conditions a LV Krone box failed and caught fire - LIS 3302395",null,null," - pole (concrete)"]
[17,23,"2017-12-14","22:34:26",-37.909946890000001,145.10213469999999,"8B RAILWAY AV OAKLEIGH",2325346,"OE 04","11kV AC","Urban"," - connector / termination","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5373,"20171215UTD_01","Fire start adjacent to \"Railway P1 West-  Warner\"  S/Stn.  The Red phase P/F Fuse unit failed on the top contact of clamp and fuse fell to the ground igniting a small 3Sq/m grass fire - LIS 2325346",null,null," - pole (steel)"]
[17,24,"2017-12-17","20:58:17",-38.182984060000003,145.07573959999999,"14 KOORNALLA CRESCENT MOUNT ELIZA",3314469,"MTN22","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5387,"20180109UTD_01","Although fire was out when crew arrived the first call comments state flames were visable from a 3 phase FMB - Lis 3314469",null,null," - pole (wood)"]
[17,25,"2017-12-20","22:35:24",-37.959178659999999,145.17856979999999,"44 CALLANDER ROAD NOBLE PARK",633975,"NP 16","22kV AC","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5386,"20180108UTD_04","Capbank CALLANDER JASON LLC flex at top of fuse unit is failing, causing arcing, no fire at the time of linsmans arrival however 1st call comments idicate flames were witnessed.  LIS  0633975",null,null,"Crossarms"]
[17,26,"2017-12-22","04:21:11",-38.348867579999997,144.94286679999999,"13 BAYVIEW ROAD MCCRAE",8825718,"RBD13","Low voltage AC (<1kV)","Urban"," - luminaries (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,5375,"20171222UTD_01","a 150W Lantern on pole lis-8825718 Ccaught fire in Bayview Rd, McCrae",null,null," - crossarm (wood)"]
[17,27,"2017-12-29","20:18:32",-38.010770000000001,145.22143600000001,"78-80 WILLIAMS ROAD, DANDENONG SOUTH",9575750,"DSH22","Low voltage AC (<1kV)","Urban"," - LV pillar","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5379,"20180102UTD_01","An LV Distribution cabinet caught fire outside 78 Williams Rd, Dandenong - Closest LIS # 9575750",null,null," - crossarm (steel)"]
[17,28,"2018-01-04","00:22:50",-37.965473410000001,145.17369350000001,"6 DOUGLAS STREET NOBLE PARK",9821648,"NP 25","Low voltage AC (<1kV)","Urban"," - luminaries (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5381,"20180104UTD_01","Pole No. 9821648 s/l head melted & wiring was burnt - has been isolated in the pit - crew to return  thursday night to repair. light repaired, rewired & head replaced",null,null," - crossarm (other)"]
[17,29,"2018-01-05","16:53:33",-37.95283027,145.1536208,"3 UNION GROVE SPRINGVALE",613560,"SS 13","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,"5383","20180108UTD_01","on at 1900 repl a 2 core service n/screen b/out at clamp. Started small fire in front yard to number 3. LIS # 13560 fire ignition report # 02524. Whispir sent",null,null,"Overhead assets"]
[17,30,"2018-01-07","20:30:53",-38.036416150000001,145.1061832,"2A-2B DUDLEY GROVE, EDITHVALE",3302798,"MC 01","Low voltage AC (<1kV)","Urban"," - connection box","two phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5385,"20180108UTD_03","two phase fmb box on the pole had b/out and on fire. some grass (small) fire. It fed an u/ground service which fed 2a and 2 b Denman. crew replaced box. NST and on supply. Fire ignition report num is 00349. Whispir sent",null,null," - capacity balancing units"]
[17,31,"2018-01-08","12:13:47",-37.90876239,145.0612266,"325 EAST BOUNDARY ROAD BENTLEIGH EAST",2333019,"OR 24","66kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5391,"20180109UTD_05","Tree is near 66 HTN to NB line. council tree dropped brach which caught fire is clear now but needs to be cut back ideally this week, shut down will be required, LIS - 2333019 ",null,null," - connector / termination"]
[17,32,"2018-01-12","03:58:34",-38.38687608,144.93125169999999,"69 CARRATHOOL AVENUE ROSEBUD",1311457,"RBD12","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,5396,"20180112UTD_04","EDO fuse tube candled, replaced 10a fuse and tube on the white phase, ncf. fire report #6623",null,null," - dropper / bridge"]
[17,33,"2018-01-18","00:26:55",-37.910216800000001,145.09192469999999,"1177 NORTH ROAD OAKLEIGH",2326221,"OE 04","11kV AC","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,5403,"20180122UTD_02","An cu/al ampact connection failure resulting in the 11kV conductor falling to the ground and thus scorching the grass underneath",null,null," - guy wire"]
[17,34,"2018-01-18","17:35:33",-37.969485110000001,145.18625080000001,"74 CHANDLER ROAD NOBLE PARK",619054,"NP 36","Low voltage AC (<1kV)","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,5400,"20180122UTD_01","LIS - 0619054  crew  replcd burnt off red phase lv lead conn to tx lv isolator completed fire ignition report - grass had been burnt  approx 1 cubic meter   crew have taken photos of grass and pole to be passed onto chris willey",null,null," - insulator tie wires / connections"]
[17,35,"2018-01-18","18:24:17",-38.241720829999998,145.04726160000001,"253 DUNNS ROAD MORNINGTON",1100188,"MTN31","Low voltage AC (<1kV)","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,5401,"20180122UTD_03","burnt out connection at sub IKARA DUNNS blue phs, remade connection. LIS#1100188 - base of pole had burn marks Fire report 02285 Cause unknown, grass fire 4x2 mtrs.",null,null," - insulators"]
[17,36,"2018-01-19","14:56:37",-37.823786849999998,145.1574335,"45 WELLINGTON AVENUE BLACKBURN",7037553,"NW 21","22kV AC","Urban"," - overhead conductor (bare; copper)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Severe",2,0.4,"5404","20180122UTD_04","Original Fault was private tree branch across w/b HV phases at #6 Lake Rd north east of LIS#7029960. This causes many secondary faults, onne of which resulted in HV clashing which ignited a small grass fire",null,null," - tower"]
[17,37,"2018-01-22","15:27:10",-38.009514189999997,145.216069,"90A DANDENONG-FRANKSTON RD DANDENONG SOUTH",635472,"DSH32","Low voltage AC (<1kV)","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,5405,"20180123UTD_01","W phase lv had clashed with the electrolis cable - crew installed some stinger insualtion onto the conductors & filled out fire report# 05629  less than 1 square meter of grass burnt.",null,null," - traction lines"]
[17,38,"2018-01-22","17:35:17",-37.909338669999997,145.1957907,"13 PALMERSTON CRESCENT WHEELERS HILL",8808475,"MGE12","Low voltage AC (<1kV)","Urban"," - LV pillar","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,{"$f":"IF(OR(P75=\"\",R75=\"\"),\"\",IF(AND(O75=\"within electric line construction area\",Q75=\"No forecast\"),1,P75*R75))","v":0.1},5406,"20180123UTD_02","Refer to t/o: 1140334 - u/g pillar @14 Palmerston St blew up - fire report #: 1140338 - (fire burnt customers knee high plant to the ground - u/g crew on site replacing pillar - ",null,null,"Underground assets"]
[{"$f":"COUNTA(C76:O76,Q76,T76:V76)","v":17},39,"2018-01-25","12:43:55",-37.780930400000003,145.12340739999999,"71 WILLIAMSONS ROAD DONCASTER",7055546,"WD 15","11kV AC","Urban"," - capacity balancing units","three phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O76=\"\",\"\",IF(O76=\"LBRA only\",0.2,IF(O76=\"HBRA only\",1,IF(O76=\"within electric line construction area\",19.8,IF(O76=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"High",{"$f":"IF(Q76=\"\",\"\",IF(Q76=\"No forecast\",0.1,IF(Q76=\"Low-moderate\",0.2,IF(Q76=\"High\",0.5,IF(Q76=\"Very high\",1,IF(Q76=\"Severe\",2,IF(Q76=\"Extreme\",3.5,5)))))))","v":0.5},0.1,5421,"20180205UTD_01","Isolated a damaged capacitor bank as per the control room. The Cap Back flashed over and caused a small fire up the pole that self extinguished",null,null," - LV pillar"]
[17,40,"2018-01-25","18:00:14",-37.994515110000002,145.20796809999999,"13 DALGETY STREET DANDENONG",8813035,"KBH32","22kV AC","Urban"," - transformer (pole mounted)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,5410,"20180129UTD_01","Transformer blown up and fire on the pole crew arranging // and isolating supply. 200kva transformer blown up. leaking out of LV bushings. Small fire on the ground. ",null,null," - services pit"]
[17,41,"2018-01-26","04:27:19",-37.94049029,145.18770380000001,"46 ASCOT DRIVE, NOBLE PARK NORTH",8809817,"LD 03","Low voltage AC (<1kV)","Urban"," - LV pillar","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,5418,"20180201UTD_03","UG on site replacing damaged pillar, crew attending to isolated bonded LV ccts &  issue permit. Crew reattended/cancelled permit & restored supply at 1515",null,null,"Transformers"]
[17,42,"2018-01-27","16:08:20",-38.367773800000002,144.8929704,"221 EASTBOURNE ROAD ROSEBUD",1309970,"RBD24","22kV AC","Urban"," - surge diverter","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,5412,"20180129UTD_03","Refer TE1141571, Crow at RDB24 fdr exit CHP RB0184 caused a small grass fire. Fire report#01687",null,null," - transformer (pole mounted)"]
[17,43,"2018-01-28","10:37:00",-38.159258319999999,145.10923990000001,"39A BRUARONG CRESCENT FRANKSTON SOUTH",3315978,"FSH13","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,5422,"20180205UTD_02","400a fuses in krone box feeding ABC, crew looking for //'s. Burnt out krone box on pole. No fire on the ground. Fire incident report #02805 . Replaced the north circuit krone box and 3 x 315A din fuses.  LIS# 3315978.",null,null," - transformer (kiosk mounted)"]
[17,44,"2018-01-28","19:05:00",-37.782738899999998,145.1541665,"3 DAWS ROAD DONCASTER EAST",7063276,"DC 03","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,"5423","20180205UTD_03","Replaced red and white phs south cct 315amp din fuses - cause: burnt out u/g junction box on lis: 7063276 - Possibly due to overload",null,null," - transformer (ground outdoor mounted)"]
[17,45,"2018-01-30","08:40:53",-37.830571339999999,145.1871289,"125 ROOKS RD NUNAWADING",7031360,"RWT24","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,5424,"20180205UTD_04","Construction crew on site replacing x-arm, on pole #7031360. xarm replaced. no interuption.",null,null," - transformer (indoor chamber mounted)"]
[17,46,"2018-02-10","00:05:00",-37.821614279999999,145.15765379999999,"4 GLEN EBOR AVENUE BLACKBURN",7033760,"NW 21","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,5459,"20180308UTD_04","On arrival a possum was on the top of the LV krone box and tracking accross, s/stn isolated lv/hv to remove possu, dmage to krone box... #12 Glen Ebor Ave.. LIS= 7033760",null,null," - transformer (any other type)"]
[17,47,"2018-02-12","03:28:17",-37.756405010000002,145.12487519999999,"3 SWILK STREET TEMPLESTOWE",7057869,"BU 14","11kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5430,"20180219UTD_01","Person reported loud bang off pole  12 swilks st - which meets foot st. Possum caused flashover on LIS # 7057869, no apparent damage. Small fire when fell to the ground , Fire report#03169 ",null,null," - measurement transformer (current transformer)"]
[17,48,"2018-02-13","17:36:59",-37.885280109999997,145.02524320000001,"37 MASTERS STREET CAULFIELD",2301975,"CFD13","11kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,5439,"20180223UTD_03","Customer indicated pole on fire - A HV bridge in master 1n pine lis 2301978, indicated a bird had caused a flashover which showed burn marks on crossarm",null,null," - measurement transformer (voltage transformer)"]
[17,49,"2018-02-14","08:59:15",-37.887210660000001,145.02488120000001,"865 GLEN HUNTLY ROAD CAULFIELD",2306516,"CFD13","11kV AC","Urban"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,5440,"20180308UTD_02","As per MFB-- Flames coming from powe lines from a blown HV Bridge LIS = 2306515",null,null," - measurement transformer (capacitive voltage transformer)"]
[17,50,"2018-02-14","09:51:14",-38.306943150000002,145.03019810000001,"231 NEPEAN HIGHWAY DROMANA",1103402,"DMA24","22kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Very high",1,1,5440,"20180226UTD_01","A Tree has fallen on to HV, caused grass fire at lis # 1103402, no damage to UE assets, Fire Report #6723",null,null,"Fuses and switchgear"]
[17,51,"2018-02-14","19:07:22",-37.788850289999999,145.19045460000001,"49 GARDEN ROAD DONVALE",7067244,"NW 13","22kV AC","Urban"," - overhead conductor (ABC)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,5431,"20180216UTD_01","Old Generation HV ABC failure in Garden Rd between LIS#7067244 & LIS#7067243, lying on ground, fire start approx 3m2, report #03170.",null,null," - fuse (boric acid)"]
[17,52,"2018-02-16","04:02:00",-38.090364950000001,145.1253596,"39 NEPEAN HIGHWAY SEAFORD",3318167,"CRM33","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5434,"20180219UTD_03","LIS # 3318167 fire is out but xarm is burnt. Needs replacement. ",null,null," - fuse (EDO fuse)"]
[17,53,"2018-02-16","23:02:52",-37.965490000000003,145.17343099999999,"6 DOUGLAS STREET NOBLE PARK",9821649,"NP 25","Low voltage AC (<1kV)","Urban"," - luminaries (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5433,"20180219UTD_02","There is a damaged street light head 250w HPS has been disconnected at the base of the pole. Crew to return AH during week to replace the head. TO1153661 raised for ace to repalce head LIS 9821649",null,null," - fuse (Fault Tamer)"]
[17,54,"2018-02-19","18:01:42",-37.9846012,145.0319959,"9 GARETH AVENUE BEAUMARIS",1811309,"BR 04","Low voltage AC (<1kV)","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,5456,"20180308UTD_01","Per mfb - tree has come down brought wires down & possibly tree was on fire - LIS = 1811309",null,null," - fuse (powder filled)"]
[17,55,"2018-02-21","11:55:36",-37.837054879999997,145.11798289999999,"12 LYNDOCH STREET BOX HILL SOUTH",7037421,"BH 21","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,5441,"20180226UTD_02","Contact with HV during high winds of HV outside 4 Lyndoch, some branches have burnt/appears tree has sustained fire damage.   LIS 7037421",null,null," - fuse (any other type)"]
[17,56,"2018-02-22","19:55:00",-38.131912900000003,145.2221538,"55 LYPPARDS ROAD LANGWARRIN",3312536,"LWN21","Low voltage AC (<1kV)","Rural Short"," - transformer (pole mounted)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,5445,"20180227UTD_01","LV Bushing on Tx melted Small Grass fire .  Tx replaced under A/P   Fire report# 6821    LIS#3312536 , ",null,null," - circuit breaker"]
[17,57,"2018-02-26","14:06:31",-38.404347629999997,144.93644900000001,"74 HYSLOPS ROAD BONEO",1308857,"RBD12","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","HBRA only",1,"High",0.5,0.5,5446,"20180301UTD_02","Pole fire reported. lis#1308857, Auditor on site. Burning at the king bolt.",null,null," - switch (disconnector/isolator)"]
[17,58,"2018-02-27","16:53:26",-37.927308779999997,145.00086859999999,"19 YUILLE STREET BRIGHTON",1805141,"MR 32","Low voltage AC (<1kV)","Urban"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,5448,"20180301UTD_03","Confirmed fire at the base pole, lis#1805141 and not spread. The lead coming out of the YUILLE ROSLYN transformer isolator has burnt off.  fire was out on arrival - area size of shoe box",null,null," - switch (earth)"]
[17,59,"2018-02-28","11:11:35",-38.307588789999997,145.17947359999999,"184 HIGH STREET HASTINGS",1110404,"HGS32","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,5449,"20180301UTD_04","Council tree branch cracked and fell onto HV in tee to High-Tavern S/S.  Small grass fire started underneath approx 2 square metres. CFA had already put out when crew arrived. LIS#1110404. Fire ignition report # 6724. ",null,null," - switch (FuseSaver)"]
[17,60,"2018-02-28","16:48:53",-37.885878480000002,145.1375281,"464 WAVERLEY ROAD MOUNT WAVERLEY",602741,"GW 03","Low voltage AC (<1kV)","Urban"," - overhead service conductor (residential)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,5451,"20180301UTD_05","Private tree loc at 462 Waverley came down, pulled service down, active/neutral sitting on tree cause branch to catch on fire, grass fire only in nature strip area, lis 602741.  I",null,null," - switch (any other type)"]
[17,61,"2018-03-01","04:36:47",-38.06805052,145.1231574,"14 BREEZE STREET BONBEACH",3302609,"CRM14","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5452,"20180302UTD_02","X-arm broken at pole LIS 3302609. Replaced xarm, repaired LV mains, replaced insulators on HV.",null,null,"SCADA, network control and protection systems"]
[17,62,"2018-03-01","05:21:00",-38.001837549999998,145.0875011,"32 BARKLY STREET MORDIALLOC",1807136,"MC 02","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5460,"20180308UTD_05","Hv termination xarm needs to be replaced - & hv pff fuse units & hv droppers  needs to be replaced  lis# 1807136  - ",null,null," - audio frequency load controller (AFLC)"]
[17,63,"2018-03-01","05:42:09",-37.942283410000002,145.10217,"113 ELDER STREET CLARINDA",2330256,"CDA22","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5455,"20180306UTD_02"," X arm burnt through at HV isols OA3477. Replaced x-arm and 3 HV isolators at OA3477. LIS 2330256",null,null," - arc suppresion coil"]
[17,64,"2018-03-01","06:07:14",-37.835817980000002,145.12122830000001,"2 ASQUITH STREET BOX HILL SOUTH",7037441,"BH 21","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5458,"20180308UTD_03","Arm broken 2 poles east of Station St in Asquith st. Tee Off conections broken at first pole in Asquith st. LIS 7037441",null,null," - automatic circuit recloser (ACR)"]
[17,65,"2018-03-01","07:07:16",-37.835976469999999,145.19510439999999,"678 MITCHAM ROAD VERMONT",639555,"RWT24","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5461,"20180309UTD_01","@0637 hrs mfb advised are on site - insulator has burnt off - HV is stiing on it and about to drop - xarm is on fire and mfb request attendance asap as they require to put water on fire, lis # 0639555 ",null,null," - communications linear assets"]
[17,66,"2018-03-01","07:07:25",-37.950744659999998,145.0870927,"47 GOLF VIEW ROAD HEATHERTON",1814372,"HT 10","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5462,"20180309UTD_02","X-arm fire damaged at T-off Golf View Cnr Henry. LIS 1814372. X-arm replaced under access permit.",null,null," - communications network assets"]
[17,67,"2018-03-01","07:39:32",-37.832298049999999,145.17998689999999,"1 WENDY STREET FOREST HILL",7033459,"NW 33","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Low-moderate",0.2,4.0000000000000008E-2,5463,"20180309UTD_03","LIS #7033459 pole fire / X-Arm failure Mt Pleasant Rd  X-arm replaced under Access Permit. ",null,null," - communications site infrastructure"]
[17,68,"2018-03-07","22:38:44",-37.869741810000001,144.97749279999999,"19 SPENSER STREET ST KILDA",2306019,"EW 12","11kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,5470,"20180313UTD_04","Private  large private palm tree located at #19 Spencer St buring out on hv street mains - G&B crew to attend first thing AM Thurs 8/3/18 to cut back tree - lis: 2306019",null,null," - field devices"]
[17,69,"2018-03-08","18:31:47",-37.884297449999998,144.9909998,"11A FOAM STREET ELWOOD",2308135,"EW 14","11kV AC","Urban"," - surge diverter","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,5474,"20180315UTD_02","lis 2308135 per MFB o/s #11 - fuses activated at lis 2308130 per mfb - Suspected Surge arrestor exploded igniting some vegetation underneath",null,null," - local network wiring assets"]
[17,70,"2018-03-09","08:11:20",-38.381844000000001,145.12427600000001,"5 YORK AVENUE BALNARRING",1106688,"HGS23","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (residential)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,{"$f":"IF(OR(P107=\"\",R107=\"\"),\"\",IF(AND(O107=\"within electric line construction area\",Q107=\"No forecast\"),1,P107*R107))","v":0.1},5523,"20180501UTD_03","Private tree rubbed through service and caught fire approx 2sqm on ground replaced grey twisted service that had rub thru on cust tree, LIS - 1106688, tree cut back",null,null," - master station assets"]
[17,71,"2018-03-10","18:52:27",-38.250130079999998,145.08184249999999,"945 MOOROODUC HIGHWAY MOOROODUC",1104826,"MTN24","Low voltage AC (<1kV)","Rural Short"," - connection box","single phase","Started in or originated from a distribution system","HBRA only",1,"Very high",1,1,5473,"20180313UTD_06","replcd 100amp fuse box due to burnt out box caused fire on the ground... fire report # 6761…..LIS 1104826",null,null," - neutral earthing resistor"]
[17,72,"2018-03-17","08:09:01",-38.374246319999997,145.090305,"35 STANLEYS ROAD MERRICKS",1108223,"MTN32","22kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Severe",2,2,5484,"20180320UTD_02","Tree on OHC , lis1108223 tee ex MT0227 spur. ACR open to L/O S/E/F 50a. Tree inside #31 Stanleys Rd",null,null," - oil-filled circuit recloser (OCR)"]
[17,73,"2018-03-17","14:12:42",-38.227520900000002,145.15946149999999,"66 CLARENDON DRIVE SOMERVILLE",1112407,"HGS22","22kV AC","Rural Short"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,5524,"20180501UTD_04","Passer by reported flames, sparking and acking from pole top. Tx + fuse units flashed over and have been replaced, system restored to normal.  LIS 1112407",null,null," - rapid earth fault current limiter (REFCL)"]
[17,74,"2018-03-18","10:58:08",-37.944148490000003,145.077719,"125 COCHRANES ROAD MOORABBIN",1815975,"HT 03","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,5481,"20180319UTD_04","x arm fire - lis 1815975 - HV strain arm burnt and req replacement - blue phase HV insulator on top of strain arm tracked to x-arm. ",null,null," - surge diverter"]
[17,75,"2018-03-18","12:48:04",-37.9924082,145.07235650000001,"29 THE CORSO  PARKDALE",1808896,"M  35","11kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,5482,"20180319UTD_05","Crew found HV int xarm broken with HV conductor hanging close to LV. LIS#1808896 Antibes St Nth of Corso. ",null,null," - voltage regulator"]
[17,76,"2018-03-18","12:58:04",-37.795918630000003,145.14190679999999,"85 WETHERBY ROAD DONCASTER",7061588,"DC 03","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Severe",2,0.4,5485,"20180320UTD_03","Part of DC10 DC3 feeder fault -Tree in park failed starting a ground fire - fire report 03009…..LIS 7061588",null,null,"Public lighting"]
[17,77,"2018-03-18","13:06:23",-38.022721349999998,145.2046588,"54 ELLIOTT ROAD DANDENONG SOUTH",635717,"DSH14","22kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Severe",2,0.4,5486,"20180320UTD_04"," Crew found 66/22 KV pole broken due to a pole fire at the king bolt of the tee off xarm LIS#0635717. ",null,null," - brackets (major road)"]
[17,78,"2018-03-18","13:25:47",-37.849936249999999,145.11574619999999,"213 BURWOOD HIGHWAY BURWOOD",7029110,"EB 11","Low voltage AC (<1kV)","Urban"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Severe",2,0.4,5525,"20180501UTD_05","Refer to TE#1162535. Crew found private tree from Deakin Uni on the LV mains at LIS#7029110 which caused a 15E BA fuse Bph to blow at the TX",null,null," - brackets (minor road)"]
[17,79,"2018-03-18","13:26:25",-38.346526849999997,144.9556019,"12 BRACKEN RIDGE DROMANA",1306759,"DMA13","22kV AC","Urban"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Severe",2,2,5487,"20180321UTD_01","CFAadvised that live line is whipping around on the ground causing grass spot fires-  refer details on f tbl 1162842….LIS 1306759",null,null," - lamps (major road)"]
[17,80,"2018-03-18","14:17:24",-38.227758090000002,145.19154349999999,"12 DROVERS LANE SOMERVILLE",1109045,"HGS33","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Severe",2,0.4,5488,"20180321UTD_02","Cause was private tree branch from number 14 Drovers Lane at LIS# 1109045. Damage: HV condctor on deck as above and to be repaired under A/P. Small grass fire started on site. ",null,null," - lamps (minor road)"]
[17,81,"2018-03-18","17:20:10",-38.40357899,145.06961989999999,"3670 FRANKSTON-FLINDERS RD, MERRICKS",9648679,"DMA15","22kV AC","Rural Short"," - overhead conductor (bare; steel)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Severe",2,2,5489,"20180322UTD_01","Large tree failed and brought down HV, 100m2 grass fire, LIS 9648679",null,null," - luminaires (major road)"]
[17,82,"2018-03-19","21:30:00",-38.10340437,145.128545,"48 RAILWAY PARADE SEAFORD",3306355,"CRM33","22kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,5492,"20180322UTD_04","Top of HV / LV pole on fire at 2 way tee pole corner of Station St and Railway Pde in Seaford. Emergency switching to de-energise 22 kV conductors to allow Fire brigade to put out fire. Fire Report #6824.  LIS 3306355",null,null," - luminaires (minor road)"]
[17,83,"2018-03-20","00:17:00",-38.075042420000003,145.12277929999999,"499 STATION STREET CARRUM",3304906,"CRM12","22kV AC","Urban"," - insulators","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,5527,"20180502UTD_01","Also see TE# 1163349. Cause was tracking of HV fuse units in misty weather, which flashed over to steel x-arm / concrete pole. LIS 3304906",null,null," - poles / columns (major road)"]
[17,84,"2018-03-21","13:06:18",-38.274650659999999,145.02908479999999,"21 GREENFIELD WAY MOUNT MARTHA",1102825,"DMA24","22kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,5494,"20180326UTD_01","Tree bought down HV ex HV fuses MT0042. LIS# 1102825 29 Greenfield rd. (5 doors down from Bay rd). 1 Bay of single phase HV on the ground. Repaired under AP.",null,null," - poles / columns (minor road)"]
[17,85,"2018-03-22","20:16:31",-38.382997369999998,144.9229263,"20 WAKOOL AVENUE ROSEBUD",1311483,"RBD12","Low voltage AC (<1kV)","Rural Short"," - overhead service conductor (residential)","single phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"High",0.5,0.1,5495,"20180326UTD_02","Replaced OH single phs service, cut cust tree clear, tested and left on. Started small fire half sq meter, already put out, service had rubbed through on tree,   fire start fire report 6825. LIS# 1311483.",null,null,"Other "]
[17,86,"2018-03-24","10:50:43",-37.984541700000001,145.1410649,"1 TERALBA CLOSE DINGLEY VILLAGE",618974,"NP 12","22kV AC","Urban"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,5526,"20180501UTD_06","LIS 0618974 - MFB reported pole on fire, On arrival flex had burnt off and likely cause was a possum…..however will record as connection failure",null,null," - connection box"]
[17,87,"2018-03-24","11:10:57",-38.107373389999999,145.1530874,"217R AUSTIN ROAD SEAFORD",3307951,"FTN12","22kV AC","Urban"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,5528,"20180502UTD_02","Tree branch on HV bushing, removed and replaced 16A PFF. lis 3307951. Bushing cover melted and cleaned up with new cover under EAP26809 I@15:55 C@16:05. Possom proofed.",null,null," - earth / earthing"]
[17,88,"2018-03-24","14:35:00",-37.81597249,145.16671210000001,"19 PEACEDALE GROVE NUNAWADING",7029117,"NW 21","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,5500,"20180328UTD_01","MFB advised pole fire at lis # 7029117 - This was alledgedy caused by lightening"]
[17,89,"2018-03-24","15:35:48",-38.043177579999998,145.12575570000001,"42 JACKSONS ROAD CHELSEA",3304380,"CRM35","Low voltage AC (<1kV)","Urban"," - underground cable","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,5529,"20180502UTD_03","LV crutch on U/G has blown up, requires U/G to repair  -  ug reterminated cabled that had blown at the crutch at the pole lis# 3304380 replcd white & blue 160amp hrc fuses"]
[17,90,"2018-03-26","13:36:00",-38.382314909999998,144.83208479999999,"2 CRESTVIEW COURT RYE",1317970,"STO23","22kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,5502,"20180329UTD_02","Tracking at LV X-arm King Bolt, cause pole to break, HV swinging in the air - clashed, pole LSI#1317970. crew to replace pole with HV LV strain arm with bus fuse isols on LV. 12.5/12 pole.",null,null,"Extra low voltage AC (<50V)"]
[17,91,"2018-04-11","00:49:29",-37.794009170000002,145.1418615,"77 WETHERBY ROAD DONCASTER",7061503,"DC 03","22kV AC","Urban"," - connector / termination","three phase","Started in or originated from a distribution system","LBRA only",0.2,"High",0.5,0.1,5511,"20180427UTD_04","Possum on HV open HV bridges, #3 Dunoon.  LIS#7061503 This caused HV wire on ground cnr Dunoon and Wetherby (Ampac failed at this location and centre phase HV conductor made contact with white phase LV),",null,null,"Low voltage AC (<1kV)"]
[17,92,"2018-04-12","00:02:00",-38.192153130000001,145.20681619999999,"70 WEST ROAD LANGWARRIN SOUTH",3301177,"HGS33","Low voltage AC (<1kV)","Rural Short"," - underground service cable (residential)","two phase","Started by any person, bird, reptile or other animal coming into contact with a distribution system","HBRA only",1,"Very high",1,1,5512,"20180427UTD_05","LIS# 3301177 - Pole only slight schorch marks, person had tied chain around pole to remove car from trailer, which damaged assets and caused a small fire- few square meters under base of pole,  fire report 03822",null,null,"2.2kV AC"]
[17,93,"2018-04-14","10:24:44",-38.374064199999999,145.12537349999999,"3045 FRANKSTON-FLINDERS ROAD BALNARRING",1105857,"MTN32","22kV AC","Rural Short"," - overhead conductor (bare; all aluminium conductor)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","LBRA only",0.2,"Very high",1,0.2,5556,"20180608UTD_02","Reported as tree on fire by CFA,  Tree removed from the overhead. Tree out side 3045 Frankston Flind Rd Balnarring",null,null,"6.6kV AC"]
[17,94,"2018-04-14","10:56:35",-38.33859004,145.12200669999999,"230 MYERS ROAD BALNARRING",3440979,"HGS23","22kV AC","Rural Short"," - overhead conductor (bare; aluminium core steel reinforced)","three phase","Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system","HBRA only",1,"Very high",1,1,5557,"20180608UTD_03","Cust reporting that tree branch on lines is currently on fire - Private tree branch has been taken off overhead conductors, no damage to UE assets/no follow up required, lis 3440979,",null,null,"11kV AC"]
[17,95,"2018-04-14","12:35:18",-37.982583230000003,145.0244447,"1 SURF AVENUE BEAUMARIS",1811508,"BR 04","11kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,5515,"20180430UTD_01","HV X-Arm burnt at Lis 1811508,  EAP#48659 I@19:45 C@21:15, x-arm replaced and ok for service. ",null,null,"12.7kV AC (SWER)"]
[17,96,"2018-04-14","13:07:46",-37.97207246,145.06254809999999,"1300 NEPEAN HIGHWAY CHELTENHAM",1822160,"M  23","11kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"Very high",1,0.2,5517,"20180430UTD_03","CH8926 discs damaged and pole top burning. - resagged and repaired 3 x HV conductors and replaced 2x poly HV insulators lis # 1822160- follow up is required new pole and gas switch - Fire report 2012  by",null,null,"22kV AC"]
[17,97,"2018-05-08","08:05:00",-38.318489839999998,144.98716020000001,"90 MARINE DRIVE, SAFETY BEACH",8825005,"DMA14","22kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5536,"20180514UTD_01","Pole fire at MARINE PRESCOTT s/s pole to be replaced under EAP. LIS 8825005",null,null,"33kV AC"]
[17,98,"2018-05-08","18:00:32",-37.940257619999997,145.02872579999999,"41 WIDDOP CRESCENT HAMPTON EAST",1821596,"SR 14","Low voltage AC (<1kV)","Urban"," - connection box","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5537,"20180517UTD_01","replaced burnt out 3ph fmjb on ug service feeding cricket club (LIS 1821596)",null,null,"66kV AC"]
[17,99,"2018-05-09","23:19:56",-38.338494529999998,144.96965539999999,"2 FRIEDA STREET DROMANA",1317512,"DMA13","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5538,"20180517UTD_03","crew found a HV xarm fire at pole Lis#1317512, and replaced it under EAP. PM notif# 1000651866",null,null,"132kV AC"]
[17,100,"2018-05-14","21:00:00",-37.94411625,145.06795750000001,"35A ROBERNA STREET MOORABBIN",1816408,"HT 13","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5551,"20180531UTD_02"," Crew advise burnt marks on the x-arm 35% and 20% on pole at x-arm. Followedup with duty officer who will arrange crew to replace x-arm tonight. Lis#1816408 at front of 31 ROBERNA ST MOORABBIN VIC 3189. ",null,null,"220kV AC"]
[17,101,"2018-05-17","18:49:00",-37.941950949999999,145.1022309,"109 ELDER STREET CLARINDA",2330255,"CDA22","22kV AC","Urban"," - crossarm (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5540,"20180522UTD_01","crossarm fire, section switched out for AP emergency switching, refer LIS 2330255",null,null,"330kV AC"]
[17,102,"2018-05-26","21:06:39",-37.96495762,145.17354700000001,"99A LIGHTWOOD ROAD NOBLE PARK",620877,"NP 25","Low voltage AC (<1kV)","Urban"," - luminaries (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,{"$f":"IF(OR(P139=\"\",R139=\"\"),\"\",IF(AND(O139=\"within electric line construction area\",Q139=\"No forecast\"),1,P139*R139))","v":2.0000000000000004E-2},5552,"20180531UTD_01","Crew replaced 1x150HPS street light after being burnt out. Pole is ok. Lis#0620877.",null,null,"500kV AC"]
[{"$f":"COUNTA(C140:O140,Q140,T140:V140)","v":17},103,"2018-05-26","23:50:59",-37.787902289999998,145.11929169999999,"551 DONCASTER ROAD DONCASTER",7055915,"WD 23","22kV AC","Urban"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",{"$f":"IF(O140=\"\",\"\",IF(O140=\"LBRA only\",0.2,IF(O140=\"HBRA only\",1,IF(O140=\"within electric line construction area\",19.8,IF(O140=\"within area delineated on plan LEGL./16-354\",4.6,\"\")))))","v":0.2},"No forecast",{"$f":"IF(Q140=\"\",\"\",IF(Q140=\"No forecast\",0.1,IF(Q140=\"Low-moderate\",0.2,IF(Q140=\"High\",0.5,IF(Q140=\"Very high\",1,IF(Q140=\"Severe\",2,IF(Q140=\"Extreme\",3.5,5)))))))","v":0.1},2.0000000000000004E-2,5558,"20180608UTD_04","MFB reported a fire and upon attendance a HV SW connection failed at a manual gas SW DT 0077 in Baily Grove Lis 7055915",null,null,"Extra low voltage DC (<120V ripple free)"]
[17,104,"2018-05-29","20:46:43",-38.012383800000002,145.0907076,"28 NEPEAN HWY ASPENDALE",3302246,"MC 01","Low voltage AC (<1kV)","Urban"," - dropper / bridge","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5555,"20180608UTD_01","Crew isolated the substation LV/HV and replaced the TX LV leads and Krone box as they had melted together. LIS # 3302246. ",null,null,"Low voltage DC (<1.5kV)"]
[17,105,"2018-05-31","16:55:24",-37.823082669999998,145.21209469999999,"2 WALWA STREET MITCHAM",7029309,"RWT34","22kV AC","Urban"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5553,"20180601UTD_01","Pole LIS 7029309, Culwell Av cnr Walwa St, HV anchor pole has burnt off approx 1 metre from the top. d. Ppole replaced under EAP #11320.  No report of any ground fire present.",null,null,"600V DC"]
[17,106,"2018-06-08","12:08:42",-38.256663940000003,145.1895883,"1506 FRANKSTON-FLINDERS ROAD TYABB",1108046,"HGS33","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5561,"20180612UTD_01","FRANKSTON-FLINDERS RD, LIS #1108046, 3 . Pole burning at the x-arm strap. Tracking down the pole from the top 22kV x-arm to the lighting bracket (below the LV) fire report # 00710",null,null,"1500V DC"]
[17,107,"2018-06-09","17:11:23",-38.338897930000002,144.73056800000001,"38 NORMANBY ROAD SORRENTO",1306940,"STO13","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5562,"20180612UTD_02","There was a fire at the fmb up the pole. no fire on the ground. crew replaced the FMB LIS # 1306940. Fire Report #  05305 ",null,null,"Earthing cable"]
[17,108,"2018-06-12","06:47:45",-38.220457459999999,145.04082769999999,"67 BARKLY STREET, MORNINGTON",9833531,"MTN21","Low voltage AC (<1kV)","Urban"," - luminaries (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5568,"20180626UTD_01","150w SL head burnt out. no flames visible. mfb on site. isolated SL pole# 9833531 at FMB on LIS# 1100704. head will require repalcement. TO# 1187484 raised for ace"]
[17,109,"2018-06-15","09:35:00",-37.833039210000003,145.15932570000001,"1A LAGOONA COURT BLACKBURN",7026473,"BH 11","Low voltage AC (<1kV)","Urban"," - luminaries (major road)","single phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5571,"20180626UTD_02","burnt out S/L head on lis # 7026473, 150 HPS lantern, isolated at service on lis # 7018257, traffic control required or do early or late in day, refer # 1189087"]
[17,110,"2018-06-16","06:32:05",-38.35817488,145.16248640000001,"1 WELLINGTON ROAD BITTERN",1107245,"HGS23","22kV AC","Rural Short"," - fuse (EDO fuse)","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,5566,"20180619UTD_01","LIS#1107245   Single phase sub , footpath fuse candling. replace 6 amp edo",null,null,"single wire earth return (SWER)"]
[17,111,"2018-06-19","04:30:00",-38.356940160000001,144.7508052,"1 KEATING AVENUE SORRENTO",1306410,"STO13","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","HBRA only",1,"No forecast",0.1,0.1,5572,"20180626UTD_03","repl 2 x 3ph FMB's - lis 1306410 - fire report 2044 - nst all ok and supply left on affecting #2-6, 8 and 10 - fire out on arrival - poss salt corrosion",null,null,"single phase"]
[17,112,"2018-06-25","13:09:54",-38.136116370000003,145.12891629999999,"72 DANDENONG ROAD FRANKSTON",8818998,"FTN14","Low voltage AC (<1kV)","Urban"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5595,"20180720UTD_02","Customer reported \"power pole on fire, half way up pole\" Replaced 3ph FMB feeding p2p U/g to #68,  ,lis # 8818998, ",null,null,"two phase"]
[17,113,"2018-06-26","23:58:00",-38.253624260000002,145.057301,"118 RACECOURSE ROAD MOUNT MARTHA",9751716,"MTN24","22kV AC","Rural Short"," - pole (wood)","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5581,"20180710UTD_01","lis#9751716  Confirmed pole fire. Suspect HV insulators tracking. Pole burnt out and needs replacing. Fire report # 04449 per S Goodman.",null,null,"three phase"]
[17,114,"2018-06-30","20:05:26",-38.383795339999999,144.79294329999999,"10 CLEMATIS COURT RYE",1318371,"STO21","Low voltage AC (<1kV)","Rural Short"," - connection box","three phase","Started in or originated from a distribution system","LBRA only",0.2,"No forecast",0.1,2.0000000000000004E-2,5582,"20180710UTD_02","Repaired connections at FOLCB at pole end to house 24. repaired connection to service at num 22. Fire report at pole end. # 6762. LIS 1318371"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Negligible: no ground fire"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Localised: less than 10 sq.m"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Small: 10 - 1000 aq.m"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Medium: 1000 sq.m - 10 ha"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Large: more than 10 ha"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Started in or originated from a distribution system"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Started by any tree, or part of a tree, falling upon or coming into contact with a distribution system"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Started by any person, bird, reptile or other animal coming into contact with a distribution system"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Started by lightning striking a distribution system or a part of a distribution system "]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Started by any other thing forming part of or coming into contact with a distribution system"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Otherwise started by a distribution system"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"Y177+1","v":11}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"Y178+1","v":12}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,13]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,14]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,15]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,16]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,17]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,18]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,19]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,20]

{"sheet":"3. Systems and Audit","index":4,"n_rows":29,"n_cols":5,"rows_kept":29,"cut":false,"hidden":false,"merged":[[28,1,29,4],[3,5,3,6],[4,5,4,6],[5,5,5,6],[6,1,6,4],[9,1,9,4],[14,1,14,4],[10,1,10,4],[13,1,13,4],[12,1,12,4],[11,1,11,4]]}
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name]\", Cover!D27)","v":"United Energy"}]
[null,"F-factor data reporting"]
[null,{"$f":"IF(Cover!D33=\"\",\"[Year]\",Cover!D33)","v":"2017/18"}]
[]
[]
[null,"Instructions:"]
[]
[null,{"$f":"IF(Cover!D27=\"\",\"[DNSP Name] must provide:\", CONCATENATE(Cover!D27,\" must provide:\"))","v":"United Energy must provide:"}]
[]
[null,"Table 4 - Information or reporting systems"]
[null,"   (1) Name of any IT system used to collect fire start data or fault event data - i.e. SCADA system, or fault reporting system"]
[null,"   (2) Whether the fire recording or fault recording process has been audited or complies with a relevant Australian or industry standard - Yes or No"]
[null,"   (3) List any relevant Australian or industry standards that the fire recording or fault recording process complies with"]
[null,"   (4) Whether the data entered into or removed from the IT system has been audited - Yes or No"]
[]
[]
[null,"Table 4: Information or reporting systems"]
[]
[null,"Information or reporting systems","Name","System Audited","Relevant Standards"]
[null,"System 1","Distribution Management System (DMS)","Yes","None"]
[null,"System 2","SCADA","No","None"]
[null,"System 3 ","GIS","Yes","None"]
[null,"System 4","OSIRIS","Yes","None"]
[null,"System 5"]
[null,"System 6"]
[null,"System 7"]
[null,"System 8"]
[]
[null,"The SGSPAA Internal Audit function undertakes a programme of work in accordance with the SGSPAA Group Internal Audit Plan. This internal audit activity covers elements of the systems and process used for capturing, recording and maintaining fire start data."]