## Overhead Service All
Asset Life Cycle Costing
Part 1: Population Asset Data | [7 empty] | Part 2: Management Options per km | [8 empty] | Part 3: Model Outputs |  | Adjust Chart Titles / Data Range as required.
Total Assets in SubGroup | 364628 | Services | [16 empty] | 28 | 25 | 27 | 18
[7 empty] | Option # | Option 1 | Option 2 | Option 3 | Option 4 | Option 5 | Option 6 | Option 7 | Option 8 | 1 |  |  | Installation Cost | Inspection Cost | Failure Cost | Failure Rate | Total Cost
Purchase Cost | 642 | [5 empty] | Description | Do No maintenance | Condition Monitoring | Inspect and Maintain | Proactive Replacement |  |  |  |  | 2 | Option 1 | Do No maintenance | 6.1731 | 0 | 78.5563 | 2927 | 84.7294
Total Assets in Group | 364628 | [14 empty] | 3 | Option 2 | Condition Monitoring | 6.1731 | 2.7425 | 15.7113 | 585.4 | 24.6269
Average Fleet Failure Rate | 585.4 | Failures |  |  |  |  | Purchase | 642 | 642 | 642 | 642 |  |  |  |  | 4 | Option 3 | Inspect and Maintain | 12.3462 | 0 | 78.408 | 585.4 | 90.7542
Fleet λ | 1.6055 | Failures/1000/Yr |  |  |  |  | Comment on Outcome | [8 empty] | 5 | Option 4 | Proactive Replacement | 17.589 | 0 | 7.8459 | 528.9 | 25.4349
Current Management Option | Option 2 | [14 empty] | 6 | Option 5 | 0 | 0 | 0 | 0 | 0 | 0
Average Life | 104.1794 | Years |  |  |  |  | AMI program |  | 2.7425 | [6 empty] | 7 | Option 6 | 0 | 0 | 0 | 0 | 0 | 0
Annual Proactice Replacements | 3500 | km |  |  |  |  | Inspection | [8 empty] | 8 | Option 7 | 0 | 0 | 0 | 14.1949 | 528.9 | 14.1949
[7 empty] | Act 3 Cost | [8 empty] | 9 | Option 8 | 0 | 0 | 0 | 0 | 0
[7 empty] | Act 4 Cost | [8 empty] | 10
[7 empty] | Act 5 Cost | [8 empty] | 11
[7 empty] | Act 1 Interval |  | 1 |  |  |  |  | 1 |  | 12
Failure Mode Data: | FM1 | FM2 | FM3 | FM4 | FM5 | Weighted Average | Act 2 Interval | [6 empty] | 1 |  | 13
Description | Mechanical | Vegetation | Vehicle |  |  |  | Act 3 Interval | [8 empty] | 14
Annual # of Events | 113 | 455.6 | 16.8 |  |  |  | Act 4 Interval | [8 empty] | 15
Consequence - Reliability | 6.3 | 6.3 | 6.3 |  |  | 6.3 | Act 5 Interval | [8 empty] | 16
Consequence - Safety | 50575.2212 |  |  |  |  | 9762.5555 | [9 empty] | 17
Consequence - Enviro | [5 empty] | 0 | Fleet Annual # of failures | 2927 | 585.4 | 585.4 | 528.9 |  |  | 528.9 |  | 18
Consequence - Other | 17.219 | 17.219 | 17.219 |  |  | 17.219 | [9 empty] | 19
Proportion of all Failures | 19.3% | 77.83% | 2.87% | 0% | 0% | [10 empty] | 20
Total Cost | 50598.7402 | 23.519 | 23.519 | 0 |  | 9786.0745 | [9 empty] | 21
[8 empty] | Annual Cost per Asset | [7 empty] | 22
[7 empty] | Installation | 642 | 642 | 642 | 642 | 0 | 0 | 0 |  | 23
[7 empty] | Lifetime | 104 | 104 | 52 | 36.5 | 98.8 | 109.2 | 104 |  | 24
[7 empty] | Annual Maint Cost | 0 | 2.7425 | 0 | 0 | 0 | 0 | 0 |  | 25
[7 empty] | Annual Failures | 0.0080274 | 0.0016055 | 0.0016055 | 0.0014505 | 0 | 0 | 0.0014505 |  | 26
[7 empty] | Annual Failure Cost | 78.5563 | 15.7113 | 78.408 | 7.8459 | 0 | 0 | 14.1949 |  | 27
[7 empty] | Annual Capex | 6.1731 | 6.1731 | 12.3462 | 17.589 | 0 | 0 | 0 |  | 28
29
30
[7 empty] | Total Cost | 84.7294 | 24.6269 | 90.7542 | 25.4349 | 0 | 0 | 14.1949 |  | 31
[7 empty] | %RAV | 12.24% | 2.874% | 12.21% | 1.222% | #DIV/0! | #DIV/0! | #DIV/0! |  | 32

## Overhead Service NS
Asset Life Cycle Costing
Part 1: Population Asset Data | [7 empty] | Part 2: Management Options per km | [8 empty] | Part 3: Model Outputs |  | Adjust Chart Titles / Data Range as required.
Total Assets in SubGroup | 14476 | Services | [16 empty] | 28 | 25 | 27 | 18
[7 empty] | Option # | Option 1 | Option 2 | Option 3 | Option 4 | Option 5 | Option 6 | Option 7 | Option 8 | 1 |  |  | Installation cost | Inspection cost | Failure cost | Failure Rate | Total Cost
Purchase Cost | 642 | [5 empty] | Description | No maintenance | Condition monitoring (AMI) | Proactive replacement (5Y) | Proactive replacement (10Y) | Inspect and maintain |  |  |  | 2 | Option 1 | No maintenance | 64.2 | 0 | 1048.7585 | 393.7731 | 1112.9585
Total Assets in Group | 364628 | [14 empty] | 3 | Option 2 | Condition monitoring (AMI) | 64.2 | 2.7425 | 209.7517 | 78.7546 | 276.6942
Average Fleet Failure Rate | 78.7546 | Failures |  |  |  |  | Purchase | 642 | 642 | 642 | 642 | 642 |  |  |  | 4 | Option 3 | Proactive replacement (5Y) | 256.8 | 2.7425 | 111.0743 | 41.7046 | 370.6168
Fleet λ | 5.4404 | Failures/1000/Yr |  |  |  |  | Comment on Outcome | [8 empty] | 5 | Option 4 | Proactive replacement (10Y) | 128.4 | 2.7425 | 111.0743 | 41.7046 | 242.2168
Current Management Option | Option 2 | [14 empty] | 6 | Option 5 | Inspect and maintain | 64.2 | 10 | 419.5034 | 157.5093 | 493.7034
Average Life | 7.7895 | Years |  |  |  |  | AMI program |  | 2.7425 | 2.7425 | 2.7425 |  |  |  |  | 7 | Option 6 | 0 | 0 | 0 | 0 | 0 | 0
Annual Proactice Replacements | 1858.4071 | Services |  |  |  |  | Inspection |  |  |  |  | 100 |  |  |  | 8 | Option 7 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Act 3 Cost | [8 empty] | 9 | Option 8 | 0 | 0 | 0 | 0 | 0
[7 empty] | Act 4 Cost | [8 empty] | 10
[7 empty] | Act 5 Cost | [8 empty] | 11
[7 empty] | Act 1 Interval |  | 1 | 1 | 1 |  |  |  |  | 12
Failure Mode Data: | FM1 | FM2 | FM3 | FM4 | FM5 | Weighted Average | Act 2 Interval |  |  |  |  | 10 |  |  |  | 13
Description | Mechanical | Vegetation | Vehicle |  |  |  | Act 3 Interval | [8 empty] | 14
Annual # of Events | 60 | 18.0877 | 0.66697 |  |  |  | Act 4 Interval | [8 empty] | 15
Consequence - Reliability | 6.3 | 6.3 | 6.3 |  |  | 6.3 | Act 5 Interval | [8 empty] | 16
Consequence - Safety | 50575.2212 |  |  |  |  | 38531.2376 | [9 empty] | 17
Consequence - Enviro | [5 empty] | 0 | Fleet Annual # of failures | 393.7731 | 78.7546 | 41.7046 | 41.7046 | 157.5093 |  |  |  | 18
Consequence - Other | 17.219 | 17.219 | 17.219 |  |  | 17.219 | [9 empty] | 19
Proportion of all Failures | 76.19% | 22.97% | 0.8469% | 0% | 0% | [10 empty] | 20
Total Cost | 50598.7402 | 23.519 | 23.519 | 0 |  | 38554.7566 | [9 empty] | 21
[8 empty] | Annual Cost per Asset | [7 empty] | 22
[7 empty] | Installation | 642 | 642 | 642 | 642 | 642 |  |  |  | 23
[7 empty] | Lifetime | 10 | 10 | 2.5 | 5 | 10 |  |  |  | 24
[7 empty] | Annual Maint Cost | 0 | 2.7425 | 2.7425 | 2.7425 | 10 |  |  |  | 25
[7 empty] | Annual Failures | 0.027202 | 0.0054404 | 0.0028809 | 0.0028809 | 0.010881 |  |  |  | 26
[7 empty] | Annual Failure Cost | 1048.7585 | 209.7517 | 111.0743 | 111.0743 | 419.5034 |  |  |  | 27
[7 empty] | Annual Capex | 64.2 | 64.2 | 256.8 | 128.4 | 64.2 |  |  |  | 28
29
30
[7 empty] | Total Cost | 1112.9585 | 276.6942 | 370.6168 | 242.2168 | 493.7034 |  |  |  | 31
[7 empty] | %RAV | 163.4% | 33.1% | 17.73% | 17.73% | 66.9% |  |  |  | 32

## Overhead Service PVC
Asset Life Cycle Costing
Part 1: Population Asset Data | [7 empty] | Part 2: Management Options per km | [8 empty] | Part 3: Model Outputs |  | Adjust Chart Titles / Data Range as required.
Total Assets in SubGroup | 39211 | Services | [16 empty] | 28 | 25 | 27 | 18
[7 empty] | Option # | Option 1 | Option 2 | Option 3 | Option 4 | Option 5 | Option 6 | Option 7 | Option 8 | 1 |  |  | Installation cost | Inspection cost | Failure cost | Failure Rate | Total Cost
Purchase Cost | 642 | [5 empty] | Description | No maintenance | Condition monitoring (AMI) | Proactive replacement (5Y) | Proactive replacement (10Y) | Inspect and maintain |  |  |  | 2 | Option 1 | No maintenance | 64.2 | 0 | 728.9919 | 404.0024 | 793.1919
Total Assets in Group | 364628 | [14 empty] | 3 | Option 2 | Condition monitoring (AMI) | 64.2 | 2.7425 | 145.7984 | 80.8005 | 212.7409
Average Fleet Failure Rate | 80.8005 | Failures |  |  |  |  | Purchase | 642 | 642 | 642 | 642 | 642 |  |  |  | 4 | Option 3 | Proactive replacement (5Y) | 256.8 | 2.7425 | 70.4563 | 65.3005 | 329.9988
Fleet λ | 2.0607 | Failures/1000/Yr |  |  |  |  | Comment on Outcome | [8 empty] | 5 | Option 4 | Proactive replacement (10Y) | 128.4 | 2.7425 | 70.4563 | 65.3005 | 201.5988
Current Management Option | Option 2 | [14 empty] | 6 | Option 5 | Inspect and maintain | 64.2 | 10 | 291.5968 | 161.601 | 365.7968
Average Life | 42.1985 | Years |  |  |  |  | AMI program |  | 2.7425 | 2.7425 | 2.7425 |  |  |  |  | 7 | Option 6 | 0 | 0 | 0 | 0 | 0 | 0
Annual Proactice Replacements | 929.2035 | Services |  |  |  |  | Inspection |  |  |  |  | 100 |  |  |  | 8 | Option 7 | 0 | 0 | 0 | 118.732 | 65.8005 | 118.732
[7 empty] | Act 3 Cost | [8 empty] | 9 | Option 8 | 0 | 0 | 0 | 0 | 0
[7 empty] | Act 4 Cost | [8 empty] | 10
[7 empty] | Act 5 Cost | [8 empty] | 11
[7 empty] | Act 1 Interval |  | 1 | 1 | 1 |  |  | 1 |  | 12
Failure Mode Data: | FM1 | FM2 | FM3 | FM4 | FM5 | Weighted Average | Act 2 Interval |  |  |  |  | 10 |  | 1 |  | 13
Description | Mechanical | Vegetation | Vehicle |  |  |  | Act 3 Interval | [8 empty] | 14
Annual # of Events | 30 | 48.9939 | 1.8066 |  |  |  | Act 4 Interval | [8 empty] | 15
Consequence - Reliability | 6.3 | 6.3 | 6.3 |  |  | 6.3 | Act 5 Interval | [8 empty] | 16
Consequence - Safety | 190500 |  |  |  |  | 70729.7803 | [9 empty] | 17
Consequence - Enviro | [5 empty] | 0 | Fleet Annual # of failures | 404.0024 | 80.8005 | 65.3005 | 65.3005 | 161.601 |  | 65.8005 |  | 18
Consequence - Other | 17.219 | 17.219 | 17.219 |  |  | 17.219 | [9 empty] | 19
Proportion of all Failures | 37.13% | 60.64% | 2.236% | 0% | 0% | [10 empty] | 20
Total Cost | 190523.519 | 23.519 | 23.519 | 0 |  | 70753.2993 | [9 empty] | 21
[8 empty] | Annual Cost per Asset | [7 empty] | 22
[7 empty] | Installation | 642 | 642 | 642 | 642 | 642 | 0 | 0 |  | 23
[7 empty] | Lifetime (average) | 10 | 10 | 2.5 | 5 | 10 | 10.5 | 10 |  | 24
[7 empty] | Annual Maint Cost | 0 | 2.7425 | 2.7425 | 2.7425 | 10 | 0 | 0 |  | 25
[7 empty] | Annual Failures | 0.010303 | 0.0020607 | 0.0016654 | 0.0016654 | 0.0041213 | 0 | 0.0016781 |  | 26
[7 empty] | Annual Failure Cost | 728.9919 | 145.7984 | 70.4563 | 70.4563 | 291.5968 | 0 | 118.732 |  | 27
[7 empty] | Annual Capex | 64.2 | 64.2 | 256.8 | 128.4 | 64.2 | 0 | 0 |  | 28
29
30
[7 empty] | Total Cost | 793.1919 | 212.7409 | 329.9988 | 201.5988 | 365.7968 | 0 | 118.732 |  | 31
[7 empty] | %RAV | 113.6% | 23.14% | 11.4% | 11.4% | 46.98% | #DIV/0! | #DIV/0! |  | 32

## Overhead Service Other
Asset Life Cycle Costing
Part 1: Population Asset Data | [7 empty] | Part 2: Management Options per km | [8 empty] | Part 3: Model Outputs |  | Adjust Chart Titles / Data Range as required.
Total Assets in SubGroup | 310941 | Services | [16 empty] | 28 | 25 | 27 | 18
[7 empty] | Option # | Option 1 | Option 2 | Option 3 | Option 4 | Option 5 | Option 6 | Option 7 | Option 8 | 1 |  |  | Installation cost | Inspection cost | Failure cost | Failure Rate | Total Cost
Purchase Cost | 642 | [5 empty] | Description | No maintenance | Condition monitoring (AMI) | Proactive replacement (5Y) | Proactive replacement (10Y) | Inspect and maintain |  |  |  | 2 | Option 1 | No maintenance | 32.1 | 0 | 46.3115 | 2089.5578 | 78.4115
Total Assets in Group | 364628 | [14 empty] | 3 | Option 2 | Condition monitoring (AMI) | 32.1 | 2.7425 | 9.2623 | 417.9116 | 44.1048
Average Fleet Failure Rate | 417.9116 | Failures |  |  |  |  | Purchase | 642 | 642 | 642 | 642 | 642 |  |  |  | 4 | Option 3 | Proactive replacement (5Y) | 256.8 | 2.7425 | 70.4563 | 417.3449 | 329.9988
Fleet λ | 1.344 | Failures/1000/Yr |  |  |  |  | Comment on Outcome | [8 empty] | 5 | Option 4 | Proactive replacement (10Y) | 128.4 | 2.7425 | 70.4563 | 417.3449 | 201.5988
Current Management Option | Option 2 | [14 empty] | 6 | Option 5 | Inspect and maintain | 32.1 | 10 | 18.5246 | 835.8231 | 60.6246
Average Life | 666.3021 | Years |  |  |  |  | AMI program |  | 2.7425 | 2.7425 | 2.7425 |  |  |  |  | 7 | Option 6 | 0 | 0 | 0 | 0 | 0 | 0
Annual Proactice Replacements | 466.6667 | Services |  |  |  |  | Inspection |  |  |  |  | 100 |  |  |  | 8 | Option 7 | 0 | 0 | 0 | 9.0953 | 410.3782 | 9.0953
[7 empty] | Act 3 Cost | [8 empty] | 9 | Option 8 | 0 | 0 | 0 | 0 | 0
[7 empty] | Act 4 Cost | [8 empty] | 10
[7 empty] | Act 5 Cost | [8 empty] | 11
[7 empty] | Act 1 Interval |  | 1 | 1 | 1 |  |  | 1 |  | 12
Failure Mode Data: | FM1 | FM2 | FM3 | FM4 | FM5 | Weighted Average | Act 2 Interval |  |  |  |  | 10 |  | 1 |  | 13
Description | Mechanical | Vegetation | Vehicle |  |  |  | Act 3 Interval | [8 empty] | 14
Annual # of Events | 15.0667 | 388.5185 | 14.3264 |  |  |  | Act 4 Interval | [8 empty] | 15
Consequence - Reliability | 6.3 | 6.3 | 6.3 |  |  | 6.3 | Act 5 Interval | [8 empty] | 16
Consequence - Safety | 190500 |  |  |  |  | 6867.9603 | [9 empty] | 17
Consequence - Enviro | [5 empty] | 0 | Fleet Annual # of failures | 2089.5578 | 417.9116 | 417.3449 | 417.3449 | 835.8231 |  | 410.3782 |  | 18
Consequence - Other | 17.219 | 17.219 | 17.219 |  |  | 17.219 | [9 empty] | 19
Proportion of all Failures | 3.605% | 92.97% | 3.428% | 0% | 0% | [10 empty] | 20
Total Cost | 190523.519 | 23.519 | 23.519 | 0 |  | 6891.4793 | [9 empty] | 21
[8 empty] | Annual Cost per Asset | [7 empty] | 22
[7 empty] | Installation | 642 | 642 | 642 | 642 | 642 | 0 | 0 |  | 23
[7 empty] | Lifetime | 20 | 20 | 2.5 | 5 | 20 | 21 | 20 |  | 24
[7 empty] | Annual Maint Cost | 0 | 2.7425 | 2.7425 | 2.7425 | 10 | 0 | 0 |  | 25
[7 empty] | Annual Failures | 0.0067201 | 0.001344 | 0.0013422 | 0.0013422 | 0.002688 | 0 | 0.0013198 |  | 26
[7 empty] | Annual Failure Cost | 46.3115 | 9.2623 | 70.4563 | 70.4563 | 18.5246 | 0 | 9.0953 |  | 27
[7 empty] | Annual Capex | 32.1 | 32.1 | 256.8 | 128.4 | 32.1 | 0 | 0 |  | 28
29
30
[7 empty] | Total Cost | 78.4115 | 44.1048 | 329.9988 | 201.5988 | 60.6246 | 0 | 9.0953 |  | 31
[7 empty] | %RAV | 7.214% | 1.87% | 11.4% | 11.4% | 4.443% | #DIV/0! | #DIV/0! |  | 32

## Overhead Service NS Pre-AMI
Asset Life Cycle Costing
Part 1: Population Asset Data | [7 empty] | Part 2: Management Options per km | [8 empty] | Part 3: Model Outputs |  | Adjust Chart Titles / Data Range as required.
Total Assets in SubGroup | 43428 | Services | [16 empty] | 28 | 25 | 27 | 18
[7 empty] | Option # | Option 1 | Option 2 | Option 3 | Option 4 | Option 5 | Option 6 | Option 7 | Option 8 | 1 |  |  | Installation Cost | Inspection Cost | Failure Cost | Failure Rate | Total Cost
Purchase Cost | 642 | [5 empty] | Description | Do No maintenance | Condition Monitoring | Proactive Replacement - 5Y | Proactive Replacement - 10Y |  |  |  |  | 2 | Option 1 | Do No maintenance | 27.473 | 0 | 3948.0852 | 1181.3194 | 3975.5582
Total Assets in Group | 364628 | [14 empty] | 3 | Option 2 | Condition Monitoring | 27.473 | 0 | 789.617 | 236.2639 | 817.09
Average Fleet Failure Rate | 236.2639 | Failures |  |  |  |  | Purchase | 642 | 642 | 642 | 642 |  |  |  |  | 4 | Option 3 | Proactive Replacement - 5Y | 128.4 | 0 | 488.8282 | 146.2639 | 617.2282
Fleet λ | 5.4404 | Failures/1000/Yr |  |  |  |  | Comment on Outcome | [8 empty] | 5 | Option 4 | Proactive Replacement - 10Y | 64.2 | 0 | 488.8282 | 146.2639 | 553.0282
Current Management Option | Option 2 | [14 empty] | 6 | Option 5 | 0 | 0 | 0 | 0 | 0 | 0
Average Life | 23.3684 | Years |  |  |  |  | AMI program | [8 empty] | 7 | Option 6 | 0 | 0 | 0 | 0 | 0 | 0
Annual Proactice Replacements | 1858.4071 | Services |  |  |  |  | Inspection | [8 empty] | 8 | Option 7 | 0 | 0 | 0 | 488.8282 | 146.2639 | 488.8282
[7 empty] | Act 3 Cost | [8 empty] | 9 | Option 8 | 0 | 0 | 0 | 0 | 0
[7 empty] | Act 4 Cost | [8 empty] | 10
[7 empty] | Act 5 Cost | [8 empty] | 11
[7 empty] | Act 1 Interval | [6 empty] | 1 |  | 12
Failure Mode Data: | FM1 | FM2 | FM3 | FM4 | FM5 | Weighted Average | Act 2 Interval | [6 empty] | 1 |  | 13
Description | Mechanical | Vegetation | Vehicle |  |  |  | Act 3 Interval | [8 empty] | 14
Annual # of Events | 180 | 54.263 | 2.0009 |  |  |  | Act 4 Interval | [8 empty] | 15
Consequence - Reliability | 6.3 | 6.3 | 6.3 |  |  | 6.3 | Act 5 Interval | [8 empty] | 16
Consequence - Safety | 190500 |  |  |  |  | 145134.3283 | [9 empty] | 17
Consequence - Enviro | [5 empty] | 0 | Fleet Annual # of failures | 1181.3194 | 236.2639 | 146.2639 | 146.2639 |  |  | 146.2639 |  | 18
Consequence - Other | [5 empty] | 0 | [9 empty] | 19
Proportion of all Failures | 76.19% | 22.97% | 0.8469% | 0% | 0% | [10 empty] | 20
Total Cost | 190506.3 | 6.3 | 6.3 | 0 |  | 145140.6283 | [9 empty] | 21
[8 empty] | Annual Cost per Asset | [7 empty] | 22
[7 empty] | Installation | 642 | 642 | 642 | 642 | 0 | 0 | 0 |  | 23
[7 empty] | Lifetime | 23.3684 | 23.3684 | 5 | 10 | 22.2 | 24.5368 | 23.3684 |  | 24
[7 empty] | Annual Maint Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25
[7 empty] | Annual Failures | 0.027202 | 0.0054404 | 0.003368 | 0.003368 | 0 | 0 | 0.003368 |  | 26
[7 empty] | Annual Failure Cost | 3948.0852 | 789.617 | 488.8282 | 488.8282 | 0 | 0 | 488.8282 |  | 27
[7 empty] | Annual Capex | 27.473 | 27.473 | 128.4 | 64.2 | 0 | 0 | 0 |  | 28
29
30
[7 empty] | Total Cost | 3975.5582 | 817.09 | 617.2282 | 553.0282 | 0 | 0 | 488.8282 |  | 31
[7 empty] | %RAV | 615% | 123% | 76.14% | 76.14% | #DIV/0! | #DIV/0! | #DIV/0! |  | 32

## Constants
Safety Probabilities |  |  |  | Asset-Specific Constants for LCC Model
Asset | LTI | Death to Public | Death to Staff | Parameter | Value | Comment
LV Poles | 0.000816 | 3.264e-05 | 1.632e-05 | VCR | 42
11/22kV Poles | 0.000272 | 1.088e-05 | 5.44e-06 | COST_REPL_SERVICE | 642 | RMP Unit code 2018
66kV Poles | 0.000272 | 1.088e-05 | 5.44e-06 | COST_REPL_SERVICE_UG | 1242 | RMU Unit code 2018
Conductor (All) | 0.000544 | 2.176e-05 | 0.0001088 | NUM_REPL_ANNUAL | 3500 | rounded average annual replacements
Underground Cable >1kV | 7.5e-07 | 7.5e-08 | 7.5e-08 | COST_INSPECT_SERVICE | 100 | estimate rate
HV Insulators | 0.000544 | 2.176e-05 | 0.0001088 | Asset Data
Distribution Transformer | 2.6027e-05 | 0.00023 | 0.00019606 | # PVC Twisted | 39211
ZSS Power Transformer | 0.00026027 | 0.000115 | 0.0019606 | # Neutral Screened | 14476
ZSS Circuit Breaker | 0.00026027 | 0.000115 | 0.0019606 | # ABC (xlpe) | 281931
Instrument Transformer | 0.00026027 | 0.000115 | 0.0019606 | # Other Overhead | 29010
|  |  |  | # Underground | 108365
|  |  |  | Mech/Elec Faults/yr | 113 | Approx. from Tobie's data. 2018 only.
Safety Constants |  |  |  | Shocks per annum post-NST | 70 | Average # of shocks /pa. Tobie's data
VSL | 4490000 |  |  | Shocks per annum post-remDisc | 15 | Only one year of data - no historic as change in policy (AMI detection and remote disc program in operation)
VLTI | 127000 |  |  | Vehicle Faults / yr | 16.8
Public_DF | 3 |  |  | Vegetation Faults/yr | 455.6
Staff_DF | 3 |  |  | POC_Outage | 20% | was 80/20 now 20/80 with AMI detection program. Mech Failures only
Break-in_DF | 1 |  |  | PoC_Shock | 13.27%
|  |  |  | CoC_Service_Outage | 31.5 | 0.75kW (3kW average house peak * 50% MD * 50% utilisation) x 1 hour outage
Fire Constants |  |  |  | Shock Data by Service Type
IRU | 15000 | Ignition Risk Unit |  | NS_Shocks_yr | 6 | Neutral screen service shocks
Median IRU (HBRA) | 1 |  |  | PVC_Shocks_Yr | 6 | Consider as connector + twisted service shocks
Median IRU (LBRA) | 0.1 |  |  | Other_Shocks_Yr | 2
HBRA F-Factor Cost | 15000 |  |  | UG_Shocks_Yr | 1
LBRA F-Factor Cost | 1500 |  |  | Failure Data by Service Type | Note: doesn't get captured this way - assume shocks are proportional to failures to get a split.
Weighting to LBRA | 80% |  |  | NS_Failures_yr | 60 | NS are older, more likely to fail. But more likely to be detected by analytics
Average F-Factor | 4200 |  |  | PVC_Failures_yr | 30
|  |  |  | Other_Failures_yr | 15.0667
|  |  |  | UG_Failures_Yr | 7.5333
|  |  |  | PoC_Shock_PVC | 50% | PVC service failures cant be detected by AMI analytics.
|  |  |  | Fire Starts/Yr | 2.4 | average figure
|  |  |  | Fire Start PoC | 0.41%