## Option_evaluation
United Energy
Demand Management Evaluation: Lower Mornington Peninsula
All dollars are $ real 2019
INPUTS
All dollars are $ real 2019
Current demand management contract runs finishes in 2021
Cost of capex |  | 31475607.6237
Cost of DM/MW/PA |  | 86854.5981
Real WACC |  | 2.75%
Asset Life |  | 50
O&M cost as % of capex |  | 1%
COST ANALYSIS
1. Capex without demand management
|  | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27
Capex |  | 2021/22: 31475607.6237
Annualised Capex |  |  |  | 0 | 1165885.4482 | 1165885.4482 | 1165885.4482 | 1165885.4482 | 1165885.4482
O&M |  |  |  | 0 | 314756.0762 | 314756.0762 | 314756.0762 | 314756.0762 | 314756.0762
Total cost |  |  |  | 0 | 1480641.5245 | 1480641.5245 | 1480641.5245 | 1480641.5245 | 1480641.5245
NPV of capex without demand management |  | 2019/20: 6646793.424
Demand management annual cap |  | 2019/20: 1480641.5245
2. Deferred capex with demand management
|  | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27
Expected demand management MW required |  |  | 0 | 13.1 | 13.5 | 17.7 | 21.8 | 25.6
Deferred capital cost |  |  |  | 0 | 0 | 0 | 0 | 0 | 31475607.6237
Annualised Capex |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
O&M |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
Annual cost of demand management - uncapped |  |  |  | 1137795.2348 | 1172537.074 | 1537326.386 | 1893430.2381 | 2223477.7108 | 0
Annual cost of demand management - capped |  |  |  | 1137795.2348 | 1172537.074 | 1480641.5245 | 1480641.5245 | 1480641.5245 | 0
Total cost |  |  |  | 1137795.2348 | 1172537.074 | 1480641.5245 | 1480641.5245 | 1480641.5245 | 0
NPV of deferred capex with demand management |  | 2019/20: 6204076.9482
RECOMMENDED OPTION
NPV
1. Capex without demand management |  | 2019/20: 6646793.424
2. Deferred capex with demand management |  | 2019/20: 6204076.9482
(Cost)/Benefit from deferred capex with demand management |  | 2019/20: 442716.4758
Recommended option: | 2. Deferred capex with demand management

## Output_Opex
United Energy
Demand Management Evaluation: Lower Mornington Peninsula
All dollars are $ real 2019
Forecast opex ($'000, 2019)
|  | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | Total
| Opex Step Change | 875.0322 | 909.7741 | 1217.8785 | 1217.8785 | 1217.8785 | 5438.4419

## DM cost
United Energy
Demand Management Evaluation: Lower Mornington Peninsula
Estimate of DM cost per MW pa
Customer type | Customers | Cost $/MW pa | Estimated % participation | Expected DM (KW) | Weighted Ave Cost ($/MW pa) | Comments
Residential | 629183 | 136729.0502 | 15% | 0.65 |  | Cost/MW for residential customers based on Summer Saver
Commercial & Industrial | 46690 | 75933.0397 | 2% | 300 |  | Cost/MW for C&I customers based on average of MGE12 and Rosebud to Hastings
Average cost of DM ($/MW) |  |  |  |  | 86854.5981

## Tables
United Energy
Demand Management Evaluation: Lower Mornington Peninsula
Year | Annual cost of demand management | Annual cost of augmentation | Demand management economic?
2021/22 | 1137.7952 | 1480.6415 | Yes
2022/23 | 1172.5371 | 1480.6415 | Yes
2023/24 | 1537.3264 | 1480.6415 | No
2024/25 | 1893.4302 | 1480.6415 | No
2025/26 | 2223.4777 | 1480.6415 | No
Financial Year | Annual cost of demand management (capped) | Base year demand management costs | Step change
2021/22 | 1137.7952 | 262.763 | 875.0322
2022/23 | 1172.5371 | 262.763 | 909.7741
2023/24 | 1480.6415 | 262.763 | 1217.8785
2024/25 | 1480.6415 | 262.763 | 1217.8785
2025/26 | 1480.6415 | 262.763 | 1217.8785
Total |  |  | 5438.4419
| Existing program requirement |  |  |  | Forecast program requirement
| 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Required demand response (MVA) | 11.5 | 12.2 | 13.1 | 13.1 | 13.1 | 13.5 | 17.7 | 21.8 | 25.6
Type | Program | Cost/MVA/year | Average | Weighting | Contribution to unit cost
Residential | Summer Saver | 136.7291 | 136.7291 | 17.96% | 24.5624
Commercial, industrial | Rosebud to Hastings | 67.525
| MGE 12 | 81.25 | 74.3875 | 82.04% | 61.0243
Total DM unit cost |  |  |  |  | 85.5867